## Version history
Version | Changes | Date | External Firmware Version
V1.0.0 | Initial Version | 2025-12-26

## Overview
Sheet | Start | End | Length | Comments
Real time | 1 | 26 | 26
Power Quality | 27 | 39 | 13
Demand | 40 | 45 | 6
Energy | 46 | 69 | 24
Independent Input Channel | 70 | 99 | 30
IO Pulse Couter(DI) | 1 | 3 | 3
IO Status(DI) | 1 | 3 | 3

## Real time
Real Time | ID | Name | Description | Object Type | Data type | RW | Unit
| 1 | Freq_rms | System Frequency | Object Analog Input | float | R | Hertz
| 2 | Ua_rms | Phase A Line-to-Neutral Voltage | Object Analog Input | float | R | Volts
| 3 | Ub_rms | Phase B Line-to-Neutral Voltage | Object Analog Input | float | R | Volts
| 4 | Uc_rms | Phase C Line-to-Neutral Voltage | Object Analog Input | float | R | Volts
| 5 | Uavg_rms | Average Line-to-Neutral Voltage | Object Analog Input | float | R | Volts
| 6 | Uab_rms | Phase AB Line-to-Line Voltage | Object Analog Input | float | R | Volts
| 7 | Ubc_rms | Phase BC Line-to-Line Voltage | Object Analog Input | float | R | Volts
| 8 | Uca_rms | Phase CA Line-to-Line Voltage | Object Analog Input | float | R | Volts
| 9 | Ulavg_rms | Average Line-to-Line Voltage | Object Analog Input | float | R | Volts
| 10 | Ia_rms | Phase A Current | Object Analog Input | float | R | Amperes
| 11 | Ib_rms | Phase B Current | Object Analog Input | float | R | Amperes
| 12 | Ic_rms | Phase C Current | Object Analog Input | float | R | Amperes
| 13 | Iavg_rms | Average Current | Object Analog Input | float | R | Amperes
| 14 | In_rms | Phase N Current | Object Analog Input | float | R | Amperes
| 15 | Pa_rms | Phase A Active Power | Object Analog Input | float | R | Kilowatts
| 16 | Pb_rms | Phase B Active Power | Object Analog Input | float | R | Kilowatts
| 17 | Pc_rms | Phase C Active Power | Object Analog Input | float | R | Kilowatts
| 18 | P_rms | System Active Power | Object Analog Input | float | R | Kilowatts
| 19 | Qa_rms | Phase A Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
| 20 | Qb_rms | Phase B Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
| 21 | Qc_rms | Phase C Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
| 22 | Q_rms | System Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
| 23 | Sa_rms | Phase A Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
| 24 | Sb_rms | Phase B Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
| 25 | Sc_rms | Phase C Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
| 26 | S_rms | System Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
.

## Power Quality
Power Quality | ID | Name | Description | Object Type | Data type | RW | Unit
System Power Quality | 27 | PFa_rms | Phase A Power Factor | Object Analog Input | float | R | Power Factor
| 28 | PFb_rms | Phase B Power Factor | Object Analog Input | float | R | Power Factor
| 29 | PFc_rms | Phase C Power Factor | Object Analog Input | float | R | Power Factor
| 30 | PF_rms | System Power Factor | Object Analog Input | float | R | Power Factor
| 31 | U_unbl | Voltage Unbalance Negative | Object Analog Input | float | R | Percent
| 32 | I_unbl | Current Unbalance Negative | Object Analog Input | float | R | Percent
| 33 | Rlc_val | System Load Nature(82:Resistive load 76:Inductive load 67:Capacitive load) | Object Analog Input | float | R | No Units
| 34 | V1_thd | Phase A Voltage THD | Object Analog Input | float | R | Percent
| 35 | V2_thd | Phase B Voltage THD | Object Analog Input | float | R | Percent
| 36 | V3_thd | Phase C Voltage THD | Object Analog Input | float | R | Percent
| 37 | I1_thd | Phase A Current THD | Object Analog Input | float | R | Percent
| 38 | I2_thd | Phase B Current THD | Object Analog Input | float | R | Percent
| 39 | I3_thd | Phase C Current THD | Object Analog Input | float | R | Percent

## Demand
Demand | ID | Name | Description | Object Type | Data type | RW | Unit
System Demand | 40 | p_dema | System Active Power Demand | Object Analog Input | float | R | Kilowatts
| 41 | q_dema | System Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
| 42 | s_dema | System Apparent Power Demand | Object Analog Input | float | R | Kilovolt Amperes
| 43 | Ia_dema | Phase A Current Demand | Object Analog Input | float | R | Amperes
| 44 | Ib_dema | Phase B Current Demand | Object Analog Input | float | R | Amperes
| 45 | Ic_dema | Phase C Current Demand | Object Analog Input | float | R | Amperes

## Energy
Energy | ID | Name | Description | Object Type | Data type | RW | Unit
System Energy | 46 | Active_Energy_Imp | System active energy import | Object Analog Input | float | R | Kilowatt Hours
| 47 | Active_Energy_Exp | System active energy export | Object Analog Input | float | R | Kilowatt Hours
| 48 | Reactive_Energy_Imp | System reactive energy import | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 49 | Reactive_Energy_Exp | System reactive energy export | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 50 | Active_Energy_Total | System active energy total | Object Analog Input | float | R | Kilowatt Hours
| 51 | Active_Energy_Net | System active energy net | Object Analog Input | float | R | Kilowatt Hours
| 52 | Reactive_Energy_Total | System reactive energy total | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 53 | Reactive_Energy_Net | System reactive energy net | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 54 | Apparent_Energy | System apparent energy total | Object Analog Input | float | R | Kilovolt Ampere Hours
| 55 | Active_Energy_Imp_A | Phase A active energy import | Object Analog Input | float | R | Kilowatt Hours
| 56 | Active_Energy_Exp_A | Phase A active energy export | Object Analog Input | float | R | Kilowatt Hours
| 57 | Active_Energy_Imp_B | Phase B active energy import | Object Analog Input | float | R | Kilowatt Hours
| 58 | Active_Energy_Exp_B | Phase B active energy export | Object Analog Input | float | R | Kilowatt Hours
| 59 | Active_Energy_Imp_C | Phase C active energy import | Object Analog Input | float | R | Kilowatt Hours
| 60 | Active_Energy_Exp_C | Phase C active energy export | Object Analog Input | float | R | Kilowatt Hours
| 61 | Reactive_Energy_Imp_A | Phase A reactive energy import | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 62 | Reactive_Energy_Exp_A | Phase A reactive energy export | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 63 | Reactive_Energy_Imp_B | Phase B reactive energy import | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 64 | Reactive_Energy_Exp_B | Phase B reactive energy export | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 65 | Reactive_Energy_Imp_C | Phase C reactive energy import | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 66 | Reactive_Energy_Exp_C | Phase C reactive energy export | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 67 | Apparent_Energy_A | Phase A apparent energy total | Object Analog Input | float | R | Kilovolt Ampere Hours
| 68 | Apparent_Energy_B | Phase B apparent energy total | Object Analog Input | float | R | Kilovolt Ampere Hours
| 69 | Apparent_Energy_C | Phase C apparent energy total | Object Analog Input | float | R | Kilovolt Ampere Hours

## Independent Input Channel
Independent Channel | ID | Name | Description | Object Type | Data type | RW | Unit
| 70 | I4_rms | Channel 4 Current | Object Analog Input | float | R | Amperes
| 71 | P4_rms | Channel 4 Active Power | Object Analog Input | float | R | Kilowatts
| 72 | Q4_rms | Channel 4 Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
| 73 | S4_rms | Channel 4 Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
| 74 | PF4_rms | Channel 4 Power Factor | Object Analog Input | float | R | Power Factor
| 75 | I4_thd | Channel 4 Current THD | Object Analog Input | float | R | Percent
| 76 | I4_dema | Channel 4 Current Demand | Object Analog Input | float | R | Amperes
| 77 | Isum2_avg_rms | Summation 2 Average Current | Object Analog Input | float | R | Amperes
| 78 | Psum2_rms | Summation 2 Active Power | Object Analog Input | float | R | Kilowatts
| 79 | Qsum2_rms | Summation 2 Reactive Power | Object Analog Input | float | R | Kilovolt Amperes Reactive
| 80 | Ssum2_rms | Summation 2 Apparent Power | Object Analog Input | float | R | Kilovolt Amperes
| 81 | PFsum2_rms | Summation 2 Power Factor | Object Analog Input | float | R | Power Factor
| 82 | Rlc_sum2_val | Summation 2 Load Nature(82:Resistive load 76:Inductive load 67:Capacitive load) | Object Analog Input | float | R | No Units
| 83 | Psum2_dema | Summation 2 Active Power Demand | Object Analog Input | float | R | Kilowatts
| 84 | Qsum2_dema | Summation 2 Reactive Power Demand | Object Analog Input | float | R | Kilovolt Amperes Reactive
| 85 | Ssum2_dema | Summation 2 Apparent Power Demand | Object Analog Input | float | R | Kilovolt Amperes
| 86 | CH4_Active_Energy_Imp | Channel 4 active energy import | Object Analog Input | float | R | Kilowatt Hours
| 87 | CH4_Active_Energy_Exp | Channel 4 active energy export | Object Analog Input | float | R | Kilowatt Hours
| 88 | CH4_Reactive_Energy_Imp | Channel 4 reactive energy import | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 89 | CH4_Reactive_Energy_Exp | Channel 4 reactive energy export | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 90 | CH4_Apparent_Energy_Total | Channel 4 apparent energy total | Object Analog Input | float | R | Kilovolt Ampere Hours
| 91 | Sum2_Active_Energy_Imp | Summation 2 active energy import | Object Analog Input | float | R | Kilowatt Hours
| 92 | Sum2_Active_Energy_Exp | Summation 2 active energy export | Object Analog Input | float | R | Kilowatt Hours
| 93 | Sum2_Reactive_Energy_Imp | Summation 2 reactive energy import | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 94 | Sum2_Reactive_Energy_Exp | Summation 2 reactive energy export | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 95 | Sum2_Active_Energy_Total | Summation 2 active energy total | Object Analog Input | float | R | Kilowatt Hours
| 96 | Sum2_Active_Energy_Net | Summation 2 active energy net | Object Analog Input | float | R | Kilowatt Hours
| 97 | Sum2_Reactive_Energy_Total | Summation 2 reactive energy total | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 98 | Sum2_Reactive_Energy_Net | Summation 2 reactive energy net | Object Analog Input | float | R | Kilovolt Ampere Hours Reactive
| 99 | Sum2_Apparent_Energy_Total | Summation 2 apparent energy total | Object Analog Input | float | R | Kilovolt Ampere Hours

## IO Pulse Counter
IO | ID | Name | Description | Object Type | Data type | RW | Unit
DI Pulse | 1 | DI1_pc | DI1 pulse counter | Object Pulse Converter | uint32_t | R | No Units
| 2 | DI2_pc | DI2 pulse counter | Object Pulse Converter | uint32_t | R | No Units
| 3 | DI3_pc | DI3 pulse counter | Object Pulse Converter | uint32_t | R | No Units

## IO Status
IO | ID | Name | Description | Object Type | Data type | RW | Unit
DI Status | 1 | DI1_s | Digital Input 1 Status | Object Binary_Input | bool | R | No Units
| 2 | DI2_s | Digital Input 2 Status | Object Binary_Input | bool | R | No Units
| 3 | DI3_s | Digital Input 3 Status | Object Binary_Input | bool | R | No Units