## Overview
Version | Changes | Author | Reviewer | Date | External Firmware Version
v1.01 | Init from "AcuRev2100_WEB2地址表_20251118_MC.docx" | Sam Xu | Simon Chen | 2026-04-01 | v1.20
v1.02 | Removed export energy addresses | Sam Xu | Simon Chen | 2026-04-06 | v1.20

## System Information
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Meter Base Info | 0xF000 | 0xF001 | 61440 | 61441 | Model Type | Word | R | 2 | ASCII x 4
(0x03 Read) | 0xF002 | 0xF003 | 61442 | 61443 | Hardware Version | Word | R | 2 | ASCII x 4
| 0xF004 | 0xF005 | 61444 | 61445 | Software Version | Word | R | 2 | ASCII x 4
| 0xF006 | 0xF008 | 61446 | 61448 | Release Date | Word | R | 3 | ASCII x 6
Display Module Info | 0xF009 | 0xF00A | 61449 | 61450 | Model Type | Word | R/W | 2 | ASCII x 4
(0x03 Read, 0x6A Write) | 0xF00B | 0xF00C | 61451 | 61452 | Hardware Version | Word | R/W | 2 | ASCII x 4
| 0xF00D | 0xF00E | 61453 | 61454 | Software Version | Word | R/W | 2 | ASCII x 4
| 0xF00F | 0xF011 | 61455 | 61457 | Release Date | Word | R/W | 3 | ASCII x 6
Web Module Info | 0xF012 | 0xF013 | 61458 | 61459 | Model Type | Word | R/W | 2 | ASCII x 4
(0x03 Read, 0x6A Write) | 0xF014 | 0xF015 | 61460 | 61461 | Hardware Version | Word | R/W | 2 | ASCII x 4
| 0xF016 | 0xF017 | 61462 | 61463 | Software Version | Word | R/W | 2 | ASCII x 4
| 0xF018 | 0xF01A | 61464 | 61466 | Release Date | Word | R/W | 3 | ASCII x 6
Serial Number | 0xF040 | 0xF04F | 61504 | 61519 | Serial Number |  | R/W | 16 | ASCII x 20
(0x03 Read, 0x6A Write)
Actual value ≠ Modbus value
Meter and battery run time | Rx*0.001 |  |  |  | Yellow cell: not in use
Energy | Rx*0.1
Unbalance | Rx/1000*100%
THD | (Rx/10000)*100%
Harmonics | (Rx/10000)*100%
Crest factor | Rx/1000
K factor | Rx/10
THF | (Rx/10000)*100%
Pulse value | Rx/100

## Factory Settings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Factory Settings | 0xF100 | 0xF100 | 61696 | 61696 | DM/EM Module Type | Word | R/W | 1 | 0xAA: DM module 0x55: EM module | 0x55
(0x03 Read, 0x6A Write) | 0xF101 | 0xF101 | 61697 | 61697 | Default Frequency | Word | R/W | 1 | 50 or 60 | 50
| 0xF102 | 0xF102 | 61698 | 61698 | RS485 Protocol (not in use) | Word | R/W | 1 | 0x00: Modbus-RTU | 0
| 0xF103 | 0xF103 | 61699 | 61699 | Set current TOU settings as default | Word | R/W | 1 | Set 1 to save
| 0xF104 | 0xF104 | 61700 | 61700 | Clear Calibration | Word | R/W | 1 | Set 1 to clear Set 0x55 to clear RCT calibration coefficient (non-MC only)
| 0xF105 | 0xF105 | 61701 | 61701 | Display module language (English only now) Display module backlight strength | Word | R/W | 1 | High byte: 0 English, 1 Chinese Low byte: 0 to 100 | 100
| 0xF106 | 0xF106 | 61702 | 61702 | Meter Type | Word | R/W | 1 | 1: AcuRev2110 (Write 0x3FE9)
| 0xF107 | 0xF107 | 61703 | 61703 | Flag of notifying display module | Word | R/W | 1 | 1: Chang or Valid, 0: Invalid Bit0: Setting changed Bit1: Meter reboot Bit4: Low power status Other reserved
| 0xF108 | 0xF108 | 61704 | 61704 | CT Type (DM module only) | Word | R/W | 1 | 80: CCT-80 | 80
| 0xF109 | 0xF10B | 61705 | 61707 | User Channel 1 Combination (Note: No Uc for 2LN) | Word | R/W | 3 | 1st word: Ua input channel 2nd word: Ub input channel 3rd word: Uc input channel | 1; 2; 3
| 0xF10C | 0xF10E | 61708 | 61710 | User Channel 2 Combination (Note: No Uc for 2LN) | Word | R/W | 3 | 1st word: Ua input channel 2nd word: Ub input channel 3rd word: Uc input channel | 4;5;6
| 0xF10F | 0xF111 | 61711 | 61713 | User Channel 3 Combination (Note: No Uc for 2LN) | Word | R/W | 3 | 1st word: Ua input channel 2nd word: Ub input channel 3rd word: Uc input channel | 7;8;9
| 0xF112 | 0xF114 | 61714 | 61716 | User Channel 4 Combination (Note: No Uc for 2LN) | Word | R/W | 3 | 1st word: Ua input channel 2nd word: Ub input channel 3rd word: Uc input channel | 10;11;12
| 0xF115 | 0xF117 | 61717 | 61719 | User Channel 5 Combination (Note: No Uc for 2LN) | Word | R/W | 3 | 1st word: Ua input channel 2nd word: Ub input channel 3rd word: Uc input channel | 13;14;15
| 0xF118 | 0xF11A | 61720 | 61722 | User Channel 6 Combination (Note: No Uc for 2LN) | Word | R/W | 3 | 1st word: Ua input channel 2nd word: Ub input channel 3rd word: Uc input channel | 16;17;18
| 0xF11B | 0xF11B | 61723 | 61723 | CT Type (mA or mV) | Word | R/W | 1 | 0x22: mA 0x55: mV (for non-MC) | 0x22
| 0xF11C | 0xF11E | 61724 | 61726 | Reserved |  |  | 3
| 0xF11F | 0xF121 | 61727 | 61729 | Meter Number | Word | R/W | 3
| 0xF122 | 0xF123 | 61730 | 61731 | Reserved |  |  | 2
| 0xF124 | 0xF124 | 61732 | 61732 | Programming Enable/Disable | Word | R/W | 1 | 0: Disable; 1: Enable | 0
| 0xF125 | 0xF125 | 61733 | 61733 | Sealing Enable/Disable | Word | R/W | 1 | 0: Disable; 1: Enable | MC: 1, non-MC: 0
| 0xF126 | 0xF126 | 61734 | 61734 | Support Demand Vertified (DV) | Word | R/W | 1 | 0x55: Support; 0xAA: No support | 0x55
| 0xF127 | 0xF127 | 61735 | 61735 | Support Pulse Vertified (PV) | Word | R/W | 1 | 0x55: Support; 0xAA: No support | 0x55
| 0xF128 | 0xF12F | 61736 | 61743 | Reserved |  |  | 8
* | 0xF130 | 0xF130 | 61744 | 61744 | Seal Button Status | Word | W | 1 | 0: Seal disabled; 0x0A: Seal enabled | 0
*Note: 0xF130 is for testbench to control seal function. It is write-only. To read seal status, please read 0x8B0.

## Calibration
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Self-sampling Calibration Coefficient - 50 Hz
(0x03 Read, 0x6A Write)
Modulus Compensation Coefficient | 0xF162 | 0xF162 | 61794 | 61794 | Ua220_adj | Word | R/W | 1 | -32786~32767
| 0xF163 | 0xF163 | 61795 | 61795 | Ub220_adj | Word | R/W | 1 | -32786~32767
| 0xF164 | 0xF164 | 61796 | 61796 | Uc220_adj | Word | R/W | 1 | -32786~32767
| 0xF165 | 0xF165 | 61797 | 61797 | I1 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF166 | 0xF166 | 61798 | 61798 | I2 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF167 | 0xF167 | 61799 | 61799 | I3 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF168 | 0xF168 | 61800 | 61800 | I4 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF169 | 0xF169 | 61801 | 61801 | I5 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF16A | 0xF16A | 61802 | 61802 | I6 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF16B | 0xF16B | 61803 | 61803 | I7 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF16C | 0xF16C | 61804 | 61804 | I8 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF16D | 0xF16D | 61805 | 61805 | I9 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF16E | 0xF16E | 61806 | 61806 | I10 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF16F | 0xF16F | 61807 | 61807 | I11 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF170 | 0xF170 | 61808 | 61808 | I12 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF171 | 0xF171 | 61809 | 61809 | I13 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF172 | 0xF172 | 61810 | 61810 | I14 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF173 | 0xF173 | 61811 | 61811 | I15 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF174 | 0xF174 | 61812 | 61812 | I16 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF175 | 0xF175 | 61813 | 61813 | I17 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF176 | 0xF176 | 61814 | 61814 | I18 5000_adj | Word | R/W | 1 | -32786~32767
Angle Compensation Coefficient | 0xF177 | 0xF177 | 61815 | 61815 | Ub220_ri | Word | R/W | 1 | -32786~32767
| 0xF178 | 0xF178 | 61816 | 61816 | Uc220_ri | Word | R/W | 1 | -32786~32767
| 0xF179 | 0xF179 | 61817 | 61817 | I1 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF17A | 0xF17A | 61818 | 61818 | I2 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF17B | 0xF17B | 61819 | 61819 | I3 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF17C | 0xF17C | 61820 | 61820 | I4 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF17D | 0xF17D | 61821 | 61821 | I5 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF17E | 0xF17E | 61822 | 61822 | I6 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF17F | 0xF17F | 61823 | 61823 | I7 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF180 | 0xF180 | 61824 | 61824 | I8 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF181 | 0xF181 | 61825 | 61825 | I9 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF182 | 0xF182 | 61826 | 61826 | I10 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF183 | 0xF183 | 61827 | 61827 | I11 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF184 | 0xF184 | 61828 | 61828 | I12 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF185 | 0xF185 | 61829 | 61829 | I13 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF186 | 0xF186 | 61830 | 61830 | I14 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF187 | 0xF187 | 61831 | 61831 | I15 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF188 | 0xF188 | 61832 | 61832 | I16 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF189 | 0xF189 | 61833 | 61833 | I17 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF18A | 0xF18A | 61834 | 61834 | I18 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF18B | 0xF190 | 61835 | 61840 | Reserved |  |  | 6
AD Sampling Re/Im Value of V/I | 0xF230 | 0xF230 | 62000 | 62000 | Ua Re | word | R | 1 | -32786~32767
(0x03 Read) | 0xF231 | 0xF231 | 62001 | 62001 | Ua Im | word | R | 1 | -32786~32767
| 0xF232 | 0xF232 | 62002 | 62002 | Ub Re | word | R | 1 | -32786~32767
| 0xF233 | 0xF233 | 62003 | 62003 | Ub Im | word | R | 1 | -32786~32767
| 0xF234 | 0xF234 | 62004 | 62004 | Uc Re | word | R | 1 | -32786~32767
| 0xF235 | 0xF235 | 62005 | 62005 | Uc Im | word | R | 1 | -32786~32767
| 0xF236 | 0xF236 | 62006 | 62006 | I1 Re | word | R | 1 | -32786~32767
| 0xF237 | 0xF237 | 62007 | 62007 | I1 Im | word | R | 1 | -32786~32767
| 0xF238 | 0xF238 | 62008 | 62008 | I2 Re | word | R | 1 | -32786~32767
| 0xF239 | 0xF239 | 62009 | 62009 | I2 Im | word | R | 1 | -32786~32767
| 0xF23A | 0xF23A | 62010 | 62010 | I3 Re | word | R | 1 | -32786~32767
| 0xF23B | 0xF23B | 62011 | 62011 | I3 Im | word | R | 1 | -32786~32767
| 0xF23C | 0xF23C | 62012 | 62012 | I4 Re | word | R | 1 | -32786~32767
| 0xF23D | 0xF23D | 62013 | 62013 | I4 Im | word | R | 1 | -32786~32767
| 0xF23E | 0xF23E | 62014 | 62014 | I5 Re | word | R | 1 | -32786~32767
| 0xF23F | 0xF23F | 62015 | 62015 | I5 Im | word | R | 1 | -32786~32767
| 0xF240 | 0xF240 | 62016 | 62016 | I6 Re | word | R | 1 | -32786~32767
| 0xF241 | 0xF241 | 62017 | 62017 | I6 Im | word | R | 1 | -32786~32767
| 0xF242 | 0xF242 | 62018 | 62018 | I7 Re | word | R | 1 | -32786~32767
| 0xF243 | 0xF243 | 62019 | 62019 | I7 Im | word | R | 1 | -32786~32767
| 0xF244 | 0xF244 | 62020 | 62020 | I8 Re | word | R | 1 | -32786~32767
| 0xF245 | 0xF245 | 62021 | 62021 | I8 Im | word | R | 1 | -32786~32767
| 0xF246 | 0xF246 | 62022 | 62022 | I9 Re | word | R | 1 | -32786~32767
| 0xF247 | 0xF247 | 62023 | 62023 | I9 Im | word | R | 1 | -32786~32767
| 0xF248 | 0xF248 | 62024 | 62024 | I10 Re | word | R | 1 | -32786~32767
| 0xF249 | 0xF249 | 62025 | 62025 | I10 Im | word | R | 1 | -32786~32767
| 0xF24A | 0xF24A | 62026 | 62026 | I11 Re | word | R | 1 | -32786~32767
| 0xF24B | 0xF24B | 62027 | 62027 | I11 Im | word | R | 1 | -32786~32767
| 0xF24C | 0xF24C | 62028 | 62028 | I12 Re | word | R | 1 | -32786~32767
| 0xF24D | 0xF24D | 62029 | 62029 | I12 Im | word | R | 1 | -32786~32767
| 0xF24E | 0xF24E | 62030 | 62030 | I13 Re | word | R | 1 | -32786~32767
| 0xF24F | 0xF24F | 62031 | 62031 | I13 Im | word | R | 1 | -32786~32767
| 0xF250 | 0xF250 | 62032 | 62032 | I14 Re | word | R | 1 | -32786~32767
| 0xF251 | 0xF251 | 62033 | 62033 | I14 Im | word | R | 1 | -32786~32767
| 0xF252 | 0xF252 | 62034 | 62034 | I15 Re | word | R | 1 | -32786~32767
| 0xF253 | 0xF253 | 62035 | 62035 | I15 Im | word | R | 1 | -32786~32767
| 0xF254 | 0xF254 | 62036 | 62036 | I16 Re | word | R | 1 | -32786~32767
| 0xF255 | 0xF255 | 62037 | 62037 | I16 Im | word | R | 1 | -32786~32767
| 0xF256 | 0xF256 | 62038 | 62038 | I17 Re | word | R | 1 | -32786~32767
| 0xF257 | 0xF257 | 62039 | 62039 | I17 Im | word | R | 1 | -32786~32767
| 0xF258 | 0xF258 | 62040 | 62040 | I18 Re | word | R | 1 | -32786~32767
| 0xF259 | 0xF259 | 62041 | 62041 | I18 Im | word | R | 1 | -32786~32767
| 0xF25A | 0xF25A | 62042 | 62042 | Ua-b Re | word | R | 1 | -32786~32767
| 0xF25B | 0xF25B | 62043 | 62043 | Ua-b Im | word | R | 1 | -32786~32767
| 0xF25C | 0xF25C | 62044 | 62044 | Ua-c Re | word | R | 1 | -32786~32767
| 0xF25D | 0xF25D | 62045 | 62045 | Ua-c Im | word | R | 1 | -32786~32767
| 0xF25E | 0xF25F | 62046 | 62047 | Reserved |  |  | 2
Calibration Metering Data | 0xF260 | 0xF261 | 62048 | 62049 | ua | float | R | 2
| 0xF262 | 0xF263 | 62050 | 62051 | ub | float | R | 2
| 0xF264 | 0xF265 | 62052 | 62053 | uc | float | R | 2
| 0xF266 | 0xF267 | 62054 | 62055 | i1 | float | R | 2
| 0xF268 | 0xF269 | 62056 | 62057 | i2 | float | R | 2
| 0xF26A | 0xF26B | 62058 | 62059 | i3 | float | R | 2
| 0xF26C | 0xF26D | 62060 | 62061 | i4 | float | R | 2
| 0xF26E | 0xF26F | 62062 | 62063 | i5 | float | R | 2
| 0xF270 | 0xF271 | 62064 | 62065 | i6 | float | R | 2
| 0xF272 | 0xF273 | 62066 | 62067 | i7 | float | R | 2
| 0xF274 | 0xF275 | 62068 | 62069 | i8 | float | R | 2
| 0xF276 | 0xF277 | 62070 | 62071 | i9 | float | R | 2
| 0xF278 | 0xF279 | 62072 | 62073 | i10 | float | R | 2
| 0xF27A | 0xF27B | 62074 | 62075 | i11 | float | R | 2
| 0xF27C | 0xF27D | 62076 | 62077 | i12 | float | R | 2
| 0xF27E | 0xF27F | 62078 | 62079 | i13 | float | R | 2
| 0xF280 | 0xF281 | 62080 | 62081 | i14 | float | R | 2
| 0xF282 | 0xF283 | 62082 | 62083 | i15 | float | R | 2
| 0xF284 | 0xF285 | 62084 | 62085 | i16 | float | R | 2
| 0xF286 | 0xF287 | 62086 | 62087 | i17 | float | R | 2
| 0xF288 | 0xF289 | 62088 | 62089 | i18 | float | R | 2
| 0xF28A | 0xF28F | 62090 | 62095 | Reserved |  |  | 6
ADE7816 V/I Calibration Offset Coefficient (50Hz) | 0xF300 | 0xF301 | 62208 | 62209 | Va Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF302 | 0xF303 | 62210 | 62211 | Vb Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF304 | 0xF305 | 62212 | 62213 | Vc Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF306 | 0xF307 | 62214 | 62215 | I1 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF308 | 0xF309 | 62216 | 62217 | I2 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF30A | 0xF30B | 62218 | 62219 | I3 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF30C | 0xF30D | 62220 | 62221 | I4 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF30E | 0xF30F | 62222 | 62223 | I5 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF310 | 0xF311 | 62224 | 62225 | I6 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF312 | 0xF313 | 62226 | 62227 | I7 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF314 | 0xF315 | 62228 | 62229 | I8 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF316 | 0xF317 | 62230 | 62231 | I9 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF318 | 0xF319 | 62232 | 62233 | I10 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF31A | 0xF31B | 62234 | 62235 | I11 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF31C | 0xF31D | 62236 | 62237 | I12 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF31E | 0xF31F | 62238 | 62239 | I13 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF320 | 0xF321 | 62240 | 62241 | I14 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF322 | 0xF323 | 62242 | 62243 | I15 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF324 | 0xF325 | 62244 | 62245 | I16 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF326 | 0xF327 | 62246 | 62247 | I17 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF328 | 0xF329 | 62248 | 62249 | I18 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF32A | 0xF32F | 62250 | 62255 | Reserved |  |  | 6
ADE7816 V/I Gain Calibration Coefficient (50Hz) | 0xF330 | 0xF331 | 62256 | 62257 | Va Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF332 | 0xF333 | 62258 | 62259 | Vb Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF334 | 0xF335 | 62260 | 62261 | Vc Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF336 | 0xF337 | 62262 | 62263 | I1 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF338 | 0xF339 | 62264 | 62265 | I2 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF33A | 0xF33B | 62266 | 62267 | I3 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF33C | 0xF33D | 62268 | 62269 | I4 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF33E | 0xF33F | 62270 | 62271 | I5 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF340 | 0xF341 | 62272 | 62273 | I6 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF342 | 0xF343 | 62274 | 62275 | I7 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF344 | 0xF345 | 62276 | 62277 | I8 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF346 | 0xF347 | 62278 | 62279 | I9 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF348 | 0xF349 | 62280 | 62281 | I10 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF34A | 0xF34B | 62282 | 62283 | I11 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF34C | 0xF34D | 62284 | 62285 | I12 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF34E | 0xF34F | 62286 | 62287 | I13 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF350 | 0xF351 | 62288 | 62289 | I14 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF352 | 0xF353 | 62290 | 62291 | I15 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF354 | 0xF355 | 62292 | 62293 | I16 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF356 | 0xF357 | 62294 | 62295 | I17 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF358 | 0xF359 | 62296 | 62297 | I18 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF35A | 0xF35F | 62298 | 62303 | Reserved |  |  | 6
ADE7816 Phase Calibration Coefficient (50Hz) | 0xF360 | 0xF361 | 62304 | 62305 | I1 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF362 | 0xF363 | 62306 | 62307 | I2 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF364 | 0xF365 | 62308 | 62309 | I3 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF366 | 0xF367 | 62310 | 62311 | I4 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF368 | 0xF369 | 62312 | 62313 | I5 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF36A | 0xF36B | 62314 | 62315 | I6 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF36C | 0xF36D | 62316 | 62317 | I7 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF36E | 0xF36F | 62318 | 62319 | I8 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF370 | 0xF371 | 62320 | 62321 | I9 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF372 | 0xF373 | 62322 | 62323 | I10 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF374 | 0xF375 | 62324 | 62325 | I11 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF376 | 0xF377 | 62326 | 62327 | I12 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF378 | 0xF379 | 62328 | 62329 | I13 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF37A | 0xF37B | 62330 | 62331 | I14 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF37C | 0xF37D | 62332 | 62333 | I15 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF37E | 0xF37F | 62334 | 62335 | I16 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF380 | 0xF381 | 62336 | 62337 | I17 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF382 | 0xF383 | 62338 | 62339 | I18 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF384 | 0xF38F | 62340 | 62351 | Reserved |  |  | 12
ADE7816 Ep Offset Calibration Coefficient (50Hz) | 0xF390 | 0xF391 | 62352 | 62353 | I1 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF392 | 0xF393 | 62354 | 62355 | I2 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF394 | 0xF395 | 62356 | 62357 | I3 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF396 | 0xF397 | 62358 | 62359 | I4 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF398 | 0xF399 | 62360 | 62361 | I5 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF39A | 0xF39B | 62362 | 62363 | I6 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF39C | 0xF39D | 62364 | 62365 | I7 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF39E | 0xF39F | 62366 | 62367 | I8 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3A0 | 0xF3A1 | 62368 | 62369 | I9 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3A2 | 0xF3A3 | 62370 | 62371 | I10 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3A4 | 0xF3A5 | 62372 | 62373 | I11 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3A6 | 0xF3A7 | 62374 | 62375 | I12 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3A8 | 0xF3A9 | 62376 | 62377 | I13 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3AA | 0xF3AB | 62378 | 62379 | I14 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3AC | 0xF3AD | 62380 | 62381 | I15 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3AE | 0xF3AF | 62382 | 62383 | I16 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3B0 | 0xF3B1 | 62384 | 62385 | I17 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3B2 | 0xF3B3 | 62386 | 62387 | I18 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3B4 | 0xF3BF | 62388 | 62399 | Reserved |  |  | 12
ADE7816 Ep Gain Calibration Coefficient (50Hz) | 0xF3C0 | 0xF3C1 | 62400 | 62401 | I1 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3C2 | 0xF3C3 | 62402 | 62403 | I2 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3C4 | 0xF3C5 | 62404 | 62405 | I3 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3C6 | 0xF3C7 | 62406 | 62407 | I4 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3C8 | 0xF3C9 | 62408 | 62409 | I5 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3CA | 0xF3CB | 62410 | 62411 | I6 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3CC | 0xF3CD | 62412 | 62413 | I7 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3CE | 0xF3CF | 62414 | 62415 | I8 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3D0 | 0xF3D1 | 62416 | 62417 | I9 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3D2 | 0xF3D3 | 62418 | 62419 | I10 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3D4 | 0xF3D5 | 62420 | 62421 | I11 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3D6 | 0xF3D7 | 62422 | 62423 | I12 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3D8 | 0xF3D9 | 62424 | 62425 | I13 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3DA | 0xF3DB | 62426 | 62427 | I14 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3DC | 0xF3DD | 62428 | 62429 | I15 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3DE | 0xF3DF | 62430 | 62431 | I16 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3E0 | 0xF3E1 | 62432 | 62433 | I17 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3E2 | 0xF3E3 | 62434 | 62435 | I18 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3E4 | 0xF3EF | 62436 | 62447 | Reserved |  |  | 12
ADE7816 Eq Offset Calibration Coefficient (50Hz) | 0xF3F0 | 0xF3F1 | 62448 | 62449 | I1 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3F2 | 0xF3F3 | 62450 | 62451 | I2 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3F4 | 0xF3F5 | 62452 | 62453 | I3 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3F6 | 0xF3F7 | 62454 | 62455 | I4 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3F8 | 0xF3F9 | 62456 | 62457 | I5 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3FA | 0xF3FB | 62458 | 62459 | I6 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3FC | 0xF3FD | 62460 | 62461 | I7 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF3FE | 0xF3FF | 62462 | 62463 | I8 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF400 | 0xF401 | 62464 | 62465 | I9 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF402 | 0xF403 | 62466 | 62467 | I10 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF404 | 0xF405 | 62468 | 62469 | I11 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF406 | 0xF407 | 62470 | 62471 | I12 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF408 | 0xF409 | 62472 | 62473 | I13 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF40A | 0xF40B | 62474 | 62475 | I14 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF40C | 0xF40D | 62476 | 62477 | I15 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF40E | 0xF40F | 62478 | 62479 | I16 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF410 | 0xF411 | 62480 | 62481 | I17 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF412 | 0xF413 | 62482 | 62483 | I18 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF414 | 0xF41F | 62484 | 62495 | Reserved |  |  | 12
ADE7816 Eq Gain Calibration Coefficient (50Hz) | 0xF420 | 0xF421 | 62496 | 62497 | I1 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF422 | 0xF423 | 62498 | 62499 | I2 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF424 | 0xF425 | 62500 | 62501 | I3 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF426 | 0xF427 | 62502 | 62503 | I4 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF428 | 0xF429 | 62504 | 62505 | I5 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF42A | 0xF42B | 62506 | 62507 | I6 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF42C | 0xF42D | 62508 | 62509 | I7 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF42E | 0xF42F | 62510 | 62511 | I8 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF430 | 0xF431 | 62512 | 62513 | I9 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF432 | 0xF433 | 62514 | 62515 | I10 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF434 | 0xF435 | 62516 | 62517 | I11 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF436 | 0xF437 | 62518 | 62519 | I12 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF438 | 0xF439 | 62520 | 62521 | I13 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF43A | 0xF43B | 62522 | 62523 | I14 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF43C | 0xF43D | 62524 | 62525 | I15 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF43E | 0xF43F | 62526 | 62527 | I16 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF440 | 0xF441 | 62528 | 62529 | I17 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF442 | 0xF443 | 62530 | 62531 | I18 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF444 | 0xF44F | 62532 | 62543 | Reserved |  |  | 12
ADE7816 Phase Angle Reading | 0xF500 | 0xF501 | 62720 | 62721 | I1 phase angle reading | float | R | 2
| 0xF502 | 0xF503 | 62722 | 62723 | I2 phase angle reading | float | R | 2
| 0xF504 | 0xF505 | 62724 | 62725 | I3 phase angle reading | float | R | 2
| 0xF506 | 0xF507 | 62726 | 62727 | I4 phase angle reading | float | R | 2
| 0xF508 | 0xF509 | 62728 | 62729 | I5 phase angle reading | float | R | 2
| 0xF50A | 0xF50B | 62730 | 62731 | I6 phase angle reading | float | R | 2
| 0xF50C | 0xF50D | 62732 | 62733 | I7 phase angle reading | float | R | 2
| 0xF50E | 0xF50F | 62734 | 62735 | I8 phase angle reading | float | R | 2
| 0xF510 | 0xF511 | 62736 | 62737 | I9 phase angle reading | float | R | 2
| 0xF512 | 0xF513 | 62738 | 62739 | I10 phase angle reading | float | R | 2
| 0xF514 | 0xF515 | 62740 | 62741 | I11 phase angle reading | float | R | 2
| 0xF516 | 0xF517 | 62742 | 62743 | I12 phase angle reading | float | R | 2
| 0xF518 | 0xF519 | 62744 | 62745 | I13 phase angle reading | float | R | 2
| 0xF51A | 0xF51B | 62746 | 62747 | I14 phase angle reading | float | R | 2
| 0xF51C | 0xF51D | 62748 | 62749 | I15 phase angle reading | float | R | 2
| 0xF51E | 0xF51F | 62750 | 62751 | I16 phase angle reading | float | R | 2
| 0xF520 | 0xF521 | 62752 | 62753 | I17 phase angle reading | float | R | 2
| 0xF522 | 0xF523 | 62754 | 62755 | I18 phase angle reading | float | R | 2
| 0xF524 | 0xF52F | 62756 | 62767 | Reserved |  |  | 12
ADE7816 Voltage, Current and Power Reading | 0xF550 | 0xF551 | 62800 | 62801 | Va | float | R | 2
| 0xF552 | 0xF553 | 62802 | 62803 | Vb | float | R | 2
| 0xF554 | 0xF555 | 62804 | 62805 | Vc | float | R | 2
| 0xF556 | 0xF557 | 62806 | 62807 | I1 | float | R | 2
| 0xF558 | 0xF559 | 62808 | 62809 | I2 | float | R | 2
| 0xF55A | 0xF55B | 62810 | 62811 | I3 | float | R | 2
| 0xF55C | 0xF55D | 62812 | 62813 | I4 | float | R | 2
| 0xF55E | 0xF55F | 62814 | 62815 | I5 | float | R | 2
| 0xF560 | 0xF561 | 62816 | 62817 | I6 | float | R | 2
| 0xF562 | 0xF563 | 62818 | 62819 | I7 | float | R | 2
| 0xF564 | 0xF565 | 62820 | 62821 | I8 | float | R | 2
| 0xF566 | 0xF567 | 62822 | 62823 | I9 | float | R | 2
| 0xF568 | 0xF569 | 62824 | 62825 | I10 | float | R | 2
| 0xF56A | 0xF56B | 62826 | 62827 | I11 | float | R | 2
| 0xF56C | 0xF56D | 62828 | 62829 | I12 | float | R | 2
| 0xF56E | 0xF56F | 62830 | 62831 | I13 | float | R | 2
| 0xF570 | 0xF571 | 62832 | 62833 | I14 | float | R | 2
| 0xF572 | 0xF573 | 62834 | 62835 | I15 | float | R | 2
| 0xF574 | 0xF575 | 62836 | 62837 | I16 | float | R | 2
| 0xF576 | 0xF577 | 62838 | 62839 | I17 | float | R | 2
| 0xF578 | 0xF579 | 62840 | 62841 | I18 | float | R | 2
| 0xF57A | 0xF57B | 62842 | 62843 | P1 | float | R | 2
| 0xF57C | 0xF57D | 62844 | 62845 | P2 | float | R | 2
| 0xF57E | 0xF57F | 62846 | 62847 | P3 | float | R | 2
| 0xF580 | 0xF581 | 62848 | 62849 | P4 | float | R | 2
| 0xF582 | 0xF583 | 62850 | 62851 | P5 | float | R | 2
| 0xF584 | 0xF585 | 62852 | 62853 | P6 | float | R | 2
| 0xF586 | 0xF587 | 62854 | 62855 | P7 | float | R | 2
| 0xF588 | 0xF589 | 62856 | 62857 | P8 | float | R | 2
| 0xF58A | 0xF58B | 62858 | 62859 | P9 | float | R | 2
| 0xF58C | 0xF58D | 62860 | 62861 | P10 | float | R | 2
| 0xF58E | 0xF58F | 62862 | 62863 | P11 | float | R | 2
| 0xF590 | 0xF591 | 62864 | 62865 | P12 | float | R | 2
| 0xF592 | 0xF593 | 62866 | 62867 | P13 | float | R | 2
| 0xF594 | 0xF595 | 62868 | 62869 | P14 | float | R | 2
| 0xF596 | 0xF597 | 62870 | 62871 | P15 | float | R | 2
| 0xF598 | 0xF599 | 62872 | 62873 | P16 | float | R | 2
| 0xF59A | 0xF59B | 62874 | 62875 | P17 | float | R | 2
| 0xF59C | 0xF59D | 62876 | 62877 | P18 | float | R | 2
| 0xF59E | 0xF5FF | 62878 | 62975 | Reserved |  |  | 98
Self-sampling Calibration Coefficient - 60 Hz
(0x03 Read, 0x6A Write)
Modulus Compensation Coefficient | 0xF762 | 0xF762 | 63330 | 63330 | Ua220_adj | Word | R/W | 1 | -32786~32767
| 0xF763 | 0xF763 | 63331 | 63331 | Ub220_adj | Word | R/W | 1 | -32786~32767
| 0xF764 | 0xF764 | 63332 | 63332 | Uc220_adj | Word | R/W | 1 | -32786~32767
| 0xF765 | 0xF765 | 63333 | 63333 | I1 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF766 | 0xF766 | 63334 | 63334 | I2 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF767 | 0xF767 | 63335 | 63335 | I3 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF768 | 0xF768 | 63336 | 63336 | I4 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF769 | 0xF769 | 63337 | 63337 | I5 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF76A | 0xF76A | 63338 | 63338 | I6 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF76B | 0xF76B | 63339 | 63339 | I7 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF76C | 0xF76C | 63340 | 63340 | I8 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF76D | 0xF76D | 63341 | 63341 | I9 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF76E | 0xF76E | 63342 | 63342 | I10 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF76F | 0xF76F | 63343 | 63343 | I11 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF770 | 0xF770 | 63344 | 63344 | I12 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF771 | 0xF771 | 63345 | 63345 | I13 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF772 | 0xF772 | 63346 | 63346 | I14 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF773 | 0xF773 | 63347 | 63347 | I15 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF774 | 0xF774 | 63348 | 63348 | I16 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF775 | 0xF775 | 63349 | 63349 | I17 5000_adj | Word | R/W | 1 | -32786~32767
| 0xF776 | 0xF776 | 63350 | 63350 | I18 5000_adj | Word | R/W | 1 | -32786~32767
Angle Compensation Coefficient | 0xF777 | 0xF777 | 63351 | 63351 | Ub220_ri | Word | R/W | 1 | -32786~32767
| 0xF778 | 0xF778 | 63352 | 63352 | Uc220_ri | Word | R/W | 1 | -32786~32767
| 0xF779 | 0xF779 | 63353 | 63353 | I1 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF77A | 0xF77A | 63354 | 63354 | I2 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF77B | 0xF77B | 63355 | 63355 | I3 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF77C | 0xF77C | 63356 | 63356 | I4 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF77D | 0xF77D | 63357 | 63357 | I5 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF77E | 0xF77E | 63358 | 63358 | I6 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF77F | 0xF77F | 63359 | 63359 | I7 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF780 | 0xF780 | 63360 | 63360 | I8 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF781 | 0xF781 | 63361 | 63361 | I9 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF782 | 0xF782 | 63362 | 63362 | I10 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF783 | 0xF783 | 63363 | 63363 | I11 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF784 | 0xF784 | 63364 | 63364 | I12 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF785 | 0xF785 | 63365 | 63365 | I13 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF786 | 0xF786 | 63366 | 63366 | I14 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF787 | 0xF787 | 63367 | 63367 | I15 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF788 | 0xF788 | 63368 | 63368 | I16 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF789 | 0xF789 | 63369 | 63369 | I17 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF78A | 0xF78A | 63370 | 63370 | I18 5000_ri | Word | R/W | 1 | -32786~32767
| 0xF78B | 0xF790 | 63371 | 63376 | Reserved |  |  | 6
ADE7816 V/I Calibration Offset Coefficient (60Hz) | 0xF900 | 0xF901 | 63744 | 63745 | Va Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF902 | 0xF903 | 63746 | 63747 | Vb Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF904 | 0xF905 | 63748 | 63749 | Vc Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF906 | 0xF907 | 63750 | 63751 | I1 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF908 | 0xF909 | 63752 | 63753 | I2 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF90A | 0xF90B | 63754 | 63755 | I3 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF90C | 0xF90D | 63756 | 63757 | I4 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF90E | 0xF90F | 63758 | 63759 | I5 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF910 | 0xF911 | 63760 | 63761 | I6 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF912 | 0xF913 | 63762 | 63763 | I7 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF914 | 0xF915 | 63764 | 63765 | I8 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF916 | 0xF917 | 63766 | 63767 | I9 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF918 | 0xF919 | 63768 | 63769 | I10 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF91A | 0xF91B | 63770 | 63771 | I11 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF91C | 0xF91D | 63772 | 63773 | I12 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF91E | 0xF91F | 63774 | 63775 | I13 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF920 | 0xF921 | 63776 | 63777 | I14 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF922 | 0xF923 | 63778 | 63779 | I15 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF924 | 0xF925 | 63780 | 63781 | I16 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF926 | 0xF927 | 63782 | 63783 | I17 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF928 | 0xF929 | 63784 | 63785 | I18 Calibration offset coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF92A | 0xF92F | 63786 | 63791 | Reserved |  |  | 6
ADE7816 V/I Gain Calibration Coefficient (60Hz) | 0xF930 | 0xF931 | 63792 | 63793 | Va Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF932 | 0xF933 | 63794 | 63795 | Vb Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF934 | 0xF935 | 63796 | 63797 | Vc Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF936 | 0xF937 | 63798 | 63799 | I1 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF938 | 0xF939 | 63800 | 63801 | I2 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF93A | 0xF93B | 63802 | 63803 | I3 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF93C | 0xF93D | 63804 | 63805 | I4 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF93E | 0xF93F | 63806 | 63807 | I5 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF940 | 0xF941 | 63808 | 63809 | I6 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF942 | 0xF943 | 63810 | 63811 | I7 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF944 | 0xF945 | 63812 | 63813 | I8 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF946 | 0xF947 | 63814 | 63815 | I9 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF948 | 0xF949 | 63816 | 63817 | I10 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF94A | 0xF94B | 63818 | 63819 | I11 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF94C | 0xF94D | 63820 | 63821 | I12 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF94E | 0xF94F | 63822 | 63823 | I13 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF950 | 0xF951 | 63824 | 63825 | I14 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF952 | 0xF953 | 63826 | 63827 | I15 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF954 | 0xF955 | 63828 | 63829 | I16 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF956 | 0xF957 | 63830 | 63831 | I17 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF958 | 0xF959 | 63832 | 63833 | I18 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF95A | 0xF95F | 63834 | 63839 | Reserved |  |  | 6
ADE7816 Phase Calibration Coefficient (60Hz) | 0xF960 | 0xF961 | 63840 | 63841 | I1 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF962 | 0xF963 | 63842 | 63843 | I2 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF964 | 0xF965 | 63844 | 63845 | I3 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF966 | 0xF967 | 63846 | 63847 | I4 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF968 | 0xF969 | 63848 | 63849 | I5 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF96A | 0xF96B | 63850 | 63851 | I6 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF96C | 0xF96D | 63852 | 63853 | I7 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF96E | 0xF96F | 63854 | 63855 | I8 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF970 | 0xF971 | 63856 | 63857 | I9 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF972 | 0xF973 | 63858 | 63859 | I10 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF974 | 0xF975 | 63860 | 63861 | I11 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF976 | 0xF977 | 63862 | 63863 | I12 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF978 | 0xF979 | 63864 | 63865 | I13 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF97A | 0xF97B | 63866 | 63867 | I14 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF97C | 0xF97D | 63868 | 63869 | I15 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF97E | 0xF97F | 63870 | 63871 | I16 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF980 | 0xF981 | 63872 | 63873 | I17 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF982 | 0xF983 | 63874 | 63875 | I18 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xF984 | 0xF98F | 63876 | 63887 | Reserved |  |  | 12
ADE7816 Ep Offset Calibration Coefficient (60Hz) | 0xF990 | 0xF991 | 63888 | 63889 | I1 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF992 | 0xF993 | 63890 | 63891 | I2 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF994 | 0xF995 | 63892 | 63893 | I3 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF996 | 0xF997 | 63894 | 63895 | I4 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF998 | 0xF999 | 63896 | 63897 | I5 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF99A | 0xF99B | 63898 | 63899 | I6 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF99C | 0xF99D | 63900 | 63901 | I7 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF99E | 0xF99F | 63902 | 63903 | I8 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9A0 | 0xF9A1 | 63904 | 63905 | I9 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9A2 | 0xF9A3 | 63906 | 63907 | I10 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9A4 | 0xF9A5 | 63908 | 63909 | I11 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9A6 | 0xF9A7 | 63910 | 63911 | I12 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9A8 | 0xF9A9 | 63912 | 63913 | I13 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9AA | 0xF9AB | 63914 | 63915 | I14 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9AC | 0xF9AD | 63916 | 63917 | I15 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9AE | 0xF9AF | 63918 | 63919 | I16 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9B0 | 0xF9B1 | 63920 | 63921 | I17 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9B2 | 0xF9B3 | 63922 | 63923 | I18 Ep offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9B4 | 0xF9BF | 63924 | 63935 | Reserved |  |  | 12
ADE7816 Ep Gain Calibration Coefficient (60Hz) | 0xF9C0 | 0xF9C1 | 63936 | 63937 | I1 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9C2 | 0xF9C3 | 63938 | 63939 | I2 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9C4 | 0xF9C5 | 63940 | 63941 | I3 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9C6 | 0xF9C7 | 63942 | 63943 | I4 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9C8 | 0xF9C9 | 63944 | 63945 | I5 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9CA | 0xF9CB | 63946 | 63947 | I6 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9CC | 0xF9CD | 63948 | 63949 | I7 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9CE | 0xF9CF | 63950 | 63951 | I8 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9D0 | 0xF9D1 | 63952 | 63953 | I9 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9D2 | 0xF9D3 | 63954 | 63955 | I10 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9D4 | 0xF9D5 | 63956 | 63957 | I11 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9D6 | 0xF9D7 | 63958 | 63959 | I12 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9D8 | 0xF9D9 | 63960 | 63961 | I13 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9DA | 0xF9DB | 63962 | 63963 | I14 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9DC | 0xF9DD | 63964 | 63965 | I15 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9DE | 0xF9DF | 63966 | 63967 | I16 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9E0 | 0xF9E1 | 63968 | 63969 | I17 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9E2 | 0xF9E3 | 63970 | 63971 | I18 Ep gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9E4 | 0xF9EF | 63972 | 63983 | Reserved |  |  | 12
ADE7816 Eq Offset Calibration Coefficient (60Hz) | 0xF9F0 | 0xF9F1 | 63984 | 63985 | I1 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9F2 | 0xF9F3 | 63986 | 63987 | I2 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9F4 | 0xF9F5 | 63988 | 63989 | I3 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9F6 | 0xF9F7 | 63990 | 63991 | I4 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9F8 | 0xF9F9 | 63992 | 63993 | I5 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9FA | 0xF9FB | 63994 | 63995 | I6 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9FC | 0xF9FD | 63996 | 63997 | I7 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xF9FE | 0xF9FF | 63998 | 63999 | I8 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA00 | 0xFA01 | 64000 | 64001 | I9 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA02 | 0xFA03 | 64002 | 64003 | I10 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA04 | 0xFA05 | 64004 | 64005 | I11 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA06 | 0xFA07 | 64006 | 64007 | I12 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA08 | 0xFA09 | 64008 | 64009 | I13 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA0A | 0xFA0B | 64010 | 64011 | I14 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA0C | 0xFA0D | 64012 | 64013 | I15 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA0E | 0xFA0F | 64014 | 64015 | I16 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA10 | 0xFA11 | 64016 | 64017 | I17 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA12 | 0xFA13 | 64018 | 64019 | I18 Eq offset calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA14 | 0xFA1F | 64020 | 64031 | Reserved |  |  | 12
ADE7816 Eq Gain Calibration Coefficient (60Hz) | 0xFA20 | 0xFA21 | 64032 | 64033 | I1 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA22 | 0xFA23 | 64034 | 64035 | I2 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA24 | 0xFA25 | 64036 | 64037 | I3 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA26 | 0xFA27 | 64038 | 64039 | I4 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA28 | 0xFA29 | 64040 | 64041 | I5 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA2A | 0xFA2B | 64042 | 64043 | I6 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA2C | 0xFA2D | 64044 | 64045 | I7 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA2E | 0xFA2F | 64046 | 64047 | I8 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA30 | 0xFA31 | 64048 | 64049 | I9 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA32 | 0xFA33 | 64050 | 64051 | I10 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA34 | 0xFA35 | 64052 | 64053 | I11 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA36 | 0xFA37 | 64054 | 64055 | I12 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA38 | 0xFA39 | 64056 | 64057 | I13 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA3A | 0xFA3B | 64058 | 64059 | I14 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA3C | 0xFA3D | 64060 | 64061 | I15 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA3E | 0xFA3F | 64062 | 64063 | I16 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA40 | 0xFA41 | 64064 | 64065 | I17 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA42 | 0xFA43 | 64066 | 64067 | I18 Eq gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFA44 | 0xFA4F | 64068 | 64079 | Reserved |  |  | 12
ADE7816 V/I Gain Calibration Coefficient (50Hz) | 0xFC00 | 0xFC01 | 64512 | 64513 | Va Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
(RCT, non-MC only) | 0xFC02 | 0xFC03 | 64514 | 64515 | Vb Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC04 | 0xFC05 | 64516 | 64517 | Vc Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC06 | 0xFC07 | 64518 | 64519 | I1 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC08 | 0xFC09 | 64520 | 64521 | I2 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC0A | 0xFC0B | 64522 | 64523 | I3 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC0C | 0xFC0D | 64524 | 64525 | I4 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC0E | 0xFC0F | 64526 | 64527 | I5 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC10 | 0xFC11 | 64528 | 64529 | I6 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC12 | 0xFC13 | 64530 | 64531 | I7 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC14 | 0xFC15 | 64532 | 64533 | I8 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC16 | 0xFC17 | 64534 | 64535 | I9 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC18 | 0xFC19 | 64536 | 64537 | I10 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC1A | 0xFC1B | 64538 | 64539 | I11 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC1C | 0xFC1D | 64540 | 64541 | I12 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC1E | 0xFC1F | 64542 | 64543 | I13 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC20 | 0xFC21 | 64544 | 64545 | I14 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC22 | 0xFC23 | 64546 | 64547 | I15 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC24 | 0xFC25 | 64548 | 64549 | I16 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC26 | 0xFC27 | 64550 | 64551 | I17 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC28 | 0xFC29 | 64552 | 64553 | I18 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC2A | 0xFC2F | 64554 | 64559 | Reserved |  |  | 6
ADE7816 Phase Calibration Coefficient (50Hz) | 0xFC30 | 0xFC31 | 64560 | 64561 | I1 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
(RCT, non-MC only) | 0xFC32 | 0xFC33 | 64562 | 64563 | I2 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC34 | 0xFC35 | 64564 | 64565 | I3 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC36 | 0xFC37 | 64566 | 64567 | I4 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC38 | 0xFC39 | 64568 | 64569 | I5 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC3A | 0xFC3B | 64570 | 64571 | I6 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC3C | 0xFC3D | 64572 | 64573 | I7 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC3E | 0xFC3F | 64574 | 64575 | I8 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC40 | 0xFC41 | 64576 | 64577 | I9 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC42 | 0xFC43 | 64578 | 64579 | I10 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC44 | 0xFC45 | 64580 | 64581 | I11 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC46 | 0xFC47 | 64582 | 64583 | I12 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC48 | 0xFC49 | 64584 | 64585 | I13 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC4A | 0xFC4B | 64586 | 64587 | I14 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC4C | 0xFC4D | 64588 | 64589 | I15 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC4E | 0xFC4F | 64590 | 64591 | I16 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC50 | 0xFC51 | 64592 | 64593 | I17 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC52 | 0xFC53 | 64594 | 64595 | I18 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC54 | 0xFC5F | 64596 | 64607 | Reserved |  |  | 12
ADE7816 V/I Gain Calibration Coefficient (60Hz) | 0xFC60 | 0xFC61 | 64608 | 64609 | Va Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
(RCT, non-MC only) | 0xFC62 | 0xFC63 | 64610 | 64611 | Vb Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC64 | 0xFC65 | 64612 | 64613 | Vc Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC66 | 0xFC67 | 64614 | 64615 | I1 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC68 | 0xFC69 | 64616 | 64617 | I2 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC6A | 0xFC6B | 64618 | 64619 | I3 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC6C | 0xFC6D | 64620 | 64621 | I4 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC6E | 0xFC6F | 64622 | 64623 | I5 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC70 | 0xFC71 | 64624 | 64625 | I6 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC72 | 0xFC73 | 64626 | 64627 | I7 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC74 | 0xFC75 | 64628 | 64629 | I8 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC76 | 0xFC77 | 64630 | 64631 | I9 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC78 | 0xFC79 | 64632 | 64633 | I10 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC7A | 0xFC7B | 64634 | 64635 | I11 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC7C | 0xFC7D | 64636 | 64637 | I12 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC7E | 0xFC7F | 64638 | 64639 | I13 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC80 | 0xFC81 | 64640 | 64641 | I14 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC82 | 0xFC83 | 64642 | 64643 | I15 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC84 | 0xFC85 | 64644 | 64645 | I16 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC86 | 0xFC87 | 64646 | 64647 | I17 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC88 | 0xFC89 | 64648 | 64649 | I18 Gain calibration coefficient | int32 | R/W | 2 | -8388608~+8388607
| 0xFC8A | 0xFC8F | 64650 | 64655 | Reserved |  |  | 6
ADE7816 Phase Calibration Coefficient (60Hz) | 0xFC90 | 0xFC91 | 64656 | 64657 | I1 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
(RCT, non-MC only) | 0xFC92 | 0xFC93 | 64658 | 64659 | I2 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC94 | 0xFC95 | 64660 | 64661 | I3 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC96 | 0xFC97 | 64662 | 64663 | I4 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC98 | 0xFC99 | 64664 | 64665 | I5 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC9A | 0xFC9B | 64666 | 64667 | I6 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC9C | 0xFC9D | 64668 | 64669 | I7 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFC9E | 0xFC9F | 64670 | 64671 | I8 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFCA0 | 0xFCA1 | 64672 | 64673 | I9 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFCA2 | 0xFCA3 | 64674 | 64675 | I10 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFCA4 | 0xFCA5 | 64676 | 64677 | I11 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFCA6 | 0xFCA7 | 64678 | 64679 | I12 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFCA8 | 0xFCA9 | 64680 | 64681 | I13 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFCAA | 0xFCAB | 64682 | 64683 | I14 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFCAC | 0xFCAD | 64684 | 64685 | I15 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFCAE | 0xFCAF | 64686 | 64687 | I16 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFCB0 | 0xFCB1 | 64688 | 64689 | I17 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFCB2 | 0xFCB3 | 64690 | 64691 | I18 Phase calibration coefficient | dword | R/W | 2 | 0 ~ 16777215
| 0xFCB4 | 0xFCBF | 64692 | 64703 | Reserved |  |  | 12
Utility Software Use Address | 0xFB00 | 0xFB95 | 64256 | 64405 | Utility Software Use Address | word | R/W | 150
Calibration Method:
1. Amplitude Calibration Principle
Due to differences in analog circuit components and PCB layout, for different channels, the same signal will have slight deviations from its actual value after being converted through the analog circuit to the AD input terminal. This is caused by hardware characteristics. A software calibration method is used to address this issue:
Assume the theoretical input value of a parameter is A1, and the measured value from the instrument is A2.
Calibration coefficient: adj = 65535 × (A1 − A2) / A2
Calibrated instrument output: A3 = A2 × (1 + adj / 65535)
Thus, A3 = A1
2. Phase Angle Calibration Principle
In theory, after voltage and current signals undergo A/D conversion and data processing into phasor form, the phase angle difference between them should remain unchanged. However, due to hardware factors (such as different phase shifts in transformers) and software factors (such as sampling delays), the actual measured phase angle difference contains errors.
Since current parameter calculations are based on phasors and are highly sensitive to phase angle differences, angle compensation is required.
The compensation method is to multiply the obtained phasor by a phasor factor whose phase equals the angle difference, thereby achieving angle correction.
Algorithm description:
The real and imaginary parts of the measured phasors are transmitted to the host computer via communication. The host computer calculates their phase angles and uses Ia as the reference to determine the phase angle differences relative to Ia. These are then compared with theoretical values to obtain the absolute phase error.
The cosine of this error is taken as the real part of the phasor factor, and the sine as the imaginary part. Multiplying the measured phasor by this factor achieves phase compensation.
Calibration Principles:
1. Offset Calibration Formula
The offset calibration principle for current is the same as that for voltage.
2. Gain Calibration
The current gain calibration is the same as the voltage gain calibration.
3. Phase Calibration
Phase calibration is performed when PF = 0.5L (power factor = 0.5, inductive).

## Network Module
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Net Module Setting | 0xFF | 0xFF | 255 | 255 | Net Module Reset | Word | R/W | 1 | 0: None 1: Reset 2: Reset and reset to default
(0x03 Read, 0x10 Write) | 0x100 | 0x100 | 256 | 256 | Status Flag 1 | Word | R/W | 1 | Bit 0 Connection (0: Disconnected；1: Connected) Bit 1 Reset (not in use) Bit2 Net Module Reset
| 0x101 | 0x101 | 257 | 257 | Status Flag 2 | Word | R/W | 1 | Bit 0 Setting Changed (default frequency, user channel, channel 1~18 name and mapping) Bit1 New alarm Bit2 New SOE Bit3 Reset webpage password Bit4 IP address and etc. (102H~10FH) Bit5 200H e-mail Bit6 New system event
| 0x102 | 0x102 | 258 | 258 | DHCP Enable/Disable | Word | R/W | 1 | 0: Static IP, 1: DHCP
| 0x103 | 0x103 | 259 | 259 | IP address 1st byte (high) IP address 2nd byte (low) | Word | R/W | 1 | 0~255, default 192 (high) 0~255, default 168 (low)
| 0x104 | 0x104 | 260 | 260 | IP address 3rd byte (high) IP address 4th byte (low) | Word | R/W | 1 | 0~255, default 1 (high) 0~255, default 254 (low)
| 0x105 | 0x105 | 261 | 261 | Subnet mask 1st byte (high) Subnet mask 2nd byte (low) | Word | R/W | 1 | 0~255, default 255 (high) 0~255, default 255 (low)
| 0x106 | 0x106 | 262 | 262 | Subnet mask 3rd byte (high) Subnet mask 4th byte (low) | Word | R/W | 1 | 0~255, default 255 (high) 0~255, default 0 (low)
| 0x107 | 0x107 | 263 | 263 | Gateway 1st byte (high) Gateway 2nd byte (low) | Word | R/W | 1 | 0~255, default 192 (high) 0~255, default 168 (low)
| 0x108 | 0x108 | 264 | 264 | Gateway 3rd byte (high) Gateway 4th byte (low) | Word | R/W | 1 | 0~255, default 1 (high) 0~255, default 1 (low)
| 0x109 | 0x109 | 265 | 265 | Primary DNS server 1st byte (high) Primary DNS server 2nd byte (low) | Word | R/W | 1 | 0~255, default 202 (high) 0~255, default 106 (low)
| 0x10A | 0x10A | 266 | 266 | Primary DNS server 3rd byte (high) Primary DNS server 4th byte (low) | Word | R/W | 1 | 0~255, default 0 (high) 0~255, default 20 (low)
| 0x10B | 0x10B | 267 | 267 | Secondary DNS server 1st byte (high) Secondary DNS server 2nd byte (low) | Word | R/W | 1 | 0~255 0~255
| 0x10C | 0x10C | 268 | 268 | Secondary DNS server 3rd byte (high) Secondary DNS server 4th byte (low) | Word | R/W | 1 | 0~255 0~255
| 0x10D | 0x10D | 269 | 269 | Modbus TCP/IP port | Word |  | 1 | 2000-5999 (deault 502)
| 0x10E | 0x10E | 270 | 270 | HTTP port | Word | R/W | 1 | 6000-9999 (deafult 80)
| 0x10F | 0x10F | 271 | 271 | Reserved |  |  | 1
| 0x110 | 0x110 | 272 | 272 | IP address 1st byte (high) - IP2 IP address 2nd byte (low) - IP2 | Word | R/W | 1 | 0~255, default 192 (high) 0~255, default 168 (low)
| 0x111 | 0x111 | 273 | 273 | IP address 3rd byte (high) - IP2 IP address 4th byte (low) - IP2 | Word | R/W | 1 | 0~255, default 1 (high) 0~255, default 254 (low)
| 0x112 | 0x112 | 274 | 274 | IP address 1st byte (high) - WiFi IP address 2nd byte (low) - WiFi | Word | R/W | 1 | 0~255, default 192 (high) 0~255, default 168 (low)
| 0x113 | 0x113 | 275 | 275 | IP address 3rd byte (high) - WiFi IP address 4th byte (low) - WiFi | Word | R/W | 1 | 0~255, default 1 (high) 0~255, default 254 (low)
| 0x200 | 0x20E | 512 | 526 | Device description | Word | R/W | 15

## Meter Settings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Meter Settings | 0x800 | 0x800 | 2048 | 2048 | COM1 Device address | word | R/W | 1 | 1-247 | 1
(0x03 Read, 0x10 Write) | 0x801 | 0x801 | 2049 | 2049 | COM1 Modbus Parity | word | R/W | 1 | 0: Even; 1: Odd; 2: None2; 3: None1 | 3
| 0x802 | 0x802 | 2050 | 2050 | COM2 Modbus Parity | word | R/W | 1 | 3: None1 | 3
| 0x803 | 0x803 | 2051 | 2051 | COM1 Modbus Baudrate | word | R/W | 1 | 1200-11520 (115200) | 19200
| 0x804 | 0x804 | 2052 | 2052 | COM2 Modbus Baudrate | word | R/W | 1 | 11520 (115200) | 11520
| 0x805 | 0x805 | 2053 | 2053 | Meter Password | word | R/W | 1 | 0000-9999 | 0
| 0x806 | 0x806 | 2054 | 2054 | Pulse Constant - low bytes (DO1 if pulse constant extension ON) | word | R/W | 1 | 1-65535 | 50000
| 0x807 | 0x807 | 2055 | 2055 | Pulse Width | word | R/W | 1 | 20-100ms | 80
| 0x808 | 0x808 | 2056 | 2056 | COM2 Device address | word | R/W | 1 | 1-247 | 1
| 0x809 | 0x809 | 2057 | 2057 | Pulse Constant - high bytes (DO1 if pulse constant extension ON) | word | R/W | 1 | 0-100 | 0
| 0x80A | 0x80A | 2058 | 2058 | Demand Calculation Method | word | R/W | 1 | 0: Sliding (MC not support) 1: Rolling 2: Fixed 3: Thermal | 1
| 0x80B | 0x80B | 2059 | 2059 | Demand Interval | word | R/W | 1 | 1-30 min | 15
| 0x80C | 0x80C | 2060 | 2060 | Demand Sub-Interval | word | R/W | 1 | 1-30 min | 1
| 0x80D | 0x80D | 2061 | 2061 | CT Type | word | R/W | 1 | mA: 80:80mA; 100:100mA mV: 333: 333mV; 120: RCT | 80
| 0x80E | 0x80E | 2062 | 2062 | COM1 Protocol Selection | word | R/W | 1 | 0x00：Modbus-RTU 0x02：BACnet MS/TP | 0
| 0x80F | 0x80F | 2063 | 2063 | COM1 BACnet MS/TP device address | word | R/W | 1 | 0-127 | 1
| 0x810 | 0x810 | 2064 | 2064 | COM1 BACnet MS/TP baudrate | word | R/W | 1 | 1200-11520 (115200) | 19200
| 0x811 | 0x811 | 2065 | 2065 | COM1 BACnet MS/TP max info frame | word | R/W | 1 | 1-255 | 10
| 0x812 | 0x813 | 2066 | 2067 | COM1 BACnet MS/TP BACnet ID | word | R/W | 2 | 1~4194303 | 1
| 0x814 | 0x814 | 2068 | 2068 | COM1 BACnet MS/TP Database Revision | word | R | 1 | 0-65535 | 0
| 0x815 | 0x815 | 2069 | 2069 | Current Direction high bytes | word | R/W | 1 | Bit0~Bit1: I17~I18 0: Positive; 1: Negative | 0
| 0x816 | 0x816 | 2070 | 2070 | Current Direction low bytes | word | R/W | 1 | Bit0~Bit15: I1~I16 0: Positive; 1: Negative | 0
| 0x817 | 0x817 | 2071 | 2071 | Pulse Constant Extension | word | R/W | 1 | 1: Enable; 0: Disable | 0
| 0x818 | 0x819 | 2072 | 2073 | DO2 Pulse Constant | word | R/W | 2 | 1~6000000 | 50000
| 0x81A | 0x81B | 2074 | 2075 | DO3 Pulse Constant | word | R/W | 2 | 1~6000000 | 50000
| 0x81C | 0x81D | 2076 | 2077 | DO4 Pulse Constant | word | R/W | 2 | 1~6000000 | 50000
| 0x81E | 0x81F | 2078 | 2079 | DO5 Pulse Constant | word | R/W | 2 | 1~6000000 | 50000
| 0x820 | 0x821 | 2080 | 2081 | DO6 Pulse Constant | word | R/W | 2 | 1~6000000 | 50000
| 0x822 | 0x827 | 2082 | 2087 | Reserved | word | R/W | 6
| 0x828 | 0x828 | 2088 | 2088 | Relay Work Type | word | R/W | 1 | bit0~bit1: RO1~RO2 0: Remote 1: Alarm | 0
| 0x829 | 0x829 | 2089 | 2089 | Relay Remote Output Type | word | R/W | 1 | bit0~bit1: RO1~RO2 0: Level 1: Pulse | 0
| 0x82A | 0x82A | 2090 | 2090 | Relay Pulse Width | word | R/W | 1 | 50-3000ms | 80
| 0x82B | 0x82B | 2091 | 2091 | Out-of-range Alarm Switch | word | R/W | 1 | 0: Disable 1: Enable | 0
| 0x82C | 0x82C | 2092 | 2092 | Alarm Channel 1~10 Switch | word | R/W | 1 | Bit0-bit9: Alarm Channel 1-10 1: Enable 0: Disable | 0
| 0x82D | 0x82D | 2093 | 2093 | Each event alarm outputs to the relay's enable bit. 2 bytes representing a total of 16 events. The event output is then sent to the relay for enable | word | R/W | 1 | Bit0-15: 16 events 1: Enable 0: Disable | 0
| 0x82E | 0x82E | 2094 | 2094 | Event relay alarm mode, the first 8 types Each event correspondings to relay output settings | word | R/W | 1 | 2 byte, each 2 bit: one event 00: Relay 1 01: Relay 2 | 0
| 0x82F | 0x82F | 2095 | 2095 | The rest 8 types, same as above | word | R/W | 1 | Same as above | 0
| 0x830 | 0x830 | 2096 | 2096 | Event relay alarm mode output time (Not support out-of-range alarm) | word | R/W | 1 | 1-60000 sec | 60
| 0x831 | 0x831 | 2097 | 2097 | Backlight Off Delay Time | word | R/W | 1 | 0-60 min | 1
| 0x832 | 0x832 | 2098 | 2098 | Auto-cycling Display Start Delay Time | word | R/W | 1 | 1-60 min | 1
| 0x833 | 0x833 | 2099 | 2099 | Auto-cycling Each Page Display Time | word | R/W | 1 | 5-100 sec | 5
| 0x834 | 0x834 | 2100 | 2100 | Decimal place of Power/Demand | word | R/W | 1 | 3-4 places | 3
| 0x835 | 0x835 | 2101 | 2101 | VAR Calculation Method | word | R/W | 1 | 0: True 1: Generalized | 0
| 0x836 | 0x836 | 2102 | 2102 | VAR/PF Convention | word | R/W | 1 | 0: IEC 1: IEEE | 0
| 0x837 | 0x837 | 2103 | 2103 | Clear Data | word | R/W | 1 | See Appendix A | 0
| 0x838 | 0x839 | 2104 | 2105 | Clear DI pulse counter Each bit stands for each DI | word | R/W | 2 | 0x838: bit0~bit15 DI1~DI16 0x839: bit0~bit1 DI17~DI18 Set 1 to clear | 0
| 0x83A | 0x83E | 2106 | 2110 | Reserved | word | R/W | 5
| 0x83F | 0x841 | 2111 | 2113 | user01 User Name | word | R/W | 3 | User Name (6 ASCII) | user01
| 0x842 | 0x842 | 2114 | 2114 | user01 Mapping | word | R/W | 1 | High byte 0：Not to display on HMI 1：Display on HMI Low byte 0：Disable 1-18：Individual Channel 1-18 19-27：User Channel 1-9 | 0x0101
| 0x843 | 0x845 | 2115 | 2117 | user02 User Name | word | R/W | 3 | Same as user01 User Name | user02
| 0x846 | 0x846 | 2118 | 2118 | user02 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x0102
| 0x847 | 0x849 | 2119 | 2121 | user03 User Name | word | R/W | 3 | Same as user01 User Name | user03
| 0x84A | 0x84A | 2122 | 2122 | user03 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x0103
| 0x84B | 0x84D | 2123 | 2125 | user04 User Name | word | R/W | 3 | Same as user01 User Name | user04
| 0x84E | 0x84E | 2126 | 2126 | user04 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x0104
| 0x84F | 0x851 | 2127 | 2129 | user05 User Name | word | R/W | 3 | Same as user01 User Name | user05
| 0x852 | 0x852 | 2130 | 2130 | user05 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x0105
| 0x853 | 0x855 | 2131 | 2133 | user06 User Name | word | R/W | 3 | Same as user01 User Name | user06
| 0x856 | 0x856 | 2134 | 2134 | user06 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x0106
| 0x857 | 0x859 | 2135 | 2137 | user07 User Name | word | R/W | 3 | Same as user01 User Name | user07
| 0x85A | 0x85A | 2138 | 2138 | user07 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x0107
| 0x85B | 0x85D | 2139 | 2141 | user08 User Name | word | R/W | 3 | Same as user01 User Name | user08
| 0x85E | 0x85E | 2142 | 2142 | user08 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x0108
| 0x85F | 0x861 | 2143 | 2145 | user09 User Name | word | R/W | 3 | Same as user01 User Name | user09
| 0x862 | 0x862 | 2146 | 2146 | user09 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x0109
| 0x863 | 0x865 | 2147 | 2149 | user10 User Name | word | R/W | 3 | Same as user01 User Name | user10
| 0x866 | 0x866 | 2150 | 2150 | user10 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x010a
| 0x867 | 0x869 | 2151 | 2153 | user11 User Name | word | R/W | 3 | Same as user01 User Name | user11
| 0x86A | 0x86A | 2154 | 2154 | user11 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x010b
| 0x86B | 0x86D | 2155 | 2157 | user12 User Name | word | R/W | 3 | Same as user01 User Name | user12
| 0x86E | 0x86E | 2158 | 2158 | user12 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x010c
| 0x86F | 0x871 | 2159 | 2161 | user13 User Name | word | R/W | 3 | Same as user01 User Name | user13
| 0x872 | 0x872 | 2162 | 2162 | user13 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x010d
| 0x873 | 0x875 | 2163 | 2165 | user14 User Name | word | R/W | 3 | Same as user01 User Name | user14
| 0x876 | 0x876 | 2166 | 2166 | user14 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x010e
| 0x877 | 0x879 | 2167 | 2169 | user15 User Name | word | R/W | 3 | Same as user01 User Name | user15
| 0x87A | 0x87A | 2170 | 2170 | user15 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x010f
| 0x87B | 0x87D | 2171 | 2173 | user16 User Name | word | R/W | 3 | Same as user01 User Name | user16
| 0x87E | 0x87E | 2174 | 2174 | user16 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x0110
| 0x87F | 0x881 | 2175 | 2177 | user17 User Name | word | R/W | 3 | Same as user01 User Name | user17
| 0x882 | 0x882 | 2178 | 2178 | user17 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x0111
| 0x883 | 0x885 | 2179 | 2181 | user18 User Name | word | R/W | 3 | Same as user01 User Name | user18
| 0x886 | 0x886 | 2182 | 2182 | user18 Mapping | word | R/W | 1 | Same as user01 Mapping | 0x0112
| 0x887 | 0x887 | 2183 | 2183 | Rated Voltage | word | R/W | 1 | 10~400 | 220
| 0x888 | 0x888 | 2184 | 2184 | Wiring Type | word | R/W | 1 | MC: 0: 1LN; 1: 3LN; 2: 2LN; 3: 2LL; 4: Network Non-MC: 0: 1LN; 1: 3LN; 2: 2LN; 3: High-leg delta; 4: 2LL; 5: Network | 0
| 0x889 | 0x889 | 2185 | 2185 | CT 1 Full-scale | word | R/W | 1 | Note: valid for EM, not DM Configurable, e.g. 20: CCT-20 (full scale 20A) 80: CCT-80 (full scale 80A) 150: CCT-150 (full scale 150A) 200: CCT-200 (full scale 200A) | 200
| 0x88A | 0x88A | 2186 | 2186 | CT 2 Full-scale | word | R/W | 1 | Same as above | 200
| 0x88B | 0x88B | 2187 | 2187 | CT 3 Full-scale | word | R/W | 1 | Same as above | 200
| 0x88C | 0x88C | 2188 | 2188 | CT 4 Full-scale | word | R/W | 1 | Same as above | 200
| 0x88D | 0x88D | 2189 | 2189 | CT 5 Full-scale | word | R/W | 1 | Same as above | 200
| 0x88E | 0x88E | 2190 | 2190 | CT 6 Full-scale | word | R/W | 1 | Same as above | 200
| 0x88F | 0x88F | 2191 | 2191 | CT 7 Full-scale | word | R/W | 1 | Same as above | 200
| 0x890 | 0x890 | 2192 | 2192 | CT 8 Full-scale | word | R/W | 1 | Same as above | 200
| 0x891 | 0x891 | 2193 | 2193 | CT 9 Full-scale | word | R/W | 1 | Same as above | 200
| 0x892 | 0x892 | 2194 | 2194 | CT 10 Full-scale | word | R/W | 1 | Same as above | 200
| 0x893 | 0x893 | 2195 | 2195 | CT 11 Full-scale | word | R/W | 1 | Same as above | 200
| 0x894 | 0x894 | 2196 | 2196 | CT 12 Full-scale | word | R/W | 1 | Same as above | 200
| 0x895 | 0x895 | 2197 | 2197 | CT 13 Full-scale | word | R/W | 1 | Same as above | 200
| 0x896 | 0x896 | 2198 | 2198 | CT 14 Full-scale | word | R/W | 1 | Same as above | 200
| 0x897 | 0x897 | 2199 | 2199 | CT 15 Full-scale | word | R/W | 1 | Same as above | 200
| 0x898 | 0x898 | 2200 | 2200 | CT 16 Full-scale | word | R/W | 1 | Same as above | 200
| 0x899 | 0x899 | 2201 | 2201 | CT 17 Full-scale | word | R/W | 1 | Same as above | 200
| 0x89A | 0x89A | 2202 | 2202 | CT 18 Full-scale | word | R/W | 1 | Same as above | 200
0x89B~0x8AC not in use, reserved | 0x89B | 0x89B | 2203 | 2203 | CT 1 Max Value | word | R/W | 1 | Configurable | 0
| 0x89C | 0x89C | 2204 | 2204 | CT 2 Max Value | word | R/W | 1 | Same as above | 0
| 0x89D | 0x89D | 2205 | 2205 | CT 3 Max Value | word | R/W | 1 | Same as above | 0
| 0x89E | 0x89E | 2206 | 2206 | CT 4 Max Value | word | R/W | 1 | Same as above | 0
| 0x89F | 0x89F | 2207 | 2207 | CT 5 Max Value | word | R/W | 1 | Same as above | 0
| 0x8A0 | 0x8A0 | 2208 | 2208 | CT 6 Max Value | word | R/W | 1 | Same as above | 0
| 0x8A1 | 0x8A1 | 2209 | 2209 | CT 7 Max Value | word | R/W | 1 | Same as above | 0
| 0x8A2 | 0x8A2 | 2210 | 2210 | CT 8 Max Value | word | R/W | 1 | Same as above | 0
| 0x8A3 | 0x8A3 | 2211 | 2211 | CT 9 Max Value | word | R/W | 1 | Same as above | 0
| 0x8A4 | 0x8A4 | 2212 | 2212 | CT 10 Max Value | word | R/W | 1 | Same as above | 0
| 0x8A5 | 0x8A5 | 2213 | 2213 | CT 11 Max Value | word | R/W | 1 | Same as above | 0
| 0x8A6 | 0x8A6 | 2214 | 2214 | CT 12 Max Value | word | R/W | 1 | Same as above | 0
| 0x8A7 | 0x8A7 | 2215 | 2215 | CT 13 Max Value | word | R/W | 1 | Same as above | 0
| 0x8A8 | 0x8A8 | 2216 | 2216 | CT 14 Max Value | word | R/W | 1 | Same as above | 0
| 0x8A9 | 0x8A9 | 2217 | 2217 | CT 15 Max Value | word | R/W | 1 | Same as above | 0
| 0x8AA | 0x8AA | 2218 | 2218 | CT 16 Max Value | word | R/W | 1 | Same as above | 0
| 0x8AB | 0x8AB | 2219 | 2219 | CT 17 Max Value | word | R/W | 1 | Same as above | 0
| 0x8AC | 0x8AC | 2220 | 2220 | CT 18 Max Value | word | R/W | 1 | Same as above | 0
| 0x8AD | 0x8AD | 2221 | 2221 | Reset to Default | word | R/W | 1 | 0: None 0xAA: Reset to default | 0
| 0x8AE | 0x8AE | 2222 | 2222 | Enable Ten-year Setting Download | word | R/W | 1 | 1: Enable | 0
| 0x8AF | 0x8AF | 2223 | 2223 | Non-standard Sealing Options | word | R/W | 1 | Bit0：RS485 communication Bit1：Network Bit2：Clear device run time Bit3：Reserved Bit4：TOU Bit5： RO Bit6： RTC 1: Enable 0: Disable | 0
| 0x8B0 | 0x8B0 | 2224 | 2224 | Seal Status | word | R/W | 1 | 0: Seal open, or no seal 0x0A: Sealed | 0x0
| 0x8B1 | 0x8B1 | 2225 | 2225 | DO1 Channel Setting | word | R/W | 1 | See Appendix B | 0
| 0x8B2 | 0x8B2 | 2226 | 2226 | DO2 Channel Setting | word | R/W | 1 | See Appendix B | 0
| 0x8B3 | 0x8B3 | 2227 | 2227 | DO3 Channel Setting | word | R/W | 1 | See Appendix B | 0
| 0x8B4 | 0x8B4 | 2228 | 2228 | DO4 Channel Setting | word | R/W | 1 | See Appendix B | 0
| 0x8B5 | 0x8B5 | 2229 | 2229 | DO5 Channel Setting | word | R/W | 1 | See Appendix B | 0
| 0x8B6 | 0x8B6 | 2230 | 2230 | DO6 Channel Setting | word | R/W | 1 | See Appendix B | 0
| 0x8B7 | 0x8B7 | 2231 | 2231 | DI Sync to Demand Trigger | word | R/W | 1 | 1~18: DI1~DI18 | 1
| 0x8B8 | 0x8B8 | 2232 | 2232 | DI Trigger Condition | word | R/W | 1 | 0: None 1: Rising 2: Falling 3: Triggered by change | 0
| 0x8B9 | 0x8BA | 2233 | 2234 | DI Work Type | word | R/W | 2 | 0x8B9: bit0~bit16 DI1~DI16 0x8BA: bit0~bit1 DI17~DI18 0：State 1：Counter | 1
| 0x8BB | 0x8CC | 2235 | 2252 | DI1~18 Pulse Counter Constant | word | R/W | 18 | 1-65535 | 1
| 0x8CD | 0x8DE | 2253 | 2270 | DI1~18 Pulse Counter Ratio | word | R/W | 18 | e.g. 1 pulse = 20 t water | 1
| 0x8DF | 0x8F0 | 2271 | 2288 | DI1~18 Pulse Counter Unit | word | R/W | 18 | 1: t 2: m3 3: kwh 4: ￥ 5: $ | 1
| 0x8F1 | 0x8F1 | 2289 | 2289 | Programming Key Status | word | R/W | 1 | 0: Disabled 0x0A: Enabled | 0x0
| 0x8F2 | 0x8FF | 2290 | 2303 | Reserved | word |  | 14

## Demand Max Reset & Wire Check
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Demand Max Reset | 0x900 | 0x900 | 2304 | 2304 | Mode of demand max reset | Word | R/W | 1 | 0: Disable; 1: Auto; 2: Manual | 2
(0x03 Read, 0x10 Write) | 0x901 | 0x901 | 2305 | 2305 | Demand max reset counter | Word | R | 1 |  | 0
| 0x902 | 0x907 | 2306 | 2311 | Last demand max reset timestamp | Word | R | 6 | YY MM DD hh mm ss | 00 01 01 00 00 00
Wire Check | 0x910 | 0x910 | 2320 | 2320 | Wire check enable/disable | Word | R/W | 1 | 0: Disable; 1: Enable | 0
(0x03 Read, 0x10 Write) | 0x911 | 0x911 | 2321 | 2321 | Wire check update | Word | R/W | 1 | 0: No; 1: Yes | 0
| 0x912 | 0x912 | 2322 | 2322 | Voltage input A, B, C result | Word | R | 1 | Bit0 - Bit3: Va (missing, incorrect, reversal) Bit4 - Bit6: Vb (missing, incorrect, reversal) Bit8 - Bit10: Vc (missing, incorrect, reversal)
| 0x913 | 0x913 | 2323 | 2323 | Current input 1, 2, 3 result | Word | R | 1 | Bit0 - Bit3: I1 (missing, incorrect, reversal) Bit4 - Bit6: I2 (missing, incorrect, reversal) Bit8 - Bit10: I3 (missing, incorrect, reversal)
| 0x914 | 0x914 | 2324 | 2324 | Current input 4, 5, 6 result | Word | R | 1 | Bit0 - Bit3: I4 (missing, incorrect, reversal) Bit4 - Bit6: I5 (missing, incorrect, reversal) Bit8 - Bit10: I6 (missing, incorrect, reversal)
| 0x915 | 0x915 | 2325 | 2325 | Current input 7, 8, 9 result | Word | R | 1 | Bit0 - Bit3: I7 (missing, incorrect, reversal) Bit4 - Bit6: I8 (missing, incorrect, reversal) Bit8 - Bit10: I9 (missing, incorrect, reversal)
| 0x916 | 0x916 | 2326 | 2326 | Current input 10, 11, 12 result | Word | R | 1 | Bit0 - Bit3: I10 (missing, incorrect, reversal) Bit4 - Bit6: I11 (missing, incorrect, reversal) Bit8 - Bit10: I12 (missing, incorrect, reversal)
| 0x917 | 0x917 | 2327 | 2327 | Current input 13, 14, 15 result | Word | R | 1 | Bit0 - Bit3: I13 (missing, incorrect, reversal) Bit4 - Bit6: I14 (missing, incorrect, reversal) Bit8 - Bit10: I15 (missing, incorrect, reversal)
| 0x918 | 0x918 | 2328 | 2328 | Current input 16, 17, 18 result | Word | R | 1 | Bit0 - Bit3: I16 (missing, incorrect, reversal) Bit4 - Bit6: I17 (missing, incorrect, reversal) Bit8 - Bit10: I18 (missing, incorrect, reversal)

## Meter Run Time & Clock
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Device Run Time | 0x1050 | 0x1051 | 4176 | 4177 | Device Run Time | Dword | R | 2
(0x03 Read)
System Clock | 0x1054 | 0x1054 | 4180 | 4180 | Year | Word | R/W | 1 | 0~99
(0x03 Read, 0x10 Write) | 0x1055 | 0x1055 | 4181 | 4181 | Month | Word | R/W | 1 | 1~12
| 0x1056 | 0x1056 | 4182 | 4182 | Day | Word | R/W | 1 | 1~31
| 0x1057 | 0x1057 | 4183 | 4183 | Hour | Word | R/W | 1 | 0~23
| 0x1058 | 0x1058 | 4184 | 4184 | Minute | Word | R/W | 1 | 0~59
| 0x1059 | 0x1059 | 4185 | 4185 | Second | Word | R/W | 1 | 0~59
| 0x105A | 0x105A | 4186 | 4186 | Week | Word | R/W | 1 | 0~6, 0: Sunday

## Alarm Settings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Alarm Settings | 0x105B | 0x105B | 4187 | 4187 | 1st group: Alarm Parameter Number | integer | R/W | 1 | 0~370 (if wiring type is Network, then 0~400)
(0x03 Read, 0x10 Write) | 0x105C | 0x105C | 4188 | 4188 | 1st group: Comparing Method | integer | R/W | 1 | 1: greater; 2: equal; 3: less (only "equal" in DI state)
| 0x105D | 0x105D | 4189 | 4189 | 1st group: Set Value | integer | R/W | 1 | % * rated value (only 1: ON and 0: OFF in DI state)
| 0x105E | 0x105E | 4190 | 4190 | 1st group: Delay time | integer | R/W | 1 | 0～30000ms
| 0x105F | 0x105F | 4191 | 4191 | 1st group: Output to Relay | integer | R/W | 1 | 0: None; 1: RO1; 2: RO2
| 0x1060 | 0x1064 | 4192 | 4196 | 2nd group Settings | integer | R/W | 5 | Same as 1st group
| 0x1065 | 0x1069 | 4197 | 4201 | 3rd group Settings | integer | R/W | 5 | Same as 1st group
| 0x106A | 0x106E | 4202 | 4206 | 4th group Settings | integer | R/W | 5 | Same as 1st group
| 0x106F | 0x1073 | 4207 | 4211 | 5th group Settings | integer | R/W | 5 | Same as 1st group
| 0x1074 | 0x1078 | 4212 | 4216 | 6th group Settings | integer | R/W | 5 | Same as 1st group
| 0x1079 | 0x107D | 4217 | 4221 | 7th group Settings | integer | R/W | 5 | Same as 1st group
| 0x107E | 0x1082 | 4222 | 4226 | 8th group Settings | integer | R/W | 5 | Same as 1st group
| 0x1083 | 0x1087 | 4227 | 4231 | 9th group Settings | integer | R/W | 5 | Same as 1st group
| 0x1088 | 0x108C | 4232 | 4236 | 10th group Settings | integer | R/W | 5 | Same as 1st group
Note:
There are 10 alarm setting values ​​in total. Note that the parameter setting value here is an integer.
The load rated voltage and load rated current settings are set by the user. The parameter setting values ​​in the alarm parameter settings are expressed as a percentage of the rated value. For example, if the rated voltage is set to 220V, the rated current to 5A, and the alarm is set to alarm for power greater than 3KW, then the percentage of the setting value is 273%, which is 2.73 times the rated power of 1100W. The power factor alarm setting value is -1000 to +1000, and the frequency alarm setting value is 4500-6500.

## TOU Settings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
TOU Basic Settings | 0x1090 | 0x1090 | 4240 | 4240 | Error code 1 (Basic parameter) | Word | R | 1 | See Appendix A
(0x03 Read, 0x10 Write) | 0x1091 | 0x1091 | 4241 | 4241 | Error code 2 (Schedule parameter) | Word | R | 1 | See Appendix A
| 0x1092 | 0x1092 | 4242 | 4242 | Current tariff | Word | R/W | 1 | 1~4 | 1
| 0x1093 | 0x1093 | 4243 | 4243 | Season | Word | R/W | 1 | 1~14 | 2
| 0x1094 | 0x1094 | 4244 | 4244 | Schedule | Word | R/W | 1 | 1~8 | 2
| 0x1095 | 0x1095 | 4245 | 4245 | Segment | Word | R/W | 1 | 1~14 | 9
| 0x1096 | 0x1096 | 4246 | 4246 | Tariff | Word | R/W | 1 | 1~4 | 4
| 0x1097 | 0x1097 | 4247 | 4247 | Weekend day | Word | R/W | 1 | Bit0~7: 1 for weekday, 0 for weekend | 0x7F
| 0x1098 | 0x1098 | 4248 | 4248 | Weekend schedule | Word | R/W | 1 | 1~8 | 2
| 0x1099 | 0x1099 | 4249 | 4249 | Number of special day | Word | R/W | 1 | 0~30 | 0
| 0x109A | 0x109A | 4250 | 4250 | Monthly billing mode | Word | R/W | 1 | 1: Assigned date; 0: End of month | 0
| 0x109B | 0x109B | 4251 | 4251 | Monthly billing time (day) | Word | R/W | 1 | 1~28 | 1
| 0x109C | 0x109C | 4252 | 4252 | Monthly billing time (hour) | Word | R/W | 1 | 0~23 | 0
| 0x109D | 0x109D | 4253 | 4253 | TOU enable | Word | R/W | 1 | 1: Enable; 0: Disable | 1
| 0x109E | 0x109E | 4254 | 4254 | TOU reset to default | Word | R/W | 1 | 1: Reset; 0: None | 0
| 0x109F | 0x10AF | 4255 | 4271 | Reserved |  |  | 17
TOU Scedule Settings | 0x10B0 | 0x10B2 | 4272 | 4274 | 1st Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10B3 | 0x10B5 | 4275 | 4277 | 2nd Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10B6 | 0x10B8 | 4278 | 4280 | 3rd Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10B9 | 0x10BB | 4281 | 4283 | 4th Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10BC | 0x10BE | 4284 | 4286 | 5th Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10BF | 0x10C1 | 4287 | 4289 | 6th Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10C2 | 0x10C4 | 4290 | 4292 | 7th Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10C5 | 0x10C7 | 4293 | 4295 | 8th Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10C8 | 0x10CA | 4296 | 4298 | 9th Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10CB | 0x10CD | 4299 | 4301 | 10th Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10CE | 0x10D0 | 4302 | 4304 | 11th Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10D1 | 0x10D3 | 4305 | 4307 | 12th Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10D4 | 0x10D6 | 4308 | 4310 | 13th Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10D7 | 0x10D9 | 4311 | 4313 | 14th Season - Start date & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x10DA | 0x10DC | 4314 | 4316 | 1st Schedule - 1st Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10DD | 0x10DF | 4317 | 4319 | 1st Schedule - 2nd Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10E0 | 0x10E2 | 4320 | 4322 | 1st Schedule -3rd Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10E3 | 0x10E5 | 4323 | 4325 | 1st Schedule -4th Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10E6 | 0x10E8 | 4326 | 4328 | 1st Schedule -5th Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10E9 | 0x10EB | 4329 | 4331 | 1st Schedule -6th Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10EC | 0x10EE | 4332 | 4334 | 1st Schedule -7th Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10EF | 0x10F1 | 4335 | 4337 | 1st Schedule -8th Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10F2 | 0x10F4 | 4338 | 4340 | 1st Schedule -9th Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10F5 | 0x10F7 | 4341 | 4343 | 1st Schedule -10th Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10F8 | 0x10FA | 4344 | 4346 | 1st Schedule -11th Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10FB | 0x10FD | 4347 | 4349 | 1st Schedule -12th Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x10FE | 0x1100 | 4350 | 4352 | 1st Schedule -13th Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x1101 | 0x1103 | 4353 | 4355 | 1st Schedule -14th Start time & Tariff number | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x1104 | 0x112D | 4356 | 4397 | 2nd Schedule - 1st~14th Start time & Tariff number | word | R/W | 42 | Hour, Minute, Tariff Number
| 0x112E | 0x1157 | 4398 | 4439 | 3rd Schedule - 1st~14th Start time & Tariff number | word | R/W | 42 | Hour, Minute, Tariff Number
| 0x1158 | 0x1181 | 4440 | 4481 | 4th Schedule - 1st~14th Start time & Tariff number | word | R/W | 42 | Hour, Minute, Tariff Number
| 0x1182 | 0x11AB | 4482 | 4523 | 5th Schedule - 1st~14th Start time & Tariff number | word | R/W | 42 | Hour, Minute, Tariff Number
| 0x11AC | 0x11D5 | 4524 | 4565 | 6th Schedule - 1st~14th Start time & Tariff number | word | R/W | 42 | Hour, Minute, Tariff Number
| 0x11D6 | 0x11FF | 4566 | 4607 | 7th Schedule - 1st~14th Start time & Tariff number | word | R/W | 42 | Hour, Minute, Tariff Number
| 0x1200 | 0x1229 | 4608 | 4649 | 8th Schedule - 1st~14th Start time & Tariff number | word | R/W | 42 | Hour, Minute, Tariff Number
| 0x122A | 0x122C | 4650 | 4652 | 1st Special Day - Start time & Schedule ID | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x122D | 0x122F | 4653 | 4655 | 2nd Special Day - Start time & Schedule ID | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x1230 | 0x1232 | 4656 | 4658 | 3rd Special Day - Start time & Schedule ID | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x1233 | 0x1235 | 4659 | 4661 | 4th Special Day - Start time & Schedule ID | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x1236 | 0x1238 | 4662 | 4664 | 5th Special Day - Start time & Schedule ID | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x1239 | 0x123B | 4665 | 4667 | 6th Special Day - Start time & Schedule ID | word | R/W | 3 | Hour, Minute, Tariff Number
| 0x123C | 0x123E | 4668 | 4670 | 7th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x123F | 0x1241 | 4671 | 4673 | 8th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1242 | 0x1244 | 4674 | 4676 | 9th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1245 | 0x1247 | 4677 | 4679 | 10th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1248 | 0x124A | 4680 | 4682 | 11th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x124B | 0x124D | 4683 | 4685 | 12th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x124E | 0x1250 | 4686 | 4688 | 13th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1251 | 0x1253 | 4689 | 4691 | 14th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1254 | 0x1256 | 4692 | 4694 | 15th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1257 | 0x1259 | 4695 | 4697 | 16th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x125A | 0x125C | 4698 | 4700 | 17th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x125D | 0x125F | 4701 | 4703 | 18th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1260 | 0x1262 | 4704 | 4706 | 19th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1263 | 0x1265 | 4707 | 4709 | 20th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1266 | 0x1268 | 4710 | 4712 | 21st Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1269 | 0x126B | 4713 | 4715 | 22nd Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x126C | 0x126E | 4716 | 4718 | 23rd Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x126F | 0x1271 | 4719 | 4721 | 24th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1272 | 0x1274 | 4722 | 4724 | 25th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1275 | 0x1277 | 4725 | 4727 | 26th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1278 | 0x127A | 4728 | 4730 | 27th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x127B | 0x127D | 4731 | 4733 | 28th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x127E | 0x1280 | 4734 | 4736 | 29th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
| 0x1281 | 0x1283 | 4737 | 4739 | 30th Special Day - Start time & Schedule ID | word | R/W | 3 | Month, Day, Schedule ID
Utility software can read the values ​​of error code two bytes to determine which part of TOU settings has error. After setting TOU parameters, it can read these two status words and then pop up a dialog box to tell users. When TOU reset to defaut is enabled, the TOU settings will be reset to the default settings stored in FLASH.

## Datalog Settings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Datalog Settings | 0x1300 | 0x1300 | 4864 | 4864 | Log1 #Registers # Sectors | uinteger | R/W | 1 | #Registers: 0-117 # Sectors: 0-10 | 2
(0x03 Read, 0x10 Write) | 0x1301 | 0x1301 | 4865 | 4865 | Log1 Interval | uinteger | R/W | 1 | 0~65535
| 0x1302 | 0x1376 | 4866 | 4982 | Log1 register #1-#117 identifier | uinteger | R/W | 117 | 0~65535
| 0x1377 | 0x13B1 | 4983 | 5041 | Log1 register #1-#117 descriptors | byte | R/W | 59 | High 4 bits: data type Low 4 bits: data length
| 0x13B2 | 0x13B2 | 5042 | 5042 | Datalog mode | uinteger | R/W | 1 | 0: Mode 1; 1: Mode 2; 2: Mode 3
| 0x13B3 | 0x13B3 | 5043 | 5043 | Start - year, month | uinteger | R/W | 1
| 0x13B4 | 0x13B4 | 5044 | 5044 | Start - day, hour | uinteger | R/W | 1
| 0x13B5 | 0x13B5 | 5045 | 5045 | Start - minute, second | uinteger | R/W | 1
| 0x13B6 | 0x13B6 | 5046 | 5046 | End - year, month | uinteger | R/W | 1
| 0x13B7 | 0x13B7 | 5047 | 5047 | End - day, hour | uinteger | R/W | 1
| 0x13B8 | 0x13B8 | 5048 | 5048 | End - minute, second | uinteger | R/W | 1
| 0x13B9 | 0x13B9 | 5049 | 5049 | Clear datalog | uinteger | R/W | 1 | 0: None; 1: Clear
| 0x13C0 | 0x1479 | 5056 | 5241 | Log2 settings |  | R/W | 186 | Same as Log1
| 0x1480 | 0x1539 | 5248 | 5433 | Log3 settings |  | R/W | 186 | Same as Log1

## Real-time Readings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Inline | 0x2000 | 0x2001 | 8192 | 8193 | Freq | Float | R | 2 | x.xx
(0x03 Read) | 0x2002 | 0x2003 | 8194 | 8195 | U1 | Float | R | 2 | x.x
| 0x2004 | 0x2005 | 8196 | 8197 | U2 | Float | R | 2 | x.x
| 0x2006 | 0x2007 | 8198 | 8199 | U3 | Float | R | 2 | x.x
| 0x2008 | 0x2009 | 8200 | 8201 | Uavg | Float | R | 2 | x.x
| 0x200A | 0x200B | 8202 | 8203 | U12 | Float | R | 2 | x.x
| 0x200C | 0x200D | 8204 | 8205 | U23 | Float | R | 2 | x.x
| 0x200E | 0x200F | 8206 | 8207 | U31 | Float | R | 2 | x.x
| 0x2010 | 0x2011 | 8208 | 8209 | Ulavg | Float | R | 2 | x.x
| 0x2012 | 0x2013 | 8210 | 8211 | IL1 | Float | R | 2 | x.xxx
| 0x2014 | 0x2015 | 8212 | 8213 | IL2 | Float | R | 2 | x.xxx
| 0x2016 | 0x2017 | 8214 | 8215 | IL3 | Float | R | 2 | x.xxx
| 0x2018 | 0x2019 | 8216 | 8217 | Iavg | Float | R | 2 | x.xxx
| 0x201A | 0x201B | 8218 | 8219 | Pin-s | Float | R | 2 | x.xxxx
| 0x201C | 0x201D | 8220 | 8221 | Qin-s | Float | R | 2 | x.xxxx
| 0x201E | 0x201F | 8222 | 8223 | Sin-s | Float | R | 2 | x.xxxx
| 0x2020 | 0x2021 | 8224 | 8225 | PFin-s | Float | R | 2 | x.xxx
| 0x2022 | 0x2023 | 8226 | 8227 | Load Nature S | Float | R | 2 | 1: R; 2: L; 3: C
| 0x2024 | 0x2025 | 8228 | 8229 | Pin-A | Float | R | 2 | x.xxxx
| 0x2026 | 0x2027 | 8230 | 8231 | Pin-B | Float | R | 2 | x.xxxx
| 0x2028 | 0x2029 | 8232 | 8233 | Pin-C | Float | R | 2 | x.xxxx
| 0x202A | 0x202B | 8234 | 8235 | Qin-A | Float | R | 2 | x.xxxx
| 0x202C | 0x202D | 8236 | 8237 | Qin-B | Float | R | 2 | x.xxxx
| 0x202E | 0x202F | 8238 | 8239 | Qin-C | Float | R | 2 | x.xxxx
| 0x2030 | 0x2031 | 8240 | 8241 | Sin-A | Float | R | 2 | x.xxxx
| 0x2032 | 0x2033 | 8242 | 8243 | Sin-B | Float | R | 2 | x.xxxx
| 0x2034 | 0x2035 | 8244 | 8245 | Sin-C | Float | R | 2 | x.xxxx
| 0x2036 | 0x2037 | 8246 | 8247 | PFin-A | Float | R | 2 | x.xxx
| 0x2038 | 0x2039 | 8248 | 8249 | PFin-B | Float | R | 2 | x.xxx
| 0x203A | 0x203B | 8250 | 8251 | PFin-C | Float | R | 2 | x.xxx
| 0x203C | 0x203D | 8252 | 8253 | Load Nature A | Float | R | 2 | 1: R; 2: L; 3: C
| 0x203E | 0x203F | 8254 | 8255 | Load Nature B | Float | R | 2 | 1: R; 2: L; 3: C
| 0x2040 | 0x2041 | 8256 | 8257 | Load Nature C | Float | R | 2 | 1: R; 2: L; 3: C
Individual/User Channel | 0x2100 | 0x2101 | 8448 | 8449 | I1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
(0x03 Read) | 0x2102 | 0x2103 | 8450 | 8451 | P1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
| 0x2104 | 0x2105 | 8452 | 8453 | Q1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
| 0x2106 | 0x2107 | 8454 | 8455 | S1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
| 0x2108 | 0x2109 | 8456 | 8457 | PF1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
| 0x210A | 0x210B | 8458 | 8459 | Load Nature 1 - Individual channel 1 | Float | R | 2 | Same as in "Inline"
| 0x210C | 0x2117 | 8460 | 8471 | Individual channel 2 | Float | R | 12 | Same as in "Inline"
| 0x2118 | 0x2123 | 8472 | 8483 | Individual channel 3 | Float | R | 12 | Same as in "Inline"
| 0x2124 | 0x212F | 8484 | 8495 | Individual channel 4 | Float | R | 12 | Same as in "Inline"
| 0x2130 | 0x213B | 8496 | 8507 | Individual channel 5 | Float | R | 12 | Same as in "Inline"
| 0x213C | 0x2147 | 8508 | 8519 | Individual channel 6 | Float | R | 12 | Same as in "Inline"
| 0x2148 | 0x2153 | 8520 | 8531 | Individual channel 7 | Float | R | 12 | Same as in "Inline"
| 0x2154 | 0x215F | 8532 | 8543 | Individual channel 8 | Float | R | 12 | Same as in "Inline"
| 0x2160 | 0x216B | 8544 | 8555 | Individual channel 9 | Float | R | 12 | Same as in "Inline"
| 0x216C | 0x2177 | 8556 | 8567 | Individual channel 10 | Float | R | 12 | Same as in "Inline"
| 0x2178 | 0x2183 | 8568 | 8579 | Individual channel 11 | Float | R | 12 | Same as in "Inline"
| 0x2184 | 0x218F | 8580 | 8591 | Individual channel 12 | Float | R | 12 | Same as in "Inline"
| 0x2190 | 0x219B | 8592 | 8603 | Individual channel 13 | Float | R | 12 | Same as in "Inline"
| 0x219C | 0x21A7 | 8604 | 8615 | Individual channel 14 | Float | R | 12 | Same as in "Inline"
| 0x21A8 | 0x21B3 | 8616 | 8627 | Individual channel 15 | Float | R | 12 | Same as in "Inline"
| 0x21B4 | 0x21BF | 8628 | 8639 | Individual channel 16 | Float | R | 12 | Same as in "Inline"
| 0x21C0 | 0x21CB | 8640 | 8651 | Individual channel 17 | Float | R | 12 | Same as in "Inline"
| 0x21CC | 0x21D7 | 8652 | 8663 | Individual channel 18 | Float | R | 12 | Same as in "Inline"
| 0x21D8 | 0x21D9 | 8664 | 8665 | Ps1 - User channel 1 | Float | R | 2 | Same as in "Inline"
| 0x21DA | 0x21DB | 8666 | 8667 | Qs1 - User channel 1 | Float | R | 2 | Same as in "Inline"
| 0x21DC | 0x21DD | 8668 | 8669 | Ss1 - User channel 1 | Float | R | 2 | Same as in "Inline"
| 0x21DE | 0x21DF | 8670 | 8671 | PFs1 - User channel 1 | Float | R | 2 | Same as in "Inline"
| 0x21E0 | 0x21E1 | 8672 | 8673 | Load Nature s1 - User channel 1 | Float | R | 2 | Same as in "Inline"
| 0x21E2 | 0x21EB | 8674 | 8683 | User channel 2 | Float | R | 10 | Same as in "Inline"
| 0x21EC | 0x21F5 | 8684 | 8693 | User channel 3 | Float | R | 10 | Same as in "Inline"
| 0x21F6 | 0x21FF | 8694 | 8703 | User channel 4 | Float | R | 10 | Same as in "Inline"
| 0x2200 | 0x2209 | 8704 | 8713 | User channel 5 | Float | R | 10 | Same as in "Inline"
| 0x220A | 0x2213 | 8714 | 8723 | User channel 6 | Float | R | 10 | Same as in "Inline"
| 0x2214 | 0x221D | 8724 | 8733 | User channel 7 | Float | R | 10 | Same as in "Inline"
| 0x221E | 0x2227 | 8734 | 8743 | User channel 8 | Float | R | 10 | Same as in "Inline"
| 0x2228 | 0x2231 | 8744 | 8753 | User channel 9 | Float | R | 10 | Same as in "Inline"

## Active Energy
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Import Active Energy | 0x2500 | 0x2501 | 9472 | 9473 | Epin-A import | Dword | R/W | 2 | Max 999999999 (99999999.9)
(0x03 Read, 0x10 Write) | 0x2502 | 0x2503 | 9474 | 9475 | Epin-B import | Dword | R/W | 2 | All same as above
| 0x2504 | 0x2505 | 9476 | 9477 | Epin-C import | Dword | R/W | 2
| 0x2506 | 0x2507 | 9478 | 9479 | Epin-S import | Dword | R/W | 2
| 0x2508 | 0x2509 | 9480 | 9481 | Ep import - Individual channel 1 | Dword | R/W | 2
| 0x250A | 0x250B | 9482 | 9483 | Ep import - Individual channel 2 | Dword | R/W | 2
| 0x250C | 0x250D | 9484 | 9485 | Ep import - Individual channel 3 | Dword | R/W | 2
| 0x250E | 0x250F | 9486 | 9487 | Ep import - Individual channel 4 | Dword | R/W | 2
| 0x2510 | 0x2511 | 9488 | 9489 | Ep import - Individual channel 5 | Dword | R/W | 2
| 0x2512 | 0x2513 | 9490 | 9491 | Ep import - Individual channel 6 | Dword | R/W | 2
| 0x2514 | 0x2515 | 9492 | 9493 | Ep import - Individual channel 7 | Dword | R/W | 2
| 0x2516 | 0x2517 | 9494 | 9495 | Ep import - Individual channel 8 | Dword | R/W | 2
| 0x2518 | 0x2519 | 9496 | 9497 | Ep import - Individual channel 9 | Dword | R/W | 2
| 0x251A | 0x251B | 9498 | 9499 | Ep import - Individual channel 10 | Dword | R/W | 2
| 0x251C | 0x251D | 9500 | 9501 | Ep import - Individual channel 11 | Dword | R/W | 2
| 0x251E | 0x251F | 9502 | 9503 | Ep import - Individual channel 12 | Dword | R/W | 2
| 0x2520 | 0x2521 | 9504 | 9505 | Ep import - Individual channel 13 | Dword | R/W | 2
| 0x2522 | 0x2523 | 9506 | 9507 | Ep import - Individual channel 14 | Dword | R/W | 2
| 0x2524 | 0x2525 | 9508 | 9509 | Ep import - Individual channel 15 | Dword | R/W | 2
| 0x2526 | 0x2527 | 9510 | 9511 | Ep import - Individual channel 16 | Dword | R/W | 2
| 0x2528 | 0x2529 | 9512 | 9513 | Ep import - Individual channel 17 | Dword | R/W | 2
| 0x252A | 0x252B | 9514 | 9515 | Ep import - Individual channel 18 | Dword | R/W | 2
| 0x252C | 0x252D | 9516 | 9517 | Ep import - User channel 1 | Dword | R/W | 2
| 0x252E | 0x252F | 9518 | 9519 | Ep import - User channel 2 | Dword | R/W | 2
| 0x2530 | 0x2531 | 9520 | 9521 | Ep import - User channel 3 | Dword | R/W | 2
| 0x2532 | 0x2533 | 9522 | 9523 | Ep import - User channel 4 | Dword | R/W | 2
| 0x2534 | 0x2535 | 9524 | 9525 | Ep import - User channel 5 | Dword | R/W | 2
| 0x2536 | 0x2537 | 9526 | 9527 | Ep import - User channel 6 | Dword | R/W | 2
| 0x2538 | 0x2539 | 9528 | 9529 | Ep import - User channel 7 | Dword | R/W | 2
| 0x253A | 0x253B | 9530 | 9531 | Ep import - User channel 8 | Dword | R/W | 2
| 0x253C | 0x253D | 9532 | 9533 | Ep import - User channel 9 | Dword | R/W | 2
Previous 1~7 days Energy | 0x4C00 | 0x4C37 | 19456 | 19511 | Previous 1-day energy | Dword | R | 56
(0x03 Read) | 0x4D00 | 0x4D37 | 19712 | 19767 | Previous 2-day energy | Dword | R | 56
| 0x4E00 | 0x4E37 | 19968 | 20023 | Previous 3-day energy | Dword | R | 56
| 0x4F00 | 0x4F37 | 20224 | 20279 | Previous 4-day energy | Dword | R | 56
| 0x5000 | 0x5037 | 20480 | 20535 | Previous 5-day energy | Dword | R | 56
| 0x5100 | 0x5137 | 20736 | 20791 | Previous 6-day energy | Dword | R | 56
| 0x5200 | 0x5237 | 20992 | 21047 | Previous 7-day energy | Dword | R | 56
TOU Ep import (curren month) | 0x2600 | 0x2601 | 9728 | 9729 | Epin-S import - current month - total | Dword | R/W | 2
(0x03 Read, 0x10 Write) | 0x2602 | 0x2603 | 9730 | 9731 | Epin-S import - current month - tariff 1 | Dword | R/W | 2
| 0x2604 | 0x2605 | 9732 | 9733 | Epin-S import - current month - tariff 2 | Dword | R/W | 2
| 0x2606 | 0x2607 | 9734 | 9735 | Epin-S import - current month - tariff 3 | Dword | R/W | 2
| 0x2608 | 0x2609 | 9736 | 9737 | Epin-S import - current month - tariff 4 | Dword | R/W | 2
| 0x260A | 0x260B | 9738 | 9739 | Epin-A import - current month - total | Dword | R/W | 2
| 0x260C | 0x260D | 9740 | 9741 | Epin-A import - current month - tariff 1 | Dword | R/W | 2
| 0x260E | 0x260F | 9742 | 9743 | Epin-A import - current month - tariff 2 | Dword | R/W | 2
| 0x2610 | 0x2611 | 9744 | 9745 | Epin-A import - current month - tariff 3 | Dword | R/W | 2
| 0x2612 | 0x2613 | 9746 | 9747 | Epin-A import - current month - tariff 4 | Dword | R/W | 2
| 0x2614 | 0x2615 | 9748 | 9749 | Epin-B import - current month - total | Dword | R/W | 2
| 0x2616 | 0x2617 | 9750 | 9751 | Epin-B import - current month - tariff 1 | Dword | R/W | 2
| 0x2618 | 0x2619 | 9752 | 9753 | Epin-B import - current month - tariff 2 | Dword | R/W | 2
| 0x261A | 0x261B | 9754 | 9755 | Epin-B import - current month - tariff 3 | Dword | R/W | 2
| 0x261C | 0x261D | 9756 | 9757 | Epin-B import - current month - tariff 4 | Dword | R/W | 2
| 0x261E | 0x261F | 9758 | 9759 | Epin-C import - current month - total | Dword | R/W | 2
| 0x2620 | 0x2621 | 9760 | 9761 | Epin-C import - current month - tariff 1 | Dword | R/W | 2
| 0x2622 | 0x2623 | 9762 | 9763 | Epin-C import - current month - tariff 2 | Dword | R/W | 2
| 0x2624 | 0x2625 | 9764 | 9765 | Epin-C import - current month - tariff 3 | Dword | R/W | 2
| 0x2626 | 0x2627 | 9766 | 9767 | Epin-C import - current month - tariff 4 | Dword | R/W | 2
| 0x2628 | 0x2629 | 9768 | 9769 | Ep1 import - current month - total | Dword | R/W | 2
| 0x262A | 0x262B | 9770 | 9771 | Ep1 import - current month - tariff 1 | Dword | R/W | 2
| 0x262C | 0x262D | 9772 | 9773 | Ep1 import - current month - tariff 2 | Dword | R/W | 2
| 0x262E | 0x262F | 9774 | 9775 | Ep1 import - current month - tariff 3 | Dword | R/W | 2
| 0x2630 | 0x2631 | 9776 | 9777 | Ep1 import - current month - tariff 4 | Dword | R/W | 2
| 0x2632 | 0x263B | 9778 | 9787 | Ep2 import - current month (same as Ep1) | Dword | R/W | 10
| 0x263C | 0x2645 | 9788 | 9797 | Ep3 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2646 | 0x264F | 9798 | 9807 | Ep4 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2650 | 0x2659 | 9808 | 9817 | Ep5 import - current month (same as Ep1) | Dword | R/W | 10
| 0x265A | 0x2663 | 9818 | 9827 | Ep6 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2664 | 0x266D | 9828 | 9837 | Ep7 import - current month (same as Ep1) | Dword | R/W | 10
| 0x266E | 0x2677 | 9838 | 9847 | Ep8 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2678 | 0x2681 | 9848 | 9857 | Ep9 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2682 | 0x268B | 9858 | 9867 | Ep10 import - current month (same as Ep1) | Dword | R/W | 10
| 0x268C | 0x2695 | 9868 | 9877 | Ep11 import - current month (same as Ep1) | Dword | R/W | 10
| 0x2696 | 0x269F | 9878 | 9887 | Ep12 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26A0 | 0x26A9 | 9888 | 9897 | Ep13 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26AA | 0x26B3 | 9898 | 9907 | Ep14 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26B4 | 0x26BD | 9908 | 9917 | Ep15 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26BE | 0x26C7 | 9918 | 9927 | Ep16 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26C8 | 0x26D1 | 9928 | 9937 | Ep17 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26D2 | 0x26DB | 9938 | 9947 | Ep18 import - current month (same as Ep1) | Dword | R/W | 10
| 0x26DC | 0x26DD | 9948 | 9949 | Eps1 import - current month - total | Dword | R/W | 2
| 0x26DE | 0x26DF | 9950 | 9951 | Eps1 import - current month - tariff 1 | Dword | R/W | 2
| 0x26E0 | 0x26E1 | 9952 | 9953 | Eps1 import - current month - tariff 2 | Dword | R/W | 2
| 0x26E2 | 0x26E3 | 9954 | 9955 | Eps1 import - current month - tariff 3 | Dword | R/W | 2
| 0x26E4 | 0x26E5 | 9956 | 9957 | Eps1 import - current month - tariff 4 | Dword | R/W | 2
| 0x26E6 | 0x26EF | 9958 | 9967 | Eps2 import - current month (same as Eps1) | Dword | R/W | 10
| 0x26F0 | 0x26F9 | 9968 | 9977 | Eps3 import - current month (same as Eps1) | Dword | R/W | 10
| 0x26FA | 0x2703 | 9978 | 9987 | Eps4 import - current month (same as Eps1) | Dword | R/W | 10
| 0x2704 | 0x270D | 9988 | 9997 | Eps5 import - current month (same as Eps1) | Dword | R/W | 10
| 0x270E | 0x2717 | 9998 | 10007 | Eps6 import - current month (same as Eps1) | Dword | R/W | 10
TOU Ep import (previous month) | 0x2900 | 0x2901 | 10496 | 10497 | Epin-S import - previous month - total | Dword | R/W | 2
(0x03 Read, 0x10 Write) | 0x2902 | 0x2903 | 10498 | 10499 | Epin-S import - previous month - tariff 1 | Dword | R/W | 2
| 0x2904 | 0x2905 | 10500 | 10501 | Epin-S import - previous month - tariff 2 | Dword | R/W | 2
| 0x2906 | 0x2907 | 10502 | 10503 | Epin-S import - previous month - tariff 3 | Dword | R/W | 2
| 0x2908 | 0x2909 | 10504 | 10505 | Epin-S import - previous month - tariff 4 | Dword | R/W | 2
| 0x290A | 0x290B | 10506 | 10507 | Epin-A import - previous month - total | Dword | R/W | 2
| 0x290C | 0x290D | 10508 | 10509 | Epin-A import - previous month - tariff 1 | Dword | R/W | 2
| 0x290E | 0x290F | 10510 | 10511 | Epin-A import - previous month - tariff 2 | Dword | R/W | 2
| 0x2910 | 0x2911 | 10512 | 10513 | Epin-A import - previous month - tariff 3 | Dword | R/W | 2
| 0x2912 | 0x2913 | 10514 | 10515 | Epin-A import - previous month - tariff 4 | Dword | R/W | 2
| 0x2914 | 0x2915 | 10516 | 10517 | Epin-B import - previous month - total | Dword | R/W | 2
| 0x2916 | 0x2917 | 10518 | 10519 | Epin-B import - previous month - tariff 1 | Dword | R/W | 2
| 0x2918 | 0x2919 | 10520 | 10521 | Epin-B import - previous month - tariff 2 | Dword | R/W | 2
| 0x291A | 0x291B | 10522 | 10523 | Epin-B import - previous month - tariff 3 | Dword | R/W | 2
| 0x291C | 0x291D | 10524 | 10525 | Epin-B import - previous month - tariff 4 | Dword | R/W | 2
| 0x291E | 0x291F | 10526 | 10527 | Epin-C import - previous month - total | Dword | R/W | 2
| 0x2920 | 0x2921 | 10528 | 10529 | Epin-C import - previous month - tariff 1 | Dword | R/W | 2
| 0x2922 | 0x2923 | 10530 | 10531 | Epin-C import - previous month - tariff 2 | Dword | R/W | 2
| 0x2924 | 0x2925 | 10532 | 10533 | Epin-C import - previous month - tariff 3 | Dword | R/W | 2
| 0x2926 | 0x2927 | 10534 | 10535 | Epin-C import - previous month - tariff 4 | Dword | R/W | 2
| 0x2928 | 0x2929 | 10536 | 10537 | Ep1 import - previous month - total | Dword | R/W | 2
| 0x292A | 0x292B | 10538 | 10539 | Ep1 import - previous month - tariff 1 | Dword | R/W | 2
| 0x292C | 0x292D | 10540 | 10541 | Ep1 import - previous month - tariff 2 | Dword | R/W | 2
| 0x292E | 0x292F | 10542 | 10543 | Ep1 import - previous month - tariff 3 | Dword | R/W | 2
| 0x2930 | 0x2931 | 10544 | 10545 | Ep1 import - previous month - tariff 4 | Dword | R/W | 2
| 0x2932 | 0x293B | 10546 | 10555 | Ep2 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x293C | 0x2945 | 10556 | 10565 | Ep3 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2946 | 0x294F | 10566 | 10575 | Ep4 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2950 | 0x2959 | 10576 | 10585 | Ep5 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x295A | 0x2963 | 10586 | 10595 | Ep6 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2964 | 0x296D | 10596 | 10605 | Ep7 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x296E | 0x2977 | 10606 | 10615 | Ep8 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2978 | 0x2981 | 10616 | 10625 | Ep9 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2982 | 0x298B | 10626 | 10635 | Ep10 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x298C | 0x2995 | 10636 | 10645 | Ep11 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x2996 | 0x299F | 10646 | 10655 | Ep12 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29A0 | 0x29A9 | 10656 | 10665 | Ep13 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29AA | 0x29B3 | 10666 | 10675 | Ep14 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29B4 | 0x29BD | 10676 | 10685 | Ep15 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29BE | 0x29C7 | 10686 | 10695 | Ep16 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29C8 | 0x29D1 | 10696 | 10705 | Ep17 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29D2 | 0x29DB | 10706 | 10715 | Ep18 import - previous month (same as Ep1) | Dword | R/W | 10
| 0x29DC | 0x29DD | 10716 | 10717 | Eps1 import - previous month - total | Dword | R/W | 2
| 0x29DE | 0x29DF | 10718 | 10719 | Eps1 import - previous month - tariff 1 | Dword | R/W | 2
| 0x29E0 | 0x29E1 | 10720 | 10721 | Eps1 import - previous month - tariff 2 | Dword | R/W | 2
| 0x29E2 | 0x29E3 | 10722 | 10723 | Eps1 import - previous month - tariff 3 | Dword | R/W | 2
| 0x29E4 | 0x29E5 | 10724 | 10725 | Eps1 import - previous month - tariff 4 | Dword | R/W | 2
| 0x29E6 | 0x29EF | 10726 | 10735 | Eps2 import - previous month (same as Eps1) | Dword | R/W | 10
| 0x29F0 | 0x29F9 | 10736 | 10745 | Eps3 import - previous month (same as Eps1) | Dword | R/W | 10
| 0x29FA | 0x2A03 | 10746 | 10755 | Eps4 import - previous month (same as Eps1) | Dword | R/W | 10
| 0x2A04 | 0x2A0D | 10756 | 10765 | Eps5 import - previous month (same as Eps1) | Dword | R/W | 10
| 0x2A0E | 0x2A17 | 10766 | 10775 | Eps6 import - previous month (same as Eps1) | Dword | R/W | 10

## Reactive & Apparent Energy
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Import Reactive Energy | 0x2B00 | 0x2B01 | 11008 | 11009 | Eqin-A import | Dword | R/W | 2
(0x03 Read, 0x10 Write) | 0x2B02 | 0x2B03 | 11010 | 11011 | Eqin-B import | Dword | R/W | 2
| 0x2B04 | 0x2B05 | 11012 | 11013 | Eqin-C import | Dword | R/W | 2
| 0x2B06 | 0x2B07 | 11014 | 11015 | Eqin-S import | Dword | R/W | 2
| 0x2B08 | 0x2B09 | 11016 | 11017 | Eq import - Individual channel 1 | Dword | R/W | 2
| 0x2B0A | 0x2B0B | 11018 | 11019 | Eq import - Individual channel 2 | Dword | R/W | 2
| 0x2B0C | 0x2B0D | 11020 | 11021 | Eq import - Individual channel 3 | Dword | R/W | 2
| 0x2B0E | 0x2B0F | 11022 | 11023 | Eq import - Individual channel 4 | Dword | R/W | 2
| 0x2B10 | 0x2B11 | 11024 | 11025 | Eq import - Individual channel 5 | Dword | R/W | 2
| 0x2B12 | 0x2B13 | 11026 | 11027 | Eq import - Individual channel 6 | Dword | R/W | 2
| 0x2B14 | 0x2B15 | 11028 | 11029 | Eq import - Individual channel 7 | Dword | R/W | 2
| 0x2B16 | 0x2B17 | 11030 | 11031 | Eq import - Individual channel 8 | Dword | R/W | 2
| 0x2B18 | 0x2B19 | 11032 | 11033 | Eq import - Individual channel 9 | Dword | R/W | 2
| 0x2B1A | 0x2B1B | 11034 | 11035 | Eq import - Individual channel 10 | Dword | R/W | 2
| 0x2B1C | 0x2B1D | 11036 | 11037 | Eq import - Individual channel 11 | Dword | R/W | 2
| 0x2B1E | 0x2B1F | 11038 | 11039 | Eq import - Individual channel 12 | Dword | R/W | 2
| 0x2B20 | 0x2B21 | 11040 | 11041 | Eq import - Individual channel 13 | Dword | R/W | 2
| 0x2B22 | 0x2B23 | 11042 | 11043 | Eq import - Individual channel 14 | Dword | R/W | 2
| 0x2B24 | 0x2B25 | 11044 | 11045 | Eq import - Individual channel 15 | Dword | R/W | 2
| 0x2B26 | 0x2B27 | 11046 | 11047 | Eq import - Individual channel 16 | Dword | R/W | 2
| 0x2B28 | 0x2B29 | 11048 | 11049 | Eq import - Individual channel 17 | Dword | R/W | 2
| 0x2B2A | 0x2B2B | 11050 | 11051 | Eq import - Individual channel 18 | Dword | R/W | 2
| 0x2B2C | 0x2B2D | 11052 | 11053 | Eq import - User channel 1 | Dword | R/W | 2
| 0x2B2E | 0x2B2F | 11054 | 11055 | Eq import - User channel 2 | Dword | R/W | 2
| 0x2B30 | 0x2B31 | 11056 | 11057 | Eq import - User channel 3 | Dword | R/W | 2
| 0x2B32 | 0x2B33 | 11058 | 11059 | Eq import - User channel 4 | Dword | R/W | 2
| 0x2B34 | 0x2B35 | 11060 | 11061 | Eq import - User channel 5 | Dword | R/W | 2
| 0x2B36 | 0x2B37 | 11062 | 11063 | Eq import - User channel 6 | Dword | R/W | 2
| 0x2B70 | 0x2B71 | 11120 | 11121 | Eq import - User channel 7 | Dword | R/W | 2
| 0x2B72 | 0x2B73 | 11122 | 11123 | Eq import - User channel 8 | Dword | R/W | 2
| 0x2B74 | 0x2B75 | 11124 | 11125 | Eq import - User channel 9 | Dword | R/W | 2
Reactive Energy - Combined Reactive 2 | 0x4B00 | 0x4B01 | 19200 | 19201 | Eqin-A import | Dword | R/W | 2
(0x03 Read, 0x10 Write) | 0x4B02 | 0x4B03 | 19202 | 19203 | Eqin-B import | Dword | R/W | 2
| 0x4B04 | 0x4B05 | 19204 | 19205 | Eqin-C import | Dword | R/W | 2
| 0x4B06 | 0x4B07 | 19206 | 19207 | Eqin-S import | Dword | R/W | 2
| 0x4B08 | 0x4B2B | 19208 | 19243 | Eq import - Individual channel 1~18 | Dword | R/W | 36
| 0x4B2C | 0x4B2D | 19244 | 19245 | Eq import - User channel 1 | Dword | R/W | 2
| 0x4B2E | 0x4B37 | 19246 | 19255 | Eq import - User channel 2~6 | Dword | R/W | 10
Import Apparent Energy | 0x2B38 | 0x2B39 | 11064 | 11065 | Esin-A import | Dword | R/W | 2
(0x03 Read, 0x10 Write) | 0x2B3A | 0x2B3B | 11066 | 11067 | Esin-B import | Dword | R/W | 2
| 0x2B3C | 0x2B3D | 11068 | 11069 | Esin-C import | Dword | R/W | 2
| 0x2B3E | 0x2B3F | 11070 | 11071 | Esin-S import | Dword | R/W | 2
| 0x2B40 | 0x2B41 | 11072 | 11073 | Es import - Individual channel 1 | Dword | R/W | 2
| 0x2B42 | 0x2B43 | 11074 | 11075 | Es import - Individual channel 2 | Dword | R/W | 2
| 0x2B44 | 0x2B45 | 11076 | 11077 | Es import - Individual channel 3 | Dword | R/W | 2
| 0x2B46 | 0x2B47 | 11078 | 11079 | Es import - Individual channel 4 | Dword | R/W | 2
| 0x2B48 | 0x2B49 | 11080 | 11081 | Es import - Individual channel 5 | Dword | R/W | 2
| 0x2B4A | 0x2B4B | 11082 | 11083 | Es import - Individual channel 6 | Dword | R/W | 2
| 0x2B4C | 0x2B4D | 11084 | 11085 | Es import - Individual channel 7 | Dword | R/W | 2
| 0x2B4E | 0x2B4F | 11086 | 11087 | Es import - Individual channel 8 | Dword | R/W | 2
| 0x2B50 | 0x2B51 | 11088 | 11089 | Es import - Individual channel 9 | Dword | R/W | 2
| 0x2B52 | 0x2B53 | 11090 | 11091 | Es import - Individual channel 10 | Dword | R/W | 2
| 0x2B54 | 0x2B55 | 11092 | 11093 | Es import - Individual channel 11 | Dword | R/W | 2
| 0x2B56 | 0x2B57 | 11094 | 11095 | Es import - Individual channel 12 | Dword | R/W | 2
| 0x2B58 | 0x2B59 | 11096 | 11097 | Es import - Individual channel 13 | Dword | R/W | 2
| 0x2B5A | 0x2B5B | 11098 | 11099 | Es import - Individual channel 14 | Dword | R/W | 2
| 0x2B5C | 0x2B5D | 11100 | 11101 | Es import - Individual channel 15 | Dword | R/W | 2
| 0x2B5E | 0x2B5F | 11102 | 11103 | Es import - Individual channel 16 | Dword | R/W | 2
| 0x2B60 | 0x2B61 | 11104 | 11105 | Es import - Individual channel 17 | Dword | R/W | 2
| 0x2B62 | 0x2B63 | 11106 | 11107 | Es import - Individual channel 18 | Dword | R/W | 2
| 0x2B64 | 0x2B65 | 11108 | 11109 | Es import - User channel 1 | Dword | R/W | 2
| 0x2B66 | 0x2B67 | 11110 | 11111 | Es import - User channel 2 | Dword | R/W | 2
| 0x2B68 | 0x2B69 | 11112 | 11113 | Es import - User channel 3 | Dword | R/W | 2
| 0x2B6A | 0x2B6B | 11114 | 11115 | Es import - User channel 4 | Dword | R/W | 2
| 0x2B6C | 0x2B6D | 11116 | 11117 | Es import - User channel 5 | Dword | R/W | 2
| 0x2B6E | 0x2B6F | 11118 | 11119 | Es import - User channel 6 | Dword | R/W | 2
| 0x2B76 | 0x2B77 | 11126 | 11127 | Es import - User channel 7 | Dword | R/W | 2
| 0x2B78 | 0x2B79 | 11128 | 11129 | Es import - User channel 8 | Dword | R/W | 2
| 0x2B7A | 0x2B7B | 11130 | 11131 | Es import - User channel 9 | Dword | R/W | 2

## Demand
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Demand | 0x2D00 | 0x2D01 | 11520 | 11521 | Pin-s-demand | Float | R | 2
(0x03 Read) | 0x2D02 | 0x2D03 | 11522 | 11523 | Pin-s-demand Prediction | Float | R | 2
| 0x2D04 | 0x2D05 | 11524 | 11525 | Pin-s-demand-max | Float | R | 2
| 0x2D06 | 0x2D08 | 11526 | 11528 | Pin-s-demand-max Time | Word | R | 3
| 0x2D09 | 0x2D0A | 11529 | 11530 | Qin-s-demand | Float | R | 2
| 0x2D0B | 0x2D0C | 11531 | 11532 | Qin-s-demand Prediction | Float | R | 2
| 0x2D0D | 0x2D0E | 11533 | 11534 | Qin-s-demand-max | Float | R | 2
| 0x2D0F | 0x2D11 | 11535 | 11537 | Qin-s-demand-max Time | Word | R | 3
| 0x2D12 | 0x2D13 | 11538 | 11539 | Sin-s-demand | Float | R | 2
| 0x2D14 | 0x2D15 | 11540 | 11541 | Sin-s-demand Prediction | Float | R | 2
| 0x2D16 | 0x2D17 | 11542 | 11543 | Sin-s-demand-max | Float | R | 2
| 0x2D18 | 0x2D1A | 11544 | 11546 | Sin-s-demand-max Time | Word | R | 3
| 0x2D1B | 0x2D1C | 11547 | 11548 | Ia-demand | Float | R | 2
| 0x2D1D | 0x2D1E | 11549 | 11550 | Ia-demand Prediction | Float | R | 2
| 0x2D1F | 0x2D20 | 11551 | 11552 | Ia-demand-max | Float | R | 2
| 0x2D21 | 0x2D23 | 11553 | 11555 | Ia-demand-max Time | Word | R | 3
| 0x2D24 | 0x2D25 | 11556 | 11557 | Pin-A-demand | Float | R | 2
| 0x2D26 | 0x2D27 | 11558 | 11559 | Pin-A-demand Prediction | Float | R | 2
| 0x2D28 | 0x2D29 | 11560 | 11561 | Pin-A-demand-max | Float | R | 2
| 0x2D2A | 0x2D2C | 11562 | 11564 | Pin-A-demand-max Time | Word | R | 3
| 0x2D2D | 0x2D2E | 11565 | 11566 | Qin-A-demand | Float | R | 2
| 0x2D2F | 0x2D30 | 11567 | 11568 | Qin-A-demand Prediction | Float | R | 2
| 0x2D31 | 0x2D32 | 11569 | 11570 | Qin-A-demand-max | Float | R | 2
| 0x2D33 | 0x2D35 | 11571 | 11573 | Qin-A-demand-max Time | Word | R | 3
| 0x2D36 | 0x2D37 | 11574 | 11575 | Sin-A-demand | Float | R | 2
| 0x2D38 | 0x2D39 | 11576 | 11577 | Sin-A-demand Prediction | Float | R | 2
| 0x2D3A | 0x2D3B | 11578 | 11579 | Sin-A-demand-max | Float | R | 2
| 0x2D3C | 0x2D3E | 11580 | 11582 | Sin-A-demand-max Time | Word | R | 3
| 0x2D3F | 0x2D62 | 11583 | 11618 | Inline B demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2D63 | 0x2D86 | 11619 | 11654 | Inline C demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2D87 | 0x2DAA | 11655 | 11690 | Individual channel 1 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2DAB | 0x2DCE | 11691 | 11726 | Individual channel 2 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2DCF | 0x2DF2 | 11727 | 11762 | Individual channel 3 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2DF3 | 0x2E16 | 11763 | 11798 | Individual channel 4 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2E17 | 0x2E3A | 11799 | 11834 | Individual channel 5 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2E3B | 0x2E5E | 11835 | 11870 | Individual channel 6 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2E5F | 0x2E82 | 11871 | 11906 | Individual channel 7 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2E83 | 0x2EA6 | 11907 | 11942 | Individual channel 8 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2EA7 | 0x2ECA | 11943 | 11978 | Individual channel 9 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2ECB | 0x2EEE | 11979 | 12014 | Individual channel 10 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2EEF | 0x2F12 | 12015 | 12050 | Individual channel 11 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2F13 | 0x2F36 | 12051 | 12086 | Individual channel 12 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2F37 | 0x2F5A | 12087 | 12122 | Individual channel 13 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2F5B | 0x2F7E | 12123 | 12158 | Individual channel 14 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2F7F | 0x2FA2 | 12159 | 12194 | Individual channel 15 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2FA3 | 0x2FC6 | 12195 | 12230 | Individual channel 16 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2FC7 | 0x2FEA | 12231 | 12266 | Individual channel 17 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x2FEB | 0x300E | 12267 | 12302 | Individual channel 18 demand | Float + Word | R | 36 | Same as "Inline A"
| 0x300F | 0x3010 | 12303 | 12304 | User channel 1 Pin-A-demand | Float | R | 2
| 0x3011 | 0x3012 | 12305 | 12306 | User channel 1 Pin-A-demand Prediction | Float | R | 2
| 0x3013 | 0x3014 | 12307 | 12308 | User channel 1 Pin-A-demand-max | Float | R | 2
| 0x3015 | 0x3017 | 12309 | 12311 | User channel 1 Pin-A-demand-max Time | Word | R | 3
| 0x3018 | 0x3019 | 12312 | 12313 | User channel 1 Qin-A-demand | Float | R | 2
| 0x301A | 0x301B | 12314 | 12315 | User channel 1 Qin-A-demand Prediction | Float | R | 2
| 0x301C | 0x301D | 12316 | 12317 | User channel 1 Qin-A-demand-max | Float | R | 2
| 0x301E | 0x3020 | 12318 | 12320 | User channel 1 Qin-A-demand-max Time | Word | R | 3
| 0x3021 | 0x3022 | 12321 | 12322 | User channel 1 Sin-A-demand | Float | R | 2
| 0x3023 | 0x3024 | 12323 | 12324 | User channel 1 Sin-A-demand Prediction | Float | R | 2
| 0x3025 | 0x3026 | 12325 | 12326 | User channel 1 Sin-A-demand-max | Float | R | 2
| 0x3027 | 0x3029 | 12327 | 12329 | User channel 1 Sin-A-demand-max Time | Word | R | 3
| 0x302A | 0x3044 | 12330 | 12356 | User channel 2 demand | Float + Word | R | 27 | Same as "User channel 1"
| 0x3045 | 0x305F | 12357 | 12383 | User channel 3 demand | Float + Word | R | 27
| 0x3060 | 0x307A | 12384 | 12410 | User channel 4 demand | Float + Word | R | 27
| 0x307B | 0x3095 | 12411 | 12437 | User channel 5 demand | Float + Word | R | 27
| 0x3096 | 0x30B0 | 12438 | 12464 | User channel 6 demand | Float + Word | R | 27
| 0x30B1 | 0x30CB | 12465 | 12491 | User channel 7 demand | Float + Word | R | 27
| 0x30CC | 0x30E6 | 12492 | 12518 | User channel 8 demand | Float + Word | R | 27
| 0x30E7 | 0x3101 | 12519 | 12545 | User channel 9 demand | Float + Word | R | 27

## Power Quality
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Power Quality | 0x3200 | 0x3200 | 12800 | 12800 | Unbalance U | Word | R | 1
(0x03 Read) | 0x3201 | 0x3201 | 12801 | 12801 | THD-U1 or U12 | Word | R | 1
| 0x3202 | 0x3202 | 12802 | 12802 | THD-U2 or U23 | Word | R | 1
| 0x3203 | 0x3203 | 12803 | 12803 | THD-U3 or U31 | Word | R | 1
| 0x3204 | 0x3204 | 12804 | 12804 | THD-Uavg | Word | R | 1
| 0x3205 | 0x3205 | 12805 | 12805 | 2nd harmonics U1 or U12 | Word | R | 1
| 0x3206 | 0x3222 | 12806 | 12834 | 3rd~31st harmonics U1 or U12 | Word | R | 29
| 0x3223 | 0x3223 | 12835 | 12835 | 2nd harmonics U2 or U23 | Word | R | 1
| 0x3224 | 0x3240 | 12836 | 12864 | 3rd~31st harmonics U2 or U23 | Word | R | 29
| 0x3241 | 0x3241 | 12865 | 12865 | 2nd harmonics U3 or U31 | Word | R | 1
| 0x3242 | 0x325E | 12866 | 12894 | 3rd~31st harmonics U3 or U31 | Word | R | 29
| 0x325F | 0x325F | 12895 | 12895 | Unbalance I | Word | R | 1
| 0x3260 | 0x3260 | 12896 | 12896 | Odd THD U1 | Word | R | 1
| 0x3261 | 0x3261 | 12897 | 12897 | Even THD U1 | Word | R | 1
| 0x3262 | 0x3262 | 12898 | 12898 | Crest Factor U1 | Word | R | 1
| 0x3263 | 0x3263 | 12899 | 12899 | THF U1 | Word | R | 1
| 0x3264 | 0x3264 | 12900 | 12900 | Odd THD U2 | Word | R | 1
| 0x3265 | 0x3265 | 12901 | 12901 | Even THD U2 | Word | R | 1
| 0x3266 | 0x3266 | 12902 | 12902 | Crest Factor U2 | Word | R | 1
| 0x3267 | 0x3267 | 12903 | 12903 | THF U2 | Word | R | 1
| 0x3268 | 0x3268 | 12904 | 12904 | Odd THD U3 | Word | R | 1
| 0x3269 | 0x3269 | 12905 | 12905 | Even THD U3 | Word | R | 1
| 0x326A | 0x326A | 12906 | 12906 | Crest Factor U3 | Word | R | 1
| 0x326B | 0x326B | 12907 | 12907 | THF U3 | Word | R | 1
| 0x32A0 | 0x32A0 | 12960 | 12960 | Odd THD I1 | Word | R | 1
| 0x32A1 | 0x32A1 | 12961 | 12961 | Even THD I1 | Word | R | 1
| 0x32A2 | 0x32A2 | 12962 | 12962 | K Factor I1 | Word | R | 1
| 0x32A3 | 0x32A3 | 12963 | 12963 | Odd THD I2 | Word | R | 1
| 0x32A4 | 0x32A4 | 12964 | 12964 | Even THD I2 | Word | R | 1
| 0x32A5 | 0x32A5 | 12965 | 12965 | K Factor I2 | Word | R | 1
| 0x32A6 | 0x32A6 | 12966 | 12966 | Odd THD I3 | Word | R | 1
| 0x32A7 | 0x32A7 | 12967 | 12967 | Even THD I3 | Word | R | 1
| 0x32A8 | 0x32A8 | 12968 | 12968 | K Factor I3 | Word | R | 1
| 0x32A9 | 0x32A9 | 12969 | 12969 | Odd THD I4 | Word | R | 1
| 0x32AA | 0x32AA | 12970 | 12970 | Even THD I4 | Word | R | 1
| 0x32AB | 0x32AB | 12971 | 12971 | K Factor I4 | Word | R | 1
| 0x32AC | 0x32AC | 12972 | 12972 | Odd THD I5 | Word | R | 1
| 0x32AD | 0x32AD | 12973 | 12973 | Even THD I5 | Word | R | 1
| 0x32AE | 0x32AE | 12974 | 12974 | K Factor I5 | Word | R | 1
| 0x32AF | 0x32AF | 12975 | 12975 | Odd THD I6 | Word | R | 1
| 0x32B0 | 0x32B0 | 12976 | 12976 | Even THD I6 | Word | R | 1
| 0x32B1 | 0x32B1 | 12977 | 12977 | K Factor I6 | Word | R | 1
| 0x32B2 | 0x32B2 | 12978 | 12978 | Odd THD I7 | Word | R | 1
| 0x32B3 | 0x32B3 | 12979 | 12979 | Even THD I7 | Word | R | 1
| 0x32B4 | 0x32B4 | 12980 | 12980 | K Factor I7 | Word | R | 1
| 0x32B5 | 0x32B5 | 12981 | 12981 | Odd THD I8 | Word | R | 1
| 0x32B6 | 0x32B6 | 12982 | 12982 | Even THD I8 | Word | R | 1
| 0x32B7 | 0x32B7 | 12983 | 12983 | K Factor I8 | Word | R | 1
| 0x32B8 | 0x32B8 | 12984 | 12984 | Odd THD I9 | Word | R | 1
| 0x32B9 | 0x32B9 | 12985 | 12985 | Even THD I9 | Word | R | 1
| 0x32BA | 0x32BA | 12986 | 12986 | K Factor I9 | Word | R | 1
| 0x32BB | 0x32BB | 12987 | 12987 | Odd THD I10 | Word | R | 1
| 0x32BC | 0x32BC | 12988 | 12988 | Even THD I10 | Word | R | 1
| 0x32BD | 0x32BD | 12989 | 12989 | K Factor I10 | Word | R | 1
| 0x32BE | 0x32BE | 12990 | 12990 | Odd THD I11 | Word | R | 1
| 0x32BF | 0x32BF | 12991 | 12991 | Even THD I11 | Word | R | 1
| 0x32C0 | 0x32C0 | 12992 | 12992 | K Factor I11 | Word | R | 1
| 0x32C1 | 0x32C1 | 12993 | 12993 | Odd THD I12 | Word | R | 1
| 0x32C2 | 0x32C2 | 12994 | 12994 | Even THD I12 | Word | R | 1
| 0x32C3 | 0x32C3 | 12995 | 12995 | K Factor I12 | Word | R | 1
| 0x32C4 | 0x32C4 | 12996 | 12996 | Odd THD I13 | Word | R | 1
| 0x32C5 | 0x32C5 | 12997 | 12997 | Even THD I13 | Word | R | 1
| 0x32C6 | 0x32C6 | 12998 | 12998 | K Factor I13 | Word | R | 1
| 0x32C7 | 0x32C7 | 12999 | 12999 | Odd THD I14 | Word | R | 1
| 0x32C8 | 0x32C8 | 13000 | 13000 | Even THD I14 | Word | R | 1
| 0x32C9 | 0x32C9 | 13001 | 13001 | K Factor I14 | Word | R | 1
| 0x32CA | 0x32CA | 13002 | 13002 | Odd THD I15 | Word | R | 1
| 0x32CB | 0x32CB | 13003 | 13003 | Even THD I15 | Word | R | 1
| 0x32CC | 0x32CC | 13004 | 13004 | K Factor I15 | Word | R | 1
| 0x32CD | 0x32CD | 13005 | 13005 | Odd THD I16 | Word | R | 1
| 0x32CE | 0x32CE | 13006 | 13006 | Even THD I16 | Word | R | 1
| 0x32CF | 0x32CF | 13007 | 13007 | K Factor I16 | Word | R | 1
| 0x32D0 | 0x32D0 | 13008 | 13008 | Odd THD I17 | Word | R | 1
| 0x32D1 | 0x32D1 | 13009 | 13009 | Even THD I17 | Word | R | 1
| 0x32D2 | 0x32D2 | 13010 | 13010 | K Factor I17 | Word | R | 1
| 0x32D3 | 0x32D3 | 13011 | 13011 | Odd THD I18 | Word | R | 1
| 0x32D4 | 0x32D4 | 13012 | 13012 | Even THD I18 | Word | R | 1
| 0x32D5 | 0x32D5 | 13013 | 13013 | K Factor I18 | Word | R | 1
| 0x3300 | 0x3300 | 13056 | 13056 | THD I1 | Word | R | 1
| 0x3301 | 0x331E | 13057 | 13086 | 2nd~31st harmonics I1 | Word | R | 30
| 0x331F | 0x331F | 13087 | 13087 | THD I2 | Word | R | 1
| 0x3320 | 0x333D | 13088 | 13117 | 2nd~31st harmonics I2 | Word | R | 30
| 0x333E | 0x333E | 13118 | 13118 | THD I3 | Word | R | 1
| 0x333F | 0x335C | 13119 | 13148 | 2nd~31st harmonics I3 | Word | R | 30
| 0x335D | 0x335D | 13149 | 13149 | THD I4 | Word | R | 1
| 0x335E | 0x337B | 13150 | 13179 | 2nd~31st harmonics I4 | Word | R | 30
| 0x337C | 0x337C | 13180 | 13180 | THD I5 | Word | R | 1
| 0x337D | 0x339A | 13181 | 13210 | 2nd~31st harmonics I5 | Word | R | 30
| 0x339B | 0x339B | 13211 | 13211 | THD I6 | Word | R | 1
| 0x339C | 0x33B9 | 13212 | 13241 | 2nd~31st harmonics I6 | Word | R | 30
| 0x33BA | 0x33BA | 13242 | 13242 | THD I7 | Word | R | 1
| 0x33BB | 0x33D8 | 13243 | 13272 | 2nd~31st harmonics I7 | Word | R | 30
| 0x33D9 | 0x33D9 | 13273 | 13273 | THD I8 | Word | R | 1
| 0x33DA | 0x33F7 | 13274 | 13303 | 2nd~31st harmonics I8 | Word | R | 30
| 0x33F8 | 0x33F8 | 13304 | 13304 | THD I9 | Word | R | 1
| 0x33F9 | 0x3416 | 13305 | 13334 | 2nd~31st harmonics I9 | Word | R | 30
| 0x3417 | 0x3417 | 13335 | 13335 | THD I10 | Word | R | 1
| 0x3418 | 0x3435 | 13336 | 13365 | 2nd~31st harmonics I10 | Word | R | 30
| 0x3436 | 0x3436 | 13366 | 13366 | THD I11 | Word | R | 1
| 0x3437 | 0x3454 | 13367 | 13396 | 2nd~31st harmonics I11 | Word | R | 30
| 0x3455 | 0x3455 | 13397 | 13397 | THD I12 | Word | R | 1
| 0x3456 | 0x3473 | 13398 | 13427 | 2nd~31st harmonics I12 | Word | R | 30
| 0x3474 | 0x3474 | 13428 | 13428 | THD I13 | Word | R | 1
| 0x3475 | 0x3492 | 13429 | 13458 | 2nd~31st harmonics I13 | Word | R | 30
| 0x3493 | 0x3493 | 13459 | 13459 | THD I14 | Word | R | 1
| 0x3494 | 0x34B1 | 13460 | 13489 | 2nd~31st harmonics I14 | Word | R | 30
| 0x34B2 | 0x34B2 | 13490 | 13490 | THD I15 | Word | R | 1
| 0x34B3 | 0x34D0 | 13491 | 13520 | 2nd~31st harmonics I15 | Word | R | 30
| 0x34D1 | 0x34D1 | 13521 | 13521 | THD I16 | Word | R | 1
| 0x34D2 | 0x34EF | 13522 | 13551 | 2nd~31st harmonics I16 | Word | R | 30
| 0x34F0 | 0x34F0 | 13552 | 13552 | THD I17 | Word | R | 1
| 0x34F1 | 0x350E | 13553 | 13582 | 2nd~31st harmonics I17 | Word | R | 30
| 0x350F | 0x350F | 13583 | 13583 | THD I18 | Word | R | 1
| 0x3510 | 0x352D | 13584 | 13613 | 2nd~31st harmonics I18 | Word | R | 30
| 0x352E | 0x352E | 13614 | 13614 | Unbalance I - User channel 1 | Word | R | 1
| 0x352F | 0x352F | 13615 | 13615 | Unbalance I - User channel 2 | Word | R | 1
| 0x3530 | 0x3530 | 13616 | 13616 | Unbalance I - User channel 3 | Word | R | 1
| 0x3531 | 0x3531 | 13617 | 13617 | Unbalance I - User channel 4 | Word | R | 1
| 0x3532 | 0x3532 | 13618 | 13618 | Unbalance I - User channel 5 | Word | R | 1
| 0x3533 | 0x3533 | 13619 | 13619 | Unbalance I - User channel 6 | Word | R | 1
| 0x3534 | 0x3534 | 13620 | 13620 | Unbalance I - User channel 7 | Word | R | 1
| 0x3535 | 0x3535 | 13621 | 13621 | Unbalance I - User channel 8 | Word | R | 1
| 0x3536 | 0x3536 | 13622 | 13622 | Unbalance I - User channel 9 | Word | R | 1

## Phase Angle
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Phase Angle | 0x3600 | 0x3600 | 13824 | 13824 | Vb/Vbc phase angle | Word | R | 1 | 0~3600
(0x03 Read) | 0x3601 | 0x3601 | 13825 | 13825 | Vc/Vca phase angle | Word | R | 1 | 0~3600
| 0x3602 | 0x3602 | 13826 | 13826 | I1 phase angle | Word | R | 1 | 0~3600
| 0x3603 | 0x3603 | 13827 | 13827 | I2 phase angle | Word | R | 1 | 0~3600
| 0x3604 | 0x3604 | 13828 | 13828 | I3 phase angle | Word | R | 1 | 0~3600
| 0x3605 | 0x3605 | 13829 | 13829 | I4 phase angle | Word | R | 1 | 0~3600
| 0x3606 | 0x3606 | 13830 | 13830 | I5 phase angle | Word | R | 1 | 0~3600
| 0x3607 | 0x3607 | 13831 | 13831 | I6 phase angle | Word | R | 1 | 0~3600
| 0x3608 | 0x3608 | 13832 | 13832 | I7 phase angle | Word | R | 1 | 0~3600
| 0x3609 | 0x3609 | 13833 | 13833 | I8 phase angle | Word | R | 1 | 0~3600
| 0x360A | 0x360A | 13834 | 13834 | I9 phase angle | Word | R | 1 | 0~3600
| 0x360B | 0x360B | 13835 | 13835 | I10 phase angle | Word | R | 1 | 0~3600
| 0x360C | 0x360C | 13836 | 13836 | I11 phase angle | Word | R | 1 | 0~3600
| 0x360D | 0x360D | 13837 | 13837 | I12 phase angle | Word | R | 1 | 0~3600
| 0x360E | 0x360E | 13838 | 13838 | I13 phase angle | Word | R | 1 | 0~3600
| 0x360F | 0x360F | 13839 | 13839 | I14 phase angle | Word | R | 1 | 0~3600
| 0x3610 | 0x3610 | 13840 | 13840 | I15 phase angle | Word | R | 1 | 0~3600
| 0x3611 | 0x3611 | 13841 | 13841 | I16 phase angle | Word | R | 1 | 0~3600
| 0x3612 | 0x3612 | 13842 | 13842 | I17 phase angle | Word | R | 1 | 0~3600
| 0x3613 | 0x3613 | 13843 | 13843 | I18 phase angle | Word | R | 1 | 0~3600

## Alarm Record
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Alarm Record | 0x3700 | 0x3700 | 14080 | 14080 | Alarm record on reading | integer | R | 1
(0x03 Read, 0x10 Write) | 0x3701 | 0x3701 | 14081 | 14081 | Alarm parameter on reading | integer | R | 1 | See Appendix C
| 0x3702 | 0x3702 | 14082 | 14082 | Alarm set value on reading | integer | R | 1
| 0x3703 | 0x3709 | 14083 | 14089 | Alarm time on reading | integer | R | 7 | Y, M, D, h, m, s, ms
| 0x370A | 0x370A | 14090 | 14090 | Latest alarm record group number | integer | R | 1 | 1~20, 0: No alarm record
| 0x370B | 0x370B | 14091 | 14091 | Alarm record ID on reading | integer | R/W | 1 | 1~20, other value: invalid
| 0x370C | 0x3715 | 14092 | 14101 | 1st alarm record | integer | R | 10 | Same as 0x3700~0x3709
| 0x3716 | 0x371F | 14102 | 14111 | 2nd alarm record | integer | R | 10
| 0x3720 | 0x3729 | 14112 | 14121 | 3rd alarm record | integer | R | 10
| 0x372A | 0x3733 | 14122 | 14131 | 4th alarm record | integer | R | 10
| 0x3734 | 0x373D | 14132 | 14141 | 5th alarm record | integer | R | 10
| 0x373E | 0x3747 | 14142 | 14151 | 6th alarm record | integer | R | 10
| 0x3748 | 0x3751 | 14152 | 14161 | 7th alarm record | integer | R | 10
| 0x3752 | 0x375B | 14162 | 14171 | 8th alarm record | integer | R | 10
| 0x375C | 0x3765 | 14172 | 14181 | 9th alarm record | integer | R | 10
| 0x3766 | 0x376F | 14182 | 14191 | 10th alarm record | integer | R | 10
| 0x3770 | 0x3779 | 14192 | 14201 | 11th alarm record | integer | R | 10
| 0x377A | 0x3783 | 14202 | 14211 | 12th alarm record | integer | R | 10
| 0x3784 | 0x378D | 14212 | 14221 | 13th alarm record | integer | R | 10
| 0x378E | 0x3797 | 14222 | 14231 | 14th alarm record | integer | R | 10
| 0x3798 | 0x37A1 | 14232 | 14241 | 15th alarm record | integer | R | 10
| 0x37A2 | 0x37AB | 14242 | 14251 | 16th alarm record | integer | R | 10
| 0x37AC | 0x37B5 | 14252 | 14261 | 17th alarm record | integer | R | 10
| 0x37B6 | 0x37BF | 14262 | 14271 | 18th alarm record | integer | R | 10
| 0x37C0 | 0x37C9 | 14272 | 14281 | 19th alarm record | integer | R | 10
| 0x37CA | 0x37D3 | 14282 | 14291 | 20th alarm record | integer | R | 10
Alarm status: The high byte represents the alarm channel number 1-10, and the low byte bit 0 is 1 to indicate that an alarm has been triggered, and 0 to indicate that the alarm has been recovered. Only one alarm record can be read at a time, and the reading is controlled by "Alarm record ID on reading".

## System Event
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
System Event | 0x3800 | 0x3805 | 14336 | 14341 | System event time on reading | Word | R | 6
(0x03 Read, 0x10 Write) | 0x3806 | 0x3806 | 14342 | 14342 | System event identifier on reading | Word | R | 1
| 0x3807 | 0x3807 | 14343 | 14343 | Latest system event group number | Word | R | 1
| 0x3808 | 0x3808 | 14344 | 14344 | System event ID on reading | Word | R/W | 1
| 0x6000 | 0x6006 | 24576 | 24582 | 1st alarm record | Word | R | 7 | Same as "System event on reading"
| 0x6007 | 0x62BB | 24583 | 25275 | 2nd~100th alarm record | Word | R | 693
Up to 16 event types, currently supports 12 event types, maximum 100 records.
Event Identifier Definitions:
1: Reset Event
2: DI Sync Demand;
3: Clear Demand;
4: Clear Energy;
5: Clear Meter Running Time;
6: Clear Battery Running Time Event;
7: Modify System Parameter Event;
8: Modify Energy Start Value;
9: TOU Energy Parameter Initialization;
10: Modify Clock;
11: Power Reversal Event;
12: DI Pulse Clearing - Supports a total of 12 event types.

## SOE Record
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
SOE Record | 0x3900 | 0x3900 | 14592 | 14592 | DI SOE record on reading: year | Word | R | 1
(0x03 Read, 0x10 Write) | 0x3901 | 0x3901 | 14593 | 14593 | DI SOE record on reading: month | Word | R | 1
| 0x3902 | 0x3902 | 14594 | 14594 | DI SOE record on reading: day | Word | R | 1
| 0x3903 | 0x3903 | 14595 | 14595 | DI SOE record on reading: hour | Word | R | 1
| 0x3904 | 0x3904 | 14596 | 14596 | DI SOE record on reading: minute | Word | R | 1
| 0x3905 | 0x3905 | 14597 | 14597 | DI SOE record on reading: second | Word | R | 1
| 0x3906 | 0x3906 | 14598 | 14598 | DI SOE record on reading: millisecond (high byte) | Word | R | 1
| 0x3907 | 0x3907 | 14599 | 14599 | DI SOE record on reading: millisecond (low byte) | Word | R | 1
| 0x3908 | 0x3908 | 14600 | 14600 | DI SOE record on reading: state | Word | R | 1 | Bit0-7: DI1-8 state 1: ON, 0: OFF
| 0x3909 | 0x3909 | 14601 | 14601 | Latest SOE record group number | Word | R | 1 | 1-20, 0: none
| 0x390A | 0x390A | 14602 | 14602 | SOE record number on reading | Word | R/W | 1 | 1-20, other value: invalid
| 0x390B | 0x390B | 14603 | 14603 | 1st SOE record: year | Word | R | 1
| 0x390C | 0x390C | 14604 | 14604 | 1st SOE record: month | Word | R | 1
| 0x390D | 0x390D | 14605 | 14605 | 1st SOE record: day | Word | R | 1
| 0x390E | 0x390E | 14606 | 14606 | 1st SOE record: hour | Word | R | 1
| 0x390F | 0x390F | 14607 | 14607 | 1st SOE record: minute | Word | R | 1
| 0x3910 | 0x3910 | 14608 | 14608 | 1st SOE record: second | Word | R | 1
| 0x3911 | 0x3911 | 14609 | 14609 | 1st SOE record: millisecond (high byte) | Word | R | 1
| 0x3912 | 0x3912 | 14610 | 14610 | 1st SOE record: millisecond (low byte) | Word | R | 1
| 0x3913 | 0x3913 | 14611 | 14611 | 1st SOE record: status | Word | R | 1 | Bit0-7: DI1-8 status 1: ON, 0: OFF
| 0x3914 | 0x39BE | 14612 | 14782 | 2nd~20th SOE record | Word | R | 171 | Same as "1st SOE record"

## DI Pulse Counter & Value
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
DI Counter & Value | 0x3A00 | 0x3A01 | 14848 | 14849 | DI1 pulse counter number | Dword | R | 2
(0x03 Read) | 0x3A02 | 0x3A03 | 14850 | 14851 | DI2 pulse counter number | Dword | R | 2
| 0x3A04 | 0x3A05 | 14852 | 14853 | DI3 pulse counter number | Dword | R | 2
| 0x3A06 | 0x3A07 | 14854 | 14855 | DI4 pulse counter number | Dword | R | 2
| 0x3A08 | 0x3A09 | 14856 | 14857 | DI5 pulse counter number | Dword | R | 2
| 0x3A0A | 0x3A0B | 14858 | 14859 | DI6 pulse counter number | Dword | R | 2
| 0x3A0C | 0x3A0D | 14860 | 14861 | DI7 pulse counter number | Dword | R | 2
| 0x3A0E | 0x3A0F | 14862 | 14863 | DI8 pulse counter number | Dword | R | 2
| 0x3A10 | 0x3A11 | 14864 | 14865 | DI9 pulse counter number | Dword | R | 2
| 0x3A12 | 0x3A13 | 14866 | 14867 | DI10 pulse counter number | Dword | R | 2
| 0x3A14 | 0x3A15 | 14868 | 14869 | DI11 pulse counter number | Dword | R | 2
| 0x3A16 | 0x3A17 | 14870 | 14871 | DI12 pulse counter number | Dword | R | 2
| 0x3A18 | 0x3A19 | 14872 | 14873 | DI13 pulse counter number | Dword | R | 2
| 0x3A1A | 0x3A1B | 14874 | 14875 | DI14 pulse counter number | Dword | R | 2
| 0x3A1C | 0x3A1D | 14876 | 14877 | DI15 pulse counter number | Dword | R | 2
| 0x3A1E | 0x3A1F | 14878 | 14879 | DI16 pulse counter number | Dword | R | 2
| 0x3A20 | 0x3A21 | 14880 | 14881 | DI17 pulse counter number | Dword | R | 2
| 0x3A22 | 0x3A23 | 14882 | 14883 | DI18 pulse counter number | Dword | R | 2
| 0x3A24 | 0x3A25 | 14884 | 14885 | DI1 pulse counter value | Float | R | 2
| 0x3A26 | 0x3A27 | 14886 | 14887 | DI2 pulse counter value | Float | R | 2
| 0x3A28 | 0x3A29 | 14888 | 14889 | DI3 pulse counter value | Float | R | 2
| 0x3A2A | 0x3A2B | 14890 | 14891 | DI4 pulse counter value | Float | R | 2
| 0x3A2C | 0x3A2D | 14892 | 14893 | DI5 pulse counter value | Float | R | 2
| 0x3A2E | 0x3A2F | 14894 | 14895 | DI6 pulse counter value | Float | R | 2
| 0x3A30 | 0x3A31 | 14896 | 14897 | DI7 pulse counter value | Float | R | 2
| 0x3A32 | 0x3A33 | 14898 | 14899 | DI8 pulse counter value | Float | R | 2
| 0x3A34 | 0x3A35 | 14900 | 14901 | DI9 pulse counter value | Float | R | 2
| 0x3A36 | 0x3A37 | 14902 | 14903 | DI10 pulse counter value | Float | R | 2
| 0x3A38 | 0x3A39 | 14904 | 14905 | DI11 pulse counter value | Float | R | 2
| 0x3A3A | 0x3A3B | 14906 | 14907 | DI12 pulse counter value | Float | R | 2
| 0x3A3C | 0x3A3D | 14908 | 14909 | DI13 pulse counter value | Float | R | 2
| 0x3A3E | 0x3A3F | 14910 | 14911 | DI14 pulse counter value | Float | R | 2
| 0x3A40 | 0x3A41 | 14912 | 14913 | DI15 pulse counter value | Float | R | 2
| 0x3A42 | 0x3A43 | 14914 | 14915 | DI16 pulse counter value | Float | R | 2
| 0x3A44 | 0x3A45 | 14916 | 14917 | DI17 pulse counter value | Float | R | 2
| 0x3A46 | 0x3A47 | 14918 | 14919 | DI18 pulse counter value | Float | R | 2
Pulse counter value = pulse counter number * pulse counter ratio (unit)

## DI & RO State
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
DI State | 0x0 | 0x0 | 0 | 0 | DI1 state | Bit | R | 1 | 1: ON, 0: OFF
(0x02 Read) | 0x1 | 0x1 | 1 | 1 | DI2 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x2 | 0x2 | 2 | 2 | DI3 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x3 | 0x3 | 3 | 3 | DI4 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x4 | 0x4 | 4 | 4 | DI5 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x5 | 0x5 | 5 | 5 | DI6 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x6 | 0x6 | 6 | 6 | DI7 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x7 | 0x7 | 7 | 7 | DI8 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x8 | 0x8 | 8 | 8 | DI9 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x9 | 0x9 | 9 | 9 | DI10 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xA | 0xA | 10 | 10 | DI11 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xB | 0xB | 11 | 11 | DI12 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xC | 0xC | 12 | 12 | DI13 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xD | 0xD | 13 | 13 | DI14 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xE | 0xE | 14 | 14 | DI15 state | Bit | R | 1 | 1: ON, 0: OFF
| 0xF | 0xF | 15 | 15 | DI16 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x10 | 0x10 | 16 | 16 | DI17 state | Bit | R | 1 | 1: ON, 0: OFF
| 0x11 | 0x11 | 17 | 17 | DI18 state | Bit | R | 1 | 1: ON, 0: OFF
RO State | 0x0 | 0x0 | 0 | 0 | RO1 state | Bit | R/W | 1 | 1: ON, 0: OFF
(0x01 Read, 0x05 Write) | 0x1 | 0x1 | 1 | 1 | RO2 state | Bit | R/W | 1 | 1: ON, 0: OFF

## Datalog & User Defined
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Datalog Window | 0x3B00 | 0x3B00 | 15104 | 15104 | Datalog type, enable, status | Word | R/W | 1
(0x03 Read, 0x10 Write) | 0x3B01 | 0x3B01 | 15105 | 15105 | Number of each window | Word | R/W | 1
| 0x3B02 | 0x3B03 | 15106 | 15107 | Window status + offset | Word | R/W | 2
| 0x3B04 | 0x3B7E | 15108 | 15230 | Window | Word | R | 123
Datalog 1 Data | 0x3C00 | 0x3C01 | 15360 | 15361 | Max Records | UINT32 | R | 2
(0x03 Read) | 0x3C02 | 0x3C03 | 15362 | 15363 | Used Records | UINT32 | R | 2
| 0x3C04 | 0x3C04 | 15364 | 15364 | Record Size | UINT16 | R | 1
| 0x3C05 | 0x3C05 | 15365 | 15365 | Log Availability | word | R | 1
| 0x3C06 | 0x3C08 | 15366 | 15368 | First Record Timestamp | word | R | 3
| 0x3C09 | 0x3C0B | 15369 | 15371 | Last Record Timestamp, | word | R | 3
Datalog 2 Data | 0x3D00 | 0x3D01 | 15616 | 15617 | Max Records | UINT32 | R | 2
(0x03 Read) | 0x3D02 | 0x3D03 | 15618 | 15619 | Used Records | UINT32 | R | 2
| 0x3D04 | 0x3D04 | 15620 | 15620 | Record Size | UINT16 | R | 1
| 0x3D05 | 0x3D05 | 15621 | 15621 | Log Availability | word | R | 1
| 0x3D06 | 0x3D08 | 15622 | 15624 | First Record Timestamp | word | R | 3
| 0x3D09 | 0x3D0B | 15625 | 15627 | Last Record Timestamp | word | R | 3
Datalog 3 Data | 0x3E00 | 0x3E01 | 15872 | 15873 | Max Records | UINT32 | R | 2
(0x03 Read) | 0x3E02 | 0x3E03 | 15874 | 15875 | Used Records | UINT32 | R | 2
| 0x3E04 | 0x3E04 | 15876 | 15876 | Record Size | UINT16 | R | 1
| 0x3E05 | 0x3E05 | 15877 | 15877 | Log Availability | word | R | 1
| 0x3E06 | 0x3E08 | 15878 | 15880 | First Record Timestamp | word | R | 3
| 0x3E09 | 0x3E0B | 15881 | 15883 | Last Record Timestamp | word | R | 3
User Defined Parameter | 0x3F00 | 0x3FE9 | 16128 | 16361 | User defined parameter reading window | word | R | 234
(0x03 Read)

## DST Settings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
DST Settings | 0x4000 | 0x4000 | 16384 | 16384 | DST enable/disable | word | R/W | 1 | 1: enable; 0: disable | 0
(0x03 Read, 0x10 Write) | 0x4001 | 0x4001 | 16385 | 16385 | Format selection | word | R/W | 1 | 0: format 1; 1: format 2 | 0
Format 1 | 0x4002 | 0x4002 | 16386 | 16386 | DST start time: month | word | R/W | 1 | 1~12 | 1
| 0x4003 | 0x4003 | 16387 | 16387 | DST start time: day | word | R/W | 1 | 1~31 | 1
| 0x4004 | 0x4004 | 16388 | 16388 | DST start time: hour | word | R/W | 1 | 0~23 | 0
| 0x4005 | 0x4005 | 16389 | 16389 | DST start time: minute | word | R/W | 1 | 0~59 | 0
| 0x4006 | 0x4006 | 16390 | 16390 | DST start adjust time (unit: minute) | word | R/W | 1 | 1~120 | 60
| 0x4007 | 0x4007 | 16391 | 16391 | DST end time: month | word | R/W | 1 | 1~12 | 1
| 0x4008 | 0x4008 | 16392 | 16392 | DST end time: day | word | R/W | 1 | 1~31 | 1
| 0x4009 | 0x4009 | 16393 | 16393 | DST end time: hour | word | R/W | 1 | 0~23 | 0
| 0x400A | 0x400A | 16394 | 16394 | DST end time: minute | word | R/W | 1 | 0~59 | 0
| 0x400B | 0x400B | 16395 | 16395 | DST end adjust time (unit: minute) | word | R/W | 1 | 1~120 | 60
Format 2 | 0x400C | 0x400C | 16396 | 16396 | DST start time: month | word | R/W | 1 | 1~12 | 1
| 0x400D | 0x400D | 16397 | 16397 | DST start time: Sunday to Saturday | word | R/W | 1 | 0~6: Sunday to Saturday | 0
| 0x400E | 0x400E | 16398 | 16398 | DST start time: week of a month | word | R/W | 1 | 1~5 | 1
| 0x400F | 0x400F | 16399 | 16399 | DST start time: hour | word | R/W | 1 | 0~23 | 0
| 0x4010 | 0x4010 | 16400 | 16400 | DST start time: minute | word | R/W | 1 | 0~59 | 0
| 0x4011 | 0x4011 | 16401 | 16401 | DST start adjust time (unit: minute) | word | R/W | 1 | 1~120 | 60
| 0x4012 | 0x4012 | 16402 | 16402 | DST end time: month | word | R/W | 1 | 1~12 | 1
| 0x4013 | 0x4013 | 16403 | 16403 | DST end time: Sunday to Saturday | word | R/W | 1 | 0~6: Sunday to Saturday | 0
| 0x4014 | 0x4014 | 16404 | 16404 | DST end time: week of a month | word | R/W | 1 | 1~5 | 1
| 0x4015 | 0x4015 | 16405 | 16405 | DST end time: hour | word | R/W | 1 | 0~23 | 0
| 0x4016 | 0x4016 | 16406 | 16406 | DST end time: minute | word | R/W | 1 | 0~59 | 0
| 0x4017 | 0x4017 | 16407 | 16407 | DST end adjust time (unit: minute) | word | R/W | 1 | 1~120 | 60

## Ten-year Special Day
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Tne-year Special Day Settings | 0x4100 | 0x4100 | 16640 | 16640 | Ten-year special day settings enable/disable | word | R/W | 1 | 1: enable; 0: disable | 0
(0x03 Read, 0x10 Write) | 0x4101 | 0x4101 | 16641 | 16641 | Special day start year | word | R/W | 1 | 2000~2099 (end - start < 10) | 0
| 0x4102 | 0x4102 | 16642 | 16642 | Special day end year | word | R/W | 1 | 2000~2099 (end - start < 10) | 0
| 0x4103 | 0x4105 | 16643 | 16645 | 1st year setting: 1st special day - date & schedule | word | R/W | 3 | Month, day, schedule ID | 00:00 0
| 0x4106 | 0x4108 | 16646 | 16648 | 1st year setting : 2nd special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4109 | 0x410B | 16649 | 16651 | 1st year setting: 3rd special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x410C | 0x410E | 16652 | 16654 | 1st year setting: 4th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x410F | 0x4111 | 16655 | 16657 | 1st year setting: 5th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4112 | 0x4114 | 16658 | 16660 | 1st year setting: 6th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4115 | 0x4117 | 16661 | 16663 | 1st year setting: 7th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4118 | 0x411A | 16664 | 16666 | 1st year setting: 8th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x411B | 0x411D | 16667 | 16669 | 1st year setting: 9th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x411E | 0x4120 | 16670 | 16672 | 1st year setting: 10th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4121 | 0x4123 | 16673 | 16675 | 1st year setting: 11th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4124 | 0x4126 | 16676 | 16678 | 1st year setting: 12th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4127 | 0x4129 | 16679 | 16681 | 1st year setting: 13th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x412A | 0x412C | 16682 | 16684 | 1st year setting: 14th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x412D | 0x412F | 16685 | 16687 | 1st year setting: 15th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4130 | 0x4132 | 16688 | 16690 | 1st year setting: 16th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4133 | 0x4135 | 16691 | 16693 | 1st year setting: 17th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4136 | 0x4138 | 16694 | 16696 | 1st year setting: 18th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4139 | 0x413B | 16697 | 16699 | 1st year setting: 19th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x413C | 0x413E | 16700 | 16702 | 1st year setting: 20th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x413F | 0x4141 | 16703 | 16705 | 1st year setting: 21st special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4142 | 0x4144 | 16706 | 16708 | 1st year setting: 22nd special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4145 | 0x4147 | 16709 | 16711 | 1st year setting: 23rd special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4148 | 0x414A | 16712 | 16714 | 1st year setting: 24th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x414B | 0x414D | 16715 | 16717 | 1st year setting: 25th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x414E | 0x4150 | 16718 | 16720 | 1st year setting: 26th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4151 | 0x4153 | 16721 | 16723 | 1st year setting: 27th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4154 | 0x4156 | 16724 | 16726 | 1st year setting: 28th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x4157 | 0x4159 | 16727 | 16729 | 1st year setting: 29th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x415A | 0x415C | 16730 | 16732 | 1st year setting: 30th special day - date & schedule | word | R/W | 3 |  | 00:00 0
| 0x415D | 0x415D | 16733 | 16733 | 1st year setting: setting year | word | R/W | 1 |  | 0
| 0x415E | 0x415E | 16734 | 16734 | 1st year setting: special day number | word | R/W | 1 |  | 0
| 0x415F | 0x41BA | 16735 | 16826 | 2nd year setting |  |  | 92 | Same as "1st year setting"
| 0x41BB | 0x4216 | 16827 | 16918 | 3rd year setting |  |  | 92
| 0x4217 | 0x4272 | 16919 | 17010 | 4th year setting |  |  | 92
| 0x4273 | 0x42CE | 17011 | 17102 | 5th year setting |  |  | 92
| 0x42CF | 0x432A | 17103 | 17194 | 6th year setting |  |  | 92
| 0x432B | 0x4386 | 17195 | 17286 | 7th year setting |  |  | 92
| 0x4387 | 0x43E2 | 17287 | 17378 | 8th year setting |  |  | 92
| 0x43E3 | 0x443E | 17379 | 17470 | 9th year setting |  |  | 92
| 0x443F | 0x449A | 17471 | 17562 | 10th year setting |  |  | 92

## Nameplate Info
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Nameplate Info | 0x7000 | 0x700E | 28672 | 28686 | Model | ASCII | R/W | 15 | AcuRev 2120-xx-xx-MC
(0x03 Read, 0x6A Write) | 0x700F | 0x701D | 28687 | 28701 | Manufacturer | ASCII | R/W | 15 | Accuenergy(CANADA)Inc
| 0x701E | 0x7031 | 28702 | 28721 | Auxiliary Power | ASCII | R/W | 20 | 100~415VL-L, 60Hz
| 0x7032 | 0x7045 | 28722 | 28741 | Rated Voltage | ASCII | R/W | 20 | 120~600VL-L, 60Hz
| 0x7046 | 0x704A | 28742 | 28746 | Frequency | ASCII | R/W | 5 | 60Hz
| 0x704B | 0x7059 | 28747 | 28761 | Temperature Range | ASCII | R/W | 15 | "-20~53" (write) "-20~53 ℃" (display)
| 0x705A | 0x705E | 28762 | 28766 | Transformer Rated | ASCII | R/W | 5 | 0~59
| 0x705F | 0x7068 | 28767 | 28776 | Current Range | ASCII | R/W | 10 | xxxx ~ xxxxA
| 0x7069 | 0x7072 | 28777 | 28786 | Meter Constant | ASCII | R/W | 10 | xxxxx Pulses/kWh
| 0x7073 | 0x7081 | 28787 | 28801 | Approval Number | ASCII | R/W | 15 | AE-xxxx
| 0x7082 | 0x708B | 28802 | 28811 | S/N | ASCII | R/W | 10 | xxxxxxxxxxxx
New dynamic nameplate | 0x7100 | 0x711D | 28928 | 28957 | Model | ASCII | R | 30 | AcuRev 2120-xx-xx-MC
(0x03 Read) | 0x711E | 0x7131 | 28958 | 28977 | Frequency | ASCII | R | 20 | 60Hz
| 0x7132 | 0x7145 | 28978 | 28997 | Current Range | ASCII | R | 20 | xxxx ~ xxxxA
| 0x7146 | 0x7159 | 28998 | 29017 | Meter Constant | ASCII | R | 20 | xxxxx Pulses/kWh
Note: When reading or setting parameters, multiple parameter reading/writing is not allowed (i.e., only one parameter can be read or written at a time).

## Appendix A
Weekend Identifier
Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0
0 | 1: weekday | 0: weekend
Reserved | Saturday | Friday | Thursday | Wednesday | Tuesday | Monday | Sunday
TOU error code 1 (basic config)
Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0
0 | 1 | 1 | 1 | 0 | 1 | 1 | 1
Weekend schedule setting error | Weekend setting error | Holiday number out of range | Season setting error | Season number out of range | Schedule out of range | Segment out of range | Tariff number out of range
TOU error code 2 (schedule config)
Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0
0 | 1 | 1 | 1 | 0 | 1 | 1 | 1
Schedule 8 error | Schedule 7 error | Schedule 6 error | Schedule 5 error | Schedule 4 error | Schedule 3 error | Schedule 2 error | Schedule 1 error
Clearing
Bit15 | Bit14 | Bit13 | Bit12 | Bit11 | Bit10 | Bit9 | Bit8
Set 1 to clear | Set 1 to clear | Set 1 to clear | Set 1 to clear | Set 1 to clear | Set 1 to clear | Set 1 to clear | Set 1 to clear
Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Reserved | Clear max demand reset counter and timestamp history
Bit7 | Bit6 | Bit5 | Bit4 | Bit3 | Bit2 | Bit1 | Bit0
Set 1 to clear | Set 1 to clear | Set 1 to clear | Set 1 to clear | Set 1 to clear | Set 1 to clear | Set 1 to clear | Set 1 to clear
Reset max demand | Reserved | Clear meter run time | Clear system event | Clear alarm record | Reserved | Clear demand | Clear energy

## Appendix B
Pulse output
Value | Parameter
0 | None
1 | Individual channel 1
2 | Individual channel 2
3 | Individual channel 3
4 | Individual channel 4
5 | Individual channel 5
6 | Individual channel 6
7 | Individual channel 7
8 | Individual channel 8
9 | Individual channel 9
10 | Individual channel 10
11 | Individual channel 11
12 | Individual channel 12
13 | Individual channel 13
14 | Individual channel 14
15 | Individual channel 15
16 | Individual channel 16
17 | Individual channel 17
18 | Individual channel 18
19 | User channel 1
20 | User channel 2
21 | User channel 3
22 | User channel 4
23 | User channel 5
24 | User channel 6
25 | Inline total
26 | Inline phase A
27 | Inline phase B
28 | Inline phase C
29 | Demand cycle end
30 | Pulse output by second
31 | User channel 7
32 | User channel 8
33 | User channel 9

## Appendix C
Alarm ID | Parameters
0 | {"Real-Time Metering (Incoming)" | "Frequency"}
1 | {"Real-Time Metering (Incoming)" | "Volts AN"}
2 | {"Real-Time Metering (Incoming)" | "Volts BN"}
3 | {"Real-Time Metering (Incoming)" | "Volts CN"}
4 | {"Real-Time Metering (Incoming)" | "Volts LN Average"}
5 | {"Real-Time Metering (Incoming)" | "Volts AB"}
6 | {"Real-Time Metering (Incoming)" | "Volts BC"}
7 | {"Real-Time Metering (Incoming)" | "Volts CA"}
8 | {"Real-Time Metering (Incoming)" | "Volts LL Average"}
9 | {"Real-Time Metering (Incoming)" | "I A"}
10 | {"Real-Time Metering (Incoming)" | "I B"}
11 | {"Real-Time Metering (Incoming)" | "I C"}
12 | {"Real-Time Metering (Incoming)" | "I Average"}
13 | {"Real-Time Metering (Incoming)" | "Watt Total"}
14 | {"Real-Time Metering (Incoming)" | "VAR Total"}
15 | {"Real-Time Metering (Incoming)" | "VA Total"}
16 | {"Real-Time Metering (Incoming)" | "Pwr Factor Total"}
17 | {"Real-Time Metering (Incoming)" | "Watt A"}
18 | {"Real-Time Metering (Incoming)" | "Watt B"}
19 | {"Real-Time Metering (Incoming)" | "Watt C"}
20 | {"Real-Time Metering (Incoming)" | "VAR A"}
21 | {"Real-Time Metering (Incoming)" | "VAR B"}
22 | {"Real-Time Metering (Incoming)" | "VAR C"}
23 | {"Real-Time Metering (Incoming)" | "VA A"}
24 | {"Real-Time Metering (Incoming)" | "VA B"}
25 | {"Real-Time Metering (Incoming)" | "VA C"}
26 | {"Real-Time Metering (Incoming)" | "Pwr Factor A"}
27 | {"Real-Time Metering (Incoming)" | "Pwr Factor B"}
28 | {"Real-Time Metering (Incoming)" | "Pwr Factor C"}
29 | {"Real-Time Metering (User)" | "I A (CH101)"}
30 | {"Real-Time Metering (User)" | "Watt A (CH101)"}
31 | {"Real-Time Metering (User)" | "VAR A (CH101)"}
32 | {"Real-Time Metering (User)" | "VA A (CH101)"}
33 | {"Real-Time Metering (User)" | "Pwr Factor (CH101)"}
34 | {"Real-Time Metering (User)" | "I A (CH102)"}
35 | {"Real-Time Metering (User)" | "Watt A (CH102)"}
36 | {"Real-Time Metering (User)" | "VAR A (CH102)"}
37 | {"Real-Time Metering (User)" | "VA A (CH102)"}
38 | {"Real-Time Metering (User)" | "Pwr Factor (CH102)"}
39 | {"Real-Time Metering (User)" | "I A (CH103)"}
40 | {"Real-Time Metering (User)" | "Watt A (CH103)"}
41 | {"Real-Time Metering (User)" | "VAR A (CH103)"}
42 | {"Real-Time Metering (User)" | "VA A (CH103)"}
43 | {"Real-Time Metering (User)" | "Pwr Factor (CH103)"}
44 | {"Real-Time Metering (User)" | "I A (CH104)"}
45 | {"Real-Time Metering (User)" | "Watt A (CH104)"}
46 | {"Real-Time Metering (User)" | "VAR A (CH104)"}
47 | {"Real-Time Metering (User)" | "VA A (CH104)"}
48 | {"Real-Time Metering (User)" | "Pwr Factor (CH104)"}
49 | {"Real-Time Metering (User)" | "I A (CH105)"}
50 | {"Real-Time Metering (User)" | "Watt A (CH105)"}
51 | {"Real-Time Metering (User)" | "VAR A (CH105)"}
52 | {"Real-Time Metering (User)" | "VA A (CH105)"}
53 | {"Real-Time Metering (User)" | "Pwr Factor (CH105)"}
54 | {"Real-Time Metering (User)" | "I A (CH106)"}
55 | {"Real-Time Metering (User)" | "Watt A (CH106)"}
56 | {"Real-Time Metering (User)" | "VAR A (CH106)"}
57 | {"Real-Time Metering (User)" | "VA A (CH106)"}
58 | {"Real-Time Metering (User)" | "Pwr Factor (CH106)"}
59 | {"Real-Time Metering (User)" | "I A (CH107)"}
60 | {"Real-Time Metering (User)" | "Watt A (CH107)"}
61 | {"Real-Time Metering (User)" | "VAR A (CH107)"}
62 | {"Real-Time Metering (User)" | "VA A (CH107)"}
63 | {"Real-Time Metering (User)" | "Pwr Factor (CH107)"}
64 | {"Real-Time Metering (User)" | "I A (CH108)"}
65 | {"Real-Time Metering (User)" | "Watt A (CH108)"}
66 | {"Real-Time Metering (User)" | "VAR A (CH108)"}
67 | {"Real-Time Metering (User)" | "VA A (CH108)"}
68 | {"Real-Time Metering (User)" | "Pwr Factor (CH108)"}
69 | {"Real-Time Metering (User)" | "I A (CH109)"}
70 | {"Real-Time Metering (User)" | "Watt A (CH109)"}
71 | {"Real-Time Metering (User)" | "VAR A (CH109)"}
72 | {"Real-Time Metering (User)" | "VA A (CH109)"}
73 | {"Real-Time Metering (User)" | "Pwr Factor (CH109)"}
74 | {"Real-Time Metering (User)" | "I A (CH110)"}
75 | {"Real-Time Metering (User)" | "Watt A (CH110)"}
76 | {"Real-Time Metering (User)" | "VAR A (CH110)"}
77 | {"Real-Time Metering (User)" | "VA A (CH110)"}
78 | {"Real-Time Metering (User)" | "Pwr Factor (CH110)"}
79 | {"Real-Time Metering (User)" | "I A (CH111)"}
80 | {"Real-Time Metering (User)" | "Watt A (CH111)"}
81 | {"Real-Time Metering (User)" | "VAR A (CH111)"}
82 | {"Real-Time Metering (User)" | "VA A (CH111)"}
83 | {"Real-Time Metering (User)" | "Pwr Factor (CH111)"}
84 | {"Real-Time Metering (User)" | "I A (CH112)"}
85 | {"Real-Time Metering (User)" | "Watt A (CH112)"}
86 | {"Real-Time Metering (User)" | "VAR A (CH112)"}
87 | {"Real-Time Metering (User)" | "VA A (CH112)"}
88 | {"Real-Time Metering (User)" | "Pwr Factor (CH112)"}
89 | {"Real-Time Metering (User)" | "I A (CH113)"}
90 | {"Real-Time Metering (User)" | "Watt A (CH113)"}
91 | {"Real-Time Metering (User)" | "VAR A (CH113)"}
92 | {"Real-Time Metering (User)" | "VA A (CH113)"}
93 | {"Real-Time Metering (User)" | "Pwr Factor (CH113)"}
94 | {"Real-Time Metering (User)" | "I A (CH114)"}
95 | {"Real-Time Metering (User)" | "Watt A (CH114)"}
96 | {"Real-Time Metering (User)" | "VAR A (CH114)"}
97 | {"Real-Time Metering (User)" | "VA A (CH114)"}
98 | {"Real-Time Metering (User)" | "Pwr Factor (CH114)"}
99 | {"Real-Time Metering (User)" | "I A (CH115)"}
100 | {"Real-Time Metering (User)" | "Watt A (CH115)"}
101 | {"Real-Time Metering (User)" | "VAR A (CH115)"}
102 | {"Real-Time Metering (User)" | "VA A (CH115)"}
103 | {"Real-Time Metering (User)" | "Pwr Factor (CH115)"}
104 | {"Real-Time Metering (User)" | "I A (CH116)"}
105 | {"Real-Time Metering (User)" | "Watt A (CH116)"}
106 | {"Real-Time Metering (User)" | "VAR A (CH116)"}
107 | {"Real-Time Metering (User)" | "VA A (CH116)"}
108 | {"Real-Time Metering (User)" | "Pwr Factor (CH116)"}
109 | {"Real-Time Metering (User)" | "I A (CH117)"}
110 | {"Real-Time Metering (User)" | "Watt A (CH117)"}
111 | {"Real-Time Metering (User)" | "VAR A (CH117)"}
112 | {"Real-Time Metering (User)" | "VA A (CH117)"}
113 | {"Real-Time Metering (User)" | "Pwr Factor (CH117)"}
114 | {"Real-Time Metering (User)" | "I A (CH118)"}
115 | {"Real-Time Metering (User)" | "Watt A (CH118)"}
116 | {"Real-Time Metering (User)" | "VAR A (CH118)"}
117 | {"Real-Time Metering (User)" | "VA A (CH118)"}
118 | {"Real-Time Metering (User)" | "Pwr Factor (CH118)"}
119 | {"Real-Time Metering (User)" | "Watt A (CH301/201)"}
120 | {"Real-Time Metering (User)" | "VAR A (CH301/201)"}
121 | {"Real-Time Metering (User)" | "VA A (CH301/201)"}
122 | {"Real-Time Metering (User)" | "Pwr Factor (CH301/201)"}
123 | {"Real-Time Metering (User)" | "Watt A (CH302/202)"}
124 | {"Real-Time Metering (User)" | "VAR A (CH302/202)"}
125 | {"Real-Time Metering (User)" | "VA A (CH302/202)"}
126 | {"Real-Time Metering (User)" | "Pwr Factor (CH302/202)"}
127 | {"Real-Time Metering (User)" | "Watt A (CH303/203)"}
128 | {"Real-Time Metering (User)" | "VAR A (CH303/203)"}
129 | {"Real-Time Metering (User)" | "VA A (CH303/203)"}
130 | {"Real-Time Metering (User)" | "Pwr Factor (CH303/203)"}
131 | {"Real-Time Metering (User)" | "Watt A (CH304/204)"}
132 | {"Real-Time Metering (User)" | "VAR A (CH304/204)"}
133 | {"Real-Time Metering (User)" | "VA A (CH304/204)"}
134 | {"Real-Time Metering (User)" | "Pwr Factor (CH304/204)"}
135 | {"Real-Time Metering (User)" | "Watt A (CH305/205)"}
136 | {"Real-Time Metering (User)" | "VAR A (CH305/205)"}
137 | {"Real-Time Metering (User)" | "VA A (CH305/205)"}
138 | {"Real-Time Metering (User)" | "Pwr Factor (CH305/205)"}
139 | {"Real-Time Metering (User)" | "Watt A (CH306/206)"}
140 | {"Real-Time Metering (User)" | "VAR A (CH306/206)"}
141 | {"Real-Time Metering (User)" | "VA A (CH306/206)"}
142 | {"Real-Time Metering (User)" | "Pwr Factor (CH306/206)"}
143 | {"Demand (Incoming)" | "Watt Total"}
144 | {"Demand (Incoming)" | "Watt Total (Pred.)"}
145 | {"Demand (Incoming)" | "VAR Total"}
146 | {"Demand (Incoming)" | "VAR Total (Pred.)"}
147 | {"Demand (Incoming)" | "VA Total"}
148 | {"Demand (Incoming)" | "VA Total (Pred.)"}
149 | {"Demand (Incoming)" | "I A"}
150 | {"Demand (Incoming)" | "I A (Pred.)"}
151 | {"Demand (Incoming)" | "Watt A"}
152 | {"Demand (Incoming)" | "Watt A (Pred.)"}
153 | {"Demand (Incoming)" | "VAR A"}
154 | {"Demand (Incoming)" | "VAR A (Pred.)"}
155 | {"Demand (Incoming)" | "VA A"}
156 | {"Demand (Incoming)" | "VA A (Pred.)"}
157 | {"Demand (Incoming)" | "I B"}
158 | {"Demand (Incoming)" | "I B (Pred.)"}
159 | {"Demand (Incoming)" | "Watt B"}
160 | {"Demand (Incoming)" | "Watt B (Pred.)"}
161 | {"Demand (Incoming)" | "VAR B"}
162 | {"Demand (Incoming)" | "VAR B (Pred.)"}
163 | {"Demand (Incoming)" | "VA B"}
164 | {"Demand (Incoming)" | "VA B (Pred.)"}
165 | {"Demand (Incoming)" | "I C"}
166 | {"Demand (Incoming)" | "I C (Pred.)"}
167 | {"Demand (Incoming)" | "Watt C"}
168 | {"Demand (Incoming)" | "Watt C (Pred.)"}
169 | {"Demand (Incoming)" | "VAR C"}
170 | {"Demand (Incoming)" | "VAR C (Pred.)"}
171 | {"Demand (Incoming)" | "VA C"}
172 | {"Demand (Incoming)" | "VA C (Pred.)"}
173 | {"Demand (User)" | "I A (CH101)"}
174 | {"Demand (User)" | "I A (Pred.) (CH101)"}
175 | {"Demand (User)" | "Watt A (CH101)"}
176 | {"Demand (User)" | "Watt A (Pred.) (CH101)"}
177 | {"Demand (User)" | "VAR A (CH101)"}
178 | {"Demand (User)" | "VAR A (Pred.) (CH101)"}
179 | {"Demand (User)" | "VA A (CH101)"}
180 | {"Demand (User)" | "VA A (Pred.) (CH101)"}
181 | {"Demand (User)" | "I A (CH102)"}
182 | {"Demand (User)" | "I A (Pred.) (CH102)"}
183 | {"Demand (User)" | "Watt A (CH102)"}
184 | {"Demand (User)" | "Watt A (Pred.) (CH102)"}
185 | {"Demand (User)" | "VAR A (CH102)"}
186 | {"Demand (User)" | "VAR A (Pred.) (CH102)"}
187 | {"Demand (User)" | "VA A (CH102)"}
188 | {"Demand (User)" | "VA A (Pred.) (CH102)"}
189 | {"Demand (User)" | "I A (CH103)"}
190 | {"Demand (User)" | "I A (Pred.) (CH103)"}
191 | {"Demand (User)" | "Watt A (CH103)"}
192 | {"Demand (User)" | "Watt A (Pred.) (CH103)"}
193 | {"Demand (User)" | "VAR A (CH103)"}
194 | {"Demand (User)" | "VAR A (Pred.) (CH103)"}
195 | {"Demand (User)" | "VA A (CH103)"}
196 | {"Demand (User)" | "VA A (Pred.) (CH103)"}
197 | {"Demand (User)" | "I A (CH104)"}
198 | {"Demand (User)" | "I A (Pred.) (CH104)"}
199 | {"Demand (User)" | "Watt A (CH104)"}
200 | {"Demand (User)" | "Watt A (Pred.) (CH104)"}
201 | {"Demand (User)" | "VAR A (CH104)"}
202 | {"Demand (User)" | "VAR A (Pred.) (CH104)"}
203 | {"Demand (User)" | "VA A (CH104)"}
204 | {"Demand (User)" | "VA A (Pred.) (CH104)"}
205 | {"Demand (User)" | "I A (CH105)"}
206 | {"Demand (User)" | "I A (Pred.) (CH105)"}
207 | {"Demand (User)" | "Watt A (CH105)"}
208 | {"Demand (User)" | "Watt A (Pred.) (CH105)"}
209 | {"Demand (User)" | "VAR A (CH105)"}
210 | {"Demand (User)" | "VAR A (Pred.) (CH105)"}
211 | {"Demand (User)" | "VA A (CH105)"}
212 | {"Demand (User)" | "VA A (Pred.) (CH105)"}
213 | {"Demand (User)" | "I A (CH106)"}
214 | {"Demand (User)" | "I A (Pred.) (CH106)"}
215 | {"Demand (User)" | "Watt A (CH106)"}
216 | {"Demand (User)" | "Watt A (Pred.) (CH106)"}
217 | {"Demand (User)" | "VAR A (CH106)"}
218 | {"Demand (User)" | "VAR A (Pred.) (CH106)"}
219 | {"Demand (User)" | "VA A (CH106)"}
220 | {"Demand (User)" | "VA A (Pred.) (CH106)"}
221 | {"Demand (User)" | "I A (CH107)"}
222 | {"Demand (User)" | "I A (Pred.) (CH107)"}
223 | {"Demand (User)" | "Watt A (CH107)"}
224 | {"Demand (User)" | "Watt A (Pred.) (CH107)"}
225 | {"Demand (User)" | "VAR A (CH107)"}
226 | {"Demand (User)" | "VAR A (Pred.) (CH107)"}
227 | {"Demand (User)" | "VA A (CH107)"}
228 | {"Demand (User)" | "VA A (Pred.) (CH107)"}
229 | {"Demand (User)" | "I A (CH108)"}
230 | {"Demand (User)" | "I A (Pred.) (CH108)"}
231 | {"Demand (User)" | "Watt A (CH108)"}
232 | {"Demand (User)" | "Watt A (Pred.) (CH108)"}
233 | {"Demand (User)" | "VAR A (CH108)"}
234 | {"Demand (User)" | "VAR A (Pred.) (CH108)"}
235 | {"Demand (User)" | "VA A (CH108)"}
236 | {"Demand (User)" | "VA A (Pred.) (CH108)"}
237 | {"Demand (User)" | "I A (CH109)"}
238 | {"Demand (User)" | "I A (Pred.) (CH109)"}
239 | {"Demand (User)" | "Watt A (CH109)"}
240 | {"Demand (User)" | "Watt A (Pred.) (CH109)"}
241 | {"Demand (User)" | "VAR A (CH109)"}
242 | {"Demand (User)" | "VAR A (Pred.) (CH109)"}
243 | {"Demand (User)" | "VA A (CH109)"}
244 | {"Demand (User)" | "VA A (Pred.) (CH109)"}
245 | {"Demand (User)" | "I A (CH110)"}
246 | {"Demand (User)" | "I A (Pred.) (CH110)"}
247 | {"Demand (User)" | "Watt A (CH110)"}
248 | {"Demand (User)" | "Watt A (Pred.) (CH110)"}
249 | {"Demand (User)" | "VAR A (CH110)"}
250 | {"Demand (User)" | "VAR A (Pred.) (CH110)"}
251 | {"Demand (User)" | "VA A (CH110)"}
252 | {"Demand (User)" | "VA A (Pred.) (CH110)"}
253 | {"Demand (User)" | "I A (CH111)"}
254 | {"Demand (User)" | "I A (Pred.) (CH111)"}
255 | {"Demand (User)" | "Watt A (CH111)"}
256 | {"Demand (User)" | "Watt A (Pred.) (CH111)"}
257 | {"Demand (User)" | "VAR A (CH111)"}
258 | {"Demand (User)" | "VAR A (Pred.) (CH111)"}
259 | {"Demand (User)" | "VA A (CH111)"}
260 | {"Demand (User)" | "VA A (Pred.) (CH111)"}
261 | {"Demand (User)" | "I A (CH112)"}
262 | {"Demand (User)" | "I A (Pred.) (CH112)"}
263 | {"Demand (User)" | "Watt A (CH112)"}
264 | {"Demand (User)" | "Watt A (Pred.) (CH112)"}
265 | {"Demand (User)" | "VAR A (CH112)"}
266 | {"Demand (User)" | "VAR A (Pred.) (CH112)"}
267 | {"Demand (User)" | "VA A (CH112)"}
268 | {"Demand (User)" | "VA A (Pred.) (CH112)"}
269 | {"Demand (User)" | "I A (CH113)"}
270 | {"Demand (User)" | "I A (Pred.) (CH113)"}
271 | {"Demand (User)" | "Watt A (CH113)"}
272 | {"Demand (User)" | "Watt A (Pred.) (CH113)"}
273 | {"Demand (User)" | "VAR A (CH113)"}
274 | {"Demand (User)" | "VAR A (Pred.) (CH113)"}
275 | {"Demand (User)" | "VA A (CH113)"}
276 | {"Demand (User)" | "VA A (Pred.) (CH113)"}
277 | {"Demand (User)" | "I A (CH114)"}
278 | {"Demand (User)" | "I A (Pred.) (CH114)"}
279 | {"Demand (User)" | "Watt A (CH114)"}
280 | {"Demand (User)" | "Watt A (Pred.) (CH114)"}
281 | {"Demand (User)" | "VAR A (CH114)"}
282 | {"Demand (User)" | "VAR A (Pred.) (CH114)"}
283 | {"Demand (User)" | "VA A (CH114)"}
284 | {"Demand (User)" | "VA A (Pred.) (CH114)"}
285 | {"Demand (User)" | "I A (CH115)"}
286 | {"Demand (User)" | "I A (Pred.) (CH115)"}
287 | {"Demand (User)" | "Watt A (CH115)"}
288 | {"Demand (User)" | "Watt A (Pred.) (CH115)"}
289 | {"Demand (User)" | "VAR A (CH115)"}
290 | {"Demand (User)" | "VAR A (Pred.) (CH115)"}
291 | {"Demand (User)" | "VA A (CH115)"}
292 | {"Demand (User)" | "VA A (Pred.) (CH115)"}
293 | {"Demand (User)" | "I A (CH116)"}
294 | {"Demand (User)" | "I A (Pred.) (CH116)"}
295 | {"Demand (User)" | "Watt A (CH116)"}
296 | {"Demand (User)" | "Watt A (Pred.) (CH116)"}
297 | {"Demand (User)" | "VAR A (CH116)"}
298 | {"Demand (User)" | "VAR A (Pred.) (CH116)"}
299 | {"Demand (User)" | "VA A (CH116)"}
300 | {"Demand (User)" | "VA A (Pred.) (CH116)"}
301 | {"Demand (User)" | "I A (CH117)"}
302 | {"Demand (User)" | "I A (Pred.) (CH117)"}
303 | {"Demand (User)" | "Watt A (CH117)"}
304 | {"Demand (User)" | "Watt A (Pred.) (CH117)"}
305 | {"Demand (User)" | "VAR A (CH117)"}
306 | {"Demand (User)" | "VAR A (Pred.) (CH117)"}
307 | {"Demand (User)" | "VA A (CH117)"}
308 | {"Demand (User)" | "VA A (Pred.) (CH117)"}
309 | {"Demand (User)" | "I A (CH118)"}
310 | {"Demand (User)" | "I A (Pred.) (CH118)"}
311 | {"Demand (User)" | "Watt A (CH118)"}
312 | {"Demand (User)" | "Watt A (Pred.) (CH118)"}
313 | {"Demand (User)" | "VAR A (CH118)"}
314 | {"Demand (User)" | "VAR A (Pred.) (CH118)"}
315 | {"Demand (User)" | "VA A (CH118)"}
316 | {"Demand (User)" | "VA A (Pred.) (CH118)"}
317 | {"Demand (User)" | "Watt Total (CH301/201)"}
318 | {"Demand (User)" | "Watt Total (Pred.) (CH301/201)"}
319 | {"Demand (User)" | "VAR Total (CH301/201)"}
320 | {"Demand (User)" | "VAR Total (Pred.) (CH301/201)"}
321 | {"Demand (User)" | "VA Total (CH301/201)"}
322 | {"Demand (User)" | "VA Total (Pred.) (CH301/201)"}
323 | {"Demand (User)" | "Watt Total (CH302/202)"}
324 | {"Demand (User)" | "Watt Total (Pred.) (CH302/202)"}
325 | {"Demand (User)" | "VAR Total (CH302/202)"}
326 | {"Demand (User)" | "VAR Total (Pred.) (CH302/202)"}
327 | {"Demand (User)" | "VA Total (CH302/202)"}
328 | {"Demand (User)" | "VA Total (Pred.) (CH302/202)"}
329 | {"Demand (User)" | "Watt Total (CH303/203)"}
330 | {"Demand (User)" | "Watt Total (Pred.) (CH303/203)"}
331 | {"Demand (User)" | "VAR Total (CH303/203)"}
332 | {"Demand (User)" | "VAR Total (Pred.) (CH303/203)"}
333 | {"Demand (User)" | "VA Total (CH303/203)"}
334 | {"Demand (User)" | "VA Total (Pred.) (CH303/203)"}
335 | {"Demand (User)" | "Watt Total (CH304/204)"}
336 | {"Demand (User)" | "Watt Total (Pred.) (CH304/204)"}
337 | {"Demand (User)" | "VAR Total (CH304/204)"}
338 | {"Demand (User)" | "VAR Total (Pred.) (CH304/204)"}
339 | {"Demand (User)" | "VA Total (CH304/204)"}
340 | {"Demand (User)" | "VA Total (Pred.) (CH304/204)"}
341 | {"Demand (User)" | "Watt Total (CH305/205)"}
342 | {"Demand (User)" | "Watt Total (Pred.) (CH305/205)"}
343 | {"Demand (User)" | "VAR Total (CH305/205)"}
344 | {"Demand (User)" | "VAR Total (Pred.) (CH305/205)"}
345 | {"Demand (User)" | "VA Total (CH305/205)"}
346 | {"Demand (User)" | "VA Total (Pred.) (CH305/205)"}
347 | {"Demand (User)" | "Watt Total (CH306/206)"}
348 | {"Demand (User)" | "Watt Total (Pred.) (CH306/206)"}
349 | {"Demand (User)" | "VAR Total (CH306/206)"}
350 | {"Demand (User)" | "VAR Total (Pred.) (CH306/206)"}
351 | {"Demand (User)" | "VA Total (CH306/206)"}
352 | {"Demand (User)" | "VA Total (Pred.) (CH306/206)"}
353 | {"Digital Input" | "Digital Input 1"}
354 | {"Digital Input" | "Digital Input 2"}
355 | {"Digital Input" | "Digital Input 3"}
356 | {"Digital Input" | "Digital Input 4"}
357 | {"Digital Input" | "Digital Input 5"}
358 | {"Digital Input" | "Digital Input 6"}
359 | {"Digital Input" | "Digital Input 7"}
360 | {"Digital Input" | "Digital Input 8"}
361 | {"Digital Input" | "Digital Input 9"}
362 | {"Digital Input" | "Digital Input 10"}
363 | {"Digital Input" | "Digital Input 11"}
364 | {"Digital Input" | "Digital Input 12"}
365 | {"Digital Input" | "Digital Input 13"}
366 | {"Digital Input" | "Digital Input 14"}
367 | {"Digital Input" | "Digital Input 15"}
368 | {"Digital Input" | "Digital Input 16"}
369 | {"Digital Input" | "Digital Input 17"}
370 | {"Digital Input" | "Digital Input 18"}
371 | {"Real-Time Metering (User)" | "Watt A (CH207)"}
372 | {"Real-Time Metering (User)" | "VAR A (CH207)"}
373 | {"Real-Time Metering (User)" | "VA A (CH207)"}
374 | {"Real-Time Metering (User)" | "Pwr Factor (CH207)"}
375 | {"Real-Time Metering (User)" | "Watt A (CH208)"}
376 | {"Real-Time Metering (User)" | "VAR A (CH208)"}
377 | {"Real-Time Metering (User)" | "VA A (CH208)"}
378 | {"Real-Time Metering (User)" | "Pwr Factor (CH208)"}
379 | {"Real-Time Metering (User)" | "Watt A (CH209)"}
380 | {"Real-Time Metering (User)" | "VAR A (CH209)"}
381 | {"Real-Time Metering (User)" | "VA A (CH209)"}
382 | {"Real-Time Metering (User)" | "Pwr Factor (CH209)"}
383 | {"Demand (User)" | "Watt Total (CH207)"}
384 | {"Demand (User)" | "Watt Total (Pred.) (CH207)"}
385 | {"Demand (User)" | "VAR Total (CH207)"}
386 | {"Demand (User)" | "VAR Total (Pred.) (CH207)"}
387 | {"Demand (User)" | "VA Total (CH207)"}
388 | {"Demand (User)" | "VA Total (Pred.) (CH207)"}
389 | {"Demand (User)" | "Watt Total (CH208)"}
390 | {"Demand (User)" | "Watt Total (Pred.) (CH208)"}
391 | {"Demand (User)" | "VAR Total (CH208)"}
392 | {"Demand (User)" | "VAR Total (Pred.) (CH208)"}
393 | {"Demand (User)" | "VA Total (CH208)"}
394 | {"Demand (User)" | "VA Total (Pred.) (CH208)"}
395 | {"Demand (User)" | "Watt Total (CH209)"}
396 | {"Demand (User)" | "Watt Total (Pred.) (CH209)"}
397 | {"Demand (User)" | "VAR Total (CH209)"}
398 | {"Demand (User)" | "VAR Total (Pred.) (CH209)"}
399 | {"Demand (User)" | "VA Total (CH209)"}
400 | {"Demand (User)" | "VA Total (Pred.) (CH209)"}