## Version history
Version | Changes | Author | Date | Internal Firmware Version | External Firmware Version
v1.01 | Initial definition, according to PRS. | Zhouxiong Zhang Zhenjiang Guo |  | v1.01p01
| 增加USB转TTL对应串口的波特率和极性的地址 | Zhouxiong Zhang
| 依 PRS v1.04 / SRS v1.02 决策更新: 脉冲常数(电/LED)可配置0.1~50imp/kWh, 定点编码=实际×100,LED默认改50; 序列号格式改 MAC(YY+30)MMabcde; 取消认证/标准分型,仅AcuRev-101(操作由铅封开关区分); 新增 Model/Manufacturer/Device Status 寄存器 LCD背光当前不点亮; USB与RS-485功能一致(各自独立波特率/校验,共享从机地址,可同时连接). | Zhenjiang Guo | 2026-06-30

## Overview
Block | Sector | Sheet | Start(Hex) | End(Hex) | Length(reg num) | Comments
Information | Firmware Version Info | Information | 0xF000 | 0xF005 | 6
| Bootloader Info | Information | 0xF010 | 0xF017 | 8
| Product Info | Information | 0xF040 | 0xF070 | 49
Basic Settings | System Settings | Basic Settings | 0x1000 | 0x1028 | 41
| Metrology Settings | Basic Settings | 0x1040 | 0x1069 | 42
| Operations | Basic Settings | 0x1130 | 0x1148 | 25
Wiring Check | Wiring Check | Wiring Check | 0x3000 | 0x301D | 30
Real Time | Real time basic parameters（100ms) | Real Time | 0x9050 | 0x90A3 | 84
Energy | Energy | Energy（1S） | 0x4A00 | 0x4A47 | 72
Calibration | Calibration Commands | Calibration | 0x2000 | 0x2002 | 3
| Calibration OffSet Coef（50Hz/60Hz） | Calibration | 0x2010 | 0x204B | 60

## Information
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Fireware & Product information:03H Read
Firmware Version Info
| 0xF000 | 0xF001 | 61440 | 61441 | Firmware version | uint8_t | R | 2 | In the format like x.yz (e.g., 1.01) | determined by firmware
| 0xF002 | 0xF004 | 61442 | 61444 | Firmware release date | uint8_t | R | 3 | In the format like YYMMDD (221228) | determined by firmware
| 0xF005 | 0xF005 | 61445 | 61445 | Firmware patch number | uint8_t | R | 1 | In the format like xy (01) | determined by firmware
Update(0x6A to write) | 0xF000 | 0xF001 | 61440 | 61441 | Device entry update | uint8_t | W | 2 | 0xA1,0x58,0x58,0xA1 | 0
Bootloader Info
| 0xF010 | 0xF011 | 61456 | 61457 | bootloader product string | uint8_t | R | 2 | e.g. MAA1 | determined by boot
| 0xF012 | 0xF013 | 61458 | 61459 | bootloader version | uint8_t | R | 2 | In the format like x.yz (e.g., 1.01) | determined by boot
| 0xF014 | 0xF016 | 61460 | 61462 | bootloader release date | uint8_t | R | 3 | ASCII, in format of YYMMDD (e.g. 241108) | determined by boot
| 0xF017 | 0xF017 | 61463 | 61463 | bootloader patch number | uint8_t | R | 1 | In the format like xy (01) | determined by boot
Product Info (0x6A to write in factory)
| 0xF040 | 0xF04F | 61504 | 61519 | Serial Number | uint8_t | R/W | 16 | In the format like MAC(YY+30)MMabcde (PRS v1.04 / SRS v1.02)
| 0xF050 | 0xF051 | 61520 | 61521 | Hardware version | uint8_t | R/W | 2 | In the format like x.yz (e.g., 1.01) The main version and sub-version are released to the factory by the hardware engineers from the R&D department.
| 0xF052 | 0xF052 | 61522 | 61522 | Function Model Type | uint16_t | R/W | 1 | 0: AcuRev-101
| 0xF053 | 0xF053 | 61523 | 61523 | Reserved(1320 Reserved) |  |  | 1
| 0xF054 | 0xF054 | 61524 | 61524 | Reserved(1320 Current Input Type) |  |  | 1
| 0xF055 | 0xF055 | 61525 | 61525 | Reserved(1320 Power Supply Type) |  |  | 1
| 0xF056 | 0xF065 | 61526 | 61541 | Reserved(MAC address(port3)) |  |  | 16
| 0xF066 | 0xF066 | 61542 | 61542 | Certification Type | uint16_t | R/W | 1 | 0: None; 1: MC; Default:0
| 0xF067 | 0xF06F | 61543 | 61551 | Reserved(1320 Reserved) |  |  | 9 | Set the register to 0
| 0xF070 | 0xF070 | 61552 | 61552 | Hardware Patch Number | uint8_t | R/W | 1 | In the format like xy (01) The hardware patch version. The content of this register is controlled and configured by the factory.
| 0xF071 | 0xF07A | 61553 | 61562 | Model | uint8_t | R | 10 | Model name string (ASCII) | AcuRev-101
| 0xF07B | 0xF08A | 61563 | 61578 | Manufacturer | uint8_t | R | 16 | Manufacturer name string (ASCII) | Accuenergy

## Basic Setting
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
System Setting
| 0x1000 | 0x1000 | 4096 | 4096 | Password | uint16_t | R/W | 1 |  | 0
| 0x1001 | 0x1001 | 4097 | 4097 | RS485 Baud Rate | uint16_t | R/W | 1 | 9600\19200\38400\57600\76800\115200(76800 need send 7680 115200need send 11520) | 19200
| 0x1002 | 0x1002 | 4098 | 4098 | RS485 Parity | uint16_t | R/W | 1 | 0: even 1: odd 2: None2 3: None1 | 3: None1
| 0x1003 | 0x1003 | 4099 | 4099 | Reserved(1320 Ethernet Communication Mode) |  |  | 1
| 0x1004 | 0x1004 | 4100 | 4100 | Reserved(1320 DHCP enable) |  |  | 1
| 0x1005 | 0x1005 | 4101 | 4101 | Reserved(1320 IP address 1st byte IP address 2nd byte ) |  |  | 1
| 0x1006 | 0x1006 | 4102 | 4102 | Reserved(1320 IP address 3rd byte IP address 4th byte ) |  |  | 1
| 0x1007 | 0x1007 | 4103 | 4103 | Reserved(1320 Subnet mask 1st byte Subnet mask 2nd byte ) |  |  | 1
| 0x1008 | 0x1008 | 4104 | 4104 | Reserved(1320 Subnet mask 3rd byte Subnet mask 4th byte ) |  |  | 1
| 0x1009 | 0x1009 | 4105 | 4105 | Reserved(1320 Gateway 1st byte Gateway 2nd byte ) |  |  | 1
| 0x100A | 0x100A | 4106 | 4106 | Reserved(1320 Gateway 3rd byte Gateway 4th byte ) |  |  | 1
| 0x100B | 0x100B | 4107 | 4107 | Reserved(1320 DNS primary server 1st byte DNS primary server 2nd byte ) |  |  | 1
| 0x100C | 0x100C | 4108 | 4108 | Reserved(1320 DNS primary server 3rd byte DNS primary server 4th byte ) |  |  | 1
| 0x100D | 0x100D | 4109 | 4109 | Reserved(1320 DNS secondary server 1st byte DNS secondary server 2nd byte ) |  |  | 1
| 0x100E | 0x100E | 4110 | 4110 | Reserved(1320 DNS secondary server 3rd byte DNS secondary server 4th byte ) |  |  | 1
| 0x100F | 0x100F | 4111 | 4111 | Modbus Slave ID | uint16_t | R/W | 1 | 1-247 | 1
| 0x1010 | 0x1010 | 4112 | 4112 | Reserved(1320 RS485 protocol) |  |  | 1
| 0x1011 | 0x1011 | 4113 | 4113 | Reserved(1320 Modbus TCP Enable) |  |  | 1
| 0x1012 | 0x1012 | 4114 | 4114 | Reserved(1320 Modbus TCP port) |  |  | 1
| 0x1013 | 0x1013 | 4115 | 4115 | Reserved(1320 BACnet MS/TP Meter address) |  |  | 1
| 0x1014 | 0x1014 | 4116 | 4116 | Reserved(1320 BACnet MS/TP Maximum number of message frames) |  |  | 1
| 0x1015 | 0x1016 | 4117 | 4118 | Reserved(1320 BACnet MS/TP ID) |  |  | 2
| 0x1017 | 0x1017 | 4119 | 4119 | Reserved(1320 BACnet Database Revision) |  |  | 1
| 0x1018 | 0x1018 | 4120 | 4120 | LCD Backlight Time | uint16_t | R/W | 1 | 0-120 minute | 1
| 0x1019 | 0x101A | 4121 | 4122 | Device run time | uint32_t | R | 2 | uint in second | 0
| 0x101B | 0x101C | 4123 | 4124 | Device load time | uint32_t | R | 2 | uint in second | 0
| 0x101D | 0x101D | 4125 | 4125 | Reserved(1320 Non-standard Seal Parameter Select) |  |  | 1
| 0x101E | 0x101E | 4126 | 4126 | Reserved(1320 Time Zone) |  |  | 1
| 0x101F | 0x101F | 4127 | 4127 | Week | uint16_t | R/W | 1 | 1~7 | 1
| 0x1020 | 0x1020 | 4128 | 4128 | Year | uint16_t | R/W | 1 | 2000~2099 | 2024
| 0x1021 | 0x1021 | 4129 | 4129 | Month | uint16_t | R/W | 1 | 1~12 | 1
| 0x1022 | 0x1022 | 4130 | 4130 | Day | uint16_t | R/W | 1 | 1~31 | 1
| 0x1023 | 0x1023 | 4131 | 4131 | Hour | uint16_t | R/W | 1 | 0~23 | 0
| 0x1024 | 0x1024 | 4132 | 4132 | Minute | uint16_t | R/W | 1 | 0~59 | 0
| 0x1025 | 0x1025 | 4133 | 4133 | Second | uint16_t | R/W | 1 | 0~59 | 0
| 0x1026 | 0x1026 | 4134 | 4134 | Reserved(1320 millisecond) | uint16_t | R/W | 1
| 0x1027 | 0x1027 | 4135 | 4135 | USB_TTL Baud Rate | uint16_t | R/W | 1 | 9600\19200\38400\57600\76800\115200(76800 need send 7680 115200need send 11520) | 19200
| 0x1028 | 0x1028 | 4136 | 4136 | USB_TTL Parity | uint16_t | R/W | 1 | 0: even 1: odd 2: None2 3: None1 | 3: None1
| 0x1029 | 0x102A | 4137 | 4138 | Device Status / Fault Code | uint32_t | R | 2 | Bit definitions TBD (设备运行状态/故障; 位定义待补充) | 0
Metrology Settings
| 0x1040 | 0x1040 | 4160 | 4160 | Sealing Status | uint16_t | R | 1 | sealed: 0x0A unsealed: 0
| 0x1041 | 0x1041 | 4161 | 4161 | Frequency Selection | uint16_t | R/W | 1 | 0: 50Hz 1: 60Hz | 1
| 0x1042 | 0x1042 | 4162 | 4162 | Service Configuration | uint16_t | R/W | 1 | 0: ELEMENT_1_WIRE_2 1: ELEMENT_2_WIRE_3_PHASE_1 2: ELEMENT_3_WIRE_4_Y | 2
| 0x1043 | 0x1044 | 4163 | 4164 | Reserved(1320 PT1) |  |  | 2
| 0x1045 | 0x1045 | 4165 | 4165 | Reserved(1320 PT2) |  |  | 1
| 0x1046 | 0x1046 | 4166 | 4166 | Reserved(1320 In Method) |  |  | 1
| 0x1047 | 0x1047 | 4167 | 4167 | channel 1 input wiring ID | uint16_t | R/W | 1 | 1~3 | 1
| 0x1048 | 0x1048 | 4168 | 4168 | channel 1 Current Direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1049 | 0x1049 | 4169 | 4169 | channel 1 input CT Type | uint16_t | R/W | 1 | 0: 100mA | 0: 100mA for mA type
| 0x104A | 0x104A | 4170 | 4170 | channel 1 input CT Primary | uint16_t | R/W | 1 | 200/400/800/1200（Standard Type only） | 200
| 0x104B | 0x104B | 4171 | 4171 | channel 2 input wiring ID | uint16_t | R/W | 1 | 1~3 | 2
| 0x104C | 0x104C | 4172 | 4172 | channel 2 Current Direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x104D | 0x104D | 4173 | 4173 | channel 2 input CT Type | uint16_t | R/W | 1 | 0: 100mA | 0: 100mA for mA type
| 0x104E | 0x104E | 4174 | 4174 | channel 2 input CT Primary | uint16_t | R/W | 1 | 200/400/800/1200（Standard Type only） | 400
| 0x104F | 0x104F | 4175 | 4175 | channel 3 input wiring ID | uint16_t | R/W | 1 | 1~3 | 3
| 0x1050 | 0x1050 | 4176 | 4176 | channel 3 Current Direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1051 | 0x1051 | 4177 | 4177 | channel 3 input CT Type | uint16_t | R/W | 1 | 0: 100mA | 0: 100mA for mA type
| 0x1052 | 0x1052 | 4178 | 4178 | channel 3 input CT Primary | uint16_t | R/W | 1 | 200/400/800/1200（Standard Type only） | 200
| 0x1053 | 0x1053 | 4179 | 4179 | Reserved(1320 channel 4 input wiring ID) |  |  | 1
| 0x1054 | 0x1054 | 4180 | 4180 | Reserved(1320 channel 4 Current Direction) |  |  | 1
| 0x1055 | 0x1055 | 4181 | 4181 | Reserved(1320 channel 4 input CT Type ) |  |  | 1
| 0x1056 | 0x1056 | 4182 | 4182 | Reserved(1320 channel 4 input CT Primary) |  |  | 1
| 0x1057 | 0x1057 | 4183 | 4183 | Reactive Power Calculation Method | uint16_t | R/W | 1 | General: 0 True: 1 | 0
| 0x1058 | 0x1058 | 4184 | 4184 | PF Convention | uint16_t | R/W | 1 | PF Format IEC: 0 PF Format IEEE: 1 | 0
| 0x1059 | 0x1059 | 4185 | 4185 | Reserved(1320 Demand Algorithm) |  |  | 1
| 0x105A | 0x105A | 4186 | 4186 | Reserved(1320 Demand Interval) |  |  | 1
| 0x105B | 0x105B | 4187 | 4187 | Reserved(1320 Demand Update Interval) |  |  | 1
| 0x105C | 0x105C | 4188 | 4188 | Reserved(1320 MaxDemand Clear Mode) |  |  | 1
| 0x105D | 0x105E | 4189 | 4190 | Reserved(1320 MaxDemand Clear Date Setting) |  |  | 2
| 0x105F | 0x105F | 4191 | 4191 | Reserved(1320 MaxDemand Clear Total Count) |  |  | 1
| 0x1060 | 0x1062 | 4192 | 4194 | Reserved(1320 Timestamp of the most recent MaxDemand Clear) |  |  | 3
| 0x1063 | 0x1063 | 4195 | 4195 | Phase Order | uint16_t | R/W | 1 | ABC: 0 ACB: 1 | 0
| 0x1064 | 0x1064 | 4196 | 4196 | Energy Reading Display format | uint16_t | R/W | 1 | 0: Primary in 0.1 kWh;1:0.01kWh; 2: Primary in 0.001kWh | 0
| 0x1065 | 0x1065 | 4197 | 4197 | Energy Calculation Method | uint16_t | R/W | 1 | Generic: 0 Fundamental: 1 | 0
| 0x1066 | 0x1067 | 4198 | 4199 | Energy pulse constant | uint32_t | R/W | 2 | 100~50000 (=0.1~50 imp/kWh, reg value = actual ×1000) | 1000 (=1.00 imp/kWh)
| 0x1068 | 0x1068 | 4200 | 4200 | Pulse width | uint16_t | R/W | 1 | 20 | 20 ms
| 0x1069 | 0x106A | 4201 | 4202 | LED pulse constant | uint32_t | R/W | 2 | 100~50000 (=0.1~50 imp/kWh, reg value = actual ×1000) | 50000 (=50.00 imp/kWh)
Operations
| 0x1130 | 0x1130 | 4400 | 4400 | Clear energy | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1131 | 0x1131 | 4401 | 4401 | Reserved(1320 Clear Max demand ) |  |  | 1
| 0x1132 | 0x1132 | 4402 | 4402 | Reserved(1320 Clear MaxDemand ClearCount and Timestamp) |  |  | 1
| 0x1133 | 0x1133 | 4403 | 4403 | Reserved(1320 Clear max/min) |  |  | 1
| 0x1134 | 0x1134 | 4404 | 4404 | Clear device run time | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1135 | 0x1135 | 4405 | 4405 | Clear load time | uint16_t | R/W | 1 | 0: None 1: Reset | 0
| 0x1136 | 0x1136 | 4406 | 4406 | Factory reset | uint16_t | R/W | 1 | 0: None 1: Resetting | 0
| 0x1137 | 0x1137 | 4407 | 4407 | Reserved(1320 Network reset) |  |  | 1
| 0x1138 | 0x1138 | 4408 | 4408 | Reserved(1320 Clear SOE Log ) |  |  | 1
| 0x1139 | 0x1139 | 4409 | 4409 | Reserved(1320 Clear alarm Log) |  |  | 1
| 0x113A | 0x113A | 4410 | 4410 | Reserved(1320 Clear PQ event Log) |  |  | 1
| 0x113B | 0x113B | 4411 | 4411 | Reserved(1320 Clear Waveform ) |  |  | 1
| 0x113C | 0x113C | 4412 | 4412 | Reserved(1320 Clear Data Log1) |  |  | 1
| 0x113D | 0x113D | 4413 | 4413 | Reserved(1320 Clear Data Log2) |  |  | 1
| 0x113E | 0x113E | 4414 | 4414 | Reserved(1320 Clear Data Log3) |  |  | 1
| 0x113F | 0x113F | 4415 | 4415 | Reserved(1320 Clear Trend Log) |  |  | 1
| 0x1140 | 0x1140 | 4416 | 4416 | Reserved(1320 Clear DI Count ) |  |  | 1
| 0x1141 | 0x1141 | 4417 | 4417 | Reserved(1320 Clear Year 10 Holiday Number Setting) |  |  | 1
| 0x1142 | 0x1142 | 4418 | 4418 | Reserved(1320 Restore TOU factory setting) |  |  | 1
| 0x1143 | 0x1143 | 4419 | 4419 | Reserved(1320 Clear TOU Energy ) |  |  | 1
| 0x1144 | 0x1144 | 4420 | 4420 | Reserved(1320 Clear TOU Max Demand ) |  |  | 1
| 0x1145 | 0x1145 | 4421 | 4421 | Reserved(1320 Clear Dual Source energy) |  |  | 1
| 0x1146 | 0x1146 | 4422 | 4422 | Reserved(1320 Clear Dual Source energy switching record) |  |  | 1
| 0x1147 | 0x1147 | 4423 | 4423 | Device Reboot | uint16_t | R/W | 1 | 0: None 1: Reset | 0
| 0x1148 | 0x1148 | 4424 | 4424 | Communication reset | uint16_t | R/W | 1 | 0: None 1: Reset | 0
Note on F3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 这里原来是 RS485 协议选择
Note on F19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 这里原来是 RS485 协议选择
Note on J45: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 2026-05-22 By Shaohang Cui： 可能只支持 60 Hz(待定）

## Wiring Check
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Wiring Check | 0x3000 | 0x3000 | 12288 | 12288 | Wire Check Switch | uint16_t | R/W | 1 | 0:ON 1:OFF | 0
| 0x3001 | 0x3001 | 12289 | 12289 | Wire Check Status | uint16_t | R | 1 | 0: Not Started 1: In Progress 2: Completed
| 0x3002 | 0x3002 | 12290 | 12290 | Phase Voltage Error Code | uint16_t | R | 1 | Bit0:Voltage terminals Va wiring is missing Bit1:Voltage terminals Vb wiring is missing Bit2:Voltage terminals Vc wiring is missing Bit3:The voltage terminals Va and Vn are reversed. Bit4: The voltage terminals Vb and Vn are reversed. Bit5: The voltage terminals Vc and Vn are reversed. Bit6: Phase error of voltage terminals Vb Bit7: Phase error of voltage terminals Vc Bit8: ABC/ACB sequence is configured incorrectly
| 0x3003 | 0x3003 | 12291 | 12291 | Phase Current Error Code | uint16_t | R | 1 | Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Current terminals Ia and Ib are reversed Bit7:Current terminals Ia and Ic are reversed Bit8:Current terminals Ib and Ic are reversed
| 0x3004 | 0x3005 | 12292 | 12293 | Phase A Line-to-Neutral | float | R | 2
| 0x3006 | 0x3007 | 12294 | 12295 | Phase A Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x3008 | 0x3009 | 12296 | 12297 | Phase B Line-to-Neutral | float | R | 2
| 0x300A | 0x300B | 12298 | 12299 | Phase B Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x300C | 0x300D | 12300 | 12301 | Phase C Line-to-Neutral | float | R | 2
| 0x300E | 0x300F | 12302 | 12303 | Phase C Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x3010 | 0x3011 | 12304 | 12305 | Voltage Phase Order | uint32_t | R | 2 | 0：ABC 1：ACB 2：不存在
| 0x3012 | 0x3013 | 12306 | 12307 | Phase A Current | float | R | 2
| 0x3014 | 0x3015 | 12308 | 12309 | Phase A Current Angle | float | R | 2
| 0x3016 | 0x3017 | 12310 | 12311 | Phase B Current | float | R | 2
| 0x3018 | 0x3019 | 12312 | 12313 | Phase B Current Angle | float | R | 2
| 0x301A | 0x301B | 12314 | 12315 | Phase C Current | float | R | 2
| 0x301C | 0x301D | 12316 | 12317 | Phase C Current Angle | float | R | 2

## Real Time
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Real time basic parameters（100ms)
| 0x9050 | 0x9053 | 36944 | 36947 | Reserved(1320 HS Param Update Time Stamp) | uint64_t | R | 4
| 0x9054 | 0x9055 | 36948 | 36949 | System Frequency | float | R | 2
| 0x9056 | 0x9057 | 36950 | 36951 | Phase A Line-to-Neutral Voltage | float | R | 2
| 0x9058 | 0x9059 | 36952 | 36953 | Phase B Line-to-Neutral Voltage | float | R | 2
| 0x905A | 0x905B | 36954 | 36955 | Phase C Line-to-Neutral Voltage | float | R | 2
| 0x905C | 0x905D | 36956 | 36957 | Phase A Voltage Phase Angle | float | R | 2
| 0x905E | 0x905F | 36958 | 36959 | Phase B Voltage Phase Angle | float | R | 2
| 0x9060 | 0x9061 | 36960 | 36961 | Phase C Voltage Phase Angle | float | R | 2
| 0x9062 | 0x9063 | 36962 | 36963 | Average Line-to-Neutral Voltage | float | R | 2
| 0x9064 | 0x9065 | 36964 | 36965 | Phase AB Line-to-Line Voltage | float | R | 2
| 0x9066 | 0x9067 | 36966 | 36967 | Phase BC Line-to-Line Voltage | float | R | 2
| 0x9068 | 0x9069 | 36968 | 36969 | Phase CA Line-to-Line Voltage | float | R | 2
| 0x906A | 0x906B | 36970 | 36971 | Phase AB Line-to-Line Voltage Phase Angle | float | R | 2
| 0x906C | 0x906D | 36972 | 36973 | Phase BC Line-to-Line Voltage Phase Angle | float | R | 2
| 0x906E | 0x906F | 36974 | 36975 | Phase CA Line-to-Line Voltage Phase Angle | float | R | 2
| 0x9070 | 0x9071 | 36976 | 36977 | Average Line-to-Line Voltage | float | R | 2
| 0x9072 | 0x9073 | 36978 | 36979 | Phase A Current | float | R | 2
| 0x9074 | 0x9075 | 36980 | 36981 | Phase B Current | float | R | 2
| 0x9076 | 0x9077 | 36982 | 36983 | Phase C Current | float | R | 2
| 0x9078 | 0x9079 | 36984 | 36985 | Reserved(1320 Neutral Current) | float | R | 2
| 0x907A | 0x907B | 36986 | 36987 | Phase A Current Phase Angle | float | R | 2
| 0x907C | 0x907D | 36988 | 36989 | Phase B Current Phase Angle | float | R | 2
| 0x907E | 0x907F | 36990 | 36991 | Phase C Current Phase Angle | float | R | 2
| 0x9080 | 0x9081 | 36992 | 36993 | Reserved(1320 Neutral Current Phase Angle) | float | R | 2
| 0x9082 | 0x9083 | 36994 | 36995 | Average Current | float | R | 2
| 0x9084 | 0x9085 | 36996 | 36997 | Phase A Active Power | float | R | 2
| 0x9086 | 0x9087 | 36998 | 36999 | Phase B Active Power | float | R | 2
| 0x9088 | 0x9089 | 37000 | 37001 | Phase C Active Power | float | R | 2
| 0x908A | 0x908B | 37002 | 37003 | System Active Power | float | R | 2
| 0x908C | 0x908D | 37004 | 37005 | Phase A Reactive Power | float | R | 2
| 0x908E | 0x908F | 37006 | 37007 | Phase B Reactive Power | float | R | 2
| 0x9090 | 0x9091 | 37008 | 37009 | Phase C Reactive Power | float | R | 2
| 0x9092 | 0x9093 | 37010 | 37011 | System Reactive Power | float | R | 2
| 0x9094 | 0x9095 | 37012 | 37013 | Phase A Apparent Power | float | R | 2
| 0x9096 | 0x9097 | 37014 | 37015 | Phase B Apparent Power | float | R | 2
| 0x9098 | 0x9099 | 37016 | 37017 | Phase C Apparent Power | float | R | 2
| 0x909A | 0x909B | 37018 | 37019 | System Apparent Power | float | R | 2
| 0x909C | 0x909D | 37020 | 37021 | Phase A Power Factor | float | R | 2
| 0x909E | 0x909F | 37022 | 37023 | Phase B Power Factor | float | R | 2
| 0x90A0 | 0x90A1 | 37024 | 37025 | Phase C Power Factor | float | R | 2
| 0x90A2 | 0x90A3 | 37026 | 37027 | System Power Factor | float | R | 2

## Energy
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Energy Parameter ID | Range | Default
Energy( function code:03H)
Energy(1 second) | 0x4A00 | 0x4A01 | 18944 | 18945 | Phase A active energy import | uint32_t | R | 2 | 1
| 0x4A02 | 0x4A03 | 18946 | 18947 | Phase B active energy import | uint32_t | R | 2 | 2
| 0x4A04 | 0x4A05 | 18948 | 18949 | Phase C active energy import | uint32_t | R | 2 | 3
| 0x4A06 | 0x4A07 | 18950 | 18951 | System active energy import | uint32_t | R | 2 | 4
| 0x4A08 | 0x4A09 | 18952 | 18953 | Phase A active energy export | uint32_t | R | 2 | 5
| 0x4A0A | 0x4A0B | 18954 | 18955 | Phase B active energy export | uint32_t | R | 2 | 6
| 0x4A0C | 0x4A0D | 18956 | 18957 | Phase C active energy export | uint32_t | R | 2 | 7
| 0x4A0E | 0x4A0F | 18958 | 18959 | System active energy export | uint32_t | R | 2 | 8
| 0x4A10 | 0x4A11 | 18960 | 18961 | Phase A active energy total | uint32_t | R | 2 | 9
| 0x4A12 | 0x4A13 | 18962 | 18963 | Phase B active energy total | uint32_t | R | 2 | 10
| 0x4A14 | 0x4A15 | 18964 | 18965 | Phase C active energy total | uint32_t | R | 2 | 11
| 0x4A16 | 0x4A17 | 18966 | 18967 | System active energy total | uint32_t | R | 2 | 12
| 0x4A18 | 0x4A19 | 18968 | 18969 | Phase A active energy net | int32_t | R | 2 | 13
| 0x4A1A | 0x4A1B | 18970 | 18971 | Phase B active energy net | int32_t | R | 2 | 14
| 0x4A1C | 0x4A1D | 18972 | 18973 | Phase C active energy net | int32_t | R | 2 | 15
| 0x4A1E | 0x4A1F | 18974 | 18975 | System active energy net | int32_t | R | 2 | 16
| 0x4A20 | 0x4A21 | 18976 | 18977 | Phase A reactive energy import | uint32_t | R | 2 | 17
| 0x4A22 | 0x4A23 | 18978 | 18979 | Phase B reactive energy import | uint32_t | R | 2 | 18
| 0x4A24 | 0x4A25 | 18980 | 18981 | Phase C reactive energy import | uint32_t | R | 2 | 19
| 0x4A26 | 0x4A27 | 18982 | 18983 | System reactive energy import | uint32_t | R | 2 | 20
| 0x4A28 | 0x4A29 | 18984 | 18985 | Phase A reactive energy export | uint32_t | R | 2 | 21
| 0x4A2A | 0x4A2B | 18986 | 18987 | Phase B reactive energy export | uint32_t | R | 2 | 22
| 0x4A2C | 0x4A2D | 18988 | 18989 | Phase C reactive energy export | uint32_t | R | 2 | 23
| 0x4A2E | 0x4A2F | 18990 | 18991 | System reactive energy export | uint32_t | R | 2 | 24
| 0x4A30 | 0x4A31 | 18992 | 18993 | Phase A reactive energy total | uint32_t | R | 2 | 25
| 0x4A32 | 0x4A33 | 18994 | 18995 | Phase B reactive energy total | uint32_t | R | 2 | 26
| 0x4A34 | 0x4A35 | 18996 | 18997 | Phase C reactive energy total | uint32_t | R | 2 | 27
| 0x4A36 | 0x4A37 | 18998 | 18999 | System reactive energy total | uint32_t | R | 2 | 28
| 0x4A38 | 0x4A39 | 19000 | 19001 | Phase A reactive energy net | int32_t | R | 2 | 29
| 0x4A3A | 0x4A3B | 19002 | 19003 | Phase B reactive energy net | int32_t | R | 2 | 30
| 0x4A3C | 0x4A3D | 19004 | 19005 | Phase C reactive energy net | int32_t | R | 2 | 31
| 0x4A3E | 0x4A3F | 19006 | 19007 | System reactive energy net | int32_t | R | 2 | 32
| 0x4A40 | 0x4A41 | 19008 | 19009 | Phase A apparent energy total | uint32_t | R | 2 | 33
| 0x4A42 | 0x4A43 | 19010 | 19011 | Phase B apparent energy total | uint32_t | R | 2 | 34
| 0x4A44 | 0x4A45 | 19012 | 19013 | Phase C apparent energy total | uint32_t | R | 2 | 35
| 0x4A46 | 0x4A47 | 19014 | 19015 | System apparent energy total | uint32_t | R | 2 | 36

## Calibration
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Calibration Commands | 0x2000 | 0x2000 | 8192 | 8192 | factory calibration cmd |  | W | 1 | 0:start 1:abort
| 0x2001 | 0x2001 | 8193 | 8193 | factory calibration result | uint16_t | R | 1 | bit0:sampling frequency calibration fail bit1:current gain calibration fail bit2:acc signals calibration fail bit3:angle error calibration fail bit4: EM Save fail bit5: FRAM Save fail 0x00: calibration ok
| 0x2002 | 0x2002 | 8194 | 8194 | is calibrating | uint16_t | R | 1 | 0: Measuring 1: Calibrating
Calibration OffSet Coef（50Hz/60Hz）
| 0x2010 | 0x2011 | 8208 | 8209 | Sampling frequency | float | R | 2
| 0x2012 | 0x2013 | 8210 | 8211 | Phase a coeff of vrms | float | R | 2
| 0x2014 | 0x2015 | 8212 | 8213 | Phase a coeff of irms | float | R | 2
| 0x2016 | 0x2017 | 8214 | 8215 | Phase a coeff of active power | float | R | 2
| 0x2018 | 0x2019 | 8216 | 8217 | Phase a coeff of reactive power | float | R | 2
| 0x201A | 0x201B | 8218 | 8219 | Phase a coeff of apparent power | float | R | 2
| 0x201C | 0x201D | 8220 | 8221 | Phase b coeff of vrms | float | R | 2
| 0x201E | 0x201F | 8222 | 8223 | Phase b coeff of irms | float | R | 2
| 0x2020 | 0x2021 | 8224 | 8225 | Phase b coeff of active power | float | R | 2
| 0x2022 | 0x2023 | 8226 | 8227 | Phase b coeff of reactive power | float | R | 2
| 0x2024 | 0x2025 | 8228 | 8229 | Phase b coeff of apparent power | float | R | 2
| 0x2026 | 0x2027 | 8230 | 8231 | Phase c coeff of vrms | float | R | 2
| 0x2028 | 0x2029 | 8232 | 8233 | Phase c coeff of irms | float | R | 2
| 0x202A | 0x202B | 8234 | 8235 | Phase c coeff of active power | float | R | 2
| 0x202C | 0x202D | 8236 | 8237 | Phase c coeff of reactive power | float | R | 2
| 0x202E | 0x202F | 8238 | 8239 | Phase c coeff of apparent power | float | R | 2
| 0x2030 | 0x2031 | 8240 | 8241 | Coeff of Neutral irms | float | R | 2
| 0x2032 | 0x2033 | 8242 | 8243 | Phase a degree[0] | float | R | 2 |  |  | i phase degree
| 0x2034 | 0x2035 | 8244 | 8245 | Phase a degree[1] | float | R | 2 |  |  | i phase degree
| 0x2036 | 0x2037 | 8246 | 8247 | Phase b degree[0] | float | R | 2 |  |  | i phase degree
| 0x2038 | 0x2039 | 8248 | 8249 | Phase b degree[1] | float | R | 2 |  |  | i phase degree
| 0x203A | 0x203B | 8250 | 8251 | Phase c degree[0] | float | R | 2 |  |  | i phase degree
| 0x203C | 0x203D | 8252 | 8253 | Phase c degree[1] | float | R | 2 |  |  | i phase degree
| 0x203E | 0x203F | 8254 | 8255 | Phase a gain[0] | float | R | 2 |  |  | i gain value
| 0x2040 | 0x2041 | 8256 | 8257 | Phase a gain[1] | float | R | 2 |  |  | i gain value
| 0x2042 | 0x2043 | 8258 | 8259 | Phase b gain[0] | float | R | 2 |  |  | i gain value
| 0x2044 | 0x2045 | 8260 | 8261 | Phase b gain[1] | float | R | 2 |  |  | i gain value
| 0x2046 | 0x2047 | 8262 | 8263 | Phase c gain[0] | float | R | 2 |  |  | i gain value
| 0x2048 | 0x2049 | 8264 | 8265 | Phase c gain[1] | float | R | 2 |  |  | i gain value
| 0x204A | 0x204B | 8266 | 8267 | SDADGCR | uint32_t | R | 2 | SDADGCR [31:0] bits[ 3: 0] → CH0（V Phase a） bits[ 7: 4] → CH1（V Phase b） bits[11: 8] → CH2（V Phase c） bits[15:12] → CH3（I Phase a） bits[19:16] → CH4（I Phase b） bits[23:20] → CH5（I Phase c） bits[27:24] → CH6（I Neutral）