## Version
Version | Changes | Edit | Review | Change Date
v1.01 | Init from Acuvim II V3 Modbus address table | Shaohang Cui |  | 2022-12-26
v1.02 | Update the summary page according to the EV supporting features | HU BING |  | 2023-03-12
| Added Clear Charge Modbus address & Energy Pulse Parameter range | Sam Xu |  | 2023-05-10
| Added Network Reset | Sam Xu |  | 2023-05-24
| Updated energy and charge Modbus address to support double datatype Added firmware patch number in system info | Sam Xu |  | 2023-07-28
| Added CT21 and CT22 | Sam Xu |  | 2023-08-09
| Translated to English version Updated summary sheet | Sam Xu |  | 2023-08-10
| Updated MAC address and reserved area | Sam Xu |  | 2023-12-08
| Updated Real-time readings name | Sam Xu |  | 2024-04-05
| Added MC type address | Sam Xu |  | 2024-06-04
| Update LED pulse related Config, 0x1019 0x101A 0x1032 to 0x1034 | Haoliang Deng |  | 2024-06-20
| Add compenstaed voltages in max/min | Sam Xu |  | 2024-10-29
| Update product info with renamed format | Sam Xu |  | 2024-11-14
| Added bootloader info and firmware model name | Sam Xu |  | 2024-11-15
| Added 20ms real-time reading | Sam Xu |  | 2025-05-09

## Summary
Block Name | Section | Start | End | Length | Comment
Basic Meter Settings | Basic Configuration | 0x1000 | 0x1031 | 50
Real-Time Clock | Basic Configuration | 0x103F | 0x1045 | 7
Datalog 1, 2, 3 Settings | Datalog | 0x1100 | 0x1339 | 570
Datalog 4 Settings | Datalog | 0x1500 | 0x15B9 | 186
Real-Time Parameters (float) | Readings | 0x3000 | 0x301F | 32
Real-Time Parameters (int) | Readings | 0x3200 | 0x320F | 16
Energy and Charge (double) | Readings | 0x4000 | 0x405F | 96
Max | Max/Min | 0x4136 | 0x41B0 | 123
Min | Max/Min | 0x41E5 | 0x4234 | 80
Datalog 1, 2, 3 Reading | Datalog | 0x6000 | 0x607E | 127
Datalog 1, 2, 3 Status | Datalog | 0x6100 | 0x630B | 524
Datalog 4 Reading | Datalog | 0x6400 | 0x647E | 127
Datalog 4 Status | Datalog | 0x6500 | 0x650B | 12
Custom Reading | Basic Configuration | 0x6A00 | 0x6A27 | 40
Custom Reading Settings | Basic Configuration | 0x6B00 | 0x6B28 | 41
Firmware Version Info | System Info | 0xF000 | 0xF005 | 6
Product Info | System Info | 0xF040 | 0xF06F | 48
Calibration Commands | Calibration | 0xF204 | 0xF206 | 3
Calibration Values | Calibration | 0xF210 | 0xF218 | 9

## Basic Configuration
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | RW | Reg | RANGE | Default | Factory value | Note
Basic Meter Settings
0x1000 | 0x1000 | 4096 | 4096 | Meter password | word | R/W | 1 | 0－9999 | 0
0x1001 | 0x1001 | 4097 | 4097 | RS485 baud rate | word | R/W | 1 | 2400－115200 | 19200
0x1002 | 0x1002 | 4098 | 4098 | RS485 parity | word | R/W | 1 | 0：even 1：odd 2：Non2 3：Non1 | 0
0x1003 | 0x1003 | 4099 | 4099 | DHCP enable | word | R/W | 1 | 0: manual 1: DHCP | 0
0x1004 | 0x1004 | 4100 | 4100 | IP address 1st byte (high) IP address 2nd byte (low) | word | R/W | 1 | 0~255 |  | 192 168 1 254
0x1005 | 0x1005 | 4101 | 4101 | IP address 3rd byte (high) IP address 4th byte (low) | word | R/W | 1 | 0~255
0x1006 | 0x1006 | 4102 | 4102 | Subnet mask 1st byte (high) Subnet mask 2nd byte (low) | word | R/W | 1 | 0~255 |  | 255 255 255 0
0x1007 | 0x1007 | 4103 | 4103 | Subnet mask 3rd byte (high) Subnet mask 4th byte (low) | word | R/W | 1 | 0~255
0x1008 | 0x1008 | 4104 | 4104 | Gateway 1st byte (high) Gateway 2nd byte (low) | word | R/W | 1 | 0~255 |  | 192 168 1 1
0x1009 | 0x1009 | 4105 | 4105 | Gateway 3rd byte (high) Gateway 4th byte (low) | word | R/W | 1 | 0~255
0x100A | 0x100A | 4106 | 4106 | DNS primary server 1st byte (high) DNS primary server 2nd byte (low) | word | R/W | 1 | 0~255 |  | 8 8 8 8
0x100B | 0x100B | 4107 | 4107 | DNS primary server 3rd byte (high) DNS primary server 4th byte (low) | word | R/W | 1 | 0~255
0x100C | 0x100C | 4108 | 4108 | DNS secondary server 1st byte (high) DNS secondary server 2nd byte (low) | word | R/W | 1 | 0~255 |  | 8.8.4.4
0x100D | 0x100D | 4109 | 4109 | DNS secondary server 3rd byte (high) DNS secondary server 4th byte (low) | word | R/W | 1 | 0~255
0x100E | 0x100E | 4110 | 4110 | Modbus Slave ID | word | R/W | 1 | 1-247, used for both Modbus RTU and TCP | 1 | 1
0x100F | 0x100F | 4111 | 4111 | Modbus RTU Enable | word | R/W | 1 | 0: disable 1: enable | 1 | 1
0x1010 | 0x1010 | 4112 | 4112 | Modbus TCP Enable | word | R/W | 1 | 0: disable 1: enable | 1 | 1
0x1011 | 0x1011 | 4113 | 4113 | Modbus TCP port | word | R/W | 1 | 1-65534 | 502 | 502
0x1012 | 0x1012 | 4114 | 4114 | PT1 | word | R/W | 1 | fixed as 1000 for now | 1000
0x1013 | 0x1013 | 4115 | 4115 | PT2 | word | R/W | 1 | fixed as 1000 for now
0x1014 | 0x1014 | 4116 | 4116 | CT11 | word | R/W | 1 | 20 - 50000 A | 50
0x1015 | 0x1015 | 4117 | 4117 | CT12 | word | R/W | 1 | 0-100 (mV) | 75
0x1016 | 0x1016 | 4118 | 4118 | Demand calculation method | word | R/W | 1 | 0: Fixed block 1: Sliding block 2: Thermal 3: Rolling block | 1
0x1017 | 0x1017 | 4119 | 4119 | Demand window time | word | R/W | 1 | 1~30 | 15
0x1018 | 0x1018 | 4120 | 4120 | Demand update period | word | R/W | 1 | 1~30 | 1
0x1019 | 0x1019 | 4121 | 4121 | Energy pulse parameter | word | R/W | 1 | 0: None 1: Energy 2: Charge | 0
0x101A | 0x101A | 4122 | 4122 | Energy pulse Type | word | R/W | 1 | 0: EV_IMPORT, 1: EV_EXPORT, 2: EV_NET, // Imp - Exp 3: EV_TOTAL, // Imp + Exp | 0
0x101B | 0x101B | 4123 | 4123 | Energy reading type | word | R/W | 1 | 0: Primary 1: Secondary | 0 | 0
0x101C | 0x101C | 4124 | 4124 | Real-time reading type | word | R/W | 1 | 0: Secondary 1: Primary | 0
0x101D | 0x101D | 4125 | 4125 | Clear demand | word | R/W | 1 | 0: None 1: Clearing | 0
0x101E | 0x101E | 4126 | 4126 | Clear max/min | word | R/W | 1 | 0: None 1: Clearing | 0
0x101F | 0x101F | 4127 | 4127 | Clear device run time | word | R/W | 1 | 0: None 1: Clearing | 0
0x1020 | 0x1020 | 4128 | 4128 | Clear energy | word | R/W | 1 | 0: None 1: Clearing | 0
0x1021 | 0x1021 | 4129 | 4129 | Factory reset | word | R/W | 1 | 0: None 1: Resetting | 0
0x1022 | 0x1022 | 4130 | 4130 | Backlight time | Word | R/W | 1 | 0－120 | 0
0x1023 | 0x1023 | 4131 | 4131 | Seal status | word | R | 1 | Sealed: 0x0A | 0
0x1024 | 0x1024 | 4132 | 4132 | Device run time (high 16 bits) | word | R | 1
0x1025 | 0x1025 | 4133 | 4133 | Device run time (low 16 bits) | Word | R | 1
0x1026 | 0x1026 | 4134 | 4134 | Clear charge | word | R/W | 1 | 0: None 1: Clearing
0x1027 | 0x1027 | 4135 | 4135 | Network reset | word | R/W | 1 | 0: None 1: Resetting
0x1028 | 0x1028 | 4136 | 4136 | CT21 | word | R/W | 1 | 20 - 50000 A | 50
0x1029 | 0x1029 | 4137 | 4137 | CT22 | word | R/W | 1 | 0-100 (mV) | 75
0x102A | 0x102A | 4138 | 4138 | Device load time (high 16 bits) | word | R | 1
0x102B | 0x102B | 4139 | 4139 | Device load time (low 16 bits) | word | R | 1
0x102C | 0x102C | 4140 | 4140 | Clear load time | word | R/W | 1 | 0: None 1: Clearing | 0
0x102D | 0x102D | 4141 | 4141 | Enable cable loss compensation | word | R/W | 1 | 0: Disable 1: Enable | 0
0x102E | 0x102E | 4142 | 4142 | Cable 1 resistance (high 16 bits) | word | R/W | 1 | 0 ~ 9999999 | 0
0x102F | 0x102F | 4143 | 4143 | Cable 1 resistance (low 16 bits) | word | R/W | 1 | 0 ~ 9999999 | 0
0x1030 | 0x1030 | 4144 | 4144 | Cable 2 resistance (high 16 bits) | word | R/W | 1 | 0 ~ 9999999 | 0
0x1031 | 0x1031 | 4145 | 4145 | Cable 2 resistance (low 16 bits) | word | R/W | 1 | 0 ~ 9999999 | 0
0x1032 | 0x1033 | 4146 | 4147 | Energy pulse constant | word | R/W | 2 | 1 - 50000000 (0.0001 - 5000) | 1000000 (100) |  | # of pulse per KWh
0x1034 | 0x1034 | 4148 | 4148 | Pulse Channel ID | word | R/W | 1 | 0: Ch1 1: Ch2 2: Sum
Real-time clock
0x103F | 0x103F | 4159 | 4159 | Week | word | R/W | 1 | 1~7 | 0
0x1040 | 0x1040 | 4160 | 4160 | Year | word | R/W | 1 | 2000~2099 | 2000
0x1041 | 0x1041 | 4161 | 4161 | Month | word | R/W | 1 | 1~12 | 1
0x1042 | 0x1042 | 4162 | 4162 | Day | word | R/W | 1 | 1~31 | 1
0x1043 | 0x1043 | 4163 | 4163 | Hour | word | R/W | 1 | 0~23 | 0
0x1044 | 0x1044 | 4164 | 4164 | Minute | word | R/W | 1 | 0~59 | 0
0x1045 | 0x1045 | 4165 | 4165 | Second | word | R/W | 1 | 0~59 | 0
Custom reading settings
0x6B00 | 0x6B00 | 27392 | 27392 | Number of byte set | uint16 | R | 1 |  |  | 80
0x6B01 | 0x6B01 | 27393 | 27393 | 1st reading | uint16 | R/W | 1 |  |  | 0x3200 | V RMS
0x6B02 | 0x6B02 | 27394 | 27394 | 2nd reading | uint16 | R/W | 1 |  |  | 0x3201 | I1 RMS
0x6B03 | 0x6B03 | 27395 | 27395 | 3rd reading | uint16 | R/W | 1 |  |  | 0x3202 | I2 RMS
0x6B04 | 0x6B04 | 27396 | 27396 | 4th reading | uint16 | R/W | 1 |  |  | 0x3203 | Isum RMS
0x6B05 | 0x6B05 | 27397 | 27397 | 5th reading | uint16 | R/W | 1 |  |  | 0x3204 | P1
0x6B06 | 0x6B06 | 27398 | 27398 | 6th reading | uint16 | R/W | 1 |  |  | 0x3205 | P2
0x6B07 | 0x6B07 | 27399 | 27399 | 7th reading | uint16 | R/W | 1 |  |  | 0x3206 | Psum
0x6B08 | 0x6B08 | 27400 | 27400 | 8th reading | uint16 | R/W | 1 |  |  | 0x3207 | Ripple factor U
0x6B09 | 0x6B09 | 27401 | 27401 | 9th reading | uint16 | R/W | 1 |  |  | 0x3208 | Ripple factor I1
0x6B0A | 0x6B0A | 27402 | 27402 | 10th reading | uint16 | R/W | 1 |  |  | 0x3209 | Ripple factor I2
0x6B0B | 0x6B0B | 27403 | 27403 | 11th reading | uint16 | R/W | 1 |  |  | 0x320A | Demand I1
0x6B0C | 0x6B0C | 27404 | 27404 | 12th reading | uint16 | R/W | 1 |  |  | 0x320B | Demand I2
0x6B0D | 0x6B0D | 27405 | 27405 | 13th reading | uint16 | R/W | 1 |  |  | 0x320C | Demand Isum
0x6B0E | 0x6B0E | 27406 | 27406 | 14th reading | uint16 | R/W | 1 |  |  | 0x320D | Demand P1
0x6B0F | 0x6B0F | 27407 | 27407 | 15th reading | uint16 | R/W | 1 |  |  | 0x320E | Demand P2
0x6B10 | 0x6B10 | 27408 | 27408 | 16th reading | uint16 | R/W | 1 |  |  | 0x320F | Demand Psum
0x6B11 | 0x6B11 | 27409 | 27409 | 17th reading | uint16 | R/W | 1 |  |  | 0x4000 | Import Energy 1
0x6B12 | 0x6B12 | 27410 | 27410 | 18th reading | uint16 | R/W | 1 |  |  | 0x4001
0x6B13 | 0x6B13 | 27411 | 27411 | 19th reading | uint16 | R/W | 1 |  |  | 0x4002 | Export Energy 1
0x6B14 | 0x6B14 | 27412 | 27412 | 20th reading | uint16 | R/W | 1 |  |  | 0x4003
0x6B15 | 0x6B15 | 27413 | 27413 | 21st reading | uint16 | R/W | 1 |  |  | 0x4004 | Net Energy 1
0x6B16 | 0x6B16 | 27414 | 27414 | 22nd reading | uint16 | R/W | 1 |  |  | 0x4005
0x6B17 | 0x6B17 | 27415 | 27415 | 23rd reading | uint16 | R/W | 1 |  |  | 0x4006 | Total Energy 1
0x6B18 | 0x6B18 | 27416 | 27416 | 24th reading | uint16 | R/W | 1 |  |  | 0x4007
0x6B19 | 0x6B19 | 27417 | 27417 | 25th reading | uint16 | R/W | 1 |  |  | 0x4008 | Import Energy 2
0x6B1A | 0x6B1A | 27418 | 27418 | 26th reading | uint16 | R/W | 1 |  |  | 0x4009
0x6B1B | 0x6B1B | 27419 | 27419 | 27th reading | uint16 | R/W | 1 |  |  | 0x400A | Export Energy 2
0x6B1C | 0x6B1C | 27420 | 27420 | 28th reading | uint16 | R/W | 1 |  |  | 0x400B
0x6B1D | 0x6B1D | 27421 | 27421 | 29th reading | uint16 | R/W | 1 |  |  | 0x400C | Net Energy 2
0x6B1E | 0x6B1E | 27422 | 27422 | 30th reading | uint16 | R/W | 1 |  |  | 0x400D
0x6B1F | 0x6B1F | 27423 | 27423 | 31st reading | uint16 | R/W | 1 |  |  | 0x400E | Total Energy 2
0x6B20 | 0x6B20 | 27424 | 27424 | 32nd reading | uint16 | R/W | 1 |  |  | 0x400F
0x6B21 | 0x6B21 | 27425 | 27425 | 33rd reading | uint16 | R/W | 1 |  |  | 0x4010 | Import Energy Sum
0x6B22 | 0x6B22 | 27426 | 27426 | 34th reading | uint16 | R/W | 1 |  |  | 0x4011
0x6B23 | 0x6B23 | 27427 | 27427 | 35th reading | uint16 | R/W | 1 |  |  | 0x4012 | Export Energy Sum
0x6B24 | 0x6B24 | 27428 | 27428 | 36th reading | uint16 | R/W | 1 |  |  | 0x4013
0x6B25 | 0x6B25 | 27429 | 27429 | 37th reading | uint16 | R/W | 1 |  |  | 0x4014 | Net Energy Sum
0x6B26 | 0x6B26 | 27430 | 27430 | 38th reading | uint16 | R/W | 1 |  |  | 0x4015
0x6B27 | 0x6B27 | 27431 | 27431 | 39th reading | uint16 | R/W | 1 |  |  | 0x4016 | Total Energy Sum
0x6B28 | 0x6B28 | 27432 | 27432 | 40th reading | uint16 | R/W | 1 |  |  | 0x4017
Custom reading
0x6A00 | 0x6A00 | 27136 | 27136 | 1st reading |  | R | 1
0x6A01 | 0x6A01 | 27137 | 27137 | 2nd reading |  | R | 1
0x6A02 | 0x6A02 | 27138 | 27138 | 3rd reading |  | R | 1
0x6A03 | 0x6A03 | 27139 | 27139 | 4th reading |  | R | 1
0x6A04 | 0x6A04 | 27140 | 27140 | 5th reading |  | R | 1 |  |  | 0
0x6A05 | 0x6A05 | 27141 | 27141 | 6th reading |  | R | 1 |  |  | 0
0x6A06 | 0x6A06 | 27142 | 27142 | 7th reading |  | R | 1 |  |  | 0
0x6A07 | 0x6A07 | 27143 | 27143 | 8th reading |  | R | 1 |  |  | 0
0x6A08 | 0x6A08 | 27144 | 27144 | 9th reading |  | R | 1 |  |  | 0
0x6A09 | 0x6A09 | 27145 | 27145 | 10th reading |  | R | 1 |  |  | 0
0x6A0A | 0x6A0A | 27146 | 27146 | 11th reading |  | R | 1 |  |  | 0
0x6A0B | 0x6A0B | 27147 | 27147 | 12th reading |  | R | 1 |  |  | 0
0x6A0C | 0x6A0C | 27148 | 27148 | 13th reading |  | R | 1 |  |  | 0
0x6A0D | 0x6A0D | 27149 | 27149 | 14th reading |  | R | 1 |  |  | 0
0x6A0E | 0x6A0E | 27150 | 27150 | 15th reading |  | R | 1 |  |  | 0
0x6A0F | 0x6A0F | 27151 | 27151 | 16th reading |  | R | 1 |  |  | 0
0x6A10 | 0x6A10 | 27152 | 27152 | 17th reading |  | R | 1 |  |  | 0
0x6A11 | 0x6A11 | 27153 | 27153 | 18th reading |  | R | 1 |  |  | 0
0x6A12 | 0x6A12 | 27154 | 27154 | 19th reading |  | R | 1 |  |  | 0
0x6A13 | 0x6A13 | 27155 | 27155 | 20th reading |  | R | 1 |  |  | 0
0x6A14 | 0x6A14 | 27156 | 27156 | 21st reading |  | R | 1 |  |  | 0
0x6A15 | 0x6A15 | 27157 | 27157 | 22nd reading |  | R | 1 |  |  | 0
0x6A16 | 0x6A16 | 27158 | 27158 | 23rd reading |  | R | 1 |  |  | 0
0x6A17 | 0x6A17 | 27159 | 27159 | 24th reading |  | R | 1 |  |  | 0
0x6A18 | 0x6A18 | 27160 | 27160 | 25th reading |  | R | 1 |  |  | 0
0x6A19 | 0x6A19 | 27161 | 27161 | 26th reading |  | R | 1 |  |  | 0
0x6A1A | 0x6A1A | 27162 | 27162 | 27th reading |  | R | 1 |  |  | 0
0x6A1B | 0x6A1B | 27163 | 27163 | 28th reading |  | R | 1 |  |  | 0
0x6A1C | 0x6A1C | 27164 | 27164 | 29th reading |  | R | 1 |  |  | 0
0x6A1D | 0x6A1D | 27165 | 27165 | 30th reading |  | R | 1 |  |  | 0
0x6A1E | 0x6A1E | 27166 | 27166 | 31st reading |  | R | 1 |  |  | 0
0x6A1F | 0x6A1F | 27167 | 27167 | 32nd reading |  | R | 1 |  |  | 0
0x6A20 | 0x6A20 | 27168 | 27168 | 33rd reading |  | R | 1 |  |  | 0
0x6A21 | 0x6A21 | 27169 | 27169 | 34th reading |  | R | 1 |  |  | 0
0x6A22 | 0x6A22 | 27170 | 27170 | 35th reading |  | R | 1 |  |  | 0
0x6A23 | 0x6A23 | 27171 | 27171 | 36th reading |  | R | 1 |  |  | 0
0x6A24 | 0x6A24 | 27172 | 27172 | 37th reading |  | R | 1 |  |  | 0
0x6A25 | 0x6A25 | 27173 | 27173 | 38th reading |  | R | 1 |  |  | 0
0x6A26 | 0x6A26 | 27174 | 27174 | 39th reading |  | R | 1 |  |  | 0
0x6A27 | 0x6A27 | 27175 | 27175 | 40th reading |  | R | 1 |  |  | 0

## Calibration
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | RW | Reg | RANGE | Default | Factory value
Calibration Commands
0xF204 |  | 61956 |  | Start Calibration (0x6A write) | word | R/W | 1
0xF205 |  | 61957 |  | Query Calibration Status (0x03 read) | word | R/W | 1
0xF206 |  | 61958 |  | Exit Calibration (0x6A write） | word | R/W | 1
Calibration Values
0xF210 | 0xF211 | 61968 | 61969 | V Gain | int32 | R/W | 2
0xF212 | 0xF213 | 61970 | 61971 | V offset | int32 | R/W | 2
0xF214 | 0xF215 | 61972 | 61973 | I1 Gain | int32 | R/W | 2
0xF216 | 0xF217 | 61974 | 61975 | I1 offset | int32 | R/W | 2
0xF218 | 0xF219 | 61976 | 61977 | I2 Gain | int32 | R/W | 2
0xF21A | 0xF21B | 61978 | 61979 | I2 offset | int32 | R/W | 2

## MaxMin
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | RW | Reg | RANGE | Default | Factory value
Max
0x4136 | 0x4137 | 16694 | 16695 | V Max Value | Float32 | R | 2
0x4138 | 0x413D | 16696 | 16701 | V Max Timestamp | INT | R | 6
0x413E | 0x413F | 16702 | 16703 | I1 Max Value | Float32 | R | 2
0x4140 | 0x4145 | 16704 | 16709 | I1 Max Timestamp | INT | R | 6
0x4146 | 0x4147 | 16710 | 16711 | I2 Max Value | Float32 | R | 2
0x4148 | 0x414D | 16712 | 16717 | I2 Max Timestamp | INT | R | 6
0x414E | 0x414F | 16718 | 16719 | Isum Max Value | Float32 | R | 2
0x4150 | 0x4155 | 16720 | 16725 | Isum Max Timestamp | INT | R | 6
0x4156 | 0x4157 | 16726 | 16727 | P1 Max Value | Float32 | R | 2
0x4158 | 0x415D | 16728 | 16733 | P1 Max Timestamp | INT | R | 6
0x415E | 0x415F | 16734 | 16735 | P2 Max Value | Float32 | R | 2
0x4160 | 0x4165 | 16736 | 16741 | P2 Max Timestamp | INT | R | 6
0x4166 | 0x4167 | 16742 | 16743 | Psum Max Value | Float32 | R | 2
0x4168 | 0x416D | 16744 | 16749 | Psum Max Timestamp | INT | R | 6
0x416E | 0x416F | 16750 | 16751 | Ripple factor U Max Value | Float32 | R | 2
0x4170 | 0x4175 | 16752 | 16757 | Ripple factor U Max Timestamp | INT | R | 6
0x4176 | 0x4177 | 16758 | 16759 | Ripple factor I1 Max Value | Float32 | R | 2
0x4178 | 0x417D | 16760 | 16765 | Ripple factor I1 Max Timestamp | INT | R | 6
0x417E | 0x417F | 16766 | 16767 | Ripple factor I2 Max Value | Float32 | R | 2
0x4180 | 0x4185 | 16768 | 16773 | Ripple factor I2 Max Timestamp | INT | R | 6
0x4186 | 0x4187 | 16774 | 16775 | Demand I1 Max Value | Float32 | R | 2
0x4188 | 0x418D | 16776 | 16781 | Demand I1 Max Timestamp | INT | R | 6
0x418E | 0x418F | 16782 | 16783 | Demand I2 Max Value | Float32 | R | 2
0x4190 | 0x4195 | 16784 | 16789 | Demand I2 Max Timestamp | INT | R | 6
0x4196 | 0x4197 | 16790 | 16791 | Demand Isum Max Value | Float32 | R | 2
0x4198 | 0x419D | 16792 | 16797 | Demand Isum Max Timestamp | INT | R | 6
0x419E | 0x419F | 16798 | 16799 | Demand P1 Max Value | Float32 | R | 2
0x41A0 | 0x41A5 | 16800 | 16805 | Demand P1 Max Timestamp | INT | R | 6
0x41A6 | 0x41A7 | 16806 | 16807 | Demand P2 Max Value | Float32 | R | 2
0x41A8 | 0x41AD | 16808 | 16813 | Demand P2 Max Timestamp | INT | R | 6
0x41AE | 0x41AF | 16814 | 16815 | Demand Psum Max Value | Float32 | R | 2
0x41B0 | 0x41B5 | 16816 | 16821 | Demand Psum Max Timestamp | INT | R | 6
0x41B6 | 0x41B7 | 16822 | 16823 | V1 Compensated Max Value | Float32 | R | 2
0x41B8 | 0x41BD | 16824 | 16829 | V1 Compensated Max Timestamp | INT | R | 6
0x41BE | 0x41BF | 16830 | 16831 | V2 Compensated Max Value | Float32 | R | 2
0x41C0 | 0x41C5 | 16832 | 16837 | V2 Compensated Max Timestamp | INT | R | 6
Min
0x41E5 | 0x41E6 | 16869 | 16870 | V Min Value | Float32 | R | 2
0x41E7 | 0x41EC | 16871 | 16876 | V Min Timestamp | INT | R | 6
0x41ED | 0x41EE | 16877 | 16878 | I1 Min Value | Float32 | R | 2
0x41EF | 0x41F4 | 16879 | 16884 | I1 Min Timestamp | INT | R | 6
0x41F5 | 0x41F6 | 16885 | 16886 | I2 Min Value | Float32 | R | 2
0x41F7 | 0x41FC | 16887 | 16892 | I2 Min Timestamp | INT | R | 6
0x41FD | 0x41FE | 16893 | 16894 | Isum Min Value | Float32 | R | 2
0x41FF | 0x4204 | 16895 | 16900 | Isum Min Timestamp | INT | R | 6
0x4205 | 0x4206 | 16901 | 16902 | P1 Min Value | Float32 | R | 2
0x4207 | 0x420C | 16903 | 16908 | P1 Min Timestamp | INT | R | 6
0x420D | 0x420E | 16909 | 16910 | P2 Min Value | Float32 | R | 2
0x420F | 0x4214 | 16911 | 16916 | P2 Min Timestamp | INT | R | 6
0x4215 | 0x4216 | 16917 | 16918 | Psum Min Value | Float32 | R | 2
0x4217 | 0x421C | 16919 | 16924 | Psum Min Timestamp | INT | R | 6
0x421D | 0x421E | 16925 | 16926 | Ripple factor U Min Value | Float32 | R | 2
0x421F | 0x4224 | 16927 | 16932 | Ripple factor U Min Timestamp | INT | R | 6
0x4225 | 0x4226 | 16933 | 16934 | Ripple factor I1 Min Value | Float32 | R | 2
0x4227 | 0x422C | 16935 | 16940 | Ripple factor I1 Min Timestamp | INT | R | 6
0x422D | 0x422E | 16941 | 16942 | Ripple factor I2 Min Value | Float32 | R | 2
0x422F | 0x4234 | 16943 | 16948 | Ripple factor I2 Min Timestamp | INT | R | 6
0x4235 | 0x4236 | 16949 | 16950 | V1 Compensated Min Value | Float32 | R | 2
0x4237 | 0x423C | 16951 | 16956 | V1 Compensated Min Timestamp | INT | R | 6
0x423D | 0x423E | 16957 | 16958 | V2 Compensated Min Value | Float32 | R | 2
0x423F | 0x4244 | 16959 | 16964 | V2 Compensated Min Timestamp | INT | R | 6

## Readings
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | RW | Reg | RANGE | Default | Factory value
Real-time Parameters (float)
0x3000 | 0x3001 | 12288 | 12289 | V Measured | float32 | R | 2
0x3002 | 0x3003 | 12290 | 12291 | Current 1 | float32 | R | 2
0x3004 | 0x3005 | 12292 | 12293 | Current 2 | float32 | R | 2
0x3006 | 0x3007 | 12294 | 12295 | Current Sum | float32 | R | 2
0x3008 | 0x3009 | 12296 | 12297 | Power 1 | float32 | R | 2
0x300A | 0x300B | 12298 | 12299 | Power 2 | float32 | R | 2
0x300C | 0x300D | 12300 | 12301 | Power Sum | float32 | R | 2
0x300E | 0x300F | 12302 | 12303 | Voltage Ripple Factor | float32 | R | 2
0x3010 | 0x3011 | 12304 | 12305 | Current Ripple Factor 1 | float32 | R | 2
0x3012 | 0x3013 | 12306 | 12307 | Current Ripple Factor 2 | float32 | R | 2
0x3014 | 0x3015 | 12308 | 12309 | Demand Current 1 | float32 | R | 2
0x3016 | 0x3017 | 12310 | 12311 | Demand Current 2 | float32 | R | 2
0x3018 | 0x3019 | 12312 | 12313 | Demand Current Sum | float32 | R | 2
0x301A | 0x301B | 12314 | 12315 | Demand Power 1 | float32 | R | 2
0x301C | 0x301D | 12316 | 12317 | Demand Power 2 | float32 | R | 2
0x301E | 0x301F | 12318 | 12319 | Demand Power Sum | float32 | R | 2
0x3020 | 0x3021 | 12320 | 12321 | V1 Compensated | float32 | R | 2
0x3022 | 0x3023 | 12322 | 12323 | V2 Compensated | float32 | R | 2
Real-time Parameters (float) 20ms
0x3100 | 0x3101 | 12544 | 12545 | V Measured | float32 | R | 2
0x3102 | 0x3103 | 12546 | 12547 | Current 1 | float32 | R | 2
0x3104 | 0x3105 | 12548 | 12549 | Current 2 | float32 | R | 2
0x3106 | 0x3107 | 12550 | 12551 | Current Sum | float32 | R | 2
0x3108 | 0x3109 | 12552 | 12553 | Power 1 | float32 | R | 2
0x310A | 0x310B | 12554 | 12555 | Power 2 | float32 | R | 2
0x310C | 0x310D | 12556 | 12557 | Power Sum | float32 | R | 2
0x310E | 0x310F | 12558 | 12559 | Voltage Ripple Factor | float32 | R | 2
0x3110 | 0x3111 | 12560 | 12561 | Current Ripple Factor 1 | float32 | R | 2
0x3112 | 0x3113 | 12562 | 12563 | Current Ripple Factor 2 | float32 | R | 2
0x3114 | 0x3115 | 12564 | 12565 | Demand Current 1 | float32 | R | 2
0x3116 | 0x3117 | 12566 | 12567 | Demand Current 2 | float32 | R | 2
0x3118 | 0x3119 | 12568 | 12569 | Demand Current Sum | float32 | R | 2
0x311A | 0x311B | 12570 | 12571 | Demand Power 1 | float32 | R | 2
0x311C | 0x311D | 12572 | 12573 | Demand Power 2 | float32 | R | 2
0x311E | 0x311F | 12574 | 12575 | Demand Power Sum | float32 | R | 2
0x3120 | 0x3121 | 12576 | 12577 | V1 Compensated | float32 | R | 2
0x3122 | 0x3123 | 12578 | 12579 | V2 Compensated | float32 | R | 2
Real-time Parameters (Int)
0x3200 | 0x3200 | 12800 | 12800 | V Measured | int16 | R | 1
0x3201 | 0x3201 | 12801 | 12801 | Current 1 | int16 | R | 1
0x3202 | 0x3202 | 12802 | 12802 | Current 2 | int16 | R | 1
0x3203 | 0x3203 | 12803 | 12803 | Current Sum | int16 | R | 1
0x3204 | 0x3204 | 12804 | 12804 | Power 1 | int16 | R | 1
0x3205 | 0x3205 | 12805 | 12805 | Power 2 | int16 | R | 1
0x3206 | 0x3206 | 12806 | 12806 | Power Sum | int16 | R | 1
0x3207 | 0x3207 | 12807 | 12807 | Voltage Ripple Factor | int16 | R | 1
0x3208 | 0x3208 | 12808 | 12808 | Current Ripple Factor 1 | int16 | R | 1
0x3209 | 0x3209 | 12809 | 12809 | Current Ripple Factor 2 | int16 | R | 1
0x320A | 0x320A | 12810 | 12810 | Demand Current 1 | int16 | R | 1
0x320B | 0x320B | 12811 | 12811 | Demand Current 2 | int16 | R | 1
0x320C | 0x320C | 12812 | 12812 | Demand Current Sum | int16 | R | 1
0x320D | 0x320D | 12813 | 12813 | Demand Power 1 | int16 | R | 1
0x320E | 0x320E | 12814 | 12814 | Demand Power 2 | int16 | R | 1
0x320F | 0x320F | 12815 | 12815 | Demand Power Sum | int16 | R | 1
0x3210 | 0x3210 | 12816 | 12816 | V1 Compensated | int16 | R | 1
0x3211 | 0x3211 | 12817 | 12817 | V2 Compensated | int16 | R | 1
Energy & Charge
0x4000 | 0x4003 | 16384 | 16387 | Import Energy 1 | double | R/W | 4
0x4004 | 0x4007 | 16388 | 16391 | Export Energy 1 | double | R/W | 4
0x4008 | 0x400B | 16392 | 16395 | Net Energy 1 | double | R/W | 4
0x400C | 0x400F | 16396 | 16399 | Total Energy 1 | double | R/W | 4
0x4010 | 0x4013 | 16400 | 16403 | Import Energy 2 | double | R/W | 4
0x4014 | 0x4017 | 16404 | 16407 | Export Energy 2 | double | R/W | 4
0x4018 | 0x401B | 16408 | 16411 | Net Energy 2 | double | R/W | 4
0x401C | 0x401F | 16412 | 16415 | Total Energy 2 | double | R/W | 4
0x4020 | 0x4023 | 16416 | 16419 | Import Energy Sum | double | R/W | 4
0x4024 | 0x4027 | 16420 | 16423 | Export Energy Sum | double | R/W | 4
0x4028 | 0x402B | 16424 | 16427 | Net Energy Sum | double | R/W | 4
0x402C | 0x402F | 16428 | 16431 | Total Energy Sum | double | R/W | 4
0x4030 | 0x4033 | 16432 | 16435 | Import Charge 1 | double | R/W | 4
0x4034 | 0x4037 | 16436 | 16439 | Export Charge 1 | double | R/W | 4
0x4038 | 0x403B | 16440 | 16443 | Net Charge 1 | double | R/W | 4
0x403C | 0x403F | 16444 | 16447 | Total Charge 1 | double | R/W | 4
0x4040 | 0x4043 | 16448 | 16451 | Import Charge 2 | double | R/W | 4
0x4044 | 0x4047 | 16452 | 16455 | Export Charge 2 | double | R/W | 4
0x4048 | 0x404B | 16456 | 16459 | Net Charge 2 | double | R/W | 4
0x404C | 0x404F | 16460 | 16463 | Total Charge 2 | double | R/W | 4
0x4050 | 0x4053 | 16464 | 16467 | Import Charge Sum | double | R/W | 4
0x4054 | 0x4057 | 16468 | 16471 | Export Charge Sum | double | R/W | 4
0x4058 | 0x405B | 16472 | 16475 | Net Charge Sum | double | R/W | 4
0x405C | 0x405F | 16476 | 16479 | Total Charge Sum | double | R/W | 4

## System Info
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | Reg | RW | RANGE | Default | Factory value
Firmware Version Info
0xF000 | 0xF001 | 61440 | 61441 | Firmware version |  | 2 | R | ASCII, in format of x.yz (e.g., 1.01) | determined by firmware | determined by firmware
0xF002 | 0xF004 | 61442 | 61444 | Firmware release date |  | 3 | R | ASCII, in format of YYMMDD (221228) | determined by firmware | determined by firmware
0xF005 | 0xF005 | 61445 | 61445 | Firmware patch number |  | 1 | R | ASCII, in format of xy (01) | determined by firmware | determined by firmware
0xF006 | 0xF006 | 61446 | 61446 | Firmware Model Name |  | 1 |  | ASCII, in format of XYZa (e.g. DCE1) | determined by firmware | determined by firmware
Bootloader Info
0xF010 | 0xF011 | 61456 | 61457 | Bootloader Model Name |  | 2 | R | ASCII, in format of XYab (e.g. FP00) | determined by bootloader | determined by bootloader
0xF012 | 0xF014 | 61458 | 61460 | Bootloader Hardware and Software Name |  | 3 | R | ASCII, in format of xyzxyz (e.g. 101101) | determined by bootloader | determined by bootloader
0xF015 | 0xF016 | 61461 | 61462 | Bootloader Release Date |  | 2 | R | ASCII, in format of YYMMDD (e.g. 241108) | determined by bootloader | determined by bootloader
Product Info
0xF040 | 0xF04F | 61504 | 61519 | Serial Number |  | 16 | RW | In the format like DCEYYMMabcd (e.g., DCE22120001) |  |  | use 0x6A to write; 0x3 to read
0xF050 | 0xF051 | 61520 | 61521 | Hardware version |  | 2 | RW | In the format like x.yz (e.g., 1.01) | 1.01 | 1.01 | use 0x6A to write; 0x3 to read
0xF052 | 0xF052 | 61522 | 61522 | Function Model Type |  | 1 | RW | 0: AcuDC-261 | 0 | 0 | use 0x6A to write; 0x3 to read
0xF053 | 0xF053 | 61523 | 61523 | Voltage Input Type |  | 1 | RW | 0: 1000V | 0 | 0 | use 0x6A to write; 0x3 to read
0xF054 | 0xF054 | 61524 | 61524 | Current Input Type |  | 1 | RW | 0: A1 (shunt) 1: A2 (0 to 20mA Hall sensor) 2: A3 (-5V to 5V Hall sensor) 3: A4 (External MID Shunt) | 0 | 0 | use 0x6A to write; 0x3 to read
0xF055 | 0xF055 | 61525 | 61525 | Power Supply Type |  | 1 | RW | 1 for P2 | 1 | 1 | use 0x6A to write; 0x3 to read
0xF056 | 0xF065 | 61526 | 61541 | MAC address |  | 16 | RW |  |  |  | use 0x6A to write; 0x3 to read
0xF066 | 0xF066 | 61542 | 61542 | Certificate Type |  | 1 | RW | 0: None; 1: MID | 0 | 0 | use 0x6A to write; 0x3 to read
0xF067 | 0xF067 | 61543 | 61543 | External Shunt Type |  | 1 | RW | 0: None; 400: 400A; 600: 600A | 0 | 0 | use 0x6A to write; 0x3 to read
0xF068 | 0xF06F | 61544 | 61551 | Reserved |  | 8 | RW |  |  |  | use 0x6A to write; 0x3 to read

## Datalog
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Descrption | Data type | RW | Reg | RANGE | Default | Factory value
Datalog 1, 2, 3 setting
0x1100 |  | 4352 |  | Log1 #Registers # Sectors |  | R/W | 1
0x1101 |  | 4353 |  | Log1 Interval |  | R/W | 1
0x1102 | 0x1176 | 4354 | 4470 | Log1 register #1-#117 identifier |  | R/W | 117
0x1177 | 0x11B1 | 4471 | 4529 | Log1 register #1-#117 descriptors |  | R/W | 59 | Currently not used
0x11B2 |  | 4530 |  | Datalog mode selection |  | R/W | 1
0x11B3 |  | 4531 |  | Start month, year |  | R/W | 1
0x11B4 |  | 4532 |  | Start day, hour |  | R/W | 1
0x11B5 |  | 4533 |  | Start minute, second |  | R/W | 1
0x11B6 |  | 4534 |  | End month, year |  | R/W | 1
0x11B7 |  | 4535 |  | End day, hour |  | R/W | 1
0x11B8 |  | 4536 |  | End minute, second |  | R/W | 1
0x11B9 |  | 4537 |  | Clear Data Log 1 |  | R/W | 1
0x11C0 | 0x1279 | 4544 | 4729 | Log2 setting |  | R/W | 186
0x1280 | 0x1339 | 4736 | 4921 | Log3 setting |  | R/W | 186
Datalog 1, 2, 3 reading
0x6000 |  | 24576 |  | Record type, enable, state |  | R/W | 1
0x6001 |  | 24577 |  | Record # of each window +window state |  | R/W | 1
0x6002 | 0x6003 | 24578 | 24579 | OFFSET |  | R/W | 2
0x6004 | 0x607E | 24580 | 24702 | Window |  | R | 123
Datalog 1, 2, 3 status
0x6100 | 0x6101 | 24832 | 24833 | Max Records | uint32 | R | 2
0x6102 | 0x6103 | 24834 | 24835 | Used Records | uint32 | R | 2
0x6104 |  | 24836 |  | Recordsize | uint16 | R | 1
0x6105 |  | 24837 |  | Log Availability | uint16 | R | 1
0x6106 | 0x6108 | 24838 | 24840 | First Record Timestamp | word | R | 3
0x6109 | 0x610B | 24841 | 24843 | Last Record Timestamp | word | R | 3
0x6200 | 0x6201 | 25088 | 25089 | Max Records | uint32 | R | 2
0x6202 | 0x6203 | 25090 | 25091 | Used Records | uint32 |  | 2
0x6204 | 0x0000 | 25092 |  | Recordsize | uint16 | R | 1
0x6205 | 0x0000 | 25093 |  | Log Availability | uint16 | R | 1
0x6206 | 0x6208 | 25094 | 25096 | FirstRecordTimestamp | word | R | 3
0x6209 | 0x620B | 25097 | 25099 | LastRecordTimestamp, | word | R | 3
0x6300 | 0x6301 | 25344 | 25345 | Max Records | uint32 | R | 2
0x6302 | 0x6303 | 25346 | 25347 | Used Records | uint32 | R | 2
0x6304 |  | 25348 |  | Recordsize | uint16 | R | 1
0x6305 |  | 25349 |  | Log Availability | uint16 | R | 1
0x6306 | 0x6308 | 25350 | 25352 | FirstRecordTimestamp | word | R | 3
0x6309 | 0x630B | 25353 | 25355 | LastRecordTimestamp, | word | R | 3
Datalog 4 setting
0x1500 |  | 5376 |  | Log4 #Registers # Sectors |  | R/W | 1 | 0 -39；50 | 0 | 0
0x1501 |  | 5377 |  | Log4 Interval |  | R/W | 1 | 1 - 1440 | 0 | 0
0x1502 | 0x1576 | 5378 | 5494 | Log4 register #1-#117 identifier |  | R/W | 117 | Parameter selection address range: 0x3000 - 0x3013 | 0 | 0
0x1577 | 0x15B1 | 5495 | 5553 | Log4 register #1-#117 descriptors |  | R/W | 59 | 0 - 2 | 0 | 0
0x15B2 |  | 5554 |  | Datalog mode selection |  | R/W | 1 | 0 - 2 | 0 | 0
0x15B3 |  | 5555 |  | Start month, year |  | R/W | 1 | Low byte: month,high byte: year (keep consistence with Data Log123)
0x15B4 |  | 5556 |  | Start day, hour |  | R/W | 1 | Low byte: hour, high byte: day
0x15B5 |  | 5557 |  | Start minute, second |  | R/W | 1 | Low byte: second, high byte: minute
0x15B6 |  | 5558 |  | End month, year |  | R/W | 1 | Low byte: month, high byte: year
0x15B7 |  | 5559 |  | End day, hour |  | R/W | 1 | Low byte: hour, high byte: day
0x15B8 |  | 5560 |  | End minute, second |  | R/W | 1 | Low byte: second, high byte: minute
0x15B9 |  | 5561 |  | Clear Data Log 4 |  | R/W | 1 | write 1 to clear | 0 | 0
Datalog 4 reading
0x6400 |  | 25600 |  | Record type, enable, state |  | R/W | 1 | 0 - 3 （3 for Data Log4） | 0 | 0
0x6401 |  | 25601 |  | Record number of each window +window state |  | R/W | 1 | High byte: Record number of window (setting) Low byte: window state (0x0B: data effective,0xFF: data not effective,0xAA: Data Log on clearing,0xBB: Data Log clearing end)
0x6402 | 0x6403 | 25602 | 25603 | OFFSET |  | R/W | 2
0x6404 | 0x647E | 25604 | 25726 | Window |  | R | 123 | Data Log format: record number (4bytes)+ time stamps (6bytes) + [data1~dataN] (6Nbytes) + CRC (2bytes) Data format: parameter1 average value, parameter2 average value...parameter1 max value, parameter2 max value, parameter1 min value, parameter2 min value...
Datalog 4 status
0x6500 | 0x6501 | 25856 | 25857 | Max Records | uint32 | R | 2 | 0 - 468104
0x6502 | 0x6503 | 25858 | 25859 | Used Records | uint32 | R | 2 | 1 - 468104
0x6504 |  | 25860 |  | Recordsize | uint16 | R | 1 | 18 - 714
0x6505 |  | 25861 |  | Log Availability（reserve） | word | R | 1
0x6506 | 0x6508 | 25862 | 25864 | First Record Time stamp | word | R | 3
0x6509 | 0x650B | 25865 | 25867 | Last Record Time stamp | word | R | 3
note: max records of Data Log4 = 65536 / (number of register * 6 + 12) * sector number (fixed to 50 at present)