## Version history
Version | Changes | Author | Date | Internal Firmware Version | External Firmware Version
v1.01 | 初次定义 1.根据需求规格书定义 | tanghui | 2025-07-10 | v1.01p01
| 1、修改TOU Reading数据格式 2、调整TOU Setting和MaxMin地址 | tanghui | 2025-10-27 | v1.01p01
| 根据IIV3重新修改地址表 | tanghui | 2025-11-24 | v1.01p01
| Basic Setting添加Ethernet Communication Mode、UTC寄存器 | tanghui | 2025-11-27 | v1.01p01
| (1) [timestamp format] changed in [DataPost] Sheet | Wang Shaoying | 2025-12-17 | v1.01p02
| 删除独立通道无效数据 | tanghui | 2025-12-17 | v1.01p02
| Basic Settin中UTC名字更新为Time zone shift，修改参数范围 | tanghui | 2025-12-17 | v1.01p02
| 删除独立通道INT16数据类型 | tanghui | 2025-12-17 | v1.01p02
| 删除Metrology Settings中Voltage selection | tanghui | 2025-12-17 | v1.01p02
| Maxmin数据结构参考IIV3修改 | liuhongbo | 2025-12-22 | v1.01p02
| Operations中添加Clear System Log 和Clear Audit Log | tanghui | 2025-12-23 | v1.01p02
| Maxmin增加Sumation 1 Power Factor和Sumation 2 Power Factor | liuhongbo | 2026-01-06 | v1.01p02
| 添加ParaMeter Sync（Dual CPU） Sheet | tanghui | 2026-01-12 | v1.01p02
| 修改Dual Source Energy switching records协议，添加“Total number recorded”寄存器 | YangYue | 2026-01-12 | v1.01p02
| Add [Last Post time] for [Datalog Post] and [AcuCloud log] | Wang Shaoying | 2026-01-19 | v1.01p02
| Dual Source Records添加 The first index of records to read | tanghui | 2026-01-21 | v1.01p02
| 添加Time synchronization period&Time synchronization status到System Setting | Li Yong | 2026-01-23 | v1.01p02
| 修改时间同步参数与时间同步状态定义 | Li Yong | 2026-01-28 | v1.01p02
| 1、添加realtime和Energy_1s 2、删除独立通道sheet，重新调整HS、200ms、3s、10min、2hr中参数和地址 3、删除Class S PQ Event enable | tanghui | 2026-02-25 | v1.01p04
| （1）Update [Log Post Interval] in [Datalog Post] sheet: range is changed to 1~43200 in minutes. (2) [RTC] is changed to [Local Time] in [Timestamp Format] in [Datalog Post] sheet. (3)[UTC TimeStamp] is changed to [Unix timestamp] in [Log File Name time format] in [Datalog Post] sheet | Wang Shaoying | 2026-02-27 | v1.01p04
| 1、Basic Setting 添加 Bacnet IP Setting 2、haimonics修改为1-64 | tanghui | 2026-02-28 | v1.01p04
| Add [Test AcuCloud] in [AcuCloud Post] sheet | Wang Shaoying | 2026-03-02 | v1.01p04
| In the sheet"Data log And Trend log" Update the range of register 0x8001. | Wang Peigong | 2026-03-05 | v1.01p04
| Add [Test Datalog Post] in [DataLog Post] sheet | Wang Shaoying | 2026-03-11 | v1.01p04
| 修改Custom Reading参数地址，修改Tou MaxDemand数据地址 | tanghui | 2026-03-13 | v1.01p04
| 修改PT1和PT2的默认值为480 | tanghui | 2026-03-30 | v1.01p05
| 删除RS485波特率2400和4800 | tanghui | 2026-02-04 | v1.01p06
| 修改SNTP时间同参数范围 | tanghui | 2026-03-04 | v1.01p06
| 修改PT2范围最大值为830 | tanghui | 2026-04-09 | v1.01p06
| Acucloud Status和Datalog Post Status添加Post Fail File Timestamp | tanghui | 2026-04-14 | v1.01p06
| Datalog Post 添加Reading Window | tanghui | 2026-04-17 | v1.01p06
| Datalog Post 删除post interval 寄存器，调整为reserve | tanghui | 2026-04-29 | v1.01p08

## Overview
Block | Sector | Sheet | Start(Hex) | End(Hex) | Length(reg num) | Comments
Basic Settings | System、Communication、Time Settings | Basic Settings | 0x1000 | 0x1039 | 58
| Metrology Settings | Basic Settings | 0x1040 | 0x1070 | 49
| Io Settings | Basic Settings | 0x1100 | 0x110B | 12
| Operations | Basic Settings | 0x1130 | 0x114A | 27
| Independent Input Channel settings | Basic Settings | 0x1200 | 0x1206 | 7
| Bacnet IP Setting | Basic Settings | 0x1400 | 0x140B | 12
Demand | Demand | Demand | 0x2200 | 0x2231 | 50
10S Freq | 10S Freq | 10S Freq | 0x2300 | 0x2307 | 8
Real Time | Real time basic parameters（100ms) | Real Time | 0x3000 | 0x303A | 60
| Real time basic parameters（Integer） | Real Time | 0x3200 | 0x3226 | 39
| Real time Basic parameters（20ms） | Real Time | 0x3400 | 0x341D | 30
| Real time basic parameters（1S） | Real Time | 0x4000 | 0x4047 | 72
| Energy （1S） | Real Time | 0x4048 | 0x4059 | 18
| Harmonics - THD（3S） | Real Time | 0x405A | 0x412A | 209
| Sequence | Real Time | 0x4294 | 0x429F | 12
| Phase Angle | Real Time | 0x42A0 | 0x42A4 | 5
| Reserve | Real Time | 0x45F0 | 0x45F1 | 2
| Current demand | Real Time | 0x4600 | 0x4605 | 6
| Energy - continue（1S） | Real Time | 0x4620 | 0x463D | 30
Energy（1S） | Energy | Energy（1S） | 0x4A00 | 0x4A6B | 108
| Quadrant Energy | Energy（1S） | 0x4A6C | 0x4AFB | 144
Dual Source Energy | Dual Source Energy Settings | Dual Source Energy | 0x5000 | 0x5005 | 6
| Dual Source Energy Readings | Dual Source Energy | 0x5050 | 0x505B | 12
| Dual Source Energy switching records | Dual Source Energy | 0x5100 | 0x5159 | 90
MaxMin | Max value record | MaxMin | 0x5300 | 0x5407 | 264
| Min value record | MaxMin | 0x5600 | 0x5707 | 264
Max Demand | Max Demand | Max Demand | 0x5900 | 0x596D | 125
TOU Default Settings | TOU factory basic default settings | TOU Default Settings | 0x5C00 | 0x5C10 | 17
| TOU schedule & season & holiday setting | TOU Default Settings | 0x5C11 | 0x5EDD | 717
| 10years holidy factory default settings | TOU Default Settings | 0x5EDE | 0x5F73 | 150
TOU Settings | Daylight Savings Time Settings | TOU setting | 0x6000 | 0x6001 | 2
| Format 1: Fixed Date | TOU setting | 0x6002 | 0x600B | 10
| Format 2: Non Fixed Date | TOU setting | 0x600C | 0x6017 | 12
| TOU basic Setting | TOU setting | 0x6018 | 0x6025 | 14
| Season Settings | TOU setting | 0x6026 | 0x6049 | 36
| Schedule Settings | TOU setting | 0x604A | 0x6295 | 588
| Holiday Settings | TOU setting | 0x6296 | 0x62F2 | 93
| 10 Years Holiday Settings | TOU setting | 0x62F3 | 0x668A | 920
| Special Weekday Schedule Settings | TOU setting | 0x668B | 0x66EB | 97
TOU Readings | Current Month Accumulative TOU Energy | TOU Readings | 0x6700 | 0x6731 | 50
| Previous Month Accumulative TOU Energy | TOU Readings | 0x6732 | 0x6763 | 50
| Current Month Incremental TOU Energy | TOU Readings | 0x6764 | 0x6795 | 50
| Previous Month Incremental TOU Energy | TOU Readings | 0x6796 | 0x67C7 | 50
| Current Month TOU Max Demand | TOU Readings | 0x6800 | 0x68C7 | 50
| Previous Month TOU Max Demand | TOU Readings | 0x68C8 | 0x698F | 50
| TOU OverFlow flag | TOU Readings | 0x69FE | 0x69FF | 2
Custom settings and Readings | User defined reading area | Custom settings and Readings | 0x6A00 | 0x6A7d | 125
| Custom read settings | Custom settings and Readings | 0x6B00 | 0x6BCB | 126
Alarm Record ¦DI¦SOE | Alarm Setting | Alarm Record ¦DI¦SOE | 0x7000 | 0x7141 | 322
| Alarm Log Read | Alarm Record ¦DI¦SOE | 0x7300 | 0x737E | 127
| SOE Log Read | Alarm Record ¦DI¦SOE | 0x7400 | 0x747C | 125
| DI | Alarm Record ¦DI¦SOE | 0x7600 | 0x7605 | 6
| Custom Reading DI Status | DI Status | 0x7620 | 0x7623 | 3
| Datalog Post Reading Window | Datalog Post | 0x7800 | 0x787E | 127
Waveform¦PQ Event | Power Quality Event setting | Waveform¦PQ Event | 0x7A07 | 0x7A20 | 32
| Waveform record parameter setting | Waveform¦PQ Event | 0x7C00 | 0x7C06 | 7
| Waveform Reading Window | Waveform¦PQ Event | 0x7E00 | 0x7E7D | 126
| PQ Event Record Reading Window | Waveform¦PQ Event | 0x7F00 | 0x7F7D | 126
Data log And Trend log | Data log Setting | Data log And Trend log | 0x8000 | 0x84DB | 1244
| Data log Reading Window | Data log And Trend log | 0x8500 | 0x857E | 127
| Data log Status Reading | Data log And Trend log | 0x8600 | 0x864F | 80
| DataLog Sector | Data log And Trend log | 0x8700 | 0x8713 | 20
System Log | SystemLog Status | System Log | 0x8800 | 0x8803 | 4
| SystemLog Reading | System Log | 0x8810 | 0x8814 | 124
Audit Log | SystemLog Status | Audit Log | 0x8900 | 0x8903 | 4
| SystemLog Reading | Audit Log | 0x8910 | 0x898B | 124
Acucloud log | Acucloud Log Setting | Acucloud log | 0x8A00 | 0x8ADD | 222
| Acucloud Log Reading Window | Acucloud log | 0x8AE0 | 0x8B5D | 126
| Acucloud Log Status Reading | Acucloud log | 0x8B90 | 0x8B96 | 7
| Status Reading | Acucloud log | 0x8B97 | 0x8BA1 | 11
| Test AcuCloud | Acucloud log | 0x8BB0 | 0x8BB2 | 3
Datalog Post | DatalogPost Setting | Datalog Post | 0x8C00 | 0x8C1A | 27
| http setting | Datalog Post | 0x8C20 | 0x8D1F | 256
| https setting | Datalog Post | 0x8D40 | 0x8EBC | 381
| MQTT setting | Datalog Post | 0x8F00 | 0x901F | 288
| Datalog Post Status | Datalog Post | 0x9025 | 0x9031 | 13
| Test Datalog Post | Datalog Post | 0x9040 | 0x9042 | 3
HS | RMS、Unbalance V、Unbalance I (1 Cycle) | HS_20ms | 0x9050 | 0x90E1 | 146
| Energy(1 Cycle) | Energy_20ms | 0x90E2 | 0x914D | 108
| Moving Average Parameters (1 Cycle) | Moving Average 20ms | 0x9200 | 0x9291 | 146
200ms | RMS(10、12 cycle) | 200ms | 0x9300 | 0x937C | 125
| Unbalance V(10、12 cycle) | 200ms | 0x937D | 0x938C | 16
| Unbalance I(10、12 cycle) | 200ms | 0x938D | 0x939C | 16
| Harmonic V(10、12 cycle) | 200ms | 0x93DC | 0x9876 | 1179
| Harmonic I(10、12 cycle) | 200ms | 0x9877 | 0x9EA8 | 1586
3s Aggreation | RMS(150、180 cycle) | 3S Aggregation | 0x9F22 | 0x9F9E | 125
| Unbalance V(150、180 cycle) | 3S Aggregation | 0x9F9F | 0x9FAE | 16
| Unbalance I(150、180 cycle) | 3S Aggregation | 0x9FAF | 0x9FBE | 16
| Harmonic V(150、180 cycle) | 3S Aggregation | 0x9FFE | 0xA498 | 1179
| Harmonic I(150、180 cycle) | 3S Aggregation | 0xA499 | 0xAACA | 1586
| Flicker Pinst Max | 3S Aggregation | 0xAACB | 0xAAD0 | 6
10min Aggreation | RMS(10 min) | 10min Aggregation | 0xAB50 | 0xABCC | 125
| Unbalance V(10 min) | 10min Aggregation | 0xABCD | 0xABDC | 16
| Unbalance I(10 min) | 10min Aggregation | 0xABDD | 0xABEC | 16
| Harmonic V(10 min) | 10min Aggregation | 0xAC2C | 0xB0C6 | 1179
| Harmonic I(10 min) | 10min Aggregation | 0xB0C7 | 0xB6F8 | 1586
| Flicker Pinst Max(10 min) | 10min Aggregation | 0xB6F9 | 0xB6FE | 6
2hr Aggreation | RMS(2hr) | 2hr Aggregation | 0xB77E | 0xB7FA | 125
| Unbalance V(2hr) | 2hr Aggregation | 0xB7FB | 0xB80A | 16
| Unbalance I(2hr) | 2hr Aggregation | 0xB80B | 0xB81A | 16
| Harmonic V(2hr) | 2hr Aggregation | 0xB85A | 0xBCF4 | 1179
| Harmonic I(2hr) | 2hr Aggregation | 0xBCF5 | 0xC326 | 1586
| Flicker Pinst Max(2hr) | 2hr Aggregation | 0xC327 | 0xC32C | 6
Information | Firmware Version Info | Information | 0xF000 | 0xF005 | 6
| Bootloader Info | Information | 0xF010 | 0xF017 | 8
| Product Info | Information | 0xF040 | 0xF090 | 82
Calibration | Calibration Commands | Calibration | 0xF204 | 0xF219 | 22
| Calibration OffSet Coef | Calibration | 0xF250 | 0xF25D | 14
| GainCoef(V A/B/C) | Calibration | 0xF25E | 0xF263 | 6
| GainCoef(mA、 mV CT、RCT) | Calibration | 0xF264 | 0xF26B | 8
| PhaseCoef(50Hz、60Hz) | Calibration | 0xF26C | 0xF279 | 14
ParaMeter Sync（Dual CPU） | Parameter Sync | ParaMeter Sync（Dual CPU） | 0xFF00 | 0xFF02 | 3
DI Status | DI Status | DI Status | 0x0000 | 0x0002 | 3
DO | DO Status | DO Status | 0x0000 | 0x0000 | 1

## Basic Setting
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
System Setting
Communication | 0x1000 | 0x1000 | 4096 | 4096 | Password | uint16_t | R/W | 1 | 0-9999 | 0
| 0x1001 | 0x1001 | 4097 | 4097 | Baud Rate | uint16_t | R/W | 1 | 9600\19200\38400\57600\76800\115200(76800 need send 7680 115200need send 11520) | 19200
| 0x1002 | 0x1002 | 4098 | 4098 | Parity | uint16_t | R/W | 1 | 0: even 1: odd 2: None2 3: None1 | 3: None1
| 0x1003 | 0x1003 | 4099 | 4099 | Ethernet Communication Mode | uint16_t | R/W | 1 | 0:RSTP Enable 1:Dual ETH (No RSTP) /*RSTP Disable ,ETH1 Enable,ETH2 Enable*/ 2:Single ETH (No RSTP) /*RSTP Disable ,ETH1 Enable,ETH2 Disable*/
| 0x1004 | 0x1004 | 4100 | 4100 | DHCP enable | uint16_t | R/W | 1 | 0: manual 1: DHCP | 0
| 0x1005 | 0x1005 | 4101 | 4101 | IP address 1st byte IP address 2nd byte | uint8_t | R/W | 1 | 0~255 | 192 168 1 254
| 0x1006 | 0x1006 | 4102 | 4102 | IP address 3rd byte IP address 4th byte | uint8_t | R/W | 1 | 0~255
| 0x1007 | 0x1007 | 4103 | 4103 | Subnet mask 1st byte Subnet mask 2nd byte | uint8_t | R/W | 1 | 0~255 | 255 255 255 0
| 0x1008 | 0x1008 | 4104 | 4104 | Subnet mask 3rd byte Subnet mask 4th byte | uint8_t | R/W | 1 | 0~255
| 0x1009 | 0x1009 | 4105 | 4105 | Gateway 1st byte Gateway 2nd byte | uint8_t | R/W | 1 | 0~255 | 192 168 1 1
| 0x100A | 0x100A | 4106 | 4106 | Gateway 3rd byte Gateway 4th byte | uint8_t | R/W | 1 | 0~255
| 0x100B | 0x100B | 4107 | 4107 | DNS primary server 1st byte DNS primary server 2nd byte | uint8_t | R/W | 1 | 0~255 | 8 8 8 8
| 0x100C | 0x100C | 4108 | 4108 | DNS primary server 3rd byte DNS primary server 4th byte | uint8_t | R/W | 1 | 0~255
| 0x100D | 0x100D | 4109 | 4109 | DNS secondary server 1st byte DNS secondary server 2nd byte | uint8_t | R/W | 1 | 0~255 | 8.8.4.4
| 0x100E | 0x100E | 4110 | 4110 | DNS secondary server 3rd byte DNS secondary server 4th byte | uint8_t | R/W | 1 | 0~255
| 0x100F | 0x100F | 4111 | 4111 | Modbus Slave ID | uint16_t | R/W | 1 | 1-247, used for both Modbus RTU and TCP | 1
| 0x1010 | 0x1010 | 4112 | 4112 | RS485 protocol | uint16_t | R/W | 1 | 0: disable 1: Modbus RTU 2: BACnet MS/TP | 1
| 0x1011 | 0x1011 | 4113 | 4113 | Modbus TCP Enable | uint16_t | R/W | 1 | 0: disable 1: enable | 1
| 0x1012 | 0x1012 | 4114 | 4114 | Modbus TCP port | uint16_t | R/W | 1 | 1-65534 | 502
| 0x1013 | 0x1013 | 4115 | 4115 | BACnet MS/TP Meter address | uint16_t | R/W | 1 | 0 - 127 | 1
| 0x1014 | 0x1014 | 4116 | 4116 | BACnet MS/TP Maximum number of message frames | uint16_t | R/W | 1 | 1 - 255 | 255
| 0x1015 | 0x1016 | 4117 | 4118 | BACnet MS/TP ID | uint32_t | R/W | 2 | 0 ~ 4194302 | 1
| 0x1017 | 0x1017 | 4119 | 4119 | BACnet Database Revision | uint16_t | R | 1 | 0 - 65535(0xFFFF) | 0
| 0x1018 | 0x1018 | 4120 | 4120 | LCD Backlight Time | uint16_t | R/W | 1 | 0-120 minute | 1
| 0x1019 | 0x101A | 4121 | 4122 | Device run time | uint32_t | R/W | 2 | uint in second | 0
| 0x101B | 0x101C | 4123 | 4124 | Device load time | uint32_t | R/W | 2 | uint in second | 0
| 0x101D | 0x101D | 4125 | 4125 | Non-standard Seal Parameter Select | uint16_t | R/W | 1 | bit0-4 (0 :NON bit0:RS485 Setting bit1:Ethernet Setting bit2: protocol Setting bit3:Clear Loadtime bit4: Clear Runtime) | 0
| 0x101E | 0x101E | 4126 | 4126 | Time Zone | int16_t | R/W | 1 | -720~840 | 0
| 0x101F | 0x101F | 4127 | 4127 | Week | uint16_t | R/W | 1 | 1~7 | 1
| 0x1020 | 0x1020 | 4128 | 4128 | Year | uint16_t | R/W | 1 | 2000~2099 | 2024
| 0x1021 | 0x1021 | 4129 | 4129 | Month | uint16_t | R/W | 1 | 1~12 | 1
| 0x1022 | 0x1022 | 4130 | 4130 | Day | uint16_t | R/W | 1 | 1~31 | 1
| 0x1023 | 0x1023 | 4131 | 4131 | Hour | uint16_t | R/W | 1 | 0~23 | 0
| 0x1024 | 0x1024 | 4132 | 4132 | Minute | uint16_t | R/W | 1 | 0~59 | 0
| 0x1025 | 0x1025 | 4133 | 4133 | Second | uint16_t | R/W | 1 | 0~59 | 0
| 0x1026 | 0x1026 | 4134 | 4134 | millisecond | uint16_t | R/W | 1 | 0-999 | 0
| 0x1027 | 0x1027 | 4135 | 4135 | MeterTempPassword | uint16_t | R | 1 | 0~9999 | 0
| 0x1028 | 0x1028 | 4136 | 4136 | Time synchronization status | uint16_t | R | 1 | 0~1,0:Not synchronized;1：Synchronized | 0
| 0x1029 | 0x102A | 4137 | 4138 | Time synchronization period(uint:second) | uint32_t | R/W | 2 | 0,3600~604800.0:disable,3600~604800:enable | 0
| 0x102B | 0x1039 | 4139 | 4153 | Device Description | uint8_t | R/W | 15 | ASCII string, 30 bytes (15 registers), padded with 0x00
58
Metrology Settings
| 0x1040 | 0x1040 | 4160 | 4160 | Sealing Status | uint16_t | R | 1 | sealed: 0x0A unsealed: 0
| 0x1041 | 0x1041 | 4161 | 4161 | Frequency Selection | uint16_t | R/W | 1 | 0: 50Hz 1: 60Hz | 1
| 0x1042 | 0x1042 | 4162 | 4162 | Service Configuration | uint16_t | R/W | 1 | 0: ELEMENT_1_WIRE_2 1: ELEMENT_2_WIRE_3_PHASE_1 2: ELEMENT_2_WIRE_3_DELTA 3: ELEMENT_2_WIRE_3_NETWORK 4: ELEMENT_3_WIRE_4_Y 5：ELEMENT_3_WIRE_4_DELTA | 4
| 0x1043 | 0x1044 | 4163 | 4164 | PT1 | uint32_t | R/W | 2 | 50-1000000 | 480
| 0x1045 | 0x1045 | 4165 | 4165 | PT2 | uint16_t | R/W | 1 | 50-830 | 480
| 0x1046 | 0x1046 | 4166 | 4166 | In Method | uint16_t | R/W | 1 | Calculated: 0 Measured: 1 | 0
| 0x1047 | 0x1047 | 4167 | 4167 | channel 1 input wiring ID | uint16_t | R/W | 1 | 1~4 | 1
| 0x1048 | 0x1048 | 4168 | 4168 | channel 1 Current Direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1049 | 0x1049 | 4169 | 4169 | channel 1 input CT Type | uint16_t | R/W | 1 | 0:positive 1:negative | 0: 100mA for mA type 2: 333mV for mV type
| 0x104A | 0x104A | 4170 | 4170 | channel 1 input CT Primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x104B | 0x104B | 4171 | 4171 | channel 2 input wiring ID | uint16_t | R/W | 1 | 1~4 | 2
| 0x104C | 0x104C | 4172 | 4172 | channel 2 Current Direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x104D | 0x104D | 4173 | 4173 | channel 2 input CT Type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x104E | 0x104E | 4174 | 4174 | channel 2 input CT Primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x104F | 0x104F | 4175 | 4175 | channel 3 input wiring ID | uint16_t | R/W | 1 | 1~4 | 3
| 0x1050 | 0x1050 | 4176 | 4176 | channel 3 Current Direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1051 | 0x1051 | 4177 | 4177 | channel 3 input CT Type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1052 | 0x1052 | 4178 | 4178 | channel 3 input CT Primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1053 | 0x1053 | 4179 | 4179 | channel 4 input wiring ID | uint16_t | R/W | 1 | 1~4 | 4
| 0x1054 | 0x1054 | 4180 | 4180 | channel 4 Current Direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1055 | 0x1055 | 4181 | 4181 | channel 4 input CT Type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1056 | 0x1056 | 4182 | 4182 | channel 4 input CT Primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1057 | 0x1057 | 4183 | 4183 | Reactive Power Calculation Method | uint16_t | R/W | 1 | General: 0 True: 1 | 0
| 0x1058 | 0x1058 | 4184 | 4184 | PF Convention | uint16_t | R/W | 1 | PF Format IEC: 0 PF Format IEEE: 1 | 0
| 0x1059 | 0x1059 | 4185 | 4185 | Demand Algorithm | uint16_t | R/W | 1 | Fixed Window: 0 Sliding Window: 1 | 1
| 0x105A | 0x105A | 4186 | 4186 | Demand Interval | uint16_t | R/W | 1 | 1~30 minute | 15
| 0x105B | 0x105B | 4187 | 4187 | Demand Update Interval | uint16_t | R/W | 1 | 1~30 minute | 1
| 0x105C | 0x105C | 4188 | 4188 | MaxDemand Clear Mode | uint16_t | R/W | 1 | 0：Manual Mode 1：Automatic Mode 2：Disable | 0
| 0x105D | 0x105E | 4189 | 4190 | MaxDemand Clear Date Setting | uint8_t | R/W | 2 | ( day:uint8_t , hour:uint8_t, min:uint8_t , sec: uint8_t) | 0
| 0x105F | 0x105F | 4191 | 4191 | MaxDemand Clear Total Count | uint16_t | R | 1 | 0-65535 | 0
| 0x1060 | 0x1062 | 4192 | 4194 | Timestamp of the most recent MaxDemand Clear | uint8_t | R | 3 | (year：uint8_t、month：uint8_t、day:uint8_t、hour:uint8_t、min:uint8_t、sec：uint8_t) | 0
| 0x1063 | 0x1063 | 4195 | 4195 | Phase Order | uint16_t | R/W | 1 | ABC: 0 ACB: 1 | 0
| 0x1064 | 0x1064 | 4196 | 4196 | Energy Reading Display format | uint16_t | R/W | 1 | 0: Primary in 0.1 kWh;1:0.01kWh; 2: Primary in 0.001kWh | 0
| 0x1065 | 0x1065 | 4197 | 4197 | Energy Calculation Method | uint16_t | R/W | 1 | Generic: 0 Fundamental: 1 | 1
| 0x1066 | 0x1067 | 4198 | 4199 | Energy pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000
| 0x1068 | 0x1068 | 4200 | 4200 | Pulse LED width | uint16_t | R/W | 1 | 20~100ms | 100
| 0x1069 | 0x1069 | 4201 | 4201 | Pulse LED parameter selection | uint16_t | R/W | 1 | Energy parameter IDs(1-54) | 0 not in use
| 0x106A | 0x106A | 4202 | 4202 | Flicker Settings | uint16_t | R/W | 1 | 0: Disable 1: Automatic 2:120V-50Hz-60W Incandescent 3:230V-50Hz-60W Incandescent 4:120V-60Hz-60W Incandescent 5:230V-60Hz-60W Incandescent | 0
| 0x106B | 0x106B | 4203 | 4203 | Harmonic Group Setting | uint16_t | R/W | 1 | 0: Harmonic group 1: Harmonic subgroup | 0
| 0x106C | 0x106C | 4204 | 4204 | Harmonic/Inter-harmonic Setting | uint16_t | R/W | 1 | 0: Harmonic 1:Harmonic & Inter-harmonic | 0
| 0x106D | 0x106D | 4205 | 4205 | moving average window length(cycle) | uint16_t | R/W | 1 | 20 | 1
| 0x106E | 0x106E | 4206 | 4206 | moving average update rate(cycle) | uint16_t | R/W | 1 | 1—10/12 | 1
| 0x106F | 0x106F | 4207 | 4207 | Main-signalling target frequence | uint16_t | R/W | 1 | 1—500 | 50
| 0x1070 | 0x1070 | 4208 | 4208 | Main-signalling target magnitude | uint16_t | R/W | 1 | 1—300 | 120
49
IO Settings
| 0x1100 | 0x1100 | 4352 | 4352 | DO1 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication 2:Manual Control | 0
| 0x1101 | 0x1101 | 4353 | 4353 | DO1 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100
| 0x1102 | 0x1102 | 4354 | 4354 | DO1 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use
| 0x1103 | 0x1103 | 4355 | 4355 | DI1 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0
| 0x1104 | 0x1105 | 4356 | 4357 | DI1 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000
| 0x1106 | 0x1106 | 4358 | 4358 | DI2 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0
| 0x1107 | 0x1108 | 4359 | 4360 | DI2 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000
| 0x1109 | 0x1109 | 4361 | 4361 | DI3 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0
| 0x110A | 0x110B | 4362 | 4363 | DI3 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000
12
Operations | 0x1130 | 0x1130 | 4400 | 4400 | Clear energy | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1131 | 0x1131 | 4401 | 4401 | Clear Max demand | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1132 | 0x1132 | 4402 | 4402 | Clear MaxDemand ClearCount and Timestamp | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1133 | 0x1133 | 4403 | 4403 | Clear max/min | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1134 | 0x1134 | 4404 | 4404 | Clear device run time | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1135 | 0x1135 | 4405 | 4405 | Clear load time | uint16_t | R/W | 1 | 0: None 1: Reset | 0
| 0x1136 | 0x1136 | 4406 | 4406 | Factory reset | uint16_t | R/W | 1 | 0: None 1: Resetting | 0
| 0x1137 | 0x1137 | 4407 | 4407 | Network reset | uint16_t | R/W | 1 | 0: None 1: Resetting | 0
| 0x1138 | 0x1138 | 4408 | 4408 | Clear SOE Log | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1139 | 0x1139 | 4409 | 4409 | Clear alarm Log | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x113A | 0x113A | 4410 | 4410 | Clear PQ event Log | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x113B | 0x113B | 4411 | 4411 | Clear Waveform | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x113C | 0x113C | 4412 | 4412 | Clear Data Log1 | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x113D | 0x113D | 4413 | 4413 | Clear Data Log2 | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x113E | 0x113E | 4414 | 4414 | Clear Data Log3 | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x113F | 0x113F | 4415 | 4415 | Clear Trend Log | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1140 | 0x1140 | 4416 | 4416 | Clear DI Count | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1141 | 0x1141 | 4417 | 4417 | Clear Year 10 Holiday Number Setting | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1142 | 0x1142 | 4418 | 4418 | Restore TOU factory setting | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1143 | 0x1143 | 4419 | 4419 | Clear TOU Energy | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1144 | 0x1144 | 4420 | 4420 | Clear TOU Max Demand | uint16_t | R/W | 1 | 0: None 1: Clearing
| 0x1145 | 0x1145 | 4421 | 4421 | Clear Dual Source energy | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1146 | 0x1146 | 4422 | 4422 | Clear Dual Source energy switching record | uint16_t | R/W | 1 | 0: None 1: Clearing | 0
| 0x1147 | 0x1147 | 4423 | 4423 | Device Reboot | uint16_t | R/W | 1 | 0: None 1: Reset | 0
| 0x1148 | 0x1148 | 4424 | 4424 | Clear System Log | uint16_t | R/W | 1 | 0: None 1: Reset
| 0x1149 | 0x1149 | 4425 | 4425 | Clear Audit Log | uint16_t | R/W | 1 | 0: None 1: Reset
| 0x114A | 0x114A | 4426 | 4426 | Clear AcuCloud Log | uint16_t | R/W | 1 | 0: None 1: Reset
27
Independent Input Channel settings
| 0x1200 | 0x1200 | 4608 | 4608 | Enable Independent Input Channel | uint16_t | R/W | 1 | 0: disable; 1: enable | 0
| 0x1201 | 0x1201 | 4609 | 4609 | I1 power calculation Voltage selection | uint16_t | R/W | 1 | 0: disable 1: Va 2: Vb 3: Vc 4: Vab 5: Vbc 6: Vca | 0
| 0x1202 | 0x1202 | 4610 | 4610 | I2 power calculation Voltage selection | uint16_t | R/W | 1 | 0: disable 1: Va 2: Vb 3: Vc 4: Vab 5: Vbc 6: Vca | 0
| 0x1203 | 0x1203 | 4611 | 4611 | I3 power calculation Voltage selection | uint16_t | R/W | 1 | 0: disable 1: Va 2: Vb 3: Vc 4: Vab 5: Vbc 6: Vca | 0
| 0x1204 | 0x1204 | 4612 | 4612 | I4 power calculation Voltage selection | uint16_t | R/W | 1 | 0: disable 1: Va 2: Vb 3: Vc 4: Vab 5: Vbc 6: Vca | 0
| 0x1205 | 0x1205 | 4613 | 4613 | Summation 1 channel config | uint16_t | R/W | 1 | Bit0-3 for current input channel 1-4 (I1-I4) | 7
| 0x1206 | 0x1206 | 4614 | 4614 | Summation 2 channel config | uint16_t | R/W | 1 | Bit0-3 for current input channel 1-4 (I1-I4) | 0
7
Bacnet IP Setting
| 0x1400 | 0x1400 | 5120 | 5120 | Bacnet IP Enable | uint16_t | R/W | 1 | 0:Disable 1:Enable | 0
| 0x1401 | 0x1401 | 5121 | 5121 | UDP Port | uint16_t | R/W | 1 | 1-65535 | 47808
| 0x1402 | 0x1402 | 5122 | 5122 | Network Number | uint16_t | R/W | 1 | 0-65534 | 1
| 0x1403 | 0x1404 | 5123 | 5124 | Device Instance | uint32_t | R/W | 2 | 0-4194302 | 1
| 0x1405 | 0x1405 | 5125 | 5125 | Advertised APDU Timeout | uint16_t | R/W | 1 | 100-65535(ms) | 60000
| 0x1406 | 0x1406 | 5126 | 5126 | Advertised APDU Retries | uint16_t | R/W | 1 | 0-255 | 3
| 0x1407 | 0x1407 | 5127 | 5127 | Foreign Device Enable | uint16_t | R/W | 1 | 0:Disable 1:Enable | 0
| 0x1408 | 0x1409 | 5128 | 5129 | Foreign Device IP Address | uint8_t | R/W | 2 | 0~255 | 0
| 0x140A | 0x140A | 5130 | 5130 | Foreign Device UDP Port | uint16_t | R/W | 1 | 1-65535 | 47808
| 0x140B | 0x140B | 5131 | 5131 | Foreign Device Registration Time to Live | uint16_t | R/W | 1 | 0-65535(s) | 3600
12
SNTP Setting
| 0x1460 | 0x1460 | 5216 | 5216 | SNTP Enable | uint16_t | R/W | 1 | 0:Disable 1:Enable | 0
| 0x1461 | 0x14A0 | 5217 | 5280 | Server URL | uint8_t | R/W | 64 |  | 0
| 0x14A1 | 0x14A2 | 5281 | 5282 | Network Synchronization Interval | uint32_t | R/W | 2 | 60-4294967(s) | 300

## HS_20ms
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data Type | RW | Reg Num | Range | Default
RMS(1 Cycle) | 0x9050 | 0x9053 | 36944 | 36947 | HS Param Update Time Stamp | uint64_t | R | 4
| 0x9054 | 0x9055 | 36948 | 36949 | System Frequency | float | R | 2
| 0x9056 | 0x9057 | 36950 | 36951 | Phase A Line-to-Neutral Voltage | float | R | 2
| 0x9058 | 0x9059 | 36952 | 36953 | Phase B Line-to-Neutral Voltage | float | R | 2
| 0x905A | 0x905B | 36954 | 36955 | Phase C Line-to-Neutral Voltage | float | R | 2
| 0x905C | 0x905D | 36956 | 36957 | Phase A Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x905E | 0x905F | 36958 | 36959 | Phase B Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x9060 | 0x9061 | 36960 | 36961 | Phase C Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x9062 | 0x9063 | 36962 | 36963 | Average Line-to-Neutral Voltage | float | R | 2
| 0x9064 | 0x9065 | 36964 | 36965 | Phase AB Line-to-Line Voltage | float | R | 2
| 0x9066 | 0x9067 | 36966 | 36967 | Phase BC Line-to-Line Voltage | float | R | 2
| 0x9068 | 0x9069 | 36968 | 36969 | Phase CA Line-to-Line Voltage | float | R | 2
| 0x906A | 0x906B | 36970 | 36971 | Phase AB Line-to-Line Voltage Phase Angle | float | R | 2
| 0x906C | 0x906D | 36972 | 36973 | Phase BC Line-to-Line Voltage Phase Angle | float | R | 2
| 0x906E | 0x906F | 36974 | 36975 | Phase CA Line-to-Line Voltage Phase Angle | float | R | 2
| 0x9070 | 0x9071 | 36976 | 36977 | Average Line-to-Line Voltage | float | R | 2
| 0x9072 | 0x9073 | 36978 | 36979 | Phase A Current | float | R | 2
| 0x9074 | 0x9075 | 36980 | 36981 | Phase B Current | float | R | 2
| 0x9076 | 0x9077 | 36982 | 36983 | Phase C Current | float | R | 2
| 0x9078 | 0x9079 | 36984 | 36985 | Neutral Current | float | R | 2
| 0x907A | 0x907B | 36986 | 36987 | Phase A Current Phase Angle | float | R | 2
| 0x907C | 0x907D | 36988 | 36989 | Phase B Current Phase Angle | float | R | 2
| 0x907E | 0x907F | 36990 | 36991 | Phase C Current Phase Angle | float | R | 2
| 0x9080 | 0x9081 | 36992 | 36993 | Neutral Current Phase Angle | float | R | 2
| 0x9082 | 0x9083 | 36994 | 36995 | Average Current | float | R | 2
| 0x9084 | 0x9085 | 36996 | 36997 | Phase A Active Power | float | R | 2
| 0x9086 | 0x9087 | 36998 | 36999 | Phase B Active Power | float | R | 2
| 0x9088 | 0x9089 | 37000 | 37001 | Phase C Active Power | float | R | 2
| 0x908A | 0x908B | 37002 | 37003 | System Active Power | float | R | 2
| 0x908C | 0x908D | 37004 | 37005 | Phase A Reactive Power | float | R | 2
| 0x908E | 0x908F | 37006 | 37007 | Phase B Reactive Power | float | R | 2
| 0x9090 | 0x9091 | 37008 | 37009 | Phase C Reactive Power | float | R | 2
| 0x9092 | 0x9093 | 37010 | 37011 | System Reactive Power | float | R | 2
| 0x9094 | 0x9095 | 37012 | 37013 | Phase A Apparent Power | float | R | 2
| 0x9096 | 0x9097 | 37014 | 37015 | Phase B Apparent Power | float | R | 2
| 0x9098 | 0x9099 | 37016 | 37017 | Phase C Apparent Power | float | R | 2
| 0x909A | 0x909B | 37018 | 37019 | System Apparent Power | float | R | 2
| 0x909C | 0x909D | 37020 | 37021 | Phase A Power Factor | float | R | 2
| 0x909E | 0x909F | 37022 | 37023 | Phase B Power Factor | float | R | 2
| 0x90A0 | 0x90A1 | 37024 | 37025 | Phase C Power Factor | float | R | 2
| 0x90A2 | 0x90A3 | 37026 | 37027 | System Power Factor | float | R | 2
| 0x90A4 | 0x90A5 | 37028 | 37029 | Phase A Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
| 0x90A6 | 0x90A7 | 37030 | 37031 | Phase B Load Nature | uint32_t | R | 2
| 0x90A8 | 0x90A9 | 37032 | 37033 | Phase C Load Nature | uint32_t | R | 2
| 0x90AA | 0x90AB | 37034 | 37035 | System Load Nature | uint32_t | R | 2
| 0x90AC | 0x90AD | 37036 | 37037 | Channel 4 Active Power | float | R | 2
| 0x90AE | 0x90AF | 37038 | 37039 | Channel 4 Reactive Power | float | R | 2
| 0x90B0 | 0x90B1 | 37040 | 37041 | Channel 4 Apparent Power | float | R | 2
| 0x90B2 | 0x90B3 | 37042 | 37043 | Channel 4 Power Factor | float | R | 2
| 0x90B4 | 0x90B5 | 37044 | 37045 | Channel 4 Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
| 0x90B6 | 0x90B7 | 37046 | 37047 | Summation 2 Average Current | float | R | 2
| 0x90B8 | 0x90B9 | 37048 | 37049 | Summation 2 Active Power | float | R | 2
| 0x90BA | 0x90BB | 37050 | 37051 | Summation 2 Reactive Power | float | R | 2
| 0x90BC | 0x90BD | 37052 | 37053 | Summation 2 Apparent Power | float | R | 2
| 0x90BE | 0x90BF | 37054 | 37055 | Summation 2 Power Factor | float | R | 2
| 0x90C0 | 0x90C1 | 37056 | 37057 | Summation 2 Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
Unbalance V(1 Cycle) | 0x90C2 | 0x90C3 | 37058 | 37059 | Voltage Unbalance Negative | float | R | 2
| 0x90C4 | 0x90C5 | 37060 | 37061 | Voltage Unbalance Zero | float | R | 2
| 0x90C6 | 0x90C7 | 37062 | 37063 | Voltage Zero Sequnece Real Part | float | R | 2
| 0x90C8 | 0x90C9 | 37064 | 37065 | Voltage Zero Sequence Imaginary Part | float | R | 2
| 0x90CA | 0x90CB | 37066 | 37067 | Voltage Positive Sequence Real Part | float | R | 2
| 0x90CC | 0x90CD | 37068 | 37069 | Voltage Positive Sequence Imaginary Part | float | R | 2
| 0x90CE | 0x90CF | 37070 | 37071 | Voltage Negative Sequence Real Part | float | R | 2
| 0x90D0 | 0x90D1 | 37072 | 37073 | Voltage Negative Sequence Imaginary Part | float | R | 2
Unbalance I(1 Cycle) | 0x90D2 | 0x90D3 | 37074 | 37075 | Current Unbalance Negative | float | R | 2
| 0x90D4 | 0x90D5 | 37076 | 37077 | Current Unbalance Zero | float | R | 2
| 0x90D6 | 0x90D7 | 37078 | 37079 | Current Zero Sequnece Real Part | float | R | 2
| 0x90D8 | 0x90D9 | 37080 | 37081 | Current Zero Sequence Imaginary Part | float | R | 2
| 0x90DA | 0x90DB | 37082 | 37083 | Current Positive Sequence Real Part | float | R | 2
| 0x90DC | 0x90DD | 37084 | 37085 | Current Positive Sequence Imaginary Part | float | R | 2
| 0x90DE | 0x90DF | 37086 | 37087 | Current Negative Sequence Real Part | float | R | 2
| 0x90E0 | 0x90E1 | 37088 | 37089 | Current Negative Sequence Imaginary Part | float | R | 2
146

## Energy_20ms
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Energy parameter ID | Range | Default
Energy(1 Cycle) | 0x90E2 | 0x90E3 | 37090 | 37091 | Phase A active energy import | uint32_t | R | 2 | 1
| 0x90E4 | 0x90E5 | 37092 | 37093 | Phase B active energy import | uint32_t | R | 2 | 2
| 0x90E6 | 0x90E7 | 37094 | 37095 | Phase C active energy import | uint32_t | R | 2 | 3
| 0x90E8 | 0x90E9 | 37096 | 37097 | System active energy import | uint32_t | R | 2 | 4
| 0x90EA | 0x90EB | 37098 | 37099 | Phase A active energy export | uint32_t | R | 2 | 5
| 0x90EC | 0x90ED | 37100 | 37101 | Phase B active energy export | uint32_t | R | 2 | 6
| 0x90EE | 0x90EF | 37102 | 37103 | Phase C active energy export | uint32_t | R | 2 | 7
| 0x90F0 | 0x90F1 | 37104 | 37105 | System active energy export | uint32_t | R | 2 | 8
| 0x90F2 | 0x90F3 | 37106 | 37107 | Phase A active energy total | uint32_t | R | 2 | 9
| 0x90F4 | 0x90F5 | 37108 | 37109 | Phase B active energy total | uint32_t | R | 2 | 10
| 0x90F6 | 0x90F7 | 37110 | 37111 | Phase C active energy total | uint32_t | R | 2 | 11
| 0x90F8 | 0x90F9 | 37112 | 37113 | System active energy total | uint32_t | R | 2 | 12
| 0x90FA | 0x90FB | 37114 | 37115 | Phase A active energy net | int32_t | R | 2 | 13
| 0x90FC | 0x90FD | 37116 | 37117 | Phase B active energy net | int32_t | R | 2 | 14
| 0x90FE | 0x90FF | 37118 | 37119 | Phase C active energy net | int32_t | R | 2 | 15
| 0x9100 | 0x9101 | 37120 | 37121 | System active energy net | int32_t | R | 2 | 16
| 0x9102 | 0x9103 | 37122 | 37123 | Phase A reactive energy import | uint32_t | R | 2 | 17
| 0x9104 | 0x9105 | 37124 | 37125 | Phase B reactive energy import | uint32_t | R | 2 | 18
| 0x9106 | 0x9107 | 37126 | 37127 | Phase C reactive energy import | uint32_t | R | 2 | 19
| 0x9108 | 0x9109 | 37128 | 37129 | System reactive energy import | uint32_t | R | 2 | 20
| 0x910A | 0x910B | 37130 | 37131 | Phase A reactive energy export | uint32_t | R | 2 | 21
| 0x910C | 0x910D | 37132 | 37133 | Phase B reactive energy export | uint32_t | R | 2 | 22
| 0x910E | 0x910F | 37134 | 37135 | Phase C reactive energy export | uint32_t | R | 2 | 23
| 0x9110 | 0x9111 | 37136 | 37137 | System reactive energy export | uint32_t | R | 2 | 24
| 0x9112 | 0x9113 | 37138 | 37139 | Phase A reactive energy total | uint32_t | R | 2 | 25
| 0x9114 | 0x9115 | 37140 | 37141 | Phase B reactive energy total | uint32_t | R | 2 | 26
| 0x9116 | 0x9117 | 37142 | 37143 | Phase C reactive energy total | uint32_t | R | 2 | 27
| 0x9118 | 0x9119 | 37144 | 37145 | System reactive energy total | uint32_t | R | 2 | 28
| 0x911A | 0x911B | 37146 | 37147 | Phase A reactive energy net | int32_t | R | 2 | 29
| 0x911C | 0x911D | 37148 | 37149 | Phase B reactive energy net | int32_t | R | 2 | 30
| 0x911E | 0x911F | 37150 | 37151 | Phase C reactive energy net | int32_t | R | 2 | 31
| 0x9120 | 0x9121 | 37152 | 37153 | System reactive energy net | int32_t | R | 2 | 32
| 0x9122 | 0x9123 | 37154 | 37155 | Phase A apparent energy total | uint32_t | R | 2 | 33
| 0x9124 | 0x9125 | 37156 | 37157 | Phase B apparent energy total | uint32_t | R | 2 | 34
| 0x9126 | 0x9127 | 37158 | 37159 | Phase C apparent energy total | uint32_t | R | 2 | 35
| 0x9128 | 0x9129 | 37160 | 37161 | System apparent energy total | uint32_t | R | 2 | 36
| 0x912A | 0x912B | 37162 | 37163 | Channel 4 active energy import | uint32_t | R | 2 | 37
| 0x912C | 0x912D | 37164 | 37165 | Channel 4 active energy export | uint32_t | R | 2 | 38
| 0x912E | 0x912F | 37166 | 37167 | Channel 4 active energy total | uint32_t | R | 2 | 39
| 0x9130 | 0x9131 | 37168 | 37169 | Channel 4 active energy net | int32_t | R | 2 | 40
| 0x9132 | 0x9133 | 37170 | 37171 | Channel 4 reactive energy import | uint32_t | R | 2 | 41
| 0x9134 | 0x9135 | 37172 | 37173 | Channel 4 reactive energy export | uint32_t | R | 2 | 42
| 0x9136 | 0x9137 | 37174 | 37175 | Channel 4 reactive energy total | uint32_t | R | 2 | 43
| 0x9138 | 0x9139 | 37176 | 37177 | Channel 4 reactive energy net | int32_t | R | 2 | 44
| 0x913A | 0x913B | 37178 | 37179 | Channel 4 apparent energy total | uint32_t | R | 2 | 45
| 0x913C | 0x913D | 37180 | 37181 | Summation 2 active energy import | uint32_t | R | 2 | 46
| 0x913E | 0x913F | 37182 | 37183 | Summation 2 active energy export | uint32_t | R | 2 | 47
| 0x9140 | 0x9141 | 37184 | 37185 | Summation 2 active energy total | uint32_t | R | 2 | 48
| 0x9142 | 0x9143 | 37186 | 37187 | Summation 2 active energy net | int32_t | R | 2 | 49
| 0x9144 | 0x9145 | 37188 | 37189 | Summation 2 reactive energy import | uint32_t | R | 2 | 50
| 0x9146 | 0x9147 | 37190 | 37191 | Summation 2 reactive energy export | uint32_t | R | 2 | 51
| 0x9148 | 0x9149 | 37192 | 37193 | Summation 2 reactive energy total | uint32_t | R | 2 | 52
| 0x914A | 0x914B | 37194 | 37195 | Summation 2 reactive energy net | int32_t | R | 2 | 53
| 0x914C | 0x914D | 37196 | 37197 | Summation 2 apparent energy total | uint32_t | R | 2 | 54
108

## Real Time
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Real time basic parameters（100ms)
| 0x3000 | 0x3001 | 12288 | 12289 | System Frequency | float | R | 2
| 0x3002 | 0x3003 | 12290 | 12291 | Phase A Line-to-Neutral Voltage | float | R | 2
| 0x3004 | 0x3005 | 12292 | 12293 | Phase B Line-to-Neutral Voltage | float | R | 2
| 0x3006 | 0x3007 | 12294 | 12295 | Phase C Line-to-Neutral Voltage | float | R | 2
| 0x3008 | 0x3009 | 12296 | 12297 | Average Line-to-Neutral Voltage | float | R | 2
| 0x300A | 0x300B | 12298 | 12299 | Phase AB Line-to-Line Voltage | float | R | 2
| 0x300C | 0x300D | 12300 | 12301 | Phase BC Line-to-Line Voltage | float | R | 2
| 0x300E | 0x300F | 12302 | 12303 | Phase CA Line-to-Line Voltage | float | R | 2
| 0x3010 | 0x3011 | 12304 | 12305 | Average Line-to-Line Voltage | float | R | 2
| 0x3012 | 0x3013 | 12306 | 12307 | Phase A Current | float | R | 2
| 0x3014 | 0x3015 | 12308 | 12309 | Phase B Current | float | R | 2
| 0x3016 | 0x3017 | 12310 | 12311 | Phase C Current | float | R | 2
| 0x3018 | 0x3019 | 12312 | 12313 | Average Current | float | R | 2
| 0x301A | 0x301B | 12314 | 12315 | Neutral Current | float | R | 2
| 0x301C | 0x301D | 12316 | 12317 | Phase A Active Power | float | R | 2
| 0x301E | 0x301F | 12318 | 12319 | Phase B Active Power | float | R | 2
| 0x3020 | 0x3021 | 12320 | 12321 | Phase C Active Power | float | R | 2
| 0x3022 | 0x3023 | 12322 | 12323 | System Active Power | float | R | 2
| 0x3024 | 0x3025 | 12324 | 12325 | Phase A Reactive Power | float | R | 2
| 0x3026 | 0x3027 | 12326 | 12327 | Phase B Reactive Power | float | R | 2
| 0x3028 | 0x3029 | 12328 | 12329 | Phase C Reactive Power | float | R | 2
| 0x302A | 0x302B | 12330 | 12331 | System Reactive Power | float | R | 2
| 0x302C | 0x302D | 12332 | 12333 | Phase A Apparent Power | float | R | 2
| 0x302E | 0x302F | 12334 | 12335 | Phase B Apparent Power | float | R | 2
| 0x3030 | 0x3031 | 12336 | 12337 | Phase C Apparent Power | float | R | 2
| 0x3032 | 0x3033 | 12338 | 12339 | System Apparent Power | float | R | 2
| 0x3034 | 0x3035 | 12340 | 12341 | Phase A Power Factor | float | R | 2
| 0x3036 | 0x3037 | 12342 | 12343 | Phase B Power Factor | float | R | 2
| 0x3038 | 0x3039 | 12344 | 12345 | Phase C Power Factor | float | R | 2
| 0x303A | 0x303B | 12346 | 12347 | System Power Factor | float | R | 2
60
Real time basic parameters（Integer）
| 0x3200 | 0x3200 | 12800 | 12800 | System Frequency | int16_t | R | 1 |  | two decimal
| 0x3201 | 0x3201 | 12801 | 12801 | Phase A Line-to-Neutral Voltage | int16_t | R | 1 |  | one decimal
| 0x3202 | 0x3202 | 12802 | 12802 | Phase B Line-to-Neutral Voltage | int16_t | R | 1 |  | one decimal
| 0x3203 | 0x3203 | 12803 | 12803 | Phase C Line-to-Neutral Voltage | int16_t | R | 1 |  | one decimal
| 0x3204 | 0x3204 | 12804 | 12804 | Average Line-to-Neutral Voltage | int16_t | R | 1 |  | one decimal
| 0x3205 | 0x3205 | 12805 | 12805 | Phase AB Line-to-Line Voltage | int16_t | R | 1 |  | one decimal
| 0x3206 | 0x3206 | 12806 | 12806 | Phase BC Line-to-Line Voltage | int16_t | R | 1 |  | one decimal
| 0x3207 | 0x3207 | 12807 | 12807 | Phase CA Line-to-Line Voltage | int16_t | R | 1 |  | one decimal
| 0x3208 | 0x3208 | 12808 | 12808 | Average Line-to-Line Voltage | int16_t | R | 1 |  | one decimal
| 0x3209 | 0x3209 | 12809 | 12809 | Phase A Current | int16_t | R | 1 |  | three decimal
| 0x320A | 0x320A | 12810 | 12810 | Phase B Current | int16_t | R | 1 |  | three decimal
| 0x320B | 0x320B | 12811 | 12811 | Phase C Current | int16_t | R | 1 |  | three decimal
| 0x320C | 0x320C | 12812 | 12812 | Average Current | int16_t | R | 1 |  | three decimal
| 0x320D | 0x320D | 12813 | 12813 | Neutral Current | int16_t | R | 1 |  | three decimal
| 0x320E | 0x320E | 12814 | 12814 | Phase A Active Power | int16_t | R | 1 |  | truncation
| 0x320F | 0x320F | 12815 | 12815 | Phase B Active Power | int16_t | R | 1 |  | truncation
| 0x3210 | 0x3210 | 12816 | 12816 | Phase C Active Power | int16_t | R | 1 |  | truncation
| 0x3211 | 0x3211 | 12817 | 12817 | System Active Power | int16_t | R | 1 |  | truncation
| 0x3212 | 0x3212 | 12818 | 12818 | Phase A Reactive Power | int16_t | R | 1 |  | truncation
| 0x3213 | 0x3213 | 12819 | 12819 | Phase B Reactive Power | int16_t | R | 1 |  | truncation
| 0x3214 | 0x3214 | 12820 | 12820 | Phase C Reactive Power | int16_t | R | 1 |  | truncation
| 0x3215 | 0x3215 | 12821 | 12821 | System Reactive Power | int16_t | R | 1 |  | truncation
| 0x3216 | 0x3216 | 12822 | 12822 | Phase A Apparent Power | int16_t | R | 1 |  | truncation
| 0x3217 | 0x3217 | 12823 | 12823 | Phase B Apparent Power | int16_t | R | 1 |  | truncation
| 0x3218 | 0x3218 | 12824 | 12824 | Phase C Apparent Power | int16_t | R | 1 |  | truncation
| 0x3219 | 0x3219 | 12825 | 12825 | System Apparent Power | int16_t | R | 1 |  | truncation
| 0x321A | 0x321A | 12826 | 12826 | Phase A Power Factor | int16_t | R | 1 |  | three decimal
| 0x321B | 0x321B | 12827 | 12827 | Phase B Power Factor | int16_t | R | 1 |  | three decimal
| 0x321C | 0x321C | 12828 | 12828 | Phase C Power Factor | int16_t | R | 1 |  | three decimal
| 0x321D | 0x321D | 12829 | 12829 | System Power Factor | int16_t | R | 1 |  | three decimal
| 0x321E | 0x321E | 12830 | 12830 | Voltage Unbalance Negative | int16_t | R | 1 |  | three decimal
| 0x321F | 0x321F | 12831 | 12831 | Current Unbalance Negative | int16_t | R | 1 |  | three decimal
| 0x3220 | 0x3220 | 12832 | 12832 | System Load Nature | int16_t | R | 1 | 82:Resistive load 76:Inductive load 67:Capacitive load
| 0x3221 | 0x3221 | 12833 | 12833 | System Active Power Demand | int16_t | R | 1 |  | truncation
| 0x3222 | 0x3222 | 12834 | 12834 | System Reactive Power Demand | int16_t | R | 1 |  | truncation
| 0x3223 | 0x3223 | 12835 | 12835 | System Apparent Power Demand | int16_t | R | 1 |  | truncation
| 0x3224 | 0x3224 | 12836 | 12836 | Phase A Current Demand | int16_t | R | 1 |  | three decimal
| 0x3225 | 0x3225 | 12837 | 12837 | Phase B Current Demand | int16_t | R | 1 |  | three decimal
| 0x3226 | 0x3226 | 12838 | 12838 | Phase C Current Demand | int16_t | R | 1 |  | three decimal
39
Real time Basic parameters（20ms）
| 0x3400 | 0x3401 | 13312 | 13313 | HS Phase A Line-to-Neutral Voltage | float | R | 2
| 0x3402 | 0x3403 | 13314 | 13315 | HS Phase B Line-to-Neutral Voltage | float | R | 2
| 0x3404 | 0x3405 | 13316 | 13317 | HS Phase C Line-to-Neutral Voltage | float | R | 2
| 0x3406 | 0x3407 | 13318 | 13319 | HS Phase AB Line-to-Line Voltage | float | R | 2
| 0x3408 | 0x3409 | 13320 | 13321 | HS Phase BC Line-to-Line Voltage | float | R | 2
| 0x340A | 0x340B | 13322 | 13323 | HS Phase CA Line-to-Line Voltage | float | R | 2
| 0x340C | 0x340D | 13324 | 13325 | HS Phase A Current | float | R | 2
| 0x340E | 0x340F | 13326 | 13327 | HS Phase B Current | float | R | 2
| 0x3410 | 0x3411 | 13328 | 13329 | HS Phase C Current | float | R | 2
| 0x3412 | 0x3413 | 13330 | 13331 | HS Average Line-to-Neutral Voltage | float | R | 2
| 0x3414 | 0x3415 | 13332 | 13333 | HS Average Line-to-Line Voltage | float | R | 2
| 0x3416 | 0x3417 | 13334 | 13335 | HS Average Current | float | R | 2
| 0x3418 | 0x3419 | 13336 | 13337 | HS System Active Power | float | R | 2
| 0x341A | 0x341B | 13338 | 13339 | HS System Reactive Power | float | R | 2
| 0x341C | 0x341D | 13340 | 13341 | HS System Frequency | float | R | 2
30
Real time basic parameters（1S）
| 0x4000 | 0x4001 | 16384 | 16385 | System Frequency | float | R | 2
| 0x4002 | 0x4003 | 16386 | 16387 | Phase A Line-to-Neutral Voltage | float | R | 2
| 0x4004 | 0x4005 | 16388 | 16389 | Phase B Line-to-Neutral Voltage | float | R | 2
| 0x4006 | 0x4007 | 16390 | 16391 | Phase C Line-to-Neutral Voltage | float | R | 2
| 0x4008 | 0x4009 | 16392 | 16393 | Average Line-to-Neutral Voltage | float | R | 2
| 0x400A | 0x400B | 16394 | 16395 | Phase AB Line-to-Line Voltage | float | R | 2
| 0x400C | 0x400D | 16396 | 16397 | Phase BC Line-to-Line Voltage | float | R | 2
| 0x400E | 0x400F | 16398 | 16399 | Phase CA Line-to-Line Voltage | float | R | 2
| 0x4010 | 0x4011 | 16400 | 16401 | Average Line-to-Line Voltage | float | R | 2
| 0x4012 | 0x4013 | 16402 | 16403 | Phase A Current | float | R | 2
| 0x4014 | 0x4015 | 16404 | 16405 | Phase B Current | float | R | 2
| 0x4016 | 0x4017 | 16406 | 16407 | Phase C Current | float | R | 2
| 0x4018 | 0x4019 | 16408 | 16409 | Average Current | float | R | 2
| 0x401A | 0x401B | 16410 | 16411 | Neutral Current | float | R | 2
| 0x401C | 0x401D | 16412 | 16413 | Phase A Active Power | float | R | 2
| 0x401E | 0x401F | 16414 | 16415 | Phase B Active Power | float | R | 2
| 0x4020 | 0x4021 | 16416 | 16417 | Phase C Active Power | float | R | 2
| 0x4022 | 0x4023 | 16418 | 16419 | System Active Power | float | R | 2
| 0x4024 | 0x4025 | 16420 | 16421 | Phase A Reactive Power | float | R | 2
| 0x4026 | 0x4027 | 16422 | 16423 | Phase B Reactive Power | float | R | 2
| 0x4028 | 0x4029 | 16424 | 16425 | Phase C Reactive Power | float | R | 2
| 0x402A | 0x402B | 16426 | 16427 | System Reactive Power | float | R | 2
| 0x402C | 0x402D | 16428 | 16429 | Phase A Apparent Power | float | R | 2
| 0x402E | 0x402F | 16430 | 16431 | Phase B Apparent Power | float | R | 2
| 0x4030 | 0x4031 | 16432 | 16433 | Phase C Apparent Power | float | R | 2
| 0x4032 | 0x4033 | 16434 | 16435 | System Apparent Power | float | R | 2
| 0x4034 | 0x4035 | 16436 | 16437 | Phase A Power Factor | float | R | 2
| 0x4036 | 0x4037 | 16438 | 16439 | Phase B Power Factor | float | R | 2
| 0x4038 | 0x4039 | 16440 | 16441 | Phase C Power Factor | float | R | 2
| 0x403A | 0x403B | 16442 | 16443 | System Power Factor | float | R | 2
| 0x403C | 0x403D | 16444 | 16445 | Voltage Unbalance Negative | float | R | 2
| 0x403E | 0x403F | 16446 | 16447 | Current Unbalance Negative | float | R | 2
| 0x4040 | 0x4041 | 16448 | 16449 | System Load Nature | float | R | 2
| 0x4042 | 0x4043 | 16450 | 16451 | System Active Power Demand | float | R | 2
| 0x4044 | 0x4045 | 16452 | 16453 | System Reactive Power Demand | float | R | 2
| 0x4046 | 0x4047 | 16454 | 16455 | System Apparent Power Demand | float | R | 2
72
Energy （1S）
| 0x4048 | 0x4049 | 16456 | 16457 | System active energy import | uint32_t | R/W | 2
| 0x404A | 0x404B | 16458 | 16459 | System active energy export | uint32_t | R/W | 2
| 0x404C | 0x404D | 16460 | 16461 | System reactive energy import | uint32_t | R/W | 2
| 0x404E | 0x404F | 16462 | 16463 | System reactive energy export | uint32_t | R/W | 2
| 0x4050 | 0x4051 | 16464 | 16465 | System active energy total | uint32_t | R/W | 2
| 0x4052 | 0x4053 | 16466 | 16467 | System active energy net | int32_t | R/W | 2
| 0x4054 | 0x4055 | 16468 | 16469 | System reactive energy total | uint32_t | R/W | 2
| 0x4056 | 0x4057 | 16470 | 16471 | System reactive energy net | int32_t | R/W | 2
| 0x4058 | 0x4059 | 16472 | 16473 | System apparent energy total | uint32_t | R/W | 2
18
Harmonics - THD（3S）
| 0x405A | 0x405A | 16474 | 16474 | Phase A Voltage THD | int16_t | R | 1 |  | two decimal
| 0x405B | 0x405B | 16475 | 16475 | Phase B Voltage THD | int16_t | R | 1 |  | two decimal
| 0x405C | 0x405C | 16476 | 16476 | Phase C Voltage THD | int16_t | R | 1 |  | two decimal
| 0x405D | 0x405D | 16477 | 16477 | Average Voltage THD | int16_t | R | 1 |  | two decimal
| 0x405E | 0x405E | 16478 | 16478 | Phase A Current THD | int16_t | R | 1 |  | two decimal
| 0x405F | 0x405F | 16479 | 16479 | Phase B Current THD | int16_t | R | 1 |  | two decimal
| 0x4060 | 0x4060 | 16480 | 16480 | Phase C Current THD | int16_t | R | 1 |  | two decimal
| 0x4061 | 0x4061 | 16481 | 16481 | Average Current THD | int16_t | R | 1 |  | two decimal
| 0x4062 | 0x407F | 16482 | 16511 | Phase A 2-31st Voltage Magnitude Harmonics | int16_t | R | 30 |  | two decimal
| 0x4080 | 0x4080 | 16512 | 16512 | Phase A Voltage THD Odd | int16_t | R | 1 |  | two decimal
| 0x4081 | 0x4081 | 16513 | 16513 | Phase A Voltage THD Even | int16_t | R | 1 |  | two decimal
| 0x4082 | 0x4082 | 16514 | 16514 | Phase A Voltage Crest Factor | int16_t | R | 1 |  | two decimal
| 0x4083 | 0x4083 | 16515 | 16515 | Phase A Voltage THFF Factor | int16_t | R | 1 |  | two decimal
| 0x4084 | 0x40A1 | 16516 | 16545 | Phase B 2-31st Voltage Magnitude Harmonics | int16_t | R | 30 |  | two decimal
| 0x40A2 | 0x40A2 | 16546 | 16546 | Phase B Voltage THD Odd | int16_t | R | 1 |  | two decimal
| 0x40A3 | 0x40A3 | 16547 | 16547 | Phase B Voltage THD Even | int16_t | R | 1 |  | two decimal
| 0x40A4 | 0x40A4 | 16548 | 16548 | Phase B Voltage Crest Factor | int16_t | R | 1 |  | two decimal
| 0x40A5 | 0x40A5 | 16549 | 16549 | Phase B Voltage THFF Factor | int16_t | R | 1 |  | two decimal
| 0x40A6 | 0x40C3 | 16550 | 16579 | Phase C 2-31st Voltage Magnitude Harmonics | int16_t | R | 30 |  | two decimal
| 0x40C4 | 0x40C4 | 16580 | 16580 | Phase C Voltage THD Odd | int16_t | R | 1 |  | two decimal
| 0x40C5 | 0x40C5 | 16581 | 16581 | Phase C Voltage THD Even | int16_t | R | 1 |  | two decimal
| 0x40C6 | 0x40C6 | 16582 | 16582 | Phase C Voltage Crest Factor | int16_t | R | 1 |  | two decimal
| 0x40C7 | 0x40C7 | 16583 | 16583 | Phase C Voltage THFF Factor | int16_t | R | 1 |  | two decimal
| 0x40C8 | 0x40E5 | 16584 | 16613 | Phase A 2-31st Current Magnitude Harmonics | int16_t | R | 30 |  | two decimal
| 0x40E6 | 0x40E6 | 16614 | 16614 | Phase A Current THD Odd | int16_t | R | 1 |  | two decimal
| 0x40E7 | 0x40E7 | 16615 | 16615 | Phase A Current THD Even | int16_t | R | 1 |  | two decimal
| 0x40E8 | 0x40E8 | 16616 | 16616 | Phase A Current K-Factor | int16_t | R | 1 |  | two decimal
| 0x40E9 | 0x4106 | 16617 | 16646 | Phase B 2-31st Current Magnitude Harmonics | int16_t | R | 30 |  | two decimal
| 0x4107 | 0x4107 | 16647 | 16647 | Phase B Current THD Odd | int16_t | R | 1 |  | two decimal
| 0x4108 | 0x4108 | 16648 | 16648 | Phase B Current THD Even | int16_t | R | 1 |  | two decimal
| 0x4109 | 0x4109 | 16649 | 16649 | Phase B Current K-Factor | int16_t | R | 1 |  | two decimal
| 0x410A | 0x4127 | 16650 | 16679 | Phase C 2-31st Current Magnitude Harmonics | int16_t | R | 30 |  | two decimal
| 0x4128 | 0x4128 | 16680 | 16680 | Phase C Current THD Odd | int16_t | R | 1 |  | two decimal
| 0x4129 | 0x4129 | 16681 | 16681 | Phase C Current THD Even | int16_t | R | 1 |  | two decimal
| 0x412A | 0x412A | 16682 | 16682 | Phase C Current K-Factor | int16_t | R | 1 |  | two decimal
209
Sequence
| 0x4294 | 0x4294 | 17044 | 17044 | Voltage Positive Sequence Real Part | int16_t | R | 1 |  | two decimal
| 0x4295 | 0x4295 | 17045 | 17045 | Voltage Positive Sequence Imaginary Part | int16_t | R | 1 |  | two decimal
| 0x4296 | 0x4296 | 17046 | 17046 | Voltage Negative Sequence Real Part | int16_t | R | 1 |  | two decimal
| 0x4297 | 0x4297 | 17047 | 17047 | Voltage Negative Sequence Imaginary Part | int16_t | R | 1 |  | two decimal
| 0x4298 | 0x4298 | 17048 | 17048 | Voltage Zero Sequnece Real Part | int16_t | R | 1 |  | two decimal
| 0x4299 | 0x4299 | 17049 | 17049 | Voltage Zero Sequence Imaginary Part | int16_t | R | 1 |  | two decimal
| 0x429A | 0x429A | 17050 | 17050 | Current Positive Sequence Real Part | int16_t | R | 1 |  | two decimal
| 0x429B | 0x429B | 17051 | 17051 | Current Positive Sequence Imaginary Part | int16_t | R | 1 |  | two decimal
| 0x429C | 0x429C | 17052 | 17052 | Current Negative Sequence Real Part | int16_t | R | 1 |  | two decimal
| 0x429D | 0x429D | 17053 | 17053 | Current Negative Sequence Imaginary Part | int16_t | R | 1 |  | two decimal
| 0x429E | 0x429E | 17054 | 17054 | Current Zero Sequnece Real Part | int16_t | R | 1 |  | two decimal
| 0x429F | 0x429F | 17055 | 17055 | Current Zero Sequence Imaginary Part | int16_t | R | 1 |  | two decimal
12
Phase Angle
| 0x42A0 | 0x42A0 | 17056 | 17056 | Phase B Line-to-Neutral Voltage Phase Angle | uint16_t | R | 1 |  | one decimal
| 0x42A1 | 0x42A1 | 17057 | 17057 | Phase C Line-to-Neutral Voltage Phase Angle | uint16_t | R | 1 |  | one decimal
| 0x42A2 | 0x42A2 | 17058 | 17058 | Phase A Current Phase Angle | uint16_t | R | 1 |  | one decimal
| 0x42A3 | 0x42A3 | 17059 | 17059 | Phase B Current Phase Angle | uint16_t | R | 1 |  | one decimal
| 0x42A4 | 0x42A4 | 17060 | 17060 | Phase C Current Phase Angle | uint16_t | R | 1 |  | one decimal
5
Load percentage | 0x45F0 | 0x45F1 | 17904 | 17905 | reserve |  | R | 2
Current demand
| 0x4600 | 0x4601 | 17920 | 17921 | Phase A Current Demand | float | R | 2
| 0x4602 | 0x4603 | 17922 | 17923 | Phase B Current Demand | float | R | 2
| 0x4604 | 0x4605 | 17924 | 17925 | Phase C Current Demand | float | R | 2
6
Energy - continue（1S）
| 0x4620 | 0x4621 | 17952 | 17953 | Phase A active energy import | uint32_t | R/W | 2
| 0x4622 | 0x4623 | 17954 | 17955 | Phase A active energy export | uint32_t | R/W | 2
| 0x4624 | 0x4625 | 17956 | 17957 | Phase B active energy import | uint32_t | R/W | 2
| 0x4626 | 0x4627 | 17958 | 17959 | Phase B active energy export | uint32_t | R/W | 2
| 0x4628 | 0x4629 | 17960 | 17961 | Phase C active energy import | uint32_t | R/W | 2
| 0x462A | 0x462B | 17962 | 17963 | Phase C active energy export | uint32_t | R/W | 2
| 0x462C | 0x462D | 17964 | 17965 | Phase A reactive energy import | uint32_t | R/W | 2
| 0x462E | 0x462F | 17966 | 17967 | Phase A reactive energy export | uint32_t | R/W | 2
| 0x4630 | 0x4631 | 17968 | 17969 | Phase B reactive energy import | uint32_t | R/W | 2
| 0x4632 | 0x4633 | 17970 | 17971 | Phase B reactive energy export | uint32_t | R/W | 2
| 0x4634 | 0x4635 | 17972 | 17973 | Phase C reactive energy import | uint32_t | R/W | 2
| 0x4636 | 0x4637 | 17974 | 17975 | Phase C reactive energy export | uint32_t | R/W | 2
| 0x4638 | 0x4639 | 17976 | 17977 | Phase A apparent energy total | uint32_t | R/W | 2
| 0x463A | 0x463B | 17978 | 17979 | Phase B apparent energy total | uint32_t | R/W | 2
| 0x463C | 0x463D | 17980 | 17981 | Phase C apparent energy total | uint32_t | R/W | 2
30

## Energy_1s
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Energy Parameter ID | Range | Default
Energy(1 second) | 0x4A00 | 0x4A01 | 18944 | 18945 | Phase A active energy import | uint32_t | R | 2 | 1
| 0x4A02 | 0x4A03 | 18946 | 18947 | Phase B active energy import | uint32_t | R | 2 | 2
| 0x4A04 | 0x4A05 | 18948 | 18949 | Phase C active energy import | uint32_t | R | 2 | 3
| 0x4A06 | 0x4A07 | 18950 | 18951 | System active energy import | uint32_t | R | 2 | 4
| 0x4A08 | 0x4A09 | 18952 | 18953 | Phase A active energy export | uint32_t | R | 2 | 5
| 0x4A0A | 0x4A0B | 18954 | 18955 | Phase B active energy export | uint32_t | R | 2 | 6
| 0x4A0C | 0x4A0D | 18956 | 18957 | Phase C active energy export | uint32_t | R | 2 | 7
| 0x4A0E | 0x4A0F | 18958 | 18959 | System active energy export | uint32_t | R | 2 | 8
| 0x4A10 | 0x4A11 | 18960 | 18961 | Phase A active energy total | uint32_t | R | 2 | 9
| 0x4A12 | 0x4A13 | 18962 | 18963 | Phase B active energy total | uint32_t | R | 2 | 10
| 0x4A14 | 0x4A15 | 18964 | 18965 | Phase C active energy total | uint32_t | R | 2 | 11
| 0x4A16 | 0x4A17 | 18966 | 18967 | System active energy total | uint32_t | R | 2 | 12
| 0x4A18 | 0x4A19 | 18968 | 18969 | Phase A active energy net | int32_t | R | 2 | 13
| 0x4A1A | 0x4A1B | 18970 | 18971 | Phase B active energy net | int32_t | R | 2 | 14
| 0x4A1C | 0x4A1D | 18972 | 18973 | Phase C active energy net | int32_t | R | 2 | 15
| 0x4A1E | 0x4A1F | 18974 | 18975 | System active energy net | int32_t | R | 2 | 16
| 0x4A20 | 0x4A21 | 18976 | 18977 | Phase A reactive energy import | uint32_t | R | 2 | 17
| 0x4A22 | 0x4A23 | 18978 | 18979 | Phase B reactive energy import | uint32_t | R | 2 | 18
| 0x4A24 | 0x4A25 | 18980 | 18981 | Phase C reactive energy import | uint32_t | R | 2 | 19
| 0x4A26 | 0x4A27 | 18982 | 18983 | System reactive energy import | uint32_t | R | 2 | 20
| 0x4A28 | 0x4A29 | 18984 | 18985 | Phase A reactive energy export | uint32_t | R | 2 | 21
| 0x4A2A | 0x4A2B | 18986 | 18987 | Phase B reactive energy export | uint32_t | R | 2 | 22
| 0x4A2C | 0x4A2D | 18988 | 18989 | Phase C reactive energy export | uint32_t | R | 2 | 23
| 0x4A2E | 0x4A2F | 18990 | 18991 | System reactive energy export | uint32_t | R | 2 | 24
| 0x4A30 | 0x4A31 | 18992 | 18993 | Phase A reactive energy total | uint32_t | R | 2 | 25
| 0x4A32 | 0x4A33 | 18994 | 18995 | Phase B reactive energy total | uint32_t | R | 2 | 26
| 0x4A34 | 0x4A35 | 18996 | 18997 | Phase C reactive energy total | uint32_t | R | 2 | 27
| 0x4A36 | 0x4A37 | 18998 | 18999 | System reactive energy total | uint32_t | R | 2 | 28
| 0x4A38 | 0x4A39 | 19000 | 19001 | Phase A reactive energy net | int32_t | R | 2 | 29
| 0x4A3A | 0x4A3B | 19002 | 19003 | Phase B reactive energy net | int32_t | R | 2 | 30
| 0x4A3C | 0x4A3D | 19004 | 19005 | Phase C reactive energy net | int32_t | R | 2 | 31
| 0x4A3E | 0x4A3F | 19006 | 19007 | System reactive energy net | int32_t | R | 2 | 32
| 0x4A40 | 0x4A41 | 19008 | 19009 | Phase A apparent energy total | uint32_t | R | 2 | 33
| 0x4A42 | 0x4A43 | 19010 | 19011 | Phase B apparent energy total | uint32_t | R | 2 | 34
| 0x4A44 | 0x4A45 | 19012 | 19013 | Phase C apparent energy total | uint32_t | R | 2 | 35
| 0x4A46 | 0x4A47 | 19014 | 19015 | System apparent energy total | uint32_t | R | 2 | 36
| 0x4A48 | 0x4A49 | 19016 | 19017 | Channel 4 active energy import | uint32_t | R | 2 | 37
| 0x4A4A | 0x4A4B | 19018 | 19019 | Channel 4 active energy export | uint32_t | R | 2 | 38
| 0x4A4C | 0x4A4D | 19020 | 19021 | Channel 4 active energy total | uint32_t | R | 2 | 39
| 0x4A4E | 0x4A4F | 19022 | 19023 | Channel 4 active energy net | int32_t | R | 2 | 40
| 0x4A50 | 0x4A51 | 19024 | 19025 | Channel 4 reactive energy import | uint32_t | R | 2 | 41
| 0x4A52 | 0x4A53 | 19026 | 19027 | Channel 4 reactive energy export | uint32_t | R | 2 | 42
| 0x4A54 | 0x4A55 | 19028 | 19029 | Channel 4 reactive energy total | uint32_t | R | 2 | 43
| 0x4A56 | 0x4A57 | 19030 | 19031 | Channel 4 reactive energy net | int32_t | R | 2 | 44
| 0x4A58 | 0x4A59 | 19032 | 19033 | Channel 4 apparent energy total | uint32_t | R | 2 | 45
| 0x4A5A | 0x4A5B | 19034 | 19035 | Summation 2 active energy import | uint32_t | R | 2 | 46
| 0x4A5C | 0x4A5D | 19036 | 19037 | Summation 2 active energy export | uint32_t | R | 2 | 47
| 0x4A5E | 0x4A5F | 19038 | 19039 | Summation 2 active energy total | uint32_t | R | 2 | 48
| 0x4A60 | 0x4A61 | 19040 | 19041 | Summation 2 active energy net | int32_t | R | 2 | 49
| 0x4A62 | 0x4A63 | 19042 | 19043 | Summation 2 reactive energy import | uint32_t | R | 2 | 50
| 0x4A64 | 0x4A65 | 19044 | 19045 | Summation 2 reactive energy export | uint32_t | R | 2 | 51
| 0x4A66 | 0x4A67 | 19046 | 19047 | Summation 2 reactive energy total | uint32_t | R | 2 | 52
| 0x4A68 | 0x4A69 | 19048 | 19049 | Summation 2 reactive energy net | int32_t | R | 2 | 53
| 0x4A6A | 0x4A6B | 19050 | 19051 | Summation 2 apparent energy total | uint32_t | R | 2 | 54
Quadrant Energy | 0x4A6C | 0x4A6D | 19052 | 19053 | Phase A Active Energy Quad 1 | uint32_t | R | 2
| 0x4A6E | 0x4A6F | 19054 | 19055 | Phase B Active Energy Quad 1 | uint32_t | R | 2
| 0x4A70 | 0x4A71 | 19056 | 19057 | Phase C Active Energy Quad 1 | uint32_t | R | 2
| 0x4A72 | 0x4A73 | 19058 | 19059 | System Active Energy Quad 1 | uint32_t | R | 2
| 0x4A74 | 0x4A75 | 19060 | 19061 | Phase A Active Energy Quad 2 | uint32_t | R | 2
| 0x4A76 | 0x4A77 | 19062 | 19063 | Phase B Active Energy Quad 2 | uint32_t | R | 2
| 0x4A78 | 0x4A79 | 19064 | 19065 | Phase C Active Energy Quad 2 | uint32_t | R | 2
| 0x4A7A | 0x4A7B | 19066 | 19067 | System Active Energy Quad 2 | uint32_t | R | 2
| 0x4A7C | 0x4A7D | 19068 | 19069 | Phase A Active Energy Quad 3 | uint32_t | R | 2
| 0x4A7E | 0x4A7F | 19070 | 19071 | Phase B Active Energy Quad 3 | uint32_t | R | 2
| 0x4A80 | 0x4A81 | 19072 | 19073 | Phase C Active Energy Quad 3 | uint32_t | R | 2
| 0x4A82 | 0x4A83 | 19074 | 19075 | System Active Energy Quad 3 | uint32_t | R | 2
| 0x4A84 | 0x4A85 | 19076 | 19077 | Phase A Active Energy Quad 4 | uint32_t | R | 2
| 0x4A86 | 0x4A87 | 19078 | 19079 | Phase B Active Energy Quad 4 | uint32_t | R | 2
| 0x4A88 | 0x4A89 | 19080 | 19081 | Phase C Active Energy Quad 4 | uint32_t | R | 2
| 0x4A8A | 0x4A8B | 19082 | 19083 | System Active Energy Quad 4 | uint32_t | R | 2
| 0x4A8C | 0x4A8D | 19084 | 19085 | Phase A Reactive Energy Quad 1 | uint32_t | R | 2
| 0x4A8E | 0x4A8F | 19086 | 19087 | Phase B Reactive Energy Quad 1 | uint32_t | R | 2
| 0x4A90 | 0x4A91 | 19088 | 19089 | Phase C Reactive Energy Quad 1 | uint32_t | R | 2
| 0x4A92 | 0x4A93 | 19090 | 19091 | System Reactive Energy Quad 1 | uint32_t | R | 2
| 0x4A94 | 0x4A95 | 19092 | 19093 | Phase A Reactive Energy Quad 2 | uint32_t | R | 2
| 0x4A96 | 0x4A97 | 19094 | 19095 | Phase B Reactive Energy Quad 2 | uint32_t | R | 2
| 0x4A98 | 0x4A99 | 19096 | 19097 | Phase C Reactive Energy Quad 2 | uint32_t | R | 2
| 0x4A9A | 0x4A9B | 19098 | 19099 | System Reactive Energy Quad 2 | uint32_t | R | 2
| 0x4A9C | 0x4A9D | 19100 | 19101 | Phase A Reactive Energy Quad 3 | uint32_t | R | 2
| 0x4A9E | 0x4A9F | 19102 | 19103 | Phase B Reactive Energy Quad 3 | uint32_t | R | 2
| 0x4AA0 | 0x4AA1 | 19104 | 19105 | Phase C Reactive Energy Quad 3 | uint32_t | R | 2
| 0x4AA2 | 0x4AA3 | 19106 | 19107 | System Reactive Energy Quad 3 | uint32_t | R | 2
| 0x4AA4 | 0x4AA5 | 19108 | 19109 | Phase A Reactive Energy Quad 4 | uint32_t | R | 2
| 0x4AA6 | 0x4AA7 | 19110 | 19111 | Phase B Reactive Energy Quad 4 | uint32_t | R | 2
| 0x4AA8 | 0x4AA9 | 19112 | 19113 | Phase C Reactive Energy Quad 4 | uint32_t | R | 2
| 0x4AAA | 0x4AAB | 19114 | 19115 | System Reactive Energy Quad 4 | uint32_t | R | 2
| 0x4AAC | 0x4AAD | 19116 | 19117 | Phase A Apparent Energy Quad 1 | uint32_t | R | 2
| 0x4AAE | 0x4AAF | 19118 | 19119 | Phase B Apparent Energy Quad 1 | uint32_t | R | 2
| 0x4AB0 | 0x4AB1 | 19120 | 19121 | Phase C Apparent Energy Quad 1 | uint32_t | R | 2
| 0x4AB2 | 0x4AB3 | 19122 | 19123 | System Apparent Energy Quad 1 | uint32_t | R | 2
| 0x4AB4 | 0x4AB5 | 19124 | 19125 | Phase A Apparent Energy Quad 2 | uint32_t | R | 2
| 0x4AB6 | 0x4AB7 | 19126 | 19127 | Phase B Apparent Energy Quad 2 | uint32_t | R | 2
| 0x4AB8 | 0x4AB9 | 19128 | 19129 | Phase C Apparent Energy Quad 2 | uint32_t | R | 2
| 0x4ABA | 0x4ABB | 19130 | 19131 | System Apparent Energy Quad 2 | uint32_t | R | 2
| 0x4ABC | 0x4ABD | 19132 | 19133 | Phase A Apparent Energy Quad 3 | uint32_t | R | 2
| 0x4ABE | 0x4ABF | 19134 | 19135 | Phase B Apparent Energy Quad 3 | uint32_t | R | 2
| 0x4AC0 | 0x4AC1 | 19136 | 19137 | Phase C Apparent Energy Quad 3 | uint32_t | R | 2
| 0x4AC2 | 0x4AC3 | 19138 | 19139 | System Apparent Energy Quad 3 | uint32_t | R | 2
| 0x4AC4 | 0x4AC5 | 19140 | 19141 | Phase A Apparent Energy Quad 4 | uint32_t | R | 2
| 0x4AC6 | 0x4AC7 | 19142 | 19143 | Phase B Apparent Energy Quad 4 | uint32_t | R | 2
| 0x4AC8 | 0x4AC9 | 19144 | 19145 | Phase C Apparent Energy Quad 4 | uint32_t | R | 2
| 0x4ACA | 0x4ACB | 19146 | 19147 | System Apparent Energy Quad 4 | uint32_t | R | 2
| 0x4ACC | 0x4ACD | 19148 | 19149 | Channel 4 Active Energy Quad 1 | uint32_t | R | 2
| 0x4ACE | 0x4ACF | 19150 | 19151 | Channel 4 Active Energy Quad 2 | uint32_t | R | 2
| 0x4AD0 | 0x4AD1 | 19152 | 19153 | Channel 4 Active Energy Quad 3 | uint32_t | R | 2
| 0x4AD2 | 0x4AD3 | 19154 | 19155 | Channel 4 Active Energy Quad 4 | uint32_t | R | 2
| 0x4AD4 | 0x4AD5 | 19156 | 19157 | Channel 4 Reactive Energy Quad 1 | uint32_t | R | 2
| 0x4AD6 | 0x4AD7 | 19158 | 19159 | Channel 4 Reactive Energy Quad 2 | uint32_t | R | 2
| 0x4AD8 | 0x4AD9 | 19160 | 19161 | Channel 4 Reactive Energy Quad 3 | uint32_t | R | 2
| 0x4ADA | 0x4ADB | 19162 | 19163 | Channel 4 Reactive Energy Quad 4 | uint32_t | R | 2
| 0x4ADC | 0x4ADD | 19164 | 19165 | Channel 4 Apparent Energy Quad 1 | uint32_t | R | 2
| 0x4ADE | 0x4ADF | 19166 | 19167 | Channel 4 Apparent Energy Quad 2 | uint32_t | R | 2
| 0x4AE0 | 0x4AE1 | 19168 | 19169 | Channel 4 Apparent Energy Quad 3 | uint32_t | R | 2
| 0x4AE2 | 0x4AE3 | 19170 | 19171 | Channel 4 Apparent Energy Quad 4 | uint32_t | R | 2
| 0x4AE4 | 0x4AE5 | 19172 | 19173 | Summation 2 Active Energy Quad 1 | uint32_t | R | 2
| 0x4AE6 | 0x4AE7 | 19174 | 19175 | Summation 2 Active Energy Quad 2 | uint32_t | R | 2
| 0x4AE8 | 0x4AE9 | 19176 | 19177 | Summation 2 Active Energy Quad 3 | uint32_t | R | 2
| 0x4AEA | 0x4AEB | 19178 | 19179 | Summation 2 Active Energy Quad 4 | uint32_t | R | 2
| 0x4AEC | 0x4AED | 19180 | 19181 | Summation 2 Reactive Energy Quad 1 | uint32_t | R | 2
| 0x4AEE | 0x4AEF | 19182 | 19183 | Summation 2 Reactive Energy Quad 2 | uint32_t | R | 2
| 0x4AF0 | 0x4AF1 | 19184 | 19185 | Summation 2 Reactive Energy Quad 3 | uint32_t | R | 2
| 0x4AF2 | 0x4AF3 | 19186 | 19187 | Summation 2 Reactive Energy Quad 4 | uint32_t | R | 2
| 0x4AF4 | 0x4AF5 | 19188 | 19189 | Summation 2 Apparent Energy Quad 1 | uint32_t | R | 2
| 0x4AF6 | 0x4AF7 | 19190 | 19191 | Summation 2 Apparent Energy Quad 2 | uint32_t | R | 2
| 0x4AF8 | 0x4AF9 | 19192 | 19193 | Summation 2 Apparent Energy Quad 3 | uint32_t | R | 2
| 0x4AFA | 0x4AFB | 19194 | 19195 | Summation 2 Apparent Energy Quad 4 | uint32_t | R | 2
252

## Moving Average
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data Type | RW | Reg Num | Range | Default
Moving Average Parameters | 0x9200 | 0x9203 | 37376 | 37379 | Moving Average Param Update Time Stamp | uint64_t | R | 4
| 0x9204 | 0x9205 | 37380 | 37381 | System Frequency | float | R | 2
| 0x9206 | 0x9207 | 37382 | 37383 | Phase A Line-to-Neutral Voltage | float | R | 2
| 0x9208 | 0x9209 | 37384 | 37385 | Phase B Line-to-Neutral Voltage | float | R | 2
| 0x920A | 0x920B | 37386 | 37387 | Phase C Line-to-Neutral Voltage | float | R | 2
| 0x920C | 0x920D | 37388 | 37389 | Phase A Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x920E | 0x920F | 37390 | 37391 | Phase B Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x9210 | 0x9211 | 37392 | 37393 | Phase C Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x9212 | 0x9213 | 37394 | 37395 | Average Line-to-Neutral Voltage | float | R | 2
| 0x9214 | 0x9215 | 37396 | 37397 | Phase AB Line-to-Line Voltage | float | R | 2
| 0x9216 | 0x9217 | 37398 | 37399 | Phase BC Line-to-Line Voltage | float | R | 2
| 0x9218 | 0x9219 | 37400 | 37401 | Phase CA Line-to-Line Voltage | float | R | 2
| 0x921A | 0x921B | 37402 | 37403 | Phase AB Line-to-Line Voltage Phase Angle | float | R | 2
| 0x921C | 0x921D | 37404 | 37405 | Phase BC Line-to-Line Voltage Phase Angle | float | R | 2
| 0x921E | 0x921F | 37406 | 37407 | Phase CA Line-to-Line Voltage Phase Angle | float | R | 2
| 0x9220 | 0x9221 | 37408 | 37409 | Average Line-to-Line Voltage | float | R | 2
| 0x9222 | 0x9223 | 37410 | 37411 | Phase A Current | float | R | 2
| 0x9224 | 0x9225 | 37412 | 37413 | Phase B Current | float | R | 2
| 0x9226 | 0x9227 | 37414 | 37415 | Phase C Current | float | R | 2
| 0x9228 | 0x9229 | 37416 | 37417 | Phase N Current | float | R | 2
| 0x922A | 0x922B | 37418 | 37419 | Phase A Current Phase Angle | float | R | 2
| 0x922C | 0x922D | 37420 | 37421 | Phase B Current Phase Angle | float | R | 2
| 0x922E | 0x922F | 37422 | 37423 | Phase C Current Phase Angle | float | R | 2
| 0x9230 | 0x9231 | 37424 | 37425 | Phase N Current Phase Angle | float | R | 2
| 0x9232 | 0x9233 | 37426 | 37427 | Average Current | float | R | 2
| 0x9234 | 0x9235 | 37428 | 37429 | Phase A Active Power | float | R | 2
| 0x9236 | 0x9237 | 37430 | 37431 | Phase B Active Power | float | R | 2
| 0x9238 | 0x9239 | 37432 | 37433 | Phase C Active Power | float | R | 2
| 0x923A | 0x923B | 37434 | 37435 | System Active Power | float | R | 2
| 0x923C | 0x923D | 37436 | 37437 | Phase A Reactive Power | float | R | 2
| 0x923E | 0x923F | 37438 | 37439 | Phase B Reactive Power | float | R | 2
| 0x9240 | 0x9241 | 37440 | 37441 | Phase C Reactive Power | float | R | 2
| 0x9242 | 0x9243 | 37442 | 37443 | System Reactive Power | float | R | 2
| 0x9244 | 0x9245 | 37444 | 37445 | Phase A Apparent Power | float | R | 2
| 0x9246 | 0x9247 | 37446 | 37447 | Phase B Apparent Power | float | R | 2
| 0x9248 | 0x9249 | 37448 | 37449 | Phase C Apparent Power | float | R | 2
| 0x924A | 0x924B | 37450 | 37451 | System Apparent Power | float | R | 2
| 0x924C | 0x924D | 37452 | 37453 | Phase A Power Factor | float | R | 2
| 0x924E | 0x924F | 37454 | 37455 | Phase B Power Factor | float | R | 2
| 0x9250 | 0x9251 | 37456 | 37457 | Phase C Power Factor | float | R | 2
| 0x9252 | 0x9253 | 37458 | 37459 | System Power Factor | float | R | 2
| 0x9254 | 0x9255 | 37460 | 37461 | Phase A Load Nature | uint32_t | R | 2
| 0x9256 | 0x9257 | 37462 | 37463 | Phase B Load Nature | uint32_t | R | 2
| 0x9258 | 0x9259 | 37464 | 37465 | Phase C Load Nature | uint32_t | R | 2
| 0x925A | 0x925B | 37466 | 37467 | System Load Nature | uint32_t | R | 2
| 0x925C | 0x925D | 37468 | 37469 | Channel 4 Active Power | float | R | 2
| 0x925E | 0x925F | 37470 | 37471 | Channel 4 Reactive Power | float | R | 2
| 0x9260 | 0x9261 | 37472 | 37473 | Channel 4 Apparent Power | float | R | 2
| 0x9262 | 0x9263 | 37474 | 37475 | Channel 4 Power Factor | float | R | 2
| 0x9264 | 0x9265 | 37476 | 37477 | Channel 4 Load Nature | uint32_t | R | 2
| 0x9266 | 0x9267 | 37478 | 37479 | Summation 2 Average Current | float | R | 2
| 0x9268 | 0x9269 | 37480 | 37481 | Summation 2 Active Power | float | R | 2
| 0x926A | 0x926B | 37482 | 37483 | Summation 2 Reactive Power | float | R | 2
| 0x926C | 0x926D | 37484 | 37485 | Summation 2 Apparent Power | float | R | 2
| 0x926E | 0x926F | 37486 | 37487 | Summation 2 Power Factor | float | R | 2
| 0x9270 | 0x9271 | 37488 | 37489 | Summation 2 Load Nature | uint32_t | R | 2
| 0x9272 | 0x9273 | 37490 | 37491 | Voltage Unbalance Negative | float | R | 2
| 0x9274 | 0x9275 | 37492 | 37493 | Voltage Unbalance Zero | float | R | 2
| 0x9276 | 0x9277 | 37494 | 37495 | Voltage Zero Sequnece Real Part | float | R | 2
| 0x9278 | 0x9279 | 37496 | 37497 | Voltage Zero Sequence Imaginary Part | float | R | 2
| 0x927A | 0x927B | 37498 | 37499 | Voltage Positive Sequence Real Part | float | R | 2
| 0x927C | 0x927D | 37500 | 37501 | Voltage Positive Sequence Imaginary Part | float | R | 2
| 0x927E | 0x927F | 37502 | 37503 | Voltage Negative Sequence Real Part | float | R | 2
| 0x9280 | 0x9281 | 37504 | 37505 | Voltage Negative Sequence Imaginary Part | float | R | 2
| 0x9282 | 0x9283 | 37506 | 37507 | Current Unbalance Negative | float | R | 2
| 0x9284 | 0x9285 | 37508 | 37509 | Current Unbalance Zero | float | R | 2
| 0x9286 | 0x9287 | 37510 | 37511 | Current Zero Sequnece Real Part | float | R | 2
| 0x9288 | 0x9289 | 37512 | 37513 | Current Zero Sequence Imaginary Part | float | R | 2
| 0x928A | 0x928B | 37514 | 37515 | Current Positive Sequence Real Part | float | R | 2
| 0x928C | 0x928D | 37516 | 37517 | Current Positive Sequence Imaginary Part | float | R | 2
| 0x928E | 0x928F | 37518 | 37519 | Current Negative Sequence Real Part | float | R | 2
| 0x9290 | 0x9291 | 37520 | 37521 | Current Negative Sequence Imaginary Part | float | R | 2
146

## 200ms
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data Type | RW | Reg Num | Range | Default
RMS(10、12 cycle) | 0x9300 | 0x9303 | 37632 | 37635 | 200ms RMS Param Update Timestamp | uint64_t | R | 4
| 0x9304 | 0x9304 | 37636 | 37636 | 200ms RMS Param Valid Flag(50160) | uint16_t | R | 1
| 0x9305 | 0x9305 | 37637 | 37637 | 200ms RMS Param Event Flag | uint16_t | R | 1
| 0x9306 | 0x9306 | 37638 | 37638 | 200ms RMS Param Block Number | uint16_t | R | 1
| 0x9307 | 0x9308 | 37639 | 37640 | System Frequency | float | R | 2
| 0x9309 | 0x930A | 37641 | 37642 | Phase A Line-to-Neutral Voltage | float | R | 2
| 0x930B | 0x930C | 37643 | 37644 | Phase B Line-to-Neutral Voltage | float | R | 2
| 0x930D | 0x930E | 37645 | 37646 | Phase C Line-to-Neutral Voltage | float | R | 2
| 0x930F | 0x9310 | 37647 | 37648 | Phase A Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x9311 | 0x9312 | 37649 | 37650 | Phase B Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x9313 | 0x9314 | 37651 | 37652 | Phase C Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x9315 | 0x9316 | 37653 | 37654 | Average Line-to-Neutral Voltage | float | R | 2
| 0x9317 | 0x9318 | 37655 | 37656 | Phase AB Line-to-Line Voltage | float | R | 2
| 0x9319 | 0x931A | 37657 | 37658 | Phase BC Line-to-Line Voltage | float | R | 2
| 0x931B | 0x931C | 37659 | 37660 | Phase CA Line-to-Line Voltage | float | R | 2
| 0x931D | 0x931E | 37661 | 37662 | Phase AB Line-to-Line Voltage Phase Angle | float | R | 2
| 0x931F | 0x9320 | 37663 | 37664 | Phase BC Line-to-Line Voltage Phase Angle | float | R | 2
| 0x9321 | 0x9322 | 37665 | 37666 | Phase CA Line-to-Line Voltage Phase Angle | float | R | 2
| 0x9323 | 0x9324 | 37667 | 37668 | Average Line-to-Line Voltage | float | R | 2
| 0x9325 | 0x9326 | 37669 | 37670 | Phase A Current | float | R | 2
| 0x9327 | 0x9328 | 37671 | 37672 | Phase B Current | float | R | 2
| 0x9329 | 0x932A | 37673 | 37674 | Phase C Current | float | R | 2
| 0x932B | 0x932C | 37675 | 37676 | Neutral Current | float | R | 2
| 0x932D | 0x932E | 37677 | 37678 | Phase A Current Phase Angle | float | R | 2
| 0x932F | 0x9330 | 37679 | 37680 | Phase B Current Phase Angle | float | R | 2
| 0x9331 | 0x9332 | 37681 | 37682 | Phase C Current Phase Angle | float | R | 2
| 0x9333 | 0x9334 | 37683 | 37684 | Neutral Current Phase Angle | float | R | 2
| 0x9335 | 0x9336 | 37685 | 37686 | Average Current | float | R | 2
| 0x9337 | 0x9338 | 37687 | 37688 | Phase A Active Power | float | R | 2
| 0x9339 | 0x933A | 37689 | 37690 | Phase B Active Power | float | R | 2
| 0x933B | 0x933C | 37691 | 37692 | Phase C Active Power | float | R | 2
| 0x933D | 0x933E | 37693 | 37694 | System Active Power | float | R | 2
| 0x933F | 0x9340 | 37695 | 37696 | Phase A Reactive Power | float | R | 2
| 0x9341 | 0x9342 | 37697 | 37698 | Phase B Reactive Power | float | R | 2
| 0x9343 | 0x9344 | 37699 | 37700 | Phase C Reactive Power | float | R | 2
| 0x9345 | 0x9346 | 37701 | 37702 | System Reactive Power | float | R | 2
| 0x9347 | 0x9348 | 37703 | 37704 | Phase A Apparent Power | float | R | 2
| 0x9349 | 0x934A | 37705 | 37706 | Phase B Apparent Power | float | R | 2
| 0x934B | 0x934C | 37707 | 37708 | Phase C Apparent Power | float | R | 2
| 0x934D | 0x934E | 37709 | 37710 | System Apparent Power | float | R | 2
| 0x934F | 0x9350 | 37711 | 37712 | Phase A Power Factor | float | R | 2
| 0x9351 | 0x9352 | 37713 | 37714 | Phase B Power Factor | float | R | 2
| 0x9353 | 0x9354 | 37715 | 37716 | Phase C Power Factor | float | R | 2
| 0x9355 | 0x9356 | 37717 | 37718 | System Power Factor | float | R | 2
| 0x9357 | 0x9358 | 37719 | 37720 | Phase A Displacement Power Factor | float | R | 2
| 0x9359 | 0x935A | 37721 | 37722 | Phase B Displacement Power Factor | float | R | 2
| 0x935B | 0x935C | 37723 | 37724 | Phase C Displacement Power Factor | float | R | 2
| 0x935D | 0x935E | 37725 | 37726 | Phase A Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
| 0x935F | 0x9360 | 37727 | 37728 | Phase B Load Nature | uint32_t | R | 2
| 0x9361 | 0x9362 | 37729 | 37730 | Phase C Load Nature | uint32_t | R | 2
| 0x9363 | 0x9364 | 37731 | 37732 | System Load Nature | uint32_t | R | 2
| 0x9365 | 0x9366 | 37733 | 37734 | Channel 4 Active Power | float | R | 2
| 0x9367 | 0x9368 | 37735 | 37736 | Channel 4 Reactive Power | float | R | 2
| 0x9369 | 0x936A | 37737 | 37738 | Channel 4 Apparent Power | float | R | 2
| 0x936B | 0x936C | 37739 | 37740 | Channel 4 Power Factor | float | R | 2
| 0x936D | 0x936E | 37741 | 37742 | Channel 4 Displacement Power Factor | float | R | 2
| 0x936F | 0x9370 | 37743 | 37744 | Channel 4 Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
| 0x9371 | 0x9372 | 37745 | 37746 | Summation 2 Average Current | float | R | 2
| 0x9373 | 0x9374 | 37747 | 37748 | Summation 2 Active Power | float | R | 2
| 0x9375 | 0x9376 | 37749 | 37750 | Summation 2 Reactive Power | float | R | 2
| 0x9377 | 0x9378 | 37751 | 37752 | Summation 2 Apparent Power | float | R | 2
| 0x9379 | 0x937A | 37753 | 37754 | Summation 2 Power Factor | float | R | 2
| 0x937B | 0x937C | 37755 | 37756 | Summation 2 Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
Unbalance V | 0x937D | 0x937E | 37757 | 37758 | Voltage Unbalance Negative | float | R | 2
| 0x937F | 0x9380 | 37759 | 37760 | Voltage Unbalance Zero | float | R | 2
| 0x9381 | 0x9382 | 37761 | 37762 | Voltage Zero Sequnece Real Part | float | R | 2
| 0x9383 | 0x9384 | 37763 | 37764 | Voltage Zero Sequence Imaginary Part | float | R | 2
| 0x9385 | 0x9386 | 37765 | 37766 | Voltage Positive Sequence Real Part | float | R | 2
| 0x9387 | 0x9388 | 37767 | 37768 | Voltage Positive Sequence Imaginary Part | float | R | 2
| 0x9389 | 0x938A | 37769 | 37770 | Voltage Negative Sequence Real Part | float | R | 2
| 0x938B | 0x938C | 37771 | 37772 | Voltage Negative Sequence Imaginary Part | float | R | 2
Unbalance I | 0x938D | 0x938E | 37773 | 37774 | Current Unbalance Negative | float | R | 2
| 0x938F | 0x9390 | 37775 | 37776 | Current Unbalance Zero | float | R | 2
| 0x9391 | 0x9392 | 37777 | 37778 | Current Zero Sequnece Real Part | float | R | 2
| 0x9393 | 0x9394 | 37779 | 37780 | Current Zero Sequence Imaginary Part | float | R | 2
| 0x9395 | 0x9396 | 37781 | 37782 | Current Positive Sequence Real Part | float | R | 2
| 0x9397 | 0x9398 | 37783 | 37784 | Current Positive Sequence Imaginary Part | float | R | 2
| 0x9399 | 0x939A | 37785 | 37786 | Current Negative Sequence Real Part | float | R | 2
| 0x939B | 0x939C | 37787 | 37788 | Current Negative Sequence Imaginary Part | float | R | 2
157
Harmonic V | 0x93DC | 0x945B | 37852 | 37979 | Phase A 1-64st Voltage Magnitude Harmonics | float | R | 128
| 0x945C | 0x94DB | 37980 | 38107 | Phase A 1-64st Voltage Harmonics Group | float | R | 128
| 0x94DC | 0x955B | 38108 | 38235 | Phase A 1-64st Voltage Angle Harmonics | float | R | 128
| 0x955C | 0x95DB | 38236 | 38363 | Phase B 1-64st Voltage Magnitude Harmonics | float | R | 128
| 0x95DC | 0x965B | 38364 | 38491 | Phase B 1-64st Voltage Harmonics Group | float | R | 128
| 0x965C | 0x96DB | 38492 | 38619 | Phase B 1-64st Voltage Angle Harmonics | float | R | 128
| 0x96DC | 0x975B | 38620 | 38747 | Phase C 1-64st Voltage Magnitude Harmonics | float | R | 128
| 0x975C | 0x97DB | 38748 | 38875 | Phase C 1-64st Voltage Harmonics Group | float | R | 128
| 0x97DC | 0x985B | 38876 | 39003 | Phase C 1-64st Voltage Angle Harmonics | float | R | 128
| 0x985C | 0x985D | 39004 | 39005 | Phase A Voltage THD | float | R | 2
| 0x985E | 0x985F | 39006 | 39007 | Phase A Voltage THD Odd | float | R | 2
| 0x9860 | 0x9861 | 39008 | 39009 | Phase A Voltage THD Even | float | R | 2
| 0x9862 | 0x9863 | 39010 | 39011 | Phase A Voltage Crest Factor | float | R | 2
| 0x9864 | 0x9865 | 39012 | 39013 | Phase A Voltage Fundamental RMS | float | R | 2
| 0x9866 | 0x9867 | 39014 | 39015 | Phase B Voltage THD | float | R | 2
| 0x9868 | 0x9869 | 39016 | 39017 | Phase B Voltage THD Odd | float | R | 2
| 0x986A | 0x986B | 39018 | 39019 | Phase B Voltage THD Even | float | R | 2
| 0x986C | 0x986D | 39020 | 39021 | Phase B Voltage Crest Factor | float | R | 2
| 0x986E | 0x986F | 39022 | 39023 | Phase B Voltage Fundamental RMS | float | R | 2
| 0x9870 | 0x9871 | 39024 | 39025 | Phase C Voltage THD | float | R | 2
| 0x9872 | 0x9873 | 39026 | 39027 | Phase C Voltage THD Odd | float | R | 2
| 0x9874 | 0x9875 | 39028 | 39029 | Phase C Voltage THD Even | float | R | 2
| 0x9876 | 0x9877 | 39030 | 39031 | Phase C Voltage Crest Factor | float | R | 2
| 0x9878 | 0x9879 | 39032 | 39033 | Phase C Voltage Fundamental RMS | float | R | 2
| 0x987A | 0x987B | 39034 | 39035 | Average Voltage THD | float | R | 2
| 0x987C | 0x987D | 39036 | 39037 | Average Voltage THD Odd | float | R | 2
| 0x987E | 0x987F | 39038 | 39039 | Average Voltage THD Even | float | R | 2
Harmonic I | 0x9880 | 0x98FF | 39040 | 39167 | Phase A 1-64st Current Magnitude Harmonics | float | R | 128
| 0x9900 | 0x997F | 39168 | 39295 | Phase A 1-64st Current Harmonics Group | float | R | 128
| 0x9980 | 0x99FF | 39296 | 39423 | Phase A 1-64st Current Angle Harmonics | float | R | 128
| 0x9A00 | 0x9A7F | 39424 | 39551 | Phase B 1-64st Current Magnitude Harmonics | float | R | 128
| 0x9A80 | 0x9AFF | 39552 | 39679 | Phase B 1-64st Current Harmonics Group | float | R | 128
| 0x9B00 | 0x9B7F | 39680 | 39807 | Phase B 1-64st Current Angle Harmonics | float | R | 128
| 0x9B80 | 0x9BFF | 39808 | 39935 | Phase C 1-64st Current Magnitude Harmonics | float | R | 128
| 0x9C00 | 0x9C7F | 39936 | 40063 | Phase C 1-64st Current Harmonics Group | float | R | 128
| 0x9C80 | 0x9CFF | 40064 | 40191 | Phase C 1-64st Current Angle Harmonics | float | R | 128
| 0x9D00 | 0x9D7F | 40192 | 40319 | Neutral 1-64st Current Magnitude Harmonics | float | R | 128
| 0x9D80 | 0x9DFF | 40320 | 40447 | Neutral 1-64st Current Harmonics Group | float | R | 128
| 0x9E00 | 0x9E7F | 40448 | 40575 | Neutral 1-64st Current Angle Harmonics | float | R | 128
| 0x9E80 | 0x9E81 | 40576 | 40577 | Phase A Current THD | float | R | 2
| 0x9E82 | 0x9E83 | 40578 | 40579 | Phase A Current THD Odd | float | R | 2
| 0x9E84 | 0x9E85 | 40580 | 40581 | Phase A Current THD Even | float | R | 2
| 0x9E86 | 0x9E87 | 40582 | 40583 | Phase A Current Crest-Factor | float | R | 2
| 0x9E88 | 0x9E89 | 40584 | 40585 | Phase A Current Fundamental RMS | float | R | 2
| 0x9E8A | 0x9E8B | 40586 | 40587 | Phase A Current K-Factor | float | R | 2
| 0x9E8C | 0x9E8D | 40588 | 40589 | Phase A Current TDD | float | R | 2
| 0x9E8E | 0x9E8F | 40590 | 40591 | Phase B Current THD | float | R | 2
| 0x9E90 | 0x9E91 | 40592 | 40593 | Phase B Current THD Odd | float | R | 2
| 0x9E92 | 0x9E93 | 40594 | 40595 | Phase B Current THD Even | float | R | 2
| 0x9E94 | 0x9E95 | 40596 | 40597 | Phase B Current Crest-Factor | float | R | 2
| 0x9E96 | 0x9E97 | 40598 | 40599 | Phase B Current Fundamental RMS | float | R | 2
| 0x9E98 | 0x9E99 | 40600 | 40601 | Phase B Current K-Factor | float | R | 2
| 0x9E9A | 0x9E9B | 40602 | 40603 | Phase B Current TDD | float | R | 2
| 0x9E9C | 0x9E9D | 40604 | 40605 | Phase C Current THD | float | R | 2
| 0x9E9E | 0x9E9F | 40606 | 40607 | Phase C Current THD Odd | float | R | 2
| 0x9EA0 | 0x9EA1 | 40608 | 40609 | Phase C Current THD Even | float | R | 2
| 0x9EA2 | 0x9EA3 | 40610 | 40611 | Phase C Current Crest-Factor | float | R | 2
| 0x9EA4 | 0x9EA5 | 40612 | 40613 | Phase C Current Fundamental RMS | float | R | 2
| 0x9EA6 | 0x9EA7 | 40614 | 40615 | Phase C Current K-Factor | float | R | 2
| 0x9EA8 | 0x9EA9 | 40616 | 40617 | Phase C Current TDD | float | R | 2
| 0x9EAA | 0x9EAB | 40618 | 40619 | Neutral Current THD | float | R | 2
| 0x9EAC | 0x9EAD | 40620 | 40621 | Neutral Current THD Odd | float | R | 2
| 0x9EAE | 0x9EAF | 40622 | 40623 | Neutral Current THD Even | float | R | 2
| 0x9EB0 | 0x9EB1 | 40624 | 40625 | Neutral Current Crest-Factor | float | R | 2
| 0x9EB2 | 0x9EB3 | 40626 | 40627 | Neutral Current FFTRms | float | R | 2
| 0x9EB4 | 0x9EB5 | 40628 | 40629 | Neutral Current K-Factor | float | R | 2
| 0x9EB6 | 0x9EB7 | 40630 | 40631 | Neutral Current TDD | float | R | 2
| 0x9EB8 | 0x9EB9 | 40632 | 40633 | Average Current THD | float | R | 2
| 0x9EBA | 0x9EBB | 40634 | 40635 | Average Current THD Odd | float | R | 2
| 0x9EBC | 0x9EBD | 40636 | 40637 | Average Current THD Even | float | R | 2
2786
5886

## 3S Aggregation
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data Type | RW | Reg Num | Range | Default
RMS(150、180 cycle) | 0x9F22 | 0x9F25 | 40738 | 40741 | Aggr 3sec Param Update Time Stamp | uint64_t | R | 4
| 0x9F26 | 0x9F26 | 40742 | 40742 | Aggr 3sec Param Valid Flag（50160） | uint16_t | R | 1
| 0x9F27 | 0x9F27 | 40743 | 40743 | Aggr 3sec Param Event status | uint16_t | R | 1
| 0x9F28 | 0x9F28 | 40744 | 40744 | Aggr 3sec Param Block Number | uint16_t | R | 1
| 0x9F29 | 0x9F2A | 40745 | 40746 | Aggr 3sec System Frequency | float | R | 2
| 0x9F2B | 0x9F2C | 40747 | 40748 | Aggr 3sec Phase A Line-to-Neutral Voltage | float | R | 2
| 0x9F2D | 0x9F2E | 40749 | 40750 | Aggr 3sec Phase B Line-to-Neutral Voltage | float | R | 2
| 0x9F2F | 0x9F30 | 40751 | 40752 | Aggr 3sec Phase C Line-to-Neutral Voltage | float | R | 2
| 0x9F31 | 0x9F32 | 40753 | 40754 | Aggr 3sec Phase A Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x9F33 | 0x9F34 | 40755 | 40756 | Aggr 3sec Phase B Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x9F35 | 0x9F36 | 40757 | 40758 | Aggr 3sec Phase C Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x9F37 | 0x9F38 | 40759 | 40760 | Aggr 3sec Average Line-to-Neutral Voltage | float | R | 2
| 0x9F39 | 0x9F3A | 40761 | 40762 | Aggr 3sec Phase AB Line-to-Line Voltage | float | R | 2
| 0x9F3B | 0x9F3C | 40763 | 40764 | Aggr 3sec Phase BC Line-to-Line Voltage | float | R | 2
| 0x9F3D | 0x9F3E | 40765 | 40766 | Aggr 3sec Phase CA Line-to-Line Voltage | float | R | 2
| 0x9F3F | 0x9F40 | 40767 | 40768 | Aggr 3sec Phase A Line-to-Line Voltage Phase Angle | float | R | 2
| 0x9F41 | 0x9F42 | 40769 | 40770 | Aggr 3sec Phase B Line-to-Line Voltage Phase Angle | float | R | 2
| 0x9F43 | 0x9F44 | 40771 | 40772 | Aggr 3sec Phase C Line-to-Line Voltage Phase Angle | float | R | 2
| 0x9F45 | 0x9F46 | 40773 | 40774 | Aggr 3sec Average Line-to-Line Voltage | float | R | 2
| 0x9F47 | 0x9F48 | 40775 | 40776 | Aggr 3sec Phase A Current | float | R | 2
| 0x9F49 | 0x9F4A | 40777 | 40778 | Aggr 3sec Phase B Current | float | R | 2
| 0x9F4B | 0x9F4C | 40779 | 40780 | Aggr 3sec Phase C Current | float | R | 2
| 0x9F4D | 0x9F4E | 40781 | 40782 | Aggr 3sec Neutral Current | float | R | 2
| 0x9F4F | 0x9F50 | 40783 | 40784 | Aggr 3sec Phase A Current Phase Angle | float | R | 2
| 0x9F51 | 0x9F52 | 40785 | 40786 | Aggr 3sec Phase B Current Phase Angle | float | R | 2
| 0x9F53 | 0x9F54 | 40787 | 40788 | Aggr 3sec Phase C Current Phase Angle | float | R | 2
| 0x9F55 | 0x9F56 | 40789 | 40790 | Aggr 3sec Neutral Current Phase Angle | float | R | 2
| 0x9F57 | 0x9F58 | 40791 | 40792 | Aggr 3sec Average Current | float | R | 2
| 0x9F59 | 0x9F5A | 40793 | 40794 | Aggr 3sec Phase A Active Power | float | R | 2
| 0x9F5B | 0x9F5C | 40795 | 40796 | Aggr 3sec Phase B Active Power | float | R | 2
| 0x9F5D | 0x9F5E | 40797 | 40798 | Aggr 3sec Phase C Active Power | float | R | 2
| 0x9F5F | 0x9F60 | 40799 | 40800 | Aggr 3sec System Active Power | float | R | 2
| 0x9F61 | 0x9F62 | 40801 | 40802 | Aggr 3sec Phase A Reactive Power | float | R | 2
| 0x9F63 | 0x9F64 | 40803 | 40804 | Aggr 3sec Phase B Reactive Power | float | R | 2
| 0x9F65 | 0x9F66 | 40805 | 40806 | Aggr 3sec Phase C Reactive Power | float | R | 2
| 0x9F67 | 0x9F68 | 40807 | 40808 | Aggr 3sec System Reactive Power | float | R | 2
| 0x9F69 | 0x9F6A | 40809 | 40810 | Aggr 3sec Phase A Apparent Power | float | R | 2
| 0x9F6B | 0x9F6C | 40811 | 40812 | Aggr 3sec Phase B Apparent Power | float | R | 2
| 0x9F6D | 0x9F6E | 40813 | 40814 | Aggr 3sec Phase C Apparent Power | float | R | 2
| 0x9F6F | 0x9F70 | 40815 | 40816 | Aggr 3sec System Apparent Power | float | R | 2
| 0x9F71 | 0x9F72 | 40817 | 40818 | Aggr 3sec Phase A Power Factor | float | R | 2
| 0x9F73 | 0x9F74 | 40819 | 40820 | Aggr 3sec Phase B Power Factor | float | R | 2
| 0x9F75 | 0x9F76 | 40821 | 40822 | Aggr 3sec Phase C Power Factor | float | R | 2
| 0x9F77 | 0x9F78 | 40823 | 40824 | Aggr 3sec System Power Factor | float | R | 2
| 0x9F79 | 0x9F7A | 40825 | 40826 | Aggr 3sec Phase A Displacement Power Factor | float | R | 2
| 0x9F7B | 0x9F7C | 40827 | 40828 | Aggr 3sec Phase B Displacement Power Factor | float | R | 2
| 0x9F7D | 0x9F7E | 40829 | 40830 | Aggr 3sec Phase C Displacement Power Factor | float | R | 2
| 0x9F7F | 0x9F80 | 40831 | 40832 | Aggr 3sec Phase A Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
| 0x9F81 | 0x9F82 | 40833 | 40834 | Aggr 3sec Phase B Load Nature | uint32_t | R | 2
| 0x9F83 | 0x9F84 | 40835 | 40836 | Aggr 3sec Phase C Load Nature | uint32_t | R | 2
| 0x9F85 | 0x9F86 | 40837 | 40838 | Aggr 3sec System Load Nature | uint32_t | R | 2
| 0x9F87 | 0x9F88 | 40839 | 40840 | Aggr 3sec Channel 4 Active Power | float | R | 2
| 0x9F89 | 0x9F8A | 40841 | 40842 | Aggr 3sec Channel 4 Reactive Power | float | R | 2
| 0x9F8B | 0x9F8C | 40843 | 40844 | Aggr 3sec Channel 4 Apparent Power | float | R | 2
| 0x9F8D | 0x9F8E | 40845 | 40846 | Aggr 3sec Channel 4 Power Factor | float | R | 2
| 0x9F8F | 0x9F90 | 40847 | 40848 | Aggr 3sec Channel 4 Displacement Power Factor | float | R | 2
| 0x9F91 | 0x9F92 | 40849 | 40850 | Aggr 3sec Channel 4 Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
| 0x9F93 | 0x9F94 | 40851 | 40852 | Aggr 3sec Summation 2 Average Current | float | R | 2
| 0x9F95 | 0x9F96 | 40853 | 40854 | Aggr 3sec Summation 2 Active Power | float | R | 2
| 0x9F97 | 0x9F98 | 40855 | 40856 | Aggr 3sec Summation 2 Reactive Power | float | R | 2
| 0x9F99 | 0x9F9A | 40857 | 40858 | Aggr 3sec Summation 2 Apparent Power | float | R | 2
| 0x9F9B | 0x9F9C | 40859 | 40860 | Aggr 3sec Summation 2 Power Factor | float | R | 2
| 0x9F9D | 0x9F9E | 40861 | 40862 | Aggr 3sec Summation 2 Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
Unbalance V | 0x9F9F | 0x9FA0 | 40863 | 40864 | Aggr 3sec Voltage Unbalance Negative | float | R | 2
| 0x9FA1 | 0x9FA2 | 40865 | 40866 | Aggr 3sec Voltage Unbalance Zero | float | R | 2
| 0x9FA3 | 0x9FA4 | 40867 | 40868 | Aggr 3sec Voltage Zero Sequnece Real Part | float | R | 2
| 0x9FA5 | 0x9FA6 | 40869 | 40870 | Aggr 3sec Voltage Zero Sequence Imaginary Part | float | R | 2
| 0x9FA7 | 0x9FA8 | 40871 | 40872 | Aggr 3sec Voltage Positive Sequence Real Part | float | R | 2
| 0x9FA9 | 0x9FAA | 40873 | 40874 | Aggr 3sec Voltage Positive Sequence Imaginary Part | float | R | 2
| 0x9FAB | 0x9FAC | 40875 | 40876 | Aggr 3sec Voltage Negative Sequence Real Part | float | R | 2
| 0x9FAD | 0x9FAE | 40877 | 40878 | Aggr 3sec Voltage Negative Sequence Imaginary Part | float | R | 2
Unbalance I | 0x9FAF | 0x9FB0 | 40879 | 40880 | Aggr 3sec Current Unbalance Negative | float | R | 2
| 0x9FB1 | 0x9FB2 | 40881 | 40882 | Aggr 3sec Current Unbalance Zero | float | R | 2
| 0x9FB3 | 0x9FB4 | 40883 | 40884 | Aggr 3sec Current Zero Sequnece Real Part | float | R | 2
| 0x9FB5 | 0x9FB6 | 40885 | 40886 | Aggr 3sec Current Zero Sequence Imaginary Part | float | R | 2
| 0x9FB7 | 0x9FB8 | 40887 | 40888 | Aggr 3sec Current Positive Sequence Real Part | float | R | 2
| 0x9FB9 | 0x9FBA | 40889 | 40890 | Aggr 3sec Current Positive Sequence Imaginary Part | float | R | 2
| 0x9FBB | 0x9FBC | 40891 | 40892 | Aggr 3sec Current Negative Sequence Real Part | float | R | 2
| 0x9FBD | 0x9FBE | 40893 | 40894 | Aggr 3sec Current Negative Sequence Imaginary Part | float | R | 2
157
Harmonic V | 0x9FFE | 0xA07D | 40958 | 41085 | Aggr 3sec Phase A 1-64st Voltage Magnitude Harmonics | float | R | 128
| 0xA07E | 0xA0FD | 41086 | 41213 | Aggr 3sec Phase A 1-64st Voltage Harmonics Group | float | R | 128
| 0xA0FE | 0xA17D | 41214 | 41341 | Aggr 3sec Phase A 1-64st Voltage Angle Harmonics | float | R | 128
| 0xA17E | 0xA1FD | 41342 | 41469 | Aggr 3sec Phase B 1-64st Voltage Magnitude Harmonics | float | R | 128
| 0xA1FE | 0xA27D | 41470 | 41597 | Aggr 3sec Phase B 1-64st Voltage Harmonics Group | float | R | 128
| 0xA27E | 0xA2FD | 41598 | 41725 | Aggr 3sec Phase B 1-64st Voltage Angle Harmonics | float | R | 128
| 0xA2FE | 0xA37D | 41726 | 41853 | Aggr 3sec Phase C 1-64st Voltage Magnitude Harmonics | float | R | 128
| 0xA37E | 0xA3FD | 41854 | 41981 | Aggr 3sec Phase C 1-64st Voltage Harmonics Group | float | R | 128
| 0xA3FE | 0xA47D | 41982 | 42109 | Aggr 3sec Phase C 1-64st Voltage Angle Harmonics | float | R | 128
| 0xA47E | 0xA47F | 42110 | 42111 | Aggr 3sec Phase A Voltage THD | float | R | 2
| 0xA480 | 0xA481 | 42112 | 42113 | Aggr 3sec Phase A Voltage THD Odd | float | R | 2
| 0xA482 | 0xA483 | 42114 | 42115 | Aggr 3sec Phase A Voltage THD Even | float | R | 2
| 0xA484 | 0xA485 | 42116 | 42117 | Aggr 3sec Phase A Voltage Crest Factor | float | R | 2
| 0xA486 | 0xA487 | 42118 | 42119 | Aggr 3sec Phase A Voltage Fundamental RMS | float | R | 2
| 0xA488 | 0xA489 | 42120 | 42121 | Aggr 3sec Phase B Voltage THD | float | R | 2
| 0xA48A | 0xA48B | 42122 | 42123 | Aggr 3sec Phase B Voltage THD Odd | float | R | 2
| 0xA48C | 0xA48D | 42124 | 42125 | Aggr 3sec Phase B Voltage THD Even | float | R | 2
| 0xA48E | 0xA48F | 42126 | 42127 | Aggr 3sec Phase B Voltage Crest Factor | float | R | 2
| 0xA490 | 0xA491 | 42128 | 42129 | Aggr 3sec Phase B Voltage Fundamental RMS | float | R | 2
| 0xA492 | 0xA493 | 42130 | 42131 | Aggr 3sec Phase C Voltage THD | float | R | 2
| 0xA494 | 0xA495 | 42132 | 42133 | Aggr 3sec Phase C Voltage THD Odd | float | R | 2
| 0xA496 | 0xA497 | 42134 | 42135 | Aggr 3sec Phase C Voltage THD Even | float | R | 2
| 0xA498 | 0xA499 | 42136 | 42137 | Aggr 3sec Phase C Voltage Crest Factor | float | R | 2
| 0xA49A | 0xA49B | 42138 | 42139 | Aggr 3sec Phase C Voltage Fundamental RMS | float | R | 2
| 0xA49C | 0xA49D | 42140 | 42141 | Aggr 3sec Average Voltage THD | float | R | 2
| 0xA49E | 0xA49F | 42142 | 42143 | Aggr 3sec Average Voltage THD Odd | float | R | 2
| 0xA4A0 | 0xA4A1 | 42144 | 42145 | Aggr 3sec Average Voltage THD Even | float | R | 2
Harmonic I | 0xA4A2 | 0xA521 | 42146 | 42273 | Aggr 3sec Phase A 1-64st Current Magnitude Harmonics | float | R | 128
| 0xA522 | 0xA5A1 | 42274 | 42401 | Aggr 3sec Phase A 1-64st Current Harmonics Group | float | R | 128
| 0xA5A2 | 0xA621 | 42402 | 42529 | Aggr 3sec Phase A 1-64st Current Angle Harmonics | float | R | 128
| 0xA622 | 0xA6A1 | 42530 | 42657 | Aggr 3sec Phase B 1-64st Current Magnitude Harmonics | float | R | 128
| 0xA6A2 | 0xA721 | 42658 | 42785 | Aggr 3sec Phase B 1-64st Current Harmonics Group | float | R | 128
| 0xA722 | 0xA7A1 | 42786 | 42913 | Aggr 3sec Phase B 1-64st Current Angle Harmonics | float | R | 128
| 0xA7A2 | 0xA821 | 42914 | 43041 | Aggr 3sec Phase C 1-64st Current Magnitude Harmonics | float | R | 128
| 0xA822 | 0xA8A1 | 43042 | 43169 | Aggr 3sec Phase C 1-64st Current Harmonics Group | float | R | 128
| 0xA8A2 | 0xA921 | 43170 | 43297 | Aggr 3sec Phase C 1-64st Current Angle Harmonics | float | R | 128
| 0xA922 | 0xA9A1 | 43298 | 43425 | Aggr 3sec Neutral 1-64st Current Magnitude Harmonics | float | R | 128
| 0xA9A2 | 0xAA21 | 43426 | 43553 | Aggr 3sec Neutral 1-64st Current Harmonics Group | float | R | 128
| 0xAA22 | 0xAAA1 | 43554 | 43681 | Aggr 3sec Neutral 1-64st Current Angle Harmonics | float | R | 128
| 0xAAA2 | 0xAAA3 | 43682 | 43683 | Aggr 3sec Phase A Current THD | float | R | 2
| 0xAAA4 | 0xAAA5 | 43684 | 43685 | Aggr 3sec Phase A Current THD Odd | float | R | 2
| 0xAAA6 | 0xAAA7 | 43686 | 43687 | Aggr 3sec Phase A Current THD Even | float | R | 2
| 0xAAA8 | 0xAAA9 | 43688 | 43689 | Aggr 3sec Phase A Current Crest-Factor | float | R | 2
| 0xAAAA | 0xAAAB | 43690 | 43691 | Aggr 3sec Phase A Current Fundamental RMS | float | R | 2
| 0xAAAC | 0xAAAD | 43692 | 43693 | Aggr 3sec Phase A Current K-Factor | float | R | 2
| 0xAAAE | 0xAAAF | 43694 | 43695 | Aggr 3sec Phase A Current TDD | float | R | 2
| 0xAAB0 | 0xAAB1 | 43696 | 43697 | Aggr 3sec Phase B Current THD | float | R | 2
| 0xAAB2 | 0xAAB3 | 43698 | 43699 | Aggr 3sec Phase B Current THD Odd | float | R | 2
| 0xAAB4 | 0xAAB5 | 43700 | 43701 | Aggr 3sec Phase B Current THD Even | float | R | 2
| 0xAAB6 | 0xAAB7 | 43702 | 43703 | Aggr 3sec Phase B Current Crest-Factor | float | R | 2
| 0xAAB8 | 0xAAB9 | 43704 | 43705 | Aggr 3sec Phase B Current Fundamental RMS | float | R | 2
| 0xAABA | 0xAABB | 43706 | 43707 | Aggr 3sec Phase B Current K-Factor | float | R | 2
| 0xAABC | 0xAABD | 43708 | 43709 | Aggr 3sec Phase B Current TDD | float | R | 2
| 0xAABE | 0xAABF | 43710 | 43711 | Aggr 3sec Phase C Current THD | float | R | 2
| 0xAAC0 | 0xAAC1 | 43712 | 43713 | Aggr 3sec Phase C Current THD Odd | float | R | 2
| 0xAAC2 | 0xAAC3 | 43714 | 43715 | Aggr 3sec Phase C Current THD Even | float | R | 2
| 0xAAC4 | 0xAAC5 | 43716 | 43717 | Aggr 3sec Phase C Current Crest-Factor | float | R | 2
| 0xAAC6 | 0xAAC7 | 43718 | 43719 | Aggr 3sec Phase C Current Fundamental RMS | float | R | 2
| 0xAAC8 | 0xAAC9 | 43720 | 43721 | Aggr 3sec Phase C Current K-Factor | float | R | 2
| 0xAACA | 0xAACB | 43722 | 43723 | Aggr 3sec Phase C Current TDD | float | R | 2
| 0xAACC | 0xAACD | 43724 | 43725 | Aggr 3sec Neutral Current THD | float | R | 2
| 0xAACE | 0xAACF | 43726 | 43727 | Aggr 3sec Neutral Current THD Odd | float | R | 2
| 0xAAD0 | 0xAAD1 | 43728 | 43729 | Aggr 3sec Neutral Current THD Even | float | R | 2
| 0xAAD2 | 0xAAD3 | 43730 | 43731 | Aggr 3sec Neutral Current Crest-Factor | float | R | 2
| 0xAAD4 | 0xAAD5 | 43732 | 43733 | Aggr 3sec Neutral Current Fundamental RMS | float | R | 2
| 0xAAD6 | 0xAAD7 | 43734 | 43735 | Aggr 3sec Neutral Current K-Factor | float | R | 2
| 0xAAD8 | 0xAAD9 | 43736 | 43737 | Aggr 3sec Neutral Current TDD | float | R | 2
| 0xAADA | 0xAADB | 43738 | 43739 | Aggr 3sec Average Current THD | float | R | 2
| 0xAADC | 0xAADD | 43740 | 43741 | Aggr 3sec Average Current THD Odd | float | R | 2
| 0xAADE | 0xAADF | 43742 | 43743 | Aggr 3sec Average Current THD Even | float | R | 2
Flicker Pinst Max | 0xAAE0 | 0xAAE1 | 43744 | 43745 | Aggr 3sec Phase A Flicker Pinst Max | float | R | 2
| 0xAAE2 | 0xAAE3 | 43746 | 43747 | Aggr 3sec Phase B Flicker Pinst Max | float | R | 2
| 0xAAE4 | 0xAAE5 | 43748 | 43749 | Aggr 3sec Phase C Flicker Pinst Max | float | R | 2
2792

## 10min Aggregation
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data Type | RW | Reg Num | Range | Default
RMS(10 min) | 0xAB50 | 0xAB53 | 43856 | 43859 | Aggr 10min Param Update Time Stamp | uint64_t | R | 4
| 0xAB54 | 0xAB54 | 43860 | 43860 | Aggr 10min Param Valid Flag（50160） | uint16_t | R | 1
| 0xAB55 | 0xAB55 | 43861 | 43861 | Aggr 10min Param Event status | uint16_t | R | 1
| 0xAB56 | 0xAB56 | 43862 | 43862 | Aggr 10min Param Block Number | uint16_t | R | 1
| 0xAB57 | 0xAB58 | 43863 | 43864 | Aggr 10min System Frequency | float | R | 2
| 0xAB59 | 0xAB5A | 43865 | 43866 | Aggr 10min Phase A Line-to-Neutral Voltage | float | R | 2
| 0xAB5B | 0xAB5C | 43867 | 43868 | Aggr 10min Phase B Line-to-Neutral Voltage | float | R | 2
| 0xAB5D | 0xAB5E | 43869 | 43870 | Aggr 10min Phase C Line-to-Neutral Voltage | float | R | 2
| 0xAB5F | 0xAB60 | 43871 | 43872 | Aggr 10min Phase A Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0xAB61 | 0xAB62 | 43873 | 43874 | Aggr 10min Phase B Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0xAB63 | 0xAB64 | 43875 | 43876 | Aggr 10min Phase C Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0xAB65 | 0xAB66 | 43877 | 43878 | Aggr 10min Average Line-to-Neutral Voltage | float | R | 2
| 0xAB67 | 0xAB68 | 43879 | 43880 | Aggr 10min Phase AB Line-to-Line Voltage | float | R | 2
| 0xAB69 | 0xAB6A | 43881 | 43882 | Aggr 10min Phase BC Line-to-Line Voltage | float | R | 2
| 0xAB6B | 0xAB6C | 43883 | 43884 | Aggr 10min Phase CA Line-to-Line Voltage | float | R | 2
| 0xAB6D | 0xAB6E | 43885 | 43886 | Aggr 10min Phase AB Line-to-Line Voltage Phase Angle | float | R | 2
| 0xAB6F | 0xAB70 | 43887 | 43888 | Aggr 10min Phase BC Line-to-Line Voltage Phase Angle | float | R | 2
| 0xAB71 | 0xAB72 | 43889 | 43890 | Aggr 10min Phase CA Line-to-Line Voltage Phase Angle | float | R | 2
| 0xAB73 | 0xAB74 | 43891 | 43892 | Aggr 10min Average Line-to-Line Voltage | float | R | 2
| 0xAB75 | 0xAB76 | 43893 | 43894 | Aggr 10min Phase A Current | float | R | 2
| 0xAB77 | 0xAB78 | 43895 | 43896 | Aggr 10min Phase B Current | float | R | 2
| 0xAB79 | 0xAB7A | 43897 | 43898 | Aggr 10min Phase C Current | float | R | 2
| 0xAB7B | 0xAB7C | 43899 | 43900 | Aggr 10min Neutral Current | float | R | 2
| 0xAB7D | 0xAB7E | 43901 | 43902 | Aggr 10min Phase A Current Phase Angle | float | R | 2
| 0xAB7F | 0xAB80 | 43903 | 43904 | Aggr 10min Phase B Current Phase Angle | float | R | 2
| 0xAB81 | 0xAB82 | 43905 | 43906 | Aggr 10min Phase C Current Phase Angle | float | R | 2
| 0xAB83 | 0xAB84 | 43907 | 43908 | Aggr 10min Neutral Current Phase Angle | float | R | 2
| 0xAB85 | 0xAB86 | 43909 | 43910 | Aggr 10min Average Current | float | R | 2
| 0xAB87 | 0xAB88 | 43911 | 43912 | Aggr 10min Phase A Active Power | float | R | 2
| 0xAB89 | 0xAB8A | 43913 | 43914 | Aggr 10min Phase B Active Power | float | R | 2
| 0xAB8B | 0xAB8C | 43915 | 43916 | Aggr 10min Phase C Active Power | float | R | 2
| 0xAB8D | 0xAB8E | 43917 | 43918 | Aggr 10min System Active Power | float | R | 2
| 0xAB8F | 0xAB90 | 43919 | 43920 | Aggr 10min Phase A Reactive Power | float | R | 2
| 0xAB91 | 0xAB92 | 43921 | 43922 | Aggr 10min Phase B Reactive Power | float | R | 2
| 0xAB93 | 0xAB94 | 43923 | 43924 | Aggr 10min Phase C Reactive Power | float | R | 2
| 0xAB95 | 0xAB96 | 43925 | 43926 | Aggr 10min System Reactive Power | float | R | 2
| 0xAB97 | 0xAB98 | 43927 | 43928 | Aggr 10min Phase A Apparent Power | float | R | 2
| 0xAB99 | 0xAB9A | 43929 | 43930 | Aggr 10min Phase B Apparent Power | float | R | 2
| 0xAB9B | 0xAB9C | 43931 | 43932 | Aggr 10min Phase C Apparent Power | float | R | 2
| 0xAB9D | 0xAB9E | 43933 | 43934 | Aggr 10min System Apparent Power | float | R | 2
| 0xAB9F | 0xABA0 | 43935 | 43936 | Aggr 10min Phase A Power Factor | float | R | 2
| 0xABA1 | 0xABA2 | 43937 | 43938 | Aggr 10min Phase B Power Factor | float | R | 2
| 0xABA3 | 0xABA4 | 43939 | 43940 | Aggr 10min Phase C Power Factor | float | R | 2
| 0xABA5 | 0xABA6 | 43941 | 43942 | Aggr 10min System Power Factor | float | R | 2
| 0xABA7 | 0xABA8 | 43943 | 43944 | Aggr 10min Phase A Displacement Power Factor | float | R | 2
| 0xABA9 | 0xABAA | 43945 | 43946 | Aggr 10min Phase B Displacement Power Factor | float | R | 2
| 0xABAB | 0xABAC | 43947 | 43948 | Aggr 10min Phase C Displacement Power Factor | float | R | 2
| 0xABAD | 0xABAE | 43949 | 43950 | Aggr 10min Phase A Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
| 0xABAF | 0xABB0 | 43951 | 43952 | Aggr 10min Phase B Load Nature | uint32_t | R | 2
| 0xABB1 | 0xABB2 | 43953 | 43954 | Aggr 10min Phase C Load Nature | uint32_t | R | 2
| 0xABB3 | 0xABB4 | 43955 | 43956 | Aggr 10min System Load Nature | uint32_t | R | 2
| 0xABB5 | 0xABB6 | 43957 | 43958 | Aggr 10min Channel 4 Active Power | float | R | 2
| 0xABB7 | 0xABB8 | 43959 | 43960 | Aggr 10min Channel 4 Reactive Power | float | R | 2
| 0xABB9 | 0xABBA | 43961 | 43962 | Aggr 10min Channel 4 Apparent Power | float | R | 2
| 0xABBB | 0xABBC | 43963 | 43964 | Aggr 10min Channel 4 Power Factor | float | R | 2
| 0xABBD | 0xABBE | 43965 | 43966 | Aggr 10min Channel 4 Displacement Power Factor | float | R | 2
| 0xABBF | 0xABC0 | 43967 | 43968 | Aggr 10min Channel 4 Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
| 0xABC1 | 0xABC2 | 43969 | 43970 | Aggr 10min Summation 2 Average Current | float | R | 2
| 0xABC3 | 0xABC4 | 43971 | 43972 | Aggr 10min Summation 2 Active Power | float | R | 2
| 0xABC5 | 0xABC6 | 43973 | 43974 | Aggr 10min Summation 2 Reactive Power | float | R | 2
| 0xABC7 | 0xABC8 | 43975 | 43976 | Aggr 10min Summation 2 Apparent Power | float | R | 2
| 0xABC9 | 0xABCA | 43977 | 43978 | Aggr 10min Summation 2 Power Factor | float | R | 2
| 0xABCB | 0xABCC | 43979 | 43980 | Aggr 10min Summation 2 Load Nature | uint32_t | R | 2 | 82:Resistive load 76:Inductive load 67:Capacitive load
Unbalance V | 0xABCD | 0xABCE | 43981 | 43982 | Aggr 10min Voltage Unbalance Negative | float | R | 2
| 0xABCF | 0xABD0 | 43983 | 43984 | Aggr 10min Voltage Unbalance Zero | float | R | 2
| 0xABD1 | 0xABD2 | 43985 | 43986 | Aggr 10min Voltage Zero Sequnece Real Part | float | R | 2
| 0xABD3 | 0xABD4 | 43987 | 43988 | Aggr 10min Voltage Zero Sequence Imaginary Part | float | R | 2
| 0xABD5 | 0xABD6 | 43989 | 43990 | Aggr 10min Voltage Positive Sequence Real Part | float | R | 2
| 0xABD7 | 0xABD8 | 43991 | 43992 | Aggr 10min Voltage Positive Sequence Imaginary Part | float | R | 2
| 0xABD9 | 0xABDA | 43993 | 43994 | Aggr 10min Voltage Negative Sequence Real Part | float | R | 2
| 0xABDB | 0xABDC | 43995 | 43996 | Aggr 10min Voltage Negative Sequence Imaginary Part | float | R | 2
Unbalance I | 0xABDD | 0xABDE | 43997 | 43998 | Aggr 10min Current Unbalance Negative | float | R | 2
| 0xABDF | 0xABE0 | 43999 | 44000 | Aggr 10min Current Unbalance Zero | float | R | 2
| 0xABE1 | 0xABE2 | 44001 | 44002 | Aggr 10min Current Zero Sequnece Real Part | float | R | 2
| 0xABE3 | 0xABE4 | 44003 | 44004 | Aggr 10min Current Zero Sequence Imaginary Part | float | R | 2
| 0xABE5 | 0xABE6 | 44005 | 44006 | Aggr 10min Current Positive Sequence Real Part | float | R | 2
| 0xABE7 | 0xABE8 | 44007 | 44008 | Aggr 10min Current Positive Sequence Imaginary Part | float | R | 2
| 0xABE9 | 0xABEA | 44009 | 44010 | Aggr 10min Current Negative Sequence Real Part | float | R | 2
| 0xABEB | 0xABEC | 44011 | 44012 | Aggr 10min Current Negative Sequence Imaginary Part | float | R | 2
157
Harmonic V | 0xAC2C | 0xACAB | 44076 | 44203 | Aggr 10min Phase A 1-64st Voltage Magnitude Harmonics | float | R | 128
| 0xACAC | 0xAD2B | 44204 | 44331 | Aggr 10min Phase A 1-64st Voltage Harmonics Group | float | R | 128
| 0xAD2C | 0xADAB | 44332 | 44459 | Aggr 10min Phase A 1-64st Voltage Angle Harmonics | float | R | 128
| 0xADAC | 0xAE2B | 44460 | 44587 | Aggr 10min Phase B 1-64st Voltage Magnitude Harmonics | float | R | 128
| 0xAE2C | 0xAEAB | 44588 | 44715 | Aggr 10min Phase B 1-64st Voltage Harmonics Group | float | R | 128
| 0xAEAC | 0xAF2B | 44716 | 44843 | Aggr 10min Phase B 1-64st Voltage Angle Harmonics | float | R | 128
| 0xAF2C | 0xAFAB | 44844 | 44971 | Aggr 10min Phase C 1-64st Voltage Magnitude Harmonics | float | R | 128
| 0xAFAC | 0xB02B | 44972 | 45099 | Aggr 10min Phase C 1-64st Voltage Harmonics Group | float | R | 128
| 0xB02C | 0xB0AB | 45100 | 45227 | Aggr 10min Phase C 1-64st Voltage Angle Harmonics | float | R | 128
| 0xB0AC | 0xB0AD | 45228 | 45229 | Aggr 10min Phase A Voltage THD | float | R | 2
| 0xB0AE | 0xB0AF | 45230 | 45231 | Aggr 10min Phase A Voltage THD Odd | float | R | 2
| 0xB0B0 | 0xB0B1 | 45232 | 45233 | Aggr 10min Phase A Voltage THD Even | float | R | 2
| 0xB0B2 | 0xB0B3 | 45234 | 45235 | Aggr 10min Phase A Voltage Crest Factor | float | R | 2
| 0xB0B4 | 0xB0B5 | 45236 | 45237 | Aggr 10min Phase A Voltage Fundamental RMS | float | R | 2
| 0xB0B6 | 0xB0B7 | 45238 | 45239 | Aggr 10min Phase B Voltage THD | float | R | 2
| 0xB0B8 | 0xB0B9 | 45240 | 45241 | Aggr 10min Phase B Voltage THD Odd | float | R | 2
| 0xB0BA | 0xB0BB | 45242 | 45243 | Aggr 10min Phase B Voltage THD Even | float | R | 2
| 0xB0BC | 0xB0BD | 45244 | 45245 | Aggr 10min Phase B Voltage Crest Factor | float | R | 2
| 0xB0BE | 0xB0BF | 45246 | 45247 | Aggr 10min Phase B Voltage Fundamental RMS | float | R | 2
| 0xB0C0 | 0xB0C1 | 45248 | 45249 | Aggr 10min Phase C Voltage THD | float | R | 2
| 0xB0C2 | 0xB0C3 | 45250 | 45251 | Aggr 10min Phase C Voltage THD Odd | float | R | 2
| 0xB0C4 | 0xB0C5 | 45252 | 45253 | Aggr 10min Phase C Voltage THD Even | float | R | 2
| 0xB0C6 | 0xB0C7 | 45254 | 45255 | Aggr 10min Phase C Voltage Crest Factor | float | R | 2
| 0xB0C8 | 0xB0C9 | 45256 | 45257 | Aggr 10min Phase C Voltage Fundamental RMS | float | R | 2
| 0xB0CA | 0xB0CB | 45258 | 45259 | Aggr 10min Average Voltage THD | float | R | 2
| 0xB0CC | 0xB0CD | 45260 | 45261 | Aggr 10min Average Voltage THD Odd | float | R | 2
| 0xB0CE | 0xB0CF | 45262 | 45263 | Aggr 10min Average Voltage THD Even | float | R | 2
Harmonic I | 0xB0D0 | 0xB14F | 45264 | 45391 | Aggr 10min Phase A 1-64st Current Magnitude Harmonics | float | R | 128
| 0xB150 | 0xB1CF | 45392 | 45519 | Aggr 10min Phase A 1-64st Current Harmonics Group | float | R | 128
| 0xB1D0 | 0xB24F | 45520 | 45647 | Aggr 10min Phase A 1-64st Current Angle Harmonics | float | R | 128
| 0xB250 | 0xB2CF | 45648 | 45775 | Aggr 10min Phase B 1-64st Current Magnitude Harmonics | float | R | 128
| 0xB2D0 | 0xB34F | 45776 | 45903 | Aggr 10min Phase B 1-64st Current Harmonics Group | float | R | 128
| 0xB350 | 0xB3CF | 45904 | 46031 | Aggr 10min Phase B 1-64st Current Angle Harmonics | float | R | 128
| 0xB3D0 | 0xB44F | 46032 | 46159 | Aggr 10min Phase C 1-64st Current Magnitude Harmonics | float | R | 128
| 0xB450 | 0xB4CF | 46160 | 46287 | Aggr 10min Phase C 1-64st Current Harmonics Group | float | R | 128
| 0xB4D0 | 0xB54F | 46288 | 46415 | Aggr 10min Phase C 1-64st Current Angle Harmonics | float | R | 128
| 0xB550 | 0xB5CF | 46416 | 46543 | Aggr 10min Neutral 1-64st Current Magnitude Harmonics | float | R | 128
| 0xB5D0 | 0xB64F | 46544 | 46671 | Aggr 10min Neutral 1-64st Current Harmonics Group | float | R | 128
| 0xB650 | 0xB6CF | 46672 | 46799 | Aggr 10min Neutral 1-64st Current Angle Harmonics | float | R | 128
| 0xB6D0 | 0xB6D1 | 46800 | 46801 | Aggr 10min Phase A Current THD | float | R | 2
| 0xB6D2 | 0xB6D3 | 46802 | 46803 | Aggr 10min Phase A Current THD Odd | float | R | 2
| 0xB6D4 | 0xB6D5 | 46804 | 46805 | Aggr 10min Phase A Current THD Even | float | R | 2
| 0xB6D6 | 0xB6D7 | 46806 | 46807 | Aggr 10min Phase A Current Crest-Factor | float | R | 2
| 0xB6D8 | 0xB6D9 | 46808 | 46809 | Aggr 10min Phase A Current Fundamental RMS | float | R | 2
| 0xB6DA | 0xB6DB | 46810 | 46811 | Aggr 10min Phase A Current K-Factor | float | R | 2
| 0xB6DC | 0xB6DD | 46812 | 46813 | Aggr 10min Phase A Current TDD | float | R | 2
| 0xB6DE | 0xB6DF | 46814 | 46815 | Aggr 10min Phase B Current THD | float | R | 2
| 0xB6E0 | 0xB6E1 | 46816 | 46817 | Aggr 10min Phase B Current THD Odd | float | R | 2
| 0xB6E2 | 0xB6E3 | 46818 | 46819 | Aggr 10min Phase B Current THD Even | float | R | 2
| 0xB6E4 | 0xB6E5 | 46820 | 46821 | Aggr 10min Phase B Current Crest-Factor | float | R | 2
| 0xB6E6 | 0xB6E7 | 46822 | 46823 | Aggr 10min Phase B Current Fundamental RMS | float | R | 2
| 0xB6E8 | 0xB6E9 | 46824 | 46825 | Aggr 10min Phase B Current K-Factor | float | R | 2
| 0xB6EA | 0xB6EB | 46826 | 46827 | Aggr 10min Phase B Current TDD | float | R | 2
| 0xB6EC | 0xB6ED | 46828 | 46829 | Aggr 10min Phase C Current THD | float | R | 2
| 0xB6EE | 0xB6EF | 46830 | 46831 | Aggr 10min Phase C Current THD Odd | float | R | 2
| 0xB6F0 | 0xB6F1 | 46832 | 46833 | Aggr 10min Phase C Current THD Even | float | R | 2
| 0xB6F2 | 0xB6F3 | 46834 | 46835 | Aggr 10min Phase C Current Crest-Factor | float | R | 2
| 0xB6F4 | 0xB6F5 | 46836 | 46837 | Aggr 10min Phase C Current Fundamental RMS | float | R | 2
| 0xB6F6 | 0xB6F7 | 46838 | 46839 | Aggr 10min Phase C Current K-Factor | float | R | 2
| 0xB6F8 | 0xB6F9 | 46840 | 46841 | Aggr 10min Phase C Current TDD | float | R | 2
| 0xB6FA | 0xB6FB | 46842 | 46843 | Aggr 10min Neutral Current THD | float | R | 2
| 0xB6FC | 0xB6FD | 46844 | 46845 | Aggr 10min Neutral Current THD Odd | float | R | 2
| 0xB6FE | 0xB6FF | 46846 | 46847 | Aggr 10min Neutral Current THD Even | float | R | 2
| 0xB700 | 0xB701 | 46848 | 46849 | Aggr 10min Neutral Current Crest-Factor | float | R | 2
| 0xB702 | 0xB703 | 46850 | 46851 | Aggr 10min Neutral Current Fundamental RMS | float | R | 2
| 0xB704 | 0xB705 | 46852 | 46853 | Aggr 10min Neutral Current K-Factor | float | R | 2
| 0xB706 | 0xB707 | 46854 | 46855 | Aggr 10min Neutral Current TDD | float | R | 2
| 0xB708 | 0xB709 | 46856 | 46857 | Aggr 10min Average Current THD | float | R | 2
| 0xB70A | 0xB70B | 46858 | 46859 | Aggr 10min Average Current THD Odd | float | R | 2
| 0xB70C | 0xB70D | 46860 | 46861 | Aggr 10min Average Current THD Even | float | R | 2
Flicker Pst | 0xB70E | 0xB70F | 46862 | 46863 | Aggr 10min Phase A Flicker Pst | float | R | 2
| 0xB710 | 0xB711 | 46864 | 46865 | Aggr 10min Phase B Flicker Pst | float | R | 2
| 0xB712 | 0xB713 | 46866 | 46867 | Aggr 10min Phase C Flicker Pst | float | R | 2
2792
5898

## 2hr Aggregation
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data Type | Reg Num | RW | Range | Default
RMS(2 hr) | 0xB77E | 0xB781 | 46974 | 46977 | Aggr 2hr Param Update Time Stamp | uint64_t | 4 | R
| 0xB782 | 0xB782 | 46978 | 46978 | Aggr 2hr Param Valid Flag（50160） | uint16_t | 1 | R
| 0xB783 | 0xB783 | 46979 | 46979 | Aggr 2hr Param Event status | uint16_t | 1 | R
| 0xB784 | 0xB784 | 46980 | 46980 | Aggr 2hr Param Block Number | uint16_t | 1 | R
| 0xB785 | 0xB786 | 46981 | 46982 | Aggr 2hr System Frequency | float | 2 | R
| 0xB787 | 0xB788 | 46983 | 46984 | Aggr 2hr Phase A Line-to-Neutral Voltage | float | 2 | R
| 0xB789 | 0xB78A | 46985 | 46986 | Aggr 2hr Phase B Line-to-Neutral Voltage | float | 2 | R
| 0xB78B | 0xB78C | 46987 | 46988 | Aggr 2hr Phase C Line-to-Neutral Voltage | float | 2 | R
| 0xB78D | 0xB78E | 46989 | 46990 | Aggr 2hr Phase A Line-to-Neutral Voltage Phase Angle | float | 2 | R
| 0xB78F | 0xB790 | 46991 | 46992 | Aggr 2hr Phase B Line-to-Neutral Voltage Phase Angle | float | 2 | R
| 0xB791 | 0xB792 | 46993 | 46994 | Aggr 2hr Phase C Line-to-Neutral Voltage Phase Angle | float | 2 | R
| 0xB793 | 0xB794 | 46995 | 46996 | Aggr 2hr Average Line-to-Neutral Voltage | float | 2 | R
| 0xB795 | 0xB796 | 46997 | 46998 | Aggr 2hr Phase AB Line-to-Line Voltage | float | 2 | R
| 0xB797 | 0xB798 | 46999 | 47000 | Aggr 2hr Phase BC Line-to-Line Voltage | float | 2 | R
| 0xB799 | 0xB79A | 47001 | 47002 | Aggr 2hr Phase CA Line-to-Line Voltage | float | 2 | R
| 0xB79B | 0xB79C | 47003 | 47004 | Aggr 2hr Phase AB Line-to-Line Voltage Phase Angle | float | 2 | R
| 0xB79D | 0xB79E | 47005 | 47006 | Aggr 2hr Phase BC Line-to-Line Voltage Phase Angle | float | 2 | R
| 0xB79F | 0xB7A0 | 47007 | 47008 | Aggr 2hr Phase CA Line-to-Line Voltage Phase Angle | float | 2 | R
| 0xB7A1 | 0xB7A2 | 47009 | 47010 | Aggr 2hr Average Line-to-Line Voltage | float | 2 | R
| 0xB7A3 | 0xB7A4 | 47011 | 47012 | Aggr 2hr Phase A Current | float | 2 | R
| 0xB7A5 | 0xB7A6 | 47013 | 47014 | Aggr 2hr Phase B Current | float | 2 | R
| 0xB7A7 | 0xB7A8 | 47015 | 47016 | Aggr 2hr Phase C Current | float | 2 | R
| 0xB7A9 | 0xB7AA | 47017 | 47018 | Aggr 2hr Neutral Current | float | 2 | R
| 0xB7AB | 0xB7AC | 47019 | 47020 | Aggr 2hr Phase A Current Phase Angle | float | 2 | R
| 0xB7AD | 0xB7AE | 47021 | 47022 | Aggr 2hr Phase B Current Phase Angle | float | 2 | R
| 0xB7AF | 0xB7B0 | 47023 | 47024 | Aggr 2hr Phase C Current Phase Angle | float | 2 | R
| 0xB7B1 | 0xB7B2 | 47025 | 47026 | Aggr 2hr Neutral Current Phase Angle | float | 2 | R
| 0xB7B3 | 0xB7B4 | 47027 | 47028 | Aggr 2hr Average Current | float | 2 | R
| 0xB7B5 | 0xB7B6 | 47029 | 47030 | Aggr 2hr Phase A Active Power | float | 2 | R
| 0xB7B7 | 0xB7B8 | 47031 | 47032 | Aggr 2hr Phase B Active Power | float | 2 | R
| 0xB7B9 | 0xB7BA | 47033 | 47034 | Aggr 2hr Phase C Active Power | float | 2 | R
| 0xB7BB | 0xB7BC | 47035 | 47036 | Aggr 2hr System Active Power | float | 2 | R
| 0xB7BD | 0xB7BE | 47037 | 47038 | Aggr 2hr Phase A Reactive Power | float | 2 | R
| 0xB7BF | 0xB7C0 | 47039 | 47040 | Aggr 2hr Phase B Reactive Power | float | 2 | R
| 0xB7C1 | 0xB7C2 | 47041 | 47042 | Aggr 2hr Phase C Reactive Power | float | 2 | R
| 0xB7C3 | 0xB7C4 | 47043 | 47044 | Aggr 2hr System Reactive Power | float | 2 | R
| 0xB7C5 | 0xB7C6 | 47045 | 47046 | Aggr 2hr Phase A Apparent Power | float | 2 | R
| 0xB7C7 | 0xB7C8 | 47047 | 47048 | Aggr 2hr Phase B Apparent Power | float | 2 | R
| 0xB7C9 | 0xB7CA | 47049 | 47050 | Aggr 2hr Phase C Apparent Power | float | 2 | R
| 0xB7CB | 0xB7CC | 47051 | 47052 | Aggr 2hr System Apparent Power | float | 2 | R
| 0xB7CD | 0xB7CE | 47053 | 47054 | Aggr 2hr Phase A Power Factor | float | 2 | R
| 0xB7CF | 0xB7D0 | 47055 | 47056 | Aggr 2hr Phase B Power Factor | float | 2 | R
| 0xB7D1 | 0xB7D2 | 47057 | 47058 | Aggr 2hr Phase C Power Factor | float | 2 | R
| 0xB7D3 | 0xB7D4 | 47059 | 47060 | Aggr 2hr System Power Factor | float | 2 | R
| 0xB7D5 | 0xB7D6 | 47061 | 47062 | Aggr 2hr Phase A Displacement Power Factor | float | 2 | R
| 0xB7D7 | 0xB7D8 | 47063 | 47064 | Aggr 2hr Phase B Displacement Power Factor | float | 2 | R
| 0xB7D9 | 0xB7DA | 47065 | 47066 | Aggr 2hr Phase C Displacement Power Factor | float | 2 | R
| 0xB7DB | 0xB7DC | 47067 | 47068 | Aggr 2hr Phase A Load Nature | uint32_t | 2 | R | 82:Resistive load 76:Inductive load 67:Capacitive load
| 0xB7DD | 0xB7DE | 47069 | 47070 | Aggr 2hr Phase B Load Nature | uint32_t | 2 | R
| 0xB7DF | 0xB7E0 | 47071 | 47072 | Aggr 2hr Phase C Load Nature | uint32_t | 2 | R
| 0xB7E1 | 0xB7E2 | 47073 | 47074 | Aggr 2hr System Load Nature | uint32_t | 2 | R
| 0xB7E3 | 0xB7E4 | 47075 | 47076 | Aggr 2hr Channel 4 Active Power | float | 2 | R
| 0xB7E5 | 0xB7E6 | 47077 | 47078 | Aggr 2hr Channel 4 Reactive Power | float | 2 | R
| 0xB7E7 | 0xB7E8 | 47079 | 47080 | Aggr 2hr Channel 4 Apparent Power | float | 2 | R
| 0xB7E9 | 0xB7EA | 47081 | 47082 | Aggr 2hr Channel 4 PF | float | 2 | R
| 0xB7EB | 0xB7EC | 47083 | 47084 | Aggr 2hr Channel 4 Displacement Power Factor | float | 2 | R
| 0xB7ED | 0xB7EE | 47085 | 47086 | Aggr 2hr Channel 4 LN (L/C/R) | uint32_t | 2 | R | 82:Resistive load 76:Inductive load 67:Capacitive load
| 0xB7EF | 0xB7F0 | 47087 | 47088 | Aggr 2hr Summation 2 Iavg | float | 2 | R
| 0xB7F1 | 0xB7F2 | 47089 | 47090 | Aggr 2hr Summation 2 P | float | 2 | R
| 0xB7F3 | 0xB7F4 | 47091 | 47092 | Aggr 2hr Summation 2 Q | float | 2 | R
| 0xB7F5 | 0xB7F6 | 47093 | 47094 | Aggr 2hr Summation 2 S | float | 2 | R
| 0xB7F7 | 0xB7F8 | 47095 | 47096 | Aggr 2hr Summation 2 PF | float | 2 | R
| 0xB7F9 | 0xB7FA | 47097 | 47098 | Aggr 2hr Summation 2 LN (L/C/R) | uint32_t | 2 | R | 82:Resistive load 76:Inductive load 67:Capacitive load
Unbalance V | 0xB7FB | 0xB7FC | 47099 | 47100 | Aggr 2hr Voltage Unbalance Negative | float | 2 | R
| 0xB7FD | 0xB7FE | 47101 | 47102 | Aggr 2hr Voltage Unbalance Zero | float | 2 | R
| 0xB7FF | 0xB800 | 47103 | 47104 | Aggr 2hr Voltage Zero Sequnece Real Part | float | 2 | R
| 0xB801 | 0xB802 | 47105 | 47106 | Aggr 2hr Voltage Zero Sequence Imaginary Part | float | 2 | R
| 0xB803 | 0xB804 | 47107 | 47108 | Aggr 2hr Voltage Positive Sequence Real Part | float | 2 | R
| 0xB805 | 0xB806 | 47109 | 47110 | Aggr 2hr Voltage Positive Sequence Imaginary Part | float | 2 | R
| 0xB807 | 0xB808 | 47111 | 47112 | Aggr 2hr Voltage Negative Sequence Real Part | float | 2 | R
| 0xB809 | 0xB80A | 47113 | 47114 | Aggr 2hr Voltage Negative Sequence Imaginary Part | float | 2 | R
Unbalance I | 0xB80B | 0xB80C | 47115 | 47116 | Aggr 2hr Current Unbalance Negative | float | 2 | R
| 0xB80D | 0xB80E | 47117 | 47118 | Aggr 2hr Current Unbalance Zero | float | 2 | R
| 0xB80F | 0xB810 | 47119 | 47120 | Aggr 2hr Current Zero Sequnece Real Part | float | 2 | R
| 0xB811 | 0xB812 | 47121 | 47122 | Aggr 2hr Current Zero Sequence Imaginary Part | float | 2 | R
| 0xB813 | 0xB814 | 47123 | 47124 | Aggr 2hr Current Positive Sequence Real Part | float | 2 | R
| 0xB815 | 0xB816 | 47125 | 47126 | Aggr 2hr Current Positive Sequence Imaginary Part | float | 2 | R
| 0xB817 | 0xB818 | 47127 | 47128 | Aggr 2hr Current Negative Sequence Real Part | float | 2 | R
| 0xB819 | 0xB81A | 47129 | 47130 | Aggr 2hr Current Negative Sequence Imaginary Part | float | 2 | R
157
Harmonic V | 0xB85A | 0xB8D9 | 47194 | 47321 | Aggr 2hr Phase A 1-64st Voltage Magnitude Harmonics | float | 128 | R
| 0xB8DA | 0xB959 | 47322 | 47449 | Aggr 2h Phase A 1-64st Voltage Harmonics Group | float | 128 | R
| 0xB95A | 0xB9D9 | 47450 | 47577 | Aggr 2hr Phase A 1-64st Voltage Angle Harmonics | float | 128 | R
| 0xB9DA | 0xBA59 | 47578 | 47705 | Aggr 2hr Phase B 1-64st Voltage Magnitude Harmonics | float | 128 | R
| 0xBA5A | 0xBAD9 | 47706 | 47833 | Aggr 2hr Phase B 1-64st Voltage Harmonics Group | float | 128 | R
| 0xBADA | 0xBB59 | 47834 | 47961 | Aggr 2hr Phase B 1-64st Voltage Angle Harmonics | float | 128 | R
| 0xBB5A | 0xBBD9 | 47962 | 48089 | Aggr 2hr Phase C 1-64st Voltage Magnitude Harmonics | float | 128 | R
| 0xBBDA | 0xBC59 | 48090 | 48217 | Aggr 2hr Phase C 1-64st Voltage Harmonics Group | float | 128 | R
| 0xBC5A | 0xBCD9 | 48218 | 48345 | Aggr 2hr Phase C 1-64st Voltage Angle Harmonics | float | 128 | R
| 0xBCDA | 0xBCDB | 48346 | 48347 | Aggr 2hr Phase A Voltage THD | float | 2 | R
| 0xBCDC | 0xBCDD | 48348 | 48349 | Aggr 2hr Phase A Voltage THD Odd | float | 2 | R
| 0xBCDE | 0xBCDF | 48350 | 48351 | Aggr 2hr Phase A Voltage THD Even | float | 2 | R
| 0xBCE0 | 0xBCE1 | 48352 | 48353 | Aggr 2hr Phase A Voltage Crest Factor | float | 2 | R
| 0xBCE2 | 0xBCE3 | 48354 | 48355 | Aggr 2hr Phase A Voltage Fundamental RMS | float | 2 | R
| 0xBCE4 | 0xBCE5 | 48356 | 48357 | Aggr 2hr Phase B Voltage THD | float | 2 | R
| 0xBCE6 | 0xBCE7 | 48358 | 48359 | Aggr 2hr Phase B Voltage THD Odd | float | 2 | R
| 0xBCE8 | 0xBCE9 | 48360 | 48361 | Aggr 2hr Phase B Voltage THD Even | float | 2 | R
| 0xBCEA | 0xBCEB | 48362 | 48363 | Aggr 2hr Phase B Voltage Crest Factor | float | 2 | R
| 0xBCEC | 0xBCED | 48364 | 48365 | Aggr 2hr Phase B Voltage Fundamental RMS | float | 2 | R
| 0xBCEE | 0xBCEF | 48366 | 48367 | Aggr 2hr Phase C Voltage THD | float | 2 | R
| 0xBCF0 | 0xBCF1 | 48368 | 48369 | Aggr 2hr Phase C Voltage THD Odd | float | 2 | R
| 0xBCF2 | 0xBCF3 | 48370 | 48371 | Aggr 2hr Phase C Voltage THD Even | float | 2 | R
| 0xBCF4 | 0xBCF5 | 48372 | 48373 | Aggr 2hr Phase C Voltage Crest Factor | float | 2 | R
| 0xBCF6 | 0xBCF7 | 48374 | 48375 | Aggr 2hr Phase C Voltage Fundamental RMS | float | 2 | R
| 0xBCF8 | 0xBCF9 | 48376 | 48377 | Aggr 2hr Average Voltage THD | float | 2 | R
| 0xBCFA | 0xBCFB | 48378 | 48379 | Aggr 2hr Average Voltage THD Odd | float | 2 | R
| 0xBCFC | 0xBCFD | 48380 | 48381 | Aggr 2hr Average Voltage THD Even | float | 2 | R
Harmonic I | 0xBCFE | 0xBD7D | 48382 | 48509 | Aggr 2hr Phase A 1-64st Current Magnitude Harmonics | float | 128 | R
| 0xBD7E | 0xBDFD | 48510 | 48637 | Aggr 2hr Phase A 1-64st Current Harmonics Group | float | 128 | R
| 0xBDFE | 0xBE7D | 48638 | 48765 | Aggr 2hr Phase A 1-64st Current Angle Harmonics | float | 128 | R
| 0xBE7E | 0xBEFD | 48766 | 48893 | Aggr 2hr Phase B 1-64st Current Magnitude Harmonics | float | 128 | R
| 0xBEFE | 0xBF7D | 48894 | 49021 | Aggr 2hr Phase B 1-64st Current Harmonics Group | float | 128 | R
| 0xBF7E | 0xBFFD | 49022 | 49149 | Aggr 2hr Phase B 1-64st Current Angle Harmonics | float | 128 | R
| 0xBFFE | 0xC07D | 49150 | 49277 | Aggr 2hr Phase C 1-64st Current Magnitude Harmonics | float | 128 | R
| 0xC07E | 0xC0FD | 49278 | 49405 | Aggr 2hr Phase C 1-64st Current Harmonics Group | float | 128 | R
| 0xC0FE | 0xC17D | 49406 | 49533 | Aggr 2hr Phase C 1-64st Current Angle Harmonics | float | 128 | R
| 0xC17E | 0xC1FD | 49534 | 49661 | Aggr 2hr Neutral 1-64st Current Magnitude Harmonics | float | 128 | R
| 0xC1FE | 0xC27D | 49662 | 49789 | Aggr 2hr Neutral 1-64st Current Harmonics Group | float | 128 | R
| 0xC27E | 0xC2FD | 49790 | 49917 | Aggr 2hr Neutral 1-64st Current Angle Harmonics | float | 128 | R
| 0xC2FE | 0xC2FF | 49918 | 49919 | Aggr 2hr Phase A Current THD | float | 2 | R
| 0xC300 | 0xC301 | 49920 | 49921 | Aggr 2hr Phase A Current THD Odd | float | 2 | R
| 0xC302 | 0xC303 | 49922 | 49923 | Aggr 2hr Phase A Current THD Even | float | 2 | R
| 0xC304 | 0xC305 | 49924 | 49925 | Aggr 2hr Phase A Current Crest-Factor | float | 2 | R
| 0xC306 | 0xC307 | 49926 | 49927 | Aggr 2hr Phase A Current Fundamental RMS | float | 2 | R
| 0xC308 | 0xC309 | 49928 | 49929 | Aggr 2hr Phase A Current K-Factor | float | 2 | R
| 0xC30A | 0xC30B | 49930 | 49931 | Aggr 2hr Phase A Current TDD | float | 2 | R
| 0xC30C | 0xC30D | 49932 | 49933 | Aggr 2hr Phase B Current THD | float | 2 | R
| 0xC30E | 0xC30F | 49934 | 49935 | Aggr 2hr Phase B Current THD Odd | float | 2 | R
| 0xC310 | 0xC311 | 49936 | 49937 | Aggr 2hr Phase B Current THD Even | float | 2 | R
| 0xC312 | 0xC313 | 49938 | 49939 | Aggr 2hr Phase B Current Crest-Factor | float | 2 | R
| 0xC314 | 0xC315 | 49940 | 49941 | Aggr 2hr Phase B Current Fundamental RMS | float | 2 | R
| 0xC316 | 0xC317 | 49942 | 49943 | Aggr 2hr Phase B Current K-Factor | float | 2 | R
| 0xC318 | 0xC319 | 49944 | 49945 | Aggr 2hr Phase B Current TDD | float | 2 | R
| 0xC31A | 0xC31B | 49946 | 49947 | Aggr 2hr Phase C Current THD | float | 2 | R
| 0xC31C | 0xC31D | 49948 | 49949 | Aggr 2hr Phase C Current THD Odd | float | 2 | R
| 0xC31E | 0xC31F | 49950 | 49951 | Aggr 2hr Phase C Current THD Even | float | 2 | R
| 0xC320 | 0xC321 | 49952 | 49953 | Aggr 2hr Phase C Current Crest-Factor | float | 2 | R
| 0xC322 | 0xC323 | 49954 | 49955 | Aggr 2hr Phase C Current Fundamental RMS | float | 2 | R
| 0xC324 | 0xC325 | 49956 | 49957 | Aggr 2hr Phase C Current K-Factor | float | 2 | R
| 0xC326 | 0xC327 | 49958 | 49959 | Aggr 2hr Phase C Current TDD | float | 2 | R
| 0xC328 | 0xC329 | 49960 | 49961 | Aggr 2hr Neutral Current THD | float | 2 | R
| 0xC32A | 0xC32B | 49962 | 49963 | Aggr 2hr Neutral Current THD Odd | float | 2 | R
| 0xC32C | 0xC32D | 49964 | 49965 | Aggr 2hr Neutral Current THD Even | float | 2 | R
| 0xC32E | 0xC32F | 49966 | 49967 | Aggr 2hr Neutral Current Crest-Factor | float | 2 | R
| 0xC330 | 0xC331 | 49968 | 49969 | Aggr 2hr Neutral Current Fundamental RMS | float | 2 | R
| 0xC332 | 0xC333 | 49970 | 49971 | Aggr 2hr Neutral Current K-Factor | float | 2 | R
| 0xC334 | 0xC335 | 49972 | 49973 | Aggr 2hr Neutral Current TDD | float | 2 | R
| 0xC336 | 0xC337 | 49974 | 49975 | Aggr 2hr Average Current THD | float | 2 | R
| 0xC338 | 0xC339 | 49976 | 49977 | Aggr 2hr Average Current THD Odd | float | 2 | R
| 0xC33A | 0xC33B | 49978 | 49979 | Aggr 2hr Average Current THD Even | float | 2 | R
Flicker Plt | 0xC33C | 0xC33D | 49980 | 49981 | Aggr 2hr Phase A Flicker Plt | float | 2 | R
| 0xC33E | 0xC33F | 49982 | 49983 | Aggr 2hr Phase B Flicker Plt | float | 2 | R
| 0xC340 | 0xC341 | 49984 | 49985 | Aggr 2hr Phase C Flicker Plt | float | 2 | R
2792

## Demand
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Demand(code function : 03H Read) | 0x2200 | 0x2201 | 8704 | 8705 | Phase A Active Power Demand | float | R | 2
| 0x2202 | 0x2203 | 8706 | 8707 | Phase B Active Power Demand | float | R | 2
| 0x2204 | 0x2205 | 8708 | 8709 | Phase C Active Power Demand | float | R | 2
| 0x2206 | 0x2207 | 8710 | 8711 | System Active Power Demand | float | R | 2
| 0x2208 | 0x2209 | 8712 | 8713 | Phase A Reactive Power Demand | float | R | 2
| 0x220A | 0x220B | 8714 | 8715 | Phase B Reactive Power Demand | float | R | 2
| 0x220C | 0x220D | 8716 | 8717 | Phase C Reactive Power Demand | float | R | 2
| 0x220E | 0x220F | 8718 | 8719 | System Reactive Power Demand | float | R | 2
| 0x2210 | 0x2211 | 8720 | 8721 | Phase A Apparent Power Demand | float | R | 2
| 0x2212 | 0x2213 | 8722 | 8723 | Phase B Apparent Power Demand | float | R | 2
| 0x2214 | 0x2215 | 8724 | 8725 | Phase C Apparent Power Demand | float | R | 2
| 0x2216 | 0x2217 | 8726 | 8727 | System Apparent Power Demand | float | R | 2
| 0x2218 | 0x2219 | 8728 | 8729 | Phase A Current Demand | float | R | 2
| 0x221A | 0x221B | 8730 | 8731 | Phase B Current Demand | float | R | 2
| 0x221C | 0x221D | 8732 | 8733 | Phase C Current Demand | float | R | 2
| 0x221E | 0x221F | 8734 | 8735 | Neutral Current Demand | float | R | 2
| 0x2220 | 0x2221 | 8736 | 8737 | Channel 4 Active Power Demand | float | R | 2
| 0x2222 | 0x2223 | 8738 | 8739 | Channel 4 Reactive Power Demand | float | R | 2
| 0x2224 | 0x2225 | 8740 | 8741 | Channel 4 Apparent Power Demand | float | R | 2
| 0x2226 | 0x2227 | 8742 | 8743 | Summation 2 Active Power Demand | float | R | 2
| 0x2228 | 0x2229 | 8744 | 8745 | Summation 2 Reactive Power Demand | float | R | 2
| 0x222A | 0x222B | 8746 | 8747 | Summation 2 Apparent Power Demand | float | R | 2
| 0x222C | 0x222D | 8748 | 8749 | Predictive System Active Power Demand | float | R | 2
| 0x222E | 0x222F | 8750 | 8751 | Predictive System Reactive Power Demand | float | R | 2
| 0x2230 | 0x2231 | 8752 | 8753 | Predictive System Apparent Power Demand | float | R | 2
50

## 10S Freq
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data Type | RW | Reg Num | Range | Default
| 0x2300 | 0x2303 | 8960 | 8963 | 10s Param Update Time Stamp | uint64_t | R | 4
| 0x2304 | 0x2305 | 8964 | 8965 | 10s System Frequency | uint32_t | R | 2
| 0x2306 | 0x2306 | 8966 | 8966 | 10s Param Event Info | uint16_t | R | 1
| 0x2307 | 0x2307 | 8967 | 8967 | 10s Param Event Flag | uint16_t | R | 1
8

## Dual Source Energy
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Dual Source Energy Settings
| 0x5000 | 0x5000 | 20480 | 20480 | Dual source energy enable/disable | uint16_t | R/W | 1 | 0: Disabled; 1: Enabled | 0
| 0x5001 | 0x5001 | 20481 | 20481 | Energy 1 selection | uint16_t | R/W | 1 | 0: Not selected 1: Active energy 2: Phase A active energy 3: Phase B active energy 4: Phase C active energy 5: Reactive energy 6: Phase A reactive energy 7: Phase B reactive energy 8: Phase C reactive energy 9: Apparent energy 10: Phase A apparent energy 11: Phase B apparent energy 12: Phase C apparent energy | 0
| 0x5002 | 0x5002 | 20482 | 20482 | Energy 2 selection | uint16_t | R/W | 1 | 0: Not selected 1: Active energy 2: Phase A active energy 3: Phase B active energy 4: Phase C active energy 5: Reactive energy 6: Phase A reactive energy 7: Phase B reactive energy 8: Phase C reactive energy 9: Apparent energy 10: Phase A apparent energy 11: Phase B apparent energy 12: Phase C apparent energy | 0
| 0x5003 | 0x5003 | 20483 | 20483 | Energy 3 selection | uint16_t | R/W | 1 | 0: Not selected 1: Active energy 2: Phase A active energy 3: Phase B active energy 4: Phase C active energy 5: Reactive energy 6: Phase A reactive energy 7: Phase B reactive energy 8: Phase C reactive energy 9: Apparent energy 10: Phase A apparent energy 11: Phase B apparent energy 12: Phase C apparent energy | 0
| 0x5004 | 0x5004 | 20484 | 20484 | Control modeL | uint16_t | R/W | 1 | 0: Controlled by communication 1 ~ 3: Controlled by DI1-DI3 | 0
| 0x5005 | 0x5005 | 20485 | 20485 | Direction flag | uint16_t | R/W | 1 | When control mode is controlled by commnication, the value is writeable via communication; when control mode is controlled by DI, the value is readonly. 0: grid direction; 1: generator direction. | 0
Dual Source Energy Readings
| 0x5050 | 0x5051 | 20560 | 20561 | Energy 1 - Grid Direction | uint32_t | R | 2
| 0x5052 | 0x5053 | 20562 | 20563 | Energy 1 - Generator Direction | uint32_t | R | 2
| 0x5054 | 0x5055 | 20564 | 20565 | Energy 2 - Grid Direction | uint32_t | R | 2
| 0x5056 | 0x5057 | 20566 | 20567 | Energy 2 - Generator Direction | uint32_t | R | 2
| 0x5058 | 0x5059 | 20568 | 20569 | Energy 3 - Grid Direction | uint32_t | R | 2
| 0x505A | 0x505B | 20570 | 20571 | Energy 3 - Generator Direction | uint32_t | R | 2
Dual Source Energy switching records
| 0x5100 | 0x5100 | 20736 | 20736 | The first index of records to read | uint16_t | R/W | 1 | 1 to 20 | 0
| 0x5101 | 0x5101 | 20737 | 20737 | the number of records to read | uint16_t | R/W | 1 | 1 to 5 | 0
| 0x5102 | 0x5102 | 20738 | 20738 | The ID of current switching record | uint16_t | R | 1 | 0 to 20 | 0
| 0x5103 | 0x5103 | 20739 | 20739 | Total number recorded | uint16_t | R | 1 | 0 to 20，values greater than 20 are limited to 20. | 0
| 0x5104 | 0x5104 | 20740 | 20740 | The length of bytes that can be read by the current window | uint16_t | R | 1 | 0 to 170, The value shall be either 0 or a multiple of 34; 0: the window data is invalid. | 0
| 0x5105 | 0x5105 | 20741 | 20741 | 1st switch record - timestamp year&month | uint16_t | R | 1 | High byte: year Low byte: month
| 0x5106 | 0x5106 | 20742 | 20742 | 1st switch record - timestamp date&hour | uint16_t | R | 1 | High byte: date Low byte: hour
| 0x5107 | 0x5107 | 20743 | 20743 | 1st switch record - timestamp minute&second | uint16_t | R | 1 | High byte: minute Low byte: second
| 0x5108 | 0x5108 | 20744 | 20744 | 1st switch record - switch command source | uint16_t | R | 1 | 0: Controlled by communication 1 ~3: Controlled by DI1-DI3
| 0x5109 | 0x5109 | 20745 | 20745 | 1st switch record - switch command | uint16_t | R | 1 | 0: grid direction, 1: generator direction
| 0x510A | 0x510B | 20746 | 20747 | 1st Switch Record - Energy 1 - Grid Direction | uint32_t | R | 2
| 0x510C | 0x510D | 20748 | 20749 | 1st Switch Record - Energy 1 - Generator Direction | uint32_t | R | 2
| 0x510E | 0x510F | 20750 | 20751 | 1st Switch Record - Energy 2 - Grid Direction | uint32_t | R | 2
| 0x5110 | 0x5111 | 20752 | 20753 | 1st Switch Record - Energy 2 - Generator Direction | uint32_t | R | 2
| 0x5112 | 0x5113 | 20754 | 20755 | 1st Switch Record - Energy 3 - Grid Direction | uint32_t | R | 2
| 0x5114 | 0x5115 | 20756 | 20757 | 1st Switch Record - Energy 3 - Generator Direction | uint32_t | R | 2
| 0x5116 | 0x5126 | 20758 | 20774 | 2nd switch record data | uint16_t | R | 17
| 0x5127 | 0x5137 | 20775 | 20791 | 3rd switch record data | uint16_t | R | 17
| 0x5138 | 0x5148 | 20792 | 20808 | 4th switch record data | uint16_t | R | 17
| 0x5149 | 0x5159 | 20809 | 20825 | 5th switch record data | uint16_t | R | 17
90

## MaxMin
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Max value record code function : 03H Read
| 0x5300 | 0x5301 | 21248 | 21249 | System Frequency Max value | float | R | 2
| 0x5302 | 0x5305 | 21250 | 21253 | System Frequency Max value Timestamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：timestamp ) | timestamp | R | 4
| 0x5306 | 0x5307 | 21254 | 21255 | Phase A Line-to-Neutral Voltage Max value | float | R | 2
| 0x5308 | 0x530B | 21256 | 21259 | Phase A Line-to-Neutral Voltage Max value Timestamp | timestamp | R | 4
| 0x530C | 0x530D | 21260 | 21261 | Phase B Line-to-Neutral Voltage Max value | float | R | 2
| 0x530E | 0x5311 | 21262 | 21265 | Phase B Line-to-Neutral Voltage Max value Timestamp | timestamp | R | 4
| 0x5312 | 0x5313 | 21266 | 21267 | Phase C Line-to-Neutral Voltage Max value | float | R | 2
| 0x5314 | 0x5317 | 21268 | 21271 | Phase C Line-to-Neutral Voltage Max value Timestamp | timestamp | R | 4
| 0x5318 | 0x5319 | 21272 | 21273 | Phase AB Line-to-Line Voltage Max value | float | R | 2
| 0x531A | 0x531D | 21274 | 21277 | Phase AB Line-to-Line Voltage Max value Timestamp | timestamp | R | 4
| 0x531E | 0x531F | 21278 | 21279 | Phase BC Line-to-Line Voltage Max value | float | R | 2
| 0x5320 | 0x5323 | 21280 | 21283 | Phase BC Line-to-Line Voltage Max value Timestamp | timestamp | R | 4
| 0x5324 | 0x5325 | 21284 | 21285 | Phase CA Line-to-Line Voltage Max value | float | R | 2
| 0x5326 | 0x5329 | 21286 | 21289 | Phase CA Line-to-Line Voltage Max value Timestamp | timestamp | R | 4
| 0x532A | 0x532B | 21290 | 21291 | Phase A Current Max value | float | R | 2
| 0x532C | 0x532F | 21292 | 21295 | Phase A Current Max value Timestamp | timestamp | R | 4
| 0x5330 | 0x5331 | 21296 | 21297 | Phase B Current Max value | float | R | 2
| 0x5332 | 0x5335 | 21298 | 21301 | Phase B Current Max value Timestamp | timestamp | R | 4
| 0x5336 | 0x5337 | 21302 | 21303 | Phase C Current Max value | float | R | 2
| 0x5338 | 0x533B | 21304 | 21307 | Phase C Current Max value Timestamp | timestamp | R | 4
| 0x533C | 0x533D | 21308 | 21309 | Neutral Current Max value | float | R | 2
| 0x533E | 0x5341 | 21310 | 21313 | Neutral Current Max value Timestamp | timestamp | R | 4
| 0x5342 | 0x5343 | 21314 | 21315 | Phase A Active Power Max value | float | R | 2
| 0x5344 | 0x5347 | 21316 | 21319 | Phase A Active Power Max value Timestamp | timestamp | R | 4
| 0x5348 | 0x5349 | 21320 | 21321 | Phase B Active Power Max value | float | R | 2
| 0x534A | 0x534D | 21322 | 21325 | Phase B Active Power Max value Timestamp | timestamp | R | 4
| 0x534E | 0x534F | 21326 | 21327 | Phase C Active Power Max value | float | R | 2
| 0x5350 | 0x5353 | 21328 | 21331 | Phase C Active Power Max value Timestamp | timestamp | R | 4
| 0x5354 | 0x5355 | 21332 | 21333 | System Active Power Max value | float | R | 2
| 0x5356 | 0x5359 | 21334 | 21337 | System Active Power Max value Timestamp | timestamp | R | 4
| 0x535A | 0x535B | 21338 | 21339 | Phase A Reactive Power Max value | float | R | 2
| 0x535C | 0x535F | 21340 | 21343 | Phase A Reactive Power Max value Timestamp | timestamp | R | 4
| 0x5360 | 0x5361 | 21344 | 21345 | Phase B Reactive Power Max value | float | R | 2
| 0x5362 | 0x5365 | 21346 | 21349 | Phase B Reactive Power Max value Timestamp | timestamp | R | 4
| 0x5366 | 0x5367 | 21350 | 21351 | Phase C Reactive Power Max value | float | R | 2
| 0x5368 | 0x536B | 21352 | 21355 | Phase C Reactive Power Max value Timestamp | timestamp | R | 4
| 0x536C | 0x536D | 21356 | 21357 | System Reactive Power Max value | float | R | 2
| 0x536E | 0x5371 | 21358 | 21361 | System Reactive Power Max value Timestamp | timestamp | R | 4
| 0x5372 | 0x5373 | 21362 | 21363 | Phase A Apparent Power Max value | float | R | 2
| 0x5374 | 0x5377 | 21364 | 21367 | Phase A Apparent Power Max value Timestamp | timestamp | R | 4
| 0x5378 | 0x5379 | 21368 | 21369 | Phase B Apparent Power Max value | float | R | 2
| 0x537A | 0x537D | 21370 | 21373 | Phase B Apparent Power Max value Timestamp | timestamp | R | 4
| 0x537E | 0x537F | 21374 | 21375 | Phase C Apparent Power Max value | float | R | 2
| 0x5380 | 0x5383 | 21376 | 21379 | Phase C Apparent Power Max value Timestamp | timestamp | R | 4
| 0x5384 | 0x5385 | 21380 | 21381 | System Apparent Power Max value | float | R | 2
| 0x5386 | 0x5389 | 21382 | 21385 | System Apparent Power Max value Timestamp | timestamp | R | 4
| 0x538A | 0x538B | 21386 | 21387 | Phase A Power Factor Max value | timestamp | R | 2
| 0x538C | 0x538F | 21388 | 21391 | Phase A Power Factor Max value Timestamp | float | R | 4
| 0x5390 | 0x5391 | 21392 | 21393 | Phase B Power Factor Max value | timestamp | R | 2
| 0x5392 | 0x5395 | 21394 | 21397 | Phase B Power Factor Max value Timestamp | float | R | 4
| 0x5396 | 0x5397 | 21398 | 21399 | Phase C Power Factor Max value | timestamp | R | 2
| 0x5398 | 0x539B | 21400 | 21403 | Phase C Power Factor Max value Timestamp | float | R | 4
| 0x539C | 0x539D | 21404 | 21405 | System Power Factor Max value | timestamp | R | 2
| 0x539E | 0x53A1 | 21406 | 21409 | System Power Factor Max value Timestamp | float | R | 4
| 0x53A2 | 0x53A3 | 21410 | 21411 | Voltage Unbalance Negative Max value | timestamp | R | 2
| 0x53A4 | 0x53A7 | 21412 | 21415 | Voltage Unbalance Negative Max value Timestamp | float | R | 4
| 0x53A8 | 0x53A9 | 21416 | 21417 | Current Unbalance Negative Max value | float | R | 2
| 0x53AA | 0x53AD | 21418 | 21421 | Current Unbalance Negative Max value Timestamp | timestamp | R | 4
| 0x53AE | 0x53AF | 21422 | 21423 | Phase A Voltage THD Max value | float | R | 2
| 0x53B0 | 0x53B3 | 21424 | 21427 | Phase A Voltage THD Max value Timestamp | timestamp | R | 4
| 0x53B4 | 0x53B5 | 21428 | 21429 | Phase B Voltage THD Max value | float | R | 2
| 0x53B6 | 0x53B9 | 21430 | 21433 | Phase B Voltage THD Max value Timestamp | timestamp | R | 4
| 0x53BA | 0x53BB | 21434 | 21435 | Phase C Voltage THD Max value | timestamp | R | 2
| 0x53BC | 0x53BF | 21436 | 21439 | Phase C Voltage THD Max value Timestamp | float | R | 4
| 0x53C0 | 0x53C1 | 21440 | 21441 | Phase A Current THD Max value | float | R | 2
| 0x53C2 | 0x53C5 | 21442 | 21445 | Phase A Current THD Max value Timestamp | timestamp | R | 4
| 0x53C6 | 0x53C7 | 21446 | 21447 | Phase B Current THD Max value | float | R | 2
| 0x53C8 | 0x53CB | 21448 | 21451 | Phase B Current THD Max value Timestamp | timestamp | R | 4
| 0x53CC | 0x53CD | 21452 | 21453 | Phase C Current THD Max value | float | R | 2
| 0x53CE | 0x53D1 | 21454 | 21457 | Phase C Current THD Max value Timestamp | timestamp | R | 4
| 0x53D2 | 0x53D3 | 21458 | 21459 | Neutral Current THD Max value | float | R | 2
| 0x53D4 | 0x53D7 | 21460 | 21463 | Neutral Current THD Max value Timestamp | timestamp | R | 4
| 0x53D8 | 0x53D9 | 21464 | 21465 | Input Channel 4 Active Power Max value | float | R | 2
| 0x53DA | 0x53DD | 21466 | 21469 | Input Channel 4 Active Power Max value Timestamp | timestamp | R | 4
| 0x53DE | 0x53DF | 21470 | 21471 | Input Channel 4 Reactive Power Max value | float | R | 2
| 0x53E0 | 0x53E3 | 21472 | 21475 | Input Channel 4 Reactive Power Max value Timestamp | timestamp | R | 4
| 0x53E4 | 0x53E5 | 21476 | 21477 | Input Channel 4 Apparent Power Max value | float | R | 2
| 0x53E6 | 0x53E9 | 21478 | 21481 | Input Channel 4 Apparent Power Max value Timestamp | timestamp | R | 4
| 0x53EA | 0x53EB | 21482 | 21483 | Input Channel 4 Power Factor Max value | float | R | 2
| 0x53EC | 0x53EF | 21484 | 21487 | Input Channel 4 Power Factor Max value Timestamp | timestamp | R | 4
| 0x53F0 | 0x53F1 | 21488 | 21489 | Summation 2 Active Power Max value | float | R | 2
| 0x53F2 | 0x53F5 | 21490 | 21493 | Summation 2 Active Power Max value Timestamp | timestamp | R | 4
| 0x53F6 | 0x53F7 | 21494 | 21495 | Summation 2 Reactive Power Max value | float | R | 2
| 0x53F8 | 0x53FB | 21496 | 21499 | Summation 2 Reactive Power Max value Timestamp | timestamp | R | 4
| 0x53FC | 0x53FD | 21500 | 21501 | Summation 2 Apparent Power Max value | float | R | 2
| 0x53FE | 0x5401 | 21502 | 21505 | Summation 2 Apparent Power Max value Timestamp | timestamp | R | 4
| 0x5402 | 0x5403 | 21506 | 21507 | Summation 2 Power Factor Max value | float | R | 2
| 0x5404 | 0x5407 | 21508 | 21511 | Summation 2 Power Factor Max value Timestamp | timestamp | R | 4
264
Min value record
| 0x5600 | 0x5601 | 22016 | 22017 | System Frequency Min value | float | R | 2
| 0x5602 | 0x5605 | 22018 | 22021 | System Frequency Min value Timestamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t ) | timestamp | R | 4
| 0x5606 | 0x5607 | 22022 | 22023 | Phase A Line-to-Neutral Voltage Min value | float | R | 2
| 0x5608 | 0x560B | 22024 | 22027 | Phase A Line-to-Neutral Voltage Min value Timestamp | timestamp | R | 4
| 0x560C | 0x560D | 22028 | 22029 | Phase B Line-to-Neutral Voltage Min value | float | R | 2
| 0x560E | 0x5611 | 22030 | 22033 | Phase B Line-to-Neutral Voltage Min value Timestamp | timestamp | R | 4
| 0x5612 | 0x5613 | 22034 | 22035 | Phase C Line-to-Neutral Voltage Min value | float | R | 2
| 0x5614 | 0x5617 | 22036 | 22039 | Phase C Line-to-Neutral Voltage Min value Timestamp | timestamp | R | 4
| 0x5618 | 0x5619 | 22040 | 22041 | Phase AB Line-to-Line Voltage Min value | float | R | 2
| 0x561A | 0x561D | 22042 | 22045 | Phase AB Line-to-Line Voltage Min value Timestamp | timestamp | R | 4
| 0x561E | 0x561F | 22046 | 22047 | Phase BC Line-to-Line Voltage Min value | float | R | 2
| 0x5620 | 0x5623 | 22048 | 22051 | Phase BC Line-to-Line Voltage Min value Timestamp | timestamp | R | 4
| 0x5624 | 0x5625 | 22052 | 22053 | Phase CA Line-to-Line Voltage Min value | float | R | 2
| 0x5626 | 0x5629 | 22054 | 22057 | Phase CA Line-to-Line Voltage Min value Timestamp | timestamp | R | 4
| 0x562A | 0x562B | 22058 | 22059 | Phase A Current Min value | float | R | 2
| 0x562C | 0x562F | 22060 | 22063 | Phase A Current Min value Timestamp | timestamp | R | 4
| 0x5630 | 0x5631 | 22064 | 22065 | Phase B Current Min value | float | R | 2
| 0x5632 | 0x5635 | 22066 | 22069 | Phase B Current Min value Timestamp | timestamp | R | 4
| 0x5636 | 0x5637 | 22070 | 22071 | Phase C Current Min value | float | R | 2
| 0x5638 | 0x563B | 22072 | 22075 | Phase C Current Min value Timestamp | timestamp | R | 4
| 0x563C | 0x563D | 22076 | 22077 | Phase N Current Min value | float | R | 2
| 0x563E | 0x5641 | 22078 | 22081 | Phase N Current Min value Timestamp | timestamp | R | 4
| 0x5642 | 0x5643 | 22082 | 22083 | Phase A Active Power Min value | float | R | 2
| 0x5644 | 0x5647 | 22084 | 22087 | Phase A Active Power Min value Timestamp | timestamp | R | 4
| 0x5648 | 0x5649 | 22088 | 22089 | Phase B Active Power Min value | float | R | 2
| 0x564A | 0x564D | 22090 | 22093 | Phase B Active Power Min value Timestamp | timestamp | R | 4
| 0x564E | 0x564F | 22094 | 22095 | Phase C Active Power Min value | float | R | 2
| 0x5650 | 0x5653 | 22096 | 22099 | Phase C Active Power Min value Timestamp | timestamp | R | 4
| 0x5654 | 0x5655 | 22100 | 22101 | System Active Power Min value | float | R | 2
| 0x5656 | 0x5659 | 22102 | 22105 | System Active Power Min value Timestamp | timestamp | R | 4
| 0x565A | 0x565B | 22106 | 22107 | Phase A Reactive Power Min value | float | R | 2
| 0x565C | 0x565F | 22108 | 22111 | Phase A Reactive Power Min value Timestamp | timestamp | R | 4
| 0x5660 | 0x5661 | 22112 | 22113 | Phase B Reactive Power Min value | float | R | 2
| 0x5662 | 0x5665 | 22114 | 22117 | Phase B Reactive Power Min value Timestamp | timestamp | R | 4
| 0x5666 | 0x5667 | 22118 | 22119 | Phase C Reactive Power Min value | float | R | 2
| 0x5668 | 0x566B | 22120 | 22123 | Phase C Reactive Power Min value Timestamp | timestamp | R | 4
| 0x566C | 0x566D | 22124 | 22125 | System Reactive Power Min value | float | R | 2
| 0x566E | 0x5671 | 22126 | 22129 | System Reactive Power Min value Timestamp | timestamp | R | 4
| 0x5672 | 0x5673 | 22130 | 22131 | Phase A Apparent Power Min value | float | R | 2
| 0x5674 | 0x5677 | 22132 | 22135 | Phase A Apparent Power Min value Timestamp | timestamp | R | 4
| 0x5678 | 0x5679 | 22136 | 22137 | Phase B Apparent Power Min value | float | R | 2
| 0x567A | 0x567D | 22138 | 22141 | Phase B Apparent Power Min value Timestamp | timestamp | R | 4
| 0x567E | 0x567F | 22142 | 22143 | Phase C Apparent Power Min value | float | R | 2
| 0x5680 | 0x5683 | 22144 | 22147 | Phase C Apparent Power Min value Timestamp | timestamp | R | 4
| 0x5684 | 0x5685 | 22148 | 22149 | System Apparent Power Min value | float | R | 2
| 0x5686 | 0x5689 | 22150 | 22153 | System Apparent Power Min value Timestamp | timestamp | R | 4
| 0x568A | 0x568B | 22154 | 22155 | Phase A Power Factor Min value | float | R | 2
| 0x568C | 0x568F | 22156 | 22159 | Phase A Power Factor Min value Timestamp | timestamp | R | 4
| 0x5690 | 0x5691 | 22160 | 22161 | Phase B Power Factor Min value | float | R | 2
| 0x5692 | 0x5695 | 22162 | 22165 | Phase B Power Factor Min value Timestamp | timestamp | R | 4
| 0x5696 | 0x5697 | 22166 | 22167 | Phase C Power Factor Min value | float | R | 2
| 0x5698 | 0x569B | 22168 | 22171 | Phase C Power Factor Min value Timestamp | timestamp | R | 4
| 0x569C | 0x569D | 22172 | 22173 | System Power Factor Min value | float | R | 2
| 0x569E | 0x56A1 | 22174 | 22177 | System Power Factor Min value Timestamp | timestamp | R | 4
| 0x56A2 | 0x56A3 | 22178 | 22179 | Voltage Unbalance Negative Min value | float | R | 2
| 0x56A4 | 0x56A7 | 22180 | 22183 | Voltage Unbalance Negative Min value Timestamp | timestamp | R | 4
| 0x56A8 | 0x56A9 | 22184 | 22185 | Current Unbalance Negative Min value | float | R | 2
| 0x56AA | 0x56AD | 22186 | 22189 | Current Unbalance Negative Min value Timestamp | timestamp | R | 4
| 0x56AE | 0x56AF | 22190 | 22191 | Phase A Voltage THD Min value | float | R | 2
| 0x56B0 | 0x56B3 | 22192 | 22195 | Phase A Voltage THD Min value Timestamp | timestamp | R | 4
| 0x56B4 | 0x56B5 | 22196 | 22197 | Phase B Voltage THD Min value | float | R | 2
| 0x56B6 | 0x56B9 | 22198 | 22201 | Phase B Voltage THD Min value Timestamp | timestamp | R | 4
| 0x56BA | 0x56BB | 22202 | 22203 | Phase C Voltage THD Min value | float | R | 2
| 0x56BC | 0x56BF | 22204 | 22207 | Phase C Voltage THD Min value Timestamp | timestamp | R | 4
| 0x56C0 | 0x56C1 | 22208 | 22209 | Phase A Current THD Min value | float | R | 2
| 0x56C2 | 0x56C5 | 22210 | 22213 | Phase A Current THD Min value Timestamp | timestamp | R | 4
| 0x56C6 | 0x56C7 | 22214 | 22215 | Phase B Current THD Min value | float | R | 2
| 0x56C8 | 0x56CB | 22216 | 22219 | Phase B Current THD Min value Timestamp | timestamp | R | 4
| 0x56CC | 0x56CD | 22220 | 22221 | Phase C Current THD Min value | float | R | 2
| 0x56CE | 0x56D1 | 22222 | 22225 | Phase C Current THD Min value Timestamp | timestamp | R | 4
| 0x56D2 | 0x56D3 | 22226 | 22227 | Phase N Current THD Min value | timestamp | R | 2
| 0x56D4 | 0x56D7 | 22228 | 22231 | Phase N Current THD Min value Timestamp | float | R | 4
| 0x56D8 | 0x56D9 | 22232 | 22233 | Input Channel 4 Active Power Min value | timestamp | R | 2
| 0x56DA | 0x56DD | 22234 | 22237 | Input Channel 4 Active Power Min value Timestamp | float | R | 4
| 0x56DE | 0x56DF | 22238 | 22239 | Input Channel 4 Reactive Power Min value | timestamp | R | 2
| 0x56E0 | 0x56E3 | 22240 | 22243 | Input Channel 4 Reactive Power Min value Timestamp | float | R | 4
| 0x56E4 | 0x56E5 | 22244 | 22245 | Input Channel 4 Apparent Power Min value | timestamp | R | 2
| 0x56E6 | 0x56E9 | 22246 | 22249 | Input Channel 4 Apparent Power Min value Timestamp | float | R | 4
| 0x56EA | 0x56EB | 22250 | 22251 | Input Channel 4 Power Factor Min value | timestamp | R | 2
| 0x56EC | 0x56EF | 22252 | 22255 | Input Channel 4 Power Factor Min value Timestamp | float | R | 4
| 0x56F0 | 0x56F1 | 22256 | 22257 | Summation 2 Active Power Min value | timestamp | R | 2
| 0x56F2 | 0x56F5 | 22258 | 22261 | Summation 2 Active Power Min value Timestamp | float | R | 4
| 0x56F6 | 0x56F7 | 22262 | 22263 | Summation 2 Reactive Power Min value | timestamp | R | 2
| 0x56F8 | 0x56FB | 22264 | 22267 | Summation 2 Reactive Power Min value Timestamp | float | R | 4
| 0x56FC | 0x56FD | 22268 | 22269 | Summation 2 Apparent Power Min value | float | R | 2
| 0x56FE | 0x5701 | 22270 | 22273 | Summation 2 Apparent Power Min value Timestamp | timestamp | R | 4
| 0x5702 | 0x5703 | 22274 | 22275 | Summation 2 Power Factor Min value | float | R | 2
| 0x5704 | 0x5707 | 22276 | 22279 | Summation 2 Power Factor Min value Timestamp | timestamp | R | 4
264

## Max Demand
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Max Demand(code function : 03H Read)
System Max Demand | 0x5900 | 0x5901 | 22784 | 22785 | Phase A/Channel 1 Active Power Max Demand | float | R | 2
| 0x5902 | 0x5904 | 22786 | 22788 | Phase A/Channel 1 Active Power Max Demand timestamp (year : uint16_t ; month、day : uint16_t ( High byte: month,Low byte: day); hour、min : uint16_t ( High byte: hour,Low byte: minute); ) | timestamp | R | 3
| 0x5905 | 0x5906 | 22789 | 22790 | Phase B/Channel 2 Active Power Max Demand | float | R | 2
| 0x5907 | 0x5909 | 22791 | 22793 | Phase B/Channel 2 Active Power Max Demand timestamp | timestamp | R | 3
| 0x590A | 0x590B | 22794 | 22795 | Phase C/Channel 3 Active Power Max Demand | float | R | 2
| 0x590C | 0x590E | 22796 | 22798 | Phase C/Channel 3 Active Power Max Demand timestamp | timestamp | R | 3
| 0x590F | 0x5910 | 22799 | 22800 | System/Summation 1 Active Power Max Demand | float | R | 2
| 0x5911 | 0x5913 | 22801 | 22803 | System/Summation 1 Active Power MaxDemand timestamp | timestamp | R | 3
| 0x5914 | 0x5915 | 22804 | 22805 | Phase A/Channel 1 Reactive Power Max Demand | float | R | 2
| 0x5916 | 0x5918 | 22806 | 22808 | Phase A/Channel 1 Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x5919 | 0x591A | 22809 | 22810 | Phase B/Channel 2 Reactive Power Max Demand | float | R | 2
| 0x591B | 0x591D | 22811 | 22813 | Phase B/Channel 2 Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x591E | 0x591F | 22814 | 22815 | Phase C/Channel 3 Reactive Power Max Demand | float | R | 2
| 0x5920 | 0x5922 | 22816 | 22818 | Phase C/Channel 3 Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x5923 | 0x5924 | 22819 | 22820 | System/Summation 1 Reactive Power Max Demand | float | R | 2
| 0x5925 | 0x5927 | 22821 | 22823 | System /Summation 1 Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x5928 | 0x5929 | 22824 | 22825 | Phase A/Channel 1 Apparent Power Max Demand | float | R | 2
| 0x592A | 0x592C | 22826 | 22828 | Phase A/Channel 1 Apparent Power Max Demand timestamp | timestamp | R | 3
| 0x592D | 0x592E | 22829 | 22830 | Phase B/Channel 2 Apparent Power Max Demand | float | R | 2
| 0x592F | 0x5931 | 22831 | 22833 | Phase B/Channel 2 Apparent Power Max Demand timestamp | timestamp | R | 3
| 0x5932 | 0x5933 | 22834 | 22835 | Phase C/Channel 3 Apparent Power Max Demand | float | R | 2
| 0x5934 | 0x5936 | 22836 | 22838 | Phase C/Channel 3 Apparent Power Max Demand timestamp | timestamp | R | 3
| 0x5937 | 0x5938 | 22839 | 22840 | System /Summation 1 Apparent Power Max Demand | float | R | 2
| 0x5939 | 0x593B | 22841 | 22843 | System /Summation 1 Apparent Power Max Demand timestamp | timestamp | R | 3
| 0x593C | 0x593D | 22844 | 22845 | Phase A/Channel 1 Current Max Demand | float | R | 2
| 0x593E | 0x5940 | 22846 | 22848 | Phase A/Channel 1 Current Max Demand timestamp | timestamp | R | 3
| 0x5941 | 0x5942 | 22849 | 22850 | Phase B/Channel 2 Current Max Demand | float | R | 2
| 0x5943 | 0x5945 | 22851 | 22853 | Phase B/Channel 2 Current Max Demand timestamp | timestamp | R | 3
| 0x5946 | 0x5947 | 22854 | 22855 | Phase C/Channel 3 Current Max Demand | float | R | 2
| 0x5948 | 0x594A | 22856 | 22858 | Phase C//Channel 3 Current Max Demand timestamp | timestamp | R | 3
| 0x594B | 0x594C | 22859 | 22860 | Neutral/Channel 4 Current Max Demand | float | R | 2
| 0x594D | 0x594F | 22861 | 22863 | Neutral/Channel 4 Current Max Demand timestamp | timestamp | R | 3
| 0x5950 | 0x5951 | 22864 | 22865 | Channel 4 Active Power Max Demand | float | R | 2
| 0x5952 | 0x5954 | 22866 | 22868 | Channel 4 Active Power Max Demand timestamp | timestamp | R | 3
| 0x5955 | 0x5956 | 22869 | 22870 | Channel 4 Reactive Power Max Demand | float | R | 2
| 0x5957 | 0x5959 | 22871 | 22873 | Channel 4 Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x595A | 0x595B | 22874 | 22875 | Channel 4 Apparent Power Max Demand | float | R | 2
| 0x595C | 0x595E | 22876 | 22878 | Channel 4 Apparent Power Max Demand timestamp | timestamp | R | 3
| 0x595F | 0x5960 | 22879 | 22880 | Summation 2 Active Power Max Demand | float | R | 2
| 0x5961 | 0x5963 | 22881 | 22883 | Summation 2 Active Power Max Demand timestamp | timestamp | R | 3
| 0x5964 | 0x5965 | 22884 | 22885 | Summation 2 Reactive Power Max Demand | float | R | 2
| 0x5966 | 0x5968 | 22886 | 22888 | Summation 2 Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x5969 | 0x596A | 22889 | 22890 | Summation 2 Apparent Power Max Demand | float | R | 2
| 0x596B | 0x596D | 22891 | 22893 | Summation 2 Apparent Power Max Demand timestamp | timestamp | R | 3
| 0x596E | 0x596F | 22894 | 22895 | Predictive System Active Power Max Demand | float | R | 2
| 0x5970 | 0x5972 | 22896 | 22898 | Predictive System Active Power Max Demand timestamp | timestamp | R | 3
| 0x5973 | 0x5974 | 22899 | 22900 | Predictive System Reactive Power Max Demand | float | R | 2
| 0x5975 | 0x5977 | 22901 | 22903 | Predictive System Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x5978 | 0x5979 | 22904 | 22905 | Predictive System Apparent Power Max Demand | float | R | 2
| 0x597A | 0x597C | 22906 | 22908 | Predictive System Apparent Power Max Demand timestamp | timestamp | R | 3
125

## Custom settings and Readings
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
User defined reading area
| 0x6A00 | 0x6A00 | 27136 | 27136 | Parameter 1 reading | uint16_t | R | 1
| 0x6A01 | 0x6A01 | 27137 | 27137 | Parameter 2 reading | uint16_t | R | 1
| 0x6A02 | 0x6A02 | 27138 | 27138 | Parameter 3 reading | uint16_t | R | 1
| 0x6A03 | 0x6A03 | 27139 | 27139 | Parameter 4 reading | uint16_t | R | 1
| 0x6A04 | 0x6A04 | 27140 | 27140 | Parameter 5 reading | uint16_t | R | 1
| 0x6A05 | 0x6A05 | 27141 | 27141 | Parameter 6 reading | uint16_t | R | 1
| 0x6A06 | 0x6A06 | 27142 | 27142 | Parameter 7 reading | uint16_t | R | 1
| 0x6A07 | 0x6A07 | 27143 | 27143 | Parameter 8 reading | uint16_t | R | 1
| 0x6A08 | 0x6A08 | 27144 | 27144 | Parameter 9 reading | uint16_t | R | 1
| 0x6A09 | 0x6A09 | 27145 | 27145 | Parameter 10 reading | uint16_t | R | 1
| 0x6A0A | 0x6A0A | 27146 | 27146 | Parameter 11 reading | uint16_t | R | 1
| 0x6A0B | 0x6A0B | 27147 | 27147 | Parameter 12 reading | uint16_t | R | 1
| 0x6A0C | 0x6A0C | 27148 | 27148 | Parameter 13 reading | uint16_t | R | 1
| 0x6A0D | 0x6A0D | 27149 | 27149 | Parameter 14 reading | uint16_t | R | 1
| 0x6A0E | 0x6A0E | 27150 | 27150 | Parameter 15 reading | uint16_t | R | 1
| 0x6A0F | 0x6A0F | 27151 | 27151 | Parameter 16 reading | uint16_t | R | 1
| 0x6A10 | 0x6A10 | 27152 | 27152 | Parameter 17 reading | uint16_t | R | 1
| 0x6A11 | 0x6A11 | 27153 | 27153 | Parameter 18 reading | uint16_t | R | 1
| 0x6A12 | 0x6A12 | 27154 | 27154 | Parameter 19 reading | uint16_t | R | 1
| 0x6A13 | 0x6A13 | 27155 | 27155 | Parameter 20 reading | uint16_t | R | 1
| 0x6A14 | 0x6A14 | 27156 | 27156 | Parameter 21 reading | uint16_t | R | 1
| 0x6A15 | 0x6A15 | 27157 | 27157 | Parameter 22 reading | uint16_t | R | 1
| 0x6A16 | 0x6A16 | 27158 | 27158 | Parameter 23 reading | uint16_t | R | 1
| 0x6A17 | 0x6A17 | 27159 | 27159 | Parameter 24 reading | uint16_t | R | 1
| 0x6A18 | 0x6A18 | 27160 | 27160 | Parameter 25 reading | uint16_t | R | 1
| 0x6A19 | 0x6A19 | 27161 | 27161 | Parameter 26 reading | uint16_t | R | 1
| 0x6A1A | 0x6A1A | 27162 | 27162 | Parameter 27 reading | uint16_t | R | 1
| 0x6A1B | 0x6A1B | 27163 | 27163 | Parameter 28 reading | uint16_t | R | 1
| 0x6A1C | 0x6A1C | 27164 | 27164 | Parameter 29 reading | uint16_t | R | 1
| 0x6A1D | 0x6A1D | 27165 | 27165 | Parameter 30 reading | uint16_t | R | 1
| 0x6A1E | 0x6A1E | 27166 | 27166 | Parameter 31 reading | uint16_t | R | 1
| 0x6A1F | 0x6A1F | 27167 | 27167 | Parameter 32 reading | uint16_t | R | 1
| 0x6A20 | 0x6A20 | 27168 | 27168 | Parameter 33 reading | uint16_t | R | 1
| 0x6A21 | 0x6A21 | 27169 | 27169 | Parameter 34 reading | uint16_t | R | 1
| 0x6A22 | 0x6A22 | 27170 | 27170 | Parameter 35 reading | uint16_t | R | 1
| 0x6A23 | 0x6A23 | 27171 | 27171 | Parameter 36 reading | uint16_t | R | 1
| 0x6A24 | 0x6A24 | 27172 | 27172 | Parameter 37 reading | uint16_t | R | 1
| 0x6A25 | 0x6A25 | 27173 | 27173 | Parameter 38 reading | uint16_t | R | 1
| 0x6A26 | 0x6A26 | 27174 | 27174 | Parameter 39 reading | uint16_t | R | 1
| 0x6A27 | 0x6A27 | 27175 | 27175 | Parameter 40 reading | uint16_t | R | 1
| 0x6A28 | 0x6A28 | 27176 | 27176 | Parameter 41 reading | uint16_t | R | 1
| 0x6A29 | 0x6A29 | 27177 | 27177 | Parameter 42 reading | uint16_t | R | 1
| 0x6A2A | 0x6A2A | 27178 | 27178 | Parameter 43 reading | uint16_t | R | 1
| 0x6A2B | 0x6A2B | 27179 | 27179 | Parameter 44 reading | uint16_t | R | 1
| 0x6A2C | 0x6A2C | 27180 | 27180 | Parameter 45 reading | uint16_t | R | 1
| 0x6A2D | 0x6A2D | 27181 | 27181 | Parameter 46 reading | uint16_t | R | 1
| 0x6A2E | 0x6A2E | 27182 | 27182 | Parameter 47 reading | uint16_t | R | 1
| 0x6A2F | 0x6A2F | 27183 | 27183 | Parameter 48 reading | uint16_t | R | 1
| 0x6A30 | 0x6A30 | 27184 | 27184 | Parameter 49 reading | uint16_t | R | 1
| 0x6A31 | 0x6A31 | 27185 | 27185 | Parameter 50 reading | uint16_t | R | 1
| 0x6A32 | 0x6A32 | 27186 | 27186 | Parameter 51 reading | uint16_t | R | 1
| 0x6A33 | 0x6A33 | 27187 | 27187 | Parameter 52 reading | uint16_t | R | 1
| 0x6A34 | 0x6A34 | 27188 | 27188 | Parameter 53 reading | uint16_t | R | 1
| 0x6A35 | 0x6A35 | 27189 | 27189 | Parameter 54 reading | uint16_t | R | 1
| 0x6A36 | 0x6A36 | 27190 | 27190 | Parameter 55 reading | uint16_t | R | 1
| 0x6A37 | 0x6A37 | 27191 | 27191 | Parameter 56 reading | uint16_t | R | 1
| 0x6A38 | 0x6A38 | 27192 | 27192 | Parameter 57 reading | uint16_t | R | 1
| 0x6A39 | 0x6A39 | 27193 | 27193 | Parameter 58 reading | uint16_t | R | 1
| 0x6A3A | 0x6A3A | 27194 | 27194 | Parameter 59 reading | uint16_t | R | 1
| 0x6A3B | 0x6A3B | 27195 | 27195 | Parameter 60 reading | uint16_t | R | 1
| 0x6A3C | 0x6A3C | 27196 | 27196 | Parameter 61 reading | uint16_t | R | 1
| 0x6A3D | 0x6A3D | 27197 | 27197 | Parameter 62 reading | uint16_t | R | 1
| 0x6A3E | 0x6A3E | 27198 | 27198 | Parameter 63 reading | uint16_t | R | 1
| 0x6A3F | 0x6A3F | 27199 | 27199 | Parameter 64 reading | uint16_t | R | 1
| 0x6A40 | 0x6A40 | 27200 | 27200 | Parameter 65 reading | uint16_t | R | 1
| 0x6A41 | 0x6A41 | 27201 | 27201 | Parameter 66 reading | uint16_t | R | 1
| 0x6A42 | 0x6A42 | 27202 | 27202 | Parameter 67 reading | uint16_t | R | 1
| 0x6A43 | 0x6A43 | 27203 | 27203 | Parameter 68 reading | uint16_t | R | 1
| 0x6A44 | 0x6A44 | 27204 | 27204 | Parameter 69 reading | uint16_t | R | 1
| 0x6A45 | 0x6A45 | 27205 | 27205 | Parameter 70 reading | uint16_t | R | 1
| 0x6A46 | 0x6A46 | 27206 | 27206 | Parameter 71 reading | uint16_t | R | 1
| 0x6A47 | 0x6A47 | 27207 | 27207 | Parameter 71 reading | uint16_t | R | 1
| 0x6A48 | 0x6A48 | 27208 | 27208 | Parameter 73 reading | uint16_t | R | 1
| 0x6A49 | 0x6A49 | 27209 | 27209 | Parameter 74 reading | uint16_t | R | 1
| 0x6A4A | 0x6A4A | 27210 | 27210 | Parameter 75 reading | uint16_t | R | 1
| 0x6A4B | 0x6A4B | 27211 | 27211 | Parameter 76 reading | uint16_t | R | 1
| 0x6A4C | 0x6A4C | 27212 | 27212 | Parameter 77 reading | uint16_t | R | 1
| 0x6A4D | 0x6A4D | 27213 | 27213 | Parameter 78 reading | uint16_t | R | 1
| 0x6A4E | 0x6A4E | 27214 | 27214 | Parameter 79 reading | uint16_t | R | 1
| 0x6A4F | 0x6A4F | 27215 | 27215 | Parameter 80 reading | uint16_t | R | 1
| 0x6A50 | 0x6A50 | 27216 | 27216 | Parameter 81 reading | uint16_t | R | 1
| 0x6A51 | 0x6A51 | 27217 | 27217 | Parameter 82 reading | uint16_t | R | 1
| 0x6A52 | 0x6A52 | 27218 | 27218 | Parameter 83 reading | uint16_t | R | 1
| 0x6A53 | 0x6A53 | 27219 | 27219 | Parameter 84 reading | uint16_t | R | 1
| 0x6A54 | 0x6A54 | 27220 | 27220 | Parameter 85 reading | uint16_t | R | 1
| 0x6A55 | 0x6A55 | 27221 | 27221 | Parameter 86 reading | uint16_t | R | 1
| 0x6A56 | 0x6A56 | 27222 | 27222 | Parameter 87 reading | uint16_t | R | 1
| 0x6A57 | 0x6A57 | 27223 | 27223 | Parameter 88 reading | uint16_t | R | 1
| 0x6A58 | 0x6A58 | 27224 | 27224 | Parameter 89 reading | uint16_t | R | 1
| 0x6A59 | 0x6A59 | 27225 | 27225 | Parameter 90 reading | uint16_t | R | 1
| 0x6A5A | 0x6A5A | 27226 | 27226 | Parameter 91 reading | uint16_t | R | 1
| 0x6A5B | 0x6A5B | 27227 | 27227 | Parameter 92 reading | uint16_t | R | 1
| 0x6A5C | 0x6A5C | 27228 | 27228 | Parameter 93 reading | uint16_t | R | 1
| 0x6A5D | 0x6A5D | 27229 | 27229 | Parameter 94 reading | uint16_t | R | 1
| 0x6A5E | 0x6A5E | 27230 | 27230 | Parameter 95 reading | uint16_t | R | 1
| 0x6A5F | 0x6A5F | 27231 | 27231 | Parameter 96 reading | uint16_t | R | 1
| 0x6A60 | 0x6A60 | 27232 | 27232 | Parameter 97 reading | uint16_t | R | 1
| 0x6A61 | 0x6A61 | 27233 | 27233 | Parameter 98 reading | uint16_t | R | 1
| 0x6A62 | 0x6A62 | 27234 | 27234 | Parameter 99 reading | uint16_t | R | 1
| 0x6A63 | 0x6A63 | 27235 | 27235 | Parameter 100 reading | uint16_t | R | 1
| 0x6A64 | 0x6A64 | 27236 | 27236 | Parameter 101 reading | uint16_t | R | 1
| 0x6A65 | 0x6A65 | 27237 | 27237 | Parameter 102 reading | uint16_t | R | 1
| 0x6A66 | 0x6A66 | 27238 | 27238 | Parameter 103 reading | uint16_t | R | 1
| 0x6A67 | 0x6A67 | 27239 | 27239 | Parameter 104 reading | uint16_t | R | 1
| 0x6A68 | 0x6A68 | 27240 | 27240 | Parameter 105 reading | uint16_t | R | 1
| 0x6A69 | 0x6A69 | 27241 | 27241 | Parameter 106 reading | uint16_t | R | 1
| 0x6A6A | 0x6A6A | 27242 | 27242 | Parameter 107 reading | uint16_t | R | 1
| 0x6A6B | 0x6A6B | 27243 | 27243 | Parameter 108 reading | uint16_t | R | 1
| 0x6A6C | 0x6A6C | 27244 | 27244 | Parameter 109 reading | uint16_t | R | 1
| 0x6A6D | 0x6A6D | 27245 | 27245 | Parameter 110 reading | uint16_t | R | 1
| 0x6A6E | 0x6A6E | 27246 | 27246 | Parameter 111 reading | uint16_t | R | 1
| 0x6A6F | 0x6A6F | 27247 | 27247 | Parameter 112 reading | uint16_t | R | 1
| 0x6A70 | 0x6A70 | 27248 | 27248 | Parameter 113 reading | uint16_t | R | 1
| 0x6A71 | 0x6A71 | 27249 | 27249 | Parameter 114 reading | uint16_t | R | 1
| 0x6A72 | 0x6A72 | 27250 | 27250 | Parameter 115 reading | uint16_t | R | 1
| 0x6A73 | 0x6A73 | 27251 | 27251 | Parameter 116 reading | uint16_t | R | 1
| 0x6A74 | 0x6A74 | 27252 | 27252 | Parameter 117 reading | uint16_t | R | 1
| 0x6A75 | 0x6A75 | 27253 | 27253 | Parameter 118 reading | uint16_t | R | 1
| 0x6A76 | 0x6A76 | 27254 | 27254 | Parameter 119 reading | uint16_t | R | 1
| 0x6A77 | 0x6A77 | 27255 | 27255 | Parameter 120 reading | uint16_t | R | 1
| 0x6A78 | 0x6A78 | 27256 | 27256 | Parameter 121 reading | uint16_t | R | 1
| 0x6A79 | 0x6A79 | 27257 | 27257 | Parameter 122 reading | uint16_t | R | 1
| 0x6A7A | 0x6A7A | 27258 | 27258 | Parameter 123 reading | uint16_t | R | 1
| 0x6A7B | 0x6A7B | 27259 | 27259 | Parameter 124 reading | uint16_t | R | 1
| 0x6A7C | 0x6A7C | 27260 | 27260 | Parameter 125 reading | uint16_t | R | 1
125
Custom read settings area | 0x6B00 | 0x6B00 | 27392 | 27392 | The number of bytes have been set | uint16_t | R/W | 1
| 0x6B01 | 0x6B01 | 27393 | 27393 | Parameter 1 Selection | uint16_t | R/W | 1
| 0x6B02 | 0x6B02 | 27394 | 27394 | Parameter 2 Selection | uint16_t | R/W | 1
| 0x6B03 | 0x6B03 | 27395 | 27395 | Parameter 3 Selection | uint16_t | R/W | 1
| 0x6B04 | 0x6B04 | 27396 | 27396 | Parameter 4 Selection | uint16_t | R/W | 1
| 0x6B05 | 0x6B05 | 27397 | 27397 | Parameter 5 Selection | uint16_t | R/W | 1
| 0x6B06 | 0x6B06 | 27398 | 27398 | Parameter 6 Selection | uint16_t | R/W | 1
| 0x6B07 | 0x6B07 | 27399 | 27399 | Parameter 7 Selection | uint16_t | R/W | 1
| 0x6B08 | 0x6B08 | 27400 | 27400 | Parameter 8 Selection | uint16_t | R/W | 1
| 0x6B09 | 0x6B09 | 27401 | 27401 | Parameter 9 Selection | uint16_t | R/W | 1
| 0x6B0A | 0x6B0A | 27402 | 27402 | Parameter 10 Selection | uint16_t | R/W | 1
| 0x6B0B | 0x6B0B | 27403 | 27403 | Parameter 11 Selection | uint16_t | R/W | 1
| 0x6B0C | 0x6B0C | 27404 | 27404 | Parameter 12 Selection | uint16_t | R/W | 1
| 0x6B0D | 0x6B0D | 27405 | 27405 | Parameter 13 Selection | uint16_t | R/W | 1
| 0x6B0E | 0x6B0E | 27406 | 27406 | Parameter 14 Selection | uint16_t | R/W | 1
| 0x6B0F | 0x6B0F | 27407 | 27407 | Parameter 15 Selection | uint16_t | R/W | 1
| 0x6B10 | 0x6B10 | 27408 | 27408 | Parameter 16 Selection | uint16_t | R/W | 1
| 0x6B11 | 0x6B11 | 27409 | 27409 | Parameter 17 Selection | uint16_t | R/W | 1
| 0x6B12 | 0x6B12 | 27410 | 27410 | Parameter 18 Selection | uint16_t | R/W | 1
| 0x6B13 | 0x6B13 | 27411 | 27411 | Parameter 19 Selection | uint16_t | R/W | 1
| 0x6B14 | 0x6B14 | 27412 | 27412 | Parameter 20 Selection | uint16_t | R/W | 1
| 0x6B15 | 0x6B15 | 27413 | 27413 | Parameter 21 Selection | uint16_t | R/W | 1
| 0x6B16 | 0x6B16 | 27414 | 27414 | Parameter 22 Selection | uint16_t | R/W | 1
| 0x6B17 | 0x6B17 | 27415 | 27415 | Parameter 23 Selection | uint16_t | R/W | 1
| 0x6B18 | 0x6B18 | 27416 | 27416 | Parameter 24 Selection | uint16_t | R/W | 1
| 0x6B19 | 0x6B19 | 27417 | 27417 | Parameter 25 Selection | uint16_t | R/W | 1
| 0x6B1A | 0x6B1A | 27418 | 27418 | Parameter 26 Selection | uint16_t | R/W | 1
| 0x6B1B | 0x6B1B | 27419 | 27419 | Parameter 27 Selection | uint16_t | R/W | 1
| 0x6B1C | 0x6B1C | 27420 | 27420 | Parameter 28 Selection | uint16_t | R/W | 1
| 0x6B1D | 0x6B1D | 27421 | 27421 | Parameter 29 Selection | uint16_t | R/W | 1
| 0x6B1E | 0x6B1E | 27422 | 27422 | Parameter 30 Selection | uint16_t | R/W | 1
| 0x6B1F | 0x6B1F | 27423 | 27423 | Parameter 31 Selection | uint16_t | R/W | 1
| 0x6B20 | 0x6B20 | 27424 | 27424 | Parameter 32 Selection | uint16_t | R/W | 1
| 0x6B21 | 0x6B21 | 27425 | 27425 | Parameter 33 Selection | uint16_t | R/W | 1
| 0x6B22 | 0x6B22 | 27426 | 27426 | Parameter 34 Selection | uint16_t | R/W | 1
| 0x6B23 | 0x6B23 | 27427 | 27427 | Parameter 35 Selection | uint16_t | R/W | 1
| 0x6B24 | 0x6B24 | 27428 | 27428 | Parameter 36 Selection | uint16_t | R/W | 1
| 0x6B25 | 0x6B25 | 27429 | 27429 | Parameter 37 Selection | uint16_t | R/W | 1
| 0x6B26 | 0x6B26 | 27430 | 27430 | Parameter 38 Selection | uint16_t | R/W | 1
| 0x6B27 | 0x6B27 | 27431 | 27431 | Parameter 39 Selection | uint16_t | R/W | 1
| 0x6B28 | 0x6B28 | 27432 | 27432 | Parameter 40 Selection | uint16_t | R/W | 1
| 0x6B29 | 0x6B29 | 27433 | 27433 | Parameter 41 Selection | uint16_t | R/W | 1
| 0x6B2A | 0x6B2A | 27434 | 27434 | Parameter 42 Selection | uint16_t | R/W | 1
| 0x6B2B | 0x6B2B | 27435 | 27435 | Parameter 43 Selection | uint16_t | R/W | 1
| 0x6B2C | 0x6B2C | 27436 | 27436 | Parameter 44 Selection | uint16_t | R/W | 1
| 0x6B2D | 0x6B2D | 27437 | 27437 | Parameter 45 Selection | uint16_t | R/W | 1
| 0x6B2E | 0x6B2E | 27438 | 27438 | Parameter 46 Selection | uint16_t | R/W | 1
| 0x6B2F | 0x6B2F | 27439 | 27439 | Parameter 47 Selection | uint16_t | R/W | 1
| 0x6B30 | 0x6B30 | 27440 | 27440 | Parameter 48 Selection | uint16_t | R/W | 1
| 0x6B31 | 0x6B31 | 27441 | 27441 | Parameter 49 Selection | uint16_t | R/W | 1
| 0x6B32 | 0x6B32 | 27442 | 27442 | Parameter 50 Selection | uint16_t | R/W | 1
| 0x6B33 | 0x6B33 | 27443 | 27443 | Parameter 51 Selection | uint16_t | R/W | 1
| 0x6B34 | 0x6B34 | 27444 | 27444 | Parameter 52 Selection | uint16_t | R/W | 1
| 0x6B35 | 0x6B35 | 27445 | 27445 | Parameter 53 Selection | uint16_t | R/W | 1
| 0x6B36 | 0x6B36 | 27446 | 27446 | Parameter 54 Selection | uint16_t | R/W | 1
| 0x6B37 | 0x6B37 | 27447 | 27447 | Parameter 55 Selection | uint16_t | R/W | 1
| 0x6B38 | 0x6B38 | 27448 | 27448 | Parameter 56 Selection | uint16_t | R/W | 1
| 0x6B39 | 0x6B39 | 27449 | 27449 | Parameter 57 Selection | uint16_t | R/W | 1
| 0x6B3A | 0x6B3A | 27450 | 27450 | Parameter 58 Selection | uint16_t | R/W | 1
| 0x6B3B | 0x6B3B | 27451 | 27451 | Parameter 59 Selection | uint16_t | R/W | 1
| 0x6B3C | 0x6B3C | 27452 | 27452 | Parameter 60 Selection | uint16_t | R/W | 1
| 0x6B3D | 0x6B3D | 27453 | 27453 | Parameter 61 Selection | uint16_t | R/W | 1
| 0x6B3E | 0x6B3E | 27454 | 27454 | Parameter 61 Selection | uint16_t | R/W | 1
| 0x6B3F | 0x6B3F | 27455 | 27455 | Parameter 63 Selection | uint16_t | R/W | 1
| 0x6B40 | 0x6B40 | 27456 | 27456 | Parameter 64 Selection | uint16_t | R/W | 1
| 0x6B41 | 0x6B41 | 27457 | 27457 | Parameter 65 Selection | uint16_t | R/W | 1
| 0x6B42 | 0x6B42 | 27458 | 27458 | Parameter 66 Selection | uint16_t | R/W | 1
| 0x6B43 | 0x6B43 | 27459 | 27459 | Parameter 67 Selection | uint16_t | R/W | 1
| 0x6B44 | 0x6B44 | 27460 | 27460 | Parameter 68 Selection | uint16_t | R/W | 1
| 0x6B45 | 0x6B45 | 27461 | 27461 | Parameter 69 Selection | uint16_t | R/W | 1
| 0x6B46 | 0x6B46 | 27462 | 27462 | Parameter 70 Selection | uint16_t | R/W | 1
| 0x6B47 | 0x6B47 | 27463 | 27463 | Parameter 71 Selection | uint16_t | R/W | 1
| 0x6B48 | 0x6B48 | 27464 | 27464 | Parameter 72 Selection | uint16_t | R/W | 1
| 0x6B49 | 0x6B49 | 27465 | 27465 | Parameter 73 Selection | uint16_t | R/W | 1
| 0x6B4A | 0x6B4A | 27466 | 27466 | Parameter 74 Selection | uint16_t | R/W | 1
| 0x6B4B | 0x6B4B | 27467 | 27467 | Parameter 75 Selection | uint16_t | R/W | 1
| 0x6B4C | 0x6B4C | 27468 | 27468 | Parameter 76 Selection | uint16_t | R/W | 1
| 0x6B4D | 0x6B4D | 27469 | 27469 | Parameter 77 Selection | uint16_t | R/W | 1
| 0x6B4E | 0x6B4E | 27470 | 27470 | Parameter 78 Selection | uint16_t | R/W | 1
| 0x6B4F | 0x6B4F | 27471 | 27471 | Parameter 79 Selection | uint16_t | R/W | 1
| 0x6B50 | 0x6B50 | 27472 | 27472 | Parameter 80 Selection | uint16_t | R/W | 1
| 0x6B51 | 0x6B51 | 27473 | 27473 | Parameter 81 Selection | uint16_t | R/W | 1
| 0x6B52 | 0x6B52 | 27474 | 27474 | Parameter 82 Selection | uint16_t | R/W | 1
| 0x6B53 | 0x6B53 | 27475 | 27475 | Parameter 83 Selection | uint16_t | R/W | 1
| 0x6B54 | 0x6B54 | 27476 | 27476 | Parameter 84 Selection | uint16_t | R/W | 1
| 0x6B55 | 0x6B55 | 27477 | 27477 | Parameter 85 Selection | uint16_t | R/W | 1
| 0x6B56 | 0x6B56 | 27478 | 27478 | Parameter 86 Selection | uint16_t | R/W | 1
| 0x6B57 | 0x6B57 | 27479 | 27479 | Parameter 87 Selection | uint16_t | R/W | 1
| 0x6B58 | 0x6B58 | 27480 | 27480 | Parameter 88 Selection | uint16_t | R/W | 1
| 0x6B59 | 0x6B59 | 27481 | 27481 | Parameter 89 Selection | uint16_t | R/W | 1
| 0x6B5A | 0x6B5A | 27482 | 27482 | Parameter 90 Selection | uint16_t | R/W | 1
| 0x6B5B | 0x6B5B | 27483 | 27483 | Parameter 91 Selection | uint16_t | R/W | 1
| 0x6B5C | 0x6B5C | 27484 | 27484 | Parameter 92 Selection | uint16_t | R/W | 1
| 0x6B5D | 0x6B5D | 27485 | 27485 | Parameter 93 Selection | uint16_t | R/W | 1
| 0x6B5E | 0x6B5E | 27486 | 27486 | Parameter 94 Selection | uint16_t | R/W | 1
| 0x6B5F | 0x6B5F | 27487 | 27487 | Parameter 95 Selection | uint16_t | R/W | 1
| 0x6B60 | 0x6B60 | 27488 | 27488 | Parameter 96 Selection | uint16_t | R/W | 1
| 0x6B61 | 0x6B61 | 27489 | 27489 | Parameter 97 Selection | uint16_t | R/W | 1
| 0x6B62 | 0x6B62 | 27490 | 27490 | Parameter 98 Selection | uint16_t | R/W | 1
| 0x6B63 | 0x6B63 | 27491 | 27491 | Parameter 99 Selection | uint16_t | R/W | 1
| 0x6B64 | 0x6B64 | 27492 | 27492 | Parameter 100 Selection | uint16_t | R/W | 1
| 0x6B65 | 0x6B65 | 27493 | 27493 | Parameter 101 Selection | uint16_t | R/W | 1
| 0x6B66 | 0x6B66 | 27494 | 27494 | Parameter 102 Selection | uint16_t | R/W | 1
| 0x6B67 | 0x6B67 | 27495 | 27495 | Parameter 103 Selection | uint16_t | R/W | 1
| 0x6B68 | 0x6B68 | 27496 | 27496 | Parameter 104 Selection | uint16_t | R/W | 1
| 0x6B69 | 0x6B69 | 27497 | 27497 | Parameter 105 Selection | uint16_t | R/W | 1
| 0x6B6A | 0x6B6A | 27498 | 27498 | Parameter 106 Selection | uint16_t | R/W | 1
| 0x6B6B | 0x6B6B | 27499 | 27499 | Parameter 107 Selection | uint16_t | R/W | 1
| 0x6B6C | 0x6B6C | 27500 | 27500 | Parameter 108 Selection | uint16_t | R/W | 1
| 0x6B6D | 0x6B6D | 27501 | 27501 | Parameter 109 Selection | uint16_t | R/W | 1
| 0x6B6E | 0x6B6E | 27502 | 27502 | Parameter 110 Selection | uint16_t | R/W | 1
| 0x6B6F | 0x6B6F | 27503 | 27503 | Parameter 111 Selection | uint16_t | R/W | 1
| 0x6B70 | 0x6B70 | 27504 | 27504 | Parameter 112 Selection | uint16_t | R/W | 1
| 0x6B71 | 0x6B71 | 27505 | 27505 | Parameter 113 Selection | uint16_t | R/W | 1
| 0x6B72 | 0x6B72 | 27506 | 27506 | Parameter 114 Selection | uint16_t | R/W | 1
| 0x6B73 | 0x6B73 | 27507 | 27507 | Parameter 115 Selection | uint16_t | R/W | 1
| 0x6B74 | 0x6B74 | 27508 | 27508 | Parameter 116 Selection | uint16_t | R/W | 1
| 0x6B75 | 0x6B75 | 27509 | 27509 | Parameter 117 Selection | uint16_t | R/W | 1
| 0x6B76 | 0x6B76 | 27510 | 27510 | Parameter 118 Selection | uint16_t | R/W | 1
| 0x6B77 | 0x6B77 | 27511 | 27511 | Parameter 119 Selection | uint16_t | R/W | 1
| 0x6B78 | 0x6B78 | 27512 | 27512 | Parameter 120 Selection | uint16_t | R/W | 1
| 0x6B79 | 0x6B79 | 27513 | 27513 | Parameter 121 Selection | uint16_t | R/W | 1
| 0x6B7A | 0x6B7A | 27514 | 27514 | Parameter 122 Selection | uint16_t | R/W | 1
| 0x6B7B | 0x6B7B | 27515 | 27515 | Parameter 123 Selection | uint16_t | R/W | 1
| 0x6B7C | 0x6B7C | 27516 | 27516 | Parameter 124 Selection | uint16_t | R/W | 1
| 0x6B7D | 0x6B7D | 27517 | 27517 | Parameter 125 Selection | uint16_t | R/W | 1

## TOU Default Setting
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
TOU factory default setting code function : 03H Read, 10H Write
| 0x5C00 | 0x5C00 | 23552 | 23552 | Clear factory value of multiple rates time zone | uint16_t | R/W | 1 | Send 0xAA to clear
| 0x5C01 | 0x5C01 | 23553 | 23553 | Note: Before setting factory value of multiple rates time zone, this command is needed | uint16_t | R/W | 1
| 0x5C02 | 0x5C02 | 23554 | 23554 | Year time zone number | uint16_t | R/W | 1 | 0~12
| 0x5C03 | 0x5C03 | 23555 | 23555 | day time section record number | uint16_t | R/W | 1 | 0~14
| 0x5C04 | 0x5C04 | 23556 | 23556 | day time section number | uint16_t | R/W | 1 | 0~14
| 0x5C05 | 0x5C05 | 23557 | 23557 | Tarif number | uint16_t | R/W | 1 | 0~3
| 0x5C06 | 0x5C06 | 23558 | 23558 | Week off（0: no week off day;1: Sunday;2: Saturday;3: Sunday, Saturday） | uint16_t | R/W | 1 | 0~127
| 0x5C07 | 0x5C07 | 23559 | 23559 | Week off time section | uint16_t | R/W | 1 | 0~14
| 0x5C08 | 0x5C08 | 23560 | 23560 | Special day number | uint16_t | R/W | 1 | 0~30
| 0x5C09 | 0x5C09 | 23561 | 23561 | Enable TOU | uint16_t | R/W | 1 | 1: enable
| 0x5C0A | 0x5C0A | 23562 | 23562 | Enable TOU time setup restoring to factory value | uint16_t | R/W | 1 | 1: enable
| 0x5C0B | 0x5C0B | 23563 | 23563 | Tou month settlement model 0: nature weekend） | uint16_t | R/W | 1 | 0~1
| 0x5C0C | 0x5C0C | 23564 | 23564 | Tou month settlement time: day （default: 1） | uint16_t | R/W | 1 | 1~31
| 0x5C0D | 0x5C0D | 23565 | 23565 | Tou month settlement time: hour （default: 0） | uint16_t | R/W | 1 | 0~23
| 0x5C0E | 0x5C0E | 23566 | 23566 | Tou month settlement time: minute （default: 0） | uint16_t | R/W | 1 | 0~59
| 0x5C0F | 0x5C0F | 23567 | 23567 | Tou month settlement time: second （default: 0） | uint16_t | R/W | 1 | 0~59
| 0x5C10 | 0x5C10 | 23568 | 23568 | Fault state word（default） | uint16_t | R | 1 | 0: Settings correct
17
TOU schedule & season & holiday setting code function : 03H Read, 6AH Write
| 0x5C11 | 0x5C13 | 23569 | 23571 | 1st time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C14 | 0x5C16 | 23572 | 23574 | 2nd time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C17 | 0x5C19 | 23575 | 23577 | 3rd time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C1A | 0x5C1C | 23578 | 23580 | 4th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C1D | 0x5C1F | 23581 | 23583 | 5th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C20 | 0x5C22 | 23584 | 23586 | 6th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C23 | 0x5C25 | 23587 | 23589 | 7th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C26 | 0x5C28 | 23590 | 23592 | 8th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C29 | 0x5C2B | 23593 | 23595 | 9th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C2C | 0x5C2E | 23596 | 23598 | 10th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C2F | 0x5C31 | 23599 | 23601 | 11th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C32 | 0x5C34 | 23602 | 23604 | 12th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x5C35 | 0x5C37 | 23605 | 23607 | 1st day time section, 1st time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C38 | 0x5C3A | 23608 | 23610 | 1st day time section, 2nd time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C3B | 0x5C3D | 23611 | 23613 | 1st day time section, 3rd time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C3E | 0x5C40 | 23614 | 23616 | 1st day time section, 4th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C41 | 0x5C43 | 23617 | 23619 | 1st day time section, 5th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C44 | 0x5C46 | 23620 | 23622 | 1st day time section, 6th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C47 | 0x5C49 | 23623 | 23625 | 1st day time section, 7th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C4A | 0x5C4C | 23626 | 23628 | 1st day time section, 8th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C4D | 0x5C4F | 23629 | 23631 | 1st day time section, 9th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C50 | 0x5C52 | 23632 | 23634 | 1st day time section, 10th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C53 | 0x5C55 | 23635 | 23637 | 1st day time section, 11th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C56 | 0x5C58 | 23638 | 23640 | 1st day time section, 12th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C59 | 0x5C5B | 23641 | 23643 | 1st day time section, 13th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C5C | 0x5C5E | 23644 | 23646 | 1st day time section, 14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x5C5F | 0x5C88 | 23647 | 23688 | 2nd day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5C89 | 0x5CB2 | 23689 | 23730 | 3rd day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5CB3 | 0x5CDC | 23731 | 23772 | 4th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5CDD | 0x5D06 | 23773 | 23814 | 5th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5D07 | 0x5D30 | 23815 | 23856 | 6th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5D31 | 0x5D5A | 23857 | 23898 | 7th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5D5B | 0x5D84 | 23899 | 23940 | 8th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5D85 | 0x5DAE | 23941 | 23982 | 9th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5DAF | 0x5DD8 | 23983 | 24024 | 10th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5DD9 | 0x5E02 | 24025 | 24066 | 11th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5E03 | 0x5E2C | 24067 | 24108 | 12th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5E2D | 0x5E56 | 24109 | 24150 | 13th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5E57 | 0x5E80 | 24151 | 24192 | 14th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x5E81 | 0x5E83 | 24193 | 24195 | 1st special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5E84 | 0x5E86 | 24196 | 24198 | 2nd special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5E87 | 0x5E89 | 24199 | 24201 | 3rd special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5E8A | 0x5E8C | 24202 | 24204 | 4th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5E8D | 0x5E8F | 24205 | 24207 | 5th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5E90 | 0x5E92 | 24208 | 24210 | 6th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5E93 | 0x5E95 | 24211 | 24213 | 7th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5E96 | 0x5E98 | 24214 | 24216 | 8th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5E99 | 0x5E9B | 24217 | 24219 | 9th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5E9C | 0x5E9E | 24220 | 24222 | 10th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5E9F | 0x5EA1 | 24223 | 24225 | 11th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EA2 | 0x5EA4 | 24226 | 24228 | 12th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EA5 | 0x5EA7 | 24229 | 24231 | 13th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EA8 | 0x5EAA | 24232 | 24234 | 14th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EAB | 0x5EAD | 24235 | 24237 | 15th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EAE | 0x5EB0 | 24238 | 24240 | 16th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EB1 | 0x5EB3 | 24241 | 24243 | 17th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EB4 | 0x5EB6 | 24244 | 24246 | 18th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EB7 | 0x5EB9 | 24247 | 24249 | 19th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EBA | 0x5EBC | 24250 | 24252 | 20th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EBD | 0x5EBF | 24253 | 24255 | 21st special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EC0 | 0x5EC2 | 24256 | 24258 | 22nd special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EC3 | 0x5EC5 | 24259 | 24261 | 23rd special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EC6 | 0x5EC8 | 24262 | 24264 | 24th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EC9 | 0x5ECB | 24265 | 24267 | 25th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5ECC | 0x5ECE | 24268 | 24270 | 26th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5ECF | 0x5ED1 | 24271 | 24273 | 27th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5ED2 | 0x5ED4 | 24274 | 24276 | 28th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5ED5 | 0x5ED7 | 24277 | 24279 | 29th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5ED8 | 0x5EDA | 24280 | 24282 | 30th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x5EDB | 0x5EDB | 24283 | 24283 | Default enable/disable ”Holiday many year setup“ | uint16_t | R/W | 1 | 1: enable
| 0x5EDC | 0x5EDC | 24284 | 24284 | Default beginning year of ”Holiday many year setup“ | uint16_t | R/W | 1 | 2000~2099
| 0x5EDD | 0x5EDD | 24285 | 24285 | Default ending year of ”Holiday many year setup“ | uint16_t | R/W | 1 | 2000~2099
717
10years holidy factory default setting code function : 03H Read, 6AH Write
| 0x5EDE | 0x5F73 | 24286 | 24435 | Setup address for ten year holiday by PC | uint16_t | R/W | 150

## TOU Setting
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Daylight Savings Time Settings code function : 03H Read, 10H Write
| 0x6000 | 0x6000 | 24576 | 24576 | DST enable | uint16_t | R/W | 1 | 0: disable 1: enable
| 0x6001 | 0x6001 | 24577 | 24577 | DST format | uint16_t | R/W | 1 | 0: format 1(fixed date) 1: format 2 (non fixed date)
Format 1: Fixed Date : 03H Read, 10H Write
| 0x6002 | 0x6002 | 24578 | 24578 | DST Start Month | uint16_t | R/W | 1 | 1~12
| 0x6003 | 0x6003 | 24579 | 24579 | DST Start Day | uint16_t | R/W | 1 | 1~31
| 0x6004 | 0x6004 | 24580 | 24580 | DST Start Hour | uint16_t | R/W | 1 | 0-23
| 0x6005 | 0x6005 | 24581 | 24581 | DST Start Min | uint16_t | R/W | 1 | 0-59
| 0x6006 | 0x6006 | 24582 | 24582 | DST Start Adjust time (Unit: Min) | uint16_t | R/W | 1 | 1-120
| 0x6007 | 0x6007 | 24583 | 24583 | DST End Month | uint16_t | R/W | 1 | 1~12
| 0x6008 | 0x6008 | 24584 | 24584 | DST End Day | uint16_t | R/W | 1 | 1~31
| 0x6009 | 0x6009 | 24585 | 24585 | DST End Hour | uint16_t | R/W | 1 | 0-23
| 0x600A | 0x600A | 24586 | 24586 | DST End Minute | uint16_t | R/W | 1 | 0-59
| 0x600B | 0x600B | 24587 | 24587 | DST End Adjust time (Unit: Minute) | uint16_t | R/W | 1 | 1-120
Format 2: Non Fixed Date : 03H Read, 10H Write
| 0x600C | 0x600C | 24588 | 24588 | DST Start Month | uint16_t | R/W | 1 | 1~12
| 0x600D | 0x600D | 24589 | 24589 | DST Start Day | uint16_t | R/W | 1 | 0-6 0: Sunday 1~6: Monday to Saturday
| 0x600E | 0x600E | 24590 | 24590 | DST Start Week | uint16_t | R/W | 1 | 1~5
| 0x600F | 0x600F | 24591 | 24591 | DST Start Hour | uint16_t | R/W | 1 | 0-23
| 0x6010 | 0x6010 | 24592 | 24592 | DST Start Minute | uint16_t | R/W | 1 | 0-59
| 0x6011 | 0x6011 | 24593 | 24593 | DST Start Adjust time (Unit: Minute) | uint16_t | R/W | 1 | 1-120
| 0x6012 | 0x6012 | 24594 | 24594 | DST End Month | uint16_t | R/W | 1 | 1~12
| 0x6013 | 0x6013 | 24595 | 24595 | DST End Day | uint16_t | R/W | 1 | 0-6 0: Sunday 1~6 Monday to Saturday
| 0x6014 | 0x6014 | 24596 | 24596 | DST End Week | uint16_t | R/W | 1 | 1~5
| 0x6015 | 0x6015 | 24597 | 24597 | DST End Hour | uint16_t | R/W | 1 | 0-23
| 0x6016 | 0x6016 | 24598 | 24598 | DST End Minute | uint16_t | R/W | 1 | 0-59
| 0x6017 | 0x6017 | 24599 | 24599 | DST End Adjust time (Unit: Minute) | uint16_t | R/W | 1 | 1-120
TOU Basic Setting : 03H Read, 10H Write
| 0x6018 | 0x6018 | 24600 | 24600 | Number of seasons | uint16_t | R/W | 1 | 0~12
| 0x6019 | 0x6019 | 24601 | 24601 | Number of schedules | uint16_t | R/W | 1 | 0~14
| 0x601A | 0x601A | 24602 | 24602 | Number of segments | uint16_t | R/W | 1 | 0~14
| 0x601B | 0x601B | 24603 | 24603 | Number of tariffs | uint16_t | R/W | 1 | 0~3
| 0x601C | 0x601C | 24604 | 24604 | Weekend setting (Bit0: Sunday; Bit1-Bit6: Mon-Sat) bit=0: not weekend bit=1: is weekend | uint16_t | R/W | 1 | 0~127
| 0x601D | 0x601D | 24605 | 24605 | Weekend Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x601E | 0x601E | 24606 | 24606 | Number of holidays | uint16_t | R/W | 1 | 0~30
| 0x601F | 0x601F | 24607 | 24607 | Enable TOU | uint16_t | R/W | 1 | 1: enable
| 0x6020 |  | 24608
| 0x6020 | 0x6020 | 24608 | 24608 | Monthly Billing Mode | uint16_t | R/W | 1 | 0~1
| 0x6021 | 0x6021 | 24609 | 24609 | Billing time: day | uint16_t | R/W | 1 | 1~31
| 0x6022 | 0x6022 | 24610 | 24610 | Billing time : hour | uint16_t | R/W | 1 | 0~23
| 0x6023 | 0x6023 | 24611 | 24611 | Billing time: minute | uint16_t | R/W | 1 | 0~59
| 0x6024 | 0x6024 | 24612 | 24612 | Billing time: second | uint16_t | R/W | 1 | 0~59
| 0x6025 | 0x6025 | 24613 | 24613 | Error Code | uint16_t | R | 1 | 0: Settings correct
Season setting : 03H Read, 10H Write
| 0x6026 | 0x6028 | 24614 | 24616 | TOU Season 1 | uint16_t | R/W | 3 | In format of month, day, schedule ID
| 0x6029 | 0x602B | 24617 | 24619 | TOU Season 2 | uint16_t | R/W | 3
| 0x602C | 0x602E | 24620 | 24622 | TOU Season 3 | uint16_t | R/W | 3
| 0x602F | 0x6031 | 24623 | 24625 | TOU Season 4 | uint16_t | R/W | 3
| 0x6032 | 0x6034 | 24626 | 24628 | TOU Season 5 | uint16_t | R/W | 3
| 0x6035 | 0x6037 | 24629 | 24631 | TOU Season 6 | uint16_t | R/W | 3
| 0x6038 | 0x603A | 24632 | 24634 | TOU Season 7 | uint16_t | R/W | 3
| 0x603B | 0x603D | 24635 | 24637 | TOU Season 8 | uint16_t | R/W | 3
| 0x603E | 0x6040 | 24638 | 24640 | TOU Season 9 | uint16_t | R/W | 3
| 0x6041 | 0x6043 | 24641 | 24643 | TOU Season 10 | uint16_t | R/W | 3
| 0x6044 | 0x6046 | 24644 | 24646 | TOU Season 11 | uint16_t | R/W | 3
| 0x6047 | 0x6049 | 24647 | 24649 | TOU Season 12 | uint16_t | R/W | 3
Schedule setting : 03H Read, 10H Write
| 0x604A | 0x604C | 24650 | 24652 | Schedule 1 Segment 1 setting In format of hour, minutes, segment （是tariffs）ID | uint16_t | R/W | 3
| 0x604D | 0x604F | 24653 | 24655 | Schedule 1 Segment 2 setting | uint16_t | R/W | 3
| 0x6050 | 0x6052 | 24656 | 24658 | Schedule 1 Segment 3 setting | uint16_t | R/W | 3
| 0x6053 | 0x6055 | 24659 | 24661 | Schedule 1 Segment 4 setting | uint16_t | R/W | 3
| 0x6056 | 0x6058 | 24662 | 24664 | Schedule 1 Segment 5 setting | uint16_t | R/W | 3
| 0x6059 | 0x605B | 24665 | 24667 | Schedule 1 Segment 6 setting | uint16_t | R/W | 3
| 0x605C | 0x605E | 24668 | 24670 | Schedule 1 Segment 7 setting | uint16_t | R/W | 3
| 0x605F | 0x6061 | 24671 | 24673 | Schedule 1 Segment 8 setting | uint16_t | R/W | 3
| 0x6062 | 0x6064 | 24674 | 24676 | Schedule 1 Segment 9 setting | uint16_t | R/W | 3
| 0x6065 | 0x6067 | 24677 | 24679 | Schedule 1 Segment 10 setting | uint16_t | R/W | 3
| 0x6068 | 0x606A | 24680 | 24682 | Schedule 1 Segment 11 setting | uint16_t | R/W | 3
| 0x606B | 0x606D | 24683 | 24685 | Schedule 1 Segment 12 setting | uint16_t | R/W | 3
| 0x606E | 0x6070 | 24686 | 24688 | Schedule 1 Segment 13 setting | uint16_t | R/W | 3
| 0x6071 | 0x6073 | 24689 | 24691 | Schedule 1 Segment 14 setting | uint16_t | R/W | 3
| 0x6074 | 0x609D | 24692 | 24733 | Schedule 2 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x609E | 0x60C7 | 24734 | 24775 | Schedule 3 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x60C8 | 0x60F1 | 24776 | 24817 | Schedule 4 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x60F2 | 0x611B | 24818 | 24859 | Schedule 5 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x611C | 0x6145 | 24860 | 24901 | Schedule 6 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x6146 | 0x616F | 24902 | 24943 | Schedule 7 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x6170 | 0x6199 | 24944 | 24985 | Schedule 8 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x619A | 0x61C3 | 24986 | 25027 | Schedule 9 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x61C4 | 0x61ED | 25028 | 25069 | Schedule 10 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x61EE | 0x6217 | 25070 | 25111 | Schedule 11 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x6218 | 0x6241 | 25112 | 25153 | Schedule 12 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x6242 | 0x626B | 25154 | 25195 | Schedule 13 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
| 0x626C | 0x6295 | 25196 | 25237 | Schedule 14 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting
Holiday setting : 03H Read, 10H Write
| 0x6296 | 0x6298 | 25238 | 25240 | 1st Holiday setting In format of month, day, schedule ID | uint16_t | R/W | 3
| 0x6299 | 0x629B | 25241 | 25243 | 2nd Holiday setting | uint16_t | R/W | 3
| 0x629C | 0x629E | 25244 | 25246 | 3rd Holiday setting | uint16_t | R/W | 3
| 0x629F | 0x62A1 | 25247 | 25249 | 4th Holiday setting | uint16_t | R/W | 3
| 0x62A2 | 0x62A4 | 25250 | 25252 | 5th Holiday setting | uint16_t | R/W | 3
| 0x62A5 | 0x62A7 | 25253 | 25255 | 6th Holiday setting | uint16_t | R/W | 3
| 0x62A8 | 0x62AA | 25256 | 25258 | 7th Holiday setting | uint16_t | R/W | 3
| 0x62AB | 0x62AD | 25259 | 25261 | 8th Holiday setting | uint16_t | R/W | 3
| 0x62AE | 0x62B0 | 25262 | 25264 | 9th Holiday setting | uint16_t | R/W | 3
| 0x62B1 | 0x62B3 | 25265 | 25267 | 10th Holiday setting | uint16_t | R/W | 3
| 0x62B4 | 0x62B6 | 25268 | 25270 | 11th Holiday setting | uint16_t | R/W | 3
| 0x62B7 | 0x62B9 | 25271 | 25273 | 12th Holiday setting | uint16_t | R/W | 3
| 0x62BA | 0x62BC | 25274 | 25276 | 13th Holiday setting | uint16_t | R/W | 3
| 0x62BD | 0x62BF | 25277 | 25279 | 14th Holiday setting | uint16_t | R/W | 3
| 0x62C0 | 0x62C2 | 25280 | 25282 | 15th Holiday setting | uint16_t | R/W | 3
| 0x62C3 | 0x62C5 | 25283 | 25285 | 16th Holiday setting | uint16_t | R/W | 3
| 0x62C6 | 0x62C8 | 25286 | 25288 | 17th Holiday setting | uint16_t | R/W | 3
| 0x62C9 | 0x62CB | 25289 | 25291 | 18th Holiday setting | uint16_t | R/W | 3
| 0x62CC | 0x62CE | 25292 | 25294 | 19th Holiday setting | uint16_t | R/W | 3
| 0x62CF | 0x62D1 | 25295 | 25297 | 20th Holiday setting | uint16_t | R/W | 3
| 0x62D2 | 0x62D4 | 25298 | 25300 | 21st Holiday setting | uint16_t | R/W | 3
| 0x62D5 | 0x62D7 | 25301 | 25303 | 22nd Holiday setting | uint16_t | R/W | 3
| 0x62D8 | 0x62DA | 25304 | 25306 | 23rd Holiday setting | uint16_t | R/W | 3
| 0x62DB | 0x62DD | 25307 | 25309 | 24th Holiday setting | uint16_t | R/W | 3
| 0x62DE | 0x62E0 | 25310 | 25312 | 25th Holiday setting | uint16_t | R/W | 3
| 0x62E1 | 0x62E3 | 25313 | 25315 | 26th Holiday setting | uint16_t | R/W | 3
| 0x62E4 | 0x62E6 | 25316 | 25318 | 27th Holiday setting | uint16_t | R/W | 3
| 0x62E7 | 0x62E9 | 25319 | 25321 | 28th Holiday setting | uint16_t | R/W | 3
| 0x62EA | 0x62EC | 25322 | 25324 | 29th Holiday setting | uint16_t | R/W | 3
| 0x62ED | 0x62EF | 25325 | 25327 | 30th Holiday setting | uint16_t | R/W | 3
| 0x62F0 | 0x62F0 | 25328 | 25328 | Holiday Setting enable | uint16_t | R/W | 1 | 752
| 0x62F1 | 0x62F1 | 25329 | 25329 | Start Year | uint16_t | R/W | 1
| 0x62F2 | 0x62F2 | 25330 | 25330 | End Year | uint16_t | R/W | 1
755
10 years holiday setting : 03H Read, 10H Write
| 0x62F3 | 0x62F5 | 25331 | 25333 | Year 1 holiday 1 setting In format of month, day, schedule ID | uint16_t | R/W | 3
| 0x62F6 | 0x62F8 | 25334 | 25336 | Year 1 holiday 2 setting | uint16_t | R/W | 3
| 0x62F9 | 0x62FB | 25337 | 25339 | Year 1 holiday 3 setting | uint16_t | R/W | 3
| 0x62FC | 0x62FE | 25340 | 25342 | Year 1 holiday 4 setting | uint16_t | R/W | 3
| 0x62FF | 0x6301 | 25343 | 25345 | Year 1 holiday 5 setting | uint16_t | R/W | 3
| 0x6302 | 0x6304 | 25346 | 25348 | Year 1 holiday 6 setting | uint16_t | R/W | 3
| 0x6305 | 0x6307 | 25349 | 25351 | Year 1 holiday 7 setting | uint16_t | R/W | 3
| 0x6308 | 0x630A | 25352 | 25354 | Year 1 holiday 8 setting | uint16_t | R/W | 3
| 0x630B | 0x630D | 25355 | 25357 | Year 1 holiday 9 setting | uint16_t | R/W | 3
| 0x630E | 0x6310 | 25358 | 25360 | Year 1 holiday 10 setting | uint16_t | R/W | 3
| 0x6311 | 0x6313 | 25361 | 25363 | Year 1 holiday 11 setting | uint16_t | R/W | 3
| 0x6314 | 0x6316 | 25364 | 25366 | Year 1 holiday 12 setting | uint16_t | R/W | 3
| 0x6317 | 0x6319 | 25367 | 25369 | Year 1 holiday 13 setting | uint16_t | R/W | 3
| 0x631A | 0x631C | 25370 | 25372 | Year 1 holiday 14 setting | uint16_t | R/W | 3
| 0x631D | 0x631F | 25373 | 25375 | Year 1 holiday 15 setting | uint16_t | R/W | 3
| 0x6320 | 0x6322 | 25376 | 25378 | Year 1 holiday 16 setting | uint16_t | R/W | 3
| 0x6323 | 0x6325 | 25379 | 25381 | Year 1 holiday 17 setting | uint16_t | R/W | 3
| 0x6326 | 0x6328 | 25382 | 25384 | Year 1 holiday 18 setting | uint16_t | R/W | 3
| 0x6329 | 0x632B | 25385 | 25387 | Year 1 holiday 19 setting | uint16_t | R/W | 3
| 0x632C | 0x632E | 25388 | 25390 | Year 1 holiday 20 setting | uint16_t | R/W | 3
| 0x632F | 0x6331 | 25391 | 25393 | Year 1 holiday 21 setting | uint16_t | R/W | 3
| 0x6332 | 0x6334 | 25394 | 25396 | Year 1 holiday 22 setting | uint16_t | R/W | 3
| 0x6335 | 0x6337 | 25397 | 25399 | Year 1 holiday 23 setting | uint16_t | R/W | 3
| 0x6338 | 0x633A | 25400 | 25402 | Year 1 holiday 24 setting | uint16_t | R/W | 3
| 0x633B | 0x633D | 25403 | 25405 | Year 1 holiday 25 setting | uint16_t | R/W | 3
| 0x633E | 0x6340 | 25406 | 25408 | Year 1 holiday 26 setting | uint16_t | R/W | 3
| 0x6341 | 0x6343 | 25409 | 25411 | Year 1 holiday 27 setting | uint16_t | R/W | 3
| 0x6344 | 0x6346 | 25412 | 25414 | Year 1 holiday 28 setting | uint16_t | R/W | 3
| 0x6347 | 0x6349 | 25415 | 25417 | Year 1 holiday 29 setting | uint16_t | R/W | 3
| 0x634A | 0x634C | 25418 | 25420 | Year 1 holiday 30 setting | uint16_t | R/W | 3
| 0x634D | 0x634D | 25421 | 25421 | Year 1 setting Year | uint16_t | R/W | 1
| 0x634E | 0x634E | 25422 | 25422 | Year 1 Number of holidays | uint16_t | R/W | 1
| 0x634F | 0x6351 | 25423 | 25425 | Year 2 holiday 1 setting | uint16_t | R/W | 3
| 0x6352 | 0x6354 | 25426 | 25428 | Year 2 holiday 2 setting | uint16_t | R/W | 3
| 0x6355 | 0x6357 | 25429 | 25431 | Year 2 holiday 3 setting | uint16_t | R/W | 3
| 0x6358 | 0x635A | 25432 | 25434 | Year 2 holiday 4 setting | uint16_t | R/W | 3
| 0x635B | 0x635D | 25435 | 25437 | Year 2 holiday 5 setting | uint16_t | R/W | 3
| 0x635E | 0x6360 | 25438 | 25440 | Year 2 holiday 6 setting | uint16_t | R/W | 3
| 0x6361 | 0x6363 | 25441 | 25443 | Year 2 holiday 7 setting | uint16_t | R/W | 3
| 0x6364 | 0x6366 | 25444 | 25446 | Year 2 holiday 8 setting | uint16_t | R/W | 3
| 0x6367 | 0x6369 | 25447 | 25449 | Year 2 holiday 9 setting | uint16_t | R/W | 3
| 0x636A | 0x636C | 25450 | 25452 | Year 2 holiday 10 setting | uint16_t | R/W | 3
| 0x636D | 0x636F | 25453 | 25455 | Year 2 holiday 11 setting | uint16_t | R/W | 3
| 0x6370 | 0x6372 | 25456 | 25458 | Year 2 holiday 12 setting | uint16_t | R/W | 3
| 0x6373 | 0x6375 | 25459 | 25461 | Year 2 holiday 13 setting | uint16_t | R/W | 3
| 0x6376 | 0x6378 | 25462 | 25464 | Year 2 holiday 14 setting | uint16_t | R/W | 3
| 0x6379 | 0x637B | 25465 | 25467 | Year 2 holiday 15 setting | uint16_t | R/W | 3
| 0x637C | 0x637E | 25468 | 25470 | Year 2 holiday 16 setting | uint16_t | R/W | 3
| 0x637F | 0x6381 | 25471 | 25473 | Year 2 holiday 17 setting | uint16_t | R/W | 3
| 0x6382 | 0x6384 | 25474 | 25476 | Year 2 holiday 18 setting | uint16_t | R/W | 3
| 0x6385 | 0x6387 | 25477 | 25479 | Year 2 holiday 19 setting | uint16_t | R/W | 3
| 0x6388 | 0x638A | 25480 | 25482 | Year 2 holiday 20 setting | uint16_t | R/W | 3
| 0x638B | 0x638D | 25483 | 25485 | Year 2 holiday 21 setting | uint16_t | R/W | 3
| 0x638E | 0x6390 | 25486 | 25488 | Year 2 holiday 22 setting | uint16_t | R/W | 3
| 0x6391 | 0x6393 | 25489 | 25491 | Year 2 holiday 23 setting | uint16_t | R/W | 3
| 0x6394 | 0x6396 | 25492 | 25494 | Year 2 holiday 24 setting | uint16_t | R/W | 3
| 0x6397 | 0x6399 | 25495 | 25497 | Year 2 holiday 25 setting | uint16_t | R/W | 3
| 0x639A | 0x639C | 25498 | 25500 | Year 2 holiday 26 setting | uint16_t | R/W | 3
| 0x639D | 0x639F | 25501 | 25503 | Year 2 holiday 27 setting | uint16_t | R/W | 3
| 0x63A0 | 0x63A2 | 25504 | 25506 | Year 2 holiday 28 setting | uint16_t | R/W | 3
| 0x63A3 | 0x63A5 | 25507 | 25509 | Year 2 holiday 29 setting | uint16_t | R/W | 3
| 0x63A6 | 0x63A8 | 25510 | 25512 | Year 2 holiday 30 setting | uint16_t | R/W | 3
| 0x63A9 | 0x63A9 | 25513 | 25513 | Year 2 Setting Year | uint16_t | R/W | 1
| 0x63AA | 0x63AA | 25514 | 25514 | Year 2 Holiday Number setting | uint16_t | R/W | 1
| 0x63AB | 0x63AD | 25515 | 25517 | Year 3 holiday 1 setting | uint16_t | R/W | 3
| 0x63AE | 0x63B0 | 25518 | 25520 | Year 3 holiday 2 setting | uint16_t | R/W | 3
| 0x63B1 | 0x63B3 | 25521 | 25523 | Year 3 holiday 3 setting | uint16_t | R/W | 3
| 0x63B4 | 0x63B6 | 25524 | 25526 | Year 3 holiday 4 setting | uint16_t | R/W | 3
| 0x63B7 | 0x63B9 | 25527 | 25529 | Year 3 holiday 5 setting | uint16_t | R/W | 3
| 0x63BA | 0x63BC | 25530 | 25532 | Year 3 holiday 6 setting | uint16_t | R/W | 3
| 0x63BD | 0x63BF | 25533 | 25535 | Year 3 holiday 7 setting | uint16_t | R/W | 3
| 0x63C0 | 0x63C2 | 25536 | 25538 | Year 3 holiday 8 setting | uint16_t | R/W | 3
| 0x63C3 | 0x63C5 | 25539 | 25541 | Year 3 holiday 9 setting | uint16_t | R/W | 3
| 0x63C6 | 0x63C8 | 25542 | 25544 | Year 3 holiday 10 setting | uint16_t | R/W | 3
| 0x63C9 | 0x63CB | 25545 | 25547 | Year 3 holiday 11 setting | uint16_t | R/W | 3
| 0x63CC | 0x63CE | 25548 | 25550 | Year 3 holiday 12 setting | uint16_t | R/W | 3
| 0x63CF | 0x63D1 | 25551 | 25553 | Year 3 holiday 13 setting | uint16_t | R/W | 3
| 0x63D2 | 0x63D4 | 25554 | 25556 | Year 3 holiday 14 setting | uint16_t | R/W | 3
| 0x63D5 | 0x63D7 | 25557 | 25559 | Year 3 holiday 15 setting | uint16_t | R/W | 3
| 0x63D8 | 0x63DA | 25560 | 25562 | Year 3 holiday 16 setting | uint16_t | R/W | 3
| 0x63DB | 0x63DD | 25563 | 25565 | Year 3 holiday 17 setting | uint16_t | R/W | 3
| 0x63DE | 0x63E0 | 25566 | 25568 | Year 3 holiday 18 setting | uint16_t | R/W | 3
| 0x63E1 | 0x63E3 | 25569 | 25571 | Year 3 holiday 19 setting | uint16_t | R/W | 3
| 0x63E4 | 0x63E6 | 25572 | 25574 | Year 3 holiday 20 setting | uint16_t | R/W | 3
| 0x63E7 | 0x63E9 | 25575 | 25577 | Year 3 holiday 21 setting | uint16_t | R/W | 3
| 0x63EA | 0x63EC | 25578 | 25580 | Year 3 holiday 22 setting | uint16_t | R/W | 3
| 0x63ED | 0x63EF | 25581 | 25583 | Year 3 holiday 23 setting | uint16_t | R/W | 3
| 0x63F0 | 0x63F2 | 25584 | 25586 | Year 3 holiday 24 setting | uint16_t | R/W | 3
| 0x63F3 | 0x63F5 | 25587 | 25589 | Year 3 holiday 25 setting | uint16_t | R/W | 3
| 0x63F6 | 0x63F8 | 25590 | 25592 | Year 3 holiday 26 setting | uint16_t | R/W | 3
| 0x63F9 | 0x63FB | 25593 | 25595 | Year 3 holiday 27 setting | uint16_t | R/W | 3
| 0x63FC | 0x63FE | 25596 | 25598 | Year 3 holiday 28 setting | uint16_t | R/W | 3
| 0x63FF | 0x6401 | 25599 | 25601 | Year 3 holiday 29 setting | uint16_t | R/W | 3
| 0x6402 | 0x6404 | 25602 | 25604 | Year 3 holiday 30 setting | uint16_t | R/W | 3
| 0x6405 | 0x6405 | 25605 | 25605 | Year 3 Setting Year | uint16_t | R/W | 1
| 0x6406 | 0x6406 | 25606 | 25606 | Year 3 Holiday Number setting | uint16_t | R/W | 1
| 0x6407 | 0x6409 | 25607 | 25609 | Year 4 holiday 1 setting | uint16_t | R/W | 3
| 0x640A | 0x640C | 25610 | 25612 | Year 4 holiday 2 setting | uint16_t | R/W | 3
| 0x640D | 0x640F | 25613 | 25615 | Year 4 holiday 3 setting | uint16_t | R/W | 3
| 0x6410 | 0x6412 | 25616 | 25618 | Year 4 holiday 4 setting | uint16_t | R/W | 3
| 0x6413 | 0x6415 | 25619 | 25621 | Year 4 holiday 5 setting | uint16_t | R/W | 3
| 0x6416 | 0x6418 | 25622 | 25624 | Year 4 holiday 6 setting | uint16_t | R/W | 3
| 0x6419 | 0x641B | 25625 | 25627 | Year 4 holiday 7 setting | uint16_t | R/W | 3
| 0x641C | 0x641E | 25628 | 25630 | Year 4 holiday 8 setting | uint16_t | R/W | 3
| 0x641F | 0x6421 | 25631 | 25633 | Year 4 holiday 9 setting | uint16_t | R/W | 3
| 0x6422 | 0x6424 | 25634 | 25636 | Year 4 holiday 10 setting | uint16_t | R/W | 3
| 0x6425 | 0x6427 | 25637 | 25639 | Year 4 holiday 11 setting | uint16_t | R/W | 3
| 0x6428 | 0x642A | 25640 | 25642 | Year 4 holiday 12 setting | uint16_t | R/W | 3
| 0x642B | 0x642D | 25643 | 25645 | Year 4 holiday 13 setting | uint16_t | R/W | 3
| 0x642E | 0x6430 | 25646 | 25648 | Year 4 holiday 14 setting | uint16_t | R/W | 3
| 0x6431 | 0x6433 | 25649 | 25651 | Year 4 holiday 15 setting | uint16_t | R/W | 3
| 0x6434 | 0x6436 | 25652 | 25654 | Year 4 holiday 16 setting | uint16_t | R/W | 3
| 0x6437 | 0x6439 | 25655 | 25657 | Year 4 holiday 17 setting | uint16_t | R/W | 3
| 0x643A | 0x643C | 25658 | 25660 | Year 4 holiday 18 setting | uint16_t | R/W | 3
| 0x643D | 0x643F | 25661 | 25663 | Year 4 holiday 19 setting | uint16_t | R/W | 3
| 0x6440 | 0x6442 | 25664 | 25666 | Year 4 holiday 20 setting | uint16_t | R/W | 3
| 0x6443 | 0x6445 | 25667 | 25669 | Year 4 holiday 21 setting | uint16_t | R/W | 3
| 0x6446 | 0x6448 | 25670 | 25672 | Year 4 holiday 22 setting | uint16_t | R/W | 3
| 0x6449 | 0x644B | 25673 | 25675 | Year 4 holiday 23 setting | uint16_t | R/W | 3
| 0x644C | 0x644E | 25676 | 25678 | Year 4 holiday 24 setting | uint16_t | R/W | 3
| 0x644F | 0x6451 | 25679 | 25681 | Year 4 holiday 25 setting | uint16_t | R/W | 3
| 0x6452 | 0x6454 | 25682 | 25684 | Year 4 holiday 26 setting | uint16_t | R/W | 3
| 0x6455 | 0x6457 | 25685 | 25687 | Year 4 holiday 27 setting | uint16_t | R/W | 3
| 0x6458 | 0x645A | 25688 | 25690 | Year 4 holiday 28 setting | uint16_t | R/W | 3
| 0x645B | 0x645D | 25691 | 25693 | Year 4 holiday 29 setting | uint16_t | R/W | 3
| 0x645E | 0x6460 | 25694 | 25696 | Year 4 holiday 30 setting | uint16_t | R/W | 3
| 0x6461 | 0x6461 | 25697 | 25697 | Year 4 Setting Year | uint16_t | R/W | 1
| 0x6462 | 0x6462 | 25698 | 25698 | Year 4 Holiday Number setting | uint16_t | R/W | 1
| 0x6463 | 0x6465 | 25699 | 25701 | Year 5 holiday 1 setting | uint16_t | R/W | 3
| 0x6466 | 0x6468 | 25702 | 25704 | Year 5 holiday 2 setting | uint16_t | R/W | 3
| 0x6469 | 0x646B | 25705 | 25707 | Year 5 holiday 3 setting | uint16_t | R/W | 3
| 0x646C | 0x646E | 25708 | 25710 | Year 5 holiday 4 setting | uint16_t | R/W | 3
| 0x646F | 0x6471 | 25711 | 25713 | Year 5 holiday 5 setting | uint16_t | R/W | 3
| 0x6472 | 0x6474 | 25714 | 25716 | Year 5 holiday 6 setting | uint16_t | R/W | 3
| 0x6475 | 0x6477 | 25717 | 25719 | Year 5 holiday 7 setting | uint16_t | R/W | 3
| 0x6478 | 0x647A | 25720 | 25722 | Year 5 holiday 8 setting | uint16_t | R/W | 3
| 0x647B | 0x647D | 25723 | 25725 | Year 5 holiday 9 setting | uint16_t | R/W | 3
| 0x647E | 0x6480 | 25726 | 25728 | Year 5 holiday 10 setting | uint16_t | R/W | 3
| 0x6481 | 0x6483 | 25729 | 25731 | Year 5 holiday 11 setting | uint16_t | R/W | 3
| 0x6484 | 0x6486 | 25732 | 25734 | Year 5 holiday 12 setting | uint16_t | R/W | 3
| 0x6487 | 0x6489 | 25735 | 25737 | Year 5 holiday 13 setting | uint16_t | R/W | 3
| 0x648A | 0x648C | 25738 | 25740 | Year 5 holiday 14 setting | uint16_t | R/W | 3
| 0x648D | 0x648F | 25741 | 25743 | Year 5 holiday 15 setting | uint16_t | R/W | 3
| 0x6490 | 0x6492 | 25744 | 25746 | Year 5 holiday 16 setting | uint16_t | R/W | 3
| 0x6493 | 0x6495 | 25747 | 25749 | Year 5 holiday 17 setting | uint16_t | R/W | 3
| 0x6496 | 0x6498 | 25750 | 25752 | Year 5 holiday 18 setting | uint16_t | R/W | 3
| 0x6499 | 0x649B | 25753 | 25755 | Year 5 holiday 19 setting | uint16_t | R/W | 3
| 0x649C | 0x649E | 25756 | 25758 | Year 5 holiday 20 setting | uint16_t | R/W | 3
| 0x649F | 0x64A1 | 25759 | 25761 | Year 5 holiday 21 setting | uint16_t | R/W | 3
| 0x64A2 | 0x64A4 | 25762 | 25764 | Year 5 holiday 22 setting | uint16_t | R/W | 3
| 0x64A5 | 0x64A7 | 25765 | 25767 | Year 5 holiday 23 setting | uint16_t | R/W | 3
| 0x64A8 | 0x64AA | 25768 | 25770 | Year 5 holiday 24 setting | uint16_t | R/W | 3
| 0x64AB | 0x64AD | 25771 | 25773 | Year 5 holiday 25 setting | uint16_t | R/W | 3
| 0x64AE | 0x64B0 | 25774 | 25776 | Year 5 holiday 26 setting | uint16_t | R/W | 3
| 0x64B1 | 0x64B3 | 25777 | 25779 | Year 5 holiday 27 setting | uint16_t | R/W | 3
| 0x64B4 | 0x64B6 | 25780 | 25782 | Year 5 holiday 28 setting | uint16_t | R/W | 3
| 0x64B7 | 0x64B9 | 25783 | 25785 | Year 5 holiday 29 setting | uint16_t | R/W | 3
| 0x64BA | 0x64BC | 25786 | 25788 | Year 5 holiday 30 setting | uint16_t | R/W | 3
| 0x64BD | 0x64BD | 25789 | 25789 | Year 5 Setting Year | uint16_t | R/W | 1
| 0x64BE | 0x64BE | 25790 | 25790 | Year 5 Holiday Number setting | uint16_t | R/W | 1
| 0x64BF | 0x64C1 | 25791 | 25793 | Year 6 holiday 1 setting | uint16_t | R/W | 3
| 0x64C2 | 0x64C4 | 25794 | 25796 | Year 6 holiday 2 setting | uint16_t | R/W | 3
| 0x64C5 | 0x64C7 | 25797 | 25799 | Year 6 holiday 3 setting | uint16_t | R/W | 3
| 0x64C8 | 0x64CA | 25800 | 25802 | Year 6 holiday 4 setting | uint16_t | R/W | 3
| 0x64CB | 0x64CD | 25803 | 25805 | Year 6 holiday 5 setting | uint16_t | R/W | 3
| 0x64CE | 0x64D0 | 25806 | 25808 | Year 6 holiday 6 setting | uint16_t | R/W | 3
| 0x64D1 | 0x64D3 | 25809 | 25811 | Year 6 holiday 7 setting | uint16_t | R/W | 3
| 0x64D4 | 0x64D6 | 25812 | 25814 | Year 6 holiday 8 setting | uint16_t | R/W | 3
| 0x64D7 | 0x64D9 | 25815 | 25817 | Year 6 holiday 9 setting | uint16_t | R/W | 3
| 0x64DA | 0x64DC | 25818 | 25820 | Year 6 holiday 10 setting | uint16_t | R/W | 3
| 0x64DD | 0x64DF | 25821 | 25823 | Year 6 holiday 11 setting | uint16_t | R/W | 3
| 0x64E0 | 0x64E2 | 25824 | 25826 | Year 6 holiday 12 setting | uint16_t | R/W | 3
| 0x64E3 | 0x64E5 | 25827 | 25829 | Year 6 holiday 13 setting | uint16_t | R/W | 3
| 0x64E6 | 0x64E8 | 25830 | 25832 | Year 6 holiday 14 setting | uint16_t | R/W | 3
| 0x64E9 | 0x64EB | 25833 | 25835 | Year 6 holiday 15 setting | uint16_t | R/W | 3
| 0x64EC | 0x64EE | 25836 | 25838 | Year 6 holiday 16 setting | uint16_t | R/W | 3
| 0x64EF | 0x64F1 | 25839 | 25841 | Year 6 holiday 17 setting | uint16_t | R/W | 3
| 0x64F2 | 0x64F4 | 25842 | 25844 | Year 6 holiday 18 setting | uint16_t | R/W | 3
| 0x64F5 | 0x64F7 | 25845 | 25847 | Year 6 holiday 19 setting | uint16_t | R/W | 3
| 0x64F8 | 0x64FA | 25848 | 25850 | Year 6 holiday 20 setting | uint16_t | R/W | 3
| 0x64FB | 0x64FD | 25851 | 25853 | Year 6 holiday 21 setting | uint16_t | R/W | 3
| 0x64FE | 0x6500 | 25854 | 25856 | Year 6 holiday 22 setting | uint16_t | R/W | 3
| 0x6501 | 0x6503 | 25857 | 25859 | Year 6 holiday 23 setting | uint16_t | R/W | 3
| 0x6504 | 0x6506 | 25860 | 25862 | Year 6 holiday 24 setting | uint16_t | R/W | 3
| 0x6507 | 0x6509 | 25863 | 25865 | Year 6 holiday 25 setting | uint16_t | R/W | 3
| 0x650A | 0x650C | 25866 | 25868 | Year 6 holiday 26 setting | uint16_t | R/W | 3
| 0x650D | 0x650F | 25869 | 25871 | Year 6 holiday 27 setting | uint16_t | R/W | 3
| 0x6510 | 0x6512 | 25872 | 25874 | Year 6 holiday 28 setting | uint16_t | R/W | 3
| 0x6513 | 0x6515 | 25875 | 25877 | Year 6 holiday 29 setting | uint16_t | R/W | 3
| 0x6516 | 0x6518 | 25878 | 25880 | Year 6 holiday 30 setting | uint16_t | R/W | 3
| 0x6519 | 0x6519 | 25881 | 25881 | Year 6 setting Year | uint16_t | R/W | 1
| 0x651A | 0x651A | 25882 | 25882 | Year 6 Number of holidays | uint16_t | R/W | 1
| 0x651B | 0x651D | 25883 | 25885 | Year 7 holiday 1 setting | uint16_t | R/W | 3
| 0x651E | 0x6520 | 25886 | 25888 | Year 7 holiday 2 setting | uint16_t | R/W | 3
| 0x6521 | 0x6523 | 25889 | 25891 | Year 7 holiday 3 setting | uint16_t | R/W | 3
| 0x6524 | 0x6526 | 25892 | 25894 | Year 7 holiday 4 setting | uint16_t | R/W | 3
| 0x6527 | 0x6529 | 25895 | 25897 | Year 7 holiday 5 setting | uint16_t | R/W | 3
| 0x652A | 0x652C | 25898 | 25900 | Year 7 holiday 6 setting | uint16_t | R/W | 3
| 0x652D | 0x652F | 25901 | 25903 | Year 7 holiday 7 setting | uint16_t | R/W | 3
| 0x6530 | 0x6532 | 25904 | 25906 | Year 7 holiday 8 setting | uint16_t | R/W | 3
| 0x6533 | 0x6535 | 25907 | 25909 | Year 7 holiday 9 setting | uint16_t | R/W | 3
| 0x6536 | 0x6538 | 25910 | 25912 | Year 7 holiday 10 setting | uint16_t | R/W | 3
| 0x6539 | 0x653B | 25913 | 25915 | Year 7 holiday 11 setting | uint16_t | R/W | 3
| 0x653C | 0x653E | 25916 | 25918 | Year 7 holiday 12 setting | uint16_t | R/W | 3
| 0x653F | 0x6541 | 25919 | 25921 | Year 7 holiday 13 setting | uint16_t | R/W | 3
| 0x6542 | 0x6544 | 25922 | 25924 | Year 7 holiday 14 setting | uint16_t | R/W | 3
| 0x6545 | 0x6547 | 25925 | 25927 | Year 7 holiday 15 setting | uint16_t | R/W | 3
| 0x6548 | 0x654A | 25928 | 25930 | Year 7 holiday 16 setting | uint16_t | R/W | 3
| 0x654B | 0x654D | 25931 | 25933 | Year 7 holiday 17 setting | uint16_t | R/W | 3
| 0x654E | 0x6550 | 25934 | 25936 | Year 7 holiday 18 setting | uint16_t | R/W | 3
| 0x6551 | 0x6553 | 25937 | 25939 | Year 7 holiday 19 setting | uint16_t | R/W | 3
| 0x6554 | 0x6556 | 25940 | 25942 | Year 7 holiday 20 setting | uint16_t | R/W | 3
| 0x6557 | 0x6559 | 25943 | 25945 | Year 7 holiday 21 setting | uint16_t | R/W | 3
| 0x655A | 0x655C | 25946 | 25948 | Year 7 holiday 22 setting | uint16_t | R/W | 3
| 0x655D | 0x655F | 25949 | 25951 | Year 7 holiday 23 setting | uint16_t | R/W | 3
| 0x6560 | 0x6562 | 25952 | 25954 | Year 7 holiday 24 setting | uint16_t | R/W | 3
| 0x6563 | 0x6565 | 25955 | 25957 | Year 7 holiday 25 setting | uint16_t | R/W | 3
| 0x6566 | 0x6568 | 25958 | 25960 | Year 7 holiday 26 setting | uint16_t | R/W | 3
| 0x6569 | 0x656B | 25961 | 25963 | Year 7 holiday 27 setting | uint16_t | R/W | 3
| 0x656C | 0x656E | 25964 | 25966 | Year 7 holiday 28 setting | uint16_t | R/W | 3
| 0x656F | 0x6571 | 25967 | 25969 | Year 7 holiday 29 setting | uint16_t | R/W | 3
| 0x6572 | 0x6574 | 25970 | 25972 | Year 7 holiday 30 setting | uint16_t | R/W | 3
| 0x6575 | 0x6575 | 25973 | 25973 | Year 7 Setting Year | uint16_t | R/W | 1
| 0x6576 | 0x6576 | 25974 | 25974 | Year 7 Holiday Number setting | uint16_t | R/W | 1
| 0x6577 | 0x6579 | 25975 | 25977 | Year 8 holiday 1 setting | uint16_t | R/W | 3
| 0x657A | 0x657C | 25978 | 25980 | Year 8 holiday 2 setting | uint16_t | R/W | 3
| 0x657D | 0x657F | 25981 | 25983 | Year 8 holiday 3 setting | uint16_t | R/W | 3
| 0x6580 | 0x6582 | 25984 | 25986 | Year 8 holiday 4 setting | uint16_t | R/W | 3
| 0x6583 | 0x6585 | 25987 | 25989 | Year 8 holiday 5 setting | uint16_t | R/W | 3
| 0x6586 | 0x6588 | 25990 | 25992 | Year 8 holiday 6 setting | uint16_t | R/W | 3
| 0x6589 | 0x658B | 25993 | 25995 | Year 8 holiday 7 setting | uint16_t | R/W | 3
| 0x658C | 0x658E | 25996 | 25998 | Year 8 holiday 8 setting | uint16_t | R/W | 3
| 0x658F | 0x6591 | 25999 | 26001 | Year 8 holiday 9 setting | uint16_t | R/W | 3
| 0x6592 | 0x6594 | 26002 | 26004 | Year 8 holiday 10 setting | uint16_t | R/W | 3
| 0x6595 | 0x6597 | 26005 | 26007 | Year 8 holiday 11 setting | uint16_t | R/W | 3
| 0x6598 | 0x659A | 26008 | 26010 | Year 8 holiday 12 setting | uint16_t | R/W | 3
| 0x659B | 0x659D | 26011 | 26013 | Year 8 holiday 13 setting | uint16_t | R/W | 3
| 0x659E | 0x65A0 | 26014 | 26016 | Year 8 holiday 14 setting | uint16_t | R/W | 3
| 0x65A1 | 0x65A3 | 26017 | 26019 | Year 8 holiday 15 setting | uint16_t | R/W | 3
| 0x65A4 | 0x65A6 | 26020 | 26022 | Year 8 holiday 16 setting | uint16_t | R/W | 3
| 0x65A7 | 0x65A9 | 26023 | 26025 | Year 8 holiday 17 setting | uint16_t | R/W | 3
| 0x65AA | 0x65AC | 26026 | 26028 | Year 8 holiday 18 setting | uint16_t | R/W | 3
| 0x65AD | 0x65AF | 26029 | 26031 | Year 8 holiday 19 setting | uint16_t | R/W | 3
| 0x65B0 | 0x65B2 | 26032 | 26034 | Year 8 holiday 20 setting | uint16_t | R/W | 3
| 0x65B3 | 0x65B5 | 26035 | 26037 | Year 8 holiday 21 setting | uint16_t | R/W | 3
| 0x65B6 | 0x65B8 | 26038 | 26040 | Year 8 holiday 22 setting | uint16_t | R/W | 3
| 0x65B9 | 0x65BB | 26041 | 26043 | Year 8 holiday 23 setting | uint16_t | R/W | 3
| 0x65BC | 0x65BE | 26044 | 26046 | Year 8 holiday 24 setting | uint16_t | R/W | 3
| 0x65BF | 0x65C1 | 26047 | 26049 | Year 8 holiday 25 setting | uint16_t | R/W | 3
| 0x65C2 | 0x65C4 | 26050 | 26052 | Year 8 holiday 26 setting | uint16_t | R/W | 3
| 0x65C5 | 0x65C7 | 26053 | 26055 | Year 8 holiday 27 setting | uint16_t | R/W | 3
| 0x65C8 | 0x65CA | 26056 | 26058 | Year 8 holiday 28 setting | uint16_t | R/W | 3
| 0x65CB | 0x65CD | 26059 | 26061 | Year 8 holiday 29 setting | uint16_t | R/W | 3
| 0x65CE | 0x65D0 | 26062 | 26064 | Year 8 holiday 30 setting | uint16_t | R/W | 3
| 0x65D1 | 0x65D1 | 26065 | 26065 | Year 8 Setting Year | uint16_t | R/W | 1
| 0x65D2 | 0x65D2 | 26066 | 26066 | Year 8 Holiday Number setting | uint16_t | R/W | 1
| 0x65D3 | 0x65D5 | 26067 | 26069 | Year 9 holiday 1 setting | uint16_t | R/W | 3
| 0x65D6 | 0x65D8 | 26070 | 26072 | Year 9 holiday 2 setting | uint16_t | R/W | 3
| 0x65D9 | 0x65DB | 26073 | 26075 | Year 9 holiday 3 setting | uint16_t | R/W | 3
| 0x65DC | 0x65DE | 26076 | 26078 | Year 9 holiday 4 setting | uint16_t | R/W | 3
| 0x65DF | 0x65E1 | 26079 | 26081 | Year 9 holiday 5 setting | uint16_t | R/W | 3
| 0x65E2 | 0x65E4 | 26082 | 26084 | Year 9 holiday 6 setting | uint16_t | R/W | 3
| 0x65E5 | 0x65E7 | 26085 | 26087 | Year 9 holiday 7 setting | uint16_t | R/W | 3
| 0x65E8 | 0x65EA | 26088 | 26090 | Year 9 holiday 8 setting | uint16_t | R/W | 3
| 0x65EB | 0x65ED | 26091 | 26093 | Year 9 holiday 9 setting | uint16_t | R/W | 3
| 0x65EE | 0x65F0 | 26094 | 26096 | Year 9 holiday 10 setting | uint16_t | R/W | 3
| 0x65F1 | 0x65F3 | 26097 | 26099 | Year 9 holiday 11 setting | uint16_t | R/W | 3
| 0x65F4 | 0x65F6 | 26100 | 26102 | Year 9 holiday 12 setting | uint16_t | R/W | 3
| 0x65F7 | 0x65F9 | 26103 | 26105 | Year 9 holiday 13 setting | uint16_t | R/W | 3
| 0x65FA | 0x65FC | 26106 | 26108 | Year 9 holiday 14 setting | uint16_t | R/W | 3
| 0x65FD | 0x65FF | 26109 | 26111 | Year 9 holiday 15 setting | uint16_t | R/W | 3
| 0x6600 | 0x6602 | 26112 | 26114 | Year 9 holiday 16 setting | uint16_t | R/W | 3
| 0x6603 | 0x6605 | 26115 | 26117 | Year 9 holiday 17 setting | uint16_t | R/W | 3
| 0x6606 | 0x6608 | 26118 | 26120 | Year 9 holiday 18 setting | uint16_t | R/W | 3
| 0x6609 | 0x660B | 26121 | 26123 | Year 9 holiday 19 setting | uint16_t | R/W | 3
| 0x660C | 0x660E | 26124 | 26126 | Year 9 holiday 20 setting | uint16_t | R/W | 3
| 0x660F | 0x6611 | 26127 | 26129 | Year 9 holiday 21 setting | uint16_t | R/W | 3
| 0x6612 | 0x6614 | 26130 | 26132 | Year 9 holiday 22 setting | uint16_t | R/W | 3
| 0x6615 | 0x6617 | 26133 | 26135 | Year 9 holiday 23 setting | uint16_t | R/W | 3
| 0x6618 | 0x661A | 26136 | 26138 | Year 9 holiday 24 setting | uint16_t | R/W | 3
| 0x661B | 0x661D | 26139 | 26141 | Year 9 holiday 25 setting | uint16_t | R/W | 3
| 0x661E | 0x6620 | 26142 | 26144 | Year 9 holiday 26 setting | uint16_t | R/W | 3
| 0x6621 | 0x6623 | 26145 | 26147 | Year 9 holiday 27 setting | uint16_t | R/W | 3
| 0x6624 | 0x6626 | 26148 | 26150 | Year 9 holiday 28 setting | uint16_t | R/W | 3
| 0x6627 | 0x6629 | 26151 | 26153 | Year 9 holiday 29 setting | uint16_t | R/W | 3
| 0x662A | 0x662C | 26154 | 26156 | Year 9 holiday 30 setting | uint16_t | R/W | 3
| 0x662D | 0x662D | 26157 | 26157 | Year 9 Setting Year | uint16_t | R/W | 1
| 0x662E | 0x662E | 26158 | 26158 | Year 9 Holiday Number setting | uint16_t | R/W | 1
| 0x662F | 0x6631 | 26159 | 26161 | Year 10 holiday 1 setting | uint16_t | R/W | 3
| 0x6632 | 0x6634 | 26162 | 26164 | Year 10 holiday 2 setting | uint16_t | R/W | 3
| 0x6635 | 0x6637 | 26165 | 26167 | Year 10 holiday 3 setting | uint16_t | R/W | 3
| 0x6638 | 0x663A | 26168 | 26170 | Year 10 holiday 4 setting | uint16_t | R/W | 3
| 0x663B | 0x663D | 26171 | 26173 | Year 10 holiday 5 setting | uint16_t | R/W | 3
| 0x663E | 0x6640 | 26174 | 26176 | Year 10 holiday 6 setting | uint16_t | R/W | 3
| 0x6641 | 0x6643 | 26177 | 26179 | Year 10 holiday 7 setting | uint16_t | R/W | 3
| 0x6644 | 0x6646 | 26180 | 26182 | Year 10 holiday 8 setting | uint16_t | R/W | 3
| 0x6647 | 0x6649 | 26183 | 26185 | Year 10 holiday 9 setting | uint16_t | R/W | 3
| 0x664A | 0x664C | 26186 | 26188 | Year 10 holiday 10 setting | uint16_t | R/W | 3
| 0x664D | 0x664F | 26189 | 26191 | Year 10 holiday 11 setting | uint16_t | R/W | 3
| 0x6650 | 0x6652 | 26192 | 26194 | Year 10 holiday 12 setting | uint16_t | R/W | 3
| 0x6653 | 0x6655 | 26195 | 26197 | Year 10 holiday 13 setting | uint16_t | R/W | 3
| 0x6656 | 0x6658 | 26198 | 26200 | Year 10 holiday 14 setting | uint16_t | R/W | 3
| 0x6659 | 0x665B | 26201 | 26203 | Year 10 holiday 15 setting | uint16_t | R/W | 3
| 0x665C | 0x665E | 26204 | 26206 | Year 10 holiday 16 setting | uint16_t | R/W | 3
| 0x665F | 0x6661 | 26207 | 26209 | Year 10 holiday 17 setting | uint16_t | R/W | 3
| 0x6662 | 0x6664 | 26210 | 26212 | Year 10 holiday 18 setting | uint16_t | R/W | 3
| 0x6665 | 0x6667 | 26213 | 26215 | Year 10 holiday 19 setting | uint16_t | R/W | 3
| 0x6668 | 0x666A | 26216 | 26218 | Year 10 holiday 20 setting | uint16_t | R/W | 3
| 0x666B | 0x666D | 26219 | 26221 | Year 10 holiday 21 setting | uint16_t | R/W | 3
| 0x666E | 0x6670 | 26222 | 26224 | Year 10 holiday 22 setting | uint16_t | R/W | 3
| 0x6671 | 0x6673 | 26225 | 26227 | Year 10 holiday 23 setting | uint16_t | R/W | 3
| 0x6674 | 0x6676 | 26228 | 26230 | Year 10 holiday 24 setting | uint16_t | R/W | 3
| 0x6677 | 0x6679 | 26231 | 26233 | Year 10 holiday 25 setting | uint16_t | R/W | 3
| 0x667A | 0x667C | 26234 | 26236 | Year 10 holiday 26 setting | uint16_t | R/W | 3
| 0x667D | 0x667F | 26237 | 26239 | Year 10 holiday 27 setting | uint16_t | R/W | 3
| 0x6680 | 0x6682 | 26240 | 26242 | Year 10 holiday 28 setting | uint16_t | R/W | 3
| 0x6683 | 0x6685 | 26243 | 26245 | Year 10 holiday 29 setting | uint16_t | R/W | 3
| 0x6686 | 0x6688 | 26246 | 26248 | Year 10 holiday 30 setting | uint16_t | R/W | 3
| 0x6689 | 0x6689 | 26249 | 26249 | Year 10 Setting Year | uint16_t | R/W | 1 | 2000-2099
| 0x668A | 0x668A | 26250 | 26250 | Year 10 Holiday Number setting | uint16_t | R/W | 1 | 0-30
Special weekday schedule settings : 03H Read, 10H Write
| 0x668B | 0x668B | 26251 | 26251 | Enable special weekday schedule | uint16_t | R/W | 1 | 0: Disable 1: Enable If 0, Weekend schedule uses registers 0x7804H & 0x7805H
| 0x668C | 0x668C | 26252 | 26252 | Season 1 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x668D | 0x668D | 26253 | 26253 | Season 1 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x668E | 0x668E | 26254 | 26254 | Season 1 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x668F | 0x668F | 26255 | 26255 | Season 1 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x6690 | 0x6690 | 26256 | 26256 | Season 1 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x6691 | 0x6691 | 26257 | 26257 | Season 1 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x6692 | 0x6692 | 26258 | 26258 | Season 1 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x6693 | 0x6693 | 26259 | 26259 | Season 1 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x6694 | 0x6694 | 26260 | 26260 | Season 2 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x6695 | 0x6695 | 26261 | 26261 | Season 2 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x6696 | 0x6696 | 26262 | 26262 | Season 2 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x6697 | 0x6697 | 26263 | 26263 | Season 2 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x6698 | 0x6698 | 26264 | 26264 | Season 2 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x6699 | 0x6699 | 26265 | 26265 | Season 2 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x669A | 0x669A | 26266 | 26266 | Season 2 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x669B | 0x669B | 26267 | 26267 | Season 2 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x669C | 0x669C | 26268 | 26268 | Season 3 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x669D | 0x669D | 26269 | 26269 | Season 3 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x669E | 0x669E | 26270 | 26270 | Season 3 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x669F | 0x669F | 26271 | 26271 | Season 3 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66A0 | 0x66A0 | 26272 | 26272 | Season 3 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66A1 | 0x66A1 | 26273 | 26273 | Season 3 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66A2 | 0x66A2 | 26274 | 26274 | Season 3 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66A3 | 0x66A3 | 26275 | 26275 | Season 3 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66A4 | 0x66A4 | 26276 | 26276 | Season 4 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x66A5 | 0x66A5 | 26277 | 26277 | Season 4 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66A6 | 0x66A6 | 26278 | 26278 | Season 4 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66A7 | 0x66A7 | 26279 | 26279 | Season 4 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66A8 | 0x66A8 | 26280 | 26280 | Season 4 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66A9 | 0x66A9 | 26281 | 26281 | Season 4 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66AA | 0x66AA | 26282 | 26282 | Season 4 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66AB | 0x66AB | 26283 | 26283 | Season 4 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66AC | 0x66AC | 26284 | 26284 | Season 5 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x66AD | 0x66AD | 26285 | 26285 | Season 5 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66AE | 0x66AE | 26286 | 26286 | Season 5 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66AF | 0x66AF | 26287 | 26287 | Season 5 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66B0 | 0x66B0 | 26288 | 26288 | Season 5 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66B1 | 0x66B1 | 26289 | 26289 | Season 5 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66B2 | 0x66B2 | 26290 | 26290 | Season 5 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66B3 | 0x66B3 | 26291 | 26291 | Season 5 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66B4 | 0x66B4 | 26292 | 26292 | Season 6 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x66B5 | 0x66B5 | 26293 | 26293 | Season 6 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66B6 | 0x66B6 | 26294 | 26294 | Season 6 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66B7 | 0x66B7 | 26295 | 26295 | Season 6 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66B8 | 0x66B8 | 26296 | 26296 | Season 6 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66B9 | 0x66B9 | 26297 | 26297 | Season 6 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66BA | 0x66BA | 26298 | 26298 | Season 6 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66BB | 0x66BB | 26299 | 26299 | Season 6 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66BC | 0x66BC | 26300 | 26300 | Season 7 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x66BD | 0x66BD | 26301 | 26301 | Season 7 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66BE | 0x66BE | 26302 | 26302 | Season 7 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66BF | 0x66BF | 26303 | 26303 | Season 7 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66C0 | 0x66C0 | 26304 | 26304 | Season 7 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66C1 | 0x66C1 | 26305 | 26305 | Season 7 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66C2 | 0x66C2 | 26306 | 26306 | Season 7 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66C3 | 0x66C3 | 26307 | 26307 | Season 7 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66C4 | 0x66C4 | 26308 | 26308 | Season 8 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x66C5 | 0x66C5 | 26309 | 26309 | Season 8 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66C6 | 0x66C6 | 26310 | 26310 | Season 8 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66C7 | 0x66C7 | 26311 | 26311 | Season 8 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66C8 | 0x66C8 | 26312 | 26312 | Season 8 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66C9 | 0x66C9 | 26313 | 26313 | Season 8 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66CA | 0x66CA | 26314 | 26314 | Season 8 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66CB | 0x66CB | 26315 | 26315 | Season 8 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66CC | 0x66CC | 26316 | 26316 | Season 9 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x66CD | 0x66CD | 26317 | 26317 | Season 9 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66CE | 0x66CE | 26318 | 26318 | Season 9 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66CF | 0x66CF | 26319 | 26319 | Season 9 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66D0 | 0x66D0 | 26320 | 26320 | Season 9 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66D1 | 0x66D1 | 26321 | 26321 | Season 9 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66D2 | 0x66D2 | 26322 | 26322 | Season 9 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66D3 | 0x66D3 | 26323 | 26323 | Season 9 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66D4 | 0x66D4 | 26324 | 26324 | Season 10 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x66D5 | 0x66D5 | 26325 | 26325 | Season 10 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66D6 | 0x66D6 | 26326 | 26326 | Season 10 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66D7 | 0x66D7 | 26327 | 26327 | Season 10 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66D8 | 0x66D8 | 26328 | 26328 | Season 10 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66D9 | 0x66D9 | 26329 | 26329 | Season 10 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66DA | 0x66DA | 26330 | 26330 | Season 10 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66DB | 0x66DB | 26331 | 26331 | Season 10 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66DC | 0x66DC | 26332 | 26332 | Season 11 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x66DD | 0x66DD | 26333 | 26333 | Season 11 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66DE | 0x66DE | 26334 | 26334 | Season 11 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66DF | 0x66DF | 26335 | 26335 | Season 11 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66E0 | 0x66E0 | 26336 | 26336 | Season 11 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66E1 | 0x66E1 | 26337 | 26337 | Season 11 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66E2 | 0x66E2 | 26338 | 26338 | Season 11 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66E3 | 0x66E3 | 26339 | 26339 | Season 11 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66E4 | 0x66E4 | 26340 | 26340 | Season 12 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x66E5 | 0x66E5 | 26341 | 26341 | Season 12 Sunday schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66E6 | 0x66E6 | 26342 | 26342 | Season 12 Monday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66E7 | 0x66E7 | 26343 | 26343 | Season 12 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66E8 | 0x66E8 | 26344 | 26344 | Season 12 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66E9 | 0x66E9 | 26345 | 26345 | Season 12 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66EA | 0x66EA | 26346 | 26346 | Season 12 Friday Schedule ID | uint16_t | R/W | 1 | 0~14
| 0x66EB | 0x66EB | 26347 | 26347 | Season 12 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14
1017

## TOU Reading
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Current Month Accumulative TOU Energy: 03H Read
| 0x6700 | 0x6701 | 26368 | 26369 | sharp - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6702 | 0x6703 | 26370 | 26371 | sharp - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6704 | 0x6705 | 26372 | 26373 | sharp - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6706 | 0x6707 | 26374 | 26375 | sharp - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6708 | 0x6709 | 26376 | 26377 | sharp - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x670A | 0x670B | 26378 | 26379 | peak - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x670C | 0x670D | 26380 | 26381 | peak - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x670E | 0x670F | 26382 | 26383 | peak - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6710 | 0x6711 | 26384 | 26385 | peak - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6712 | 0x6713 | 26386 | 26387 | peak - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x6714 | 0x6715 | 26388 | 26389 | valley - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6716 | 0x6717 | 26390 | 26391 | valley - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6718 | 0x6719 | 26392 | 26393 | valley - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x671A | 0x671B | 26394 | 26395 | valley - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x671C | 0x671D | 26396 | 26397 | valley - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x671E | 0x671F | 26398 | 26399 | normal - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6720 | 0x6721 | 26400 | 26401 | normal - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6722 | 0x6723 | 26402 | 26403 | normal - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6724 | 0x6725 | 26404 | 26405 | normal - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6726 | 0x6727 | 26406 | 26407 | normal - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x6728 | 0x6729 | 26408 | 26409 | total - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x672A | 0x672B | 26410 | 26411 | total - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x672C | 0x672D | 26412 | 26413 | total - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x672E | 0x672F | 26414 | 26415 | total - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6730 | 0x6731 | 26416 | 26417 | total - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
50
Previous Month Accumulative TOU Energy: 03H Read | 0x6732 | 0x6733 | 26418 | 26419 | sharp - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6734 | 0x6735 | 26420 | 26421 | sharp - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6736 | 0x6737 | 26422 | 26423 | sharp - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6738 | 0x6739 | 26424 | 26425 | sharp - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x673A | 0x673B | 26426 | 26427 | sharp - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x673C | 0x673D | 26428 | 26429 | peak - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x673E | 0x673F | 26430 | 26431 | peak - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6740 | 0x6741 | 26432 | 26433 | peak - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6742 | 0x6743 | 26434 | 26435 | peak - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6744 | 0x6745 | 26436 | 26437 | peak - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x6746 | 0x6747 | 26438 | 26439 | valley - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6748 | 0x6749 | 26440 | 26441 | valley - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x674A | 0x674B | 26442 | 26443 | valley - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x674C | 0x674D | 26444 | 26445 | valley - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x674E | 0x674F | 26446 | 26447 | valley - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x6750 | 0x6751 | 26448 | 26449 | normal - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6752 | 0x6753 | 26450 | 26451 | normal - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6754 | 0x6755 | 26452 | 26453 | normal - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6756 | 0x6757 | 26454 | 26455 | normal - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6758 | 0x6759 | 26456 | 26457 | normal - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x675A | 0x675B | 26458 | 26459 | total - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x675C | 0x675D | 26460 | 26461 | total - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x675E | 0x675F | 26462 | 26463 | total - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6760 | 0x6761 | 26464 | 26465 | total - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6762 | 0x6763 | 26466 | 26467 | total - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
50
Current Month Incremental TOU Energy: 03H Read | 0x6764 | 0x6765 | 26468 | 26469 | sharp - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6766 | 0x6767 | 26470 | 26471 | sharp - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6768 | 0x6769 | 26472 | 26473 | sharp - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x676A | 0x676B | 26474 | 26475 | sharp - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x676C | 0x676D | 26476 | 26477 | sharp - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x676E | 0x676F | 26478 | 26479 | peak - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6770 | 0x6771 | 26480 | 26481 | peak - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6772 | 0x6773 | 26482 | 26483 | peak - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6774 | 0x6775 | 26484 | 26485 | peak - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6776 | 0x6777 | 26486 | 26487 | peak - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x6778 | 0x6779 | 26488 | 26489 | valley - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x677A | 0x677B | 26490 | 26491 | valley - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x677C | 0x677D | 26492 | 26493 | valley - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x677E | 0x677F | 26494 | 26495 | valley - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6780 | 0x6781 | 26496 | 26497 | valley - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x6782 | 0x6783 | 26498 | 26499 | normal - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6784 | 0x6785 | 26500 | 26501 | normal - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6786 | 0x6787 | 26502 | 26503 | normal - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6788 | 0x6789 | 26504 | 26505 | normal - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x678A | 0x678B | 26506 | 26507 | normal - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x678C | 0x678D | 26508 | 26509 | total - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x678E | 0x678F | 26510 | 26511 | total - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6790 | 0x6791 | 26512 | 26513 | total - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6792 | 0x6793 | 26514 | 26515 | total - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x6794 | 0x6795 | 26516 | 26517 | total - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
50
Previous Month Incremental TOU Energy: 03H Read | 0x6796 | 0x6797 | 26518 | 26519 | sharp - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x6798 | 0x6799 | 26520 | 26521 | sharp - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x679A | 0x679B | 26522 | 26523 | sharp - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x679C | 0x679D | 26524 | 26525 | sharp - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x679E | 0x679F | 26526 | 26527 | sharp - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x67A0 | 0x67A1 | 26528 | 26529 | peak - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x67A2 | 0x67A3 | 26530 | 26531 | peak - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x67A4 | 0x67A5 | 26532 | 26533 | peak - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x67A6 | 0x67A7 | 26534 | 26535 | peak - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x67A8 | 0x67A9 | 26536 | 26537 | peak - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x67AA | 0x67AB | 26538 | 26539 | valley - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x67AC | 0x67AD | 26540 | 26541 | valley - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x67AE | 0x67AF | 26542 | 26543 | valley - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x67B0 | 0x67B1 | 26544 | 26545 | valley - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x67B2 | 0x67B3 | 26546 | 26547 | valley - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x67B4 | 0x67B5 | 26548 | 26549 | normal - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x67B6 | 0x67B7 | 26550 | 26551 | normal - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x67B8 | 0x67B9 | 26552 | 26553 | normal - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x67BA | 0x67BB | 26554 | 26555 | normal - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x67BC | 0x67BD | 26556 | 26557 | normal - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
| 0x67BE | 0x67BF | 26558 | 26559 | total - Ep_Imp Import active energy | uint32_t | R/W | 2 | 0~999999999
| 0x67C0 | 0x67C1 | 26560 | 26561 | total - Ep_Exp Export active energy | uint32_t | R/W | 2 | 0~999999999
| 0x67C2 | 0x67C3 | 26562 | 26563 | total - Eq_Imp Import reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x67C4 | 0x67C5 | 26564 | 26565 | total - Eq_Exp Export reactive energy | uint32_t | R/W | 2 | 0~999999999
| 0x67C6 | 0x67C7 | 26566 | 26567 | total - Es Apparent energy | uint32_t | R/W | 2 | 0~999999999
50
Current Month TOU Max Demand
| 0x6800 | 0x6801 | 26624 | 26625 | sharp - max import active power demand | float | R | 2
| 0x6802 | 0x6804 | 26626 | 26628 | sharp - max import active power demand timestamp (year : uint16_t ; month、day : uint16_t ( High byte: month,Low byte: day); hour、min : uint16_t ( High byte: hour,Low byte: minute); ) | timestamp | R | 3
| 0x6805 | 0x6806 | 26629 | 26630 | sharp - max export active power demand | float | R | 2
| 0x6807 | 0x6809 | 26631 | 26633 | sharp - max export active power demand timestamp | timestamp | R | 3
| 0x680A | 0x680B | 26634 | 26635 | sharp - max import reactive power demand | float | R | 2
| 0x680C | 0x680E | 26636 | 26638 | sharp - max import reactive power demand timestamp | timestamp | R | 3
| 0x680F | 0x6810 | 26639 | 26640 | sharp - max export reactive power demand | float | R | 2
| 0x6811 | 0x6813 | 26641 | 26643 | sharp - max export reactive power demand timestamp | timestamp | R | 3
| 0x6814 | 0x6815 | 26644 | 26645 | sharp - max apparent power demand | float | R | 2
| 0x6816 | 0x6818 | 26646 | 26648 | sharp - max apparent power demand timestamp | timestamp | R | 3
| 0x6819 | 0x681A | 26649 | 26650 | sharp - max Ia demand | float | R | 2
| 0x681B | 0x681D | 26651 | 26653 | sharp - max Ia demand timestamp | timestamp | R | 3
| 0x681E | 0x681F | 26654 | 26655 | sharp - max Ib demand | float | R | 2
| 0x6820 | 0x6822 | 26656 | 26658 | sharp - max Ib demand timestamp | timestamp | R | 3
| 0x6823 | 0x6824 | 26659 | 26660 | sharp - max Ic demand | float | R | 2
| 0x6825 | 0x6827 | 26661 | 26663 | sharp - max Ic demand timestamp | timestamp | R | 3
| 0x6828 | 0x6829 | 26664 | 26665 | peak - max import active power demand | float | R | 2
| 0x682A | 0x682C | 26666 | 26668 | peak - max import active power demand timestamp | timestamp | R | 3
| 0x682D | 0x682E | 26669 | 26670 | peak - max export active power demand | float | R | 2
| 0x682F | 0x6831 | 26671 | 26673 | peak - max export active power demand timestamp | timestamp | R | 3
| 0x6832 | 0x6833 | 26674 | 26675 | peak - max import reactive power demand | float | R | 2
| 0x6834 | 0x6836 | 26676 | 26678 | peak - max import reactive power demand timestamp | timestamp | R | 3
| 0x6837 | 0x6838 | 26679 | 26680 | peak - max export reactive power demand | float | R | 2
| 0x6839 | 0x683B | 26681 | 26683 | peak - max export reactive power demand timestamp | timestamp | R | 3
| 0x683C | 0x683D | 26684 | 26685 | peak - max apparent power demand | float | R | 2
| 0x683E | 0x6840 | 26686 | 26688 | peak - max apparent power demand timestamp | timestamp | R | 3
| 0x6841 | 0x6842 | 26689 | 26690 | peak - max Ia demand | float | R | 2
| 0x6843 | 0x6845 | 26691 | 26693 | peak - max Ia demand timestamp | timestamp | R | 3
| 0x6846 | 0x6847 | 26694 | 26695 | peak - max Ib demand | float | R | 2
| 0x6848 | 0x684A | 26696 | 26698 | peak - max Ib demand timestamp | timestamp | R | 3
| 0x684B | 0x684C | 26699 | 26700 | peak - max Ic demand | float | R | 2
| 0x684D | 0x684F | 26701 | 26703 | peak - max Ic demand timestamp | timestamp | R | 3
| 0x6850 | 0x6851 | 26704 | 26705 | valley - max import active power demand | float | R | 2
| 0x6852 | 0x6854 | 26706 | 26708 | valley - max import active power demand timestamp | timestamp | R | 3
| 0x6855 | 0x6856 | 26709 | 26710 | valley - max export active power demand | float | R | 2
| 0x6857 | 0x6859 | 26711 | 26713 | valley - max export active power demand timestamp | timestamp | R | 3
| 0x685A | 0x685B | 26714 | 26715 | valley - max import reactive power demand | float | R | 2
| 0x685C | 0x685E | 26716 | 26718 | valley - max import reactive power demand timestamp | timestamp | R | 3
| 0x685F | 0x6860 | 26719 | 26720 | valley - max export reactive power demand | float | R | 2
| 0x6861 | 0x6863 | 26721 | 26723 | valley - max export reactive power demand timestamp | timestamp | R | 3
| 0x6864 | 0x6865 | 26724 | 26725 | valley - max apparent power demand | float | R | 2
| 0x6866 | 0x6868 | 26726 | 26728 | valley - max apparent power demand timestamp | timestamp | R | 3
| 0x6869 | 0x686A | 26729 | 26730 | valley - max Ia demand | float | R | 2
| 0x686B | 0x686D | 26731 | 26733 | valley - max Ia demand timestamp | timestamp | R | 3
| 0x686E | 0x686F | 26734 | 26735 | valley - max Ib demand | float | R | 2
| 0x6870 | 0x6872 | 26736 | 26738 | valley - max Ib demand timestamp | timestamp | R | 3
| 0x6873 | 0x6874 | 26739 | 26740 | valley - max Ic demand | float | R | 2
| 0x6875 | 0x6877 | 26741 | 26743 | valley - max Ic demand timestamp | timestamp | R | 3
| 0x6878 | 0x6879 | 26744 | 26745 | normal - max import active power demand | float | R | 2
| 0x687A | 0x687C | 26746 | 26748 | normal - max import active power demand timestamp | timestamp | R | 3
| 0x687D | 0x687E | 26749 | 26750 | normal - max export active power demand | float | R | 2
| 0x687F | 0x6881 | 26751 | 26753 | normal - max export active power demand timestamp | timestamp | R | 3
| 0x6882 | 0x6883 | 26754 | 26755 | normal - max import reactive power demand | float | R | 2
| 0x6884 | 0x6886 | 26756 | 26758 | normal - max import reactive power demand timestamp | timestamp | R | 3
| 0x6887 | 0x6888 | 26759 | 26760 | normal - max export reactive power demand | float | R | 2
| 0x6889 | 0x688B | 26761 | 26763 | normal - max export reactive power demand timestamp | timestamp | R | 3
| 0x688C | 0x688D | 26764 | 26765 | normal - max apparent power demand | float | R | 2
| 0x688E | 0x6890 | 26766 | 26768 | normal - max apparent power demand timestamp | timestamp | R | 3
| 0x6891 | 0x6892 | 26769 | 26770 | normal - max Ia demand | float | R | 2
| 0x6893 | 0x6895 | 26771 | 26773 | normal - max Ia demand timestamp | timestamp | R | 3
| 0x6896 | 0x6897 | 26774 | 26775 | normal - max Ib demand | float | R | 2
| 0x6898 | 0x689A | 26776 | 26778 | normal - max Ib demand timestamp | timestamp | R | 3
| 0x689B | 0x689C | 26779 | 26780 | normal - max Ic demand | float | R | 2
| 0x689D | 0x689F | 26781 | 26783 | normal - max Ic demand timestamp | timestamp | R | 3
| 0x68A0 | 0x68A1 | 26784 | 26785 | total - max import active power demand | float | R | 2
| 0x68A2 | 0x68A4 | 26786 | 26788 | total - max import active power demand timestamp | timestamp | R | 3
| 0x68A5 | 0x68A6 | 26789 | 26790 | total - max export active power demand | float | R | 2
| 0x68A7 | 0x68A9 | 26791 | 26793 | total - max export active power demand timestamp | timestamp | R | 3
| 0x68AA | 0x68AB | 26794 | 26795 | total - max import reactive power demand | float | R | 2
| 0x68AC | 0x68AE | 26796 | 26798 | total - max import reactive power demand timestamp | timestamp | R | 3
| 0x68AF | 0x68B0 | 26799 | 26800 | total - max export reactive power demand | float | R | 2
| 0x68B1 | 0x68B3 | 26801 | 26803 | total - max export reactive power demand timestamp | timestamp | R | 3
| 0x68B4 | 0x68B5 | 26804 | 26805 | total - max apparent power demand | float | R | 2
| 0x68B6 | 0x68B8 | 26806 | 26808 | total - max apparent power demand timestamp | timestamp | R | 3
| 0x68B9 | 0x68BA | 26809 | 26810 | total - max Ia demand | float | R | 2
| 0x68BB | 0x68BD | 26811 | 26813 | total - max Ia demand timestamp | timestamp | R | 3
| 0x68BE | 0x68BF | 26814 | 26815 | total - max Ib demand | float | R | 2
| 0x68C0 | 0x68C2 | 26816 | 26818 | total - max Ib demand timestamp | timestamp | R | 3
| 0x68C3 | 0x68C4 | 26819 | 26820 | total - max Ic demand | float | R | 2
| 0x68C5 | 0x68C7 | 26821 | 26823 | total - max Ic demand timestamp | timestamp | R | 3
200
Previous Month TOU Max Demand | 0x68C8 | 0x68C9 | 26824 | 26825 | sharp - max import active power demand | float | R | 2
| 0x68CA | 0x68CC | 26826 | 26828 | sharp - max import active power demand timestamp (year : uint16_t ; month、day : uint16_t ( High byte: month,Low byte: day); hour、min : uint16_t ( High byte: hour,Low byte: minute); ) | timestamp | R | 3
| 0x68CD | 0x68CE | 26829 | 26830 | sharp - max export active power demand | float | R | 2
| 0x68CF | 0x68D1 | 26831 | 26833 | sharp - max export active power demand timestamp | timestamp |  | 3
| 0x68D2 | 0x68D3 | 26834 | 26835 | sharp - max import reactive power demand | float | R | 2
| 0x68D4 | 0x68D6 | 26836 | 26838 | sharp - max import reactive power demand timestamp | timestamp |  | 3
| 0x68D7 | 0x68D8 | 26839 | 26840 | sharp - max export reactive power demand | float | R | 2
| 0x68D9 | 0x68DB | 26841 | 26843 | sharp - max export reactive power demand timestamp | timestamp |  | 3
| 0x68DC | 0x68DD | 26844 | 26845 | sharp - max apparent power demand | float | R | 2
| 0x68DE | 0x68E0 | 26846 | 26848 | sharp - max apparent power demand timestamp | timestamp |  | 3
| 0x68E1 | 0x68E2 | 26849 | 26850 | sharp - max Ia demand | float | R | 2
| 0x68E3 | 0x68E5 | 26851 | 26853 | sharp - max Ia demand timestamp | timestamp |  | 3
| 0x68E6 | 0x68E7 | 26854 | 26855 | sharp - max Ib demand | float | R | 2
| 0x68E8 | 0x68EA | 26856 | 26858 | sharp - max Ib demand timestamp | timestamp |  | 3
| 0x68EB | 0x68EC | 26859 | 26860 | sharp - max Ic demand | float | R | 2
| 0x68ED | 0x68EF | 26861 | 26863 | sharp - max Ic demand timestamp | timestamp | R | 3
| 0x68F0 | 0x68F1 | 26864 | 26865 | peak - max import active power demand | float | R | 2
| 0x68F2 | 0x68F4 | 26866 | 26868 | peak - max import active power demand timestamp | timestamp | R | 3
| 0x68F5 | 0x68F6 | 26869 | 26870 | peak - max export active power demand | float | R | 2
| 0x68F7 | 0x68F9 | 26871 | 26873 | peak - max export active power demand timestamp | timestamp | R | 3
| 0x68FA | 0x68FB | 26874 | 26875 | peak - max import reactive power demand | float | R | 2
| 0x68FC | 0x68FE | 26876 | 26878 | peak - max import reactive power demand timestamp | timestamp | R | 3
| 0x68FF | 0x6900 | 26879 | 26880 | peak - max export reactive power demand | float | R | 2
| 0x6901 | 0x6903 | 26881 | 26883 | peak - max export reactive power demand timestamp | timestamp | R | 3
| 0x6904 | 0x6905 | 26884 | 26885 | peak - max apparent power demand | float | R | 2
| 0x6906 | 0x6908 | 26886 | 26888 | peak - max apparent power demand timestamp | timestamp | R | 3
| 0x6909 | 0x690A | 26889 | 26890 | peak - max Ia demand | float | R | 2
| 0x690B | 0x690D | 26891 | 26893 | peak - max Ia demand timestamp | timestamp | R | 3
| 0x690E | 0x690F | 26894 | 26895 | peak - max Ib demand | float | R | 2
| 0x6910 | 0x6912 | 26896 | 26898 | peak - max Ib demand timestamp | timestamp | R | 3
| 0x6913 | 0x6914 | 26899 | 26900 | peak - max Ic demand | float | R | 2
| 0x6915 | 0x6917 | 26901 | 26903 | peak - max Ic demand timestamp | timestamp | R | 3
| 0x6918 | 0x6919 | 26904 | 26905 | valley - max import active power demand | float | R | 2
| 0x691A | 0x691C | 26906 | 26908 | valley - max import active power demand timestamp | timestamp | R | 3
| 0x691D | 0x691E | 26909 | 26910 | valley - max export active power demand | float | R | 2
| 0x691F | 0x6921 | 26911 | 26913 | valley - max export active power demand timestamp | timestamp | R | 3
| 0x6922 | 0x6923 | 26914 | 26915 | valley - max import reactive power demand | float | R | 2
| 0x6924 | 0x6926 | 26916 | 26918 | valley - max import reactive power demand timestamp | timestamp | R | 3
| 0x6927 | 0x6928 | 26919 | 26920 | valley - max export reactive power demand | float | R | 2
| 0x6929 | 0x692B | 26921 | 26923 | valley - max export reactive power demand timestamp | timestamp | R | 3
| 0x692C | 0x692D | 26924 | 26925 | valley - max apparent power demand | float | R | 2
| 0x692E | 0x6930 | 26926 | 26928 | valley - max apparent power demand timestamp | timestamp | R | 3
| 0x6931 | 0x6932 | 26929 | 26930 | valley - max Ia demand | float | R | 2
| 0x6933 | 0x6935 | 26931 | 26933 | valley - max Ia demand timestamp | timestamp | R | 3
| 0x6936 | 0x6937 | 26934 | 26935 | valley - max Ib demand | float | R | 2
| 0x6938 | 0x693A | 26936 | 26938 | valley - max Ib demand timestamp | timestamp | R | 3
| 0x693B | 0x693C | 26939 | 26940 | valley - max Ic demand | float | R | 2
| 0x693D | 0x693F | 26941 | 26943 | valley - max Ic demand timestamp | timestamp | R | 3
| 0x6940 | 0x6941 | 26944 | 26945 | normal - max import active power demand | float | R | 2
| 0x6942 | 0x6944 | 26946 | 26948 | normal - max import active power demand timestamp | timestamp | R | 3
| 0x6945 | 0x6946 | 26949 | 26950 | normal - max export active power demand | float | R | 2
| 0x6947 | 0x6949 | 26951 | 26953 | normal - max export active power demand timestamp | timestamp | R | 3
| 0x694A | 0x694B | 26954 | 26955 | normal - max import reactive power demand | float | R | 2
| 0x694C | 0x694E | 26956 | 26958 | normal - max import reactive power demand timestamp | timestamp | R | 3
| 0x694F | 0x6950 | 26959 | 26960 | normal - max export reactive power demand | float | R | 2
| 0x6951 | 0x6953 | 26961 | 26963 | normal - max export reactive power demand timestamp | timestamp | R | 3
| 0x6954 | 0x6955 | 26964 | 26965 | normal - max apparent power demand | float | R | 2
| 0x6956 | 0x6958 | 26966 | 26968 | normal - max apparent power demand timestamp | timestamp | R | 3
| 0x6959 | 0x695A | 26969 | 26970 | normal - max Ia demand | float | R | 2
| 0x695B | 0x695D | 26971 | 26973 | normal - max Ia demand timestamp | timestamp | R | 3
| 0x695E | 0x695F | 26974 | 26975 | normal - max Ib demand | float | R | 2
| 0x6960 | 0x6962 | 26976 | 26978 | normal - max Ib demand timestamp | timestamp | R | 3
| 0x6963 | 0x6964 | 26979 | 26980 | normal - max Ic demand | float | R | 2
| 0x6965 | 0x6967 | 26981 | 26983 | normal - max Ic demand timestamp | timestamp | R | 3
| 0x6968 | 0x6969 | 26984 | 26985 | total - max import active power demand | float | R | 2
| 0x696A | 0x696C | 26986 | 26988 | total - max import active power demand timestamp | timestamp | R | 3
| 0x696D | 0x696E | 26989 | 26990 | total - max export active power demand | float | R | 2
| 0x696F | 0x6971 | 26991 | 26993 | total - max export active power demand timestamp | timestamp | R | 3
| 0x6972 | 0x6973 | 26994 | 26995 | total - max import reactive power demand | float | R | 2
| 0x6974 | 0x6976 | 26996 | 26998 | total - max import reactive power demand timestamp | timestamp | R | 3
| 0x6977 | 0x6978 | 26999 | 27000 | total - max export reactive power demand | float | R | 2
| 0x6979 | 0x697B | 27001 | 27003 | total - max export reactive power demand timestamp | timestamp | R | 3
| 0x697C | 0x697D | 27004 | 27005 | total - max apparent power demand | float | R | 2
| 0x697E | 0x6980 | 27006 | 27008 | total - max apparent power demand timestamp | timestamp | R | 3
| 0x6981 | 0x6982 | 27009 | 27010 | total - max Ia demand | float | R | 2
| 0x6983 | 0x6985 | 27011 | 27013 | total - max Ia demand timestamp | timestamp | R | 3
| 0x6986 | 0x6987 | 27014 | 27015 | total - max Ib demand | float | R | 2
| 0x6988 | 0x698A | 27016 | 27018 | total - max Ib demand timestamp | timestamp | R | 3
| 0x698B | 0x698C | 27019 | 27020 | total - max Ic demand | float | R | 2
| 0x698D | 0x698F | 27021 | 27023 | total - max Ic demand timestamp | timestamp | R | 3
200
TOU OverFlow flag | 0x69FE | 0x69FF | 27134 | 27135 | TOU OverFlow flag | uint32_t | R | 2 | 0
2

## Alarm Record ¦DI¦SOE
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Alarm settings code function : 03H Read, 10H Write
| 0x7000 | 0x7001 | 28672 | 28673 | Enable all alarm | uint32_t | R/W | 2 | Bit 0~19 for alarm channel 1~20 (0: disabled; 1：enabled | 0
| 0x7002 | 0x7002 | 28674 | 28674 | Alarm Channel 1 Logic | uint16_t | R/W | 1 | bit2-0= 000：parameter 1 is not involved in the alert logic calculation bit2-0= 001：parameter 1 is used as the "=" condition in the alert logic calculation bit2-0= 010：parameter 1 is used for the ">" condition in the alert logic calculation bit2-0= 011：parameter 1 is used for the "<" condition in the alert logic calculation bit 5-3 = 000：parameter 2 is not involved in the alert logic calculation bit5-3= 001： parameter 2 is used as the "=" condition in the alert logic calculation bit 5-3 = 010：parameter 2 is used for the ">" condition in the alert logic calculation bit 5-3 =0 11：parameter 2 is used for the "<" condition in the alert logic calculation bit7-6=01：Parameters 1 and 2 have an "&&" relationship in the alert logic calculation bit7-6=10：Parameters 1 and 2 have an "¦¦" relationship in the alert logic calculation | 0
| 0x7003 | 0x7003 | 28675 | 28675 | Alarm channel 1 DO selection | uint16_t | R/W | 1 | 0: no output 1：output DO | 0
| 0x7004 | 0x7004 | 28676 | 28676 | Alarm channel 1 parameter1 index | uint16_t | R/W | 1 | modbus addr (DI :1-3)、Basic Parameters 、Demand、Power Quality | 0
| 0x7005 | 0x7006 | 28677 | 28678 | Alarm channel 1 parameter1 Pickup Value | float | R/W | 2 |  | 0
| 0x7007 | 0x7007 | 28679 | 28679 | Alarm channel 1 parameter1 Pickup Delay | uint16_t | R/W | 1 | 1-65535 | 0
| 0x7008 | 0x7009 | 28680 | 28681 | Alarm channel 1 parameter1 Dropout Value | float | R/W | 2
| 0x700A | 0x700A | 28682 | 28682 | Alarm channel 1 parameter1 Dropout Delay | uint16_t | R/W | 1 | 1-65535
| 0x700B | 0x700B | 28683 | 28683 | Alarm channel 1 parameter2 index | uint16_t | R/W | 1 | modbus addr (DI :1-3)、Basic Parameters 、Demand、Power Quality
| 0x700C | 0x700D | 28684 | 28685 | Alarm channel 1 parameter2 Pickup Value | float | R/W | 2
| 0x700E | 0x700E | 28686 | 28686 | Alarm channel 1 parameter2 Pickup Delay | uint16_t | R/W | 1
| 0x700F | 0x7010 | 28687 | 28688 | Alarm channel 1 parameter2 Dropout Value | float | R/W | 2
| 0x7011 | 0x7011 | 28689 | 28689 | Alarm channel 1 parameter2 Dropout Delay | uint16_t | R/W | 1
| 0x7012 | 0x7021 | 28690 | 28705 | Alarm channel 2 configuration |  | R/W | 16
| 0x7022 | 0x7031 | 28706 | 28721 | Alarm channel 3 configuration |  | R/W | 16
| 0x7032 | 0x7041 | 28722 | 28737 | Alarm channel 4 configuration |  | R/W | 16
| 0x7042 | 0x7051 | 28738 | 28753 | Alarm channel 5 configuration |  | R/W | 16
| 0x7052 | 0x7061 | 28754 | 28769 | Alarm channel 6 configuration |  | R/W | 16
| 0x7062 | 0x7071 | 28770 | 28785 | Alarm channel 7 configuration |  | R/W | 16
| 0x7072 | 0x7081 | 28786 | 28801 | Alarm channel 8 configuration |  | R/W | 16
| 0x7082 | 0x7091 | 28802 | 28817 | Alarm channel 9 configuration |  | R/W | 16
| 0x7092 | 0x70A1 | 28818 | 28833 | Alarm channel 10 configuration |  | R/W | 16
| 0x70A2 | 0x70B1 | 28834 | 28849 | Alarm channel 11 configuration |  | R/W | 16
| 0x70B2 | 0x70C1 | 28850 | 28865 | Alarm channel 12 configuration |  | R/W | 16
| 0x70C2 | 0x70D1 | 28866 | 28881 | Alarm channel 13 configuration |  | R/W | 16
| 0x70D2 | 0x70E1 | 28882 | 28897 | Alarm channel 14 configuration |  | R/W | 16
| 0x70E2 | 0x70F1 | 28898 | 28913 | Alarm channel 15 configuration |  | R/W | 16
| 0x70F2 | 0x7101 | 28914 | 28929 | Alarm channel 16 configuration |  | R/W | 16
| 0x7102 | 0x7111 | 28930 | 28945 | Alarm channel 17 configuration |  | R/W | 16
| 0x7112 | 0x7121 | 28946 | 28961 | Alarm channel 18 configuration |  | R/W | 16
| 0x7122 | 0x7131 | 28962 | 28977 | Alarm channel 19 configuration |  | R/W | 16
| 0x7132 | 0x7141 | 28978 | 28993 | Alarm channel 20 configuration |  | R/W | 16
322
Alarm Log Read Window
Data Format | 0x7300 | 0x7301 | 29440 | 29441 | The alarm status of each alarm channel | uint32_t | R | 2 | bit0-bit019：0->Alarm release 1:Alarm activation
| 0x7302 | 0x7302 | 29442 | 29442 | the index of the Alarm Log | uint16_t | R | 1 | 1-200
| 0x7303 | 0x7303 | 29443 | 29443 | Number of the Alarm Log | uint16_t | R | 1 | Alarm Log already occurred Count 0：Empty
| 0x7304 | 0x7304 | 29444 | 29444 | The first index of the alarm Log will be read | uint16_t | R/W | 1 | 1-200
| 0x7305 | 0x7305 | 29445 | 29445 | Read the number of the Alarm Log offset | uint16_t | R/W | 1 | 1--8
| 0x7306 | 0x7306 | 29446 | 29446 | Data state of Alarm Log Window | uint16_t | R | 1 | 0x00: window get data failed; 0x0B: window data effective; 0xFF: window data Busy;
| 0x7307 | 0x737E | 29447 | 29566 | Alarm Log Reading Window | uint16_t | R | 120 | Alarm Log Data
127
SOE Log Status | 0x7400 | 0x7400 | 29696 | 29696 | the index of the SOE Log | uint16_t | R | 1 | 1-200
| 0x7401 | 0x7401 | 29697 | 29697 | Number of the SOE Log | uint16_t | R | 1 | SOE Log already occurred Count 0：Empty
SOE Log Read Window | 0x7402 | 0x7402 | 29698 | 29698 | The first index of the SOE Log will be read | uint16_t | R/W | 1 | 1-200
| 0x7403 | 0x7403 | 29699 | 29699 | Read the number of the SOE Log offset | uint16_t | R/W | 1 | 1--20
| 0x7404 | 0x7404 | 29700 | 29700 | Data state of SOE Log Window | uint16_t | R | 1 | 0x00: window get data failed; 0x0B: window data effective; 0xFF: window data Busy;
| 0x7405 | 0x747C | 29701 | 29820 | SOE Log Reading Window |  | R | 120 | SOE Log Data
123
DI pulse Count
| 0x7600 | 0x7601 | 30208 | 30209 | DI1 pulse count | uint32_t | R/W | 2
| 0x7602 | 0x7603 | 30210 | 30211 | DI2 pulse count | uint32_t | R/W | 2
| 0x7604 | 0x7605 | 30212 | 30213 | DI3 pulse count | uint32_t | R/W | 2
6
Alarm Log Record Data Format
[5 empty] | Alarm Log ID | uint16_t |  | 1
[5 empty] | Alarm Log Time Stamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) | uint16_t |  | 4
[5 empty] | Alarm Log Monitor ID | uint16_t |  | 1
[5 empty] | Alarm Status | uint16_t |  | 1 | 1:start 0:end 2：configuration change
[5 empty] | Alarm Log Extreme Value 1 | float |  | 2
[5 empty] | Alarm Log Extreme Value 2 | float |  | 2
[5 empty] | Alarm Log Duration | uint32_t |  | 2
Soe Log Record Data Format
[5 empty] | Soe Log ID | uint16_t |  | 1
[5 empty] | Time Stamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) | uint16_t |  | 4
[5 empty] | digtal Input Status | uint16_t |  | 1 | b2-b0->DI3-DI1 Status:1:High 0：Low

## Waveform¦PQ Event
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
code function : 03H Read, 10H Write Power Quality Event setting | 0x7A00 | 0x7A00 | 31232 | 31232 | Norminal Current | uint16_t | R/W | 1 | 1-50000A | 1000
Rated Value | 0x7A01 | 0x7A02 | 31233 | 31234 | Norminal Voltage | uint32_t | R/W | 2 | 50-1000000V | 480
Voltage Sag | 0x7A03 | 0x7A03 | 31235 | 31235 | Voltage Sag Enable | uint16_t | R/W | 1 | 0：disable 1：enable | 0
| 0x7A04 | 0x7A04 | 31236 | 31236 | Voltage Sag Threshold | uint16_t | R/W | 1 | 10%-90% | 50
| 0x7A05 | 0x7A05 | 31237 | 31237 | Voltage Sag Hysteresis | uint16_t | R/W | 1 | 1-10% | 2
| 0x7A06 | 0x7A06 | 31238 | 31238 | Voltage Sag Triggers Waveform Recording | uint16_t | R/W | 1 | 0:disable 1:enable | 0
| 0x7A07 | 0x7A07 | 31239 | 31239 | Voltage Sag - switch to output DO | uint16_t | R/W | 1 | 0:disable 1:enable | 0
Voltage Swell | 0x7A08 | 0x7A08 | 31240 | 31240 | Voltage Swell Enable | uint16_t | R/W | 1 | 0：disable 1：enable | 0
| 0x7A09 | 0x7A09 | 31241 | 31241 | Voltage Swell Threshold | uint16_t | R/W | 1 | 110%-150% | 150
| 0x7A0A | 0x7A0A | 31242 | 31242 | Voltage Swell Hysteresis | uint16_t | R/W | 1 | 1-10% | 2
| 0x7A0B | 0x7A0B | 31243 | 31243 | Voltage Swell Triggers Waveform Recording | uint16_t | R/W | 1 | 0:disable 1:enable | 0
| 0x7A0C | 0x7A0C | 31244 | 31244 | Voltage Swell - switch to output DO | uint16_t | R/W | 1 | 0:disable 1:enable | 0
Voltage Interruption | 0x7A0D | 0x7A0D | 31245 | 31245 | Voltage Interruption Enable | uint16_t | R/W | 1 | 0：disable 1：enable | 0
| 0x7A0E | 0x7A0E | 31246 | 31246 | Voltage Interruption Threshold | uint16_t | R/W | 1 | 5%-20% | 10
| 0x7A0F | 0x7A0F | 31247 | 31247 | Voltage Interruption Hysteresis | uint16_t | R/W | 1 | 1-10% | 2
| 0x7A10 | 0x7A10 | 31248 | 31248 | Voltage Interruption Triggers Waveform Recording | uint16_t | R/W | 1 | 0:disable 1:enable | 0
| 0x7A11 | 0x7A11 | 31249 | 31249 | Voltage Interruption - switch to output DO | uint16_t | R/W | 1 | 0:disable 1:enable | 0
Current Swell | 0x7A12 | 0x7A12 | 31250 | 31250 | Current Swell Enable | uint16_t | R/W | 1 | 0：disable 1：enable | 0
| 0x7A13 | 0x7A13 | 31251 | 31251 | Current Swell Threshold | uint16_t | R/W | 1 | 110%-150% | 150
| 0x7A14 | 0x7A14 | 31252 | 31252 | Current Swell Hysteresis | uint16_t | R/W | 1 | 1-10% | 5
| 0x7A15 | 0x7A15 | 31253 | 31253 | Current Triggers Waveform Recording | uint16_t | R/W | 1 | 0:disable 1:enable | 0
| 0x7A16 | 0x7A16 | 31254 | 31254 | Current Swell - switch to output DO | uint16_t | R/W | 1 | 0:disable 1:enable | 0
Voltage unbanlance | 0x7A17 | 0x7A17 | 31255 | 31255 | Voltage unbanlance Enable | uint16_t | R/W | 1 | 0：disable 1：enable | 0
| 0x7A18 | 0x7A18 | 31256 | 31256 | Voltage unbanlance Threshold | uint16_t | R/W | 1 | 5%-50% | 5
| 0x7A19 | 0x7A19 | 31257 | 31257 | Voltage unbanlance Hysteresis | uint16_t | R/W | 1 | 1%-10% | 2
| 0x7A1A | 0x7A1A | 31258 | 31258 | Voltage unbanlance Triggers Waveform Recording | uint16_t | R/W | 1 | 0:disable 1:enable | 0
| 0x7A1B | 0x7A1B | 31259 | 31259 | Voltage unbanlance - switch to output DO | uint16_t | R/W | 1 | 0:disable 1:enable | 0
Current unbanlance | 0x7A1C | 0x7A1C | 31260 | 31260 | Current unbanlance Enable | uint16_t | R/W | 1 | 0：disable 1：enable | 0
| 0x7A1D | 0x7A1D | 31261 | 31261 | Current unbanlance Threshold | uint16_t | R/W | 1 | 5%-50% | 5
| 0x7A1E | 0x7A1E | 31262 | 31262 | Current unbanlance Hysteresis | uint16_t | R/W | 1 | 1%-10% | 2
| 0x7A1F | 0x7A1F | 31263 | 31263 | Current unbanlance Triggers Waveform Recording | uint16_t | R/W | 1 | 0:disable 1:enable | 0
| 0x7A20 | 0x7A20 | 31264 | 31264 | Current unbanlance - switch to output DO | uint16_t | R/W | 1 | 0:disable 1:enable | 0
33
Waveform record parameter setting | 0x7C00 | 0x7C00 | 31744 | 31744 | sampling rate | uint16_t | R/W | 1 | 0:16 points 1:32 points 2:64 points 3:128 points 4:256points 5:512 points | 3
| 0x7C01 | 0x7C01 | 31745 | 31745 | Number of cycles before the event occurred | uint16_t | R/W | 1 | 1-159, Total numbers of recorded waves is 2560 float data points, If sampling rate is 16 points, the max recorded waves is 160, Number of recorded waves before the event occurred shoud be setted to 1-159. | 10
| 0x7C02 | 0x7C02 | 31746 | 31746 | Number of cycles after the event occurred | uint16_t | R/W | 1 | 1-159, The max recorded waves is (160 - Number of recorded waves before the event occurred) | 10
| 0x7C03 | 0x7C03 | 31747 | 31747 | DI1 Trigger | uint16_t | R/W | 1 | 0:disable, 1：enable, 0xFF:only record voltage | 0
| 0x7C04 | 0x7C04 | 31748 | 31748 | DI2 Trigger | uint16_t | R/W | 1 | 0:disable, 1：enable, 0xFF:only record voltage | 0
| 0x7C05 | 0x7C05 | 31749 | 31749 | DI3 Trigger | uint16_t | R/W | 1 | 0:disable, 1：enable, 0xFF:only record voltage | 0
| 0x7C06 | 0x7C06 | 31750 | 31750 | Manually Trigger | uint16_t | R/W | 1 | 0:disable, 1：enable, 0xFF:only record voltage | 0
Waveform Reading Window | [7 empty] | 7
Data Format
| 0x7E00 | 0x7E00 | 32256 | 32256 | Group ID of reading waveform | uint16_t | R/W | 1 | 1 - 200 | 0x6601:0 0x6602:0 read waveform information(ID,Mode,Timestamp)
| 0x7E01 | 0x7E01 | 32257 | 32257 | The nth waveform cycle | uint16_t | R/W | 1 | 0:read waveform information(ID,Mode,Timestamp), 1-160
| 0x7E02 | 0x7E02 | 32258 | 32258 | The nth register packet of one waveform cycle | uint16_t | R/W | 1 | 0:read waveform information(ID,Mode,Timestamp), 1-39(max), 39=((128*4*6)/240), Maximum data capacity of one cycle/240
| 0x7E03 | 0x7E03 | 32259 | 32259 | Total groups already recorded | uint16_t | R | 1 | 0 - 200
| 0x7E04 | 0x7E04 | 32260 | 32260 | Data state of waveform record window | uint16_t | R | 1 | 0x00: window get data failed; 0x0B: window data effective; 0xFF: window data Busy;
| 0x7E05 | 0x7E05 | 32261 | 32261 | Latest waveform record groupe ID | uint16_t | R | 1 | 1 - 200;0: no waveform record data。
| 0x7E06 | 0x7E7D | 32262 | 32381 | Waveform record data reading window |  | R | 120
126
| In the case of 16-point recording: 0:waveform ID,4bytes; Read-only waveform record reason mode,4bytes;Time of waveform recording,8bytes( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) The following data frame defines waveform data, which is read in the sequence of Ua, Ub, Uc, CH1, CH2, CH3 ,and CH4 1: The first 120 registers, one group is divided into multiple packets, each occupying 120 registers in size; 2: The second 120 registers; 3: The third 120 registers; . . . . . . n: The nth 120 registers; The host needs to calculate how many packets the waveform will be divided into, and send commands in sequence to read the data packets.When reading waveform data for a channel, the resulting data frame may contain fewer than 120 registers, The empty registers will not be filled with data from other channels. The waveform data for the next channel will be stored starting from the beginning of the next data frame. when record reason mode is 0b00001000 or 0b00010000 or 0b01000000,The host can only get Ua Ub and Uc records; when record reason mode is 0b10010000, The host can get Ua/Ub/Uc and CH1/CH2/CH3/CH4records. |  |  |  | In the case of 32-point recording and broadcasting, 0: :waveform ID,4bytes;Read-only waveform record reason mode，4bytes;waveform Frequent,4bytes;Time of waveform recording,8bytes;Trigger channel，2bytes: bit0-bit4：input;1/2/3/4，bit5：Non-independent Mode 0, Independent Mode 1；summation userID in Independent mode，2bytes； 1: The first 120 registers, one group is divided into multiple packets, each occupying 120 registers in size; 2: The second 120 registers; 3: The third 120 registers; . . . . . . n: The nth 120 registers; all reason mode: 0b00000001:DI1 trigger(voltage); 0b00000010:DI2 trigger(voltage); 0b00000011:DI3 trigger(voltage); 0b00000100:DI1 trigger(voltage&current); 0b00000101:DI2 trigger(voltage&current); 0b00000110:DI3 trigger(voltage&current); 0b00000111:manual trigger(voltage); 0b00001001:manual trigger(voltage&current); 0b00001000:voltage sag; 0b00010000:voltage swell; 0b00100000:voltage unbalance; 0b01000000:voltage interrupt; 0b10001000:current sag; 0b10010000:current swell; 0b10100000:current unbalance; |  |  |  | In the case of 128-point recording and broadcasting, 0: :waveform ID,4bytes;Read-only waveform record reason mode，4bytes;Time of waveform recording,8bytes; 1: The first 120 registers, one group is divided into multiple packets, each occupying 120 registers in size; 2: The second 120 registers; 3: The third 120 registers; . . . . . . n: The nth 120 registers;
PQ Event Record Reading Window
Data Format | 0x7F00 | 0x7F00 | 32512 | 32512 | the Status of the PQEvent | uint16_t | R | 1 | bit0:0->Volt Sag Event Out ,1->Volt Sag Event In ; bit1:0->Volt Swell Event Out ,1->Volt Swell Event In ; bit2:0->Volt Interruption Event Out ,1->Volt Interruption Event In ; bit3:0->Volt Unbalance Event Out ,1->Volt Unbalance Event In ; bit4:0->current swell Event Out ,1->current swell Event In ; bit5:0->current Unbalance Event Out ,1->current Unbalance Event In ;
| 0x7F01 | 0x7F01 | 32513 | 32513 | the index of the PQEvent Log | uint16_t | R | 1 | 1-200
| 0x7F02 | 0x7F02 | 32514 | 32514 | Number of the PQEvent Log | uint16_t | R | 1 | PQEvent Logal already occurred Count 0：Empty
| 0x7F03 | 0x7F03 | 32515 | 32515 | The first index of the PQEvent Log will be read | uint16_t | R/W | 1 | 1-200
| 0x7F04 | 0x7F04 | 32516 | 32516 | Read the number of the PQEvent Log offset | uint16_t | R/W | 1 | 1--5
| 0x7F05 | 0x7F05 | 32517 | 32517 | Data state of PQEvent Log window | uint16_t | R | 1 | 0x00: window get data failed; 0x0B: window data effective; 0xFF: window data Busy;
| 0x7F06 | 0x7F7D | 32518 | 32637 | PQEvent Log Reading window |  | R | 120 | PQ Event Log Data
PQ Event Log Record Data Format
[5 empty] | PQ Event Log ID | uint16_t |  | 1
[5 empty] | Time Stamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) | uint16_t |  | 4
[5 empty] | Event Type | uint16_t |  | 1 | 0b00001000:voltage sag; 0b00010000:voltage swell; 0b00100000:voltage unbalance; 0b01000000:voltage interrupt; 0b10001000:current sag; 0b10010000:current swell; 0b10100000:current unbalance;
[5 empty] | Event Status | uint16_t |  | 1 | 0:in 1:out
[5 empty] | Trigger channel | uint16_t |  | 1 | Volt Event : bit 0/1/2: Phase A/B/C Current Event : bit 0/1/2/3: input 1/2/3/4 independent Mode Enable：bit5：Non-independent Mode 0 ,Independent Mode 1
[5 empty] | summation userID in Independent mode | uint16_t |  | 1 | 0b00000000:current events are not associated with users; 0b00000001:current event correlation user 1; 0b00000010:current event correlation user 2; 0b00000011:current event correlation user 1、2;
[5 empty] | Associate with waveform ID | uint32_t |  | 2 | 0:No Waveform Trigger
[5 empty] | Duration of power quality events | uint32_t |  | 2
[5 empty] | Max Value of Parameter #1 | float |  | 2 | The maximum and minimum values of each phase of the channel (voltage or current, depending on the type of event)； Unbalanced event record - maximum of imbalance at Max Value of Parameter #1,minimum of imbalance at Min Value of Parameter #1,Max Value of Parameter #2/3 reset ,Min Value of Parameter #2/3
[5 empty] | Max Value of Parameter #2 | float |  | 2
[5 empty] | Max Value of Parameter #3 | float |  | 2
[5 empty] | Min Value of Parameter #1 | float |  | 2
[5 empty] | Min Value of Parameter #2 | float |  | 2
[5 empty] | Min Value of Parameter #3 | float |  | 2
25

## Audit Log
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
AuditLog Status | 0x8900 | 0x8900 | 35072 | 35072 | Max Records | uint16 | R | 1 |  | Fixed as 6000
| 0x8901 | 0x8901 | 35073 | 35073 | Record Index | uint16 | R | 1
| 0x8902 | 0x8902 | 35074 | 35074 | SystemLog full status | uint16 | R | 1 | 0x0000 - Not full 0x0001 - Full Others - Reserved
| 0x8903 | 0x8903 | 35075 | 35075 | Record Number | uint16 | R | 1
AuditLog Reading
| 0x8910 | 0x8910 | 35088 | 35088 | The AuditLog ID to to read | uint16 | R/W | 1 | 1~6000
| 0x8911 | 0x8911 | 35089 | 35089 | The AuditLog number need to read | uint16 | R/W | 1 |  | Fixed as 0x01
| 0x8912 | 0x8912 | 35090 | 35090 | The AuditLog read window status | uint16 | R | 1 | 0x0B - The data windown is ready 0xFF - The request data is invalid;
| 0x8913 | 0x8913 | 35091 | 35091 | The signatured bytes size of the AuditLog to be read | uint16 | R | 1
| 0x8914 | 0x898B | 35092 | 35211 | AuditLog data window | uint8_t | R | 120

## Data log And Trend log
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Data log Setting
| 0x8000 | 0x8000 | 32768 | 32768 | Data Log1 number of registers | uint16_t | R/W | 1 | 0-300
| 0x8001 | 0x8001 | 32769 | 32769 | Data Log1 number of blocks | uint16_t | R/W | 1 | 0-585 Datalog1, Datalog2, Datalog3 share 585 blocks, Trendlog uses 195 blocks exclusively
| 0x8002 | 0x8002 | 32770 | 32770 | Data Log1 Interval | uint16_t | R/W | 1 | 1 - 1440
| 0x8003 | 0x812E | 32771 | 33070 | Data Log1 parameter selections(up to 300 parameters) | uint16_t | R/W | 300 | (Modbus parameter statr address)
| 0x812F | 0x812F | 33071 | 33071 | Data Log1 mode selection | uint16_t | R/W | 1 | 0 - 2
| 0x8130 | 0x8130 | 33072 | 33072 | Data Log1 Mode2 Start month, year | uint8_t | R/W | 1 | Low byte: month,high byte: year（keep consistence with Data Log123）
| 0x8131 | 0x8131 | 33073 | 33073 | Data Log1 Mode2 Start day, hour | uint8_t | R/W | 1 | Low byte: hour,high byte: day
| 0x8132 | 0x8132 | 33074 | 33074 | Data Log1 Mode2 Start minute, second | uint8_t | R/W | 1 | Low byte: second,high byte: minute
| 0x8133 | 0x8133 | 33075 | 33075 | Data Log1 Mode2 End month, year | uint8_t | R/W | 1 | Low byte: month,high byte: year
| 0x8134 | 0x8134 | 33076 | 33076 | Data Log1 Mode2 End day, hour | uint8_t | R/W | 1 | Low byte: hour,high byte: day
| 0x8135 | 0x8135 | 33077 | 33077 | Data Log1 Mode2 End minute, second | uint8_t | R/W | 1 | Low byte: second,high byte: minute
| 0x8136 | 0x8136 | 33078 | 33078 | Data Log1 Mode3 Start Hour and Min | uint16_t | R/W | 1 | Low byte: min,high byte: hour
| 0x8137 | 0x826D | 33079 | 33389 | Log2 setting |  | R/W | 311
| 0x826E | 0x83A4 | 33390 | 33700 | Log3 setting |  | R/W | 311
| 0x83A5 | 0x84DB | 33701 | 34011 | Trend Log setting |  | R/W | 311
1244
Data log Reading Window
| 0x8500 | 0x8500 | 34048 | 34048 | Data logger ID | uint16_t | R/W | 1 | 0 - 3
| 0x8501 | 0x8502 | 34049 | 34050 | Read record offset | uint32_t | R/W | 2
| 0x8503 | 0x8503 | 34051 | 34051 | Read record number | uint16_t | R/W | 1
| 0x8504 | 0x8504 | 34052 | 34052 | Read record package offset | uint16_t | R/W | 1
| 0x8505 | 0x8505 | 34053 | 34053 | Read record package number | uint16_t | R/W | 1
| 0x8506 | 0x8506 | 34054 | 34054 | window state | uint16_t | R | 1 | window state（0x0B: data effective,0xFF: data not effective,0xAA: Data Log on clearing,0xBB: Data Log clearing end）
| 0x8507 | 0x857E | 34055 | 34174 | record data reading Window | uint16_t | R | 120 | Data Log format: record number（4bytes ）+ time stamps（6bytes） + [data1~dataN]（12Nbytes） + CRC( 2bytes)。 Data format: parameter1 average value, parameter2 average value...parameter1 max value, parameter2 max value, parameter1 min value, parameter2 min value...
127
Data log Status Reading
| 0x8600 | 0x8601 | 34304 | 34305 | Data Log1 Max Records | uint32_t | R | 2
| 0x8602 | 0x8603 | 34306 | 34307 | Data Log1 Used Records | uint32_t | R | 2
| 0x8604 | 0x8604 | 34308 | 34308 | Data Log1 Record size | uint16_t | R | 1
| 0x8605 | 0x8606 | 34309 | 34310 | Data Log1 current record index | uint32_t | R | 2
| 0x8607 | 0x8607 | 34311 | 34311 | Data Log1 Log Availability（reserve） | uint16_t | R | 1
| 0x8608 | 0x860A | 34312 | 34314 | Data Log1 First Record Time stamp | uint16_t | R | 3
| 0x860B | 0x860D | 34315 | 34317 | Data Log1 Last Record Time stamp | uint16_t | R | 3
| 0x860E | 0x860E | 34318 | 34318 | Data Log1 Record package counter | uint16_t | R | 1
| 0x860F | 0x860F | 34319 | 34319 | Data Log1 Record first package size | uint16_t | R | 1
| 0x8610 | 0x8610 | 34320 | 34320 | Data Log1 Record last package size | uint16_t | R | 1
| 0x8611 | 0x8612 | 34321 | 34322 | Data Log1 Record first Record Index | uint32_t | R | 2
| 0x8613 | 0x8613 | 34323 | 34323 | DataLog 1 Current Window Status | uint16_t | R | 1 | 0x00FF: Invalid, 0x00AA: Erasing, 0x000B: Valid, 0x0000: Inactive
| 0x8614 | 0x8627 | 34324 | 34343 | Data log 2 Status Reading | uint16_t | R | 20
| 0x8628 | 0x863B | 34344 | 34363 | Data log 3 Status Reading | uint16_t | R | 20
| 0x863C | 0x864F | 34364 | 34383 | Trend log Status Reading | uint16_t | R | 20
80
DataLog block
Datalog 1 Block | 0x8700 | 0x8700 | 34560 | 34560 | first block | uint16_t | R | 1
| 0x8701 | 0x8701 | 34561 | 34561 | current block | uint16_t | R | 1
| 0x8702 | 0x8703 | 34562 | 34563 | current address | uint32_t | R | 2
| 0x8704 | 0x8704 | 34564 | 34564 | full (low byte) | uint16_t | R | 1 | 0: not full 1: sector is full
Datalog 2 Block | 0x8705 | 0x8705 | 34565 | 34565 | first block | uint16_t | R | 1
| 0x8706 | 0x8706 | 34566 | 34566 | current block | uint16_t | R | 1
| 0x8707 | 0x8708 | 34567 | 34568 | current address | uint32_t | R | 2
| 0x8709 | 0x8709 | 34569 | 34569 | full (low byte) | uint16_t | R | 1 | 0: not full 1: sector is full
Datalog 3 Block | 0x870A | 0x870A | 34570 | 34570 | first block | uint16_t | R | 1
| 0x870B | 0x870B | 34571 | 34571 | current block | uint16_t | R | 1
| 0x870C | 0x870D | 34572 | 34573 | current address | uint32_t | R | 2
| 0x870E | 0x870E | 34574 | 34574 | full (low byte) | uint16_t | R | 1 | 0: not full 1: sector is full
Datalog 4 Block | 0x870F | 0x870F | 34575 | 34575 | first block | uint16_t | R | 1
| 0x8710 | 0x8710 | 34576 | 34576 | current block | uint16_t | R | 1
| 0x8711 | 0x8712 | 34577 | 34578 | current address | uint32_t | R | 2
| 0x8713 | 0x8713 | 34579 | 34579 | full (low byte) | uint16_t | R | 1 | 0: not full 1: sector is full
20

## System Log
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
SystemLog Status | 0x8800 | 0x8800 | 34816 | 34816 | Max Records | uint16 | R | 1 |  | Fixed as 5000
| 0x8801 | 0x8801 | 34817 | 34817 | Record Index | uint16 | R | 1
| 0x8803 | 0x8803 | 34819 | 34819 | Record Number | uint16 | R | 1
SystemLog Reading | 0x8810 | 0x8810 | 34832 | 34832 | The SystemLog ID to to read | uint16 | R/W | 1 |  | 1~5000
| 0x8811 | 0x8811 | 34833 | 34833 | The SystemLog number need to read | uint16 | R/W | 1 |  | max value 5000
| 0x8812 | 0x8812 | 34834 | 34834 | The SystemLog read window status | uint16 | R | 1 |  | 0x0B - The data windown is ready 0xFF - The request data is invalid;
| 0x8813 | 0x8813 | 34835 | 34835 | The signatured bytes size of the SystemLog to be read | uint16 | R | 1
| 0x8814 | 0x888B | 34836 | 34955 | SystemLog data window | uint8_t | R | 120
System Log Record Data Format
[5 empty] | Sys Log ID | uint16_t |  | 1
[5 empty] | Time Stamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) | uint16_t |  | 4
[5 empty] | uint16_t log_tyep | uint16_t |  | 1
[5 empty] | uint8_t data[20] | uint8_t |  | 20

## Acucloud log
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Acucloud Log Setting
| 0x8A00 | 0x8A00 | 35328 | 35328 | Enable Acucloud log post | uint16_t | R/W | 1 | 0:disable, 1:enable | 0: disable
| 0x8A01 | 0x8A40 | 35329 | 35392 | URL | uint8_t | R/W | 64
| 0x8A41 | 0x8A60 | 35393 | 35424 | Token | uint8_t | R/W | 32
| 0x8A61 | 0x8A61 | 35425 | 35425 | Server Cert Size(Bytes) | uint16_t | R/W | 1
| 0x8A62 | 0x8A62 | 35426 | 35426 | Server Cert offset | uint16_t | R/W | 1
| 0x8A63 | 0x8A63 | 35427 | 35427 | Server Cert package Size | uint16_t | R/W | 1
| 0x8A64 | 0x8A64 | 35428 | 35428 | Server Cert CRC | uint16_t | R/W | 1
| 0x8A65 | 0x8A65 | 35429 | 35429 | Server Cert CRC Result | uint16_t | R | 1
Acucloud Log Setting Writing Window | 0x8A66 | 0x8ADD | 35430 | 35549 | Server Cert Writing Window | uint8_t | R/W | 120
Acucloud Log Reading Window
| 0x8AE0 | 0x8AE1 | 35552 | 35553 | Read record offset | uint32_t | R/W | 2 | 1 based
| 0x8AE2 | 0x8AE2 | 35554 | 35554 | Read record number | uint16_t | R/W | 1 | fixed as 1
| 0x8AE3 | 0x8AE3 | 35555 | 35555 | Read bytes start offset | uint16_t | R/W | 1 | 0 based
| 0x8AE4 | 0x8AE4 | 35556 | 35556 | Read bytes count | uint16_t | R/W | 1 | Byte count to read
| 0x8AE5 | 0x8AE5 | 35557 | 35557 | window state | uint16_t | R | 1 | window state（0x0B: data effective,0xFF: data not effective,0xAA: Data Log on clearing,0xBB: Data Log clearing end）
| 0x8AE6 | 0x8B5D | 35558 | 35677 | record data reading Window | uint16_t | R | 120 | Log format: record number（4bytes ）+ time stamps（6bytes） + [data1~dataN]（12Nbytes） + CRC( 2bytes)。 Data format: parameter1 average value, parameter2 average value...parameter1 max value, parameter2 max value, parameter1 min value, parameter2 min value…
126
Acucloud Log Status Reading
| 0x8B90 | 0x8B90 | 35728 | 35728 | first Record Index | uint16_t | R | 1 | 1 based
| 0x8B91 | 0x8B91 | 35729 | 35729 | Cur Record Index | uint16_t | R | 1 | 1 based
| 0x8B92 | 0x8B92 | 35730 | 35730 | used records | uint16_t | R | 1
| 0x8B93 | 0x8B93 | 35731 | 35731 | max record Index | uint16_t | R | 1
| 0x8B94 | 0x8B94 | 35732 | 35732 | flash full | uint16_t | R | 1 |  | 0
| 0x8B95 | 0x8B95 | 35733 | 35733 | Log Record package counter | uint16_t | R | 1
| 0x8B96 | 0x8B96 | 35734 | 35734 | Record size | uint16_t | R | 1
7
AcuCloud Post Status
| 0x8B97 | 0x8B97 | 35735 | 35735 | previous post status | uint16_t | R/W | 1 | 0: previous post failed 1: previous post succeed
| 0x8B98 | 0x8B98 | 35736 | 35736 | is roll back | uint16_t | R/W | 1 | 0: no 1: yes
| 0x8B99 | 0x8B99 | 35737 | 35737 | cloud log last post Index | uint16_t | R/W | 1
| 0x8B9A | 0x8B9D | 35738 | 35741 | last post time | uint64_t | RW | 4 | Time in utc that last post succeed
| 0x8B9E | 0x8BA1 | 35742 | 35745 | Post Fail File Timestamp | uint64_t | RW | 4
11
Test AcuCloud
| 0x8BB0 | 0x8BB0 | 35760 | 35760 | Test AcuCloud Command | uint16_t | RW | 1 | 0: Test AcuCloud button is NOT clicked 1: Test AcuCloud button is clicked
| 0x8BB1 | 0x8BB1 | 35761 | 35761 | Test AcuCloud Status | uint16_t | R | 1 | 0x00: Testing 0x0B: Test Done.
| 0x8BB2 | 0x8BB2 | 35762 | 35762 | Test AcuCloud Result | uint16_t | R | 1 | 0: Test failed. 1: Test Success.
3

## Datalog Post
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
DatalogPost Setting
| 0x8C00 | 0x8C00 | 35840 | 35840 | Enable Datalog post | uint16_t | R/W | 1 | 0:disable, 1:enable | 0: disable
| 0x8C01 | 0x8C01 | 35841 | 35841 | Post Protocol | uint16_t | R/W | 1 | 0: http 1: https 2:MQTT | 0:http
| 0x8C02 | 0x8C02 | 35842 | 35842 | logger ID | uint16_t | R/W | 1 | 0~3 | 0
| 0x8C03 | 0x8C04 | 35843 | 35844 | Post File Length | uint32_t | R/W | 2 | 1~43200 in minutes 43200 is the minutes in a month( Say 30days a month). | 5
| 0x8C05 | 0x8C05 | 35845 | 35845 | Log File Format | uint16_t | R/W | 1 | 0:CSV, 1:JSON | 0:CSV
| 0x8C06 | 0x8C06 | 35846 | 35846 | Log File Name time format | uint16_t | R/W | 1 | 0: Unix Time Stamp 1: Time interval based | 0: Unix Time Stamp
| 0x8C07 | 0x8C19 | 35847 | 35865 | reserved | uint8_t | R/W | 19
| 0x8C1A | 0x8C1A | 35866 | 35866 | Timestamp Format | uint16_t | R/W | 1 | 0: Local Time 1: UTC Seconds 2: ISO8601 Format | 0: Local Time
27
http setting
| 0x8C20 | 0x8C9F | 35872 | 35999 | URL | uint8_t | R/W | 128
| 0x8CA0 | 0x8D1F | 36000 | 36127 | Token | uint8_t | R/W | 128
256
https setting
| 0x8D40 | 0x8DBF | 36160 | 36287 | URL | uint8_t | R/W | 128 | data post target including path e.g. http://example.org/upload
| 0x8DC0 | 0x8E3F | 36288 | 36415 | Token | uint8_t | R/W | 128
| 0x8E40 | 0x8E40 | 36416 | 36416 | Server Cert Size(Bytes) | uint16_t | R/W | 1
| 0x8E41 | 0x8E41 | 36417 | 36417 | Server Cert Index | uint16_t | R/W | 1
| 0x8E42 | 0x8E42 | 36418 | 36418 | Server Cert package Size | uint16_t | R/W | 1
| 0x8E43 | 0x8E43 | 36419 | 36419 | Server Cert CRC | uint16_t | R/W | 1
| 0x8E44 | 0x8E44 | 36420 | 36420 | Server Cert CRC Result | uint16_t | R | 1
| 0x8E45 | 0x8EBC | 36421 | 36540 | Server Cert Writing Window | uint8_t | R/W | 120
381
MQTT setting
| 0x8F00 | 0x8F1F | 36608 | 36639 | user name | uint8_t | R/W | 32
| 0x8F20 | 0x8F3F | 36640 | 36671 | user password | uint8_t | R/W | 32
| 0x8F40 | 0x8F7F | 36672 | 36735 | IP or Domain Name | uint8_t | R/W | 64
| 0x8F80 | 0x8FFF | 36736 | 36863 | Topic | uint8_t | R/W | 128
| 0x9000 | 0x901F | 36864 | 36895 | Client ID | uint8_t | R/W | 32
288
Datalog Post Status
| 0x9025 | 0x9025 | 36901 | 36901 | previous post status | uint16_t | R/W | 1 | 0: previous post failed 1: previous post succeed | 0
| 0x9026 | 0x9026 | 36902 | 36902 | is roll back | uint16_t | R/W | 1 | 0: no 1: yes | 0
| 0x9027 | 0x9028 | 36903 | 36904 | last post Index | uint32_t | R/W | 2 |  | 1
| 0x9029 | 0x902C | 36905 | 36908 | datalog last post time | uint64_t | R/W | 4 | Time in utc that last post succeed | 0
| 0x902D | 0x902D | 36909 | 36909 | Is in DST | uint16_t | R/W | 1 | Current time is in DST period? 0: No ; 1: YES | 0
| 0x902E | 0x9031 | 36910 | 36913 | Post Fail File Timestamp | uint64_t | R/W | 4
13
Test DataLog Post
| 0x9040 | 0x9040 | 36928 | 36928 | Test Datalog post Command | uint16_t | RW | 1 | 0: Test Datalog Post button is NOT clicked 1: Test Datalog Post button is clicked
| 0x9041 | 0x9041 | 36929 | 36929 | Test Datalog Post Status | uint16_t | R | 1 | 0x00: Testing 0x0B: Test Done.
| 0x9042 | 0x9042 | 36930 | 36930 | Test Datalog Post Result | uint16_t | R | 1 | 0: Test failed. 1: Test Success.
3
DataPost Reading Window
| 0x7800 | 0x7800 | 30720 | 30720 | Data logger ID | uint16_t | R/W | 1 | 0 - 3
| 0x7801 | 0x7802 | 30721 | 30722 | Read record offset | uint32_t | R/W | 2
| 0x7803 | 0x7803 | 30723 | 30723 | Read record number | uint16_t | R/W | 1
| 0x7804 | 0x7804 | 30724 | 30724 | Read record package offset | uint16_t | R/W | 1
| 0x7805 | 0x7805 | 30725 | 30725 | Read record package number | uint16_t | R/W | 1
| 0x7806 | 0x7806 | 30726 | 30726 | window state | uint16_t | R | 1 | window state（0x0B: data effective,0xFF: data not effective,0xAA: Data Log on clearing,0xBB: Data Log clearing end）
| 0x7807 | 0x787E | 30727 | 30846 | record data reading Window | uint16_t | R | 120 | Data Log format: record number（4bytes ）+ time stamps（6bytes） + [data1~dataN]（12Nbytes） + CRC( 2bytes)。 Data format: parameter1 average value, parameter2 average value...parameter1 max value, parameter2 max value, parameter1 min value, parameter2 min value...

## Information
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Fireware & Product information:03H Read
Firmware Version Info
| 0xF000 | 0xF001 | 61440 | 61441 | Firmware version | uint8_t | R | 2 | In the format like x.yz (e.g., 1.01) | determined by firmware
| 0xF002 | 0xF004 | 61442 | 61444 | Firmware release date | uint8_t | R | 3 | In the format like YYMMDD (221228) | determined by firmware
| 0xF005 | 0xF005 | 61445 | 61445 | Firmware patch number | uint8_t | R | 1 | In the format like xy (01) | determined by firmware
Update (0x6A to write) | 0xF000 | 0xF001 | 61440 | 61441 | Device entry update | uint8_t | W | 2 | 0xA1,0x58,0x58,0xA1
8
Bootloader Info
| 0xF010 | 0xF011 | 61456 | 61457 | bootloader product string | uint8_t | R | 2 | MAB1 | determined by boot
| 0xF012 | 0xF013 | 61458 | 61459 | bootloader version | uint8_t | R | 2 | In the format like x.yz (e.g., 1.01) | determined by boot
| 0xF014 | 0xF016 | 61460 | 61462 | bootloader release date | uint8_t | R | 3 | ASCII, in format of YYMMDD (e.g. 241108) | determined by boot
| 0xF017 | 0xF017 | 61463 | 61463 | bootloader patch number | uint8_t | R | 1 | In the format like xy (01) | determined by boot
8
Product Info (0x6A to write in factory)
| 0xF040 | 0xF04F | 61504 | 61519 | Serial Number | uint8_t | R/W | 16 | In the format like MABYYMMabcde(e.g., MAB250400001)
| 0xF050 | 0xF051 | 61520 | 61521 | Hardware version | uint8_t | R/W | 2 | In the format like x.yz (e.g., 1.01)
| 0xF052 | 0xF052 | 61522 | 61522 | Function Model Type | uint16_t | R/W | 1 | 0:AcuRev-1321 1:AcuRev-1321 2:AcuRev-1322 | 0
| 0xF053 | 0xF053 | 61523 | 61523 | Reserved | uint8_t | R/W | 1
| 0xF054 | 0xF054 | 61524 | 61524 | Current Input Type | uint16_t | R/W | 1 | 0 for mA 1 for mV
| 0xF055 | 0xF055 | 61525 | 61525 | Power Supply Type | uint16_t | R/W | 1 | Fixed as 0 for P1
| 0xF056 | 0xF065 | 61526 | 61541 | MAC address(port3) | uint8_t | R/W | 16
| 0xF066 | 0xF066 | 61542 | 61542 | Certification Type | uint16_t | R/W | 1 | 0: None; 1: MC; Default:0 | 0
| 0xF067 | 0xF06F | 61543 | 61551 | Reserved | uint8_t | R/W | 9
| 0xF070 | 0xF070 | 61552 | 61552 | Hardware Patch Number | uint8_t | R/W | 1 | In the format like xy (01)
| 0xF071 | 0xF080 | 61553 | 61568 | MAC address(port1) | uint8_t | R/W | 16
| 0xF081 | 0xF090 | 61569 | 61584 | MAC address(port2) | uint8_t | R/W | 16
81

## ParaMeter Sync（Dual CPU）
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Parameter Sync:67H write | 0xFF00 | 0xFF00 | 65280 | 65280 | Power On Synchronization | uint16_t | W | 1
| 0xFF01 | 0xFF01 | 65281 | 65281 | Clear Year 10 Holiday Number Setting Sync | uint16_t | W | 1
| 0xFF02 | 0xFF02 | 65282 | 65282 | Restore TOU factory setting Sync | uint16_t | W | 1

## Calibration
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Calibration Commands | 0xF204 | 0xF204 | 61956 | 61956 | calibration stage | uint16_t | R/W | 1 | 0:normal 1:offset reset 2:start offset 3:gain reset 4:start gain 1st 5:start gain 2nd 6:phase reset 7:start phase 8:offset write 9:gain write 10:phase write 11：factory mode offset 12: factory mode gain and pahse 13:exit 0xAA:power on ok
| 0xF205 | 0xF205 | 61957 | 61957 | H:calibStartChannelID | uint16_t | R/W | 1 | 0-6
L:caliboffsetID
| 0xF206 | 0xF213 | 61958 | 61971 | calibRmsValue[7] | uint32_t | R | 14
| 0xF214 | 0xF215 | 61972 | 61973 | factory offset calibration result | uint32_t | R | 2 | bit0：Ua，bit1:Ub,bit2:Uc,bit3:current1,....bit6:current4. 0 is fail,1 is success
| 0xF216 | 0xF217 | 61974 | 61975 | factory gain calibration result | uint32_t | R | 2
| 0xF218 | 0xF219 | 61976 | 61977 | factory phase calibration result | uint32_t | R | 2
22
Calibration OffSet Coef
| 0xF250 | 0xF251 | 62032 | 62033 | V1offSetCoef | int32_t | R/W | 2
| 0xF252 | 0xF253 | 62034 | 62035 | V2offSetCoef | int32_t | R/W | 2
| 0xF254 | 0xF255 | 62036 | 62037 | V3offSetCoef | int32_t | R/W | 2
| 0xF256 | 0xF257 | 62038 | 62039 | I1offSetCoef | int32_t | R/W | 2
| 0xF258 | 0xF259 | 62040 | 62041 | I2offSetCoef | int32_t | R/W | 2
| 0xF25A | 0xF25B | 62042 | 62043 | I3offSetCoef | int32_t | R/W | 2
| 0xF25C | 0xF25D | 62044 | 62045 | I4offSetCoef | int32_t | R/W | 2
GainCoef(V A/B/C)
| 0xF25E | 0xF25F | 62046 | 62047 | V1gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF260 | 0xF261 | 62048 | 62049 | V2gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF262 | 0xF263 | 62050 | 62051 | V3gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
GainCoef(mA、 mV CT、RCT)
| 0xF264 | 0xF265 | 62052 | 62053 | I1gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF266 | 0xF267 | 62054 | 62055 | I2gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF268 | 0xF269 | 62056 | 62057 | I3gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF26A | 0xF26B | 62058 | 62059 | I4gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
PhaseCoef(50Hz、60Hz)
| 0xF26C | 0xF26C | 62060 | 62060 | V1 adc phaseCoef | int16_t | R/W | 1
| 0xF26D | 0xF26D | 62061 | 62061 | V2 adc phaseCoef | int16_t | R/W | 1
| 0xF26E | 0xF26E | 62062 | 62062 | V3 adc phaseCoef | int16_t | R/W | 1
| 0xF26F | 0xF26F | 62063 | 62063 | I1 adc phaseCoef | int16_t | R/W | 1
| 0xF270 | 0xF270 | 62064 | 62064 | I2 adc phaseCoef | int16_t | R/W | 1
| 0xF271 | 0xF271 | 62065 | 62065 | I3 adc phaseCoef | int16_t | R/W | 1
| 0xF272 | 0xF272 | 62066 | 62066 | I4 adc phaseCoef | int16_t | R/W | 1
| 0xF273 | 0xF273 | 62067 | 62067 | V1 dsp phaseCoef | int16_t | R/W | 1
| 0xF274 | 0xF274 | 62068 | 62068 | V2 dsp phaseCoef | int16_t | R/W | 1
| 0xF275 | 0xF275 | 62069 | 62069 | V3 dsp phaseCoef | int16_t | R/W | 1
| 0xF276 | 0xF276 | 62070 | 62070 | I1 dsp phaseCoef | int16_t | R/W | 1
| 0xF277 | 0xF277 | 62071 | 62071 | I2 dsp phaseCoef | int16_t | R/W | 1
| 0xF278 | 0xF278 | 62072 | 62072 | I3 dsp phaseCoef | int16_t | R/W | 1
| 0xF279 | 0xF279 | 62073 | 62073 | I4 dsp phaseCoef | int16_t | R/W | 1
42

## DI Status
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
DI Status(code function : 02H Read)
| 0x0000 | 0x0000 | 0 | 0 | DI1 | bit | R | 1
| 0x0001 | 0x0001 | 1 | 1 | DI2 | bit | R | 1
| 0x0002 | 0x0002 | 2 | 2 | DI3 | bit | R | 1
Custom Reading DI Status(code function : 03H Read )
| 0x7620 | 0x7620 | 30240 | 30240 | DI1 | uint16_t | R | 1
| 0x7621 | 0x7621 | 30241 | 30241 | DI2 | uint16_t | R | 1
| 0x7622 | 0x7622 | 30242 | 30242 | DI3 | uint16_t | R | 1

## DO
Block code function : 01H Read,05H ¦ 0FH Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
IO Status
DO | 0x0000 | 0x0000 | 0 | 0 | DO1 | bit | R/W | 1