## 功能对比
Category | Feature | AcuRev-1321 (Standard) | AcuRev-1322 (Advanced – Power Quality)
Accuracy | Revenue-grade accuracy | Class 0.1S | Class 0.1S
Real-time | RMS, Active Power, Reactive Power, Apparent Power | 200 ms update | 1 cycle update，10、12 cycle update，150、180 cycle update，10min Aggregation update，2hr Aggregation update
Energy | Import/Export/Net/Total (kWh/kvarh/kVAh) | ✔ | ✔
Demand | Block interval + sliding window demand | ✔ | ✔
Harmonics | Harmonics (2–63th), THD/TOHD/TEHD, crest factor, THFF, K-factor | 200 ms update | With aggregation ，需要测试200ms，3s，10min，2h的聚合
Advanced Metering | Independent Input Channe | ✔ | ✔
| Dual Source Energy | ✔ | ✔
Alarms | 20 alarm monitors; AND/OR; alarm log (200 records) | ✔ | ✔
Logging | Max/Min with timestamps | ✔ | ✔
| SOE log (DI changes), 2 ms resolution (200 records) | ✔ | ✔
| System log (5000 events) | ✔ | ✔
Data Logging | 3 data loggers + 1 trend logger | ✔ | ✔
I/O | 3 DI + 1 DO | ✔ | ✔
Communications | RS485: Modbus RTU | ✔ | ✔
| RS485: BACnet MS/TP | ✔ | ✔
| Ethernet: Modbus TCP | ✔ | ✔
| Ethernet: Web Server | ✔ | ✔
| Ethernet: HTTP/HTTPs push | ✔ | ✔
Firmware | Firmware update via Ethernet / RS485 | ✔ | ✔
PQ Compliance | IEC 61000-4-30/4-7/4-15 | — | Class S
Flicker | Pinst, Pst, Plt | — | ✔
PQ Events | Sag/Swell/Interruption, Overcurrent, Transient overvoltage | — | ✔ (up to 200 events)
Waveform | Waveform recording (manual / PQ event / DI trigger), configurable sample rate & pre/post trigger | — | ✔ (up to 200 waveforms)

## Real-Time Reading
参数 | 周期
HS_20ms | 1 Cycle
200ms | 10、12 cycle
3S Aggregation | 150、180 cycle
10min Aggregation
2hr Aggregation
|  | 1321只显示10/12 Cycle页面，相关参数只测试该页面 | 1322 5种聚合页面都显示，需测试全部页面
隐藏页面对应的setting也要隐藏
Phase Angles放在Real-Time

## Harmonics
谐波的计算有四种：200ms，3s，10min，2h
1321只显示200ms计算的数据
1322可以显示四种聚合的谐波数据

## Flicker_PQ Events_Waveform
Flicker：在Real-Time Reading页面，Pinst（150/180 cycle），Pst （10min Aggregation）， Plt （2hr Aggregation）
1321在Real-Time Reading页面只显示10/12 Cycle，不会显示Flicker，无需测试Flicker
1321需隐藏Power Quality Event Log页面、ITIC/CBEMA Curve Report页面、Waveform页面，无需测试PQ Event和Waveform功能
隐藏页面对应的setting也要隐藏

## Ordering Information
Function Model | Current Input
AcuRev-1321 | mA: 80mA and 100mA CT Input mV: 333mV and Rogowski Coil Input
AcuRev-1322
Ordering Example:
AcuRev-1321-mA
AcuRev-1321- mV
AcuRev-1322- mA
AcuRev-1322-mV