## Version Record
Version Number | Version Detail | Author | Audit | Date
v0.01 | Initial version of external Modbus Address Table | Travis Si |  | 2022-06-01
v0.02 | Added current phase N harmonics parameters | Travis Si |  | 2023-01-25
v0.03 | 1. Added 200ms flicker parameters 2. Updated demand setting fields 3. Added phase order setting field | Travis Si |  | 2023-04-11
v0.04 | 1. Added mains signaling parameters to 200ms tab 2. Corrected data type of timestamp | Travis Si |  | 2023-05-02
v0.05 | 1. Added mains signaling status parameters and tab 2. Updated addresses of IO parameter | Travis Si |  | 2023-05-08
v0.06 | 1. Added moving average frequency | Travis Si |  | 2023-09-14
v0.07 | 1. Added param update fields for 200ms FFT | Travis Si |  | 2023-10-19
v0.08 | 1.Added reboot command 2. Delete Interval Energy | Ethan Chen |  | 2024-11-11
v1.04 | 1.Added Phase Selection in 0x1020 | Haibo Song |  | 2025-01-11
v1.05 | 1.Added sheet "Transmission" | Haibo Song |  | 2025-04-15
v1.06 | 1.Added variable period (1 minute) Max/Min, AI Readings | Lester Lo, Haibo Song |  | 2025-08-08
v1.07 | Added Fundamental Voltage/Current in Aggregation 3s, 10min, 2hr | Hongjian Zhu |  | 2025-12-22
v1.08 | Add Open/Short circuit detection status | Hongjian Zhu |  | 2026-01-26

## Overview
OVERVIEW
Total Param Num | 16 Info & Command | 49 Config
16296 Reading
Information & Command | Starting Address | End Address
Board Status | 0x1200 | 0x1202
Board Command | 0x12A0 | 0x12A3
Product Info | 0xF000 | 0xF03A
Meter Config | Starting Address | End Address
Meter Sys Config | 0x1000 | 0x101E
Meter IO Config | 0x1080 | 0x1096
Update Rate | Starting Address | End Address
UPDATE_RATE_10SEC | 0x2000 | 0x2009
UPDATE_RATE_HS | 0x200A | 0x2065
UPDATE_RATE_200MS | 0x2100 | 0x2FBB
UPDATE_RATE_3SEC | 0x3000 | 0x3EBB
UPDATE_RATE_10MIN | 0x4000 | 0x4EBF
UPDATE_RATE_2HR | 0x5000 | 0x5EBF
Param Group | Starting Address | End Address
PARAM_GROUP_FUND | 0x6000 | 0x6039
PARAM_GROUP_DEMAND | 0x6100 | 0x61AF
PARAM_GROUP_MAX_DEMAND | 0x6200 | 0x640F
PARAM_GROUP_ACCUM_ENERGY | 0x6500 | 0x664F
PARAM_GROUP_ACCUM_MB_ENERGY | 0x6680 | 0x67CF
PARAM_GROUP_INTL_ENERGY | 0x6800 | 0x694F
PARAM_GROUP_INTL_MB_ENERGY | 0x6980 | 0x6ACF
PARAM_GROUP_MAX | 0x6B00 | 0x6BD7
PARAM_GROUP_MIN | 0x6C00 | 0x6CD7
PARAM_GROUP_TOU | 0x6D00 | 0x6DE9
PARAM_GROUP_PQ_EVENT | 0x6E00 | 0x6E13
PARAM_GROUP_ALARM | 0x6E14 | 0x6E53
PARAM_GROUP_DI_COUNTER | 0x6E54 | 0x6ECB
PARAM_GROUP_DI_STATUS | 0x0000 | 0x003B
PARAM_GROUP_RO | 0x0000 | 0x000F
PARAM_GROUP_AI | 0x6ECC | 0x6EDB
PARAM_GROUP_AO | 0x6EDC | 0x6EEB
PARAM_GROUP_CUR_EN50160 | 0x7000 | 0x7370
PARAM_GROUP_LAST_EN50160 | 0x7400 | 0x7770
PARAM_GROUP_CUR_DAILY_IEEE519 | 0x7800 | 0x828C
PARAM_GROUP_LAST_DAILY_IEEE519 | 0x8300 | 0x8D8C
PARAM_GROUP_CUR_WEEKLY_IEEE519 | 0x8E00 | 0x9A4E
PARAM_GROUP_LAST_WEEKLY_IEEE519 | 0x9B00 | 0xA74E
PARAM_GROUP_TRANSMISSION_POWER | 0xA800 | 0xA83F
PARAM_GROUP_TRANSMISSION_ENERGY | 0xA840 | 0xA8BF
PARAM_GROUP_VAR_MAX | 0xA8C0 | 0xA90D
PARAM_GROUP_VAR_MIN | 0xA910 | 0xA95D

## Var Min Max
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
Varaible Period (1 min for now) Max
0xA8C0 | 0xA8C1 | 43200 | 43201 | MAX_VLN_a_V | Max Phase A Line-to-Neutral Voltage | float | 2 | R
0xA8C2 | 0xA8C3 | 43202 | 43203 | MAX_VLN_b_V | Max Phase B Line-to-Neutral Voltage | float | 2 | R
0xA8C4 | 0xA8C5 | 43204 | 43205 | MAX_VLN_c_V | Max Phase C Line-to-Neutral Voltage | float | 2 | R
0xA8C6 | 0xA8C7 | 43206 | 43207 | MAX_VLN_avg_V | Max Average Line-to-Neutral Voltage | float | 2 | R
0xA8C8 | 0xA8C9 | 43208 | 43209 | MAX_VLL_ab_V | Max Phase AB Line-to-Line Voltage | float | 2 | R
0xA8CA | 0xA8CB | 43210 | 43211 | MAX_VLL_bc_V | Max Phase BC Line-to-Line Voltage | float | 2 | R
0xA8CC | 0xA8CD | 43212 | 43213 | MAX_VLL_ca_V | Max Phase CA Line-to-Line Voltage | float | 2 | R
0xA8CE | 0xA8CF | 43214 | 43215 | MAX_VLL_avg_V | Max Average Line-to-Line Voltage | float | 2 | R
0xA8D0 | 0xA8D1 | 43216 | 43217 | MAX_I_a_A | Max Phase A Current | float | 2 | R
0xA8D2 | 0xA8D3 | 43218 | 43219 | MAX_I_b_A | Max Phase B Current | float | 2 | R
0xA8D4 | 0xA8D5 | 43220 | 43221 | MAX_I_c_A | Max Phase C Current | float | 2 | R
0xA8D6 | 0xA8D7 | 43222 | 43223 | MAX_I_n_A | Max Phase N Current | float | 2 | R
0xA8D8 | 0xA8D9 | 43224 | 43225 | MAX_I_avg_A | Max Average Current | float | 2 | R
0xA8DA | 0xA8DD | 43226 | 43229 | MAX_TIME_VLN_a | Max Phase A VLN Time | time_t | 4 | R
0xA8DE | 0xA8E1 | 43230 | 43233 | MAX_TIME_VLN_b | Max Phase B VLN Time | time_t | 4 | R
0xA8E2 | 0xA8E5 | 43234 | 43237 | MAX_TIME_VLN_c | Max Phase C VLN Time | time_t | 4 | R
0xA8E6 | 0xA8E9 | 43238 | 43241 | MAX_TIME_VLN_avg | Max Average VLN Time | time_t | 4 | R
0xA8EA | 0xA8ED | 43242 | 43245 | MAX_TIME_VLL_ab | Max Phase AB VLL Time | time_t | 4 | R
0xA8EE | 0xA8F1 | 43246 | 43249 | MAX_TIME_VLL_bc | Max Phase BC VLL Time | time_t | 4 | R
0xA8F2 | 0xA8F5 | 43250 | 43253 | MAX_TIME_VLL_ca | Max Phase CA VLL Time | time_t | 4 | R
0xA8F6 | 0xA8F9 | 43254 | 43257 | MAX_TIME_VLL_avg | Max Average VLL Time | time_t | 4 | R
0xA8FA | 0xA8FD | 43258 | 43261 | MAX_TIME_I_a | Max Phase A Current Time | time_t | 4 | R
0xA8FE | 0xA901 | 43262 | 43265 | MAX_TIME_I_b | Max Phase B Current Time | time_t | 4 | R
0xA902 | 0xA905 | 43266 | 43269 | MAX_TIME_I_c | Max Phase C Current Time | time_t | 4 | R
0xA906 | 0xA909 | 43270 | 43273 | MAX_TIME_I_n | Max Phase N Current Time | time_t | 4 | R
0xA90A | 0xA90D | 43274 | 43277 | MAX_TIME_I_avg | Max Average Current Time | time_t | 4 | R
Varaible Period (1 min for now) Min
0xA910 | 0xA911 | 43280 | 43281 | MIN_VLN_a_V | Min Phase A Line-to-Neutral Voltage | float | 2 | R
0xA912 | 0xA913 | 43282 | 43283 | MIN_VLN_b_V | Min Phase B Line-to-Neutral Voltage | float | 2 | R
0xA914 | 0xA915 | 43284 | 43285 | MIN_VLN_c_V | Min Phase C Line-to-Neutral Voltage | float | 2 | R
0xA916 | 0xA917 | 43286 | 43287 | MIN_VLN_avg_V | Min Average Line-to-Neutral Voltage | float | 2 | R
0xA918 | 0xA919 | 43288 | 43289 | MIN_VLL_ab_V | Min Phase AB Line-to-Line Voltage | float | 2 | R
0xA91A | 0xA91B | 43290 | 43291 | MIN_VLL_bc_V | Min Phase BC Line-to-Line Voltage | float | 2 | R
0xA91C | 0xA91D | 43292 | 43293 | MIN_VLL_ca_V | Min Phase CA Line-to-Line Voltage | float | 2 | R
0xA91E | 0xA91F | 43294 | 43295 | MIN_VLL_avg_V | Min Average Line-to-Line Voltage | float | 2 | R
0xA920 | 0xA921 | 43296 | 43297 | MIN_I_a_A | Min Phase A Current | float | 2 | R
0xA922 | 0xA923 | 43298 | 43299 | MIN_I_b_A | Min Phase B Current | float | 2 | R
0xA924 | 0xA925 | 43300 | 43301 | MIN_I_c_A | Min Phase C Current | float | 2 | R
0xA926 | 0xA927 | 43302 | 43303 | MIN_I_n_A | Min Phase N Current | float | 2 | R
0xA928 | 0xA929 | 43304 | 43305 | MIN_I_avg_A | Min Average Current | float | 2 | R
0xA92A | 0xA92D | 43306 | 43309 | MIN_TIME_VLN_a | Min Phase A VLN Time | time_t | 4 | R
0xA92E | 0xA931 | 43310 | 43313 | MIN_TIME_VLN_b | Min Phase B VLN Time | time_t | 4 | R
0xA932 | 0xA935 | 43314 | 43317 | MIN_TIME_VLN_c | Min Phase C VLN Time | time_t | 4 | R
0xA936 | 0xA939 | 43318 | 43321 | MIN_TIME_VLN_avg | Min Average VLN Time | time_t | 4 | R
0xA93A | 0xA93D | 43322 | 43325 | MIN_TIME_VLL_ab | Min Phase AB VLL Time | time_t | 4 | R
0xA93E | 0xA941 | 43326 | 43329 | MIN_TIME_VLL_bc | Min Phase BC VLL Time | time_t | 4 | R
0xA942 | 0xA945 | 43330 | 43333 | MIN_TIME_VLL_ca | Min Phase CA VLL Time | time_t | 4 | R
0xA946 | 0xA949 | 43334 | 43337 | MIN_TIME_VLL_avg | Min Average VLL Time | time_t | 4 | R
0xA94A | 0xA94D | 43338 | 43341 | MIN_TIME_I_a | Min Phase A Current Time | time_t | 4 | R
0xA94E | 0xA951 | 43342 | 43345 | MIN_TIME_I_b | Min Phase B Current Time | time_t | 4 | R
0xA952 | 0xA955 | 43346 | 43349 | MIN_TIME_I_c | Min Phase C Current Time | time_t | 4 | R
0xA956 | 0xA959 | 43350 | 43353 | MIN_TIME_I_n | Min Phase N Current Time | time_t | 4 | R
0xA95A | 0xA95D | 43354 | 43357 | MIN_TIME_I_avg | Min Average Current Time | time_t | 4 | R

## Info & Command
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data Type | Reg | RW | Range | Default | Factory Default
Reset Commands |  | Write: 0x10 Write Multiple Registers
0x12A0 | 0x12A0 | 4768 | 4768 | Reset Energy | uint16 | 1 | W | 0xAA Modbus Command Leagal Code
0x12A1 | 0x12A1 | 4769 | 4769 | Reset Max Demand | uint16 | 1 | W | 0xAA Modbus Command Leagal Code
0x12A2 | 0x12A2 | 4770 | 4770 | Reset Max Min | uint16 | 1 | W | 0xAA Modbus Command Leagal Code
0x12A3 | 0x12A3 | 4771 | 4771 | Reset DI Counter | uint16 | 1 | W | 0xAA Modbus Command Leagal Code
Product Info |  | Write: 0x10 Write Multiple Registers |  |  |  | Read: 0x03 Read Holding Registers
0xF000 | 0xF001 | 61440 | 61441 | Product Type | string | 2 | R
0xF002 | 0xF003 | 61442 | 61443 | Prod HW Version | string | 2 | R
0xF004 | 0xF005 | 61444 | 61445 | Prod SW Version | string | 2 | R
0xF006 | 0xF008 | 61446 | 61448 | Prod Last Update Time | string | 3 | R
0xF009 | 0xF018 | 61449 | 61464 | Prod Serial Number | string | 16 | R
0xF019 | 0xF028 | 61465 | 61480 | Prod Model | string | 16 | R
0xF029 | 0xF02E | 61481 | 61486 | Eth0 MAC Addr | string | 6 | R
0xF02F | 0xF034 | 61487 | 61492 | Eth1 MAC Addr | string | 6 | R
0xF035 | 0xF03A | 61493 | 61498 | WIFI MAC Addr | string | 6 | R
System Control |  | Write: 0x10 Write Multiple Registers
0xF2C0 | 0xF2C0 | 62144 | 62144 | SystemReboot | uint16 | 1 | W | 0xAA Modbus Command Leagal Code

## Meter Sys Config
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x1000 | 0x1001 | 4096 | 4097 | Nominal Voltage | uint32 | 2 | R |  |  | 120
0x1002 | 0x1003 | 4098 | 4099 | Nominal Current | uint32 | 2 | R |  |  | 5
0x1004 | 0x1004 | 4100 | 4100 | Nominal Frequency | enum | 1 | R | 50Hz: 0 60Hz: 1 |  | 1
0x1005 | 0x1005 | 4101 | 4101 | Service Configuration | enum | 1 | R | 1 ELEMENT_2WIRE: 0 2 ELEMENT_3WIRE_1PHASE: 1 2 ELEMENT_3WIRE_DELTA_2CT: 2 2 ELEMENT_3WIRE_DELTA_3CT: 3 3 ELEMENT_4WIRE_Y: 4 |  | 4
0x1006 | 0x1007 | 4102 | 4103 | PT Input | uint32 | 2 | R |  |  | 120
0x1008 | 0x1009 | 4104 | 4105 | PT Output | uint32 | 2 | R |  |  | 120
0x100A | 0x100B | 4106 | 4107 | CT Input | uint32 | 2 | R |  |  | 5
0x100C | 0x100D | 4108 | 4109 | CT Output | uint32 | 2 | R | For 5A model only: TYPE 1A: 1 TYPE 5A: 5 For mV model only: TYPE RCT: 1 TYPE MV: 5 |  | 5
0x100E | 0x100F | 4110 | 4111 | I4 CT Input | uint32 | 2 | R |  |  | 5
0x1010 | 0x1011 | 4112 | 4113 | I4 CT Output | uint32 | 2 | R | For 5A model only: TYPE 1A: 1 TYPE 5A: 5 For mV model only: TYPE RCT: 1 TYPE MV: 5 |  | 5
0x1012 | 0x1012 | 4114 | 4114 | In Method | enum | 1 | R | Calculated: 0 Measured: 1 |  | 0
0x1013 | 0x1013 | 4115 | 4115 | Phase A Current Direction | enum | 1 | R | Positive: 0 Negative: 1 |  | 0
0x1014 | 0x1014 | 4116 | 4116 | Phase B Current Direction | enum | 1 | R | Positive: 0 Negative: 1 |  | 0
0x1015 | 0x1015 | 4117 | 4117 | Phase C Current Direction | enum | 1 | R | Positive: 0 Negative: 1 |  | 0
0x1016 | 0x1016 | 4118 | 4118 | Phase N Current Direction | enum | 1 | R | Positive: 0 Negative: 1 |  | 0
0x1017 | 0x1017 | 4119 | 4119 | Reactive Power Calculation Method | enum | 1 | R | General: 0 True: 1 |  | 0
0x1018 | 0x1018 | 4120 | 4120 | PF Convention | enum | 1 | R | PF Format IEC: 0 PF Format IEEE: 1 |  | 0
0x1019 | 0x1019 | 4121 | 4121 | Demand Algorithm | enum | 1 | R | Fixed Window: 0 Sliding Window: 1 |  | 0
0x101A | 0x101A | 4122 | 4122 | Demand Interval | uint16 | 1 | R |  |  | 5
0x101B | 0x101B | 4123 | 4123 | Demand Update Interval | uint16 | 1 | R |  |  | 1
0x101C | 0x101C | 4124 | 4124 | Energy Calculation Method | enum | 1 | R | Generic: 0 Fundamental: 1 |  | 0
0x101D | 0x101E | 4125 | 4126 | Energy Scale Factor | uint32 | 2 | R |  |  | 1000
0x101F | 0x101F | 4127 | 4127 | Phase Order | enum | 1 | R | ABC: 0 ACB: 1 |  | 0
0x1020 | 0x1020 | 4128 | 4128 | Phase Selection | enum | 1 | R | 0bxx xx xx xx for NCBA phase； value 0b00: A; 0b01: B; 0b10: C; 0b11: N |  | 0b11100100

## Meter IO Config
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x1080 | 0x1080 | 4224 | 4224 | DI 1 Type | enum | 1 | R | Status: 0 Counter: 1 | 1
0x1081 | 0x1082 | 4225 | 4226 | DI 1 Ratio | float | 2 | R |  | 1.0
0x1083 | 0x1083 | 4227 | 4227 | DI 2 Type | enum | 1 | R | Status: 0 Counter: 1 | 1
0x1084 | 0x1085 | 4228 | 4229 | DI 2 Ratio | float | 2 | R |  | 1.0
0x1086 | 0x1086 | 4230 | 4230 | DI 3 Type | enum | 1 | R | Status: 0 Counter: 1 | 1
0x1087 | 0x1088 | 4231 | 4232 | DI 3 Ratio | float | 2 | R |  | 1.0
0x1089 | 0x1089 | 4233 | 4233 | DI 4 Type | enum | 1 | R | Status: 0 Counter: 1 | 1
0x108A | 0x108B | 4234 | 4235 | DI 4 Ratio | float | 2 | R |  | 1.0
0x108C | 0x108C | 4236 | 4236 | DO Mode | enum | 1 | R | Alarm: 0 Pulse: 1 | 1
0x108D | 0x108E | 4237 | 4238 | DO Width | uint32 | 2 | R |  | 100
0x108F | 0x108F | 4239 | 4239 | LED 1 Mode | enum | 1 | R | Alarm: 0 Pulse: 1 | 0
0x1090 | 0x1091 | 4240 | 4241 | LED 1 Width | uint32 | 2 | R |  | 200
0x1092 | 0x1092 | 4242 | 4242 | LED 2 Mode | enum | 1 | R | Alarm: 0 Pulse: 1 | 0
0x1093 | 0x1094 | 4243 | 4244 | LED 2 Width | uint32 | 2 | R |  | 200
0x1095 | 0x1096 | 4245 | 4246 | Pulse Ratio | float | 2 | R |  | 0.1

## 10s
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x2000 | 0x2003 | 8192 | 8195 | 10S_TIMESTAMP | 10s Param Update Time Stamp | double | 4 | R
0x2004 | 0x2005 | 8196 | 8197 | 10S_FLAG | 10s Param Valid Flag | bool | 2 | R
0x2006 | 0x2007 | 8198 | 8199 | 10S_EVENT_FLAG | 10s Param Event Flag | uint32 | 2 | R
0x2008 | 0x2009 | 8200 | 8201 | 10S_Freq_Hz | 10s System Frequency | float | 2 | R

## HS
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x200A | 0x200D | 8202 | 8205 | HS_TIMESTAMP | HS Param Update Time Stamp | double | 4 | R
0x200E | 0x200F | 8206 | 8207 | HS_FLAG | HS Param Valid Flag | bool | 2 | R
0x2010 | 0x2011 | 8208 | 8209 | HS_EVENT_FLAG | HS Param Event Flag | uint32 | 2 | R
0x2012 | 0x2013 | 8210 | 8211 | HS_Freq_Hz | HS System Frequency | float | 2 | R
0x2014 | 0x2015 | 8212 | 8213 | HS_VLN_a_V | HS Phase A Line-to-Neutral Voltage | float | 2 | R
0x2016 | 0x2017 | 8214 | 8215 | HS_VLN_b_V | HS Phase B Line-to-Neutral Voltage | float | 2 | R
0x2018 | 0x2019 | 8216 | 8217 | HS_VLN_c_V | HS Phase C Line-to-Neutral Voltage | float | 2 | R
0x201A | 0x201B | 8218 | 8219 | HS_VLN_avg_V | HS Average Line-to-Neutral Voltage | float | 2 | R
0x201C | 0x201D | 8220 | 8221 | HS_VLL_ab_V | HS Phase AB Line-to-Line Voltage | float | 2 | R
0x201E | 0x201F | 8222 | 8223 | HS_VLL_bc_V | HS Phase BC Line-to-Line Voltage | float | 2 | R
0x2020 | 0x2021 | 8224 | 8225 | HS_VLL_ca_V | HS Phase CA Line-to-Line Voltage | float | 2 | R
0x2022 | 0x2023 | 8226 | 8227 | HS_VLL_avg_V | HS Average Line-to-Line Voltage | float | 2 | R
0x2024 | 0x2025 | 8228 | 8229 | HS_I_a_A | HS Phase A Current | float | 2 | R
0x2026 | 0x2027 | 8230 | 8231 | HS_I_b_A | HS Phase B Current | float | 2 | R
0x2028 | 0x2029 | 8232 | 8233 | HS_I_c_A | HS Phase C Current | float | 2 | R
0x202A | 0x202B | 8234 | 8235 | HS_I_n_A | HS Phase N Current | float | 2 | R
0x202C | 0x202D | 8236 | 8237 | HS_I_avg_A | HS Average Current | float | 2 | R
0x202E | 0x202F | 8238 | 8239 | HS_P_a_kW | HS Phase A Active Power | float | 2 | R
0x2030 | 0x2031 | 8240 | 8241 | HS_P_b_kW | HS Phase B Active Power | float | 2 | R
0x2032 | 0x2033 | 8242 | 8243 | HS_P_c_kW | HS Phase C Active Power | float | 2 | R
0x2034 | 0x2035 | 8244 | 8245 | HS_P_kW | HS System Active Power | float | 2 | R
0x2036 | 0x2037 | 8246 | 8247 | HS_Q_a_kvar | HS Phase A Reactive Power | float | 2 | R
0x2038 | 0x2039 | 8248 | 8249 | HS_Q_b_kvar | HS Phase B Reactive Power | float | 2 | R
0x203A | 0x203B | 8250 | 8251 | HS_Q_c_kvar | HS Phase C Reactive Power | float | 2 | R
0x203C | 0x203D | 8252 | 8253 | HS_Q_kvar | HS System Reactive Power | float | 2 | R
0x203E | 0x203F | 8254 | 8255 | HS_S_a_kVA | HS Phase A Apparent Power | float | 2 | R
0x2040 | 0x2041 | 8256 | 8257 | HS_S_b_kVA | HS Phase B Apparent Power | float | 2 | R
0x2042 | 0x2043 | 8258 | 8259 | HS_S_c_kVA | HS Phase C Apparent Power | float | 2 | R
0x2044 | 0x2045 | 8260 | 8261 | HS_S_kVA | HS System Apparent Power | float | 2 | R
0x2046 | 0x2047 | 8262 | 8263 | HS_LC_a | HS Phase A Load Nature | float | 2 | R
0x2048 | 0x2049 | 8264 | 8265 | HS_LC_b | HS Phase B Load Nature | float | 2 | R
0x204A | 0x204B | 8266 | 8267 | HS_LC_c | HS Phase C Load Nature | float | 2 | R
0x204C | 0x204D | 8268 | 8269 | HS_LC | HS System Load Nature | float | 2 | R
0x204E | 0x204F | 8270 | 8271 | HS_PF_a | HS Phase A Power Factor | float | 2 | R
0x2050 | 0x2051 | 8272 | 8273 | HS_PF_b | HS Phase B Power Factor | float | 2 | R
0x2052 | 0x2053 | 8274 | 8275 | HS_PF_c | HS Phase C Power Factor | float | 2 | R
0x2054 | 0x2055 | 8276 | 8277 | HS_PF | HS System Power Factor | float | 2 | R
0x2056 | 0x2057 | 8278 | 8279 | HS_LEAD_PF_a | HS Phase A Leading Power Factor | float | 2 | R
0x2058 | 0x2059 | 8280 | 8281 | HS_LEAD_PF_b | HS Phase B Leading Power Factor | float | 2 | R
0x205A | 0x205B | 8282 | 8283 | HS_LEAD_PF_c | HS Phase C Leading Power Factor | float | 2 | R
0x205C | 0x205D | 8284 | 8285 | HS_LEAD_PF | HS System Leading Power Factor | float | 2 | R
0x205E | 0x205F | 8286 | 8287 | HS_LAG_PF_a | HS Phase A Lagging Power Factor | float | 2 | R
0x2060 | 0x2061 | 8288 | 8289 | HS_LAG_PF_b | HS Phase B Lagging Power Factor | float | 2 | R
0x2062 | 0x2063 | 8290 | 8291 | HS_LAG_PF_c | HS Phase C Lagging Power Factor | float | 2 | R
0x2064 | 0x2065 | 8292 | 8293 | HS_LAG_PF | HS System Lagging Power Factor | float | 2 | R

## 3s Aggregation
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x3000 | 0x3003 | 12288 | 12291 | 3S_TIMESTAMP | Aggr 3sec Param Update Time Stamp | double | 4 | R
0x3004 | 0x3005 | 12292 | 12293 | 3S_FLAG | Aggr 3sec Param Valid Flag | bool | 2 | R
0x3006 | 0x3007 | 12294 | 12295 | 3S_BLOCK_NUM | Aggr 3sec Param Block Number | uint32 | 2 | R
0x3008 | 0x3009 | 12296 | 12297 | 3S_EVENT_FLAG | Aggr 3sec Param Event Flag | uint32 | 2 | R
0x300A | 0x300B | 12298 | 12299 | 3S_Freq_Hz | Aggr 3sec System Frequency | float | 2 | R
0x300C | 0x300D | 12300 | 12301 | 3S_VLN_a_V | Aggr 3sec Phase A Line-to-Neutral Voltage | float | 2 | R
0x300E | 0x300F | 12302 | 12303 | 3S_VLN_b_V | Aggr 3sec Phase B Line-to-Neutral Voltage | float | 2 | R
0x3010 | 0x3011 | 12304 | 12305 | 3S_VLN_c_V | Aggr 3sec Phase C Line-to-Neutral Voltage | float | 2 | R
0x3012 | 0x3013 | 12306 | 12307 | 3S_VLN_avg_V | Aggr 3sec Average Line-to-Neutral Voltage | float | 2 | R
0x3014 | 0x3015 | 12308 | 12309 | 3S_VLL_ab_V | Aggr 3sec Phase AB Line-to-Line Voltage | float | 2 | R
0x3016 | 0x3017 | 12310 | 12311 | 3S_VLL_bc_V | Aggr 3sec Phase BC Line-to-Line Voltage | float | 2 | R
0x3018 | 0x3019 | 12312 | 12313 | 3S_VLL_ca_V | Aggr 3sec Phase CA Line-to-Line Voltage | float | 2 | R
0x301A | 0x301B | 12314 | 12315 | 3S_VLL_avg_V | Aggr 3sec Average Line-to-Line Voltage | float | 2 | R
0x301C | 0x301D | 12316 | 12317 | 3S_I_a_A | Aggr 3sec Phase A Current | float | 2 | R
0x301E | 0x301F | 12318 | 12319 | 3S_I_b_A | Aggr 3sec Phase B Current | float | 2 | R
0x3020 | 0x3021 | 12320 | 12321 | 3S_I_c_A | Aggr 3sec Phase C Current | float | 2 | R
0x3022 | 0x3023 | 12322 | 12323 | 3S_I_n_A | Aggr 3sec Phase N Current | float | 2 | R
0x3024 | 0x3025 | 12324 | 12325 | 3S_I_avg_A | Aggr 3sec Average Current | float | 2 | R
0x3026 | 0x3027 | 12326 | 12327 | 3S_P_a_kW | Aggr 3sec Phase A Active Power | float | 2 | R
0x3028 | 0x3029 | 12328 | 12329 | 3S_P_b_kW | Aggr 3sec Phase B Active Power | float | 2 | R
0x302A | 0x302B | 12330 | 12331 | 3S_P_c_kW | Aggr 3sec Phase C Active Power | float | 2 | R
0x302C | 0x302D | 12332 | 12333 | 3S_P_kW | Aggr 3sec System Active Power | float | 2 | R
0x302E | 0x302F | 12334 | 12335 | 3S_Q_a_kvar | Aggr 3sec Phase A Reactive Power | float | 2 | R
0x3030 | 0x3031 | 12336 | 12337 | 3S_Q_b_kvar | Aggr 3sec Phase B Reactive Power | float | 2 | R
0x3032 | 0x3033 | 12338 | 12339 | 3S_Q_c_kvar | Aggr 3sec Phase C Reactive Power | float | 2 | R
0x3034 | 0x3035 | 12340 | 12341 | 3S_Q_kvar | Aggr 3sec System Reactive Power | float | 2 | R
0x3036 | 0x3037 | 12342 | 12343 | 3S_S_a_kVA | Aggr 3sec Phase A Apparent Power | float | 2 | R
0x3038 | 0x3039 | 12344 | 12345 | 3S_S_b_kVA | Aggr 3sec Phase B Apparent Power | float | 2 | R
0x303A | 0x303B | 12346 | 12347 | 3S_S_c_kVA | Aggr 3sec Phase C Apparent Power | float | 2 | R
0x303C | 0x303D | 12348 | 12349 | 3S_S_kVA | Aggr 3sec System Apparent Power | float | 2 | R
0x303E | 0x303F | 12350 | 12351 | 3S_LC_a | Aggr 3sec Phase A Load Nature | float | 2 | R
0x3040 | 0x3041 | 12352 | 12353 | 3S_LC_b | Aggr 3sec Phase B Load Nature | float | 2 | R
0x3042 | 0x3043 | 12354 | 12355 | 3S_LC_c | Aggr 3sec Phase C Load Nature | float | 2 | R
0x3044 | 0x3045 | 12356 | 12357 | 3S_LC | Aggr 3sec System Load Nature | float | 2 | R
0x3046 | 0x3047 | 12358 | 12359 | 3S_PF_a | Aggr 3sec Phase A Power Factor | float | 2 | R
0x3048 | 0x3049 | 12360 | 12361 | 3S_PF_b | Aggr 3sec Phase B Power Factor | float | 2 | R
0x304A | 0x304B | 12362 | 12363 | 3S_PF_c | Aggr 3sec Phase C Power Factor | float | 2 | R
0x304C | 0x304D | 12364 | 12365 | 3S_PF | Aggr 3sec System Power Factor | float | 2 | R
0x304E | 0x304F | 12366 | 12367 | 3S_LEAD_PF_a | Aggr 3sec Phase A Leading Power Factor | float | 2 | R
0x3050 | 0x3051 | 12368 | 12369 | 3S_LEAD_PF_b | Aggr 3sec Phase B Leading Power Factor | float | 2 | R
0x3052 | 0x3053 | 12370 | 12371 | 3S_LEAD_PF_c | Aggr 3sec Phase C Leading Power Factor | float | 2 | R
0x3054 | 0x3055 | 12372 | 12373 | 3S_LEAD_PF | Aggr 3sec System Leading Power Factor | float | 2 | R
0x3056 | 0x3057 | 12374 | 12375 | 3S_LAG_PF_a | Aggr 3sec Phase A Lagging Power Factor | float | 2 | R
0x3058 | 0x3059 | 12376 | 12377 | 3S_LAG_PF_b | Aggr 3sec Phase B Lagging Power Factor | float | 2 | R
0x305A | 0x305B | 12378 | 12379 | 3S_LAG_PF_c | Aggr 3sec Phase C Lagging Power Factor | float | 2 | R
0x305C | 0x305D | 12380 | 12381 | 3S_LAG_PF | Aggr 3sec System Lagging Power Factor | float | 2 | R
0x305E | 0x305F | 12382 | 12383 | 3S_PA_VLN_a | Aggr 3sec Phase A Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x3060 | 0x3061 | 12384 | 12385 | 3S_PA_VLN_b | Aggr 3sec Phase B Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x3062 | 0x3063 | 12386 | 12387 | 3S_PA_VLN_c | Aggr 3sec Phase C Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x3064 | 0x3065 | 12388 | 12389 | 3S_PA_VLL_ab | Aggr 3sec Phase AB Line-to-Line Voltage Phase Angle | float | 2 | R
0x3066 | 0x3067 | 12390 | 12391 | 3S_PA_VLL_bc | Aggr 3sec Phase BC Line-to-Line Voltage Phase Angle | float | 2 | R
0x3068 | 0x3069 | 12392 | 12393 | 3S_PA_VLL_ca | Aggr 3sec Phase CA Line-to-Line Voltage Phase Angle | float | 2 | R
0x306A | 0x306B | 12394 | 12395 | 3S_PA_I_a | Aggr 3sec Phase A Current Phase Angle | float | 2 | R
0x306C | 0x306D | 12396 | 12397 | 3S_PA_I_b | Aggr 3sec Phase B Current Phase Angle | float | 2 | R
0x306E | 0x306F | 12398 | 12399 | 3S_PA_I_c | Aggr 3sec Phase C Current Phase Angle | float | 2 | R
0x3070 | 0x3071 | 12400 | 12401 | MAG_3S_SEQ_POS_V_V | Aggr 3sec Voltage Positive Sequence Magnitude | float | 2 | R
0x3072 | 0x3073 | 12402 | 12403 | MAG_3S_SEQ_ZERO_V_V | Aggr 3sec Voltage Zero Sequence Magnitude | float | 2 | R
0x3074 | 0x3075 | 12404 | 12405 | MAG_3S_SEQ_NEG_V_V | Aggr 3sec Voltage Negative Sequence Magnitude | float | 2 | R
0x3076 | 0x3077 | 12406 | 12407 | MAG_3S_SEQ_ZERO_RATIO_V_% | Aggr 3sec Voltage Zero Sequence Ratio Magnitude | float | 2 | R
0x3078 | 0x3079 | 12408 | 12409 | MAG_3S_UNBL_V_% | Aggr 3sec Voltage Unbalance Factor Magnitude | float | 2 | R
0x307A | 0x307B | 12410 | 12411 | MAG_3S_SEQ_POS_I_A | Aggr 3sec Current Positive Sequence Magnitude | float | 2 | R
0x307C | 0x307D | 12412 | 12413 | MAG_3S_SEQ_ZERO_I_A | Aggr 3sec Current Zero Sequence Magnitude | float | 2 | R
0x307E | 0x307F | 12414 | 12415 | MAG_3S_SEQ_NEG_I_A | Aggr 3sec Current Negative Sequence Magnitude | float | 2 | R
0x3080 | 0x3081 | 12416 | 12417 | MAG_3S_SEQ_ZERO_RATIO_I_% | Aggr 3sec Current Zero Sequence Ratio Magnitude | float | 2 | R
0x3082 | 0x3083 | 12418 | 12419 | MAG_3S_UNBL_I_% | Aggr 3sec Current Unbalance Factor Magnitude | float | 2 | R
0x3084 | 0x3085 | 12420 | 12421 | ANG_3S_SEQ_POS_V | Aggr 3sec Voltage Positive Sequence Angle | float | 2 | R
0x3086 | 0x3087 | 12422 | 12423 | ANG_3S_SEQ_ZERO_V | Aggr 3sec Voltage Zero Sequence Angle | float | 2 | R
0x3088 | 0x3089 | 12424 | 12425 | ANG_3S_SEQ_NEG_V | Aggr 3sec Voltage Negative Sequence Angle | float | 2 | R
0x308A | 0x308B | 12426 | 12427 | ANG_3S_SEQ_POS_I_A | Aggr 3sec Current Positive Sequence Angle | float | 2 | R
0x308C | 0x308D | 12428 | 12429 | ANG_3S_SEQ_ZERO_I_A | Aggr 3sec Current Zero Sequence Angle | float | 2 | R
0x308E | 0x308F | 12430 | 12431 | ANG_3S_SEQ_NEG_I_A | Aggr 3sec Current Negative Sequence Angle | float | 2 | R
0x3090 | 0x3091 | 12432 | 12433 | 3S_THD_V_a_% | Aggr 3sec Phase A Voltage THD | float | 2 | R
0x3092 | 0x3093 | 12434 | 12435 | 3S_THD_V_b_% | Aggr 3sec Phase B Voltage THD | float | 2 | R
0x3094 | 0x3095 | 12436 | 12437 | 3S_THD_V_c_% | Aggr 3sec Phase C Voltage THD | float | 2 | R
0x3096 | 0x3097 | 12438 | 12439 | 3S_OTHD_V_a_% | Aggr 3sec Phase A Voltage THD Odd | float | 2 | R
0x3098 | 0x3099 | 12440 | 12441 | 3S_OTHD_V_b_% | Aggr 3sec Phase B Voltage THD Odd | float | 2 | R
0x309A | 0x309B | 12442 | 12443 | 3S_OTHD_V_c_% | Aggr 3sec Phase C Voltage THD Odd | float | 2 | R
0x309C | 0x309D | 12444 | 12445 | 3S_ETHD_V_a_% | Aggr 3sec Phase A Voltage THD Even | float | 2 | R
0x309E | 0x309F | 12446 | 12447 | 3S_ETHD_V_b_% | Aggr 3sec Phase B Voltage THD Even | float | 2 | R
0x30A0 | 0x30A1 | 12448 | 12449 | 3S_ETHD_V_c_% | Aggr 3sec Phase C Voltage THD Even | float | 2 | R
0x30A2 | 0x30A3 | 12450 | 12451 | 3S_CF_V_a_% | Aggr 3sec Phase A Voltage Crest Factor | float | 2 | R
0x30A4 | 0x30A5 | 12452 | 12453 | 3S_CF_V_b_% | Aggr 3sec Phase B Voltage Crest Factor | float | 2 | R
0x30A6 | 0x30A7 | 12454 | 12455 | 3S_CF_V_c_% | Aggr 3sec Phase C Voltage Crest Factor | float | 2 | R
0x30A8 | 0x30A9 | 12456 | 12457 | 3S_THD_I_a_% | Aggr 3sec Phase A Current THD | float | 2 | R
0x30AA | 0x30AB | 12458 | 12459 | 3S_THD_I_b_% | Aggr 3sec Phase B Current THD | float | 2 | R
0x30AC | 0x30AD | 12460 | 12461 | 3S_THD_I_c_% | Aggr 3sec Phase C Current THD | float | 2 | R
0x30AE | 0x30AF | 12462 | 12463 | 3S_THD_I_n_% | Aggr 3sec Phase N Current THD | float | 2 | R
0x30B0 | 0x30B1 | 12464 | 12465 | 3S_OTHD_I_a_% | Aggr 3sec Phase A Current THD Odd | float | 2 | R
0x30B2 | 0x30B3 | 12466 | 12467 | 3S_OTHD_I_b_% | Aggr 3sec Phase B Current THD Odd | float | 2 | R
0x30B4 | 0x30B5 | 12468 | 12469 | 3S_OTHD_I_c_% | Aggr 3sec Phase C Current THD Odd | float | 2 | R
0x30B6 | 0x30B7 | 12470 | 12471 | 3S_OTHD_I_n_% | Aggr 3sec Phase N Current THD Odd | float | 2 | R
0x30B8 | 0x30B9 | 12472 | 12473 | 3S_ETHD_I_a_% | Aggr 3sec Phase A Current THD Even | float | 2 | R
0x30BA | 0x30BB | 12474 | 12475 | 3S_ETHD_I_b_% | Aggr 3sec Phase B Current THD Even | float | 2 | R
0x30BC | 0x30BD | 12476 | 12477 | 3S_ETHD_I_c_% | Aggr 3sec Phase C Current THD Even | float | 2 | R
0x30BE | 0x30BF | 12478 | 12479 | 3S_ETHD_I_n_% | Aggr 3sec Phase N Current THD Even | float | 2 | R
0x30C0 | 0x30C1 | 12480 | 12481 | 3S_TDD_I_a_% | Aggr 3sec Phase A Current TDD | float | 2 | R
0x30C2 | 0x30C3 | 12482 | 12483 | 3S_TDD_I_b_% | Aggr 3sec Phase B Current TDD | float | 2 | R
0x30C4 | 0x30C5 | 12484 | 12485 | 3S_TDD_I_c_% | Aggr 3sec Phase C Current TDD | float | 2 | R
0x30C6 | 0x30C7 | 12486 | 12487 | 3S_TDD_I_n_% | Aggr 3sec Phase N Current TDD | float | 2 | R
0x30C8 | 0x30C9 | 12488 | 12489 | 3S_CF_I_a_% | Aggr 3sec Phase A Current Crest-Factor | float | 2 | R
0x30CA | 0x30CB | 12490 | 12491 | 3S_CF_I_b_% | Aggr 3sec Phase B Current Crest-Factor | float | 2 | R
0x30CC | 0x30CD | 12492 | 12493 | 3S_CF_I_c_% | Aggr 3sec Phase C Current Crest-Factor | float | 2 | R
0x30CE | 0x30CF | 12494 | 12495 | 3S_CF_I_n_% | Aggr 3sec Phase N Current Crest-Factor | float | 2 | R
0x30D0 | 0x30D1 | 12496 | 12497 | 3S_KF_I_a_% | Aggr 3sec Phase A Current K-Factor | float | 2 | R
0x30D2 | 0x30D3 | 12498 | 12499 | 3S_KF_I_b_% | Aggr 3sec Phase B Current K-Factor | float | 2 | R
0x30D4 | 0x30D5 | 12500 | 12501 | 3S_KF_I_c_% | Aggr 3sec Phase C Current K-Factor | float | 2 | R
0x30D6 | 0x30D7 | 12502 | 12503 | 3S_KF_I_n_% | Aggr 3sec Phase N Current K-Factor | float | 2 | R
0x30D8 | 0x30D9 | 12504 | 12505 | MAG_3S_HAR_V_1th_a_% | Aggr 3sec Phase A 1st Voltage Magnitude Harmonics | float | 2 | R
0x30DA | 0x30DB | 12506 | 12507 | MAG_3S_HAR_V_1th_b_% | Aggr 3sec Phase B 1st Voltage Magnitude Harmonics | float | 2 | R
0x30DC | 0x30DD | 12508 | 12509 | MAG_3S_HAR_V_1th_c_% | Aggr 3sec Phase C 1st Voltage Magnitude Harmonics | float | 2 | R
0x30DE | 0x30DF | 12510 | 12511 | MAG_3S_HAR_I_1th_a_% | Aggr 3sec Phase A 1st Current Magnitude Harmonics | float | 2 | R
0x30E0 | 0x30E1 | 12512 | 12513 | MAG_3S_HAR_I_1th_b_% | Aggr 3sec Phase B 1st Current Magnitude Harmonics | float | 2 | R
0x30E2 | 0x30E3 | 12514 | 12515 | MAG_3S_HAR_I_1th_c_% | Aggr 3sec Phase C 1st Current Magnitude Harmonics | float | 2 | R
0x30E4 | 0x30E5 | 12516 | 12517 | MAG_3S_HAR_I_1th_n_% | Aggr 3sec Phase N 1st Current Magnitude Harmonics | float | 2 | R
0x30E6 | 0x30E7 | 12518 | 12519 | MAG_3S_HAR_V_2th_a_% | Aggr 3sec Phase A 2nd Voltage Magnitude Harmonics | float | 2 | R
0x30E8 | 0x30E9 | 12520 | 12521 | MAG_3S_HAR_V_2th_b_% | Aggr 3sec Phase B 2nd Voltage Magnitude Harmonics | float | 2 | R
0x30EA | 0x30EB | 12522 | 12523 | MAG_3S_HAR_V_2th_c_% | Aggr 3sec Phase C 2nd Voltage Magnitude Harmonics | float | 2 | R
0x30EC | 0x30ED | 12524 | 12525 | MAG_3S_HAR_I_2th_a_% | Aggr 3sec Phase A 2nd Current Magnitude Harmonics | float | 2 | R
0x30EE | 0x30EF | 12526 | 12527 | MAG_3S_HAR_I_2th_b_% | Aggr 3sec Phase B 2nd Current Magnitude Harmonics | float | 2 | R
0x30F0 | 0x30F1 | 12528 | 12529 | MAG_3S_HAR_I_2th_c_% | Aggr 3sec Phase C 2nd Current Magnitude Harmonics | float | 2 | R
0x30F2 | 0x30F3 | 12530 | 12531 | MAG_3S_HAR_I_2th_n_% | Aggr 3sec Phase N 2nd Current Magnitude Harmonics | float | 2 | R
0x30F4 | 0x30F5 | 12532 | 12533 | MAG_3S_HAR_V_3th_a_% | Aggr 3sec Phase A 3rd Voltage Magnitude Harmonics | float | 2 | R
0x30F6 | 0x30F7 | 12534 | 12535 | MAG_3S_HAR_V_3th_b_% | Aggr 3sec Phase B 3rd Voltage Magnitude Harmonics | float | 2 | R
0x30F8 | 0x30F9 | 12536 | 12537 | MAG_3S_HAR_V_3th_c_% | Aggr 3sec Phase C 3rd Voltage Magnitude Harmonics | float | 2 | R
0x30FA | 0x30FB | 12538 | 12539 | MAG_3S_HAR_I_3th_a_% | Aggr 3sec Phase A 3rd Current Magnitude Harmonics | float | 2 | R
0x30FC | 0x30FD | 12540 | 12541 | MAG_3S_HAR_I_3th_b_% | Aggr 3sec Phase B 3rd Current Magnitude Harmonics | float | 2 | R
0x30FE | 0x30FF | 12542 | 12543 | MAG_3S_HAR_I_3th_c_% | Aggr 3sec Phase C 3rd Current Magnitude Harmonics | float | 2 | R
0x3100 | 0x3101 | 12544 | 12545 | MAG_3S_HAR_I_3th_n_% | Aggr 3sec Phase N 3rd Current Magnitude Harmonics | float | 2 | R
0x3102 | 0x3103 | 12546 | 12547 | MAG_3S_HAR_V_4th_a_% | Aggr 3sec Phase A 4th Voltage Magnitude Harmonics | float | 2 | R
0x3104 | 0x3105 | 12548 | 12549 | MAG_3S_HAR_V_4th_b_% | Aggr 3sec Phase B 4th Voltage Magnitude Harmonics | float | 2 | R
0x3106 | 0x3107 | 12550 | 12551 | MAG_3S_HAR_V_4th_c_% | Aggr 3sec Phase C 4th Voltage Magnitude Harmonics | float | 2 | R
0x3108 | 0x3109 | 12552 | 12553 | MAG_3S_HAR_I_4th_a_% | Aggr 3sec Phase A 4th Current Magnitude Harmonics | float | 2 | R
0x310A | 0x310B | 12554 | 12555 | MAG_3S_HAR_I_4th_b_% | Aggr 3sec Phase B 4th Current Magnitude Harmonics | float | 2 | R
0x310C | 0x310D | 12556 | 12557 | MAG_3S_HAR_I_4th_c_% | Aggr 3sec Phase C 4th Current Magnitude Harmonics | float | 2 | R
0x310E | 0x310F | 12558 | 12559 | MAG_3S_HAR_I_4th_n_% | Aggr 3sec Phase N 4th Current Magnitude Harmonics | float | 2 | R
0x3110 | 0x3111 | 12560 | 12561 | MAG_3S_HAR_V_5th_a_% | Aggr 3sec Phase A 5th Voltage Magnitude Harmonics | float | 2 | R
0x3112 | 0x3113 | 12562 | 12563 | MAG_3S_HAR_V_5th_b_% | Aggr 3sec Phase B 5th Voltage Magnitude Harmonics | float | 2 | R
0x3114 | 0x3115 | 12564 | 12565 | MAG_3S_HAR_V_5th_c_% | Aggr 3sec Phase C 5th Voltage Magnitude Harmonics | float | 2 | R
0x3116 | 0x3117 | 12566 | 12567 | MAG_3S_HAR_I_5th_a_% | Aggr 3sec Phase A 5th Current Magnitude Harmonics | float | 2 | R
0x3118 | 0x3119 | 12568 | 12569 | MAG_3S_HAR_I_5th_b_% | Aggr 3sec Phase B 5th Current Magnitude Harmonics | float | 2 | R
0x311A | 0x311B | 12570 | 12571 | MAG_3S_HAR_I_5th_c_% | Aggr 3sec Phase C 5th Current Magnitude Harmonics | float | 2 | R
0x311C | 0x311D | 12572 | 12573 | MAG_3S_HAR_I_5th_n_% | Aggr 3sec Phase N 5th Current Magnitude Harmonics | float | 2 | R
0x311E | 0x311F | 12574 | 12575 | MAG_3S_HAR_V_6th_a_% | Aggr 3sec Phase A 6th Voltage Magnitude Harmonics | float | 2 | R
0x3120 | 0x3121 | 12576 | 12577 | MAG_3S_HAR_V_6th_b_% | Aggr 3sec Phase B 6th Voltage Magnitude Harmonics | float | 2 | R
0x3122 | 0x3123 | 12578 | 12579 | MAG_3S_HAR_V_6th_c_% | Aggr 3sec Phase C 6th Voltage Magnitude Harmonics | float | 2 | R
0x3124 | 0x3125 | 12580 | 12581 | MAG_3S_HAR_I_6th_a_% | Aggr 3sec Phase A 6th Current Magnitude Harmonics | float | 2 | R
0x3126 | 0x3127 | 12582 | 12583 | MAG_3S_HAR_I_6th_b_% | Aggr 3sec Phase B 6th Current Magnitude Harmonics | float | 2 | R
0x3128 | 0x3129 | 12584 | 12585 | MAG_3S_HAR_I_6th_c_% | Aggr 3sec Phase C 6th Current Magnitude Harmonics | float | 2 | R
0x312A | 0x312B | 12586 | 12587 | MAG_3S_HAR_I_6th_n_% | Aggr 3sec Phase N 6th Current Magnitude Harmonics | float | 2 | R
0x312C | 0x312D | 12588 | 12589 | MAG_3S_HAR_V_7th_a_% | Aggr 3sec Phase A 7th Voltage Magnitude Harmonics | float | 2 | R
0x312E | 0x312F | 12590 | 12591 | MAG_3S_HAR_V_7th_b_% | Aggr 3sec Phase B 7th Voltage Magnitude Harmonics | float | 2 | R
0x3130 | 0x3131 | 12592 | 12593 | MAG_3S_HAR_V_7th_c_% | Aggr 3sec Phase C 7th Voltage Magnitude Harmonics | float | 2 | R
0x3132 | 0x3133 | 12594 | 12595 | MAG_3S_HAR_I_7th_a_% | Aggr 3sec Phase A 7th Current Magnitude Harmonics | float | 2 | R
0x3134 | 0x3135 | 12596 | 12597 | MAG_3S_HAR_I_7th_b_% | Aggr 3sec Phase B 7th Current Magnitude Harmonics | float | 2 | R
0x3136 | 0x3137 | 12598 | 12599 | MAG_3S_HAR_I_7th_c_% | Aggr 3sec Phase C 7th Current Magnitude Harmonics | float | 2 | R
0x3138 | 0x3139 | 12600 | 12601 | MAG_3S_HAR_I_7th_n_% | Aggr 3sec Phase N 7th Current Magnitude Harmonics | float | 2 | R
0x313A | 0x313B | 12602 | 12603 | MAG_3S_HAR_V_8th_a_% | Aggr 3sec Phase A 8th Voltage Magnitude Harmonics | float | 2 | R
0x313C | 0x313D | 12604 | 12605 | MAG_3S_HAR_V_8th_b_% | Aggr 3sec Phase B 8th Voltage Magnitude Harmonics | float | 2 | R
0x313E | 0x313F | 12606 | 12607 | MAG_3S_HAR_V_8th_c_% | Aggr 3sec Phase C 8th Voltage Magnitude Harmonics | float | 2 | R
0x3140 | 0x3141 | 12608 | 12609 | MAG_3S_HAR_I_8th_a_% | Aggr 3sec Phase A 8th Current Magnitude Harmonics | float | 2 | R
0x3142 | 0x3143 | 12610 | 12611 | MAG_3S_HAR_I_8th_b_% | Aggr 3sec Phase B 8th Current Magnitude Harmonics | float | 2 | R
0x3144 | 0x3145 | 12612 | 12613 | MAG_3S_HAR_I_8th_c_% | Aggr 3sec Phase C 8th Current Magnitude Harmonics | float | 2 | R
0x3146 | 0x3147 | 12614 | 12615 | MAG_3S_HAR_I_8th_n_% | Aggr 3sec Phase N 8th Current Magnitude Harmonics | float | 2 | R
0x3148 | 0x3149 | 12616 | 12617 | MAG_3S_HAR_V_9th_a_% | Aggr 3sec Phase A 9th Voltage Magnitude Harmonics | float | 2 | R
0x314A | 0x314B | 12618 | 12619 | MAG_3S_HAR_V_9th_b_% | Aggr 3sec Phase B 9th Voltage Magnitude Harmonics | float | 2 | R
0x314C | 0x314D | 12620 | 12621 | MAG_3S_HAR_V_9th_c_% | Aggr 3sec Phase C 9th Voltage Magnitude Harmonics | float | 2 | R
0x314E | 0x314F | 12622 | 12623 | MAG_3S_HAR_I_9th_a_% | Aggr 3sec Phase A 9th Current Magnitude Harmonics | float | 2 | R
0x3150 | 0x3151 | 12624 | 12625 | MAG_3S_HAR_I_9th_b_% | Aggr 3sec Phase B 9th Current Magnitude Harmonics | float | 2 | R
0x3152 | 0x3153 | 12626 | 12627 | MAG_3S_HAR_I_9th_c_% | Aggr 3sec Phase C 9th Current Magnitude Harmonics | float | 2 | R
0x3154 | 0x3155 | 12628 | 12629 | MAG_3S_HAR_I_9th_n_% | Aggr 3sec Phase N 9th Current Magnitude Harmonics | float | 2 | R
0x3156 | 0x3157 | 12630 | 12631 | MAG_3S_HAR_V_10th_a_% | Aggr 3sec Phase A 10th Voltage Magnitude Harmonics | float | 2 | R
0x3158 | 0x3159 | 12632 | 12633 | MAG_3S_HAR_V_10th_b_% | Aggr 3sec Phase B 10th Voltage Magnitude Harmonics | float | 2 | R
0x315A | 0x315B | 12634 | 12635 | MAG_3S_HAR_V_10th_c_% | Aggr 3sec Phase C 10th Voltage Magnitude Harmonics | float | 2 | R
0x315C | 0x315D | 12636 | 12637 | MAG_3S_HAR_I_10th_a_% | Aggr 3sec Phase A 10th Current Magnitude Harmonics | float | 2 | R
0x315E | 0x315F | 12638 | 12639 | MAG_3S_HAR_I_10th_b_% | Aggr 3sec Phase B 10th Current Magnitude Harmonics | float | 2 | R
0x3160 | 0x3161 | 12640 | 12641 | MAG_3S_HAR_I_10th_c_% | Aggr 3sec Phase C 10th Current Magnitude Harmonics | float | 2 | R
0x3162 | 0x3163 | 12642 | 12643 | MAG_3S_HAR_I_10th_n_% | Aggr 3sec Phase N 10th Current Magnitude Harmonics | float | 2 | R
0x3164 | 0x3165 | 12644 | 12645 | MAG_3S_HAR_V_11th_a_% | Aggr 3sec Phase A 11st Voltage Magnitude Harmonics | float | 2 | R
0x3166 | 0x3167 | 12646 | 12647 | MAG_3S_HAR_V_11th_b_% | Aggr 3sec Phase B 11st Voltage Magnitude Harmonics | float | 2 | R
0x3168 | 0x3169 | 12648 | 12649 | MAG_3S_HAR_V_11th_c_% | Aggr 3sec Phase C 11st Voltage Magnitude Harmonics | float | 2 | R
0x316A | 0x316B | 12650 | 12651 | MAG_3S_HAR_I_11th_a_% | Aggr 3sec Phase A 11st Current Magnitude Harmonics | float | 2 | R
0x316C | 0x316D | 12652 | 12653 | MAG_3S_HAR_I_11th_b_% | Aggr 3sec Phase B 11st Current Magnitude Harmonics | float | 2 | R
0x316E | 0x316F | 12654 | 12655 | MAG_3S_HAR_I_11th_c_% | Aggr 3sec Phase C 11st Current Magnitude Harmonics | float | 2 | R
0x3170 | 0x3171 | 12656 | 12657 | MAG_3S_HAR_I_11th_n_% | Aggr 3sec Phase N 11st Current Magnitude Harmonics | float | 2 | R
0x3172 | 0x3173 | 12658 | 12659 | MAG_3S_HAR_V_12th_a_% | Aggr 3sec Phase A 12nd Voltage Magnitude Harmonics | float | 2 | R
0x3174 | 0x3175 | 12660 | 12661 | MAG_3S_HAR_V_12th_b_% | Aggr 3sec Phase B 12nd Voltage Magnitude Harmonics | float | 2 | R
0x3176 | 0x3177 | 12662 | 12663 | MAG_3S_HAR_V_12th_c_% | Aggr 3sec Phase C 12nd Voltage Magnitude Harmonics | float | 2 | R
0x3178 | 0x3179 | 12664 | 12665 | MAG_3S_HAR_I_12th_a_% | Aggr 3sec Phase A 12nd Current Magnitude Harmonics | float | 2 | R
0x317A | 0x317B | 12666 | 12667 | MAG_3S_HAR_I_12th_b_% | Aggr 3sec Phase B 12nd Current Magnitude Harmonics | float | 2 | R
0x317C | 0x317D | 12668 | 12669 | MAG_3S_HAR_I_12th_c_% | Aggr 3sec Phase C 12nd Current Magnitude Harmonics | float | 2 | R
0x317E | 0x317F | 12670 | 12671 | MAG_3S_HAR_I_12th_n_% | Aggr 3sec Phase N 12nd Current Magnitude Harmonics | float | 2 | R
0x3180 | 0x3181 | 12672 | 12673 | MAG_3S_HAR_V_13th_a_% | Aggr 3sec Phase A 13rd Voltage Magnitude Harmonics | float | 2 | R
0x3182 | 0x3183 | 12674 | 12675 | MAG_3S_HAR_V_13th_b_% | Aggr 3sec Phase B 13rd Voltage Magnitude Harmonics | float | 2 | R
0x3184 | 0x3185 | 12676 | 12677 | MAG_3S_HAR_V_13th_c_% | Aggr 3sec Phase C 13rd Voltage Magnitude Harmonics | float | 2 | R
0x3186 | 0x3187 | 12678 | 12679 | MAG_3S_HAR_I_13th_a_% | Aggr 3sec Phase A 13rd Current Magnitude Harmonics | float | 2 | R
0x3188 | 0x3189 | 12680 | 12681 | MAG_3S_HAR_I_13th_b_% | Aggr 3sec Phase B 13rd Current Magnitude Harmonics | float | 2 | R
0x318A | 0x318B | 12682 | 12683 | MAG_3S_HAR_I_13th_c_% | Aggr 3sec Phase C 13rd Current Magnitude Harmonics | float | 2 | R
0x318C | 0x318D | 12684 | 12685 | MAG_3S_HAR_I_13th_n_% | Aggr 3sec Phase N 13rd Current Magnitude Harmonics | float | 2 | R
0x318E | 0x318F | 12686 | 12687 | MAG_3S_HAR_V_14th_a_% | Aggr 3sec Phase A 14th Voltage Magnitude Harmonics | float | 2 | R
0x3190 | 0x3191 | 12688 | 12689 | MAG_3S_HAR_V_14th_b_% | Aggr 3sec Phase B 14th Voltage Magnitude Harmonics | float | 2 | R
0x3192 | 0x3193 | 12690 | 12691 | MAG_3S_HAR_V_14th_c_% | Aggr 3sec Phase C 14th Voltage Magnitude Harmonics | float | 2 | R
0x3194 | 0x3195 | 12692 | 12693 | MAG_3S_HAR_I_14th_a_% | Aggr 3sec Phase A 14th Current Magnitude Harmonics | float | 2 | R
0x3196 | 0x3197 | 12694 | 12695 | MAG_3S_HAR_I_14th_b_% | Aggr 3sec Phase B 14th Current Magnitude Harmonics | float | 2 | R
0x3198 | 0x3199 | 12696 | 12697 | MAG_3S_HAR_I_14th_c_% | Aggr 3sec Phase C 14th Current Magnitude Harmonics | float | 2 | R
0x319A | 0x319B | 12698 | 12699 | MAG_3S_HAR_I_14th_n_% | Aggr 3sec Phase N 14th Current Magnitude Harmonics | float | 2 | R
0x319C | 0x319D | 12700 | 12701 | MAG_3S_HAR_V_15th_a_% | Aggr 3sec Phase A 15th Voltage Magnitude Harmonics | float | 2 | R
0x319E | 0x319F | 12702 | 12703 | MAG_3S_HAR_V_15th_b_% | Aggr 3sec Phase B 15th Voltage Magnitude Harmonics | float | 2 | R
0x31A0 | 0x31A1 | 12704 | 12705 | MAG_3S_HAR_V_15th_c_% | Aggr 3sec Phase C 15th Voltage Magnitude Harmonics | float | 2 | R
0x31A2 | 0x31A3 | 12706 | 12707 | MAG_3S_HAR_I_15th_a_% | Aggr 3sec Phase A 15th Current Magnitude Harmonics | float | 2 | R
0x31A4 | 0x31A5 | 12708 | 12709 | MAG_3S_HAR_I_15th_b_% | Aggr 3sec Phase B 15th Current Magnitude Harmonics | float | 2 | R
0x31A6 | 0x31A7 | 12710 | 12711 | MAG_3S_HAR_I_15th_c_% | Aggr 3sec Phase C 15th Current Magnitude Harmonics | float | 2 | R
0x31A8 | 0x31A9 | 12712 | 12713 | MAG_3S_HAR_I_15th_n_% | Aggr 3sec Phase N 15th Current Magnitude Harmonics | float | 2 | R
0x31AA | 0x31AB | 12714 | 12715 | MAG_3S_HAR_V_16th_a_% | Aggr 3sec Phase A 16th Voltage Magnitude Harmonics | float | 2 | R
0x31AC | 0x31AD | 12716 | 12717 | MAG_3S_HAR_V_16th_b_% | Aggr 3sec Phase B 16th Voltage Magnitude Harmonics | float | 2 | R
0x31AE | 0x31AF | 12718 | 12719 | MAG_3S_HAR_V_16th_c_% | Aggr 3sec Phase C 16th Voltage Magnitude Harmonics | float | 2 | R
0x31B0 | 0x31B1 | 12720 | 12721 | MAG_3S_HAR_I_16th_a_% | Aggr 3sec Phase A 16th Current Magnitude Harmonics | float | 2 | R
0x31B2 | 0x31B3 | 12722 | 12723 | MAG_3S_HAR_I_16th_b_% | Aggr 3sec Phase B 16th Current Magnitude Harmonics | float | 2 | R
0x31B4 | 0x31B5 | 12724 | 12725 | MAG_3S_HAR_I_16th_c_% | Aggr 3sec Phase C 16th Current Magnitude Harmonics | float | 2 | R
0x31B6 | 0x31B7 | 12726 | 12727 | MAG_3S_HAR_I_16th_n_% | Aggr 3sec Phase N 16th Current Magnitude Harmonics | float | 2 | R
0x31B8 | 0x31B9 | 12728 | 12729 | MAG_3S_HAR_V_17th_a_% | Aggr 3sec Phase A 17th Voltage Magnitude Harmonics | float | 2 | R
0x31BA | 0x31BB | 12730 | 12731 | MAG_3S_HAR_V_17th_b_% | Aggr 3sec Phase B 17th Voltage Magnitude Harmonics | float | 2 | R
0x31BC | 0x31BD | 12732 | 12733 | MAG_3S_HAR_V_17th_c_% | Aggr 3sec Phase C 17th Voltage Magnitude Harmonics | float | 2 | R
0x31BE | 0x31BF | 12734 | 12735 | MAG_3S_HAR_I_17th_a_% | Aggr 3sec Phase A 17th Current Magnitude Harmonics | float | 2 | R
0x31C0 | 0x31C1 | 12736 | 12737 | MAG_3S_HAR_I_17th_b_% | Aggr 3sec Phase B 17th Current Magnitude Harmonics | float | 2 | R
0x31C2 | 0x31C3 | 12738 | 12739 | MAG_3S_HAR_I_17th_c_% | Aggr 3sec Phase C 17th Current Magnitude Harmonics | float | 2 | R
0x31C4 | 0x31C5 | 12740 | 12741 | MAG_3S_HAR_I_17th_n_% | Aggr 3sec Phase N 17th Current Magnitude Harmonics | float | 2 | R
0x31C6 | 0x31C7 | 12742 | 12743 | MAG_3S_HAR_V_18th_a_% | Aggr 3sec Phase A 18th Voltage Magnitude Harmonics | float | 2 | R
0x31C8 | 0x31C9 | 12744 | 12745 | MAG_3S_HAR_V_18th_b_% | Aggr 3sec Phase B 18th Voltage Magnitude Harmonics | float | 2 | R
0x31CA | 0x31CB | 12746 | 12747 | MAG_3S_HAR_V_18th_c_% | Aggr 3sec Phase C 18th Voltage Magnitude Harmonics | float | 2 | R
0x31CC | 0x31CD | 12748 | 12749 | MAG_3S_HAR_I_18th_a_% | Aggr 3sec Phase A 18th Current Magnitude Harmonics | float | 2 | R
0x31CE | 0x31CF | 12750 | 12751 | MAG_3S_HAR_I_18th_b_% | Aggr 3sec Phase B 18th Current Magnitude Harmonics | float | 2 | R
0x31D0 | 0x31D1 | 12752 | 12753 | MAG_3S_HAR_I_18th_c_% | Aggr 3sec Phase C 18th Current Magnitude Harmonics | float | 2 | R
0x31D2 | 0x31D3 | 12754 | 12755 | MAG_3S_HAR_I_18th_n_% | Aggr 3sec Phase N 18th Current Magnitude Harmonics | float | 2 | R
0x31D4 | 0x31D5 | 12756 | 12757 | MAG_3S_HAR_V_19th_a_% | Aggr 3sec Phase A 19th Voltage Magnitude Harmonics | float | 2 | R
0x31D6 | 0x31D7 | 12758 | 12759 | MAG_3S_HAR_V_19th_b_% | Aggr 3sec Phase B 19th Voltage Magnitude Harmonics | float | 2 | R
0x31D8 | 0x31D9 | 12760 | 12761 | MAG_3S_HAR_V_19th_c_% | Aggr 3sec Phase C 19th Voltage Magnitude Harmonics | float | 2 | R
0x31DA | 0x31DB | 12762 | 12763 | MAG_3S_HAR_I_19th_a_% | Aggr 3sec Phase A 19th Current Magnitude Harmonics | float | 2 | R
0x31DC | 0x31DD | 12764 | 12765 | MAG_3S_HAR_I_19th_b_% | Aggr 3sec Phase B 19th Current Magnitude Harmonics | float | 2 | R
0x31DE | 0x31DF | 12766 | 12767 | MAG_3S_HAR_I_19th_c_% | Aggr 3sec Phase C 19th Current Magnitude Harmonics | float | 2 | R
0x31E0 | 0x31E1 | 12768 | 12769 | MAG_3S_HAR_I_19th_n_% | Aggr 3sec Phase N 19th Current Magnitude Harmonics | float | 2 | R
0x31E2 | 0x31E3 | 12770 | 12771 | MAG_3S_HAR_V_20th_a_% | Aggr 3sec Phase A 20th Voltage Magnitude Harmonics | float | 2 | R
0x31E4 | 0x31E5 | 12772 | 12773 | MAG_3S_HAR_V_20th_b_% | Aggr 3sec Phase B 20th Voltage Magnitude Harmonics | float | 2 | R
0x31E6 | 0x31E7 | 12774 | 12775 | MAG_3S_HAR_V_20th_c_% | Aggr 3sec Phase C 20th Voltage Magnitude Harmonics | float | 2 | R
0x31E8 | 0x31E9 | 12776 | 12777 | MAG_3S_HAR_I_20th_a_% | Aggr 3sec Phase A 20th Current Magnitude Harmonics | float | 2 | R
0x31EA | 0x31EB | 12778 | 12779 | MAG_3S_HAR_I_20th_b_% | Aggr 3sec Phase B 20th Current Magnitude Harmonics | float | 2 | R
0x31EC | 0x31ED | 12780 | 12781 | MAG_3S_HAR_I_20th_c_% | Aggr 3sec Phase C 20th Current Magnitude Harmonics | float | 2 | R
0x31EE | 0x31EF | 12782 | 12783 | MAG_3S_HAR_I_20th_n_% | Aggr 3sec Phase N 20th Current Magnitude Harmonics | float | 2 | R
0x31F0 | 0x31F1 | 12784 | 12785 | MAG_3S_HAR_V_21th_a_% | Aggr 3sec Phase A 21st Voltage Magnitude Harmonics | float | 2 | R
0x31F2 | 0x31F3 | 12786 | 12787 | MAG_3S_HAR_V_21th_b_% | Aggr 3sec Phase B 21st Voltage Magnitude Harmonics | float | 2 | R
0x31F4 | 0x31F5 | 12788 | 12789 | MAG_3S_HAR_V_21th_c_% | Aggr 3sec Phase C 21st Voltage Magnitude Harmonics | float | 2 | R
0x31F6 | 0x31F7 | 12790 | 12791 | MAG_3S_HAR_I_21th_a_% | Aggr 3sec Phase A 21st Current Magnitude Harmonics | float | 2 | R
0x31F8 | 0x31F9 | 12792 | 12793 | MAG_3S_HAR_I_21th_b_% | Aggr 3sec Phase B 21st Current Magnitude Harmonics | float | 2 | R
0x31FA | 0x31FB | 12794 | 12795 | MAG_3S_HAR_I_21th_c_% | Aggr 3sec Phase C 21st Current Magnitude Harmonics | float | 2 | R
0x31FC | 0x31FD | 12796 | 12797 | MAG_3S_HAR_I_21th_n_% | Aggr 3sec Phase N 21st Current Magnitude Harmonics | float | 2 | R
0x31FE | 0x31FF | 12798 | 12799 | MAG_3S_HAR_V_22th_a_% | Aggr 3sec Phase A 22nd Voltage Magnitude Harmonics | float | 2 | R
0x3200 | 0x3201 | 12800 | 12801 | MAG_3S_HAR_V_22th_b_% | Aggr 3sec Phase B 22nd Voltage Magnitude Harmonics | float | 2 | R
0x3202 | 0x3203 | 12802 | 12803 | MAG_3S_HAR_V_22th_c_% | Aggr 3sec Phase C 22nd Voltage Magnitude Harmonics | float | 2 | R
0x3204 | 0x3205 | 12804 | 12805 | MAG_3S_HAR_I_22th_a_% | Aggr 3sec Phase A 22nd Current Magnitude Harmonics | float | 2 | R
0x3206 | 0x3207 | 12806 | 12807 | MAG_3S_HAR_I_22th_b_% | Aggr 3sec Phase B 22nd Current Magnitude Harmonics | float | 2 | R
0x3208 | 0x3209 | 12808 | 12809 | MAG_3S_HAR_I_22th_c_% | Aggr 3sec Phase C 22nd Current Magnitude Harmonics | float | 2 | R
0x320A | 0x320B | 12810 | 12811 | MAG_3S_HAR_I_22th_n_% | Aggr 3sec Phase N 22nd Current Magnitude Harmonics | float | 2 | R
0x320C | 0x320D | 12812 | 12813 | MAG_3S_HAR_V_23th_a_% | Aggr 3sec Phase A 23rd Voltage Magnitude Harmonics | float | 2 | R
0x320E | 0x320F | 12814 | 12815 | MAG_3S_HAR_V_23th_b_% | Aggr 3sec Phase B 23rd Voltage Magnitude Harmonics | float | 2 | R
0x3210 | 0x3211 | 12816 | 12817 | MAG_3S_HAR_V_23th_c_% | Aggr 3sec Phase C 23rd Voltage Magnitude Harmonics | float | 2 | R
0x3212 | 0x3213 | 12818 | 12819 | MAG_3S_HAR_I_23th_a_% | Aggr 3sec Phase A 23rd Current Magnitude Harmonics | float | 2 | R
0x3214 | 0x3215 | 12820 | 12821 | MAG_3S_HAR_I_23th_b_% | Aggr 3sec Phase B 23rd Current Magnitude Harmonics | float | 2 | R
0x3216 | 0x3217 | 12822 | 12823 | MAG_3S_HAR_I_23th_c_% | Aggr 3sec Phase C 23rd Current Magnitude Harmonics | float | 2 | R
0x3218 | 0x3219 | 12824 | 12825 | MAG_3S_HAR_I_23th_n_% | Aggr 3sec Phase N 23rd Current Magnitude Harmonics | float | 2 | R
0x321A | 0x321B | 12826 | 12827 | MAG_3S_HAR_V_24th_a_% | Aggr 3sec Phase A 24th Voltage Magnitude Harmonics | float | 2 | R
0x321C | 0x321D | 12828 | 12829 | MAG_3S_HAR_V_24th_b_% | Aggr 3sec Phase B 24th Voltage Magnitude Harmonics | float | 2 | R
0x321E | 0x321F | 12830 | 12831 | MAG_3S_HAR_V_24th_c_% | Aggr 3sec Phase C 24th Voltage Magnitude Harmonics | float | 2 | R
0x3220 | 0x3221 | 12832 | 12833 | MAG_3S_HAR_I_24th_a_% | Aggr 3sec Phase A 24th Current Magnitude Harmonics | float | 2 | R
0x3222 | 0x3223 | 12834 | 12835 | MAG_3S_HAR_I_24th_b_% | Aggr 3sec Phase B 24th Current Magnitude Harmonics | float | 2 | R
0x3224 | 0x3225 | 12836 | 12837 | MAG_3S_HAR_I_24th_c_% | Aggr 3sec Phase C 24th Current Magnitude Harmonics | float | 2 | R
0x3226 | 0x3227 | 12838 | 12839 | MAG_3S_HAR_I_24th_n_% | Aggr 3sec Phase N 24th Current Magnitude Harmonics | float | 2 | R
0x3228 | 0x3229 | 12840 | 12841 | MAG_3S_HAR_V_25th_a_% | Aggr 3sec Phase A 25th Voltage Magnitude Harmonics | float | 2 | R
0x322A | 0x322B | 12842 | 12843 | MAG_3S_HAR_V_25th_b_% | Aggr 3sec Phase B 25th Voltage Magnitude Harmonics | float | 2 | R
0x322C | 0x322D | 12844 | 12845 | MAG_3S_HAR_V_25th_c_% | Aggr 3sec Phase C 25th Voltage Magnitude Harmonics | float | 2 | R
0x322E | 0x322F | 12846 | 12847 | MAG_3S_HAR_I_25th_a_% | Aggr 3sec Phase A 25th Current Magnitude Harmonics | float | 2 | R
0x3230 | 0x3231 | 12848 | 12849 | MAG_3S_HAR_I_25th_b_% | Aggr 3sec Phase B 25th Current Magnitude Harmonics | float | 2 | R
0x3232 | 0x3233 | 12850 | 12851 | MAG_3S_HAR_I_25th_c_% | Aggr 3sec Phase C 25th Current Magnitude Harmonics | float | 2 | R
0x3234 | 0x3235 | 12852 | 12853 | MAG_3S_HAR_I_25th_n_% | Aggr 3sec Phase N 25th Current Magnitude Harmonics | float | 2 | R
0x3236 | 0x3237 | 12854 | 12855 | MAG_3S_HAR_V_26th_a_% | Aggr 3sec Phase A 26th Voltage Magnitude Harmonics | float | 2 | R
0x3238 | 0x3239 | 12856 | 12857 | MAG_3S_HAR_V_26th_b_% | Aggr 3sec Phase B 26th Voltage Magnitude Harmonics | float | 2 | R
0x323A | 0x323B | 12858 | 12859 | MAG_3S_HAR_V_26th_c_% | Aggr 3sec Phase C 26th Voltage Magnitude Harmonics | float | 2 | R
0x323C | 0x323D | 12860 | 12861 | MAG_3S_HAR_I_26th_a_% | Aggr 3sec Phase A 26th Current Magnitude Harmonics | float | 2 | R
0x323E | 0x323F | 12862 | 12863 | MAG_3S_HAR_I_26th_b_% | Aggr 3sec Phase B 26th Current Magnitude Harmonics | float | 2 | R
0x3240 | 0x3241 | 12864 | 12865 | MAG_3S_HAR_I_26th_c_% | Aggr 3sec Phase C 26th Current Magnitude Harmonics | float | 2 | R
0x3242 | 0x3243 | 12866 | 12867 | MAG_3S_HAR_I_26th_n_% | Aggr 3sec Phase N 26th Current Magnitude Harmonics | float | 2 | R
0x3244 | 0x3245 | 12868 | 12869 | MAG_3S_HAR_V_27th_a_% | Aggr 3sec Phase A 27th Voltage Magnitude Harmonics | float | 2 | R
0x3246 | 0x3247 | 12870 | 12871 | MAG_3S_HAR_V_27th_b_% | Aggr 3sec Phase B 27th Voltage Magnitude Harmonics | float | 2 | R
0x3248 | 0x3249 | 12872 | 12873 | MAG_3S_HAR_V_27th_c_% | Aggr 3sec Phase C 27th Voltage Magnitude Harmonics | float | 2 | R
0x324A | 0x324B | 12874 | 12875 | MAG_3S_HAR_I_27th_a_% | Aggr 3sec Phase A 27th Current Magnitude Harmonics | float | 2 | R
0x324C | 0x324D | 12876 | 12877 | MAG_3S_HAR_I_27th_b_% | Aggr 3sec Phase B 27th Current Magnitude Harmonics | float | 2 | R
0x324E | 0x324F | 12878 | 12879 | MAG_3S_HAR_I_27th_c_% | Aggr 3sec Phase C 27th Current Magnitude Harmonics | float | 2 | R
0x3250 | 0x3251 | 12880 | 12881 | MAG_3S_HAR_I_27th_n_% | Aggr 3sec Phase N 27th Current Magnitude Harmonics | float | 2 | R
0x3252 | 0x3253 | 12882 | 12883 | MAG_3S_HAR_V_28th_a_% | Aggr 3sec Phase A 28th Voltage Magnitude Harmonics | float | 2 | R
0x3254 | 0x3255 | 12884 | 12885 | MAG_3S_HAR_V_28th_b_% | Aggr 3sec Phase B 28th Voltage Magnitude Harmonics | float | 2 | R
0x3256 | 0x3257 | 12886 | 12887 | MAG_3S_HAR_V_28th_c_% | Aggr 3sec Phase C 28th Voltage Magnitude Harmonics | float | 2 | R
0x3258 | 0x3259 | 12888 | 12889 | MAG_3S_HAR_I_28th_a_% | Aggr 3sec Phase A 28th Current Magnitude Harmonics | float | 2 | R
0x325A | 0x325B | 12890 | 12891 | MAG_3S_HAR_I_28th_b_% | Aggr 3sec Phase B 28th Current Magnitude Harmonics | float | 2 | R
0x325C | 0x325D | 12892 | 12893 | MAG_3S_HAR_I_28th_c_% | Aggr 3sec Phase C 28th Current Magnitude Harmonics | float | 2 | R
0x325E | 0x325F | 12894 | 12895 | MAG_3S_HAR_I_28th_n_% | Aggr 3sec Phase N 28th Current Magnitude Harmonics | float | 2 | R
0x3260 | 0x3261 | 12896 | 12897 | MAG_3S_HAR_V_29th_a_% | Aggr 3sec Phase A 29th Voltage Magnitude Harmonics | float | 2 | R
0x3262 | 0x3263 | 12898 | 12899 | MAG_3S_HAR_V_29th_b_% | Aggr 3sec Phase B 29th Voltage Magnitude Harmonics | float | 2 | R
0x3264 | 0x3265 | 12900 | 12901 | MAG_3S_HAR_V_29th_c_% | Aggr 3sec Phase C 29th Voltage Magnitude Harmonics | float | 2 | R
0x3266 | 0x3267 | 12902 | 12903 | MAG_3S_HAR_I_29th_a_% | Aggr 3sec Phase A 29th Current Magnitude Harmonics | float | 2 | R
0x3268 | 0x3269 | 12904 | 12905 | MAG_3S_HAR_I_29th_b_% | Aggr 3sec Phase B 29th Current Magnitude Harmonics | float | 2 | R
0x326A | 0x326B | 12906 | 12907 | MAG_3S_HAR_I_29th_c_% | Aggr 3sec Phase C 29th Current Magnitude Harmonics | float | 2 | R
0x326C | 0x326D | 12908 | 12909 | MAG_3S_HAR_I_29th_n_% | Aggr 3sec Phase N 29th Current Magnitude Harmonics | float | 2 | R
0x326E | 0x326F | 12910 | 12911 | MAG_3S_HAR_V_30th_a_% | Aggr 3sec Phase A 30th Voltage Magnitude Harmonics | float | 2 | R
0x3270 | 0x3271 | 12912 | 12913 | MAG_3S_HAR_V_30th_b_% | Aggr 3sec Phase B 30th Voltage Magnitude Harmonics | float | 2 | R
0x3272 | 0x3273 | 12914 | 12915 | MAG_3S_HAR_V_30th_c_% | Aggr 3sec Phase C 30th Voltage Magnitude Harmonics | float | 2 | R
0x3274 | 0x3275 | 12916 | 12917 | MAG_3S_HAR_I_30th_a_% | Aggr 3sec Phase A 30th Current Magnitude Harmonics | float | 2 | R
0x3276 | 0x3277 | 12918 | 12919 | MAG_3S_HAR_I_30th_b_% | Aggr 3sec Phase B 30th Current Magnitude Harmonics | float | 2 | R
0x3278 | 0x3279 | 12920 | 12921 | MAG_3S_HAR_I_30th_c_% | Aggr 3sec Phase C 30th Current Magnitude Harmonics | float | 2 | R
0x327A | 0x327B | 12922 | 12923 | MAG_3S_HAR_I_30th_n_% | Aggr 3sec Phase N 30th Current Magnitude Harmonics | float | 2 | R
0x327C | 0x327D | 12924 | 12925 | MAG_3S_HAR_V_31th_a_% | Aggr 3sec Phase A 31st Voltage Magnitude Harmonics | float | 2 | R
0x327E | 0x327F | 12926 | 12927 | MAG_3S_HAR_V_31th_b_% | Aggr 3sec Phase B 31st Voltage Magnitude Harmonics | float | 2 | R
0x3280 | 0x3281 | 12928 | 12929 | MAG_3S_HAR_V_31th_c_% | Aggr 3sec Phase C 31st Voltage Magnitude Harmonics | float | 2 | R
0x3282 | 0x3283 | 12930 | 12931 | MAG_3S_HAR_I_31th_a_% | Aggr 3sec Phase A 31st Current Magnitude Harmonics | float | 2 | R
0x3284 | 0x3285 | 12932 | 12933 | MAG_3S_HAR_I_31th_b_% | Aggr 3sec Phase B 31st Current Magnitude Harmonics | float | 2 | R
0x3286 | 0x3287 | 12934 | 12935 | MAG_3S_HAR_I_31th_c_% | Aggr 3sec Phase C 31st Current Magnitude Harmonics | float | 2 | R
0x3288 | 0x3289 | 12936 | 12937 | MAG_3S_HAR_I_31th_n_% | Aggr 3sec Phase N 31st Current Magnitude Harmonics | float | 2 | R
0x328A | 0x328B | 12938 | 12939 | MAG_3S_HAR_V_32th_a_% | Aggr 3sec Phase A 32nd Voltage Magnitude Harmonics | float | 2 | R
0x328C | 0x328D | 12940 | 12941 | MAG_3S_HAR_V_32th_b_% | Aggr 3sec Phase B 32nd Voltage Magnitude Harmonics | float | 2 | R
0x328E | 0x328F | 12942 | 12943 | MAG_3S_HAR_V_32th_c_% | Aggr 3sec Phase C 32nd Voltage Magnitude Harmonics | float | 2 | R
0x3290 | 0x3291 | 12944 | 12945 | MAG_3S_HAR_I_32th_a_% | Aggr 3sec Phase A 32nd Current Magnitude Harmonics | float | 2 | R
0x3292 | 0x3293 | 12946 | 12947 | MAG_3S_HAR_I_32th_b_% | Aggr 3sec Phase B 32nd Current Magnitude Harmonics | float | 2 | R
0x3294 | 0x3295 | 12948 | 12949 | MAG_3S_HAR_I_32th_c_% | Aggr 3sec Phase C 32nd Current Magnitude Harmonics | float | 2 | R
0x3296 | 0x3297 | 12950 | 12951 | MAG_3S_HAR_I_32th_n_% | Aggr 3sec Phase N 32nd Current Magnitude Harmonics | float | 2 | R
0x3298 | 0x3299 | 12952 | 12953 | MAG_3S_HAR_V_33th_a_% | Aggr 3sec Phase A 33rd Voltage Magnitude Harmonics | float | 2 | R
0x329A | 0x329B | 12954 | 12955 | MAG_3S_HAR_V_33th_b_% | Aggr 3sec Phase B 33rd Voltage Magnitude Harmonics | float | 2 | R
0x329C | 0x329D | 12956 | 12957 | MAG_3S_HAR_V_33th_c_% | Aggr 3sec Phase C 33rd Voltage Magnitude Harmonics | float | 2 | R
0x329E | 0x329F | 12958 | 12959 | MAG_3S_HAR_I_33th_a_% | Aggr 3sec Phase A 33rd Current Magnitude Harmonics | float | 2 | R
0x32A0 | 0x32A1 | 12960 | 12961 | MAG_3S_HAR_I_33th_b_% | Aggr 3sec Phase B 33rd Current Magnitude Harmonics | float | 2 | R
0x32A2 | 0x32A3 | 12962 | 12963 | MAG_3S_HAR_I_33th_c_% | Aggr 3sec Phase C 33rd Current Magnitude Harmonics | float | 2 | R
0x32A4 | 0x32A5 | 12964 | 12965 | MAG_3S_HAR_I_33th_n_% | Aggr 3sec Phase N 33rd Current Magnitude Harmonics | float | 2 | R
0x32A6 | 0x32A7 | 12966 | 12967 | MAG_3S_HAR_V_34th_a_% | Aggr 3sec Phase A 34th Voltage Magnitude Harmonics | float | 2 | R
0x32A8 | 0x32A9 | 12968 | 12969 | MAG_3S_HAR_V_34th_b_% | Aggr 3sec Phase B 34th Voltage Magnitude Harmonics | float | 2 | R
0x32AA | 0x32AB | 12970 | 12971 | MAG_3S_HAR_V_34th_c_% | Aggr 3sec Phase C 34th Voltage Magnitude Harmonics | float | 2 | R
0x32AC | 0x32AD | 12972 | 12973 | MAG_3S_HAR_I_34th_a_% | Aggr 3sec Phase A 34th Current Magnitude Harmonics | float | 2 | R
0x32AE | 0x32AF | 12974 | 12975 | MAG_3S_HAR_I_34th_b_% | Aggr 3sec Phase B 34th Current Magnitude Harmonics | float | 2 | R
0x32B0 | 0x32B1 | 12976 | 12977 | MAG_3S_HAR_I_34th_c_% | Aggr 3sec Phase C 34th Current Magnitude Harmonics | float | 2 | R
0x32B2 | 0x32B3 | 12978 | 12979 | MAG_3S_HAR_I_34th_n_% | Aggr 3sec Phase N 34th Current Magnitude Harmonics | float | 2 | R
0x32B4 | 0x32B5 | 12980 | 12981 | MAG_3S_HAR_V_35th_a_% | Aggr 3sec Phase A 35th Voltage Magnitude Harmonics | float | 2 | R
0x32B6 | 0x32B7 | 12982 | 12983 | MAG_3S_HAR_V_35th_b_% | Aggr 3sec Phase B 35th Voltage Magnitude Harmonics | float | 2 | R
0x32B8 | 0x32B9 | 12984 | 12985 | MAG_3S_HAR_V_35th_c_% | Aggr 3sec Phase C 35th Voltage Magnitude Harmonics | float | 2 | R
0x32BA | 0x32BB | 12986 | 12987 | MAG_3S_HAR_I_35th_a_% | Aggr 3sec Phase A 35th Current Magnitude Harmonics | float | 2 | R
0x32BC | 0x32BD | 12988 | 12989 | MAG_3S_HAR_I_35th_b_% | Aggr 3sec Phase B 35th Current Magnitude Harmonics | float | 2 | R
0x32BE | 0x32BF | 12990 | 12991 | MAG_3S_HAR_I_35th_c_% | Aggr 3sec Phase C 35th Current Magnitude Harmonics | float | 2 | R
0x32C0 | 0x32C1 | 12992 | 12993 | MAG_3S_HAR_I_35th_n_% | Aggr 3sec Phase N 35th Current Magnitude Harmonics | float | 2 | R
0x32C2 | 0x32C3 | 12994 | 12995 | MAG_3S_HAR_V_36th_a_% | Aggr 3sec Phase A 36th Voltage Magnitude Harmonics | float | 2 | R
0x32C4 | 0x32C5 | 12996 | 12997 | MAG_3S_HAR_V_36th_b_% | Aggr 3sec Phase B 36th Voltage Magnitude Harmonics | float | 2 | R
0x32C6 | 0x32C7 | 12998 | 12999 | MAG_3S_HAR_V_36th_c_% | Aggr 3sec Phase C 36th Voltage Magnitude Harmonics | float | 2 | R
0x32C8 | 0x32C9 | 13000 | 13001 | MAG_3S_HAR_I_36th_a_% | Aggr 3sec Phase A 36th Current Magnitude Harmonics | float | 2 | R
0x32CA | 0x32CB | 13002 | 13003 | MAG_3S_HAR_I_36th_b_% | Aggr 3sec Phase B 36th Current Magnitude Harmonics | float | 2 | R
0x32CC | 0x32CD | 13004 | 13005 | MAG_3S_HAR_I_36th_c_% | Aggr 3sec Phase C 36th Current Magnitude Harmonics | float | 2 | R
0x32CE | 0x32CF | 13006 | 13007 | MAG_3S_HAR_I_36th_n_% | Aggr 3sec Phase N 36th Current Magnitude Harmonics | float | 2 | R
0x32D0 | 0x32D1 | 13008 | 13009 | MAG_3S_HAR_V_37th_a_% | Aggr 3sec Phase A 37th Voltage Magnitude Harmonics | float | 2 | R
0x32D2 | 0x32D3 | 13010 | 13011 | MAG_3S_HAR_V_37th_b_% | Aggr 3sec Phase B 37th Voltage Magnitude Harmonics | float | 2 | R
0x32D4 | 0x32D5 | 13012 | 13013 | MAG_3S_HAR_V_37th_c_% | Aggr 3sec Phase C 37th Voltage Magnitude Harmonics | float | 2 | R
0x32D6 | 0x32D7 | 13014 | 13015 | MAG_3S_HAR_I_37th_a_% | Aggr 3sec Phase A 37th Current Magnitude Harmonics | float | 2 | R
0x32D8 | 0x32D9 | 13016 | 13017 | MAG_3S_HAR_I_37th_b_% | Aggr 3sec Phase B 37th Current Magnitude Harmonics | float | 2 | R
0x32DA | 0x32DB | 13018 | 13019 | MAG_3S_HAR_I_37th_c_% | Aggr 3sec Phase C 37th Current Magnitude Harmonics | float | 2 | R
0x32DC | 0x32DD | 13020 | 13021 | MAG_3S_HAR_I_37th_n_% | Aggr 3sec Phase N 37th Current Magnitude Harmonics | float | 2 | R
0x32DE | 0x32DF | 13022 | 13023 | MAG_3S_HAR_V_38th_a_% | Aggr 3sec Phase A 38th Voltage Magnitude Harmonics | float | 2 | R
0x32E0 | 0x32E1 | 13024 | 13025 | MAG_3S_HAR_V_38th_b_% | Aggr 3sec Phase B 38th Voltage Magnitude Harmonics | float | 2 | R
0x32E2 | 0x32E3 | 13026 | 13027 | MAG_3S_HAR_V_38th_c_% | Aggr 3sec Phase C 38th Voltage Magnitude Harmonics | float | 2 | R
0x32E4 | 0x32E5 | 13028 | 13029 | MAG_3S_HAR_I_38th_a_% | Aggr 3sec Phase A 38th Current Magnitude Harmonics | float | 2 | R
0x32E6 | 0x32E7 | 13030 | 13031 | MAG_3S_HAR_I_38th_b_% | Aggr 3sec Phase B 38th Current Magnitude Harmonics | float | 2 | R
0x32E8 | 0x32E9 | 13032 | 13033 | MAG_3S_HAR_I_38th_c_% | Aggr 3sec Phase C 38th Current Magnitude Harmonics | float | 2 | R
0x32EA | 0x32EB | 13034 | 13035 | MAG_3S_HAR_I_38th_n_% | Aggr 3sec Phase N 38th Current Magnitude Harmonics | float | 2 | R
0x32EC | 0x32ED | 13036 | 13037 | MAG_3S_HAR_V_39th_a_% | Aggr 3sec Phase A 39th Voltage Magnitude Harmonics | float | 2 | R
0x32EE | 0x32EF | 13038 | 13039 | MAG_3S_HAR_V_39th_b_% | Aggr 3sec Phase B 39th Voltage Magnitude Harmonics | float | 2 | R
0x32F0 | 0x32F1 | 13040 | 13041 | MAG_3S_HAR_V_39th_c_% | Aggr 3sec Phase C 39th Voltage Magnitude Harmonics | float | 2 | R
0x32F2 | 0x32F3 | 13042 | 13043 | MAG_3S_HAR_I_39th_a_% | Aggr 3sec Phase A 39th Current Magnitude Harmonics | float | 2 | R
0x32F4 | 0x32F5 | 13044 | 13045 | MAG_3S_HAR_I_39th_b_% | Aggr 3sec Phase B 39th Current Magnitude Harmonics | float | 2 | R
0x32F6 | 0x32F7 | 13046 | 13047 | MAG_3S_HAR_I_39th_c_% | Aggr 3sec Phase C 39th Current Magnitude Harmonics | float | 2 | R
0x32F8 | 0x32F9 | 13048 | 13049 | MAG_3S_HAR_I_39th_n_% | Aggr 3sec Phase N 39th Current Magnitude Harmonics | float | 2 | R
0x32FA | 0x32FB | 13050 | 13051 | MAG_3S_HAR_V_40th_a_% | Aggr 3sec Phase A 40th Voltage Magnitude Harmonics | float | 2 | R
0x32FC | 0x32FD | 13052 | 13053 | MAG_3S_HAR_V_40th_b_% | Aggr 3sec Phase B 40th Voltage Magnitude Harmonics | float | 2 | R
0x32FE | 0x32FF | 13054 | 13055 | MAG_3S_HAR_V_40th_c_% | Aggr 3sec Phase C 40th Voltage Magnitude Harmonics | float | 2 | R
0x3300 | 0x3301 | 13056 | 13057 | MAG_3S_HAR_I_40th_a_% | Aggr 3sec Phase A 40th Current Magnitude Harmonics | float | 2 | R
0x3302 | 0x3303 | 13058 | 13059 | MAG_3S_HAR_I_40th_b_% | Aggr 3sec Phase B 40th Current Magnitude Harmonics | float | 2 | R
0x3304 | 0x3305 | 13060 | 13061 | MAG_3S_HAR_I_40th_c_% | Aggr 3sec Phase C 40th Current Magnitude Harmonics | float | 2 | R
0x3306 | 0x3307 | 13062 | 13063 | MAG_3S_HAR_I_40th_n_% | Aggr 3sec Phase N 40th Current Magnitude Harmonics | float | 2 | R
0x3308 | 0x3309 | 13064 | 13065 | MAG_3S_HAR_V_41th_a_% | Aggr 3sec Phase A 41st Voltage Magnitude Harmonics | float | 2 | R
0x330A | 0x330B | 13066 | 13067 | MAG_3S_HAR_V_41th_b_% | Aggr 3sec Phase B 41st Voltage Magnitude Harmonics | float | 2 | R
0x330C | 0x330D | 13068 | 13069 | MAG_3S_HAR_V_41th_c_% | Aggr 3sec Phase C 41st Voltage Magnitude Harmonics | float | 2 | R
0x330E | 0x330F | 13070 | 13071 | MAG_3S_HAR_I_41th_a_% | Aggr 3sec Phase A 41st Current Magnitude Harmonics | float | 2 | R
0x3310 | 0x3311 | 13072 | 13073 | MAG_3S_HAR_I_41th_b_% | Aggr 3sec Phase B 41st Current Magnitude Harmonics | float | 2 | R
0x3312 | 0x3313 | 13074 | 13075 | MAG_3S_HAR_I_41th_c_% | Aggr 3sec Phase C 41st Current Magnitude Harmonics | float | 2 | R
0x3314 | 0x3315 | 13076 | 13077 | MAG_3S_HAR_I_41th_n_% | Aggr 3sec Phase N 41st Current Magnitude Harmonics | float | 2 | R
0x3316 | 0x3317 | 13078 | 13079 | MAG_3S_HAR_V_42th_a_% | Aggr 3sec Phase A 42nd Voltage Magnitude Harmonics | float | 2 | R
0x3318 | 0x3319 | 13080 | 13081 | MAG_3S_HAR_V_42th_b_% | Aggr 3sec Phase B 42nd Voltage Magnitude Harmonics | float | 2 | R
0x331A | 0x331B | 13082 | 13083 | MAG_3S_HAR_V_42th_c_% | Aggr 3sec Phase C 42nd Voltage Magnitude Harmonics | float | 2 | R
0x331C | 0x331D | 13084 | 13085 | MAG_3S_HAR_I_42th_a_% | Aggr 3sec Phase A 42nd Current Magnitude Harmonics | float | 2 | R
0x331E | 0x331F | 13086 | 13087 | MAG_3S_HAR_I_42th_b_% | Aggr 3sec Phase B 42nd Current Magnitude Harmonics | float | 2 | R
0x3320 | 0x3321 | 13088 | 13089 | MAG_3S_HAR_I_42th_c_% | Aggr 3sec Phase C 42nd Current Magnitude Harmonics | float | 2 | R
0x3322 | 0x3323 | 13090 | 13091 | MAG_3S_HAR_I_42th_n_% | Aggr 3sec Phase N 42nd Current Magnitude Harmonics | float | 2 | R
0x3324 | 0x3325 | 13092 | 13093 | MAG_3S_HAR_V_43th_a_% | Aggr 3sec Phase A 43rd Voltage Magnitude Harmonics | float | 2 | R
0x3326 | 0x3327 | 13094 | 13095 | MAG_3S_HAR_V_43th_b_% | Aggr 3sec Phase B 43rd Voltage Magnitude Harmonics | float | 2 | R
0x3328 | 0x3329 | 13096 | 13097 | MAG_3S_HAR_V_43th_c_% | Aggr 3sec Phase C 43rd Voltage Magnitude Harmonics | float | 2 | R
0x332A | 0x332B | 13098 | 13099 | MAG_3S_HAR_I_43th_a_% | Aggr 3sec Phase A 43rd Current Magnitude Harmonics | float | 2 | R
0x332C | 0x332D | 13100 | 13101 | MAG_3S_HAR_I_43th_b_% | Aggr 3sec Phase B 43rd Current Magnitude Harmonics | float | 2 | R
0x332E | 0x332F | 13102 | 13103 | MAG_3S_HAR_I_43th_c_% | Aggr 3sec Phase C 43rd Current Magnitude Harmonics | float | 2 | R
0x3330 | 0x3331 | 13104 | 13105 | MAG_3S_HAR_I_43th_n_% | Aggr 3sec Phase N 43rd Current Magnitude Harmonics | float | 2 | R
0x3332 | 0x3333 | 13106 | 13107 | MAG_3S_HAR_V_44th_a_% | Aggr 3sec Phase A 44th Voltage Magnitude Harmonics | float | 2 | R
0x3334 | 0x3335 | 13108 | 13109 | MAG_3S_HAR_V_44th_b_% | Aggr 3sec Phase B 44th Voltage Magnitude Harmonics | float | 2 | R
0x3336 | 0x3337 | 13110 | 13111 | MAG_3S_HAR_V_44th_c_% | Aggr 3sec Phase C 44th Voltage Magnitude Harmonics | float | 2 | R
0x3338 | 0x3339 | 13112 | 13113 | MAG_3S_HAR_I_44th_a_% | Aggr 3sec Phase A 44th Current Magnitude Harmonics | float | 2 | R
0x333A | 0x333B | 13114 | 13115 | MAG_3S_HAR_I_44th_b_% | Aggr 3sec Phase B 44th Current Magnitude Harmonics | float | 2 | R
0x333C | 0x333D | 13116 | 13117 | MAG_3S_HAR_I_44th_c_% | Aggr 3sec Phase C 44th Current Magnitude Harmonics | float | 2 | R
0x333E | 0x333F | 13118 | 13119 | MAG_3S_HAR_I_44th_n_% | Aggr 3sec Phase N 44th Current Magnitude Harmonics | float | 2 | R
0x3340 | 0x3341 | 13120 | 13121 | MAG_3S_HAR_V_45th_a_% | Aggr 3sec Phase A 45th Voltage Magnitude Harmonics | float | 2 | R
0x3342 | 0x3343 | 13122 | 13123 | MAG_3S_HAR_V_45th_b_% | Aggr 3sec Phase B 45th Voltage Magnitude Harmonics | float | 2 | R
0x3344 | 0x3345 | 13124 | 13125 | MAG_3S_HAR_V_45th_c_% | Aggr 3sec Phase C 45th Voltage Magnitude Harmonics | float | 2 | R
0x3346 | 0x3347 | 13126 | 13127 | MAG_3S_HAR_I_45th_a_% | Aggr 3sec Phase A 45th Current Magnitude Harmonics | float | 2 | R
0x3348 | 0x3349 | 13128 | 13129 | MAG_3S_HAR_I_45th_b_% | Aggr 3sec Phase B 45th Current Magnitude Harmonics | float | 2 | R
0x334A | 0x334B | 13130 | 13131 | MAG_3S_HAR_I_45th_c_% | Aggr 3sec Phase C 45th Current Magnitude Harmonics | float | 2 | R
0x334C | 0x334D | 13132 | 13133 | MAG_3S_HAR_I_45th_n_% | Aggr 3sec Phase N 45th Current Magnitude Harmonics | float | 2 | R
0x334E | 0x334F | 13134 | 13135 | MAG_3S_HAR_V_46th_a_% | Aggr 3sec Phase A 46th Voltage Magnitude Harmonics | float | 2 | R
0x3350 | 0x3351 | 13136 | 13137 | MAG_3S_HAR_V_46th_b_% | Aggr 3sec Phase B 46th Voltage Magnitude Harmonics | float | 2 | R
0x3352 | 0x3353 | 13138 | 13139 | MAG_3S_HAR_V_46th_c_% | Aggr 3sec Phase C 46th Voltage Magnitude Harmonics | float | 2 | R
0x3354 | 0x3355 | 13140 | 13141 | MAG_3S_HAR_I_46th_a_% | Aggr 3sec Phase A 46th Current Magnitude Harmonics | float | 2 | R
0x3356 | 0x3357 | 13142 | 13143 | MAG_3S_HAR_I_46th_b_% | Aggr 3sec Phase B 46th Current Magnitude Harmonics | float | 2 | R
0x3358 | 0x3359 | 13144 | 13145 | MAG_3S_HAR_I_46th_c_% | Aggr 3sec Phase C 46th Current Magnitude Harmonics | float | 2 | R
0x335A | 0x335B | 13146 | 13147 | MAG_3S_HAR_I_46th_n_% | Aggr 3sec Phase N 46th Current Magnitude Harmonics | float | 2 | R
0x335C | 0x335D | 13148 | 13149 | MAG_3S_HAR_V_47th_a_% | Aggr 3sec Phase A 47th Voltage Magnitude Harmonics | float | 2 | R
0x335E | 0x335F | 13150 | 13151 | MAG_3S_HAR_V_47th_b_% | Aggr 3sec Phase B 47th Voltage Magnitude Harmonics | float | 2 | R
0x3360 | 0x3361 | 13152 | 13153 | MAG_3S_HAR_V_47th_c_% | Aggr 3sec Phase C 47th Voltage Magnitude Harmonics | float | 2 | R
0x3362 | 0x3363 | 13154 | 13155 | MAG_3S_HAR_I_47th_a_% | Aggr 3sec Phase A 47th Current Magnitude Harmonics | float | 2 | R
0x3364 | 0x3365 | 13156 | 13157 | MAG_3S_HAR_I_47th_b_% | Aggr 3sec Phase B 47th Current Magnitude Harmonics | float | 2 | R
0x3366 | 0x3367 | 13158 | 13159 | MAG_3S_HAR_I_47th_c_% | Aggr 3sec Phase C 47th Current Magnitude Harmonics | float | 2 | R
0x3368 | 0x3369 | 13160 | 13161 | MAG_3S_HAR_I_47th_n_% | Aggr 3sec Phase N 47th Current Magnitude Harmonics | float | 2 | R
0x336A | 0x336B | 13162 | 13163 | MAG_3S_HAR_V_48th_a_% | Aggr 3sec Phase A 48th Voltage Magnitude Harmonics | float | 2 | R
0x336C | 0x336D | 13164 | 13165 | MAG_3S_HAR_V_48th_b_% | Aggr 3sec Phase B 48th Voltage Magnitude Harmonics | float | 2 | R
0x336E | 0x336F | 13166 | 13167 | MAG_3S_HAR_V_48th_c_% | Aggr 3sec Phase C 48th Voltage Magnitude Harmonics | float | 2 | R
0x3370 | 0x3371 | 13168 | 13169 | MAG_3S_HAR_I_48th_a_% | Aggr 3sec Phase A 48th Current Magnitude Harmonics | float | 2 | R
0x3372 | 0x3373 | 13170 | 13171 | MAG_3S_HAR_I_48th_b_% | Aggr 3sec Phase B 48th Current Magnitude Harmonics | float | 2 | R
0x3374 | 0x3375 | 13172 | 13173 | MAG_3S_HAR_I_48th_c_% | Aggr 3sec Phase C 48th Current Magnitude Harmonics | float | 2 | R
0x3376 | 0x3377 | 13174 | 13175 | MAG_3S_HAR_I_48th_n_% | Aggr 3sec Phase N 48th Current Magnitude Harmonics | float | 2 | R
0x3378 | 0x3379 | 13176 | 13177 | MAG_3S_HAR_V_49th_a_% | Aggr 3sec Phase A 49th Voltage Magnitude Harmonics | float | 2 | R
0x337A | 0x337B | 13178 | 13179 | MAG_3S_HAR_V_49th_b_% | Aggr 3sec Phase B 49th Voltage Magnitude Harmonics | float | 2 | R
0x337C | 0x337D | 13180 | 13181 | MAG_3S_HAR_V_49th_c_% | Aggr 3sec Phase C 49th Voltage Magnitude Harmonics | float | 2 | R
0x337E | 0x337F | 13182 | 13183 | MAG_3S_HAR_I_49th_a_% | Aggr 3sec Phase A 49th Current Magnitude Harmonics | float | 2 | R
0x3380 | 0x3381 | 13184 | 13185 | MAG_3S_HAR_I_49th_b_% | Aggr 3sec Phase B 49th Current Magnitude Harmonics | float | 2 | R
0x3382 | 0x3383 | 13186 | 13187 | MAG_3S_HAR_I_49th_c_% | Aggr 3sec Phase C 49th Current Magnitude Harmonics | float | 2 | R
0x3384 | 0x3385 | 13188 | 13189 | MAG_3S_HAR_I_49th_n_% | Aggr 3sec Phase N 49th Current Magnitude Harmonics | float | 2 | R
0x3386 | 0x3387 | 13190 | 13191 | MAG_3S_HAR_V_50th_a_% | Aggr 3sec Phase A 50th Voltage Magnitude Harmonics | float | 2 | R
0x3388 | 0x3389 | 13192 | 13193 | MAG_3S_HAR_V_50th_b_% | Aggr 3sec Phase B 50th Voltage Magnitude Harmonics | float | 2 | R
0x338A | 0x338B | 13194 | 13195 | MAG_3S_HAR_V_50th_c_% | Aggr 3sec Phase C 50th Voltage Magnitude Harmonics | float | 2 | R
0x338C | 0x338D | 13196 | 13197 | MAG_3S_HAR_I_50th_a_% | Aggr 3sec Phase A 50th Current Magnitude Harmonics | float | 2 | R
0x338E | 0x338F | 13198 | 13199 | MAG_3S_HAR_I_50th_b_% | Aggr 3sec Phase B 50th Current Magnitude Harmonics | float | 2 | R
0x3390 | 0x3391 | 13200 | 13201 | MAG_3S_HAR_I_50th_c_% | Aggr 3sec Phase C 50th Current Magnitude Harmonics | float | 2 | R
0x3392 | 0x3393 | 13202 | 13203 | MAG_3S_HAR_I_50th_n_% | Aggr 3sec Phase N 50th Current Magnitude Harmonics | float | 2 | R
0x3394 | 0x3395 | 13204 | 13205 | MAG_3S_HAR_V_51th_a_% | Aggr 3sec Phase A 51st Voltage Magnitude Harmonics | float | 2 | R
0x3396 | 0x3397 | 13206 | 13207 | MAG_3S_HAR_V_51th_b_% | Aggr 3sec Phase B 51st Voltage Magnitude Harmonics | float | 2 | R
0x3398 | 0x3399 | 13208 | 13209 | MAG_3S_HAR_V_51th_c_% | Aggr 3sec Phase C 51st Voltage Magnitude Harmonics | float | 2 | R
0x339A | 0x339B | 13210 | 13211 | MAG_3S_HAR_I_51th_a_% | Aggr 3sec Phase A 51st Current Magnitude Harmonics | float | 2 | R
0x339C | 0x339D | 13212 | 13213 | MAG_3S_HAR_I_51th_b_% | Aggr 3sec Phase B 51st Current Magnitude Harmonics | float | 2 | R
0x339E | 0x339F | 13214 | 13215 | MAG_3S_HAR_I_51th_c_% | Aggr 3sec Phase C 51st Current Magnitude Harmonics | float | 2 | R
0x33A0 | 0x33A1 | 13216 | 13217 | MAG_3S_HAR_I_51th_n_% | Aggr 3sec Phase N 51st Current Magnitude Harmonics | float | 2 | R
0x33A2 | 0x33A3 | 13218 | 13219 | MAG_3S_HAR_V_52th_a_% | Aggr 3sec Phase A 52nd Voltage Magnitude Harmonics | float | 2 | R
0x33A4 | 0x33A5 | 13220 | 13221 | MAG_3S_HAR_V_52th_b_% | Aggr 3sec Phase B 52nd Voltage Magnitude Harmonics | float | 2 | R
0x33A6 | 0x33A7 | 13222 | 13223 | MAG_3S_HAR_V_52th_c_% | Aggr 3sec Phase C 52nd Voltage Magnitude Harmonics | float | 2 | R
0x33A8 | 0x33A9 | 13224 | 13225 | MAG_3S_HAR_I_52th_a_% | Aggr 3sec Phase A 52nd Current Magnitude Harmonics | float | 2 | R
0x33AA | 0x33AB | 13226 | 13227 | MAG_3S_HAR_I_52th_b_% | Aggr 3sec Phase B 52nd Current Magnitude Harmonics | float | 2 | R
0x33AC | 0x33AD | 13228 | 13229 | MAG_3S_HAR_I_52th_c_% | Aggr 3sec Phase C 52nd Current Magnitude Harmonics | float | 2 | R
0x33AE | 0x33AF | 13230 | 13231 | MAG_3S_HAR_I_52th_n_% | Aggr 3sec Phase N 52nd Current Magnitude Harmonics | float | 2 | R
0x33B0 | 0x33B1 | 13232 | 13233 | MAG_3S_HAR_V_53th_a_% | Aggr 3sec Phase A 53rd Voltage Magnitude Harmonics | float | 2 | R
0x33B2 | 0x33B3 | 13234 | 13235 | MAG_3S_HAR_V_53th_b_% | Aggr 3sec Phase B 53rd Voltage Magnitude Harmonics | float | 2 | R
0x33B4 | 0x33B5 | 13236 | 13237 | MAG_3S_HAR_V_53th_c_% | Aggr 3sec Phase C 53rd Voltage Magnitude Harmonics | float | 2 | R
0x33B6 | 0x33B7 | 13238 | 13239 | MAG_3S_HAR_I_53th_a_% | Aggr 3sec Phase A 53rd Current Magnitude Harmonics | float | 2 | R
0x33B8 | 0x33B9 | 13240 | 13241 | MAG_3S_HAR_I_53th_b_% | Aggr 3sec Phase B 53rd Current Magnitude Harmonics | float | 2 | R
0x33BA | 0x33BB | 13242 | 13243 | MAG_3S_HAR_I_53th_c_% | Aggr 3sec Phase C 53rd Current Magnitude Harmonics | float | 2 | R
0x33BC | 0x33BD | 13244 | 13245 | MAG_3S_HAR_I_53th_n_% | Aggr 3sec Phase N 53rd Current Magnitude Harmonics | float | 2 | R
0x33BE | 0x33BF | 13246 | 13247 | MAG_3S_HAR_V_54th_a_% | Aggr 3sec Phase A 54th Voltage Magnitude Harmonics | float | 2 | R
0x33C0 | 0x33C1 | 13248 | 13249 | MAG_3S_HAR_V_54th_b_% | Aggr 3sec Phase B 54th Voltage Magnitude Harmonics | float | 2 | R
0x33C2 | 0x33C3 | 13250 | 13251 | MAG_3S_HAR_V_54th_c_% | Aggr 3sec Phase C 54th Voltage Magnitude Harmonics | float | 2 | R
0x33C4 | 0x33C5 | 13252 | 13253 | MAG_3S_HAR_I_54th_a_% | Aggr 3sec Phase A 54th Current Magnitude Harmonics | float | 2 | R
0x33C6 | 0x33C7 | 13254 | 13255 | MAG_3S_HAR_I_54th_b_% | Aggr 3sec Phase B 54th Current Magnitude Harmonics | float | 2 | R
0x33C8 | 0x33C9 | 13256 | 13257 | MAG_3S_HAR_I_54th_c_% | Aggr 3sec Phase C 54th Current Magnitude Harmonics | float | 2 | R
0x33CA | 0x33CB | 13258 | 13259 | MAG_3S_HAR_I_54th_n_% | Aggr 3sec Phase N 54th Current Magnitude Harmonics | float | 2 | R
0x33CC | 0x33CD | 13260 | 13261 | MAG_3S_HAR_V_55th_a_% | Aggr 3sec Phase A 55th Voltage Magnitude Harmonics | float | 2 | R
0x33CE | 0x33CF | 13262 | 13263 | MAG_3S_HAR_V_55th_b_% | Aggr 3sec Phase B 55th Voltage Magnitude Harmonics | float | 2 | R
0x33D0 | 0x33D1 | 13264 | 13265 | MAG_3S_HAR_V_55th_c_% | Aggr 3sec Phase C 55th Voltage Magnitude Harmonics | float | 2 | R
0x33D2 | 0x33D3 | 13266 | 13267 | MAG_3S_HAR_I_55th_a_% | Aggr 3sec Phase A 55th Current Magnitude Harmonics | float | 2 | R
0x33D4 | 0x33D5 | 13268 | 13269 | MAG_3S_HAR_I_55th_b_% | Aggr 3sec Phase B 55th Current Magnitude Harmonics | float | 2 | R
0x33D6 | 0x33D7 | 13270 | 13271 | MAG_3S_HAR_I_55th_c_% | Aggr 3sec Phase C 55th Current Magnitude Harmonics | float | 2 | R
0x33D8 | 0x33D9 | 13272 | 13273 | MAG_3S_HAR_I_55th_n_% | Aggr 3sec Phase N 55th Current Magnitude Harmonics | float | 2 | R
0x33DA | 0x33DB | 13274 | 13275 | MAG_3S_HAR_V_56th_a_% | Aggr 3sec Phase A 56th Voltage Magnitude Harmonics | float | 2 | R
0x33DC | 0x33DD | 13276 | 13277 | MAG_3S_HAR_V_56th_b_% | Aggr 3sec Phase B 56th Voltage Magnitude Harmonics | float | 2 | R
0x33DE | 0x33DF | 13278 | 13279 | MAG_3S_HAR_V_56th_c_% | Aggr 3sec Phase C 56th Voltage Magnitude Harmonics | float | 2 | R
0x33E0 | 0x33E1 | 13280 | 13281 | MAG_3S_HAR_I_56th_a_% | Aggr 3sec Phase A 56th Current Magnitude Harmonics | float | 2 | R
0x33E2 | 0x33E3 | 13282 | 13283 | MAG_3S_HAR_I_56th_b_% | Aggr 3sec Phase B 56th Current Magnitude Harmonics | float | 2 | R
0x33E4 | 0x33E5 | 13284 | 13285 | MAG_3S_HAR_I_56th_c_% | Aggr 3sec Phase C 56th Current Magnitude Harmonics | float | 2 | R
0x33E6 | 0x33E7 | 13286 | 13287 | MAG_3S_HAR_I_56th_n_% | Aggr 3sec Phase N 56th Current Magnitude Harmonics | float | 2 | R
0x33E8 | 0x33E9 | 13288 | 13289 | MAG_3S_HAR_V_57th_a_% | Aggr 3sec Phase A 57th Voltage Magnitude Harmonics | float | 2 | R
0x33EA | 0x33EB | 13290 | 13291 | MAG_3S_HAR_V_57th_b_% | Aggr 3sec Phase B 57th Voltage Magnitude Harmonics | float | 2 | R
0x33EC | 0x33ED | 13292 | 13293 | MAG_3S_HAR_V_57th_c_% | Aggr 3sec Phase C 57th Voltage Magnitude Harmonics | float | 2 | R
0x33EE | 0x33EF | 13294 | 13295 | MAG_3S_HAR_I_57th_a_% | Aggr 3sec Phase A 57th Current Magnitude Harmonics | float | 2 | R
0x33F0 | 0x33F1 | 13296 | 13297 | MAG_3S_HAR_I_57th_b_% | Aggr 3sec Phase B 57th Current Magnitude Harmonics | float | 2 | R
0x33F2 | 0x33F3 | 13298 | 13299 | MAG_3S_HAR_I_57th_c_% | Aggr 3sec Phase C 57th Current Magnitude Harmonics | float | 2 | R
0x33F4 | 0x33F5 | 13300 | 13301 | MAG_3S_HAR_I_57th_n_% | Aggr 3sec Phase N 57th Current Magnitude Harmonics | float | 2 | R
0x33F6 | 0x33F7 | 13302 | 13303 | MAG_3S_HAR_V_58th_a_% | Aggr 3sec Phase A 58th Voltage Magnitude Harmonics | float | 2 | R
0x33F8 | 0x33F9 | 13304 | 13305 | MAG_3S_HAR_V_58th_b_% | Aggr 3sec Phase B 58th Voltage Magnitude Harmonics | float | 2 | R
0x33FA | 0x33FB | 13306 | 13307 | MAG_3S_HAR_V_58th_c_% | Aggr 3sec Phase C 58th Voltage Magnitude Harmonics | float | 2 | R
0x33FC | 0x33FD | 13308 | 13309 | MAG_3S_HAR_I_58th_a_% | Aggr 3sec Phase A 58th Current Magnitude Harmonics | float | 2 | R
0x33FE | 0x33FF | 13310 | 13311 | MAG_3S_HAR_I_58th_b_% | Aggr 3sec Phase B 58th Current Magnitude Harmonics | float | 2 | R
0x3400 | 0x3401 | 13312 | 13313 | MAG_3S_HAR_I_58th_c_% | Aggr 3sec Phase C 58th Current Magnitude Harmonics | float | 2 | R
0x3402 | 0x3403 | 13314 | 13315 | MAG_3S_HAR_I_58th_n_% | Aggr 3sec Phase N 58th Current Magnitude Harmonics | float | 2 | R
0x3404 | 0x3405 | 13316 | 13317 | MAG_3S_HAR_V_59th_a_% | Aggr 3sec Phase A 59th Voltage Magnitude Harmonics | float | 2 | R
0x3406 | 0x3407 | 13318 | 13319 | MAG_3S_HAR_V_59th_b_% | Aggr 3sec Phase B 59th Voltage Magnitude Harmonics | float | 2 | R
0x3408 | 0x3409 | 13320 | 13321 | MAG_3S_HAR_V_59th_c_% | Aggr 3sec Phase C 59th Voltage Magnitude Harmonics | float | 2 | R
0x340A | 0x340B | 13322 | 13323 | MAG_3S_HAR_I_59th_a_% | Aggr 3sec Phase A 59th Current Magnitude Harmonics | float | 2 | R
0x340C | 0x340D | 13324 | 13325 | MAG_3S_HAR_I_59th_b_% | Aggr 3sec Phase B 59th Current Magnitude Harmonics | float | 2 | R
0x340E | 0x340F | 13326 | 13327 | MAG_3S_HAR_I_59th_c_% | Aggr 3sec Phase C 59th Current Magnitude Harmonics | float | 2 | R
0x3410 | 0x3411 | 13328 | 13329 | MAG_3S_HAR_I_59th_n_% | Aggr 3sec Phase N 59th Current Magnitude Harmonics | float | 2 | R
0x3412 | 0x3413 | 13330 | 13331 | MAG_3S_HAR_V_60th_a_% | Aggr 3sec Phase A 60th Voltage Magnitude Harmonics | float | 2 | R
0x3414 | 0x3415 | 13332 | 13333 | MAG_3S_HAR_V_60th_b_% | Aggr 3sec Phase B 60th Voltage Magnitude Harmonics | float | 2 | R
0x3416 | 0x3417 | 13334 | 13335 | MAG_3S_HAR_V_60th_c_% | Aggr 3sec Phase C 60th Voltage Magnitude Harmonics | float | 2 | R
0x3418 | 0x3419 | 13336 | 13337 | MAG_3S_HAR_I_60th_a_% | Aggr 3sec Phase A 60th Current Magnitude Harmonics | float | 2 | R
0x341A | 0x341B | 13338 | 13339 | MAG_3S_HAR_I_60th_b_% | Aggr 3sec Phase B 60th Current Magnitude Harmonics | float | 2 | R
0x341C | 0x341D | 13340 | 13341 | MAG_3S_HAR_I_60th_c_% | Aggr 3sec Phase C 60th Current Magnitude Harmonics | float | 2 | R
0x341E | 0x341F | 13342 | 13343 | MAG_3S_HAR_I_60th_n_% | Aggr 3sec Phase N 60th Current Magnitude Harmonics | float | 2 | R
0x3420 | 0x3421 | 13344 | 13345 | MAG_3S_HAR_V_61th_a_% | Aggr 3sec Phase A 61st Voltage Magnitude Harmonics | float | 2 | R
0x3422 | 0x3423 | 13346 | 13347 | MAG_3S_HAR_V_61th_b_% | Aggr 3sec Phase B 61st Voltage Magnitude Harmonics | float | 2 | R
0x3424 | 0x3425 | 13348 | 13349 | MAG_3S_HAR_V_61th_c_% | Aggr 3sec Phase C 61st Voltage Magnitude Harmonics | float | 2 | R
0x3426 | 0x3427 | 13350 | 13351 | MAG_3S_HAR_I_61th_a_% | Aggr 3sec Phase A 61st Current Magnitude Harmonics | float | 2 | R
0x3428 | 0x3429 | 13352 | 13353 | MAG_3S_HAR_I_61th_b_% | Aggr 3sec Phase B 61st Current Magnitude Harmonics | float | 2 | R
0x342A | 0x342B | 13354 | 13355 | MAG_3S_HAR_I_61th_c_% | Aggr 3sec Phase C 61st Current Magnitude Harmonics | float | 2 | R
0x342C | 0x342D | 13356 | 13357 | MAG_3S_HAR_I_61th_n_% | Aggr 3sec Phase N 61st Current Magnitude Harmonics | float | 2 | R
0x342E | 0x342F | 13358 | 13359 | MAG_3S_HAR_V_62th_a_% | Aggr 3sec Phase A 62nd Voltage Magnitude Harmonics | float | 2 | R
0x3430 | 0x3431 | 13360 | 13361 | MAG_3S_HAR_V_62th_b_% | Aggr 3sec Phase B 62nd Voltage Magnitude Harmonics | float | 2 | R
0x3432 | 0x3433 | 13362 | 13363 | MAG_3S_HAR_V_62th_c_% | Aggr 3sec Phase C 62nd Voltage Magnitude Harmonics | float | 2 | R
0x3434 | 0x3435 | 13364 | 13365 | MAG_3S_HAR_I_62th_a_% | Aggr 3sec Phase A 62nd Current Magnitude Harmonics | float | 2 | R
0x3436 | 0x3437 | 13366 | 13367 | MAG_3S_HAR_I_62th_b_% | Aggr 3sec Phase B 62nd Current Magnitude Harmonics | float | 2 | R
0x3438 | 0x3439 | 13368 | 13369 | MAG_3S_HAR_I_62th_c_% | Aggr 3sec Phase C 62nd Current Magnitude Harmonics | float | 2 | R
0x343A | 0x343B | 13370 | 13371 | MAG_3S_HAR_I_62th_n_% | Aggr 3sec Phase N 62nd Current Magnitude Harmonics | float | 2 | R
0x343C | 0x343D | 13372 | 13373 | MAG_3S_HAR_V_63th_a_% | Aggr 3sec Phase A 63rd Voltage Magnitude Harmonics | float | 2 | R
0x343E | 0x343F | 13374 | 13375 | MAG_3S_HAR_V_63th_b_% | Aggr 3sec Phase B 63rd Voltage Magnitude Harmonics | float | 2 | R
0x3440 | 0x3441 | 13376 | 13377 | MAG_3S_HAR_V_63th_c_% | Aggr 3sec Phase C 63rd Voltage Magnitude Harmonics | float | 2 | R
0x3442 | 0x3443 | 13378 | 13379 | MAG_3S_HAR_I_63th_a_% | Aggr 3sec Phase A 63rd Current Magnitude Harmonics | float | 2 | R
0x3444 | 0x3445 | 13380 | 13381 | MAG_3S_HAR_I_63th_b_% | Aggr 3sec Phase B 63rd Current Magnitude Harmonics | float | 2 | R
0x3446 | 0x3447 | 13382 | 13383 | MAG_3S_HAR_I_63th_c_% | Aggr 3sec Phase C 63rd Current Magnitude Harmonics | float | 2 | R
0x3448 | 0x3449 | 13384 | 13385 | MAG_3S_HAR_I_63th_n_% | Aggr 3sec Phase N 63rd Current Magnitude Harmonics | float | 2 | R
0x344A | 0x344B | 13386 | 13387 | MAG_3S_HAR_V_64th_a_% | Aggr 3sec Phase A 64th Voltage Magnitude Harmonics | float | 2 | R
0x344C | 0x344D | 13388 | 13389 | MAG_3S_HAR_V_64th_b_% | Aggr 3sec Phase B 64th Voltage Magnitude Harmonics | float | 2 | R
0x344E | 0x344F | 13390 | 13391 | MAG_3S_HAR_V_64th_c_% | Aggr 3sec Phase C 64th Voltage Magnitude Harmonics | float | 2 | R
0x3450 | 0x3451 | 13392 | 13393 | MAG_3S_HAR_I_64th_a_% | Aggr 3sec Phase A 64th Current Magnitude Harmonics | float | 2 | R
0x3452 | 0x3453 | 13394 | 13395 | MAG_3S_HAR_I_64th_b_% | Aggr 3sec Phase B 64th Current Magnitude Harmonics | float | 2 | R
0x3454 | 0x3455 | 13396 | 13397 | MAG_3S_HAR_I_64th_c_% | Aggr 3sec Phase C 64th Current Magnitude Harmonics | float | 2 | R
0x3456 | 0x3457 | 13398 | 13399 | MAG_3S_HAR_I_64th_n_% | Aggr 3sec Phase N 64th Current Magnitude Harmonics | float | 2 | R
0x3458 | 0x3459 | 13400 | 13401 | MAG_3S_HAR_V_65th_a_% | Aggr 3sec Phase A 65th Voltage Magnitude Harmonics | float | 2 | R
0x345A | 0x345B | 13402 | 13403 | MAG_3S_HAR_V_65th_b_% | Aggr 3sec Phase B 65th Voltage Magnitude Harmonics | float | 2 | R
0x345C | 0x345D | 13404 | 13405 | MAG_3S_HAR_V_65th_c_% | Aggr 3sec Phase C 65th Voltage Magnitude Harmonics | float | 2 | R
0x345E | 0x345F | 13406 | 13407 | MAG_3S_HAR_I_65th_a_% | Aggr 3sec Phase A 65th Current Magnitude Harmonics | float | 2 | R
0x3460 | 0x3461 | 13408 | 13409 | MAG_3S_HAR_I_65th_b_% | Aggr 3sec Phase B 65th Current Magnitude Harmonics | float | 2 | R
0x3462 | 0x3463 | 13410 | 13411 | MAG_3S_HAR_I_65th_c_% | Aggr 3sec Phase C 65th Current Magnitude Harmonics | float | 2 | R
0x3464 | 0x3465 | 13412 | 13413 | MAG_3S_HAR_I_65th_n_% | Aggr 3sec Phase N 65th Current Magnitude Harmonics | float | 2 | R
0x3466 | 0x3467 | 13414 | 13415 | MAG_3S_HAR_V_66th_a_% | Aggr 3sec Phase A 66th Voltage Magnitude Harmonics | float | 2 | R
0x3468 | 0x3469 | 13416 | 13417 | MAG_3S_HAR_V_66th_b_% | Aggr 3sec Phase B 66th Voltage Magnitude Harmonics | float | 2 | R
0x346A | 0x346B | 13418 | 13419 | MAG_3S_HAR_V_66th_c_% | Aggr 3sec Phase C 66th Voltage Magnitude Harmonics | float | 2 | R
0x346C | 0x346D | 13420 | 13421 | MAG_3S_HAR_I_66th_a_% | Aggr 3sec Phase A 66th Current Magnitude Harmonics | float | 2 | R
0x346E | 0x346F | 13422 | 13423 | MAG_3S_HAR_I_66th_b_% | Aggr 3sec Phase B 66th Current Magnitude Harmonics | float | 2 | R
0x3470 | 0x3471 | 13424 | 13425 | MAG_3S_HAR_I_66th_c_% | Aggr 3sec Phase C 66th Current Magnitude Harmonics | float | 2 | R
0x3472 | 0x3473 | 13426 | 13427 | MAG_3S_HAR_I_66th_n_% | Aggr 3sec Phase N 66th Current Magnitude Harmonics | float | 2 | R
0x3474 | 0x3475 | 13428 | 13429 | MAG_3S_HAR_V_67th_a_% | Aggr 3sec Phase A 67th Voltage Magnitude Harmonics | float | 2 | R
0x3476 | 0x3477 | 13430 | 13431 | MAG_3S_HAR_V_67th_b_% | Aggr 3sec Phase B 67th Voltage Magnitude Harmonics | float | 2 | R
0x3478 | 0x3479 | 13432 | 13433 | MAG_3S_HAR_V_67th_c_% | Aggr 3sec Phase C 67th Voltage Magnitude Harmonics | float | 2 | R
0x347A | 0x347B | 13434 | 13435 | MAG_3S_HAR_I_67th_a_% | Aggr 3sec Phase A 67th Current Magnitude Harmonics | float | 2 | R
0x347C | 0x347D | 13436 | 13437 | MAG_3S_HAR_I_67th_b_% | Aggr 3sec Phase B 67th Current Magnitude Harmonics | float | 2 | R
0x347E | 0x347F | 13438 | 13439 | MAG_3S_HAR_I_67th_c_% | Aggr 3sec Phase C 67th Current Magnitude Harmonics | float | 2 | R
0x3480 | 0x3481 | 13440 | 13441 | MAG_3S_HAR_I_67th_n_% | Aggr 3sec Phase N 67th Current Magnitude Harmonics | float | 2 | R
0x3482 | 0x3483 | 13442 | 13443 | MAG_3S_HAR_V_68th_a_% | Aggr 3sec Phase A 68th Voltage Magnitude Harmonics | float | 2 | R
0x3484 | 0x3485 | 13444 | 13445 | MAG_3S_HAR_V_68th_b_% | Aggr 3sec Phase B 68th Voltage Magnitude Harmonics | float | 2 | R
0x3486 | 0x3487 | 13446 | 13447 | MAG_3S_HAR_V_68th_c_% | Aggr 3sec Phase C 68th Voltage Magnitude Harmonics | float | 2 | R
0x3488 | 0x3489 | 13448 | 13449 | MAG_3S_HAR_I_68th_a_% | Aggr 3sec Phase A 68th Current Magnitude Harmonics | float | 2 | R
0x348A | 0x348B | 13450 | 13451 | MAG_3S_HAR_I_68th_b_% | Aggr 3sec Phase B 68th Current Magnitude Harmonics | float | 2 | R
0x348C | 0x348D | 13452 | 13453 | MAG_3S_HAR_I_68th_c_% | Aggr 3sec Phase C 68th Current Magnitude Harmonics | float | 2 | R
0x348E | 0x348F | 13454 | 13455 | MAG_3S_HAR_I_68th_n_% | Aggr 3sec Phase N 68th Current Magnitude Harmonics | float | 2 | R
0x3490 | 0x3491 | 13456 | 13457 | MAG_3S_HAR_V_69th_a_% | Aggr 3sec Phase A 69th Voltage Magnitude Harmonics | float | 2 | R
0x3492 | 0x3493 | 13458 | 13459 | MAG_3S_HAR_V_69th_b_% | Aggr 3sec Phase B 69th Voltage Magnitude Harmonics | float | 2 | R
0x3494 | 0x3495 | 13460 | 13461 | MAG_3S_HAR_V_69th_c_% | Aggr 3sec Phase C 69th Voltage Magnitude Harmonics | float | 2 | R
0x3496 | 0x3497 | 13462 | 13463 | MAG_3S_HAR_I_69th_a_% | Aggr 3sec Phase A 69th Current Magnitude Harmonics | float | 2 | R
0x3498 | 0x3499 | 13464 | 13465 | MAG_3S_HAR_I_69th_b_% | Aggr 3sec Phase B 69th Current Magnitude Harmonics | float | 2 | R
0x349A | 0x349B | 13466 | 13467 | MAG_3S_HAR_I_69th_c_% | Aggr 3sec Phase C 69th Current Magnitude Harmonics | float | 2 | R
0x349C | 0x349D | 13468 | 13469 | MAG_3S_HAR_I_69th_n_% | Aggr 3sec Phase N 69th Current Magnitude Harmonics | float | 2 | R
0x349E | 0x349F | 13470 | 13471 | MAG_3S_HAR_V_70th_a_% | Aggr 3sec Phase A 70th Voltage Magnitude Harmonics | float | 2 | R
0x34A0 | 0x34A1 | 13472 | 13473 | MAG_3S_HAR_V_70th_b_% | Aggr 3sec Phase B 70th Voltage Magnitude Harmonics | float | 2 | R
0x34A2 | 0x34A3 | 13474 | 13475 | MAG_3S_HAR_V_70th_c_% | Aggr 3sec Phase C 70th Voltage Magnitude Harmonics | float | 2 | R
0x34A4 | 0x34A5 | 13476 | 13477 | MAG_3S_HAR_I_70th_a_% | Aggr 3sec Phase A 70th Current Magnitude Harmonics | float | 2 | R
0x34A6 | 0x34A7 | 13478 | 13479 | MAG_3S_HAR_I_70th_b_% | Aggr 3sec Phase B 70th Current Magnitude Harmonics | float | 2 | R
0x34A8 | 0x34A9 | 13480 | 13481 | MAG_3S_HAR_I_70th_c_% | Aggr 3sec Phase C 70th Current Magnitude Harmonics | float | 2 | R
0x34AA | 0x34AB | 13482 | 13483 | MAG_3S_HAR_I_70th_n_% | Aggr 3sec Phase N 70th Current Magnitude Harmonics | float | 2 | R
0x34AC | 0x34AD | 13484 | 13485 | MAG_3S_HAR_V_71th_a_% | Aggr 3sec Phase A 71st Voltage Magnitude Harmonics | float | 2 | R
0x34AE | 0x34AF | 13486 | 13487 | MAG_3S_HAR_V_71th_b_% | Aggr 3sec Phase B 71st Voltage Magnitude Harmonics | float | 2 | R
0x34B0 | 0x34B1 | 13488 | 13489 | MAG_3S_HAR_V_71th_c_% | Aggr 3sec Phase C 71st Voltage Magnitude Harmonics | float | 2 | R
0x34B2 | 0x34B3 | 13490 | 13491 | MAG_3S_HAR_I_71th_a_% | Aggr 3sec Phase A 71st Current Magnitude Harmonics | float | 2 | R
0x34B4 | 0x34B5 | 13492 | 13493 | MAG_3S_HAR_I_71th_b_% | Aggr 3sec Phase B 71st Current Magnitude Harmonics | float | 2 | R
0x34B6 | 0x34B7 | 13494 | 13495 | MAG_3S_HAR_I_71th_c_% | Aggr 3sec Phase C 71st Current Magnitude Harmonics | float | 2 | R
0x34B8 | 0x34B9 | 13496 | 13497 | MAG_3S_HAR_I_71th_n_% | Aggr 3sec Phase N 71st Current Magnitude Harmonics | float | 2 | R
0x34BA | 0x34BB | 13498 | 13499 | MAG_3S_HAR_V_72th_a_% | Aggr 3sec Phase A 72nd Voltage Magnitude Harmonics | float | 2 | R
0x34BC | 0x34BD | 13500 | 13501 | MAG_3S_HAR_V_72th_b_% | Aggr 3sec Phase B 72nd Voltage Magnitude Harmonics | float | 2 | R
0x34BE | 0x34BF | 13502 | 13503 | MAG_3S_HAR_V_72th_c_% | Aggr 3sec Phase C 72nd Voltage Magnitude Harmonics | float | 2 | R
0x34C0 | 0x34C1 | 13504 | 13505 | MAG_3S_HAR_I_72th_a_% | Aggr 3sec Phase A 72nd Current Magnitude Harmonics | float | 2 | R
0x34C2 | 0x34C3 | 13506 | 13507 | MAG_3S_HAR_I_72th_b_% | Aggr 3sec Phase B 72nd Current Magnitude Harmonics | float | 2 | R
0x34C4 | 0x34C5 | 13508 | 13509 | MAG_3S_HAR_I_72th_c_% | Aggr 3sec Phase C 72nd Current Magnitude Harmonics | float | 2 | R
0x34C6 | 0x34C7 | 13510 | 13511 | MAG_3S_HAR_I_72th_n_% | Aggr 3sec Phase N 72nd Current Magnitude Harmonics | float | 2 | R
0x34C8 | 0x34C9 | 13512 | 13513 | MAG_3S_HAR_V_73th_a_% | Aggr 3sec Phase A 73rd Voltage Magnitude Harmonics | float | 2 | R
0x34CA | 0x34CB | 13514 | 13515 | MAG_3S_HAR_V_73th_b_% | Aggr 3sec Phase B 73rd Voltage Magnitude Harmonics | float | 2 | R
0x34CC | 0x34CD | 13516 | 13517 | MAG_3S_HAR_V_73th_c_% | Aggr 3sec Phase C 73rd Voltage Magnitude Harmonics | float | 2 | R
0x34CE | 0x34CF | 13518 | 13519 | MAG_3S_HAR_I_73th_a_% | Aggr 3sec Phase A 73rd Current Magnitude Harmonics | float | 2 | R
0x34D0 | 0x34D1 | 13520 | 13521 | MAG_3S_HAR_I_73th_b_% | Aggr 3sec Phase B 73rd Current Magnitude Harmonics | float | 2 | R
0x34D2 | 0x34D3 | 13522 | 13523 | MAG_3S_HAR_I_73th_c_% | Aggr 3sec Phase C 73rd Current Magnitude Harmonics | float | 2 | R
0x34D4 | 0x34D5 | 13524 | 13525 | MAG_3S_HAR_I_73th_n_% | Aggr 3sec Phase N 73rd Current Magnitude Harmonics | float | 2 | R
0x34D6 | 0x34D7 | 13526 | 13527 | MAG_3S_HAR_V_74th_a_% | Aggr 3sec Phase A 74th Voltage Magnitude Harmonics | float | 2 | R
0x34D8 | 0x34D9 | 13528 | 13529 | MAG_3S_HAR_V_74th_b_% | Aggr 3sec Phase B 74th Voltage Magnitude Harmonics | float | 2 | R
0x34DA | 0x34DB | 13530 | 13531 | MAG_3S_HAR_V_74th_c_% | Aggr 3sec Phase C 74th Voltage Magnitude Harmonics | float | 2 | R
0x34DC | 0x34DD | 13532 | 13533 | MAG_3S_HAR_I_74th_a_% | Aggr 3sec Phase A 74th Current Magnitude Harmonics | float | 2 | R
0x34DE | 0x34DF | 13534 | 13535 | MAG_3S_HAR_I_74th_b_% | Aggr 3sec Phase B 74th Current Magnitude Harmonics | float | 2 | R
0x34E0 | 0x34E1 | 13536 | 13537 | MAG_3S_HAR_I_74th_c_% | Aggr 3sec Phase C 74th Current Magnitude Harmonics | float | 2 | R
0x34E2 | 0x34E3 | 13538 | 13539 | MAG_3S_HAR_I_74th_n_% | Aggr 3sec Phase N 74th Current Magnitude Harmonics | float | 2 | R
0x34E4 | 0x34E5 | 13540 | 13541 | MAG_3S_HAR_V_75th_a_% | Aggr 3sec Phase A 75th Voltage Magnitude Harmonics | float | 2 | R
0x34E6 | 0x34E7 | 13542 | 13543 | MAG_3S_HAR_V_75th_b_% | Aggr 3sec Phase B 75th Voltage Magnitude Harmonics | float | 2 | R
0x34E8 | 0x34E9 | 13544 | 13545 | MAG_3S_HAR_V_75th_c_% | Aggr 3sec Phase C 75th Voltage Magnitude Harmonics | float | 2 | R
0x34EA | 0x34EB | 13546 | 13547 | MAG_3S_HAR_I_75th_a_% | Aggr 3sec Phase A 75th Current Magnitude Harmonics | float | 2 | R
0x34EC | 0x34ED | 13548 | 13549 | MAG_3S_HAR_I_75th_b_% | Aggr 3sec Phase B 75th Current Magnitude Harmonics | float | 2 | R
0x34EE | 0x34EF | 13550 | 13551 | MAG_3S_HAR_I_75th_c_% | Aggr 3sec Phase C 75th Current Magnitude Harmonics | float | 2 | R
0x34F0 | 0x34F1 | 13552 | 13553 | MAG_3S_HAR_I_75th_n_% | Aggr 3sec Phase N 75th Current Magnitude Harmonics | float | 2 | R
0x34F2 | 0x34F3 | 13554 | 13555 | MAG_3S_HAR_V_76th_a_% | Aggr 3sec Phase A 76th Voltage Magnitude Harmonics | float | 2 | R
0x34F4 | 0x34F5 | 13556 | 13557 | MAG_3S_HAR_V_76th_b_% | Aggr 3sec Phase B 76th Voltage Magnitude Harmonics | float | 2 | R
0x34F6 | 0x34F7 | 13558 | 13559 | MAG_3S_HAR_V_76th_c_% | Aggr 3sec Phase C 76th Voltage Magnitude Harmonics | float | 2 | R
0x34F8 | 0x34F9 | 13560 | 13561 | MAG_3S_HAR_I_76th_a_% | Aggr 3sec Phase A 76th Current Magnitude Harmonics | float | 2 | R
0x34FA | 0x34FB | 13562 | 13563 | MAG_3S_HAR_I_76th_b_% | Aggr 3sec Phase B 76th Current Magnitude Harmonics | float | 2 | R
0x34FC | 0x34FD | 13564 | 13565 | MAG_3S_HAR_I_76th_c_% | Aggr 3sec Phase C 76th Current Magnitude Harmonics | float | 2 | R
0x34FE | 0x34FF | 13566 | 13567 | MAG_3S_HAR_I_76th_n_% | Aggr 3sec Phase N 76th Current Magnitude Harmonics | float | 2 | R
0x3500 | 0x3501 | 13568 | 13569 | MAG_3S_HAR_V_77th_a_% | Aggr 3sec Phase A 77th Voltage Magnitude Harmonics | float | 2 | R
0x3502 | 0x3503 | 13570 | 13571 | MAG_3S_HAR_V_77th_b_% | Aggr 3sec Phase B 77th Voltage Magnitude Harmonics | float | 2 | R
0x3504 | 0x3505 | 13572 | 13573 | MAG_3S_HAR_V_77th_c_% | Aggr 3sec Phase C 77th Voltage Magnitude Harmonics | float | 2 | R
0x3506 | 0x3507 | 13574 | 13575 | MAG_3S_HAR_I_77th_a_% | Aggr 3sec Phase A 77th Current Magnitude Harmonics | float | 2 | R
0x3508 | 0x3509 | 13576 | 13577 | MAG_3S_HAR_I_77th_b_% | Aggr 3sec Phase B 77th Current Magnitude Harmonics | float | 2 | R
0x350A | 0x350B | 13578 | 13579 | MAG_3S_HAR_I_77th_c_% | Aggr 3sec Phase C 77th Current Magnitude Harmonics | float | 2 | R
0x350C | 0x350D | 13580 | 13581 | MAG_3S_HAR_I_77th_n_% | Aggr 3sec Phase N 77th Current Magnitude Harmonics | float | 2 | R
0x350E | 0x350F | 13582 | 13583 | MAG_3S_HAR_V_78th_a_% | Aggr 3sec Phase A 78th Voltage Magnitude Harmonics | float | 2 | R
0x3510 | 0x3511 | 13584 | 13585 | MAG_3S_HAR_V_78th_b_% | Aggr 3sec Phase B 78th Voltage Magnitude Harmonics | float | 2 | R
0x3512 | 0x3513 | 13586 | 13587 | MAG_3S_HAR_V_78th_c_% | Aggr 3sec Phase C 78th Voltage Magnitude Harmonics | float | 2 | R
0x3514 | 0x3515 | 13588 | 13589 | MAG_3S_HAR_I_78th_a_% | Aggr 3sec Phase A 78th Current Magnitude Harmonics | float | 2 | R
0x3516 | 0x3517 | 13590 | 13591 | MAG_3S_HAR_I_78th_b_% | Aggr 3sec Phase B 78th Current Magnitude Harmonics | float | 2 | R
0x3518 | 0x3519 | 13592 | 13593 | MAG_3S_HAR_I_78th_c_% | Aggr 3sec Phase C 78th Current Magnitude Harmonics | float | 2 | R
0x351A | 0x351B | 13594 | 13595 | MAG_3S_HAR_I_78th_n_% | Aggr 3sec Phase N 78th Current Magnitude Harmonics | float | 2 | R
0x351C | 0x351D | 13596 | 13597 | MAG_3S_HAR_V_79th_a_% | Aggr 3sec Phase A 79th Voltage Magnitude Harmonics | float | 2 | R
0x351E | 0x351F | 13598 | 13599 | MAG_3S_HAR_V_79th_b_% | Aggr 3sec Phase B 79th Voltage Magnitude Harmonics | float | 2 | R
0x3520 | 0x3521 | 13600 | 13601 | MAG_3S_HAR_V_79th_c_% | Aggr 3sec Phase C 79th Voltage Magnitude Harmonics | float | 2 | R
0x3522 | 0x3523 | 13602 | 13603 | MAG_3S_HAR_I_79th_a_% | Aggr 3sec Phase A 79th Current Magnitude Harmonics | float | 2 | R
0x3524 | 0x3525 | 13604 | 13605 | MAG_3S_HAR_I_79th_b_% | Aggr 3sec Phase B 79th Current Magnitude Harmonics | float | 2 | R
0x3526 | 0x3527 | 13606 | 13607 | MAG_3S_HAR_I_79th_c_% | Aggr 3sec Phase C 79th Current Magnitude Harmonics | float | 2 | R
0x3528 | 0x3529 | 13608 | 13609 | MAG_3S_HAR_I_79th_n_% | Aggr 3sec Phase N 79th Current Magnitude Harmonics | float | 2 | R
0x352A | 0x352B | 13610 | 13611 | MAG_3S_HAR_V_80th_a_% | Aggr 3sec Phase A 80th Voltage Magnitude Harmonics | float | 2 | R
0x352C | 0x352D | 13612 | 13613 | MAG_3S_HAR_V_80th_b_% | Aggr 3sec Phase B 80th Voltage Magnitude Harmonics | float | 2 | R
0x352E | 0x352F | 13614 | 13615 | MAG_3S_HAR_V_80th_c_% | Aggr 3sec Phase C 80th Voltage Magnitude Harmonics | float | 2 | R
0x3530 | 0x3531 | 13616 | 13617 | MAG_3S_HAR_I_80th_a_% | Aggr 3sec Phase A 80th Current Magnitude Harmonics | float | 2 | R
0x3532 | 0x3533 | 13618 | 13619 | MAG_3S_HAR_I_80th_b_% | Aggr 3sec Phase B 80th Current Magnitude Harmonics | float | 2 | R
0x3534 | 0x3535 | 13620 | 13621 | MAG_3S_HAR_I_80th_c_% | Aggr 3sec Phase C 80th Current Magnitude Harmonics | float | 2 | R
0x3536 | 0x3537 | 13622 | 13623 | MAG_3S_HAR_I_80th_n_% | Aggr 3sec Phase N 80th Current Magnitude Harmonics | float | 2 | R
0x3538 | 0x3539 | 13624 | 13625 | MAG_3S_HAR_V_81th_a_% | Aggr 3sec Phase A 81st Voltage Magnitude Harmonics | float | 2 | R
0x353A | 0x353B | 13626 | 13627 | MAG_3S_HAR_V_81th_b_% | Aggr 3sec Phase B 81st Voltage Magnitude Harmonics | float | 2 | R
0x353C | 0x353D | 13628 | 13629 | MAG_3S_HAR_V_81th_c_% | Aggr 3sec Phase C 81st Voltage Magnitude Harmonics | float | 2 | R
0x353E | 0x353F | 13630 | 13631 | MAG_3S_HAR_I_81th_a_% | Aggr 3sec Phase A 81st Current Magnitude Harmonics | float | 2 | R
0x3540 | 0x3541 | 13632 | 13633 | MAG_3S_HAR_I_81th_b_% | Aggr 3sec Phase B 81st Current Magnitude Harmonics | float | 2 | R
0x3542 | 0x3543 | 13634 | 13635 | MAG_3S_HAR_I_81th_c_% | Aggr 3sec Phase C 81st Current Magnitude Harmonics | float | 2 | R
0x3544 | 0x3545 | 13636 | 13637 | MAG_3S_HAR_I_81th_n_% | Aggr 3sec Phase N 81st Current Magnitude Harmonics | float | 2 | R
0x3546 | 0x3547 | 13638 | 13639 | MAG_3S_HAR_V_82th_a_% | Aggr 3sec Phase A 82nd Voltage Magnitude Harmonics | float | 2 | R
0x3548 | 0x3549 | 13640 | 13641 | MAG_3S_HAR_V_82th_b_% | Aggr 3sec Phase B 82nd Voltage Magnitude Harmonics | float | 2 | R
0x354A | 0x354B | 13642 | 13643 | MAG_3S_HAR_V_82th_c_% | Aggr 3sec Phase C 82nd Voltage Magnitude Harmonics | float | 2 | R
0x354C | 0x354D | 13644 | 13645 | MAG_3S_HAR_I_82th_a_% | Aggr 3sec Phase A 82nd Current Magnitude Harmonics | float | 2 | R
0x354E | 0x354F | 13646 | 13647 | MAG_3S_HAR_I_82th_b_% | Aggr 3sec Phase B 82nd Current Magnitude Harmonics | float | 2 | R
0x3550 | 0x3551 | 13648 | 13649 | MAG_3S_HAR_I_82th_c_% | Aggr 3sec Phase C 82nd Current Magnitude Harmonics | float | 2 | R
0x3552 | 0x3553 | 13650 | 13651 | MAG_3S_HAR_I_82th_n_% | Aggr 3sec Phase N 82nd Current Magnitude Harmonics | float | 2 | R
0x3554 | 0x3555 | 13652 | 13653 | MAG_3S_HAR_V_83th_a_% | Aggr 3sec Phase A 83rd Voltage Magnitude Harmonics | float | 2 | R
0x3556 | 0x3557 | 13654 | 13655 | MAG_3S_HAR_V_83th_b_% | Aggr 3sec Phase B 83rd Voltage Magnitude Harmonics | float | 2 | R
0x3558 | 0x3559 | 13656 | 13657 | MAG_3S_HAR_V_83th_c_% | Aggr 3sec Phase C 83rd Voltage Magnitude Harmonics | float | 2 | R
0x355A | 0x355B | 13658 | 13659 | MAG_3S_HAR_I_83th_a_% | Aggr 3sec Phase A 83rd Current Magnitude Harmonics | float | 2 | R
0x355C | 0x355D | 13660 | 13661 | MAG_3S_HAR_I_83th_b_% | Aggr 3sec Phase B 83rd Current Magnitude Harmonics | float | 2 | R
0x355E | 0x355F | 13662 | 13663 | MAG_3S_HAR_I_83th_c_% | Aggr 3sec Phase C 83rd Current Magnitude Harmonics | float | 2 | R
0x3560 | 0x3561 | 13664 | 13665 | MAG_3S_HAR_I_83th_n_% | Aggr 3sec Phase N 83rd Current Magnitude Harmonics | float | 2 | R
0x3562 | 0x3563 | 13666 | 13667 | MAG_3S_HAR_V_84th_a_% | Aggr 3sec Phase A 84th Voltage Magnitude Harmonics | float | 2 | R
0x3564 | 0x3565 | 13668 | 13669 | MAG_3S_HAR_V_84th_b_% | Aggr 3sec Phase B 84th Voltage Magnitude Harmonics | float | 2 | R
0x3566 | 0x3567 | 13670 | 13671 | MAG_3S_HAR_V_84th_c_% | Aggr 3sec Phase C 84th Voltage Magnitude Harmonics | float | 2 | R
0x3568 | 0x3569 | 13672 | 13673 | MAG_3S_HAR_I_84th_a_% | Aggr 3sec Phase A 84th Current Magnitude Harmonics | float | 2 | R
0x356A | 0x356B | 13674 | 13675 | MAG_3S_HAR_I_84th_b_% | Aggr 3sec Phase B 84th Current Magnitude Harmonics | float | 2 | R
0x356C | 0x356D | 13676 | 13677 | MAG_3S_HAR_I_84th_c_% | Aggr 3sec Phase C 84th Current Magnitude Harmonics | float | 2 | R
0x356E | 0x356F | 13678 | 13679 | MAG_3S_HAR_I_84th_n_% | Aggr 3sec Phase N 84th Current Magnitude Harmonics | float | 2 | R
0x3570 | 0x3571 | 13680 | 13681 | MAG_3S_HAR_V_85th_a_% | Aggr 3sec Phase A 85th Voltage Magnitude Harmonics | float | 2 | R
0x3572 | 0x3573 | 13682 | 13683 | MAG_3S_HAR_V_85th_b_% | Aggr 3sec Phase B 85th Voltage Magnitude Harmonics | float | 2 | R
0x3574 | 0x3575 | 13684 | 13685 | MAG_3S_HAR_V_85th_c_% | Aggr 3sec Phase C 85th Voltage Magnitude Harmonics | float | 2 | R
0x3576 | 0x3577 | 13686 | 13687 | MAG_3S_HAR_I_85th_a_% | Aggr 3sec Phase A 85th Current Magnitude Harmonics | float | 2 | R
0x3578 | 0x3579 | 13688 | 13689 | MAG_3S_HAR_I_85th_b_% | Aggr 3sec Phase B 85th Current Magnitude Harmonics | float | 2 | R
0x357A | 0x357B | 13690 | 13691 | MAG_3S_HAR_I_85th_c_% | Aggr 3sec Phase C 85th Current Magnitude Harmonics | float | 2 | R
0x357C | 0x357D | 13692 | 13693 | MAG_3S_HAR_I_85th_n_% | Aggr 3sec Phase N 85th Current Magnitude Harmonics | float | 2 | R
0x357E | 0x357F | 13694 | 13695 | MAG_3S_HAR_V_86th_a_% | Aggr 3sec Phase A 86th Voltage Magnitude Harmonics | float | 2 | R
0x3580 | 0x3581 | 13696 | 13697 | MAG_3S_HAR_V_86th_b_% | Aggr 3sec Phase B 86th Voltage Magnitude Harmonics | float | 2 | R
0x3582 | 0x3583 | 13698 | 13699 | MAG_3S_HAR_V_86th_c_% | Aggr 3sec Phase C 86th Voltage Magnitude Harmonics | float | 2 | R
0x3584 | 0x3585 | 13700 | 13701 | MAG_3S_HAR_I_86th_a_% | Aggr 3sec Phase A 86th Current Magnitude Harmonics | float | 2 | R
0x3586 | 0x3587 | 13702 | 13703 | MAG_3S_HAR_I_86th_b_% | Aggr 3sec Phase B 86th Current Magnitude Harmonics | float | 2 | R
0x3588 | 0x3589 | 13704 | 13705 | MAG_3S_HAR_I_86th_c_% | Aggr 3sec Phase C 86th Current Magnitude Harmonics | float | 2 | R
0x358A | 0x358B | 13706 | 13707 | MAG_3S_HAR_I_86th_n_% | Aggr 3sec Phase N 86th Current Magnitude Harmonics | float | 2 | R
0x358C | 0x358D | 13708 | 13709 | MAG_3S_HAR_V_87th_a_% | Aggr 3sec Phase A 87th Voltage Magnitude Harmonics | float | 2 | R
0x358E | 0x358F | 13710 | 13711 | MAG_3S_HAR_V_87th_b_% | Aggr 3sec Phase B 87th Voltage Magnitude Harmonics | float | 2 | R
0x3590 | 0x3591 | 13712 | 13713 | MAG_3S_HAR_V_87th_c_% | Aggr 3sec Phase C 87th Voltage Magnitude Harmonics | float | 2 | R
0x3592 | 0x3593 | 13714 | 13715 | MAG_3S_HAR_I_87th_a_% | Aggr 3sec Phase A 87th Current Magnitude Harmonics | float | 2 | R
0x3594 | 0x3595 | 13716 | 13717 | MAG_3S_HAR_I_87th_b_% | Aggr 3sec Phase B 87th Current Magnitude Harmonics | float | 2 | R
0x3596 | 0x3597 | 13718 | 13719 | MAG_3S_HAR_I_87th_c_% | Aggr 3sec Phase C 87th Current Magnitude Harmonics | float | 2 | R
0x3598 | 0x3599 | 13720 | 13721 | MAG_3S_HAR_I_87th_n_% | Aggr 3sec Phase N 87th Current Magnitude Harmonics | float | 2 | R
0x359A | 0x359B | 13722 | 13723 | MAG_3S_HAR_V_88th_a_% | Aggr 3sec Phase A 88th Voltage Magnitude Harmonics | float | 2 | R
0x359C | 0x359D | 13724 | 13725 | MAG_3S_HAR_V_88th_b_% | Aggr 3sec Phase B 88th Voltage Magnitude Harmonics | float | 2 | R
0x359E | 0x359F | 13726 | 13727 | MAG_3S_HAR_V_88th_c_% | Aggr 3sec Phase C 88th Voltage Magnitude Harmonics | float | 2 | R
0x35A0 | 0x35A1 | 13728 | 13729 | MAG_3S_HAR_I_88th_a_% | Aggr 3sec Phase A 88th Current Magnitude Harmonics | float | 2 | R
0x35A2 | 0x35A3 | 13730 | 13731 | MAG_3S_HAR_I_88th_b_% | Aggr 3sec Phase B 88th Current Magnitude Harmonics | float | 2 | R
0x35A4 | 0x35A5 | 13732 | 13733 | MAG_3S_HAR_I_88th_c_% | Aggr 3sec Phase C 88th Current Magnitude Harmonics | float | 2 | R
0x35A6 | 0x35A7 | 13734 | 13735 | MAG_3S_HAR_I_88th_n_% | Aggr 3sec Phase N 88th Current Magnitude Harmonics | float | 2 | R
0x35A8 | 0x35A9 | 13736 | 13737 | MAG_3S_HAR_V_89th_a_% | Aggr 3sec Phase A 89th Voltage Magnitude Harmonics | float | 2 | R
0x35AA | 0x35AB | 13738 | 13739 | MAG_3S_HAR_V_89th_b_% | Aggr 3sec Phase B 89th Voltage Magnitude Harmonics | float | 2 | R
0x35AC | 0x35AD | 13740 | 13741 | MAG_3S_HAR_V_89th_c_% | Aggr 3sec Phase C 89th Voltage Magnitude Harmonics | float | 2 | R
0x35AE | 0x35AF | 13742 | 13743 | MAG_3S_HAR_I_89th_a_% | Aggr 3sec Phase A 89th Current Magnitude Harmonics | float | 2 | R
0x35B0 | 0x35B1 | 13744 | 13745 | MAG_3S_HAR_I_89th_b_% | Aggr 3sec Phase B 89th Current Magnitude Harmonics | float | 2 | R
0x35B2 | 0x35B3 | 13746 | 13747 | MAG_3S_HAR_I_89th_c_% | Aggr 3sec Phase C 89th Current Magnitude Harmonics | float | 2 | R
0x35B4 | 0x35B5 | 13748 | 13749 | MAG_3S_HAR_I_89th_n_% | Aggr 3sec Phase N 89th Current Magnitude Harmonics | float | 2 | R
0x35B6 | 0x35B7 | 13750 | 13751 | MAG_3S_HAR_V_90th_a_% | Aggr 3sec Phase A 90th Voltage Magnitude Harmonics | float | 2 | R
0x35B8 | 0x35B9 | 13752 | 13753 | MAG_3S_HAR_V_90th_b_% | Aggr 3sec Phase B 90th Voltage Magnitude Harmonics | float | 2 | R
0x35BA | 0x35BB | 13754 | 13755 | MAG_3S_HAR_V_90th_c_% | Aggr 3sec Phase C 90th Voltage Magnitude Harmonics | float | 2 | R
0x35BC | 0x35BD | 13756 | 13757 | MAG_3S_HAR_I_90th_a_% | Aggr 3sec Phase A 90th Current Magnitude Harmonics | float | 2 | R
0x35BE | 0x35BF | 13758 | 13759 | MAG_3S_HAR_I_90th_b_% | Aggr 3sec Phase B 90th Current Magnitude Harmonics | float | 2 | R
0x35C0 | 0x35C1 | 13760 | 13761 | MAG_3S_HAR_I_90th_c_% | Aggr 3sec Phase C 90th Current Magnitude Harmonics | float | 2 | R
0x35C2 | 0x35C3 | 13762 | 13763 | MAG_3S_HAR_I_90th_n_% | Aggr 3sec Phase N 90th Current Magnitude Harmonics | float | 2 | R
0x35C4 | 0x35C5 | 13764 | 13765 | MAG_3S_HAR_V_91th_a_% | Aggr 3sec Phase A 91st Voltage Magnitude Harmonics | float | 2 | R
0x35C6 | 0x35C7 | 13766 | 13767 | MAG_3S_HAR_V_91th_b_% | Aggr 3sec Phase B 91st Voltage Magnitude Harmonics | float | 2 | R
0x35C8 | 0x35C9 | 13768 | 13769 | MAG_3S_HAR_V_91th_c_% | Aggr 3sec Phase C 91st Voltage Magnitude Harmonics | float | 2 | R
0x35CA | 0x35CB | 13770 | 13771 | MAG_3S_HAR_I_91th_a_% | Aggr 3sec Phase A 91st Current Magnitude Harmonics | float | 2 | R
0x35CC | 0x35CD | 13772 | 13773 | MAG_3S_HAR_I_91th_b_% | Aggr 3sec Phase B 91st Current Magnitude Harmonics | float | 2 | R
0x35CE | 0x35CF | 13774 | 13775 | MAG_3S_HAR_I_91th_c_% | Aggr 3sec Phase C 91st Current Magnitude Harmonics | float | 2 | R
0x35D0 | 0x35D1 | 13776 | 13777 | MAG_3S_HAR_I_91th_n_% | Aggr 3sec Phase N 91st Current Magnitude Harmonics | float | 2 | R
0x35D2 | 0x35D3 | 13778 | 13779 | MAG_3S_HAR_V_92th_a_% | Aggr 3sec Phase A 92nd Voltage Magnitude Harmonics | float | 2 | R
0x35D4 | 0x35D5 | 13780 | 13781 | MAG_3S_HAR_V_92th_b_% | Aggr 3sec Phase B 92nd Voltage Magnitude Harmonics | float | 2 | R
0x35D6 | 0x35D7 | 13782 | 13783 | MAG_3S_HAR_V_92th_c_% | Aggr 3sec Phase C 92nd Voltage Magnitude Harmonics | float | 2 | R
0x35D8 | 0x35D9 | 13784 | 13785 | MAG_3S_HAR_I_92th_a_% | Aggr 3sec Phase A 92nd Current Magnitude Harmonics | float | 2 | R
0x35DA | 0x35DB | 13786 | 13787 | MAG_3S_HAR_I_92th_b_% | Aggr 3sec Phase B 92nd Current Magnitude Harmonics | float | 2 | R
0x35DC | 0x35DD | 13788 | 13789 | MAG_3S_HAR_I_92th_c_% | Aggr 3sec Phase C 92nd Current Magnitude Harmonics | float | 2 | R
0x35DE | 0x35DF | 13790 | 13791 | MAG_3S_HAR_I_92th_n_% | Aggr 3sec Phase N 92nd Current Magnitude Harmonics | float | 2 | R
0x35E0 | 0x35E1 | 13792 | 13793 | MAG_3S_HAR_V_93th_a_% | Aggr 3sec Phase A 93rd Voltage Magnitude Harmonics | float | 2 | R
0x35E2 | 0x35E3 | 13794 | 13795 | MAG_3S_HAR_V_93th_b_% | Aggr 3sec Phase B 93rd Voltage Magnitude Harmonics | float | 2 | R
0x35E4 | 0x35E5 | 13796 | 13797 | MAG_3S_HAR_V_93th_c_% | Aggr 3sec Phase C 93rd Voltage Magnitude Harmonics | float | 2 | R
0x35E6 | 0x35E7 | 13798 | 13799 | MAG_3S_HAR_I_93th_a_% | Aggr 3sec Phase A 93rd Current Magnitude Harmonics | float | 2 | R
0x35E8 | 0x35E9 | 13800 | 13801 | MAG_3S_HAR_I_93th_b_% | Aggr 3sec Phase B 93rd Current Magnitude Harmonics | float | 2 | R
0x35EA | 0x35EB | 13802 | 13803 | MAG_3S_HAR_I_93th_c_% | Aggr 3sec Phase C 93rd Current Magnitude Harmonics | float | 2 | R
0x35EC | 0x35ED | 13804 | 13805 | MAG_3S_HAR_I_93th_n_% | Aggr 3sec Phase N 93rd Current Magnitude Harmonics | float | 2 | R
0x35EE | 0x35EF | 13806 | 13807 | MAG_3S_HAR_V_94th_a_% | Aggr 3sec Phase A 94th Voltage Magnitude Harmonics | float | 2 | R
0x35F0 | 0x35F1 | 13808 | 13809 | MAG_3S_HAR_V_94th_b_% | Aggr 3sec Phase B 94th Voltage Magnitude Harmonics | float | 2 | R
0x35F2 | 0x35F3 | 13810 | 13811 | MAG_3S_HAR_V_94th_c_% | Aggr 3sec Phase C 94th Voltage Magnitude Harmonics | float | 2 | R
0x35F4 | 0x35F5 | 13812 | 13813 | MAG_3S_HAR_I_94th_a_% | Aggr 3sec Phase A 94th Current Magnitude Harmonics | float | 2 | R
0x35F6 | 0x35F7 | 13814 | 13815 | MAG_3S_HAR_I_94th_b_% | Aggr 3sec Phase B 94th Current Magnitude Harmonics | float | 2 | R
0x35F8 | 0x35F9 | 13816 | 13817 | MAG_3S_HAR_I_94th_c_% | Aggr 3sec Phase C 94th Current Magnitude Harmonics | float | 2 | R
0x35FA | 0x35FB | 13818 | 13819 | MAG_3S_HAR_I_94th_n_% | Aggr 3sec Phase N 94th Current Magnitude Harmonics | float | 2 | R
0x35FC | 0x35FD | 13820 | 13821 | MAG_3S_HAR_V_95th_a_% | Aggr 3sec Phase A 95th Voltage Magnitude Harmonics | float | 2 | R
0x35FE | 0x35FF | 13822 | 13823 | MAG_3S_HAR_V_95th_b_% | Aggr 3sec Phase B 95th Voltage Magnitude Harmonics | float | 2 | R
0x3600 | 0x3601 | 13824 | 13825 | MAG_3S_HAR_V_95th_c_% | Aggr 3sec Phase C 95th Voltage Magnitude Harmonics | float | 2 | R
0x3602 | 0x3603 | 13826 | 13827 | MAG_3S_HAR_I_95th_a_% | Aggr 3sec Phase A 95th Current Magnitude Harmonics | float | 2 | R
0x3604 | 0x3605 | 13828 | 13829 | MAG_3S_HAR_I_95th_b_% | Aggr 3sec Phase B 95th Current Magnitude Harmonics | float | 2 | R
0x3606 | 0x3607 | 13830 | 13831 | MAG_3S_HAR_I_95th_c_% | Aggr 3sec Phase C 95th Current Magnitude Harmonics | float | 2 | R
0x3608 | 0x3609 | 13832 | 13833 | MAG_3S_HAR_I_95th_n_% | Aggr 3sec Phase N 95th Current Magnitude Harmonics | float | 2 | R
0x360A | 0x360B | 13834 | 13835 | MAG_3S_HAR_V_96th_a_% | Aggr 3sec Phase A 96th Voltage Magnitude Harmonics | float | 2 | R
0x360C | 0x360D | 13836 | 13837 | MAG_3S_HAR_V_96th_b_% | Aggr 3sec Phase B 96th Voltage Magnitude Harmonics | float | 2 | R
0x360E | 0x360F | 13838 | 13839 | MAG_3S_HAR_V_96th_c_% | Aggr 3sec Phase C 96th Voltage Magnitude Harmonics | float | 2 | R
0x3610 | 0x3611 | 13840 | 13841 | MAG_3S_HAR_I_96th_a_% | Aggr 3sec Phase A 96th Current Magnitude Harmonics | float | 2 | R
0x3612 | 0x3613 | 13842 | 13843 | MAG_3S_HAR_I_96th_b_% | Aggr 3sec Phase B 96th Current Magnitude Harmonics | float | 2 | R
0x3614 | 0x3615 | 13844 | 13845 | MAG_3S_HAR_I_96th_c_% | Aggr 3sec Phase C 96th Current Magnitude Harmonics | float | 2 | R
0x3616 | 0x3617 | 13846 | 13847 | MAG_3S_HAR_I_96th_n_% | Aggr 3sec Phase N 96th Current Magnitude Harmonics | float | 2 | R
0x3618 | 0x3619 | 13848 | 13849 | MAG_3S_HAR_V_97th_a_% | Aggr 3sec Phase A 97th Voltage Magnitude Harmonics | float | 2 | R
0x361A | 0x361B | 13850 | 13851 | MAG_3S_HAR_V_97th_b_% | Aggr 3sec Phase B 97th Voltage Magnitude Harmonics | float | 2 | R
0x361C | 0x361D | 13852 | 13853 | MAG_3S_HAR_V_97th_c_% | Aggr 3sec Phase C 97th Voltage Magnitude Harmonics | float | 2 | R
0x361E | 0x361F | 13854 | 13855 | MAG_3S_HAR_I_97th_a_% | Aggr 3sec Phase A 97th Current Magnitude Harmonics | float | 2 | R
0x3620 | 0x3621 | 13856 | 13857 | MAG_3S_HAR_I_97th_b_% | Aggr 3sec Phase B 97th Current Magnitude Harmonics | float | 2 | R
0x3622 | 0x3623 | 13858 | 13859 | MAG_3S_HAR_I_97th_c_% | Aggr 3sec Phase C 97th Current Magnitude Harmonics | float | 2 | R
0x3624 | 0x3625 | 13860 | 13861 | MAG_3S_HAR_I_97th_n_% | Aggr 3sec Phase N 97th Current Magnitude Harmonics | float | 2 | R
0x3626 | 0x3627 | 13862 | 13863 | MAG_3S_HAR_V_98th_a_% | Aggr 3sec Phase A 98th Voltage Magnitude Harmonics | float | 2 | R
0x3628 | 0x3629 | 13864 | 13865 | MAG_3S_HAR_V_98th_b_% | Aggr 3sec Phase B 98th Voltage Magnitude Harmonics | float | 2 | R
0x362A | 0x362B | 13866 | 13867 | MAG_3S_HAR_V_98th_c_% | Aggr 3sec Phase C 98th Voltage Magnitude Harmonics | float | 2 | R
0x362C | 0x362D | 13868 | 13869 | MAG_3S_HAR_I_98th_a_% | Aggr 3sec Phase A 98th Current Magnitude Harmonics | float | 2 | R
0x362E | 0x362F | 13870 | 13871 | MAG_3S_HAR_I_98th_b_% | Aggr 3sec Phase B 98th Current Magnitude Harmonics | float | 2 | R
0x3630 | 0x3631 | 13872 | 13873 | MAG_3S_HAR_I_98th_c_% | Aggr 3sec Phase C 98th Current Magnitude Harmonics | float | 2 | R
0x3632 | 0x3633 | 13874 | 13875 | MAG_3S_HAR_I_98th_n_% | Aggr 3sec Phase N 98th Current Magnitude Harmonics | float | 2 | R
0x3634 | 0x3635 | 13876 | 13877 | MAG_3S_HAR_V_99th_a_% | Aggr 3sec Phase A 99th Voltage Magnitude Harmonics | float | 2 | R
0x3636 | 0x3637 | 13878 | 13879 | MAG_3S_HAR_V_99th_b_% | Aggr 3sec Phase B 99th Voltage Magnitude Harmonics | float | 2 | R
0x3638 | 0x3639 | 13880 | 13881 | MAG_3S_HAR_V_99th_c_% | Aggr 3sec Phase C 99th Voltage Magnitude Harmonics | float | 2 | R
0x363A | 0x363B | 13882 | 13883 | MAG_3S_HAR_I_99th_a_% | Aggr 3sec Phase A 99th Current Magnitude Harmonics | float | 2 | R
0x363C | 0x363D | 13884 | 13885 | MAG_3S_HAR_I_99th_b_% | Aggr 3sec Phase B 99th Current Magnitude Harmonics | float | 2 | R
0x363E | 0x363F | 13886 | 13887 | MAG_3S_HAR_I_99th_c_% | Aggr 3sec Phase C 99th Current Magnitude Harmonics | float | 2 | R
0x3640 | 0x3641 | 13888 | 13889 | MAG_3S_HAR_I_99th_n_% | Aggr 3sec Phase N 99th Current Magnitude Harmonics | float | 2 | R
0x3642 | 0x3643 | 13890 | 13891 | MAG_3S_HAR_V_100th_a_% | Aggr 3sec Phase A 100th Voltage Magnitude Harmonics | float | 2 | R
0x3644 | 0x3645 | 13892 | 13893 | MAG_3S_HAR_V_100th_b_% | Aggr 3sec Phase B 100th Voltage Magnitude Harmonics | float | 2 | R
0x3646 | 0x3647 | 13894 | 13895 | MAG_3S_HAR_V_100th_c_% | Aggr 3sec Phase C 100th Voltage Magnitude Harmonics | float | 2 | R
0x3648 | 0x3649 | 13896 | 13897 | MAG_3S_HAR_I_100th_a_% | Aggr 3sec Phase A 100th Current Magnitude Harmonics | float | 2 | R
0x364A | 0x364B | 13898 | 13899 | MAG_3S_HAR_I_100th_b_% | Aggr 3sec Phase B 100th Current Magnitude Harmonics | float | 2 | R
0x364C | 0x364D | 13900 | 13901 | MAG_3S_HAR_I_100th_c_% | Aggr 3sec Phase C 100th Current Magnitude Harmonics | float | 2 | R
0x364E | 0x364F | 13902 | 13903 | MAG_3S_HAR_I_100th_n_% | Aggr 3sec Phase N 100th Current Magnitude Harmonics | float | 2 | R
0x3650 | 0x3651 | 13904 | 13905 | MAG_3S_HAR_V_101th_a_% | Aggr 3sec Phase A 101st Voltage Magnitude Harmonics | float | 2 | R
0x3652 | 0x3653 | 13906 | 13907 | MAG_3S_HAR_V_101th_b_% | Aggr 3sec Phase B 101st Voltage Magnitude Harmonics | float | 2 | R
0x3654 | 0x3655 | 13908 | 13909 | MAG_3S_HAR_V_101th_c_% | Aggr 3sec Phase C 101st Voltage Magnitude Harmonics | float | 2 | R
0x3656 | 0x3657 | 13910 | 13911 | MAG_3S_HAR_I_101th_a_% | Aggr 3sec Phase A 101st Current Magnitude Harmonics | float | 2 | R
0x3658 | 0x3659 | 13912 | 13913 | MAG_3S_HAR_I_101th_b_% | Aggr 3sec Phase B 101st Current Magnitude Harmonics | float | 2 | R
0x365A | 0x365B | 13914 | 13915 | MAG_3S_HAR_I_101th_c_% | Aggr 3sec Phase C 101st Current Magnitude Harmonics | float | 2 | R
0x365C | 0x365D | 13916 | 13917 | MAG_3S_HAR_I_101th_n_% | Aggr 3sec Phase N 101st Current Magnitude Harmonics | float | 2 | R
0x365E | 0x365F | 13918 | 13919 | MAG_3S_HAR_V_102th_a_% | Aggr 3sec Phase A 102nd Voltage Magnitude Harmonics | float | 2 | R
0x3660 | 0x3661 | 13920 | 13921 | MAG_3S_HAR_V_102th_b_% | Aggr 3sec Phase B 102nd Voltage Magnitude Harmonics | float | 2 | R
0x3662 | 0x3663 | 13922 | 13923 | MAG_3S_HAR_V_102th_c_% | Aggr 3sec Phase C 102nd Voltage Magnitude Harmonics | float | 2 | R
0x3664 | 0x3665 | 13924 | 13925 | MAG_3S_HAR_I_102th_a_% | Aggr 3sec Phase A 102nd Current Magnitude Harmonics | float | 2 | R
0x3666 | 0x3667 | 13926 | 13927 | MAG_3S_HAR_I_102th_b_% | Aggr 3sec Phase B 102nd Current Magnitude Harmonics | float | 2 | R
0x3668 | 0x3669 | 13928 | 13929 | MAG_3S_HAR_I_102th_c_% | Aggr 3sec Phase C 102nd Current Magnitude Harmonics | float | 2 | R
0x366A | 0x366B | 13930 | 13931 | MAG_3S_HAR_I_102th_n_% | Aggr 3sec Phase N 102nd Current Magnitude Harmonics | float | 2 | R
0x366C | 0x366D | 13932 | 13933 | MAG_3S_HAR_V_103th_a_% | Aggr 3sec Phase A 103rd Voltage Magnitude Harmonics | float | 2 | R
0x366E | 0x366F | 13934 | 13935 | MAG_3S_HAR_V_103th_b_% | Aggr 3sec Phase B 103rd Voltage Magnitude Harmonics | float | 2 | R
0x3670 | 0x3671 | 13936 | 13937 | MAG_3S_HAR_V_103th_c_% | Aggr 3sec Phase C 103rd Voltage Magnitude Harmonics | float | 2 | R
0x3672 | 0x3673 | 13938 | 13939 | MAG_3S_HAR_I_103th_a_% | Aggr 3sec Phase A 103rd Current Magnitude Harmonics | float | 2 | R
0x3674 | 0x3675 | 13940 | 13941 | MAG_3S_HAR_I_103th_b_% | Aggr 3sec Phase B 103rd Current Magnitude Harmonics | float | 2 | R
0x3676 | 0x3677 | 13942 | 13943 | MAG_3S_HAR_I_103th_c_% | Aggr 3sec Phase C 103rd Current Magnitude Harmonics | float | 2 | R
0x3678 | 0x3679 | 13944 | 13945 | MAG_3S_HAR_I_103th_n_% | Aggr 3sec Phase N 103rd Current Magnitude Harmonics | float | 2 | R
0x367A | 0x367B | 13946 | 13947 | MAG_3S_HAR_V_104th_a_% | Aggr 3sec Phase A 104th Voltage Magnitude Harmonics | float | 2 | R
0x367C | 0x367D | 13948 | 13949 | MAG_3S_HAR_V_104th_b_% | Aggr 3sec Phase B 104th Voltage Magnitude Harmonics | float | 2 | R
0x367E | 0x367F | 13950 | 13951 | MAG_3S_HAR_V_104th_c_% | Aggr 3sec Phase C 104th Voltage Magnitude Harmonics | float | 2 | R
0x3680 | 0x3681 | 13952 | 13953 | MAG_3S_HAR_I_104th_a_% | Aggr 3sec Phase A 104th Current Magnitude Harmonics | float | 2 | R
0x3682 | 0x3683 | 13954 | 13955 | MAG_3S_HAR_I_104th_b_% | Aggr 3sec Phase B 104th Current Magnitude Harmonics | float | 2 | R
0x3684 | 0x3685 | 13956 | 13957 | MAG_3S_HAR_I_104th_c_% | Aggr 3sec Phase C 104th Current Magnitude Harmonics | float | 2 | R
0x3686 | 0x3687 | 13958 | 13959 | MAG_3S_HAR_I_104th_n_% | Aggr 3sec Phase N 104th Current Magnitude Harmonics | float | 2 | R
0x3688 | 0x3689 | 13960 | 13961 | MAG_3S_HAR_V_105th_a_% | Aggr 3sec Phase A 105th Voltage Magnitude Harmonics | float | 2 | R
0x368A | 0x368B | 13962 | 13963 | MAG_3S_HAR_V_105th_b_% | Aggr 3sec Phase B 105th Voltage Magnitude Harmonics | float | 2 | R
0x368C | 0x368D | 13964 | 13965 | MAG_3S_HAR_V_105th_c_% | Aggr 3sec Phase C 105th Voltage Magnitude Harmonics | float | 2 | R
0x368E | 0x368F | 13966 | 13967 | MAG_3S_HAR_I_105th_a_% | Aggr 3sec Phase A 105th Current Magnitude Harmonics | float | 2 | R
0x3690 | 0x3691 | 13968 | 13969 | MAG_3S_HAR_I_105th_b_% | Aggr 3sec Phase B 105th Current Magnitude Harmonics | float | 2 | R
0x3692 | 0x3693 | 13970 | 13971 | MAG_3S_HAR_I_105th_c_% | Aggr 3sec Phase C 105th Current Magnitude Harmonics | float | 2 | R
0x3694 | 0x3695 | 13972 | 13973 | MAG_3S_HAR_I_105th_n_% | Aggr 3sec Phase N 105th Current Magnitude Harmonics | float | 2 | R
0x3696 | 0x3697 | 13974 | 13975 | MAG_3S_HAR_V_106th_a_% | Aggr 3sec Phase A 106th Voltage Magnitude Harmonics | float | 2 | R
0x3698 | 0x3699 | 13976 | 13977 | MAG_3S_HAR_V_106th_b_% | Aggr 3sec Phase B 106th Voltage Magnitude Harmonics | float | 2 | R
0x369A | 0x369B | 13978 | 13979 | MAG_3S_HAR_V_106th_c_% | Aggr 3sec Phase C 106th Voltage Magnitude Harmonics | float | 2 | R
0x369C | 0x369D | 13980 | 13981 | MAG_3S_HAR_I_106th_a_% | Aggr 3sec Phase A 106th Current Magnitude Harmonics | float | 2 | R
0x369E | 0x369F | 13982 | 13983 | MAG_3S_HAR_I_106th_b_% | Aggr 3sec Phase B 106th Current Magnitude Harmonics | float | 2 | R
0x36A0 | 0x36A1 | 13984 | 13985 | MAG_3S_HAR_I_106th_c_% | Aggr 3sec Phase C 106th Current Magnitude Harmonics | float | 2 | R
0x36A2 | 0x36A3 | 13986 | 13987 | MAG_3S_HAR_I_106th_n_% | Aggr 3sec Phase N 106th Current Magnitude Harmonics | float | 2 | R
0x36A4 | 0x36A5 | 13988 | 13989 | MAG_3S_HAR_V_107th_a_% | Aggr 3sec Phase A 107th Voltage Magnitude Harmonics | float | 2 | R
0x36A6 | 0x36A7 | 13990 | 13991 | MAG_3S_HAR_V_107th_b_% | Aggr 3sec Phase B 107th Voltage Magnitude Harmonics | float | 2 | R
0x36A8 | 0x36A9 | 13992 | 13993 | MAG_3S_HAR_V_107th_c_% | Aggr 3sec Phase C 107th Voltage Magnitude Harmonics | float | 2 | R
0x36AA | 0x36AB | 13994 | 13995 | MAG_3S_HAR_I_107th_a_% | Aggr 3sec Phase A 107th Current Magnitude Harmonics | float | 2 | R
0x36AC | 0x36AD | 13996 | 13997 | MAG_3S_HAR_I_107th_b_% | Aggr 3sec Phase B 107th Current Magnitude Harmonics | float | 2 | R
0x36AE | 0x36AF | 13998 | 13999 | MAG_3S_HAR_I_107th_c_% | Aggr 3sec Phase C 107th Current Magnitude Harmonics | float | 2 | R
0x36B0 | 0x36B1 | 14000 | 14001 | MAG_3S_HAR_I_107th_n_% | Aggr 3sec Phase N 107th Current Magnitude Harmonics | float | 2 | R
0x36B2 | 0x36B3 | 14002 | 14003 | MAG_3S_HAR_V_108th_a_% | Aggr 3sec Phase A 108th Voltage Magnitude Harmonics | float | 2 | R
0x36B4 | 0x36B5 | 14004 | 14005 | MAG_3S_HAR_V_108th_b_% | Aggr 3sec Phase B 108th Voltage Magnitude Harmonics | float | 2 | R
0x36B6 | 0x36B7 | 14006 | 14007 | MAG_3S_HAR_V_108th_c_% | Aggr 3sec Phase C 108th Voltage Magnitude Harmonics | float | 2 | R
0x36B8 | 0x36B9 | 14008 | 14009 | MAG_3S_HAR_I_108th_a_% | Aggr 3sec Phase A 108th Current Magnitude Harmonics | float | 2 | R
0x36BA | 0x36BB | 14010 | 14011 | MAG_3S_HAR_I_108th_b_% | Aggr 3sec Phase B 108th Current Magnitude Harmonics | float | 2 | R
0x36BC | 0x36BD | 14012 | 14013 | MAG_3S_HAR_I_108th_c_% | Aggr 3sec Phase C 108th Current Magnitude Harmonics | float | 2 | R
0x36BE | 0x36BF | 14014 | 14015 | MAG_3S_HAR_I_108th_n_% | Aggr 3sec Phase N 108th Current Magnitude Harmonics | float | 2 | R
0x36C0 | 0x36C1 | 14016 | 14017 | MAG_3S_HAR_V_109th_a_% | Aggr 3sec Phase A 109th Voltage Magnitude Harmonics | float | 2 | R
0x36C2 | 0x36C3 | 14018 | 14019 | MAG_3S_HAR_V_109th_b_% | Aggr 3sec Phase B 109th Voltage Magnitude Harmonics | float | 2 | R
0x36C4 | 0x36C5 | 14020 | 14021 | MAG_3S_HAR_V_109th_c_% | Aggr 3sec Phase C 109th Voltage Magnitude Harmonics | float | 2 | R
0x36C6 | 0x36C7 | 14022 | 14023 | MAG_3S_HAR_I_109th_a_% | Aggr 3sec Phase A 109th Current Magnitude Harmonics | float | 2 | R
0x36C8 | 0x36C9 | 14024 | 14025 | MAG_3S_HAR_I_109th_b_% | Aggr 3sec Phase B 109th Current Magnitude Harmonics | float | 2 | R
0x36CA | 0x36CB | 14026 | 14027 | MAG_3S_HAR_I_109th_c_% | Aggr 3sec Phase C 109th Current Magnitude Harmonics | float | 2 | R
0x36CC | 0x36CD | 14028 | 14029 | MAG_3S_HAR_I_109th_n_% | Aggr 3sec Phase N 109th Current Magnitude Harmonics | float | 2 | R
0x36CE | 0x36CF | 14030 | 14031 | MAG_3S_HAR_V_110th_a_% | Aggr 3sec Phase A 110th Voltage Magnitude Harmonics | float | 2 | R
0x36D0 | 0x36D1 | 14032 | 14033 | MAG_3S_HAR_V_110th_b_% | Aggr 3sec Phase B 110th Voltage Magnitude Harmonics | float | 2 | R
0x36D2 | 0x36D3 | 14034 | 14035 | MAG_3S_HAR_V_110th_c_% | Aggr 3sec Phase C 110th Voltage Magnitude Harmonics | float | 2 | R
0x36D4 | 0x36D5 | 14036 | 14037 | MAG_3S_HAR_I_110th_a_% | Aggr 3sec Phase A 110th Current Magnitude Harmonics | float | 2 | R
0x36D6 | 0x36D7 | 14038 | 14039 | MAG_3S_HAR_I_110th_b_% | Aggr 3sec Phase B 110th Current Magnitude Harmonics | float | 2 | R
0x36D8 | 0x36D9 | 14040 | 14041 | MAG_3S_HAR_I_110th_c_% | Aggr 3sec Phase C 110th Current Magnitude Harmonics | float | 2 | R
0x36DA | 0x36DB | 14042 | 14043 | MAG_3S_HAR_I_110th_n_% | Aggr 3sec Phase N 110th Current Magnitude Harmonics | float | 2 | R
0x36DC | 0x36DD | 14044 | 14045 | MAG_3S_HAR_V_111th_a_% | Aggr 3sec Phase A 111st Voltage Magnitude Harmonics | float | 2 | R
0x36DE | 0x36DF | 14046 | 14047 | MAG_3S_HAR_V_111th_b_% | Aggr 3sec Phase B 111st Voltage Magnitude Harmonics | float | 2 | R
0x36E0 | 0x36E1 | 14048 | 14049 | MAG_3S_HAR_V_111th_c_% | Aggr 3sec Phase C 111st Voltage Magnitude Harmonics | float | 2 | R
0x36E2 | 0x36E3 | 14050 | 14051 | MAG_3S_HAR_I_111th_a_% | Aggr 3sec Phase A 111st Current Magnitude Harmonics | float | 2 | R
0x36E4 | 0x36E5 | 14052 | 14053 | MAG_3S_HAR_I_111th_b_% | Aggr 3sec Phase B 111st Current Magnitude Harmonics | float | 2 | R
0x36E6 | 0x36E7 | 14054 | 14055 | MAG_3S_HAR_I_111th_c_% | Aggr 3sec Phase C 111st Current Magnitude Harmonics | float | 2 | R
0x36E8 | 0x36E9 | 14056 | 14057 | MAG_3S_HAR_I_111th_n_% | Aggr 3sec Phase N 111st Current Magnitude Harmonics | float | 2 | R
0x36EA | 0x36EB | 14058 | 14059 | MAG_3S_HAR_V_112th_a_% | Aggr 3sec Phase A 112nd Voltage Magnitude Harmonics | float | 2 | R
0x36EC | 0x36ED | 14060 | 14061 | MAG_3S_HAR_V_112th_b_% | Aggr 3sec Phase B 112nd Voltage Magnitude Harmonics | float | 2 | R
0x36EE | 0x36EF | 14062 | 14063 | MAG_3S_HAR_V_112th_c_% | Aggr 3sec Phase C 112nd Voltage Magnitude Harmonics | float | 2 | R
0x36F0 | 0x36F1 | 14064 | 14065 | MAG_3S_HAR_I_112th_a_% | Aggr 3sec Phase A 112nd Current Magnitude Harmonics | float | 2 | R
0x36F2 | 0x36F3 | 14066 | 14067 | MAG_3S_HAR_I_112th_b_% | Aggr 3sec Phase B 112nd Current Magnitude Harmonics | float | 2 | R
0x36F4 | 0x36F5 | 14068 | 14069 | MAG_3S_HAR_I_112th_c_% | Aggr 3sec Phase C 112nd Current Magnitude Harmonics | float | 2 | R
0x36F6 | 0x36F7 | 14070 | 14071 | MAG_3S_HAR_I_112th_n_% | Aggr 3sec Phase N 112nd Current Magnitude Harmonics | float | 2 | R
0x36F8 | 0x36F9 | 14072 | 14073 | MAG_3S_HAR_V_113th_a_% | Aggr 3sec Phase A 113rd Voltage Magnitude Harmonics | float | 2 | R
0x36FA | 0x36FB | 14074 | 14075 | MAG_3S_HAR_V_113th_b_% | Aggr 3sec Phase B 113rd Voltage Magnitude Harmonics | float | 2 | R
0x36FC | 0x36FD | 14076 | 14077 | MAG_3S_HAR_V_113th_c_% | Aggr 3sec Phase C 113rd Voltage Magnitude Harmonics | float | 2 | R
0x36FE | 0x36FF | 14078 | 14079 | MAG_3S_HAR_I_113th_a_% | Aggr 3sec Phase A 113rd Current Magnitude Harmonics | float | 2 | R
0x3700 | 0x3701 | 14080 | 14081 | MAG_3S_HAR_I_113th_b_% | Aggr 3sec Phase B 113rd Current Magnitude Harmonics | float | 2 | R
0x3702 | 0x3703 | 14082 | 14083 | MAG_3S_HAR_I_113th_c_% | Aggr 3sec Phase C 113rd Current Magnitude Harmonics | float | 2 | R
0x3704 | 0x3705 | 14084 | 14085 | MAG_3S_HAR_I_113th_n_% | Aggr 3sec Phase N 113rd Current Magnitude Harmonics | float | 2 | R
0x3706 | 0x3707 | 14086 | 14087 | MAG_3S_HAR_V_114th_a_% | Aggr 3sec Phase A 114th Voltage Magnitude Harmonics | float | 2 | R
0x3708 | 0x3709 | 14088 | 14089 | MAG_3S_HAR_V_114th_b_% | Aggr 3sec Phase B 114th Voltage Magnitude Harmonics | float | 2 | R
0x370A | 0x370B | 14090 | 14091 | MAG_3S_HAR_V_114th_c_% | Aggr 3sec Phase C 114th Voltage Magnitude Harmonics | float | 2 | R
0x370C | 0x370D | 14092 | 14093 | MAG_3S_HAR_I_114th_a_% | Aggr 3sec Phase A 114th Current Magnitude Harmonics | float | 2 | R
0x370E | 0x370F | 14094 | 14095 | MAG_3S_HAR_I_114th_b_% | Aggr 3sec Phase B 114th Current Magnitude Harmonics | float | 2 | R
0x3710 | 0x3711 | 14096 | 14097 | MAG_3S_HAR_I_114th_c_% | Aggr 3sec Phase C 114th Current Magnitude Harmonics | float | 2 | R
0x3712 | 0x3713 | 14098 | 14099 | MAG_3S_HAR_I_114th_n_% | Aggr 3sec Phase N 114th Current Magnitude Harmonics | float | 2 | R
0x3714 | 0x3715 | 14100 | 14101 | MAG_3S_HAR_V_115th_a_% | Aggr 3sec Phase A 115th Voltage Magnitude Harmonics | float | 2 | R
0x3716 | 0x3717 | 14102 | 14103 | MAG_3S_HAR_V_115th_b_% | Aggr 3sec Phase B 115th Voltage Magnitude Harmonics | float | 2 | R
0x3718 | 0x3719 | 14104 | 14105 | MAG_3S_HAR_V_115th_c_% | Aggr 3sec Phase C 115th Voltage Magnitude Harmonics | float | 2 | R
0x371A | 0x371B | 14106 | 14107 | MAG_3S_HAR_I_115th_a_% | Aggr 3sec Phase A 115th Current Magnitude Harmonics | float | 2 | R
0x371C | 0x371D | 14108 | 14109 | MAG_3S_HAR_I_115th_b_% | Aggr 3sec Phase B 115th Current Magnitude Harmonics | float | 2 | R
0x371E | 0x371F | 14110 | 14111 | MAG_3S_HAR_I_115th_c_% | Aggr 3sec Phase C 115th Current Magnitude Harmonics | float | 2 | R
0x3720 | 0x3721 | 14112 | 14113 | MAG_3S_HAR_I_115th_n_% | Aggr 3sec Phase N 115th Current Magnitude Harmonics | float | 2 | R
0x3722 | 0x3723 | 14114 | 14115 | MAG_3S_HAR_V_116th_a_% | Aggr 3sec Phase A 116th Voltage Magnitude Harmonics | float | 2 | R
0x3724 | 0x3725 | 14116 | 14117 | MAG_3S_HAR_V_116th_b_% | Aggr 3sec Phase B 116th Voltage Magnitude Harmonics | float | 2 | R
0x3726 | 0x3727 | 14118 | 14119 | MAG_3S_HAR_V_116th_c_% | Aggr 3sec Phase C 116th Voltage Magnitude Harmonics | float | 2 | R
0x3728 | 0x3729 | 14120 | 14121 | MAG_3S_HAR_I_116th_a_% | Aggr 3sec Phase A 116th Current Magnitude Harmonics | float | 2 | R
0x372A | 0x372B | 14122 | 14123 | MAG_3S_HAR_I_116th_b_% | Aggr 3sec Phase B 116th Current Magnitude Harmonics | float | 2 | R
0x372C | 0x372D | 14124 | 14125 | MAG_3S_HAR_I_116th_c_% | Aggr 3sec Phase C 116th Current Magnitude Harmonics | float | 2 | R
0x372E | 0x372F | 14126 | 14127 | MAG_3S_HAR_I_116th_n_% | Aggr 3sec Phase N 116th Current Magnitude Harmonics | float | 2 | R
0x3730 | 0x3731 | 14128 | 14129 | MAG_3S_HAR_V_117th_a_% | Aggr 3sec Phase A 117th Voltage Magnitude Harmonics | float | 2 | R
0x3732 | 0x3733 | 14130 | 14131 | MAG_3S_HAR_V_117th_b_% | Aggr 3sec Phase B 117th Voltage Magnitude Harmonics | float | 2 | R
0x3734 | 0x3735 | 14132 | 14133 | MAG_3S_HAR_V_117th_c_% | Aggr 3sec Phase C 117th Voltage Magnitude Harmonics | float | 2 | R
0x3736 | 0x3737 | 14134 | 14135 | MAG_3S_HAR_I_117th_a_% | Aggr 3sec Phase A 117th Current Magnitude Harmonics | float | 2 | R
0x3738 | 0x3739 | 14136 | 14137 | MAG_3S_HAR_I_117th_b_% | Aggr 3sec Phase B 117th Current Magnitude Harmonics | float | 2 | R
0x373A | 0x373B | 14138 | 14139 | MAG_3S_HAR_I_117th_c_% | Aggr 3sec Phase C 117th Current Magnitude Harmonics | float | 2 | R
0x373C | 0x373D | 14140 | 14141 | MAG_3S_HAR_I_117th_n_% | Aggr 3sec Phase N 117th Current Magnitude Harmonics | float | 2 | R
0x373E | 0x373F | 14142 | 14143 | MAG_3S_HAR_V_118th_a_% | Aggr 3sec Phase A 118th Voltage Magnitude Harmonics | float | 2 | R
0x3740 | 0x3741 | 14144 | 14145 | MAG_3S_HAR_V_118th_b_% | Aggr 3sec Phase B 118th Voltage Magnitude Harmonics | float | 2 | R
0x3742 | 0x3743 | 14146 | 14147 | MAG_3S_HAR_V_118th_c_% | Aggr 3sec Phase C 118th Voltage Magnitude Harmonics | float | 2 | R
0x3744 | 0x3745 | 14148 | 14149 | MAG_3S_HAR_I_118th_a_% | Aggr 3sec Phase A 118th Current Magnitude Harmonics | float | 2 | R
0x3746 | 0x3747 | 14150 | 14151 | MAG_3S_HAR_I_118th_b_% | Aggr 3sec Phase B 118th Current Magnitude Harmonics | float | 2 | R
0x3748 | 0x3749 | 14152 | 14153 | MAG_3S_HAR_I_118th_c_% | Aggr 3sec Phase C 118th Current Magnitude Harmonics | float | 2 | R
0x374A | 0x374B | 14154 | 14155 | MAG_3S_HAR_I_118th_n_% | Aggr 3sec Phase N 118th Current Magnitude Harmonics | float | 2 | R
0x374C | 0x374D | 14156 | 14157 | MAG_3S_HAR_V_119th_a_% | Aggr 3sec Phase A 119th Voltage Magnitude Harmonics | float | 2 | R
0x374E | 0x374F | 14158 | 14159 | MAG_3S_HAR_V_119th_b_% | Aggr 3sec Phase B 119th Voltage Magnitude Harmonics | float | 2 | R
0x3750 | 0x3751 | 14160 | 14161 | MAG_3S_HAR_V_119th_c_% | Aggr 3sec Phase C 119th Voltage Magnitude Harmonics | float | 2 | R
0x3752 | 0x3753 | 14162 | 14163 | MAG_3S_HAR_I_119th_a_% | Aggr 3sec Phase A 119th Current Magnitude Harmonics | float | 2 | R
0x3754 | 0x3755 | 14164 | 14165 | MAG_3S_HAR_I_119th_b_% | Aggr 3sec Phase B 119th Current Magnitude Harmonics | float | 2 | R
0x3756 | 0x3757 | 14166 | 14167 | MAG_3S_HAR_I_119th_c_% | Aggr 3sec Phase C 119th Current Magnitude Harmonics | float | 2 | R
0x3758 | 0x3759 | 14168 | 14169 | MAG_3S_HAR_I_119th_n_% | Aggr 3sec Phase N 119th Current Magnitude Harmonics | float | 2 | R
0x375A | 0x375B | 14170 | 14171 | MAG_3S_HAR_V_120th_a_% | Aggr 3sec Phase A 120th Voltage Magnitude Harmonics | float | 2 | R
0x375C | 0x375D | 14172 | 14173 | MAG_3S_HAR_V_120th_b_% | Aggr 3sec Phase B 120th Voltage Magnitude Harmonics | float | 2 | R
0x375E | 0x375F | 14174 | 14175 | MAG_3S_HAR_V_120th_c_% | Aggr 3sec Phase C 120th Voltage Magnitude Harmonics | float | 2 | R
0x3760 | 0x3761 | 14176 | 14177 | MAG_3S_HAR_I_120th_a_% | Aggr 3sec Phase A 120th Current Magnitude Harmonics | float | 2 | R
0x3762 | 0x3763 | 14178 | 14179 | MAG_3S_HAR_I_120th_b_% | Aggr 3sec Phase B 120th Current Magnitude Harmonics | float | 2 | R
0x3764 | 0x3765 | 14180 | 14181 | MAG_3S_HAR_I_120th_c_% | Aggr 3sec Phase C 120th Current Magnitude Harmonics | float | 2 | R
0x3766 | 0x3767 | 14182 | 14183 | MAG_3S_HAR_I_120th_n_% | Aggr 3sec Phase N 120th Current Magnitude Harmonics | float | 2 | R
0x3768 | 0x3769 | 14184 | 14185 | MAG_3S_HAR_V_121th_a_% | Aggr 3sec Phase A 121st Voltage Magnitude Harmonics | float | 2 | R
0x376A | 0x376B | 14186 | 14187 | MAG_3S_HAR_V_121th_b_% | Aggr 3sec Phase B 121st Voltage Magnitude Harmonics | float | 2 | R
0x376C | 0x376D | 14188 | 14189 | MAG_3S_HAR_V_121th_c_% | Aggr 3sec Phase C 121st Voltage Magnitude Harmonics | float | 2 | R
0x376E | 0x376F | 14190 | 14191 | MAG_3S_HAR_I_121th_a_% | Aggr 3sec Phase A 121st Current Magnitude Harmonics | float | 2 | R
0x3770 | 0x3771 | 14192 | 14193 | MAG_3S_HAR_I_121th_b_% | Aggr 3sec Phase B 121st Current Magnitude Harmonics | float | 2 | R
0x3772 | 0x3773 | 14194 | 14195 | MAG_3S_HAR_I_121th_c_% | Aggr 3sec Phase C 121st Current Magnitude Harmonics | float | 2 | R
0x3774 | 0x3775 | 14196 | 14197 | MAG_3S_HAR_I_121th_n_% | Aggr 3sec Phase N 121st Current Magnitude Harmonics | float | 2 | R
0x3776 | 0x3777 | 14198 | 14199 | MAG_3S_HAR_V_122th_a_% | Aggr 3sec Phase A 122nd Voltage Magnitude Harmonics | float | 2 | R
0x3778 | 0x3779 | 14200 | 14201 | MAG_3S_HAR_V_122th_b_% | Aggr 3sec Phase B 122nd Voltage Magnitude Harmonics | float | 2 | R
0x377A | 0x377B | 14202 | 14203 | MAG_3S_HAR_V_122th_c_% | Aggr 3sec Phase C 122nd Voltage Magnitude Harmonics | float | 2 | R
0x377C | 0x377D | 14204 | 14205 | MAG_3S_HAR_I_122th_a_% | Aggr 3sec Phase A 122nd Current Magnitude Harmonics | float | 2 | R
0x377E | 0x377F | 14206 | 14207 | MAG_3S_HAR_I_122th_b_% | Aggr 3sec Phase B 122nd Current Magnitude Harmonics | float | 2 | R
0x3780 | 0x3781 | 14208 | 14209 | MAG_3S_HAR_I_122th_c_% | Aggr 3sec Phase C 122nd Current Magnitude Harmonics | float | 2 | R
0x3782 | 0x3783 | 14210 | 14211 | MAG_3S_HAR_I_122th_n_% | Aggr 3sec Phase N 122nd Current Magnitude Harmonics | float | 2 | R
0x3784 | 0x3785 | 14212 | 14213 | MAG_3S_HAR_V_123th_a_% | Aggr 3sec Phase A 123rd Voltage Magnitude Harmonics | float | 2 | R
0x3786 | 0x3787 | 14214 | 14215 | MAG_3S_HAR_V_123th_b_% | Aggr 3sec Phase B 123rd Voltage Magnitude Harmonics | float | 2 | R
0x3788 | 0x3789 | 14216 | 14217 | MAG_3S_HAR_V_123th_c_% | Aggr 3sec Phase C 123rd Voltage Magnitude Harmonics | float | 2 | R
0x378A | 0x378B | 14218 | 14219 | MAG_3S_HAR_I_123th_a_% | Aggr 3sec Phase A 123rd Current Magnitude Harmonics | float | 2 | R
0x378C | 0x378D | 14220 | 14221 | MAG_3S_HAR_I_123th_b_% | Aggr 3sec Phase B 123rd Current Magnitude Harmonics | float | 2 | R
0x378E | 0x378F | 14222 | 14223 | MAG_3S_HAR_I_123th_c_% | Aggr 3sec Phase C 123rd Current Magnitude Harmonics | float | 2 | R
0x3790 | 0x3791 | 14224 | 14225 | MAG_3S_HAR_I_123th_n_% | Aggr 3sec Phase N 123rd Current Magnitude Harmonics | float | 2 | R
0x3792 | 0x3793 | 14226 | 14227 | MAG_3S_HAR_V_124th_a_% | Aggr 3sec Phase A 124th Voltage Magnitude Harmonics | float | 2 | R
0x3794 | 0x3795 | 14228 | 14229 | MAG_3S_HAR_V_124th_b_% | Aggr 3sec Phase B 124th Voltage Magnitude Harmonics | float | 2 | R
0x3796 | 0x3797 | 14230 | 14231 | MAG_3S_HAR_V_124th_c_% | Aggr 3sec Phase C 124th Voltage Magnitude Harmonics | float | 2 | R
0x3798 | 0x3799 | 14232 | 14233 | MAG_3S_HAR_I_124th_a_% | Aggr 3sec Phase A 124th Current Magnitude Harmonics | float | 2 | R
0x379A | 0x379B | 14234 | 14235 | MAG_3S_HAR_I_124th_b_% | Aggr 3sec Phase B 124th Current Magnitude Harmonics | float | 2 | R
0x379C | 0x379D | 14236 | 14237 | MAG_3S_HAR_I_124th_c_% | Aggr 3sec Phase C 124th Current Magnitude Harmonics | float | 2 | R
0x379E | 0x379F | 14238 | 14239 | MAG_3S_HAR_I_124th_n_% | Aggr 3sec Phase N 124th Current Magnitude Harmonics | float | 2 | R
0x37A0 | 0x37A1 | 14240 | 14241 | MAG_3S_HAR_V_125th_a_% | Aggr 3sec Phase A 125th Voltage Magnitude Harmonics | float | 2 | R
0x37A2 | 0x37A3 | 14242 | 14243 | MAG_3S_HAR_V_125th_b_% | Aggr 3sec Phase B 125th Voltage Magnitude Harmonics | float | 2 | R
0x37A4 | 0x37A5 | 14244 | 14245 | MAG_3S_HAR_V_125th_c_% | Aggr 3sec Phase C 125th Voltage Magnitude Harmonics | float | 2 | R
0x37A6 | 0x37A7 | 14246 | 14247 | MAG_3S_HAR_I_125th_a_% | Aggr 3sec Phase A 125th Current Magnitude Harmonics | float | 2 | R
0x37A8 | 0x37A9 | 14248 | 14249 | MAG_3S_HAR_I_125th_b_% | Aggr 3sec Phase B 125th Current Magnitude Harmonics | float | 2 | R
0x37AA | 0x37AB | 14250 | 14251 | MAG_3S_HAR_I_125th_c_% | Aggr 3sec Phase C 125th Current Magnitude Harmonics | float | 2 | R
0x37AC | 0x37AD | 14252 | 14253 | MAG_3S_HAR_I_125th_n_% | Aggr 3sec Phase N 125th Current Magnitude Harmonics | float | 2 | R
0x37AE | 0x37AF | 14254 | 14255 | MAG_3S_HAR_V_126th_a_% | Aggr 3sec Phase A 126th Voltage Magnitude Harmonics | float | 2 | R
0x37B0 | 0x37B1 | 14256 | 14257 | MAG_3S_HAR_V_126th_b_% | Aggr 3sec Phase B 126th Voltage Magnitude Harmonics | float | 2 | R
0x37B2 | 0x37B3 | 14258 | 14259 | MAG_3S_HAR_V_126th_c_% | Aggr 3sec Phase C 126th Voltage Magnitude Harmonics | float | 2 | R
0x37B4 | 0x37B5 | 14260 | 14261 | MAG_3S_HAR_I_126th_a_% | Aggr 3sec Phase A 126th Current Magnitude Harmonics | float | 2 | R
0x37B6 | 0x37B7 | 14262 | 14263 | MAG_3S_HAR_I_126th_b_% | Aggr 3sec Phase B 126th Current Magnitude Harmonics | float | 2 | R
0x37B8 | 0x37B9 | 14264 | 14265 | MAG_3S_HAR_I_126th_c_% | Aggr 3sec Phase C 126th Current Magnitude Harmonics | float | 2 | R
0x37BA | 0x37BB | 14266 | 14267 | MAG_3S_HAR_I_126th_n_% | Aggr 3sec Phase N 126th Current Magnitude Harmonics | float | 2 | R
0x37BC | 0x37BD | 14268 | 14269 | MAG_3S_HAR_V_127th_a_% | Aggr 3sec Phase A 127th Voltage Magnitude Harmonics | float | 2 | R
0x37BE | 0x37BF | 14270 | 14271 | MAG_3S_HAR_V_127th_b_% | Aggr 3sec Phase B 127th Voltage Magnitude Harmonics | float | 2 | R
0x37C0 | 0x37C1 | 14272 | 14273 | MAG_3S_HAR_V_127th_c_% | Aggr 3sec Phase C 127th Voltage Magnitude Harmonics | float | 2 | R
0x37C2 | 0x37C3 | 14274 | 14275 | MAG_3S_HAR_I_127th_a_% | Aggr 3sec Phase A 127th Current Magnitude Harmonics | float | 2 | R
0x37C4 | 0x37C5 | 14276 | 14277 | MAG_3S_HAR_I_127th_b_% | Aggr 3sec Phase B 127th Current Magnitude Harmonics | float | 2 | R
0x37C6 | 0x37C7 | 14278 | 14279 | MAG_3S_HAR_I_127th_c_% | Aggr 3sec Phase C 127th Current Magnitude Harmonics | float | 2 | R
0x37C8 | 0x37C9 | 14280 | 14281 | MAG_3S_HAR_I_127th_n_% | Aggr 3sec Phase N 127th Current Magnitude Harmonics | float | 2 | R
0x37CA | 0x37CB | 14282 | 14283 | ANG_3S_HAR_V_1th_a | Aggr 3sec Phase A 1st Voltage Angle Harmonics | float | 2 | R
0x37CC | 0x37CD | 14284 | 14285 | ANG_3S_HAR_V_1th_b | Aggr 3sec Phase B 1st Voltage Angle Harmonics | float | 2 | R
0x37CE | 0x37CF | 14286 | 14287 | ANG_3S_HAR_V_1th_c | Aggr 3sec Phase C 1st Voltage Angle Harmonics | float | 2 | R
0x37D0 | 0x37D1 | 14288 | 14289 | ANG_3S_HAR_I_1th_a | Aggr 3sec Phase A 1st Current Angle Harmonics | float | 2 | R
0x37D2 | 0x37D3 | 14290 | 14291 | ANG_3S_HAR_I_1th_b | Aggr 3sec Phase B 1st Current Angle Harmonics | float | 2 | R
0x37D4 | 0x37D5 | 14292 | 14293 | ANG_3S_HAR_I_1th_c | Aggr 3sec Phase C 1st Current Angle Harmonics | float | 2 | R
0x37D6 | 0x37D7 | 14294 | 14295 | ANG_3S_HAR_I_1th_n | Aggr 3sec Phase N 1st Current Angle Harmonics | float | 2 | R
0x37D8 | 0x37D9 | 14296 | 14297 | ANG_3S_HAR_V_2th_a | Aggr 3sec Phase A 2nd Voltage Angle Harmonics | float | 2 | R
0x37DA | 0x37DB | 14298 | 14299 | ANG_3S_HAR_V_2th_b | Aggr 3sec Phase B 2nd Voltage Angle Harmonics | float | 2 | R
0x37DC | 0x37DD | 14300 | 14301 | ANG_3S_HAR_V_2th_c | Aggr 3sec Phase C 2nd Voltage Angle Harmonics | float | 2 | R
0x37DE | 0x37DF | 14302 | 14303 | ANG_3S_HAR_I_2th_a | Aggr 3sec Phase A 2nd Current Angle Harmonics | float | 2 | R
0x37E0 | 0x37E1 | 14304 | 14305 | ANG_3S_HAR_I_2th_b | Aggr 3sec Phase B 2nd Current Angle Harmonics | float | 2 | R
0x37E2 | 0x37E3 | 14306 | 14307 | ANG_3S_HAR_I_2th_c | Aggr 3sec Phase C 2nd Current Angle Harmonics | float | 2 | R
0x37E4 | 0x37E5 | 14308 | 14309 | ANG_3S_HAR_I_2th_n | Aggr 3sec Phase N 2nd Current Angle Harmonics | float | 2 | R
0x37E6 | 0x37E7 | 14310 | 14311 | ANG_3S_HAR_V_3th_a | Aggr 3sec Phase A 3rd Voltage Angle Harmonics | float | 2 | R
0x37E8 | 0x37E9 | 14312 | 14313 | ANG_3S_HAR_V_3th_b | Aggr 3sec Phase B 3rd Voltage Angle Harmonics | float | 2 | R
0x37EA | 0x37EB | 14314 | 14315 | ANG_3S_HAR_V_3th_c | Aggr 3sec Phase C 3rd Voltage Angle Harmonics | float | 2 | R
0x37EC | 0x37ED | 14316 | 14317 | ANG_3S_HAR_I_3th_a | Aggr 3sec Phase A 3rd Current Angle Harmonics | float | 2 | R
0x37EE | 0x37EF | 14318 | 14319 | ANG_3S_HAR_I_3th_b | Aggr 3sec Phase B 3rd Current Angle Harmonics | float | 2 | R
0x37F0 | 0x37F1 | 14320 | 14321 | ANG_3S_HAR_I_3th_c | Aggr 3sec Phase C 3rd Current Angle Harmonics | float | 2 | R
0x37F2 | 0x37F3 | 14322 | 14323 | ANG_3S_HAR_I_3th_n | Aggr 3sec Phase N 3rd Current Angle Harmonics | float | 2 | R
0x37F4 | 0x37F5 | 14324 | 14325 | ANG_3S_HAR_V_4th_a | Aggr 3sec Phase A 4th Voltage Angle Harmonics | float | 2 | R
0x37F6 | 0x37F7 | 14326 | 14327 | ANG_3S_HAR_V_4th_b | Aggr 3sec Phase B 4th Voltage Angle Harmonics | float | 2 | R
0x37F8 | 0x37F9 | 14328 | 14329 | ANG_3S_HAR_V_4th_c | Aggr 3sec Phase C 4th Voltage Angle Harmonics | float | 2 | R
0x37FA | 0x37FB | 14330 | 14331 | ANG_3S_HAR_I_4th_a | Aggr 3sec Phase A 4th Current Angle Harmonics | float | 2 | R
0x37FC | 0x37FD | 14332 | 14333 | ANG_3S_HAR_I_4th_b | Aggr 3sec Phase B 4th Current Angle Harmonics | float | 2 | R
0x37FE | 0x37FF | 14334 | 14335 | ANG_3S_HAR_I_4th_c | Aggr 3sec Phase C 4th Current Angle Harmonics | float | 2 | R
0x3800 | 0x3801 | 14336 | 14337 | ANG_3S_HAR_I_4th_n | Aggr 3sec Phase N 4th Current Angle Harmonics | float | 2 | R
0x3802 | 0x3803 | 14338 | 14339 | ANG_3S_HAR_V_5th_a | Aggr 3sec Phase A 5th Voltage Angle Harmonics | float | 2 | R
0x3804 | 0x3805 | 14340 | 14341 | ANG_3S_HAR_V_5th_b | Aggr 3sec Phase B 5th Voltage Angle Harmonics | float | 2 | R
0x3806 | 0x3807 | 14342 | 14343 | ANG_3S_HAR_V_5th_c | Aggr 3sec Phase C 5th Voltage Angle Harmonics | float | 2 | R
0x3808 | 0x3809 | 14344 | 14345 | ANG_3S_HAR_I_5th_a | Aggr 3sec Phase A 5th Current Angle Harmonics | float | 2 | R
0x380A | 0x380B | 14346 | 14347 | ANG_3S_HAR_I_5th_b | Aggr 3sec Phase B 5th Current Angle Harmonics | float | 2 | R
0x380C | 0x380D | 14348 | 14349 | ANG_3S_HAR_I_5th_c | Aggr 3sec Phase C 5th Current Angle Harmonics | float | 2 | R
0x380E | 0x380F | 14350 | 14351 | ANG_3S_HAR_I_5th_n | Aggr 3sec Phase N 5th Current Angle Harmonics | float | 2 | R
0x3810 | 0x3811 | 14352 | 14353 | ANG_3S_HAR_V_6th_a | Aggr 3sec Phase A 6th Voltage Angle Harmonics | float | 2 | R
0x3812 | 0x3813 | 14354 | 14355 | ANG_3S_HAR_V_6th_b | Aggr 3sec Phase B 6th Voltage Angle Harmonics | float | 2 | R
0x3814 | 0x3815 | 14356 | 14357 | ANG_3S_HAR_V_6th_c | Aggr 3sec Phase C 6th Voltage Angle Harmonics | float | 2 | R
0x3816 | 0x3817 | 14358 | 14359 | ANG_3S_HAR_I_6th_a | Aggr 3sec Phase A 6th Current Angle Harmonics | float | 2 | R
0x3818 | 0x3819 | 14360 | 14361 | ANG_3S_HAR_I_6th_b | Aggr 3sec Phase B 6th Current Angle Harmonics | float | 2 | R
0x381A | 0x381B | 14362 | 14363 | ANG_3S_HAR_I_6th_c | Aggr 3sec Phase C 6th Current Angle Harmonics | float | 2 | R
0x381C | 0x381D | 14364 | 14365 | ANG_3S_HAR_I_6th_n | Aggr 3sec Phase N 6th Current Angle Harmonics | float | 2 | R
0x381E | 0x381F | 14366 | 14367 | ANG_3S_HAR_V_7th_a | Aggr 3sec Phase A 7th Voltage Angle Harmonics | float | 2 | R
0x3820 | 0x3821 | 14368 | 14369 | ANG_3S_HAR_V_7th_b | Aggr 3sec Phase B 7th Voltage Angle Harmonics | float | 2 | R
0x3822 | 0x3823 | 14370 | 14371 | ANG_3S_HAR_V_7th_c | Aggr 3sec Phase C 7th Voltage Angle Harmonics | float | 2 | R
0x3824 | 0x3825 | 14372 | 14373 | ANG_3S_HAR_I_7th_a | Aggr 3sec Phase A 7th Current Angle Harmonics | float | 2 | R
0x3826 | 0x3827 | 14374 | 14375 | ANG_3S_HAR_I_7th_b | Aggr 3sec Phase B 7th Current Angle Harmonics | float | 2 | R
0x3828 | 0x3829 | 14376 | 14377 | ANG_3S_HAR_I_7th_c | Aggr 3sec Phase C 7th Current Angle Harmonics | float | 2 | R
0x382A | 0x382B | 14378 | 14379 | ANG_3S_HAR_I_7th_n | Aggr 3sec Phase N 7th Current Angle Harmonics | float | 2 | R
0x382C | 0x382D | 14380 | 14381 | ANG_3S_HAR_V_8th_a | Aggr 3sec Phase A 8th Voltage Angle Harmonics | float | 2 | R
0x382E | 0x382F | 14382 | 14383 | ANG_3S_HAR_V_8th_b | Aggr 3sec Phase B 8th Voltage Angle Harmonics | float | 2 | R
0x3830 | 0x3831 | 14384 | 14385 | ANG_3S_HAR_V_8th_c | Aggr 3sec Phase C 8th Voltage Angle Harmonics | float | 2 | R
0x3832 | 0x3833 | 14386 | 14387 | ANG_3S_HAR_I_8th_a | Aggr 3sec Phase A 8th Current Angle Harmonics | float | 2 | R
0x3834 | 0x3835 | 14388 | 14389 | ANG_3S_HAR_I_8th_b | Aggr 3sec Phase B 8th Current Angle Harmonics | float | 2 | R
0x3836 | 0x3837 | 14390 | 14391 | ANG_3S_HAR_I_8th_c | Aggr 3sec Phase C 8th Current Angle Harmonics | float | 2 | R
0x3838 | 0x3839 | 14392 | 14393 | ANG_3S_HAR_I_8th_n | Aggr 3sec Phase N 8th Current Angle Harmonics | float | 2 | R
0x383A | 0x383B | 14394 | 14395 | ANG_3S_HAR_V_9th_a | Aggr 3sec Phase A 9th Voltage Angle Harmonics | float | 2 | R
0x383C | 0x383D | 14396 | 14397 | ANG_3S_HAR_V_9th_b | Aggr 3sec Phase B 9th Voltage Angle Harmonics | float | 2 | R
0x383E | 0x383F | 14398 | 14399 | ANG_3S_HAR_V_9th_c | Aggr 3sec Phase C 9th Voltage Angle Harmonics | float | 2 | R
0x3840 | 0x3841 | 14400 | 14401 | ANG_3S_HAR_I_9th_a | Aggr 3sec Phase A 9th Current Angle Harmonics | float | 2 | R
0x3842 | 0x3843 | 14402 | 14403 | ANG_3S_HAR_I_9th_b | Aggr 3sec Phase B 9th Current Angle Harmonics | float | 2 | R
0x3844 | 0x3845 | 14404 | 14405 | ANG_3S_HAR_I_9th_c | Aggr 3sec Phase C 9th Current Angle Harmonics | float | 2 | R
0x3846 | 0x3847 | 14406 | 14407 | ANG_3S_HAR_I_9th_n | Aggr 3sec Phase N 9th Current Angle Harmonics | float | 2 | R
0x3848 | 0x3849 | 14408 | 14409 | ANG_3S_HAR_V_10th_a | Aggr 3sec Phase A 10th Voltage Angle Harmonics | float | 2 | R
0x384A | 0x384B | 14410 | 14411 | ANG_3S_HAR_V_10th_b | Aggr 3sec Phase B 10th Voltage Angle Harmonics | float | 2 | R
0x384C | 0x384D | 14412 | 14413 | ANG_3S_HAR_V_10th_c | Aggr 3sec Phase C 10th Voltage Angle Harmonics | float | 2 | R
0x384E | 0x384F | 14414 | 14415 | ANG_3S_HAR_I_10th_a | Aggr 3sec Phase A 10th Current Angle Harmonics | float | 2 | R
0x3850 | 0x3851 | 14416 | 14417 | ANG_3S_HAR_I_10th_b | Aggr 3sec Phase B 10th Current Angle Harmonics | float | 2 | R
0x3852 | 0x3853 | 14418 | 14419 | ANG_3S_HAR_I_10th_c | Aggr 3sec Phase C 10th Current Angle Harmonics | float | 2 | R
0x3854 | 0x3855 | 14420 | 14421 | ANG_3S_HAR_I_10th_n | Aggr 3sec Phase N 10th Current Angle Harmonics | float | 2 | R
0x3856 | 0x3857 | 14422 | 14423 | ANG_3S_HAR_V_11th_a | Aggr 3sec Phase A 11st Voltage Angle Harmonics | float | 2 | R
0x3858 | 0x3859 | 14424 | 14425 | ANG_3S_HAR_V_11th_b | Aggr 3sec Phase B 11st Voltage Angle Harmonics | float | 2 | R
0x385A | 0x385B | 14426 | 14427 | ANG_3S_HAR_V_11th_c | Aggr 3sec Phase C 11st Voltage Angle Harmonics | float | 2 | R
0x385C | 0x385D | 14428 | 14429 | ANG_3S_HAR_I_11th_a | Aggr 3sec Phase A 11st Current Angle Harmonics | float | 2 | R
0x385E | 0x385F | 14430 | 14431 | ANG_3S_HAR_I_11th_b | Aggr 3sec Phase B 11st Current Angle Harmonics | float | 2 | R
0x3860 | 0x3861 | 14432 | 14433 | ANG_3S_HAR_I_11th_c | Aggr 3sec Phase C 11st Current Angle Harmonics | float | 2 | R
0x3862 | 0x3863 | 14434 | 14435 | ANG_3S_HAR_I_11th_n | Aggr 3sec Phase N 11st Current Angle Harmonics | float | 2 | R
0x3864 | 0x3865 | 14436 | 14437 | ANG_3S_HAR_V_12th_a | Aggr 3sec Phase A 12nd Voltage Angle Harmonics | float | 2 | R
0x3866 | 0x3867 | 14438 | 14439 | ANG_3S_HAR_V_12th_b | Aggr 3sec Phase B 12nd Voltage Angle Harmonics | float | 2 | R
0x3868 | 0x3869 | 14440 | 14441 | ANG_3S_HAR_V_12th_c | Aggr 3sec Phase C 12nd Voltage Angle Harmonics | float | 2 | R
0x386A | 0x386B | 14442 | 14443 | ANG_3S_HAR_I_12th_a | Aggr 3sec Phase A 12nd Current Angle Harmonics | float | 2 | R
0x386C | 0x386D | 14444 | 14445 | ANG_3S_HAR_I_12th_b | Aggr 3sec Phase B 12nd Current Angle Harmonics | float | 2 | R
0x386E | 0x386F | 14446 | 14447 | ANG_3S_HAR_I_12th_c | Aggr 3sec Phase C 12nd Current Angle Harmonics | float | 2 | R
0x3870 | 0x3871 | 14448 | 14449 | ANG_3S_HAR_I_12th_n | Aggr 3sec Phase N 12nd Current Angle Harmonics | float | 2 | R
0x3872 | 0x3873 | 14450 | 14451 | ANG_3S_HAR_V_13th_a | Aggr 3sec Phase A 13rd Voltage Angle Harmonics | float | 2 | R
0x3874 | 0x3875 | 14452 | 14453 | ANG_3S_HAR_V_13th_b | Aggr 3sec Phase B 13rd Voltage Angle Harmonics | float | 2 | R
0x3876 | 0x3877 | 14454 | 14455 | ANG_3S_HAR_V_13th_c | Aggr 3sec Phase C 13rd Voltage Angle Harmonics | float | 2 | R
0x3878 | 0x3879 | 14456 | 14457 | ANG_3S_HAR_I_13th_a | Aggr 3sec Phase A 13rd Current Angle Harmonics | float | 2 | R
0x387A | 0x387B | 14458 | 14459 | ANG_3S_HAR_I_13th_b | Aggr 3sec Phase B 13rd Current Angle Harmonics | float | 2 | R
0x387C | 0x387D | 14460 | 14461 | ANG_3S_HAR_I_13th_c | Aggr 3sec Phase C 13rd Current Angle Harmonics | float | 2 | R
0x387E | 0x387F | 14462 | 14463 | ANG_3S_HAR_I_13th_n | Aggr 3sec Phase N 13rd Current Angle Harmonics | float | 2 | R
0x3880 | 0x3881 | 14464 | 14465 | ANG_3S_HAR_V_14th_a | Aggr 3sec Phase A 14th Voltage Angle Harmonics | float | 2 | R
0x3882 | 0x3883 | 14466 | 14467 | ANG_3S_HAR_V_14th_b | Aggr 3sec Phase B 14th Voltage Angle Harmonics | float | 2 | R
0x3884 | 0x3885 | 14468 | 14469 | ANG_3S_HAR_V_14th_c | Aggr 3sec Phase C 14th Voltage Angle Harmonics | float | 2 | R
0x3886 | 0x3887 | 14470 | 14471 | ANG_3S_HAR_I_14th_a | Aggr 3sec Phase A 14th Current Angle Harmonics | float | 2 | R
0x3888 | 0x3889 | 14472 | 14473 | ANG_3S_HAR_I_14th_b | Aggr 3sec Phase B 14th Current Angle Harmonics | float | 2 | R
0x388A | 0x388B | 14474 | 14475 | ANG_3S_HAR_I_14th_c | Aggr 3sec Phase C 14th Current Angle Harmonics | float | 2 | R
0x388C | 0x388D | 14476 | 14477 | ANG_3S_HAR_I_14th_n | Aggr 3sec Phase N 14th Current Angle Harmonics | float | 2 | R
0x388E | 0x388F | 14478 | 14479 | ANG_3S_HAR_V_15th_a | Aggr 3sec Phase A 15th Voltage Angle Harmonics | float | 2 | R
0x3890 | 0x3891 | 14480 | 14481 | ANG_3S_HAR_V_15th_b | Aggr 3sec Phase B 15th Voltage Angle Harmonics | float | 2 | R
0x3892 | 0x3893 | 14482 | 14483 | ANG_3S_HAR_V_15th_c | Aggr 3sec Phase C 15th Voltage Angle Harmonics | float | 2 | R
0x3894 | 0x3895 | 14484 | 14485 | ANG_3S_HAR_I_15th_a | Aggr 3sec Phase A 15th Current Angle Harmonics | float | 2 | R
0x3896 | 0x3897 | 14486 | 14487 | ANG_3S_HAR_I_15th_b | Aggr 3sec Phase B 15th Current Angle Harmonics | float | 2 | R
0x3898 | 0x3899 | 14488 | 14489 | ANG_3S_HAR_I_15th_c | Aggr 3sec Phase C 15th Current Angle Harmonics | float | 2 | R
0x389A | 0x389B | 14490 | 14491 | ANG_3S_HAR_I_15th_n | Aggr 3sec Phase N 15th Current Angle Harmonics | float | 2 | R
0x389C | 0x389D | 14492 | 14493 | ANG_3S_HAR_V_16th_a | Aggr 3sec Phase A 16th Voltage Angle Harmonics | float | 2 | R
0x389E | 0x389F | 14494 | 14495 | ANG_3S_HAR_V_16th_b | Aggr 3sec Phase B 16th Voltage Angle Harmonics | float | 2 | R
0x38A0 | 0x38A1 | 14496 | 14497 | ANG_3S_HAR_V_16th_c | Aggr 3sec Phase C 16th Voltage Angle Harmonics | float | 2 | R
0x38A2 | 0x38A3 | 14498 | 14499 | ANG_3S_HAR_I_16th_a | Aggr 3sec Phase A 16th Current Angle Harmonics | float | 2 | R
0x38A4 | 0x38A5 | 14500 | 14501 | ANG_3S_HAR_I_16th_b | Aggr 3sec Phase B 16th Current Angle Harmonics | float | 2 | R
0x38A6 | 0x38A7 | 14502 | 14503 | ANG_3S_HAR_I_16th_c | Aggr 3sec Phase C 16th Current Angle Harmonics | float | 2 | R
0x38A8 | 0x38A9 | 14504 | 14505 | ANG_3S_HAR_I_16th_n | Aggr 3sec Phase N 16th Current Angle Harmonics | float | 2 | R
0x38AA | 0x38AB | 14506 | 14507 | ANG_3S_HAR_V_17th_a | Aggr 3sec Phase A 17th Voltage Angle Harmonics | float | 2 | R
0x38AC | 0x38AD | 14508 | 14509 | ANG_3S_HAR_V_17th_b | Aggr 3sec Phase B 17th Voltage Angle Harmonics | float | 2 | R
0x38AE | 0x38AF | 14510 | 14511 | ANG_3S_HAR_V_17th_c | Aggr 3sec Phase C 17th Voltage Angle Harmonics | float | 2 | R
0x38B0 | 0x38B1 | 14512 | 14513 | ANG_3S_HAR_I_17th_a | Aggr 3sec Phase A 17th Current Angle Harmonics | float | 2 | R
0x38B2 | 0x38B3 | 14514 | 14515 | ANG_3S_HAR_I_17th_b | Aggr 3sec Phase B 17th Current Angle Harmonics | float | 2 | R
0x38B4 | 0x38B5 | 14516 | 14517 | ANG_3S_HAR_I_17th_c | Aggr 3sec Phase C 17th Current Angle Harmonics | float | 2 | R
0x38B6 | 0x38B7 | 14518 | 14519 | ANG_3S_HAR_I_17th_n | Aggr 3sec Phase N 17th Current Angle Harmonics | float | 2 | R
0x38B8 | 0x38B9 | 14520 | 14521 | ANG_3S_HAR_V_18th_a | Aggr 3sec Phase A 18th Voltage Angle Harmonics | float | 2 | R
0x38BA | 0x38BB | 14522 | 14523 | ANG_3S_HAR_V_18th_b | Aggr 3sec Phase B 18th Voltage Angle Harmonics | float | 2 | R
0x38BC | 0x38BD | 14524 | 14525 | ANG_3S_HAR_V_18th_c | Aggr 3sec Phase C 18th Voltage Angle Harmonics | float | 2 | R
0x38BE | 0x38BF | 14526 | 14527 | ANG_3S_HAR_I_18th_a | Aggr 3sec Phase A 18th Current Angle Harmonics | float | 2 | R
0x38C0 | 0x38C1 | 14528 | 14529 | ANG_3S_HAR_I_18th_b | Aggr 3sec Phase B 18th Current Angle Harmonics | float | 2 | R
0x38C2 | 0x38C3 | 14530 | 14531 | ANG_3S_HAR_I_18th_c | Aggr 3sec Phase C 18th Current Angle Harmonics | float | 2 | R
0x38C4 | 0x38C5 | 14532 | 14533 | ANG_3S_HAR_I_18th_n | Aggr 3sec Phase N 18th Current Angle Harmonics | float | 2 | R
0x38C6 | 0x38C7 | 14534 | 14535 | ANG_3S_HAR_V_19th_a | Aggr 3sec Phase A 19th Voltage Angle Harmonics | float | 2 | R
0x38C8 | 0x38C9 | 14536 | 14537 | ANG_3S_HAR_V_19th_b | Aggr 3sec Phase B 19th Voltage Angle Harmonics | float | 2 | R
0x38CA | 0x38CB | 14538 | 14539 | ANG_3S_HAR_V_19th_c | Aggr 3sec Phase C 19th Voltage Angle Harmonics | float | 2 | R
0x38CC | 0x38CD | 14540 | 14541 | ANG_3S_HAR_I_19th_a | Aggr 3sec Phase A 19th Current Angle Harmonics | float | 2 | R
0x38CE | 0x38CF | 14542 | 14543 | ANG_3S_HAR_I_19th_b | Aggr 3sec Phase B 19th Current Angle Harmonics | float | 2 | R
0x38D0 | 0x38D1 | 14544 | 14545 | ANG_3S_HAR_I_19th_c | Aggr 3sec Phase C 19th Current Angle Harmonics | float | 2 | R
0x38D2 | 0x38D3 | 14546 | 14547 | ANG_3S_HAR_I_19th_n | Aggr 3sec Phase N 19th Current Angle Harmonics | float | 2 | R
0x38D4 | 0x38D5 | 14548 | 14549 | ANG_3S_HAR_V_20th_a | Aggr 3sec Phase A 20th Voltage Angle Harmonics | float | 2 | R
0x38D6 | 0x38D7 | 14550 | 14551 | ANG_3S_HAR_V_20th_b | Aggr 3sec Phase B 20th Voltage Angle Harmonics | float | 2 | R
0x38D8 | 0x38D9 | 14552 | 14553 | ANG_3S_HAR_V_20th_c | Aggr 3sec Phase C 20th Voltage Angle Harmonics | float | 2 | R
0x38DA | 0x38DB | 14554 | 14555 | ANG_3S_HAR_I_20th_a | Aggr 3sec Phase A 20th Current Angle Harmonics | float | 2 | R
0x38DC | 0x38DD | 14556 | 14557 | ANG_3S_HAR_I_20th_b | Aggr 3sec Phase B 20th Current Angle Harmonics | float | 2 | R
0x38DE | 0x38DF | 14558 | 14559 | ANG_3S_HAR_I_20th_c | Aggr 3sec Phase C 20th Current Angle Harmonics | float | 2 | R
0x38E0 | 0x38E1 | 14560 | 14561 | ANG_3S_HAR_I_20th_n | Aggr 3sec Phase N 20th Current Angle Harmonics | float | 2 | R
0x38E2 | 0x38E3 | 14562 | 14563 | ANG_3S_HAR_V_21th_a | Aggr 3sec Phase A 21st Voltage Angle Harmonics | float | 2 | R
0x38E4 | 0x38E5 | 14564 | 14565 | ANG_3S_HAR_V_21th_b | Aggr 3sec Phase B 21st Voltage Angle Harmonics | float | 2 | R
0x38E6 | 0x38E7 | 14566 | 14567 | ANG_3S_HAR_V_21th_c | Aggr 3sec Phase C 21st Voltage Angle Harmonics | float | 2 | R
0x38E8 | 0x38E9 | 14568 | 14569 | ANG_3S_HAR_I_21th_a | Aggr 3sec Phase A 21st Current Angle Harmonics | float | 2 | R
0x38EA | 0x38EB | 14570 | 14571 | ANG_3S_HAR_I_21th_b | Aggr 3sec Phase B 21st Current Angle Harmonics | float | 2 | R
0x38EC | 0x38ED | 14572 | 14573 | ANG_3S_HAR_I_21th_c | Aggr 3sec Phase C 21st Current Angle Harmonics | float | 2 | R
0x38EE | 0x38EF | 14574 | 14575 | ANG_3S_HAR_I_21th_n | Aggr 3sec Phase N 21st Current Angle Harmonics | float | 2 | R
0x38F0 | 0x38F1 | 14576 | 14577 | ANG_3S_HAR_V_22th_a | Aggr 3sec Phase A 22nd Voltage Angle Harmonics | float | 2 | R
0x38F2 | 0x38F3 | 14578 | 14579 | ANG_3S_HAR_V_22th_b | Aggr 3sec Phase B 22nd Voltage Angle Harmonics | float | 2 | R
0x38F4 | 0x38F5 | 14580 | 14581 | ANG_3S_HAR_V_22th_c | Aggr 3sec Phase C 22nd Voltage Angle Harmonics | float | 2 | R
0x38F6 | 0x38F7 | 14582 | 14583 | ANG_3S_HAR_I_22th_a | Aggr 3sec Phase A 22nd Current Angle Harmonics | float | 2 | R
0x38F8 | 0x38F9 | 14584 | 14585 | ANG_3S_HAR_I_22th_b | Aggr 3sec Phase B 22nd Current Angle Harmonics | float | 2 | R
0x38FA | 0x38FB | 14586 | 14587 | ANG_3S_HAR_I_22th_c | Aggr 3sec Phase C 22nd Current Angle Harmonics | float | 2 | R
0x38FC | 0x38FD | 14588 | 14589 | ANG_3S_HAR_I_22th_n | Aggr 3sec Phase N 22nd Current Angle Harmonics | float | 2 | R
0x38FE | 0x38FF | 14590 | 14591 | ANG_3S_HAR_V_23th_a | Aggr 3sec Phase A 23rd Voltage Angle Harmonics | float | 2 | R
0x3900 | 0x3901 | 14592 | 14593 | ANG_3S_HAR_V_23th_b | Aggr 3sec Phase B 23rd Voltage Angle Harmonics | float | 2 | R
0x3902 | 0x3903 | 14594 | 14595 | ANG_3S_HAR_V_23th_c | Aggr 3sec Phase C 23rd Voltage Angle Harmonics | float | 2 | R
0x3904 | 0x3905 | 14596 | 14597 | ANG_3S_HAR_I_23th_a | Aggr 3sec Phase A 23rd Current Angle Harmonics | float | 2 | R
0x3906 | 0x3907 | 14598 | 14599 | ANG_3S_HAR_I_23th_b | Aggr 3sec Phase B 23rd Current Angle Harmonics | float | 2 | R
0x3908 | 0x3909 | 14600 | 14601 | ANG_3S_HAR_I_23th_c | Aggr 3sec Phase C 23rd Current Angle Harmonics | float | 2 | R
0x390A | 0x390B | 14602 | 14603 | ANG_3S_HAR_I_23th_n | Aggr 3sec Phase N 23rd Current Angle Harmonics | float | 2 | R
0x390C | 0x390D | 14604 | 14605 | ANG_3S_HAR_V_24th_a | Aggr 3sec Phase A 24th Voltage Angle Harmonics | float | 2 | R
0x390E | 0x390F | 14606 | 14607 | ANG_3S_HAR_V_24th_b | Aggr 3sec Phase B 24th Voltage Angle Harmonics | float | 2 | R
0x3910 | 0x3911 | 14608 | 14609 | ANG_3S_HAR_V_24th_c | Aggr 3sec Phase C 24th Voltage Angle Harmonics | float | 2 | R
0x3912 | 0x3913 | 14610 | 14611 | ANG_3S_HAR_I_24th_a | Aggr 3sec Phase A 24th Current Angle Harmonics | float | 2 | R
0x3914 | 0x3915 | 14612 | 14613 | ANG_3S_HAR_I_24th_b | Aggr 3sec Phase B 24th Current Angle Harmonics | float | 2 | R
0x3916 | 0x3917 | 14614 | 14615 | ANG_3S_HAR_I_24th_c | Aggr 3sec Phase C 24th Current Angle Harmonics | float | 2 | R
0x3918 | 0x3919 | 14616 | 14617 | ANG_3S_HAR_I_24th_n | Aggr 3sec Phase N 24th Current Angle Harmonics | float | 2 | R
0x391A | 0x391B | 14618 | 14619 | ANG_3S_HAR_V_25th_a | Aggr 3sec Phase A 25th Voltage Angle Harmonics | float | 2 | R
0x391C | 0x391D | 14620 | 14621 | ANG_3S_HAR_V_25th_b | Aggr 3sec Phase B 25th Voltage Angle Harmonics | float | 2 | R
0x391E | 0x391F | 14622 | 14623 | ANG_3S_HAR_V_25th_c | Aggr 3sec Phase C 25th Voltage Angle Harmonics | float | 2 | R
0x3920 | 0x3921 | 14624 | 14625 | ANG_3S_HAR_I_25th_a | Aggr 3sec Phase A 25th Current Angle Harmonics | float | 2 | R
0x3922 | 0x3923 | 14626 | 14627 | ANG_3S_HAR_I_25th_b | Aggr 3sec Phase B 25th Current Angle Harmonics | float | 2 | R
0x3924 | 0x3925 | 14628 | 14629 | ANG_3S_HAR_I_25th_c | Aggr 3sec Phase C 25th Current Angle Harmonics | float | 2 | R
0x3926 | 0x3927 | 14630 | 14631 | ANG_3S_HAR_I_25th_n | Aggr 3sec Phase N 25th Current Angle Harmonics | float | 2 | R
0x3928 | 0x3929 | 14632 | 14633 | ANG_3S_HAR_V_26th_a | Aggr 3sec Phase A 26th Voltage Angle Harmonics | float | 2 | R
0x392A | 0x392B | 14634 | 14635 | ANG_3S_HAR_V_26th_b | Aggr 3sec Phase B 26th Voltage Angle Harmonics | float | 2 | R
0x392C | 0x392D | 14636 | 14637 | ANG_3S_HAR_V_26th_c | Aggr 3sec Phase C 26th Voltage Angle Harmonics | float | 2 | R
0x392E | 0x392F | 14638 | 14639 | ANG_3S_HAR_I_26th_a | Aggr 3sec Phase A 26th Current Angle Harmonics | float | 2 | R
0x3930 | 0x3931 | 14640 | 14641 | ANG_3S_HAR_I_26th_b | Aggr 3sec Phase B 26th Current Angle Harmonics | float | 2 | R
0x3932 | 0x3933 | 14642 | 14643 | ANG_3S_HAR_I_26th_c | Aggr 3sec Phase C 26th Current Angle Harmonics | float | 2 | R
0x3934 | 0x3935 | 14644 | 14645 | ANG_3S_HAR_I_26th_n | Aggr 3sec Phase N 26th Current Angle Harmonics | float | 2 | R
0x3936 | 0x3937 | 14646 | 14647 | ANG_3S_HAR_V_27th_a | Aggr 3sec Phase A 27th Voltage Angle Harmonics | float | 2 | R
0x3938 | 0x3939 | 14648 | 14649 | ANG_3S_HAR_V_27th_b | Aggr 3sec Phase B 27th Voltage Angle Harmonics | float | 2 | R
0x393A | 0x393B | 14650 | 14651 | ANG_3S_HAR_V_27th_c | Aggr 3sec Phase C 27th Voltage Angle Harmonics | float | 2 | R
0x393C | 0x393D | 14652 | 14653 | ANG_3S_HAR_I_27th_a | Aggr 3sec Phase A 27th Current Angle Harmonics | float | 2 | R
0x393E | 0x393F | 14654 | 14655 | ANG_3S_HAR_I_27th_b | Aggr 3sec Phase B 27th Current Angle Harmonics | float | 2 | R
0x3940 | 0x3941 | 14656 | 14657 | ANG_3S_HAR_I_27th_c | Aggr 3sec Phase C 27th Current Angle Harmonics | float | 2 | R
0x3942 | 0x3943 | 14658 | 14659 | ANG_3S_HAR_I_27th_n | Aggr 3sec Phase N 27th Current Angle Harmonics | float | 2 | R
0x3944 | 0x3945 | 14660 | 14661 | ANG_3S_HAR_V_28th_a | Aggr 3sec Phase A 28th Voltage Angle Harmonics | float | 2 | R
0x3946 | 0x3947 | 14662 | 14663 | ANG_3S_HAR_V_28th_b | Aggr 3sec Phase B 28th Voltage Angle Harmonics | float | 2 | R
0x3948 | 0x3949 | 14664 | 14665 | ANG_3S_HAR_V_28th_c | Aggr 3sec Phase C 28th Voltage Angle Harmonics | float | 2 | R
0x394A | 0x394B | 14666 | 14667 | ANG_3S_HAR_I_28th_a | Aggr 3sec Phase A 28th Current Angle Harmonics | float | 2 | R
0x394C | 0x394D | 14668 | 14669 | ANG_3S_HAR_I_28th_b | Aggr 3sec Phase B 28th Current Angle Harmonics | float | 2 | R
0x394E | 0x394F | 14670 | 14671 | ANG_3S_HAR_I_28th_c | Aggr 3sec Phase C 28th Current Angle Harmonics | float | 2 | R
0x3950 | 0x3951 | 14672 | 14673 | ANG_3S_HAR_I_28th_n | Aggr 3sec Phase N 28th Current Angle Harmonics | float | 2 | R
0x3952 | 0x3953 | 14674 | 14675 | ANG_3S_HAR_V_29th_a | Aggr 3sec Phase A 29th Voltage Angle Harmonics | float | 2 | R
0x3954 | 0x3955 | 14676 | 14677 | ANG_3S_HAR_V_29th_b | Aggr 3sec Phase B 29th Voltage Angle Harmonics | float | 2 | R
0x3956 | 0x3957 | 14678 | 14679 | ANG_3S_HAR_V_29th_c | Aggr 3sec Phase C 29th Voltage Angle Harmonics | float | 2 | R
0x3958 | 0x3959 | 14680 | 14681 | ANG_3S_HAR_I_29th_a | Aggr 3sec Phase A 29th Current Angle Harmonics | float | 2 | R
0x395A | 0x395B | 14682 | 14683 | ANG_3S_HAR_I_29th_b | Aggr 3sec Phase B 29th Current Angle Harmonics | float | 2 | R
0x395C | 0x395D | 14684 | 14685 | ANG_3S_HAR_I_29th_c | Aggr 3sec Phase C 29th Current Angle Harmonics | float | 2 | R
0x395E | 0x395F | 14686 | 14687 | ANG_3S_HAR_I_29th_n | Aggr 3sec Phase N 29th Current Angle Harmonics | float | 2 | R
0x3960 | 0x3961 | 14688 | 14689 | ANG_3S_HAR_V_30th_a | Aggr 3sec Phase A 30th Voltage Angle Harmonics | float | 2 | R
0x3962 | 0x3963 | 14690 | 14691 | ANG_3S_HAR_V_30th_b | Aggr 3sec Phase B 30th Voltage Angle Harmonics | float | 2 | R
0x3964 | 0x3965 | 14692 | 14693 | ANG_3S_HAR_V_30th_c | Aggr 3sec Phase C 30th Voltage Angle Harmonics | float | 2 | R
0x3966 | 0x3967 | 14694 | 14695 | ANG_3S_HAR_I_30th_a | Aggr 3sec Phase A 30th Current Angle Harmonics | float | 2 | R
0x3968 | 0x3969 | 14696 | 14697 | ANG_3S_HAR_I_30th_b | Aggr 3sec Phase B 30th Current Angle Harmonics | float | 2 | R
0x396A | 0x396B | 14698 | 14699 | ANG_3S_HAR_I_30th_c | Aggr 3sec Phase C 30th Current Angle Harmonics | float | 2 | R
0x396C | 0x396D | 14700 | 14701 | ANG_3S_HAR_I_30th_n | Aggr 3sec Phase N 30th Current Angle Harmonics | float | 2 | R
0x396E | 0x396F | 14702 | 14703 | ANG_3S_HAR_V_31th_a | Aggr 3sec Phase A 31st Voltage Angle Harmonics | float | 2 | R
0x3970 | 0x3971 | 14704 | 14705 | ANG_3S_HAR_V_31th_b | Aggr 3sec Phase B 31st Voltage Angle Harmonics | float | 2 | R
0x3972 | 0x3973 | 14706 | 14707 | ANG_3S_HAR_V_31th_c | Aggr 3sec Phase C 31st Voltage Angle Harmonics | float | 2 | R
0x3974 | 0x3975 | 14708 | 14709 | ANG_3S_HAR_I_31th_a | Aggr 3sec Phase A 31st Current Angle Harmonics | float | 2 | R
0x3976 | 0x3977 | 14710 | 14711 | ANG_3S_HAR_I_31th_b | Aggr 3sec Phase B 31st Current Angle Harmonics | float | 2 | R
0x3978 | 0x3979 | 14712 | 14713 | ANG_3S_HAR_I_31th_c | Aggr 3sec Phase C 31st Current Angle Harmonics | float | 2 | R
0x397A | 0x397B | 14714 | 14715 | ANG_3S_HAR_I_31th_n | Aggr 3sec Phase N 31st Current Angle Harmonics | float | 2 | R
0x397C | 0x397D | 14716 | 14717 | ANG_3S_HAR_V_32th_a | Aggr 3sec Phase A 32nd Voltage Angle Harmonics | float | 2 | R
0x397E | 0x397F | 14718 | 14719 | ANG_3S_HAR_V_32th_b | Aggr 3sec Phase B 32nd Voltage Angle Harmonics | float | 2 | R
0x3980 | 0x3981 | 14720 | 14721 | ANG_3S_HAR_V_32th_c | Aggr 3sec Phase C 32nd Voltage Angle Harmonics | float | 2 | R
0x3982 | 0x3983 | 14722 | 14723 | ANG_3S_HAR_I_32th_a | Aggr 3sec Phase A 32nd Current Angle Harmonics | float | 2 | R
0x3984 | 0x3985 | 14724 | 14725 | ANG_3S_HAR_I_32th_b | Aggr 3sec Phase B 32nd Current Angle Harmonics | float | 2 | R
0x3986 | 0x3987 | 14726 | 14727 | ANG_3S_HAR_I_32th_c | Aggr 3sec Phase C 32nd Current Angle Harmonics | float | 2 | R
0x3988 | 0x3989 | 14728 | 14729 | ANG_3S_HAR_I_32th_n | Aggr 3sec Phase N 32nd Current Angle Harmonics | float | 2 | R
0x398A | 0x398B | 14730 | 14731 | ANG_3S_HAR_V_33th_a | Aggr 3sec Phase A 33rd Voltage Angle Harmonics | float | 2 | R
0x398C | 0x398D | 14732 | 14733 | ANG_3S_HAR_V_33th_b | Aggr 3sec Phase B 33rd Voltage Angle Harmonics | float | 2 | R
0x398E | 0x398F | 14734 | 14735 | ANG_3S_HAR_V_33th_c | Aggr 3sec Phase C 33rd Voltage Angle Harmonics | float | 2 | R
0x3990 | 0x3991 | 14736 | 14737 | ANG_3S_HAR_I_33th_a | Aggr 3sec Phase A 33rd Current Angle Harmonics | float | 2 | R
0x3992 | 0x3993 | 14738 | 14739 | ANG_3S_HAR_I_33th_b | Aggr 3sec Phase B 33rd Current Angle Harmonics | float | 2 | R
0x3994 | 0x3995 | 14740 | 14741 | ANG_3S_HAR_I_33th_c | Aggr 3sec Phase C 33rd Current Angle Harmonics | float | 2 | R
0x3996 | 0x3997 | 14742 | 14743 | ANG_3S_HAR_I_33th_n | Aggr 3sec Phase N 33rd Current Angle Harmonics | float | 2 | R
0x3998 | 0x3999 | 14744 | 14745 | ANG_3S_HAR_V_34th_a | Aggr 3sec Phase A 34th Voltage Angle Harmonics | float | 2 | R
0x399A | 0x399B | 14746 | 14747 | ANG_3S_HAR_V_34th_b | Aggr 3sec Phase B 34th Voltage Angle Harmonics | float | 2 | R
0x399C | 0x399D | 14748 | 14749 | ANG_3S_HAR_V_34th_c | Aggr 3sec Phase C 34th Voltage Angle Harmonics | float | 2 | R
0x399E | 0x399F | 14750 | 14751 | ANG_3S_HAR_I_34th_a | Aggr 3sec Phase A 34th Current Angle Harmonics | float | 2 | R
0x39A0 | 0x39A1 | 14752 | 14753 | ANG_3S_HAR_I_34th_b | Aggr 3sec Phase B 34th Current Angle Harmonics | float | 2 | R
0x39A2 | 0x39A3 | 14754 | 14755 | ANG_3S_HAR_I_34th_c | Aggr 3sec Phase C 34th Current Angle Harmonics | float | 2 | R
0x39A4 | 0x39A5 | 14756 | 14757 | ANG_3S_HAR_I_34th_n | Aggr 3sec Phase N 34th Current Angle Harmonics | float | 2 | R
0x39A6 | 0x39A7 | 14758 | 14759 | ANG_3S_HAR_V_35th_a | Aggr 3sec Phase A 35th Voltage Angle Harmonics | float | 2 | R
0x39A8 | 0x39A9 | 14760 | 14761 | ANG_3S_HAR_V_35th_b | Aggr 3sec Phase B 35th Voltage Angle Harmonics | float | 2 | R
0x39AA | 0x39AB | 14762 | 14763 | ANG_3S_HAR_V_35th_c | Aggr 3sec Phase C 35th Voltage Angle Harmonics | float | 2 | R
0x39AC | 0x39AD | 14764 | 14765 | ANG_3S_HAR_I_35th_a | Aggr 3sec Phase A 35th Current Angle Harmonics | float | 2 | R
0x39AE | 0x39AF | 14766 | 14767 | ANG_3S_HAR_I_35th_b | Aggr 3sec Phase B 35th Current Angle Harmonics | float | 2 | R
0x39B0 | 0x39B1 | 14768 | 14769 | ANG_3S_HAR_I_35th_c | Aggr 3sec Phase C 35th Current Angle Harmonics | float | 2 | R
0x39B2 | 0x39B3 | 14770 | 14771 | ANG_3S_HAR_I_35th_n | Aggr 3sec Phase N 35th Current Angle Harmonics | float | 2 | R
0x39B4 | 0x39B5 | 14772 | 14773 | ANG_3S_HAR_V_36th_a | Aggr 3sec Phase A 36th Voltage Angle Harmonics | float | 2 | R
0x39B6 | 0x39B7 | 14774 | 14775 | ANG_3S_HAR_V_36th_b | Aggr 3sec Phase B 36th Voltage Angle Harmonics | float | 2 | R
0x39B8 | 0x39B9 | 14776 | 14777 | ANG_3S_HAR_V_36th_c | Aggr 3sec Phase C 36th Voltage Angle Harmonics | float | 2 | R
0x39BA | 0x39BB | 14778 | 14779 | ANG_3S_HAR_I_36th_a | Aggr 3sec Phase A 36th Current Angle Harmonics | float | 2 | R
0x39BC | 0x39BD | 14780 | 14781 | ANG_3S_HAR_I_36th_b | Aggr 3sec Phase B 36th Current Angle Harmonics | float | 2 | R
0x39BE | 0x39BF | 14782 | 14783 | ANG_3S_HAR_I_36th_c | Aggr 3sec Phase C 36th Current Angle Harmonics | float | 2 | R
0x39C0 | 0x39C1 | 14784 | 14785 | ANG_3S_HAR_I_36th_n | Aggr 3sec Phase N 36th Current Angle Harmonics | float | 2 | R
0x39C2 | 0x39C3 | 14786 | 14787 | ANG_3S_HAR_V_37th_a | Aggr 3sec Phase A 37th Voltage Angle Harmonics | float | 2 | R
0x39C4 | 0x39C5 | 14788 | 14789 | ANG_3S_HAR_V_37th_b | Aggr 3sec Phase B 37th Voltage Angle Harmonics | float | 2 | R
0x39C6 | 0x39C7 | 14790 | 14791 | ANG_3S_HAR_V_37th_c | Aggr 3sec Phase C 37th Voltage Angle Harmonics | float | 2 | R
0x39C8 | 0x39C9 | 14792 | 14793 | ANG_3S_HAR_I_37th_a | Aggr 3sec Phase A 37th Current Angle Harmonics | float | 2 | R
0x39CA | 0x39CB | 14794 | 14795 | ANG_3S_HAR_I_37th_b | Aggr 3sec Phase B 37th Current Angle Harmonics | float | 2 | R
0x39CC | 0x39CD | 14796 | 14797 | ANG_3S_HAR_I_37th_c | Aggr 3sec Phase C 37th Current Angle Harmonics | float | 2 | R
0x39CE | 0x39CF | 14798 | 14799 | ANG_3S_HAR_I_37th_n | Aggr 3sec Phase N 37th Current Angle Harmonics | float | 2 | R
0x39D0 | 0x39D1 | 14800 | 14801 | ANG_3S_HAR_V_38th_a | Aggr 3sec Phase A 38th Voltage Angle Harmonics | float | 2 | R
0x39D2 | 0x39D3 | 14802 | 14803 | ANG_3S_HAR_V_38th_b | Aggr 3sec Phase B 38th Voltage Angle Harmonics | float | 2 | R
0x39D4 | 0x39D5 | 14804 | 14805 | ANG_3S_HAR_V_38th_c | Aggr 3sec Phase C 38th Voltage Angle Harmonics | float | 2 | R
0x39D6 | 0x39D7 | 14806 | 14807 | ANG_3S_HAR_I_38th_a | Aggr 3sec Phase A 38th Current Angle Harmonics | float | 2 | R
0x39D8 | 0x39D9 | 14808 | 14809 | ANG_3S_HAR_I_38th_b | Aggr 3sec Phase B 38th Current Angle Harmonics | float | 2 | R
0x39DA | 0x39DB | 14810 | 14811 | ANG_3S_HAR_I_38th_c | Aggr 3sec Phase C 38th Current Angle Harmonics | float | 2 | R
0x39DC | 0x39DD | 14812 | 14813 | ANG_3S_HAR_I_38th_n | Aggr 3sec Phase N 38th Current Angle Harmonics | float | 2 | R
0x39DE | 0x39DF | 14814 | 14815 | ANG_3S_HAR_V_39th_a | Aggr 3sec Phase A 39th Voltage Angle Harmonics | float | 2 | R
0x39E0 | 0x39E1 | 14816 | 14817 | ANG_3S_HAR_V_39th_b | Aggr 3sec Phase B 39th Voltage Angle Harmonics | float | 2 | R
0x39E2 | 0x39E3 | 14818 | 14819 | ANG_3S_HAR_V_39th_c | Aggr 3sec Phase C 39th Voltage Angle Harmonics | float | 2 | R
0x39E4 | 0x39E5 | 14820 | 14821 | ANG_3S_HAR_I_39th_a | Aggr 3sec Phase A 39th Current Angle Harmonics | float | 2 | R
0x39E6 | 0x39E7 | 14822 | 14823 | ANG_3S_HAR_I_39th_b | Aggr 3sec Phase B 39th Current Angle Harmonics | float | 2 | R
0x39E8 | 0x39E9 | 14824 | 14825 | ANG_3S_HAR_I_39th_c | Aggr 3sec Phase C 39th Current Angle Harmonics | float | 2 | R
0x39EA | 0x39EB | 14826 | 14827 | ANG_3S_HAR_I_39th_n | Aggr 3sec Phase N 39th Current Angle Harmonics | float | 2 | R
0x39EC | 0x39ED | 14828 | 14829 | ANG_3S_HAR_V_40th_a | Aggr 3sec Phase A 40th Voltage Angle Harmonics | float | 2 | R
0x39EE | 0x39EF | 14830 | 14831 | ANG_3S_HAR_V_40th_b | Aggr 3sec Phase B 40th Voltage Angle Harmonics | float | 2 | R
0x39F0 | 0x39F1 | 14832 | 14833 | ANG_3S_HAR_V_40th_c | Aggr 3sec Phase C 40th Voltage Angle Harmonics | float | 2 | R
0x39F2 | 0x39F3 | 14834 | 14835 | ANG_3S_HAR_I_40th_a | Aggr 3sec Phase A 40th Current Angle Harmonics | float | 2 | R
0x39F4 | 0x39F5 | 14836 | 14837 | ANG_3S_HAR_I_40th_b | Aggr 3sec Phase B 40th Current Angle Harmonics | float | 2 | R
0x39F6 | 0x39F7 | 14838 | 14839 | ANG_3S_HAR_I_40th_c | Aggr 3sec Phase C 40th Current Angle Harmonics | float | 2 | R
0x39F8 | 0x39F9 | 14840 | 14841 | ANG_3S_HAR_I_40th_n | Aggr 3sec Phase N 40th Current Angle Harmonics | float | 2 | R
0x39FA | 0x39FB | 14842 | 14843 | ANG_3S_HAR_V_41th_a | Aggr 3sec Phase A 41st Voltage Angle Harmonics | float | 2 | R
0x39FC | 0x39FD | 14844 | 14845 | ANG_3S_HAR_V_41th_b | Aggr 3sec Phase B 41st Voltage Angle Harmonics | float | 2 | R
0x39FE | 0x39FF | 14846 | 14847 | ANG_3S_HAR_V_41th_c | Aggr 3sec Phase C 41st Voltage Angle Harmonics | float | 2 | R
0x3A00 | 0x3A01 | 14848 | 14849 | ANG_3S_HAR_I_41th_a | Aggr 3sec Phase A 41st Current Angle Harmonics | float | 2 | R
0x3A02 | 0x3A03 | 14850 | 14851 | ANG_3S_HAR_I_41th_b | Aggr 3sec Phase B 41st Current Angle Harmonics | float | 2 | R
0x3A04 | 0x3A05 | 14852 | 14853 | ANG_3S_HAR_I_41th_c | Aggr 3sec Phase C 41st Current Angle Harmonics | float | 2 | R
0x3A06 | 0x3A07 | 14854 | 14855 | ANG_3S_HAR_I_41th_n | Aggr 3sec Phase N 41st Current Angle Harmonics | float | 2 | R
0x3A08 | 0x3A09 | 14856 | 14857 | ANG_3S_HAR_V_42th_a | Aggr 3sec Phase A 42nd Voltage Angle Harmonics | float | 2 | R
0x3A0A | 0x3A0B | 14858 | 14859 | ANG_3S_HAR_V_42th_b | Aggr 3sec Phase B 42nd Voltage Angle Harmonics | float | 2 | R
0x3A0C | 0x3A0D | 14860 | 14861 | ANG_3S_HAR_V_42th_c | Aggr 3sec Phase C 42nd Voltage Angle Harmonics | float | 2 | R
0x3A0E | 0x3A0F | 14862 | 14863 | ANG_3S_HAR_I_42th_a | Aggr 3sec Phase A 42nd Current Angle Harmonics | float | 2 | R
0x3A10 | 0x3A11 | 14864 | 14865 | ANG_3S_HAR_I_42th_b | Aggr 3sec Phase B 42nd Current Angle Harmonics | float | 2 | R
0x3A12 | 0x3A13 | 14866 | 14867 | ANG_3S_HAR_I_42th_c | Aggr 3sec Phase C 42nd Current Angle Harmonics | float | 2 | R
0x3A14 | 0x3A15 | 14868 | 14869 | ANG_3S_HAR_I_42th_n | Aggr 3sec Phase N 42nd Current Angle Harmonics | float | 2 | R
0x3A16 | 0x3A17 | 14870 | 14871 | ANG_3S_HAR_V_43th_a | Aggr 3sec Phase A 43rd Voltage Angle Harmonics | float | 2 | R
0x3A18 | 0x3A19 | 14872 | 14873 | ANG_3S_HAR_V_43th_b | Aggr 3sec Phase B 43rd Voltage Angle Harmonics | float | 2 | R
0x3A1A | 0x3A1B | 14874 | 14875 | ANG_3S_HAR_V_43th_c | Aggr 3sec Phase C 43rd Voltage Angle Harmonics | float | 2 | R
0x3A1C | 0x3A1D | 14876 | 14877 | ANG_3S_HAR_I_43th_a | Aggr 3sec Phase A 43rd Current Angle Harmonics | float | 2 | R
0x3A1E | 0x3A1F | 14878 | 14879 | ANG_3S_HAR_I_43th_b | Aggr 3sec Phase B 43rd Current Angle Harmonics | float | 2 | R
0x3A20 | 0x3A21 | 14880 | 14881 | ANG_3S_HAR_I_43th_c | Aggr 3sec Phase C 43rd Current Angle Harmonics | float | 2 | R
0x3A22 | 0x3A23 | 14882 | 14883 | ANG_3S_HAR_I_43th_n | Aggr 3sec Phase N 43rd Current Angle Harmonics | float | 2 | R
0x3A24 | 0x3A25 | 14884 | 14885 | ANG_3S_HAR_V_44th_a | Aggr 3sec Phase A 44th Voltage Angle Harmonics | float | 2 | R
0x3A26 | 0x3A27 | 14886 | 14887 | ANG_3S_HAR_V_44th_b | Aggr 3sec Phase B 44th Voltage Angle Harmonics | float | 2 | R
0x3A28 | 0x3A29 | 14888 | 14889 | ANG_3S_HAR_V_44th_c | Aggr 3sec Phase C 44th Voltage Angle Harmonics | float | 2 | R
0x3A2A | 0x3A2B | 14890 | 14891 | ANG_3S_HAR_I_44th_a | Aggr 3sec Phase A 44th Current Angle Harmonics | float | 2 | R
0x3A2C | 0x3A2D | 14892 | 14893 | ANG_3S_HAR_I_44th_b | Aggr 3sec Phase B 44th Current Angle Harmonics | float | 2 | R
0x3A2E | 0x3A2F | 14894 | 14895 | ANG_3S_HAR_I_44th_c | Aggr 3sec Phase C 44th Current Angle Harmonics | float | 2 | R
0x3A30 | 0x3A31 | 14896 | 14897 | ANG_3S_HAR_I_44th_n | Aggr 3sec Phase N 44th Current Angle Harmonics | float | 2 | R
0x3A32 | 0x3A33 | 14898 | 14899 | ANG_3S_HAR_V_45th_a | Aggr 3sec Phase A 45th Voltage Angle Harmonics | float | 2 | R
0x3A34 | 0x3A35 | 14900 | 14901 | ANG_3S_HAR_V_45th_b | Aggr 3sec Phase B 45th Voltage Angle Harmonics | float | 2 | R
0x3A36 | 0x3A37 | 14902 | 14903 | ANG_3S_HAR_V_45th_c | Aggr 3sec Phase C 45th Voltage Angle Harmonics | float | 2 | R
0x3A38 | 0x3A39 | 14904 | 14905 | ANG_3S_HAR_I_45th_a | Aggr 3sec Phase A 45th Current Angle Harmonics | float | 2 | R
0x3A3A | 0x3A3B | 14906 | 14907 | ANG_3S_HAR_I_45th_b | Aggr 3sec Phase B 45th Current Angle Harmonics | float | 2 | R
0x3A3C | 0x3A3D | 14908 | 14909 | ANG_3S_HAR_I_45th_c | Aggr 3sec Phase C 45th Current Angle Harmonics | float | 2 | R
0x3A3E | 0x3A3F | 14910 | 14911 | ANG_3S_HAR_I_45th_n | Aggr 3sec Phase N 45th Current Angle Harmonics | float | 2 | R
0x3A40 | 0x3A41 | 14912 | 14913 | ANG_3S_HAR_V_46th_a | Aggr 3sec Phase A 46th Voltage Angle Harmonics | float | 2 | R
0x3A42 | 0x3A43 | 14914 | 14915 | ANG_3S_HAR_V_46th_b | Aggr 3sec Phase B 46th Voltage Angle Harmonics | float | 2 | R
0x3A44 | 0x3A45 | 14916 | 14917 | ANG_3S_HAR_V_46th_c | Aggr 3sec Phase C 46th Voltage Angle Harmonics | float | 2 | R
0x3A46 | 0x3A47 | 14918 | 14919 | ANG_3S_HAR_I_46th_a | Aggr 3sec Phase A 46th Current Angle Harmonics | float | 2 | R
0x3A48 | 0x3A49 | 14920 | 14921 | ANG_3S_HAR_I_46th_b | Aggr 3sec Phase B 46th Current Angle Harmonics | float | 2 | R
0x3A4A | 0x3A4B | 14922 | 14923 | ANG_3S_HAR_I_46th_c | Aggr 3sec Phase C 46th Current Angle Harmonics | float | 2 | R
0x3A4C | 0x3A4D | 14924 | 14925 | ANG_3S_HAR_I_46th_n | Aggr 3sec Phase N 46th Current Angle Harmonics | float | 2 | R
0x3A4E | 0x3A4F | 14926 | 14927 | ANG_3S_HAR_V_47th_a | Aggr 3sec Phase A 47th Voltage Angle Harmonics | float | 2 | R
0x3A50 | 0x3A51 | 14928 | 14929 | ANG_3S_HAR_V_47th_b | Aggr 3sec Phase B 47th Voltage Angle Harmonics | float | 2 | R
0x3A52 | 0x3A53 | 14930 | 14931 | ANG_3S_HAR_V_47th_c | Aggr 3sec Phase C 47th Voltage Angle Harmonics | float | 2 | R
0x3A54 | 0x3A55 | 14932 | 14933 | ANG_3S_HAR_I_47th_a | Aggr 3sec Phase A 47th Current Angle Harmonics | float | 2 | R
0x3A56 | 0x3A57 | 14934 | 14935 | ANG_3S_HAR_I_47th_b | Aggr 3sec Phase B 47th Current Angle Harmonics | float | 2 | R
0x3A58 | 0x3A59 | 14936 | 14937 | ANG_3S_HAR_I_47th_c | Aggr 3sec Phase C 47th Current Angle Harmonics | float | 2 | R
0x3A5A | 0x3A5B | 14938 | 14939 | ANG_3S_HAR_I_47th_n | Aggr 3sec Phase N 47th Current Angle Harmonics | float | 2 | R
0x3A5C | 0x3A5D | 14940 | 14941 | ANG_3S_HAR_V_48th_a | Aggr 3sec Phase A 48th Voltage Angle Harmonics | float | 2 | R
0x3A5E | 0x3A5F | 14942 | 14943 | ANG_3S_HAR_V_48th_b | Aggr 3sec Phase B 48th Voltage Angle Harmonics | float | 2 | R
0x3A60 | 0x3A61 | 14944 | 14945 | ANG_3S_HAR_V_48th_c | Aggr 3sec Phase C 48th Voltage Angle Harmonics | float | 2 | R
0x3A62 | 0x3A63 | 14946 | 14947 | ANG_3S_HAR_I_48th_a | Aggr 3sec Phase A 48th Current Angle Harmonics | float | 2 | R
0x3A64 | 0x3A65 | 14948 | 14949 | ANG_3S_HAR_I_48th_b | Aggr 3sec Phase B 48th Current Angle Harmonics | float | 2 | R
0x3A66 | 0x3A67 | 14950 | 14951 | ANG_3S_HAR_I_48th_c | Aggr 3sec Phase C 48th Current Angle Harmonics | float | 2 | R
0x3A68 | 0x3A69 | 14952 | 14953 | ANG_3S_HAR_I_48th_n | Aggr 3sec Phase N 48th Current Angle Harmonics | float | 2 | R
0x3A6A | 0x3A6B | 14954 | 14955 | ANG_3S_HAR_V_49th_a | Aggr 3sec Phase A 49th Voltage Angle Harmonics | float | 2 | R
0x3A6C | 0x3A6D | 14956 | 14957 | ANG_3S_HAR_V_49th_b | Aggr 3sec Phase B 49th Voltage Angle Harmonics | float | 2 | R
0x3A6E | 0x3A6F | 14958 | 14959 | ANG_3S_HAR_V_49th_c | Aggr 3sec Phase C 49th Voltage Angle Harmonics | float | 2 | R
0x3A70 | 0x3A71 | 14960 | 14961 | ANG_3S_HAR_I_49th_a | Aggr 3sec Phase A 49th Current Angle Harmonics | float | 2 | R
0x3A72 | 0x3A73 | 14962 | 14963 | ANG_3S_HAR_I_49th_b | Aggr 3sec Phase B 49th Current Angle Harmonics | float | 2 | R
0x3A74 | 0x3A75 | 14964 | 14965 | ANG_3S_HAR_I_49th_c | Aggr 3sec Phase C 49th Current Angle Harmonics | float | 2 | R
0x3A76 | 0x3A77 | 14966 | 14967 | ANG_3S_HAR_I_49th_n | Aggr 3sec Phase N 49th Current Angle Harmonics | float | 2 | R
0x3A78 | 0x3A79 | 14968 | 14969 | ANG_3S_HAR_V_50th_a | Aggr 3sec Phase A 50th Voltage Angle Harmonics | float | 2 | R
0x3A7A | 0x3A7B | 14970 | 14971 | ANG_3S_HAR_V_50th_b | Aggr 3sec Phase B 50th Voltage Angle Harmonics | float | 2 | R
0x3A7C | 0x3A7D | 14972 | 14973 | ANG_3S_HAR_V_50th_c | Aggr 3sec Phase C 50th Voltage Angle Harmonics | float | 2 | R
0x3A7E | 0x3A7F | 14974 | 14975 | ANG_3S_HAR_I_50th_a | Aggr 3sec Phase A 50th Current Angle Harmonics | float | 2 | R
0x3A80 | 0x3A81 | 14976 | 14977 | ANG_3S_HAR_I_50th_b | Aggr 3sec Phase B 50th Current Angle Harmonics | float | 2 | R
0x3A82 | 0x3A83 | 14978 | 14979 | ANG_3S_HAR_I_50th_c | Aggr 3sec Phase C 50th Current Angle Harmonics | float | 2 | R
0x3A84 | 0x3A85 | 14980 | 14981 | ANG_3S_HAR_I_50th_n | Aggr 3sec Phase N 50th Current Angle Harmonics | float | 2 | R
0x3A86 | 0x3A87 | 14982 | 14983 | ANG_3S_HAR_V_51th_a | Aggr 3sec Phase A 51st Voltage Angle Harmonics | float | 2 | R
0x3A88 | 0x3A89 | 14984 | 14985 | ANG_3S_HAR_V_51th_b | Aggr 3sec Phase B 51st Voltage Angle Harmonics | float | 2 | R
0x3A8A | 0x3A8B | 14986 | 14987 | ANG_3S_HAR_V_51th_c | Aggr 3sec Phase C 51st Voltage Angle Harmonics | float | 2 | R
0x3A8C | 0x3A8D | 14988 | 14989 | ANG_3S_HAR_I_51th_a | Aggr 3sec Phase A 51st Current Angle Harmonics | float | 2 | R
0x3A8E | 0x3A8F | 14990 | 14991 | ANG_3S_HAR_I_51th_b | Aggr 3sec Phase B 51st Current Angle Harmonics | float | 2 | R
0x3A90 | 0x3A91 | 14992 | 14993 | ANG_3S_HAR_I_51th_c | Aggr 3sec Phase C 51st Current Angle Harmonics | float | 2 | R
0x3A92 | 0x3A93 | 14994 | 14995 | ANG_3S_HAR_I_51th_n | Aggr 3sec Phase N 51st Current Angle Harmonics | float | 2 | R
0x3A94 | 0x3A95 | 14996 | 14997 | ANG_3S_HAR_V_52th_a | Aggr 3sec Phase A 52nd Voltage Angle Harmonics | float | 2 | R
0x3A96 | 0x3A97 | 14998 | 14999 | ANG_3S_HAR_V_52th_b | Aggr 3sec Phase B 52nd Voltage Angle Harmonics | float | 2 | R
0x3A98 | 0x3A99 | 15000 | 15001 | ANG_3S_HAR_V_52th_c | Aggr 3sec Phase C 52nd Voltage Angle Harmonics | float | 2 | R
0x3A9A | 0x3A9B | 15002 | 15003 | ANG_3S_HAR_I_52th_a | Aggr 3sec Phase A 52nd Current Angle Harmonics | float | 2 | R
0x3A9C | 0x3A9D | 15004 | 15005 | ANG_3S_HAR_I_52th_b | Aggr 3sec Phase B 52nd Current Angle Harmonics | float | 2 | R
0x3A9E | 0x3A9F | 15006 | 15007 | ANG_3S_HAR_I_52th_c | Aggr 3sec Phase C 52nd Current Angle Harmonics | float | 2 | R
0x3AA0 | 0x3AA1 | 15008 | 15009 | ANG_3S_HAR_I_52th_n | Aggr 3sec Phase N 52nd Current Angle Harmonics | float | 2 | R
0x3AA2 | 0x3AA3 | 15010 | 15011 | ANG_3S_HAR_V_53th_a | Aggr 3sec Phase A 53rd Voltage Angle Harmonics | float | 2 | R
0x3AA4 | 0x3AA5 | 15012 | 15013 | ANG_3S_HAR_V_53th_b | Aggr 3sec Phase B 53rd Voltage Angle Harmonics | float | 2 | R
0x3AA6 | 0x3AA7 | 15014 | 15015 | ANG_3S_HAR_V_53th_c | Aggr 3sec Phase C 53rd Voltage Angle Harmonics | float | 2 | R
0x3AA8 | 0x3AA9 | 15016 | 15017 | ANG_3S_HAR_I_53th_a | Aggr 3sec Phase A 53rd Current Angle Harmonics | float | 2 | R
0x3AAA | 0x3AAB | 15018 | 15019 | ANG_3S_HAR_I_53th_b | Aggr 3sec Phase B 53rd Current Angle Harmonics | float | 2 | R
0x3AAC | 0x3AAD | 15020 | 15021 | ANG_3S_HAR_I_53th_c | Aggr 3sec Phase C 53rd Current Angle Harmonics | float | 2 | R
0x3AAE | 0x3AAF | 15022 | 15023 | ANG_3S_HAR_I_53th_n | Aggr 3sec Phase N 53rd Current Angle Harmonics | float | 2 | R
0x3AB0 | 0x3AB1 | 15024 | 15025 | ANG_3S_HAR_V_54th_a | Aggr 3sec Phase A 54th Voltage Angle Harmonics | float | 2 | R
0x3AB2 | 0x3AB3 | 15026 | 15027 | ANG_3S_HAR_V_54th_b | Aggr 3sec Phase B 54th Voltage Angle Harmonics | float | 2 | R
0x3AB4 | 0x3AB5 | 15028 | 15029 | ANG_3S_HAR_V_54th_c | Aggr 3sec Phase C 54th Voltage Angle Harmonics | float | 2 | R
0x3AB6 | 0x3AB7 | 15030 | 15031 | ANG_3S_HAR_I_54th_a | Aggr 3sec Phase A 54th Current Angle Harmonics | float | 2 | R
0x3AB8 | 0x3AB9 | 15032 | 15033 | ANG_3S_HAR_I_54th_b | Aggr 3sec Phase B 54th Current Angle Harmonics | float | 2 | R
0x3ABA | 0x3ABB | 15034 | 15035 | ANG_3S_HAR_I_54th_c | Aggr 3sec Phase C 54th Current Angle Harmonics | float | 2 | R
0x3ABC | 0x3ABD | 15036 | 15037 | ANG_3S_HAR_I_54th_n | Aggr 3sec Phase N 54th Current Angle Harmonics | float | 2 | R
0x3ABE | 0x3ABF | 15038 | 15039 | ANG_3S_HAR_V_55th_a | Aggr 3sec Phase A 55th Voltage Angle Harmonics | float | 2 | R
0x3AC0 | 0x3AC1 | 15040 | 15041 | ANG_3S_HAR_V_55th_b | Aggr 3sec Phase B 55th Voltage Angle Harmonics | float | 2 | R
0x3AC2 | 0x3AC3 | 15042 | 15043 | ANG_3S_HAR_V_55th_c | Aggr 3sec Phase C 55th Voltage Angle Harmonics | float | 2 | R
0x3AC4 | 0x3AC5 | 15044 | 15045 | ANG_3S_HAR_I_55th_a | Aggr 3sec Phase A 55th Current Angle Harmonics | float | 2 | R
0x3AC6 | 0x3AC7 | 15046 | 15047 | ANG_3S_HAR_I_55th_b | Aggr 3sec Phase B 55th Current Angle Harmonics | float | 2 | R
0x3AC8 | 0x3AC9 | 15048 | 15049 | ANG_3S_HAR_I_55th_c | Aggr 3sec Phase C 55th Current Angle Harmonics | float | 2 | R
0x3ACA | 0x3ACB | 15050 | 15051 | ANG_3S_HAR_I_55th_n | Aggr 3sec Phase N 55th Current Angle Harmonics | float | 2 | R
0x3ACC | 0x3ACD | 15052 | 15053 | ANG_3S_HAR_V_56th_a | Aggr 3sec Phase A 56th Voltage Angle Harmonics | float | 2 | R
0x3ACE | 0x3ACF | 15054 | 15055 | ANG_3S_HAR_V_56th_b | Aggr 3sec Phase B 56th Voltage Angle Harmonics | float | 2 | R
0x3AD0 | 0x3AD1 | 15056 | 15057 | ANG_3S_HAR_V_56th_c | Aggr 3sec Phase C 56th Voltage Angle Harmonics | float | 2 | R
0x3AD2 | 0x3AD3 | 15058 | 15059 | ANG_3S_HAR_I_56th_a | Aggr 3sec Phase A 56th Current Angle Harmonics | float | 2 | R
0x3AD4 | 0x3AD5 | 15060 | 15061 | ANG_3S_HAR_I_56th_b | Aggr 3sec Phase B 56th Current Angle Harmonics | float | 2 | R
0x3AD6 | 0x3AD7 | 15062 | 15063 | ANG_3S_HAR_I_56th_c | Aggr 3sec Phase C 56th Current Angle Harmonics | float | 2 | R
0x3AD8 | 0x3AD9 | 15064 | 15065 | ANG_3S_HAR_I_56th_n | Aggr 3sec Phase N 56th Current Angle Harmonics | float | 2 | R
0x3ADA | 0x3ADB | 15066 | 15067 | ANG_3S_HAR_V_57th_a | Aggr 3sec Phase A 57th Voltage Angle Harmonics | float | 2 | R
0x3ADC | 0x3ADD | 15068 | 15069 | ANG_3S_HAR_V_57th_b | Aggr 3sec Phase B 57th Voltage Angle Harmonics | float | 2 | R
0x3ADE | 0x3ADF | 15070 | 15071 | ANG_3S_HAR_V_57th_c | Aggr 3sec Phase C 57th Voltage Angle Harmonics | float | 2 | R
0x3AE0 | 0x3AE1 | 15072 | 15073 | ANG_3S_HAR_I_57th_a | Aggr 3sec Phase A 57th Current Angle Harmonics | float | 2 | R
0x3AE2 | 0x3AE3 | 15074 | 15075 | ANG_3S_HAR_I_57th_b | Aggr 3sec Phase B 57th Current Angle Harmonics | float | 2 | R
0x3AE4 | 0x3AE5 | 15076 | 15077 | ANG_3S_HAR_I_57th_c | Aggr 3sec Phase C 57th Current Angle Harmonics | float | 2 | R
0x3AE6 | 0x3AE7 | 15078 | 15079 | ANG_3S_HAR_I_57th_n | Aggr 3sec Phase N 57th Current Angle Harmonics | float | 2 | R
0x3AE8 | 0x3AE9 | 15080 | 15081 | ANG_3S_HAR_V_58th_a | Aggr 3sec Phase A 58th Voltage Angle Harmonics | float | 2 | R
0x3AEA | 0x3AEB | 15082 | 15083 | ANG_3S_HAR_V_58th_b | Aggr 3sec Phase B 58th Voltage Angle Harmonics | float | 2 | R
0x3AEC | 0x3AED | 15084 | 15085 | ANG_3S_HAR_V_58th_c | Aggr 3sec Phase C 58th Voltage Angle Harmonics | float | 2 | R
0x3AEE | 0x3AEF | 15086 | 15087 | ANG_3S_HAR_I_58th_a | Aggr 3sec Phase A 58th Current Angle Harmonics | float | 2 | R
0x3AF0 | 0x3AF1 | 15088 | 15089 | ANG_3S_HAR_I_58th_b | Aggr 3sec Phase B 58th Current Angle Harmonics | float | 2 | R
0x3AF2 | 0x3AF3 | 15090 | 15091 | ANG_3S_HAR_I_58th_c | Aggr 3sec Phase C 58th Current Angle Harmonics | float | 2 | R
0x3AF4 | 0x3AF5 | 15092 | 15093 | ANG_3S_HAR_I_58th_n | Aggr 3sec Phase N 58th Current Angle Harmonics | float | 2 | R
0x3AF6 | 0x3AF7 | 15094 | 15095 | ANG_3S_HAR_V_59th_a | Aggr 3sec Phase A 59th Voltage Angle Harmonics | float | 2 | R
0x3AF8 | 0x3AF9 | 15096 | 15097 | ANG_3S_HAR_V_59th_b | Aggr 3sec Phase B 59th Voltage Angle Harmonics | float | 2 | R
0x3AFA | 0x3AFB | 15098 | 15099 | ANG_3S_HAR_V_59th_c | Aggr 3sec Phase C 59th Voltage Angle Harmonics | float | 2 | R
0x3AFC | 0x3AFD | 15100 | 15101 | ANG_3S_HAR_I_59th_a | Aggr 3sec Phase A 59th Current Angle Harmonics | float | 2 | R
0x3AFE | 0x3AFF | 15102 | 15103 | ANG_3S_HAR_I_59th_b | Aggr 3sec Phase B 59th Current Angle Harmonics | float | 2 | R
0x3B00 | 0x3B01 | 15104 | 15105 | ANG_3S_HAR_I_59th_c | Aggr 3sec Phase C 59th Current Angle Harmonics | float | 2 | R
0x3B02 | 0x3B03 | 15106 | 15107 | ANG_3S_HAR_I_59th_n | Aggr 3sec Phase N 59th Current Angle Harmonics | float | 2 | R
0x3B04 | 0x3B05 | 15108 | 15109 | ANG_3S_HAR_V_60th_a | Aggr 3sec Phase A 60th Voltage Angle Harmonics | float | 2 | R
0x3B06 | 0x3B07 | 15110 | 15111 | ANG_3S_HAR_V_60th_b | Aggr 3sec Phase B 60th Voltage Angle Harmonics | float | 2 | R
0x3B08 | 0x3B09 | 15112 | 15113 | ANG_3S_HAR_V_60th_c | Aggr 3sec Phase C 60th Voltage Angle Harmonics | float | 2 | R
0x3B0A | 0x3B0B | 15114 | 15115 | ANG_3S_HAR_I_60th_a | Aggr 3sec Phase A 60th Current Angle Harmonics | float | 2 | R
0x3B0C | 0x3B0D | 15116 | 15117 | ANG_3S_HAR_I_60th_b | Aggr 3sec Phase B 60th Current Angle Harmonics | float | 2 | R
0x3B0E | 0x3B0F | 15118 | 15119 | ANG_3S_HAR_I_60th_c | Aggr 3sec Phase C 60th Current Angle Harmonics | float | 2 | R
0x3B10 | 0x3B11 | 15120 | 15121 | ANG_3S_HAR_I_60th_n | Aggr 3sec Phase N 60th Current Angle Harmonics | float | 2 | R
0x3B12 | 0x3B13 | 15122 | 15123 | ANG_3S_HAR_V_61th_a | Aggr 3sec Phase A 61st Voltage Angle Harmonics | float | 2 | R
0x3B14 | 0x3B15 | 15124 | 15125 | ANG_3S_HAR_V_61th_b | Aggr 3sec Phase B 61st Voltage Angle Harmonics | float | 2 | R
0x3B16 | 0x3B17 | 15126 | 15127 | ANG_3S_HAR_V_61th_c | Aggr 3sec Phase C 61st Voltage Angle Harmonics | float | 2 | R
0x3B18 | 0x3B19 | 15128 | 15129 | ANG_3S_HAR_I_61th_a | Aggr 3sec Phase A 61st Current Angle Harmonics | float | 2 | R
0x3B1A | 0x3B1B | 15130 | 15131 | ANG_3S_HAR_I_61th_b | Aggr 3sec Phase B 61st Current Angle Harmonics | float | 2 | R
0x3B1C | 0x3B1D | 15132 | 15133 | ANG_3S_HAR_I_61th_c | Aggr 3sec Phase C 61st Current Angle Harmonics | float | 2 | R
0x3B1E | 0x3B1F | 15134 | 15135 | ANG_3S_HAR_I_61th_n | Aggr 3sec Phase N 61st Current Angle Harmonics | float | 2 | R
0x3B20 | 0x3B21 | 15136 | 15137 | ANG_3S_HAR_V_62th_a | Aggr 3sec Phase A 62nd Voltage Angle Harmonics | float | 2 | R
0x3B22 | 0x3B23 | 15138 | 15139 | ANG_3S_HAR_V_62th_b | Aggr 3sec Phase B 62nd Voltage Angle Harmonics | float | 2 | R
0x3B24 | 0x3B25 | 15140 | 15141 | ANG_3S_HAR_V_62th_c | Aggr 3sec Phase C 62nd Voltage Angle Harmonics | float | 2 | R
0x3B26 | 0x3B27 | 15142 | 15143 | ANG_3S_HAR_I_62th_a | Aggr 3sec Phase A 62nd Current Angle Harmonics | float | 2 | R
0x3B28 | 0x3B29 | 15144 | 15145 | ANG_3S_HAR_I_62th_b | Aggr 3sec Phase B 62nd Current Angle Harmonics | float | 2 | R
0x3B2A | 0x3B2B | 15146 | 15147 | ANG_3S_HAR_I_62th_c | Aggr 3sec Phase C 62nd Current Angle Harmonics | float | 2 | R
0x3B2C | 0x3B2D | 15148 | 15149 | ANG_3S_HAR_I_62th_n | Aggr 3sec Phase N 62nd Current Angle Harmonics | float | 2 | R
0x3B2E | 0x3B2F | 15150 | 15151 | ANG_3S_HAR_V_63th_a | Aggr 3sec Phase A 63rd Voltage Angle Harmonics | float | 2 | R
0x3B30 | 0x3B31 | 15152 | 15153 | ANG_3S_HAR_V_63th_b | Aggr 3sec Phase B 63rd Voltage Angle Harmonics | float | 2 | R
0x3B32 | 0x3B33 | 15154 | 15155 | ANG_3S_HAR_V_63th_c | Aggr 3sec Phase C 63rd Voltage Angle Harmonics | float | 2 | R
0x3B34 | 0x3B35 | 15156 | 15157 | ANG_3S_HAR_I_63th_a | Aggr 3sec Phase A 63rd Current Angle Harmonics | float | 2 | R
0x3B36 | 0x3B37 | 15158 | 15159 | ANG_3S_HAR_I_63th_b | Aggr 3sec Phase B 63rd Current Angle Harmonics | float | 2 | R
0x3B38 | 0x3B39 | 15160 | 15161 | ANG_3S_HAR_I_63th_c | Aggr 3sec Phase C 63rd Current Angle Harmonics | float | 2 | R
0x3B3A | 0x3B3B | 15162 | 15163 | ANG_3S_HAR_I_63th_n | Aggr 3sec Phase N 63rd Current Angle Harmonics | float | 2 | R
0x3B3C | 0x3B3D | 15164 | 15165 | ANG_3S_HAR_V_64th_a | Aggr 3sec Phase A 64th Voltage Angle Harmonics | float | 2 | R
0x3B3E | 0x3B3F | 15166 | 15167 | ANG_3S_HAR_V_64th_b | Aggr 3sec Phase B 64th Voltage Angle Harmonics | float | 2 | R
0x3B40 | 0x3B41 | 15168 | 15169 | ANG_3S_HAR_V_64th_c | Aggr 3sec Phase C 64th Voltage Angle Harmonics | float | 2 | R
0x3B42 | 0x3B43 | 15170 | 15171 | ANG_3S_HAR_I_64th_a | Aggr 3sec Phase A 64th Current Angle Harmonics | float | 2 | R
0x3B44 | 0x3B45 | 15172 | 15173 | ANG_3S_HAR_I_64th_b | Aggr 3sec Phase B 64th Current Angle Harmonics | float | 2 | R
0x3B46 | 0x3B47 | 15174 | 15175 | ANG_3S_HAR_I_64th_c | Aggr 3sec Phase C 64th Current Angle Harmonics | float | 2 | R
0x3B48 | 0x3B49 | 15176 | 15177 | ANG_3S_HAR_I_64th_n | Aggr 3sec Phase N 64th Current Angle Harmonics | float | 2 | R
0x3B4A | 0x3B4B | 15178 | 15179 | ANG_3S_HAR_V_65th_a | Aggr 3sec Phase A 65th Voltage Angle Harmonics | float | 2 | R
0x3B4C | 0x3B4D | 15180 | 15181 | ANG_3S_HAR_V_65th_b | Aggr 3sec Phase B 65th Voltage Angle Harmonics | float | 2 | R
0x3B4E | 0x3B4F | 15182 | 15183 | ANG_3S_HAR_V_65th_c | Aggr 3sec Phase C 65th Voltage Angle Harmonics | float | 2 | R
0x3B50 | 0x3B51 | 15184 | 15185 | ANG_3S_HAR_I_65th_a | Aggr 3sec Phase A 65th Current Angle Harmonics | float | 2 | R
0x3B52 | 0x3B53 | 15186 | 15187 | ANG_3S_HAR_I_65th_b | Aggr 3sec Phase B 65th Current Angle Harmonics | float | 2 | R
0x3B54 | 0x3B55 | 15188 | 15189 | ANG_3S_HAR_I_65th_c | Aggr 3sec Phase C 65th Current Angle Harmonics | float | 2 | R
0x3B56 | 0x3B57 | 15190 | 15191 | ANG_3S_HAR_I_65th_n | Aggr 3sec Phase N 65th Current Angle Harmonics | float | 2 | R
0x3B58 | 0x3B59 | 15192 | 15193 | ANG_3S_HAR_V_66th_a | Aggr 3sec Phase A 66th Voltage Angle Harmonics | float | 2 | R
0x3B5A | 0x3B5B | 15194 | 15195 | ANG_3S_HAR_V_66th_b | Aggr 3sec Phase B 66th Voltage Angle Harmonics | float | 2 | R
0x3B5C | 0x3B5D | 15196 | 15197 | ANG_3S_HAR_V_66th_c | Aggr 3sec Phase C 66th Voltage Angle Harmonics | float | 2 | R
0x3B5E | 0x3B5F | 15198 | 15199 | ANG_3S_HAR_I_66th_a | Aggr 3sec Phase A 66th Current Angle Harmonics | float | 2 | R
0x3B60 | 0x3B61 | 15200 | 15201 | ANG_3S_HAR_I_66th_b | Aggr 3sec Phase B 66th Current Angle Harmonics | float | 2 | R
0x3B62 | 0x3B63 | 15202 | 15203 | ANG_3S_HAR_I_66th_c | Aggr 3sec Phase C 66th Current Angle Harmonics | float | 2 | R
0x3B64 | 0x3B65 | 15204 | 15205 | ANG_3S_HAR_I_66th_n | Aggr 3sec Phase N 66th Current Angle Harmonics | float | 2 | R
0x3B66 | 0x3B67 | 15206 | 15207 | ANG_3S_HAR_V_67th_a | Aggr 3sec Phase A 67th Voltage Angle Harmonics | float | 2 | R
0x3B68 | 0x3B69 | 15208 | 15209 | ANG_3S_HAR_V_67th_b | Aggr 3sec Phase B 67th Voltage Angle Harmonics | float | 2 | R
0x3B6A | 0x3B6B | 15210 | 15211 | ANG_3S_HAR_V_67th_c | Aggr 3sec Phase C 67th Voltage Angle Harmonics | float | 2 | R
0x3B6C | 0x3B6D | 15212 | 15213 | ANG_3S_HAR_I_67th_a | Aggr 3sec Phase A 67th Current Angle Harmonics | float | 2 | R
0x3B6E | 0x3B6F | 15214 | 15215 | ANG_3S_HAR_I_67th_b | Aggr 3sec Phase B 67th Current Angle Harmonics | float | 2 | R
0x3B70 | 0x3B71 | 15216 | 15217 | ANG_3S_HAR_I_67th_c | Aggr 3sec Phase C 67th Current Angle Harmonics | float | 2 | R
0x3B72 | 0x3B73 | 15218 | 15219 | ANG_3S_HAR_I_67th_n | Aggr 3sec Phase N 67th Current Angle Harmonics | float | 2 | R
0x3B74 | 0x3B75 | 15220 | 15221 | ANG_3S_HAR_V_68th_a | Aggr 3sec Phase A 68th Voltage Angle Harmonics | float | 2 | R
0x3B76 | 0x3B77 | 15222 | 15223 | ANG_3S_HAR_V_68th_b | Aggr 3sec Phase B 68th Voltage Angle Harmonics | float | 2 | R
0x3B78 | 0x3B79 | 15224 | 15225 | ANG_3S_HAR_V_68th_c | Aggr 3sec Phase C 68th Voltage Angle Harmonics | float | 2 | R
0x3B7A | 0x3B7B | 15226 | 15227 | ANG_3S_HAR_I_68th_a | Aggr 3sec Phase A 68th Current Angle Harmonics | float | 2 | R
0x3B7C | 0x3B7D | 15228 | 15229 | ANG_3S_HAR_I_68th_b | Aggr 3sec Phase B 68th Current Angle Harmonics | float | 2 | R
0x3B7E | 0x3B7F | 15230 | 15231 | ANG_3S_HAR_I_68th_c | Aggr 3sec Phase C 68th Current Angle Harmonics | float | 2 | R
0x3B80 | 0x3B81 | 15232 | 15233 | ANG_3S_HAR_I_68th_n | Aggr 3sec Phase N 68th Current Angle Harmonics | float | 2 | R
0x3B82 | 0x3B83 | 15234 | 15235 | ANG_3S_HAR_V_69th_a | Aggr 3sec Phase A 69th Voltage Angle Harmonics | float | 2 | R
0x3B84 | 0x3B85 | 15236 | 15237 | ANG_3S_HAR_V_69th_b | Aggr 3sec Phase B 69th Voltage Angle Harmonics | float | 2 | R
0x3B86 | 0x3B87 | 15238 | 15239 | ANG_3S_HAR_V_69th_c | Aggr 3sec Phase C 69th Voltage Angle Harmonics | float | 2 | R
0x3B88 | 0x3B89 | 15240 | 15241 | ANG_3S_HAR_I_69th_a | Aggr 3sec Phase A 69th Current Angle Harmonics | float | 2 | R
0x3B8A | 0x3B8B | 15242 | 15243 | ANG_3S_HAR_I_69th_b | Aggr 3sec Phase B 69th Current Angle Harmonics | float | 2 | R
0x3B8C | 0x3B8D | 15244 | 15245 | ANG_3S_HAR_I_69th_c | Aggr 3sec Phase C 69th Current Angle Harmonics | float | 2 | R
0x3B8E | 0x3B8F | 15246 | 15247 | ANG_3S_HAR_I_69th_n | Aggr 3sec Phase N 69th Current Angle Harmonics | float | 2 | R
0x3B90 | 0x3B91 | 15248 | 15249 | ANG_3S_HAR_V_70th_a | Aggr 3sec Phase A 70th Voltage Angle Harmonics | float | 2 | R
0x3B92 | 0x3B93 | 15250 | 15251 | ANG_3S_HAR_V_70th_b | Aggr 3sec Phase B 70th Voltage Angle Harmonics | float | 2 | R
0x3B94 | 0x3B95 | 15252 | 15253 | ANG_3S_HAR_V_70th_c | Aggr 3sec Phase C 70th Voltage Angle Harmonics | float | 2 | R
0x3B96 | 0x3B97 | 15254 | 15255 | ANG_3S_HAR_I_70th_a | Aggr 3sec Phase A 70th Current Angle Harmonics | float | 2 | R
0x3B98 | 0x3B99 | 15256 | 15257 | ANG_3S_HAR_I_70th_b | Aggr 3sec Phase B 70th Current Angle Harmonics | float | 2 | R
0x3B9A | 0x3B9B | 15258 | 15259 | ANG_3S_HAR_I_70th_c | Aggr 3sec Phase C 70th Current Angle Harmonics | float | 2 | R
0x3B9C | 0x3B9D | 15260 | 15261 | ANG_3S_HAR_I_70th_n | Aggr 3sec Phase N 70th Current Angle Harmonics | float | 2 | R
0x3B9E | 0x3B9F | 15262 | 15263 | ANG_3S_HAR_V_71th_a | Aggr 3sec Phase A 71st Voltage Angle Harmonics | float | 2 | R
0x3BA0 | 0x3BA1 | 15264 | 15265 | ANG_3S_HAR_V_71th_b | Aggr 3sec Phase B 71st Voltage Angle Harmonics | float | 2 | R
0x3BA2 | 0x3BA3 | 15266 | 15267 | ANG_3S_HAR_V_71th_c | Aggr 3sec Phase C 71st Voltage Angle Harmonics | float | 2 | R
0x3BA4 | 0x3BA5 | 15268 | 15269 | ANG_3S_HAR_I_71th_a | Aggr 3sec Phase A 71st Current Angle Harmonics | float | 2 | R
0x3BA6 | 0x3BA7 | 15270 | 15271 | ANG_3S_HAR_I_71th_b | Aggr 3sec Phase B 71st Current Angle Harmonics | float | 2 | R
0x3BA8 | 0x3BA9 | 15272 | 15273 | ANG_3S_HAR_I_71th_c | Aggr 3sec Phase C 71st Current Angle Harmonics | float | 2 | R
0x3BAA | 0x3BAB | 15274 | 15275 | ANG_3S_HAR_I_71th_n | Aggr 3sec Phase N 71st Current Angle Harmonics | float | 2 | R
0x3BAC | 0x3BAD | 15276 | 15277 | ANG_3S_HAR_V_72th_a | Aggr 3sec Phase A 72nd Voltage Angle Harmonics | float | 2 | R
0x3BAE | 0x3BAF | 15278 | 15279 | ANG_3S_HAR_V_72th_b | Aggr 3sec Phase B 72nd Voltage Angle Harmonics | float | 2 | R
0x3BB0 | 0x3BB1 | 15280 | 15281 | ANG_3S_HAR_V_72th_c | Aggr 3sec Phase C 72nd Voltage Angle Harmonics | float | 2 | R
0x3BB2 | 0x3BB3 | 15282 | 15283 | ANG_3S_HAR_I_72th_a | Aggr 3sec Phase A 72nd Current Angle Harmonics | float | 2 | R
0x3BB4 | 0x3BB5 | 15284 | 15285 | ANG_3S_HAR_I_72th_b | Aggr 3sec Phase B 72nd Current Angle Harmonics | float | 2 | R
0x3BB6 | 0x3BB7 | 15286 | 15287 | ANG_3S_HAR_I_72th_c | Aggr 3sec Phase C 72nd Current Angle Harmonics | float | 2 | R
0x3BB8 | 0x3BB9 | 15288 | 15289 | ANG_3S_HAR_I_72th_n | Aggr 3sec Phase N 72nd Current Angle Harmonics | float | 2 | R
0x3BBA | 0x3BBB | 15290 | 15291 | ANG_3S_HAR_V_73th_a | Aggr 3sec Phase A 73rd Voltage Angle Harmonics | float | 2 | R
0x3BBC | 0x3BBD | 15292 | 15293 | ANG_3S_HAR_V_73th_b | Aggr 3sec Phase B 73rd Voltage Angle Harmonics | float | 2 | R
0x3BBE | 0x3BBF | 15294 | 15295 | ANG_3S_HAR_V_73th_c | Aggr 3sec Phase C 73rd Voltage Angle Harmonics | float | 2 | R
0x3BC0 | 0x3BC1 | 15296 | 15297 | ANG_3S_HAR_I_73th_a | Aggr 3sec Phase A 73rd Current Angle Harmonics | float | 2 | R
0x3BC2 | 0x3BC3 | 15298 | 15299 | ANG_3S_HAR_I_73th_b | Aggr 3sec Phase B 73rd Current Angle Harmonics | float | 2 | R
0x3BC4 | 0x3BC5 | 15300 | 15301 | ANG_3S_HAR_I_73th_c | Aggr 3sec Phase C 73rd Current Angle Harmonics | float | 2 | R
0x3BC6 | 0x3BC7 | 15302 | 15303 | ANG_3S_HAR_I_73th_n | Aggr 3sec Phase N 73rd Current Angle Harmonics | float | 2 | R
0x3BC8 | 0x3BC9 | 15304 | 15305 | ANG_3S_HAR_V_74th_a | Aggr 3sec Phase A 74th Voltage Angle Harmonics | float | 2 | R
0x3BCA | 0x3BCB | 15306 | 15307 | ANG_3S_HAR_V_74th_b | Aggr 3sec Phase B 74th Voltage Angle Harmonics | float | 2 | R
0x3BCC | 0x3BCD | 15308 | 15309 | ANG_3S_HAR_V_74th_c | Aggr 3sec Phase C 74th Voltage Angle Harmonics | float | 2 | R
0x3BCE | 0x3BCF | 15310 | 15311 | ANG_3S_HAR_I_74th_a | Aggr 3sec Phase A 74th Current Angle Harmonics | float | 2 | R
0x3BD0 | 0x3BD1 | 15312 | 15313 | ANG_3S_HAR_I_74th_b | Aggr 3sec Phase B 74th Current Angle Harmonics | float | 2 | R
0x3BD2 | 0x3BD3 | 15314 | 15315 | ANG_3S_HAR_I_74th_c | Aggr 3sec Phase C 74th Current Angle Harmonics | float | 2 | R
0x3BD4 | 0x3BD5 | 15316 | 15317 | ANG_3S_HAR_I_74th_n | Aggr 3sec Phase N 74th Current Angle Harmonics | float | 2 | R
0x3BD6 | 0x3BD7 | 15318 | 15319 | ANG_3S_HAR_V_75th_a | Aggr 3sec Phase A 75th Voltage Angle Harmonics | float | 2 | R
0x3BD8 | 0x3BD9 | 15320 | 15321 | ANG_3S_HAR_V_75th_b | Aggr 3sec Phase B 75th Voltage Angle Harmonics | float | 2 | R
0x3BDA | 0x3BDB | 15322 | 15323 | ANG_3S_HAR_V_75th_c | Aggr 3sec Phase C 75th Voltage Angle Harmonics | float | 2 | R
0x3BDC | 0x3BDD | 15324 | 15325 | ANG_3S_HAR_I_75th_a | Aggr 3sec Phase A 75th Current Angle Harmonics | float | 2 | R
0x3BDE | 0x3BDF | 15326 | 15327 | ANG_3S_HAR_I_75th_b | Aggr 3sec Phase B 75th Current Angle Harmonics | float | 2 | R
0x3BE0 | 0x3BE1 | 15328 | 15329 | ANG_3S_HAR_I_75th_c | Aggr 3sec Phase C 75th Current Angle Harmonics | float | 2 | R
0x3BE2 | 0x3BE3 | 15330 | 15331 | ANG_3S_HAR_I_75th_n | Aggr 3sec Phase N 75th Current Angle Harmonics | float | 2 | R
0x3BE4 | 0x3BE5 | 15332 | 15333 | ANG_3S_HAR_V_76th_a | Aggr 3sec Phase A 76th Voltage Angle Harmonics | float | 2 | R
0x3BE6 | 0x3BE7 | 15334 | 15335 | ANG_3S_HAR_V_76th_b | Aggr 3sec Phase B 76th Voltage Angle Harmonics | float | 2 | R
0x3BE8 | 0x3BE9 | 15336 | 15337 | ANG_3S_HAR_V_76th_c | Aggr 3sec Phase C 76th Voltage Angle Harmonics | float | 2 | R
0x3BEA | 0x3BEB | 15338 | 15339 | ANG_3S_HAR_I_76th_a | Aggr 3sec Phase A 76th Current Angle Harmonics | float | 2 | R
0x3BEC | 0x3BED | 15340 | 15341 | ANG_3S_HAR_I_76th_b | Aggr 3sec Phase B 76th Current Angle Harmonics | float | 2 | R
0x3BEE | 0x3BEF | 15342 | 15343 | ANG_3S_HAR_I_76th_c | Aggr 3sec Phase C 76th Current Angle Harmonics | float | 2 | R
0x3BF0 | 0x3BF1 | 15344 | 15345 | ANG_3S_HAR_I_76th_n | Aggr 3sec Phase N 76th Current Angle Harmonics | float | 2 | R
0x3BF2 | 0x3BF3 | 15346 | 15347 | ANG_3S_HAR_V_77th_a | Aggr 3sec Phase A 77th Voltage Angle Harmonics | float | 2 | R
0x3BF4 | 0x3BF5 | 15348 | 15349 | ANG_3S_HAR_V_77th_b | Aggr 3sec Phase B 77th Voltage Angle Harmonics | float | 2 | R
0x3BF6 | 0x3BF7 | 15350 | 15351 | ANG_3S_HAR_V_77th_c | Aggr 3sec Phase C 77th Voltage Angle Harmonics | float | 2 | R
0x3BF8 | 0x3BF9 | 15352 | 15353 | ANG_3S_HAR_I_77th_a | Aggr 3sec Phase A 77th Current Angle Harmonics | float | 2 | R
0x3BFA | 0x3BFB | 15354 | 15355 | ANG_3S_HAR_I_77th_b | Aggr 3sec Phase B 77th Current Angle Harmonics | float | 2 | R
0x3BFC | 0x3BFD | 15356 | 15357 | ANG_3S_HAR_I_77th_c | Aggr 3sec Phase C 77th Current Angle Harmonics | float | 2 | R
0x3BFE | 0x3BFF | 15358 | 15359 | ANG_3S_HAR_I_77th_n | Aggr 3sec Phase N 77th Current Angle Harmonics | float | 2 | R
0x3C00 | 0x3C01 | 15360 | 15361 | ANG_3S_HAR_V_78th_a | Aggr 3sec Phase A 78th Voltage Angle Harmonics | float | 2 | R
0x3C02 | 0x3C03 | 15362 | 15363 | ANG_3S_HAR_V_78th_b | Aggr 3sec Phase B 78th Voltage Angle Harmonics | float | 2 | R
0x3C04 | 0x3C05 | 15364 | 15365 | ANG_3S_HAR_V_78th_c | Aggr 3sec Phase C 78th Voltage Angle Harmonics | float | 2 | R
0x3C06 | 0x3C07 | 15366 | 15367 | ANG_3S_HAR_I_78th_a | Aggr 3sec Phase A 78th Current Angle Harmonics | float | 2 | R
0x3C08 | 0x3C09 | 15368 | 15369 | ANG_3S_HAR_I_78th_b | Aggr 3sec Phase B 78th Current Angle Harmonics | float | 2 | R
0x3C0A | 0x3C0B | 15370 | 15371 | ANG_3S_HAR_I_78th_c | Aggr 3sec Phase C 78th Current Angle Harmonics | float | 2 | R
0x3C0C | 0x3C0D | 15372 | 15373 | ANG_3S_HAR_I_78th_n | Aggr 3sec Phase N 78th Current Angle Harmonics | float | 2 | R
0x3C0E | 0x3C0F | 15374 | 15375 | ANG_3S_HAR_V_79th_a | Aggr 3sec Phase A 79th Voltage Angle Harmonics | float | 2 | R
0x3C10 | 0x3C11 | 15376 | 15377 | ANG_3S_HAR_V_79th_b | Aggr 3sec Phase B 79th Voltage Angle Harmonics | float | 2 | R
0x3C12 | 0x3C13 | 15378 | 15379 | ANG_3S_HAR_V_79th_c | Aggr 3sec Phase C 79th Voltage Angle Harmonics | float | 2 | R
0x3C14 | 0x3C15 | 15380 | 15381 | ANG_3S_HAR_I_79th_a | Aggr 3sec Phase A 79th Current Angle Harmonics | float | 2 | R
0x3C16 | 0x3C17 | 15382 | 15383 | ANG_3S_HAR_I_79th_b | Aggr 3sec Phase B 79th Current Angle Harmonics | float | 2 | R
0x3C18 | 0x3C19 | 15384 | 15385 | ANG_3S_HAR_I_79th_c | Aggr 3sec Phase C 79th Current Angle Harmonics | float | 2 | R
0x3C1A | 0x3C1B | 15386 | 15387 | ANG_3S_HAR_I_79th_n | Aggr 3sec Phase N 79th Current Angle Harmonics | float | 2 | R
0x3C1C | 0x3C1D | 15388 | 15389 | ANG_3S_HAR_V_80th_a | Aggr 3sec Phase A 80th Voltage Angle Harmonics | float | 2 | R
0x3C1E | 0x3C1F | 15390 | 15391 | ANG_3S_HAR_V_80th_b | Aggr 3sec Phase B 80th Voltage Angle Harmonics | float | 2 | R
0x3C20 | 0x3C21 | 15392 | 15393 | ANG_3S_HAR_V_80th_c | Aggr 3sec Phase C 80th Voltage Angle Harmonics | float | 2 | R
0x3C22 | 0x3C23 | 15394 | 15395 | ANG_3S_HAR_I_80th_a | Aggr 3sec Phase A 80th Current Angle Harmonics | float | 2 | R
0x3C24 | 0x3C25 | 15396 | 15397 | ANG_3S_HAR_I_80th_b | Aggr 3sec Phase B 80th Current Angle Harmonics | float | 2 | R
0x3C26 | 0x3C27 | 15398 | 15399 | ANG_3S_HAR_I_80th_c | Aggr 3sec Phase C 80th Current Angle Harmonics | float | 2 | R
0x3C28 | 0x3C29 | 15400 | 15401 | ANG_3S_HAR_I_80th_n | Aggr 3sec Phase N 80th Current Angle Harmonics | float | 2 | R
0x3C2A | 0x3C2B | 15402 | 15403 | ANG_3S_HAR_V_81th_a | Aggr 3sec Phase A 81st Voltage Angle Harmonics | float | 2 | R
0x3C2C | 0x3C2D | 15404 | 15405 | ANG_3S_HAR_V_81th_b | Aggr 3sec Phase B 81st Voltage Angle Harmonics | float | 2 | R
0x3C2E | 0x3C2F | 15406 | 15407 | ANG_3S_HAR_V_81th_c | Aggr 3sec Phase C 81st Voltage Angle Harmonics | float | 2 | R
0x3C30 | 0x3C31 | 15408 | 15409 | ANG_3S_HAR_I_81th_a | Aggr 3sec Phase A 81st Current Angle Harmonics | float | 2 | R
0x3C32 | 0x3C33 | 15410 | 15411 | ANG_3S_HAR_I_81th_b | Aggr 3sec Phase B 81st Current Angle Harmonics | float | 2 | R
0x3C34 | 0x3C35 | 15412 | 15413 | ANG_3S_HAR_I_81th_c | Aggr 3sec Phase C 81st Current Angle Harmonics | float | 2 | R
0x3C36 | 0x3C37 | 15414 | 15415 | ANG_3S_HAR_I_81th_n | Aggr 3sec Phase N 81st Current Angle Harmonics | float | 2 | R
0x3C38 | 0x3C39 | 15416 | 15417 | ANG_3S_HAR_V_82th_a | Aggr 3sec Phase A 82nd Voltage Angle Harmonics | float | 2 | R
0x3C3A | 0x3C3B | 15418 | 15419 | ANG_3S_HAR_V_82th_b | Aggr 3sec Phase B 82nd Voltage Angle Harmonics | float | 2 | R
0x3C3C | 0x3C3D | 15420 | 15421 | ANG_3S_HAR_V_82th_c | Aggr 3sec Phase C 82nd Voltage Angle Harmonics | float | 2 | R
0x3C3E | 0x3C3F | 15422 | 15423 | ANG_3S_HAR_I_82th_a | Aggr 3sec Phase A 82nd Current Angle Harmonics | float | 2 | R
0x3C40 | 0x3C41 | 15424 | 15425 | ANG_3S_HAR_I_82th_b | Aggr 3sec Phase B 82nd Current Angle Harmonics | float | 2 | R
0x3C42 | 0x3C43 | 15426 | 15427 | ANG_3S_HAR_I_82th_c | Aggr 3sec Phase C 82nd Current Angle Harmonics | float | 2 | R
0x3C44 | 0x3C45 | 15428 | 15429 | ANG_3S_HAR_I_82th_n | Aggr 3sec Phase N 82nd Current Angle Harmonics | float | 2 | R
0x3C46 | 0x3C47 | 15430 | 15431 | ANG_3S_HAR_V_83th_a | Aggr 3sec Phase A 83rd Voltage Angle Harmonics | float | 2 | R
0x3C48 | 0x3C49 | 15432 | 15433 | ANG_3S_HAR_V_83th_b | Aggr 3sec Phase B 83rd Voltage Angle Harmonics | float | 2 | R
0x3C4A | 0x3C4B | 15434 | 15435 | ANG_3S_HAR_V_83th_c | Aggr 3sec Phase C 83rd Voltage Angle Harmonics | float | 2 | R
0x3C4C | 0x3C4D | 15436 | 15437 | ANG_3S_HAR_I_83th_a | Aggr 3sec Phase A 83rd Current Angle Harmonics | float | 2 | R
0x3C4E | 0x3C4F | 15438 | 15439 | ANG_3S_HAR_I_83th_b | Aggr 3sec Phase B 83rd Current Angle Harmonics | float | 2 | R
0x3C50 | 0x3C51 | 15440 | 15441 | ANG_3S_HAR_I_83th_c | Aggr 3sec Phase C 83rd Current Angle Harmonics | float | 2 | R
0x3C52 | 0x3C53 | 15442 | 15443 | ANG_3S_HAR_I_83th_n | Aggr 3sec Phase N 83rd Current Angle Harmonics | float | 2 | R
0x3C54 | 0x3C55 | 15444 | 15445 | ANG_3S_HAR_V_84th_a | Aggr 3sec Phase A 84th Voltage Angle Harmonics | float | 2 | R
0x3C56 | 0x3C57 | 15446 | 15447 | ANG_3S_HAR_V_84th_b | Aggr 3sec Phase B 84th Voltage Angle Harmonics | float | 2 | R
0x3C58 | 0x3C59 | 15448 | 15449 | ANG_3S_HAR_V_84th_c | Aggr 3sec Phase C 84th Voltage Angle Harmonics | float | 2 | R
0x3C5A | 0x3C5B | 15450 | 15451 | ANG_3S_HAR_I_84th_a | Aggr 3sec Phase A 84th Current Angle Harmonics | float | 2 | R
0x3C5C | 0x3C5D | 15452 | 15453 | ANG_3S_HAR_I_84th_b | Aggr 3sec Phase B 84th Current Angle Harmonics | float | 2 | R
0x3C5E | 0x3C5F | 15454 | 15455 | ANG_3S_HAR_I_84th_c | Aggr 3sec Phase C 84th Current Angle Harmonics | float | 2 | R
0x3C60 | 0x3C61 | 15456 | 15457 | ANG_3S_HAR_I_84th_n | Aggr 3sec Phase N 84th Current Angle Harmonics | float | 2 | R
0x3C62 | 0x3C63 | 15458 | 15459 | ANG_3S_HAR_V_85th_a | Aggr 3sec Phase A 85th Voltage Angle Harmonics | float | 2 | R
0x3C64 | 0x3C65 | 15460 | 15461 | ANG_3S_HAR_V_85th_b | Aggr 3sec Phase B 85th Voltage Angle Harmonics | float | 2 | R
0x3C66 | 0x3C67 | 15462 | 15463 | ANG_3S_HAR_V_85th_c | Aggr 3sec Phase C 85th Voltage Angle Harmonics | float | 2 | R
0x3C68 | 0x3C69 | 15464 | 15465 | ANG_3S_HAR_I_85th_a | Aggr 3sec Phase A 85th Current Angle Harmonics | float | 2 | R
0x3C6A | 0x3C6B | 15466 | 15467 | ANG_3S_HAR_I_85th_b | Aggr 3sec Phase B 85th Current Angle Harmonics | float | 2 | R
0x3C6C | 0x3C6D | 15468 | 15469 | ANG_3S_HAR_I_85th_c | Aggr 3sec Phase C 85th Current Angle Harmonics | float | 2 | R
0x3C6E | 0x3C6F | 15470 | 15471 | ANG_3S_HAR_I_85th_n | Aggr 3sec Phase N 85th Current Angle Harmonics | float | 2 | R
0x3C70 | 0x3C71 | 15472 | 15473 | ANG_3S_HAR_V_86th_a | Aggr 3sec Phase A 86th Voltage Angle Harmonics | float | 2 | R
0x3C72 | 0x3C73 | 15474 | 15475 | ANG_3S_HAR_V_86th_b | Aggr 3sec Phase B 86th Voltage Angle Harmonics | float | 2 | R
0x3C74 | 0x3C75 | 15476 | 15477 | ANG_3S_HAR_V_86th_c | Aggr 3sec Phase C 86th Voltage Angle Harmonics | float | 2 | R
0x3C76 | 0x3C77 | 15478 | 15479 | ANG_3S_HAR_I_86th_a | Aggr 3sec Phase A 86th Current Angle Harmonics | float | 2 | R
0x3C78 | 0x3C79 | 15480 | 15481 | ANG_3S_HAR_I_86th_b | Aggr 3sec Phase B 86th Current Angle Harmonics | float | 2 | R
0x3C7A | 0x3C7B | 15482 | 15483 | ANG_3S_HAR_I_86th_c | Aggr 3sec Phase C 86th Current Angle Harmonics | float | 2 | R
0x3C7C | 0x3C7D | 15484 | 15485 | ANG_3S_HAR_I_86th_n | Aggr 3sec Phase N 86th Current Angle Harmonics | float | 2 | R
0x3C7E | 0x3C7F | 15486 | 15487 | ANG_3S_HAR_V_87th_a | Aggr 3sec Phase A 87th Voltage Angle Harmonics | float | 2 | R
0x3C80 | 0x3C81 | 15488 | 15489 | ANG_3S_HAR_V_87th_b | Aggr 3sec Phase B 87th Voltage Angle Harmonics | float | 2 | R
0x3C82 | 0x3C83 | 15490 | 15491 | ANG_3S_HAR_V_87th_c | Aggr 3sec Phase C 87th Voltage Angle Harmonics | float | 2 | R
0x3C84 | 0x3C85 | 15492 | 15493 | ANG_3S_HAR_I_87th_a | Aggr 3sec Phase A 87th Current Angle Harmonics | float | 2 | R
0x3C86 | 0x3C87 | 15494 | 15495 | ANG_3S_HAR_I_87th_b | Aggr 3sec Phase B 87th Current Angle Harmonics | float | 2 | R
0x3C88 | 0x3C89 | 15496 | 15497 | ANG_3S_HAR_I_87th_c | Aggr 3sec Phase C 87th Current Angle Harmonics | float | 2 | R
0x3C8A | 0x3C8B | 15498 | 15499 | ANG_3S_HAR_I_87th_n | Aggr 3sec Phase N 87th Current Angle Harmonics | float | 2 | R
0x3C8C | 0x3C8D | 15500 | 15501 | ANG_3S_HAR_V_88th_a | Aggr 3sec Phase A 88th Voltage Angle Harmonics | float | 2 | R
0x3C8E | 0x3C8F | 15502 | 15503 | ANG_3S_HAR_V_88th_b | Aggr 3sec Phase B 88th Voltage Angle Harmonics | float | 2 | R
0x3C90 | 0x3C91 | 15504 | 15505 | ANG_3S_HAR_V_88th_c | Aggr 3sec Phase C 88th Voltage Angle Harmonics | float | 2 | R
0x3C92 | 0x3C93 | 15506 | 15507 | ANG_3S_HAR_I_88th_a | Aggr 3sec Phase A 88th Current Angle Harmonics | float | 2 | R
0x3C94 | 0x3C95 | 15508 | 15509 | ANG_3S_HAR_I_88th_b | Aggr 3sec Phase B 88th Current Angle Harmonics | float | 2 | R
0x3C96 | 0x3C97 | 15510 | 15511 | ANG_3S_HAR_I_88th_c | Aggr 3sec Phase C 88th Current Angle Harmonics | float | 2 | R
0x3C98 | 0x3C99 | 15512 | 15513 | ANG_3S_HAR_I_88th_n | Aggr 3sec Phase N 88th Current Angle Harmonics | float | 2 | R
0x3C9A | 0x3C9B | 15514 | 15515 | ANG_3S_HAR_V_89th_a | Aggr 3sec Phase A 89th Voltage Angle Harmonics | float | 2 | R
0x3C9C | 0x3C9D | 15516 | 15517 | ANG_3S_HAR_V_89th_b | Aggr 3sec Phase B 89th Voltage Angle Harmonics | float | 2 | R
0x3C9E | 0x3C9F | 15518 | 15519 | ANG_3S_HAR_V_89th_c | Aggr 3sec Phase C 89th Voltage Angle Harmonics | float | 2 | R
0x3CA0 | 0x3CA1 | 15520 | 15521 | ANG_3S_HAR_I_89th_a | Aggr 3sec Phase A 89th Current Angle Harmonics | float | 2 | R
0x3CA2 | 0x3CA3 | 15522 | 15523 | ANG_3S_HAR_I_89th_b | Aggr 3sec Phase B 89th Current Angle Harmonics | float | 2 | R
0x3CA4 | 0x3CA5 | 15524 | 15525 | ANG_3S_HAR_I_89th_c | Aggr 3sec Phase C 89th Current Angle Harmonics | float | 2 | R
0x3CA6 | 0x3CA7 | 15526 | 15527 | ANG_3S_HAR_I_89th_n | Aggr 3sec Phase N 89th Current Angle Harmonics | float | 2 | R
0x3CA8 | 0x3CA9 | 15528 | 15529 | ANG_3S_HAR_V_90th_a | Aggr 3sec Phase A 90th Voltage Angle Harmonics | float | 2 | R
0x3CAA | 0x3CAB | 15530 | 15531 | ANG_3S_HAR_V_90th_b | Aggr 3sec Phase B 90th Voltage Angle Harmonics | float | 2 | R
0x3CAC | 0x3CAD | 15532 | 15533 | ANG_3S_HAR_V_90th_c | Aggr 3sec Phase C 90th Voltage Angle Harmonics | float | 2 | R
0x3CAE | 0x3CAF | 15534 | 15535 | ANG_3S_HAR_I_90th_a | Aggr 3sec Phase A 90th Current Angle Harmonics | float | 2 | R
0x3CB0 | 0x3CB1 | 15536 | 15537 | ANG_3S_HAR_I_90th_b | Aggr 3sec Phase B 90th Current Angle Harmonics | float | 2 | R
0x3CB2 | 0x3CB3 | 15538 | 15539 | ANG_3S_HAR_I_90th_c | Aggr 3sec Phase C 90th Current Angle Harmonics | float | 2 | R
0x3CB4 | 0x3CB5 | 15540 | 15541 | ANG_3S_HAR_I_90th_n | Aggr 3sec Phase N 90th Current Angle Harmonics | float | 2 | R
0x3CB6 | 0x3CB7 | 15542 | 15543 | ANG_3S_HAR_V_91th_a | Aggr 3sec Phase A 91st Voltage Angle Harmonics | float | 2 | R
0x3CB8 | 0x3CB9 | 15544 | 15545 | ANG_3S_HAR_V_91th_b | Aggr 3sec Phase B 91st Voltage Angle Harmonics | float | 2 | R
0x3CBA | 0x3CBB | 15546 | 15547 | ANG_3S_HAR_V_91th_c | Aggr 3sec Phase C 91st Voltage Angle Harmonics | float | 2 | R
0x3CBC | 0x3CBD | 15548 | 15549 | ANG_3S_HAR_I_91th_a | Aggr 3sec Phase A 91st Current Angle Harmonics | float | 2 | R
0x3CBE | 0x3CBF | 15550 | 15551 | ANG_3S_HAR_I_91th_b | Aggr 3sec Phase B 91st Current Angle Harmonics | float | 2 | R
0x3CC0 | 0x3CC1 | 15552 | 15553 | ANG_3S_HAR_I_91th_c | Aggr 3sec Phase C 91st Current Angle Harmonics | float | 2 | R
0x3CC2 | 0x3CC3 | 15554 | 15555 | ANG_3S_HAR_I_91th_n | Aggr 3sec Phase N 91st Current Angle Harmonics | float | 2 | R
0x3CC4 | 0x3CC5 | 15556 | 15557 | ANG_3S_HAR_V_92th_a | Aggr 3sec Phase A 92nd Voltage Angle Harmonics | float | 2 | R
0x3CC6 | 0x3CC7 | 15558 | 15559 | ANG_3S_HAR_V_92th_b | Aggr 3sec Phase B 92nd Voltage Angle Harmonics | float | 2 | R
0x3CC8 | 0x3CC9 | 15560 | 15561 | ANG_3S_HAR_V_92th_c | Aggr 3sec Phase C 92nd Voltage Angle Harmonics | float | 2 | R
0x3CCA | 0x3CCB | 15562 | 15563 | ANG_3S_HAR_I_92th_a | Aggr 3sec Phase A 92nd Current Angle Harmonics | float | 2 | R
0x3CCC | 0x3CCD | 15564 | 15565 | ANG_3S_HAR_I_92th_b | Aggr 3sec Phase B 92nd Current Angle Harmonics | float | 2 | R
0x3CCE | 0x3CCF | 15566 | 15567 | ANG_3S_HAR_I_92th_c | Aggr 3sec Phase C 92nd Current Angle Harmonics | float | 2 | R
0x3CD0 | 0x3CD1 | 15568 | 15569 | ANG_3S_HAR_I_92th_n | Aggr 3sec Phase N 92nd Current Angle Harmonics | float | 2 | R
0x3CD2 | 0x3CD3 | 15570 | 15571 | ANG_3S_HAR_V_93th_a | Aggr 3sec Phase A 93rd Voltage Angle Harmonics | float | 2 | R
0x3CD4 | 0x3CD5 | 15572 | 15573 | ANG_3S_HAR_V_93th_b | Aggr 3sec Phase B 93rd Voltage Angle Harmonics | float | 2 | R
0x3CD6 | 0x3CD7 | 15574 | 15575 | ANG_3S_HAR_V_93th_c | Aggr 3sec Phase C 93rd Voltage Angle Harmonics | float | 2 | R
0x3CD8 | 0x3CD9 | 15576 | 15577 | ANG_3S_HAR_I_93th_a | Aggr 3sec Phase A 93rd Current Angle Harmonics | float | 2 | R
0x3CDA | 0x3CDB | 15578 | 15579 | ANG_3S_HAR_I_93th_b | Aggr 3sec Phase B 93rd Current Angle Harmonics | float | 2 | R
0x3CDC | 0x3CDD | 15580 | 15581 | ANG_3S_HAR_I_93th_c | Aggr 3sec Phase C 93rd Current Angle Harmonics | float | 2 | R
0x3CDE | 0x3CDF | 15582 | 15583 | ANG_3S_HAR_I_93th_n | Aggr 3sec Phase N 93rd Current Angle Harmonics | float | 2 | R
0x3CE0 | 0x3CE1 | 15584 | 15585 | ANG_3S_HAR_V_94th_a | Aggr 3sec Phase A 94th Voltage Angle Harmonics | float | 2 | R
0x3CE2 | 0x3CE3 | 15586 | 15587 | ANG_3S_HAR_V_94th_b | Aggr 3sec Phase B 94th Voltage Angle Harmonics | float | 2 | R
0x3CE4 | 0x3CE5 | 15588 | 15589 | ANG_3S_HAR_V_94th_c | Aggr 3sec Phase C 94th Voltage Angle Harmonics | float | 2 | R
0x3CE6 | 0x3CE7 | 15590 | 15591 | ANG_3S_HAR_I_94th_a | Aggr 3sec Phase A 94th Current Angle Harmonics | float | 2 | R
0x3CE8 | 0x3CE9 | 15592 | 15593 | ANG_3S_HAR_I_94th_b | Aggr 3sec Phase B 94th Current Angle Harmonics | float | 2 | R
0x3CEA | 0x3CEB | 15594 | 15595 | ANG_3S_HAR_I_94th_c | Aggr 3sec Phase C 94th Current Angle Harmonics | float | 2 | R
0x3CEC | 0x3CED | 15596 | 15597 | ANG_3S_HAR_I_94th_n | Aggr 3sec Phase N 94th Current Angle Harmonics | float | 2 | R
0x3CEE | 0x3CEF | 15598 | 15599 | ANG_3S_HAR_V_95th_a | Aggr 3sec Phase A 95th Voltage Angle Harmonics | float | 2 | R
0x3CF0 | 0x3CF1 | 15600 | 15601 | ANG_3S_HAR_V_95th_b | Aggr 3sec Phase B 95th Voltage Angle Harmonics | float | 2 | R
0x3CF2 | 0x3CF3 | 15602 | 15603 | ANG_3S_HAR_V_95th_c | Aggr 3sec Phase C 95th Voltage Angle Harmonics | float | 2 | R
0x3CF4 | 0x3CF5 | 15604 | 15605 | ANG_3S_HAR_I_95th_a | Aggr 3sec Phase A 95th Current Angle Harmonics | float | 2 | R
0x3CF6 | 0x3CF7 | 15606 | 15607 | ANG_3S_HAR_I_95th_b | Aggr 3sec Phase B 95th Current Angle Harmonics | float | 2 | R
0x3CF8 | 0x3CF9 | 15608 | 15609 | ANG_3S_HAR_I_95th_c | Aggr 3sec Phase C 95th Current Angle Harmonics | float | 2 | R
0x3CFA | 0x3CFB | 15610 | 15611 | ANG_3S_HAR_I_95th_n | Aggr 3sec Phase N 95th Current Angle Harmonics | float | 2 | R
0x3CFC | 0x3CFD | 15612 | 15613 | ANG_3S_HAR_V_96th_a | Aggr 3sec Phase A 96th Voltage Angle Harmonics | float | 2 | R
0x3CFE | 0x3CFF | 15614 | 15615 | ANG_3S_HAR_V_96th_b | Aggr 3sec Phase B 96th Voltage Angle Harmonics | float | 2 | R
0x3D00 | 0x3D01 | 15616 | 15617 | ANG_3S_HAR_V_96th_c | Aggr 3sec Phase C 96th Voltage Angle Harmonics | float | 2 | R
0x3D02 | 0x3D03 | 15618 | 15619 | ANG_3S_HAR_I_96th_a | Aggr 3sec Phase A 96th Current Angle Harmonics | float | 2 | R
0x3D04 | 0x3D05 | 15620 | 15621 | ANG_3S_HAR_I_96th_b | Aggr 3sec Phase B 96th Current Angle Harmonics | float | 2 | R
0x3D06 | 0x3D07 | 15622 | 15623 | ANG_3S_HAR_I_96th_c | Aggr 3sec Phase C 96th Current Angle Harmonics | float | 2 | R
0x3D08 | 0x3D09 | 15624 | 15625 | ANG_3S_HAR_I_96th_n | Aggr 3sec Phase N 96th Current Angle Harmonics | float | 2 | R
0x3D0A | 0x3D0B | 15626 | 15627 | ANG_3S_HAR_V_97th_a | Aggr 3sec Phase A 97th Voltage Angle Harmonics | float | 2 | R
0x3D0C | 0x3D0D | 15628 | 15629 | ANG_3S_HAR_V_97th_b | Aggr 3sec Phase B 97th Voltage Angle Harmonics | float | 2 | R
0x3D0E | 0x3D0F | 15630 | 15631 | ANG_3S_HAR_V_97th_c | Aggr 3sec Phase C 97th Voltage Angle Harmonics | float | 2 | R
0x3D10 | 0x3D11 | 15632 | 15633 | ANG_3S_HAR_I_97th_a | Aggr 3sec Phase A 97th Current Angle Harmonics | float | 2 | R
0x3D12 | 0x3D13 | 15634 | 15635 | ANG_3S_HAR_I_97th_b | Aggr 3sec Phase B 97th Current Angle Harmonics | float | 2 | R
0x3D14 | 0x3D15 | 15636 | 15637 | ANG_3S_HAR_I_97th_c | Aggr 3sec Phase C 97th Current Angle Harmonics | float | 2 | R
0x3D16 | 0x3D17 | 15638 | 15639 | ANG_3S_HAR_I_97th_n | Aggr 3sec Phase N 97th Current Angle Harmonics | float | 2 | R
0x3D18 | 0x3D19 | 15640 | 15641 | ANG_3S_HAR_V_98th_a | Aggr 3sec Phase A 98th Voltage Angle Harmonics | float | 2 | R
0x3D1A | 0x3D1B | 15642 | 15643 | ANG_3S_HAR_V_98th_b | Aggr 3sec Phase B 98th Voltage Angle Harmonics | float | 2 | R
0x3D1C | 0x3D1D | 15644 | 15645 | ANG_3S_HAR_V_98th_c | Aggr 3sec Phase C 98th Voltage Angle Harmonics | float | 2 | R
0x3D1E | 0x3D1F | 15646 | 15647 | ANG_3S_HAR_I_98th_a | Aggr 3sec Phase A 98th Current Angle Harmonics | float | 2 | R
0x3D20 | 0x3D21 | 15648 | 15649 | ANG_3S_HAR_I_98th_b | Aggr 3sec Phase B 98th Current Angle Harmonics | float | 2 | R
0x3D22 | 0x3D23 | 15650 | 15651 | ANG_3S_HAR_I_98th_c | Aggr 3sec Phase C 98th Current Angle Harmonics | float | 2 | R
0x3D24 | 0x3D25 | 15652 | 15653 | ANG_3S_HAR_I_98th_n | Aggr 3sec Phase N 98th Current Angle Harmonics | float | 2 | R
0x3D26 | 0x3D27 | 15654 | 15655 | ANG_3S_HAR_V_99th_a | Aggr 3sec Phase A 99th Voltage Angle Harmonics | float | 2 | R
0x3D28 | 0x3D29 | 15656 | 15657 | ANG_3S_HAR_V_99th_b | Aggr 3sec Phase B 99th Voltage Angle Harmonics | float | 2 | R
0x3D2A | 0x3D2B | 15658 | 15659 | ANG_3S_HAR_V_99th_c | Aggr 3sec Phase C 99th Voltage Angle Harmonics | float | 2 | R
0x3D2C | 0x3D2D | 15660 | 15661 | ANG_3S_HAR_I_99th_a | Aggr 3sec Phase A 99th Current Angle Harmonics | float | 2 | R
0x3D2E | 0x3D2F | 15662 | 15663 | ANG_3S_HAR_I_99th_b | Aggr 3sec Phase B 99th Current Angle Harmonics | float | 2 | R
0x3D30 | 0x3D31 | 15664 | 15665 | ANG_3S_HAR_I_99th_c | Aggr 3sec Phase C 99th Current Angle Harmonics | float | 2 | R
0x3D32 | 0x3D33 | 15666 | 15667 | ANG_3S_HAR_I_99th_n | Aggr 3sec Phase N 99th Current Angle Harmonics | float | 2 | R
0x3D34 | 0x3D35 | 15668 | 15669 | ANG_3S_HAR_V_100th_a | Aggr 3sec Phase A 100th Voltage Angle Harmonics | float | 2 | R
0x3D36 | 0x3D37 | 15670 | 15671 | ANG_3S_HAR_V_100th_b | Aggr 3sec Phase B 100th Voltage Angle Harmonics | float | 2 | R
0x3D38 | 0x3D39 | 15672 | 15673 | ANG_3S_HAR_V_100th_c | Aggr 3sec Phase C 100th Voltage Angle Harmonics | float | 2 | R
0x3D3A | 0x3D3B | 15674 | 15675 | ANG_3S_HAR_I_100th_a | Aggr 3sec Phase A 100th Current Angle Harmonics | float | 2 | R
0x3D3C | 0x3D3D | 15676 | 15677 | ANG_3S_HAR_I_100th_b | Aggr 3sec Phase B 100th Current Angle Harmonics | float | 2 | R
0x3D3E | 0x3D3F | 15678 | 15679 | ANG_3S_HAR_I_100th_c | Aggr 3sec Phase C 100th Current Angle Harmonics | float | 2 | R
0x3D40 | 0x3D41 | 15680 | 15681 | ANG_3S_HAR_I_100th_n | Aggr 3sec Phase N 100th Current Angle Harmonics | float | 2 | R
0x3D42 | 0x3D43 | 15682 | 15683 | ANG_3S_HAR_V_101th_a | Aggr 3sec Phase A 101st Voltage Angle Harmonics | float | 2 | R
0x3D44 | 0x3D45 | 15684 | 15685 | ANG_3S_HAR_V_101th_b | Aggr 3sec Phase B 101st Voltage Angle Harmonics | float | 2 | R
0x3D46 | 0x3D47 | 15686 | 15687 | ANG_3S_HAR_V_101th_c | Aggr 3sec Phase C 101st Voltage Angle Harmonics | float | 2 | R
0x3D48 | 0x3D49 | 15688 | 15689 | ANG_3S_HAR_I_101th_a | Aggr 3sec Phase A 101st Current Angle Harmonics | float | 2 | R
0x3D4A | 0x3D4B | 15690 | 15691 | ANG_3S_HAR_I_101th_b | Aggr 3sec Phase B 101st Current Angle Harmonics | float | 2 | R
0x3D4C | 0x3D4D | 15692 | 15693 | ANG_3S_HAR_I_101th_c | Aggr 3sec Phase C 101st Current Angle Harmonics | float | 2 | R
0x3D4E | 0x3D4F | 15694 | 15695 | ANG_3S_HAR_I_101th_n | Aggr 3sec Phase N 101st Current Angle Harmonics | float | 2 | R
0x3D50 | 0x3D51 | 15696 | 15697 | ANG_3S_HAR_V_102th_a | Aggr 3sec Phase A 102nd Voltage Angle Harmonics | float | 2 | R
0x3D52 | 0x3D53 | 15698 | 15699 | ANG_3S_HAR_V_102th_b | Aggr 3sec Phase B 102nd Voltage Angle Harmonics | float | 2 | R
0x3D54 | 0x3D55 | 15700 | 15701 | ANG_3S_HAR_V_102th_c | Aggr 3sec Phase C 102nd Voltage Angle Harmonics | float | 2 | R
0x3D56 | 0x3D57 | 15702 | 15703 | ANG_3S_HAR_I_102th_a | Aggr 3sec Phase A 102nd Current Angle Harmonics | float | 2 | R
0x3D58 | 0x3D59 | 15704 | 15705 | ANG_3S_HAR_I_102th_b | Aggr 3sec Phase B 102nd Current Angle Harmonics | float | 2 | R
0x3D5A | 0x3D5B | 15706 | 15707 | ANG_3S_HAR_I_102th_c | Aggr 3sec Phase C 102nd Current Angle Harmonics | float | 2 | R
0x3D5C | 0x3D5D | 15708 | 15709 | ANG_3S_HAR_I_102th_n | Aggr 3sec Phase N 102nd Current Angle Harmonics | float | 2 | R
0x3D5E | 0x3D5F | 15710 | 15711 | ANG_3S_HAR_V_103th_a | Aggr 3sec Phase A 103rd Voltage Angle Harmonics | float | 2 | R
0x3D60 | 0x3D61 | 15712 | 15713 | ANG_3S_HAR_V_103th_b | Aggr 3sec Phase B 103rd Voltage Angle Harmonics | float | 2 | R
0x3D62 | 0x3D63 | 15714 | 15715 | ANG_3S_HAR_V_103th_c | Aggr 3sec Phase C 103rd Voltage Angle Harmonics | float | 2 | R
0x3D64 | 0x3D65 | 15716 | 15717 | ANG_3S_HAR_I_103th_a | Aggr 3sec Phase A 103rd Current Angle Harmonics | float | 2 | R
0x3D66 | 0x3D67 | 15718 | 15719 | ANG_3S_HAR_I_103th_b | Aggr 3sec Phase B 103rd Current Angle Harmonics | float | 2 | R
0x3D68 | 0x3D69 | 15720 | 15721 | ANG_3S_HAR_I_103th_c | Aggr 3sec Phase C 103rd Current Angle Harmonics | float | 2 | R
0x3D6A | 0x3D6B | 15722 | 15723 | ANG_3S_HAR_I_103th_n | Aggr 3sec Phase N 103rd Current Angle Harmonics | float | 2 | R
0x3D6C | 0x3D6D | 15724 | 15725 | ANG_3S_HAR_V_104th_a | Aggr 3sec Phase A 104th Voltage Angle Harmonics | float | 2 | R
0x3D6E | 0x3D6F | 15726 | 15727 | ANG_3S_HAR_V_104th_b | Aggr 3sec Phase B 104th Voltage Angle Harmonics | float | 2 | R
0x3D70 | 0x3D71 | 15728 | 15729 | ANG_3S_HAR_V_104th_c | Aggr 3sec Phase C 104th Voltage Angle Harmonics | float | 2 | R
0x3D72 | 0x3D73 | 15730 | 15731 | ANG_3S_HAR_I_104th_a | Aggr 3sec Phase A 104th Current Angle Harmonics | float | 2 | R
0x3D74 | 0x3D75 | 15732 | 15733 | ANG_3S_HAR_I_104th_b | Aggr 3sec Phase B 104th Current Angle Harmonics | float | 2 | R
0x3D76 | 0x3D77 | 15734 | 15735 | ANG_3S_HAR_I_104th_c | Aggr 3sec Phase C 104th Current Angle Harmonics | float | 2 | R
0x3D78 | 0x3D79 | 15736 | 15737 | ANG_3S_HAR_I_104th_n | Aggr 3sec Phase N 104th Current Angle Harmonics | float | 2 | R
0x3D7A | 0x3D7B | 15738 | 15739 | ANG_3S_HAR_V_105th_a | Aggr 3sec Phase A 105th Voltage Angle Harmonics | float | 2 | R
0x3D7C | 0x3D7D | 15740 | 15741 | ANG_3S_HAR_V_105th_b | Aggr 3sec Phase B 105th Voltage Angle Harmonics | float | 2 | R
0x3D7E | 0x3D7F | 15742 | 15743 | ANG_3S_HAR_V_105th_c | Aggr 3sec Phase C 105th Voltage Angle Harmonics | float | 2 | R
0x3D80 | 0x3D81 | 15744 | 15745 | ANG_3S_HAR_I_105th_a | Aggr 3sec Phase A 105th Current Angle Harmonics | float | 2 | R
0x3D82 | 0x3D83 | 15746 | 15747 | ANG_3S_HAR_I_105th_b | Aggr 3sec Phase B 105th Current Angle Harmonics | float | 2 | R
0x3D84 | 0x3D85 | 15748 | 15749 | ANG_3S_HAR_I_105th_c | Aggr 3sec Phase C 105th Current Angle Harmonics | float | 2 | R
0x3D86 | 0x3D87 | 15750 | 15751 | ANG_3S_HAR_I_105th_n | Aggr 3sec Phase N 105th Current Angle Harmonics | float | 2 | R
0x3D88 | 0x3D89 | 15752 | 15753 | ANG_3S_HAR_V_106th_a | Aggr 3sec Phase A 106th Voltage Angle Harmonics | float | 2 | R
0x3D8A | 0x3D8B | 15754 | 15755 | ANG_3S_HAR_V_106th_b | Aggr 3sec Phase B 106th Voltage Angle Harmonics | float | 2 | R
0x3D8C | 0x3D8D | 15756 | 15757 | ANG_3S_HAR_V_106th_c | Aggr 3sec Phase C 106th Voltage Angle Harmonics | float | 2 | R
0x3D8E | 0x3D8F | 15758 | 15759 | ANG_3S_HAR_I_106th_a | Aggr 3sec Phase A 106th Current Angle Harmonics | float | 2 | R
0x3D90 | 0x3D91 | 15760 | 15761 | ANG_3S_HAR_I_106th_b | Aggr 3sec Phase B 106th Current Angle Harmonics | float | 2 | R
0x3D92 | 0x3D93 | 15762 | 15763 | ANG_3S_HAR_I_106th_c | Aggr 3sec Phase C 106th Current Angle Harmonics | float | 2 | R
0x3D94 | 0x3D95 | 15764 | 15765 | ANG_3S_HAR_I_106th_n | Aggr 3sec Phase N 106th Current Angle Harmonics | float | 2 | R
0x3D96 | 0x3D97 | 15766 | 15767 | ANG_3S_HAR_V_107th_a | Aggr 3sec Phase A 107th Voltage Angle Harmonics | float | 2 | R
0x3D98 | 0x3D99 | 15768 | 15769 | ANG_3S_HAR_V_107th_b | Aggr 3sec Phase B 107th Voltage Angle Harmonics | float | 2 | R
0x3D9A | 0x3D9B | 15770 | 15771 | ANG_3S_HAR_V_107th_c | Aggr 3sec Phase C 107th Voltage Angle Harmonics | float | 2 | R
0x3D9C | 0x3D9D | 15772 | 15773 | ANG_3S_HAR_I_107th_a | Aggr 3sec Phase A 107th Current Angle Harmonics | float | 2 | R
0x3D9E | 0x3D9F | 15774 | 15775 | ANG_3S_HAR_I_107th_b | Aggr 3sec Phase B 107th Current Angle Harmonics | float | 2 | R
0x3DA0 | 0x3DA1 | 15776 | 15777 | ANG_3S_HAR_I_107th_c | Aggr 3sec Phase C 107th Current Angle Harmonics | float | 2 | R
0x3DA2 | 0x3DA3 | 15778 | 15779 | ANG_3S_HAR_I_107th_n | Aggr 3sec Phase N 107th Current Angle Harmonics | float | 2 | R
0x3DA4 | 0x3DA5 | 15780 | 15781 | ANG_3S_HAR_V_108th_a | Aggr 3sec Phase A 108th Voltage Angle Harmonics | float | 2 | R
0x3DA6 | 0x3DA7 | 15782 | 15783 | ANG_3S_HAR_V_108th_b | Aggr 3sec Phase B 108th Voltage Angle Harmonics | float | 2 | R
0x3DA8 | 0x3DA9 | 15784 | 15785 | ANG_3S_HAR_V_108th_c | Aggr 3sec Phase C 108th Voltage Angle Harmonics | float | 2 | R
0x3DAA | 0x3DAB | 15786 | 15787 | ANG_3S_HAR_I_108th_a | Aggr 3sec Phase A 108th Current Angle Harmonics | float | 2 | R
0x3DAC | 0x3DAD | 15788 | 15789 | ANG_3S_HAR_I_108th_b | Aggr 3sec Phase B 108th Current Angle Harmonics | float | 2 | R
0x3DAE | 0x3DAF | 15790 | 15791 | ANG_3S_HAR_I_108th_c | Aggr 3sec Phase C 108th Current Angle Harmonics | float | 2 | R
0x3DB0 | 0x3DB1 | 15792 | 15793 | ANG_3S_HAR_I_108th_n | Aggr 3sec Phase N 108th Current Angle Harmonics | float | 2 | R
0x3DB2 | 0x3DB3 | 15794 | 15795 | ANG_3S_HAR_V_109th_a | Aggr 3sec Phase A 109th Voltage Angle Harmonics | float | 2 | R
0x3DB4 | 0x3DB5 | 15796 | 15797 | ANG_3S_HAR_V_109th_b | Aggr 3sec Phase B 109th Voltage Angle Harmonics | float | 2 | R
0x3DB6 | 0x3DB7 | 15798 | 15799 | ANG_3S_HAR_V_109th_c | Aggr 3sec Phase C 109th Voltage Angle Harmonics | float | 2 | R
0x3DB8 | 0x3DB9 | 15800 | 15801 | ANG_3S_HAR_I_109th_a | Aggr 3sec Phase A 109th Current Angle Harmonics | float | 2 | R
0x3DBA | 0x3DBB | 15802 | 15803 | ANG_3S_HAR_I_109th_b | Aggr 3sec Phase B 109th Current Angle Harmonics | float | 2 | R
0x3DBC | 0x3DBD | 15804 | 15805 | ANG_3S_HAR_I_109th_c | Aggr 3sec Phase C 109th Current Angle Harmonics | float | 2 | R
0x3DBE | 0x3DBF | 15806 | 15807 | ANG_3S_HAR_I_109th_n | Aggr 3sec Phase N 109th Current Angle Harmonics | float | 2 | R
0x3DC0 | 0x3DC1 | 15808 | 15809 | ANG_3S_HAR_V_110th_a | Aggr 3sec Phase A 110th Voltage Angle Harmonics | float | 2 | R
0x3DC2 | 0x3DC3 | 15810 | 15811 | ANG_3S_HAR_V_110th_b | Aggr 3sec Phase B 110th Voltage Angle Harmonics | float | 2 | R
0x3DC4 | 0x3DC5 | 15812 | 15813 | ANG_3S_HAR_V_110th_c | Aggr 3sec Phase C 110th Voltage Angle Harmonics | float | 2 | R
0x3DC6 | 0x3DC7 | 15814 | 15815 | ANG_3S_HAR_I_110th_a | Aggr 3sec Phase A 110th Current Angle Harmonics | float | 2 | R
0x3DC8 | 0x3DC9 | 15816 | 15817 | ANG_3S_HAR_I_110th_b | Aggr 3sec Phase B 110th Current Angle Harmonics | float | 2 | R
0x3DCA | 0x3DCB | 15818 | 15819 | ANG_3S_HAR_I_110th_c | Aggr 3sec Phase C 110th Current Angle Harmonics | float | 2 | R
0x3DCC | 0x3DCD | 15820 | 15821 | ANG_3S_HAR_I_110th_n | Aggr 3sec Phase N 110th Current Angle Harmonics | float | 2 | R
0x3DCE | 0x3DCF | 15822 | 15823 | ANG_3S_HAR_V_111th_a | Aggr 3sec Phase A 111st Voltage Angle Harmonics | float | 2 | R
0x3DD0 | 0x3DD1 | 15824 | 15825 | ANG_3S_HAR_V_111th_b | Aggr 3sec Phase B 111st Voltage Angle Harmonics | float | 2 | R
0x3DD2 | 0x3DD3 | 15826 | 15827 | ANG_3S_HAR_V_111th_c | Aggr 3sec Phase C 111st Voltage Angle Harmonics | float | 2 | R
0x3DD4 | 0x3DD5 | 15828 | 15829 | ANG_3S_HAR_I_111th_a | Aggr 3sec Phase A 111st Current Angle Harmonics | float | 2 | R
0x3DD6 | 0x3DD7 | 15830 | 15831 | ANG_3S_HAR_I_111th_b | Aggr 3sec Phase B 111st Current Angle Harmonics | float | 2 | R
0x3DD8 | 0x3DD9 | 15832 | 15833 | ANG_3S_HAR_I_111th_c | Aggr 3sec Phase C 111st Current Angle Harmonics | float | 2 | R
0x3DDA | 0x3DDB | 15834 | 15835 | ANG_3S_HAR_I_111th_n | Aggr 3sec Phase N 111st Current Angle Harmonics | float | 2 | R
0x3DDC | 0x3DDD | 15836 | 15837 | ANG_3S_HAR_V_112th_a | Aggr 3sec Phase A 112nd Voltage Angle Harmonics | float | 2 | R
0x3DDE | 0x3DDF | 15838 | 15839 | ANG_3S_HAR_V_112th_b | Aggr 3sec Phase B 112nd Voltage Angle Harmonics | float | 2 | R
0x3DE0 | 0x3DE1 | 15840 | 15841 | ANG_3S_HAR_V_112th_c | Aggr 3sec Phase C 112nd Voltage Angle Harmonics | float | 2 | R
0x3DE2 | 0x3DE3 | 15842 | 15843 | ANG_3S_HAR_I_112th_a | Aggr 3sec Phase A 112nd Current Angle Harmonics | float | 2 | R
0x3DE4 | 0x3DE5 | 15844 | 15845 | ANG_3S_HAR_I_112th_b | Aggr 3sec Phase B 112nd Current Angle Harmonics | float | 2 | R
0x3DE6 | 0x3DE7 | 15846 | 15847 | ANG_3S_HAR_I_112th_c | Aggr 3sec Phase C 112nd Current Angle Harmonics | float | 2 | R
0x3DE8 | 0x3DE9 | 15848 | 15849 | ANG_3S_HAR_I_112th_n | Aggr 3sec Phase N 112nd Current Angle Harmonics | float | 2 | R
0x3DEA | 0x3DEB | 15850 | 15851 | ANG_3S_HAR_V_113th_a | Aggr 3sec Phase A 113rd Voltage Angle Harmonics | float | 2 | R
0x3DEC | 0x3DED | 15852 | 15853 | ANG_3S_HAR_V_113th_b | Aggr 3sec Phase B 113rd Voltage Angle Harmonics | float | 2 | R
0x3DEE | 0x3DEF | 15854 | 15855 | ANG_3S_HAR_V_113th_c | Aggr 3sec Phase C 113rd Voltage Angle Harmonics | float | 2 | R
0x3DF0 | 0x3DF1 | 15856 | 15857 | ANG_3S_HAR_I_113th_a | Aggr 3sec Phase A 113rd Current Angle Harmonics | float | 2 | R
0x3DF2 | 0x3DF3 | 15858 | 15859 | ANG_3S_HAR_I_113th_b | Aggr 3sec Phase B 113rd Current Angle Harmonics | float | 2 | R
0x3DF4 | 0x3DF5 | 15860 | 15861 | ANG_3S_HAR_I_113th_c | Aggr 3sec Phase C 113rd Current Angle Harmonics | float | 2 | R
0x3DF6 | 0x3DF7 | 15862 | 15863 | ANG_3S_HAR_I_113th_n | Aggr 3sec Phase N 113rd Current Angle Harmonics | float | 2 | R
0x3DF8 | 0x3DF9 | 15864 | 15865 | ANG_3S_HAR_V_114th_a | Aggr 3sec Phase A 114th Voltage Angle Harmonics | float | 2 | R
0x3DFA | 0x3DFB | 15866 | 15867 | ANG_3S_HAR_V_114th_b | Aggr 3sec Phase B 114th Voltage Angle Harmonics | float | 2 | R
0x3DFC | 0x3DFD | 15868 | 15869 | ANG_3S_HAR_V_114th_c | Aggr 3sec Phase C 114th Voltage Angle Harmonics | float | 2 | R
0x3DFE | 0x3DFF | 15870 | 15871 | ANG_3S_HAR_I_114th_a | Aggr 3sec Phase A 114th Current Angle Harmonics | float | 2 | R
0x3E00 | 0x3E01 | 15872 | 15873 | ANG_3S_HAR_I_114th_b | Aggr 3sec Phase B 114th Current Angle Harmonics | float | 2 | R
0x3E02 | 0x3E03 | 15874 | 15875 | ANG_3S_HAR_I_114th_c | Aggr 3sec Phase C 114th Current Angle Harmonics | float | 2 | R
0x3E04 | 0x3E05 | 15876 | 15877 | ANG_3S_HAR_I_114th_n | Aggr 3sec Phase N 114th Current Angle Harmonics | float | 2 | R
0x3E06 | 0x3E07 | 15878 | 15879 | ANG_3S_HAR_V_115th_a | Aggr 3sec Phase A 115th Voltage Angle Harmonics | float | 2 | R
0x3E08 | 0x3E09 | 15880 | 15881 | ANG_3S_HAR_V_115th_b | Aggr 3sec Phase B 115th Voltage Angle Harmonics | float | 2 | R
0x3E0A | 0x3E0B | 15882 | 15883 | ANG_3S_HAR_V_115th_c | Aggr 3sec Phase C 115th Voltage Angle Harmonics | float | 2 | R
0x3E0C | 0x3E0D | 15884 | 15885 | ANG_3S_HAR_I_115th_a | Aggr 3sec Phase A 115th Current Angle Harmonics | float | 2 | R
0x3E0E | 0x3E0F | 15886 | 15887 | ANG_3S_HAR_I_115th_b | Aggr 3sec Phase B 115th Current Angle Harmonics | float | 2 | R
0x3E10 | 0x3E11 | 15888 | 15889 | ANG_3S_HAR_I_115th_c | Aggr 3sec Phase C 115th Current Angle Harmonics | float | 2 | R
0x3E12 | 0x3E13 | 15890 | 15891 | ANG_3S_HAR_I_115th_n | Aggr 3sec Phase N 115th Current Angle Harmonics | float | 2 | R
0x3E14 | 0x3E15 | 15892 | 15893 | ANG_3S_HAR_V_116th_a | Aggr 3sec Phase A 116th Voltage Angle Harmonics | float | 2 | R
0x3E16 | 0x3E17 | 15894 | 15895 | ANG_3S_HAR_V_116th_b | Aggr 3sec Phase B 116th Voltage Angle Harmonics | float | 2 | R
0x3E18 | 0x3E19 | 15896 | 15897 | ANG_3S_HAR_V_116th_c | Aggr 3sec Phase C 116th Voltage Angle Harmonics | float | 2 | R
0x3E1A | 0x3E1B | 15898 | 15899 | ANG_3S_HAR_I_116th_a | Aggr 3sec Phase A 116th Current Angle Harmonics | float | 2 | R
0x3E1C | 0x3E1D | 15900 | 15901 | ANG_3S_HAR_I_116th_b | Aggr 3sec Phase B 116th Current Angle Harmonics | float | 2 | R
0x3E1E | 0x3E1F | 15902 | 15903 | ANG_3S_HAR_I_116th_c | Aggr 3sec Phase C 116th Current Angle Harmonics | float | 2 | R
0x3E20 | 0x3E21 | 15904 | 15905 | ANG_3S_HAR_I_116th_n | Aggr 3sec Phase N 116th Current Angle Harmonics | float | 2 | R
0x3E22 | 0x3E23 | 15906 | 15907 | ANG_3S_HAR_V_117th_a | Aggr 3sec Phase A 117th Voltage Angle Harmonics | float | 2 | R
0x3E24 | 0x3E25 | 15908 | 15909 | ANG_3S_HAR_V_117th_b | Aggr 3sec Phase B 117th Voltage Angle Harmonics | float | 2 | R
0x3E26 | 0x3E27 | 15910 | 15911 | ANG_3S_HAR_V_117th_c | Aggr 3sec Phase C 117th Voltage Angle Harmonics | float | 2 | R
0x3E28 | 0x3E29 | 15912 | 15913 | ANG_3S_HAR_I_117th_a | Aggr 3sec Phase A 117th Current Angle Harmonics | float | 2 | R
0x3E2A | 0x3E2B | 15914 | 15915 | ANG_3S_HAR_I_117th_b | Aggr 3sec Phase B 117th Current Angle Harmonics | float | 2 | R
0x3E2C | 0x3E2D | 15916 | 15917 | ANG_3S_HAR_I_117th_c | Aggr 3sec Phase C 117th Current Angle Harmonics | float | 2 | R
0x3E2E | 0x3E2F | 15918 | 15919 | ANG_3S_HAR_I_117th_n | Aggr 3sec Phase N 117th Current Angle Harmonics | float | 2 | R
0x3E30 | 0x3E31 | 15920 | 15921 | ANG_3S_HAR_V_118th_a | Aggr 3sec Phase A 118th Voltage Angle Harmonics | float | 2 | R
0x3E32 | 0x3E33 | 15922 | 15923 | ANG_3S_HAR_V_118th_b | Aggr 3sec Phase B 118th Voltage Angle Harmonics | float | 2 | R
0x3E34 | 0x3E35 | 15924 | 15925 | ANG_3S_HAR_V_118th_c | Aggr 3sec Phase C 118th Voltage Angle Harmonics | float | 2 | R
0x3E36 | 0x3E37 | 15926 | 15927 | ANG_3S_HAR_I_118th_a | Aggr 3sec Phase A 118th Current Angle Harmonics | float | 2 | R
0x3E38 | 0x3E39 | 15928 | 15929 | ANG_3S_HAR_I_118th_b | Aggr 3sec Phase B 118th Current Angle Harmonics | float | 2 | R
0x3E3A | 0x3E3B | 15930 | 15931 | ANG_3S_HAR_I_118th_c | Aggr 3sec Phase C 118th Current Angle Harmonics | float | 2 | R
0x3E3C | 0x3E3D | 15932 | 15933 | ANG_3S_HAR_I_118th_n | Aggr 3sec Phase N 118th Current Angle Harmonics | float | 2 | R
0x3E3E | 0x3E3F | 15934 | 15935 | ANG_3S_HAR_V_119th_a | Aggr 3sec Phase A 119th Voltage Angle Harmonics | float | 2 | R
0x3E40 | 0x3E41 | 15936 | 15937 | ANG_3S_HAR_V_119th_b | Aggr 3sec Phase B 119th Voltage Angle Harmonics | float | 2 | R
0x3E42 | 0x3E43 | 15938 | 15939 | ANG_3S_HAR_V_119th_c | Aggr 3sec Phase C 119th Voltage Angle Harmonics | float | 2 | R
0x3E44 | 0x3E45 | 15940 | 15941 | ANG_3S_HAR_I_119th_a | Aggr 3sec Phase A 119th Current Angle Harmonics | float | 2 | R
0x3E46 | 0x3E47 | 15942 | 15943 | ANG_3S_HAR_I_119th_b | Aggr 3sec Phase B 119th Current Angle Harmonics | float | 2 | R
0x3E48 | 0x3E49 | 15944 | 15945 | ANG_3S_HAR_I_119th_c | Aggr 3sec Phase C 119th Current Angle Harmonics | float | 2 | R
0x3E4A | 0x3E4B | 15946 | 15947 | ANG_3S_HAR_I_119th_n | Aggr 3sec Phase N 119th Current Angle Harmonics | float | 2 | R
0x3E4C | 0x3E4D | 15948 | 15949 | ANG_3S_HAR_V_120th_a | Aggr 3sec Phase A 120th Voltage Angle Harmonics | float | 2 | R
0x3E4E | 0x3E4F | 15950 | 15951 | ANG_3S_HAR_V_120th_b | Aggr 3sec Phase B 120th Voltage Angle Harmonics | float | 2 | R
0x3E50 | 0x3E51 | 15952 | 15953 | ANG_3S_HAR_V_120th_c | Aggr 3sec Phase C 120th Voltage Angle Harmonics | float | 2 | R
0x3E52 | 0x3E53 | 15954 | 15955 | ANG_3S_HAR_I_120th_a | Aggr 3sec Phase A 120th Current Angle Harmonics | float | 2 | R
0x3E54 | 0x3E55 | 15956 | 15957 | ANG_3S_HAR_I_120th_b | Aggr 3sec Phase B 120th Current Angle Harmonics | float | 2 | R
0x3E56 | 0x3E57 | 15958 | 15959 | ANG_3S_HAR_I_120th_c | Aggr 3sec Phase C 120th Current Angle Harmonics | float | 2 | R
0x3E58 | 0x3E59 | 15960 | 15961 | ANG_3S_HAR_I_120th_n | Aggr 3sec Phase N 120th Current Angle Harmonics | float | 2 | R
0x3E5A | 0x3E5B | 15962 | 15963 | ANG_3S_HAR_V_121th_a | Aggr 3sec Phase A 121st Voltage Angle Harmonics | float | 2 | R
0x3E5C | 0x3E5D | 15964 | 15965 | ANG_3S_HAR_V_121th_b | Aggr 3sec Phase B 121st Voltage Angle Harmonics | float | 2 | R
0x3E5E | 0x3E5F | 15966 | 15967 | ANG_3S_HAR_V_121th_c | Aggr 3sec Phase C 121st Voltage Angle Harmonics | float | 2 | R
0x3E60 | 0x3E61 | 15968 | 15969 | ANG_3S_HAR_I_121th_a | Aggr 3sec Phase A 121st Current Angle Harmonics | float | 2 | R
0x3E62 | 0x3E63 | 15970 | 15971 | ANG_3S_HAR_I_121th_b | Aggr 3sec Phase B 121st Current Angle Harmonics | float | 2 | R
0x3E64 | 0x3E65 | 15972 | 15973 | ANG_3S_HAR_I_121th_c | Aggr 3sec Phase C 121st Current Angle Harmonics | float | 2 | R
0x3E66 | 0x3E67 | 15974 | 15975 | ANG_3S_HAR_I_121th_n | Aggr 3sec Phase N 121st Current Angle Harmonics | float | 2 | R
0x3E68 | 0x3E69 | 15976 | 15977 | ANG_3S_HAR_V_122th_a | Aggr 3sec Phase A 122nd Voltage Angle Harmonics | float | 2 | R
0x3E6A | 0x3E6B | 15978 | 15979 | ANG_3S_HAR_V_122th_b | Aggr 3sec Phase B 122nd Voltage Angle Harmonics | float | 2 | R
0x3E6C | 0x3E6D | 15980 | 15981 | ANG_3S_HAR_V_122th_c | Aggr 3sec Phase C 122nd Voltage Angle Harmonics | float | 2 | R
0x3E6E | 0x3E6F | 15982 | 15983 | ANG_3S_HAR_I_122th_a | Aggr 3sec Phase A 122nd Current Angle Harmonics | float | 2 | R
0x3E70 | 0x3E71 | 15984 | 15985 | ANG_3S_HAR_I_122th_b | Aggr 3sec Phase B 122nd Current Angle Harmonics | float | 2 | R
0x3E72 | 0x3E73 | 15986 | 15987 | ANG_3S_HAR_I_122th_c | Aggr 3sec Phase C 122nd Current Angle Harmonics | float | 2 | R
0x3E74 | 0x3E75 | 15988 | 15989 | ANG_3S_HAR_I_122th_n | Aggr 3sec Phase N 122nd Current Angle Harmonics | float | 2 | R
0x3E76 | 0x3E77 | 15990 | 15991 | ANG_3S_HAR_V_123th_a | Aggr 3sec Phase A 123rd Voltage Angle Harmonics | float | 2 | R
0x3E78 | 0x3E79 | 15992 | 15993 | ANG_3S_HAR_V_123th_b | Aggr 3sec Phase B 123rd Voltage Angle Harmonics | float | 2 | R
0x3E7A | 0x3E7B | 15994 | 15995 | ANG_3S_HAR_V_123th_c | Aggr 3sec Phase C 123rd Voltage Angle Harmonics | float | 2 | R
0x3E7C | 0x3E7D | 15996 | 15997 | ANG_3S_HAR_I_123th_a | Aggr 3sec Phase A 123rd Current Angle Harmonics | float | 2 | R
0x3E7E | 0x3E7F | 15998 | 15999 | ANG_3S_HAR_I_123th_b | Aggr 3sec Phase B 123rd Current Angle Harmonics | float | 2 | R
0x3E80 | 0x3E81 | 16000 | 16001 | ANG_3S_HAR_I_123th_c | Aggr 3sec Phase C 123rd Current Angle Harmonics | float | 2 | R
0x3E82 | 0x3E83 | 16002 | 16003 | ANG_3S_HAR_I_123th_n | Aggr 3sec Phase N 123rd Current Angle Harmonics | float | 2 | R
0x3E84 | 0x3E85 | 16004 | 16005 | ANG_3S_HAR_V_124th_a | Aggr 3sec Phase A 124th Voltage Angle Harmonics | float | 2 | R
0x3E86 | 0x3E87 | 16006 | 16007 | ANG_3S_HAR_V_124th_b | Aggr 3sec Phase B 124th Voltage Angle Harmonics | float | 2 | R
0x3E88 | 0x3E89 | 16008 | 16009 | ANG_3S_HAR_V_124th_c | Aggr 3sec Phase C 124th Voltage Angle Harmonics | float | 2 | R
0x3E8A | 0x3E8B | 16010 | 16011 | ANG_3S_HAR_I_124th_a | Aggr 3sec Phase A 124th Current Angle Harmonics | float | 2 | R
0x3E8C | 0x3E8D | 16012 | 16013 | ANG_3S_HAR_I_124th_b | Aggr 3sec Phase B 124th Current Angle Harmonics | float | 2 | R
0x3E8E | 0x3E8F | 16014 | 16015 | ANG_3S_HAR_I_124th_c | Aggr 3sec Phase C 124th Current Angle Harmonics | float | 2 | R
0x3E90 | 0x3E91 | 16016 | 16017 | ANG_3S_HAR_I_124th_n | Aggr 3sec Phase N 124th Current Angle Harmonics | float | 2 | R
0x3E92 | 0x3E93 | 16018 | 16019 | ANG_3S_HAR_V_125th_a | Aggr 3sec Phase A 125th Voltage Angle Harmonics | float | 2 | R
0x3E94 | 0x3E95 | 16020 | 16021 | ANG_3S_HAR_V_125th_b | Aggr 3sec Phase B 125th Voltage Angle Harmonics | float | 2 | R
0x3E96 | 0x3E97 | 16022 | 16023 | ANG_3S_HAR_V_125th_c | Aggr 3sec Phase C 125th Voltage Angle Harmonics | float | 2 | R
0x3E98 | 0x3E99 | 16024 | 16025 | ANG_3S_HAR_I_125th_a | Aggr 3sec Phase A 125th Current Angle Harmonics | float | 2 | R
0x3E9A | 0x3E9B | 16026 | 16027 | ANG_3S_HAR_I_125th_b | Aggr 3sec Phase B 125th Current Angle Harmonics | float | 2 | R
0x3E9C | 0x3E9D | 16028 | 16029 | ANG_3S_HAR_I_125th_c | Aggr 3sec Phase C 125th Current Angle Harmonics | float | 2 | R
0x3E9E | 0x3E9F | 16030 | 16031 | ANG_3S_HAR_I_125th_n | Aggr 3sec Phase N 125th Current Angle Harmonics | float | 2 | R
0x3EA0 | 0x3EA1 | 16032 | 16033 | ANG_3S_HAR_V_126th_a | Aggr 3sec Phase A 126th Voltage Angle Harmonics | float | 2 | R
0x3EA2 | 0x3EA3 | 16034 | 16035 | ANG_3S_HAR_V_126th_b | Aggr 3sec Phase B 126th Voltage Angle Harmonics | float | 2 | R
0x3EA4 | 0x3EA5 | 16036 | 16037 | ANG_3S_HAR_V_126th_c | Aggr 3sec Phase C 126th Voltage Angle Harmonics | float | 2 | R
0x3EA6 | 0x3EA7 | 16038 | 16039 | ANG_3S_HAR_I_126th_a | Aggr 3sec Phase A 126th Current Angle Harmonics | float | 2 | R
0x3EA8 | 0x3EA9 | 16040 | 16041 | ANG_3S_HAR_I_126th_b | Aggr 3sec Phase B 126th Current Angle Harmonics | float | 2 | R
0x3EAA | 0x3EAB | 16042 | 16043 | ANG_3S_HAR_I_126th_c | Aggr 3sec Phase C 126th Current Angle Harmonics | float | 2 | R
0x3EAC | 0x3EAD | 16044 | 16045 | ANG_3S_HAR_I_126th_n | Aggr 3sec Phase N 126th Current Angle Harmonics | float | 2 | R
0x3EAE | 0x3EAF | 16046 | 16047 | ANG_3S_HAR_V_127th_a | Aggr 3sec Phase A 127th Voltage Angle Harmonics | float | 2 | R
0x3EB0 | 0x3EB1 | 16048 | 16049 | ANG_3S_HAR_V_127th_b | Aggr 3sec Phase B 127th Voltage Angle Harmonics | float | 2 | R
0x3EB2 | 0x3EB3 | 16050 | 16051 | ANG_3S_HAR_V_127th_c | Aggr 3sec Phase C 127th Voltage Angle Harmonics | float | 2 | R
0x3EB4 | 0x3EB5 | 16052 | 16053 | ANG_3S_HAR_I_127th_a | Aggr 3sec Phase A 127th Current Angle Harmonics | float | 2 | R
0x3EB6 | 0x3EB7 | 16054 | 16055 | ANG_3S_HAR_I_127th_b | Aggr 3sec Phase B 127th Current Angle Harmonics | float | 2 | R
0x3EB8 | 0x3EB9 | 16056 | 16057 | ANG_3S_HAR_I_127th_c | Aggr 3sec Phase C 127th Current Angle Harmonics | float | 2 | R
0x3EBA | 0x3EBB | 16058 | 16059 | ANG_3S_HAR_I_127th_n | Aggr 3sec Phase N 127th Current Angle Harmonics | float | 2 | R
0x3EBC | 0x3EBD | 16060 | 16061 | FUND_HAR_Va_V | Aggr 3sec Phase A Fundamental Voltage | float | 2 | R
0x3EBE | 0x3EBF | 16062 | 16063 | FUND_HAR_Vb_V | Aggr 3sec Phase B Fundamental Voltage | float | 2 | R
0x3EC0 | 0x3EC1 | 16064 | 16065 | FUND_HAR_Vc_V | Aggr 3sec Phase C Fundamental Voltage | float | 2 | R
0x3EC2 | 0x3EC3 | 16066 | 16067 | FUND_HAR_Ia_A | Aggr 3sec Phase A Fundamental Current | float | 2 | R
0x3EC4 | 0x3EC5 | 16068 | 16069 | FUND_HAR_Ib_A | Aggr 3sec Phase B Fundamental Current | float | 2 | R
0x3EC6 | 0x3EC7 | 16070 | 16071 | FUND_HAR_Ic_A | Aggr 3sec Phase C Fundamental Current | float | 2 | R
0x3EC8 | 0x3EC9 | 16072 | 16073 | FUND_HAR_In_A | Aggr 3sec Phase N Fundamental Current | float | 2 | R

## Moving Average Frequency
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x2070 | 0x2073 | 8304 | 8307 | MOVING_AVG_TIMESTAMP | Moving Average Param Update Timestamp | double | 4 | R
0x2074 | 0x2075 | 8308 | 8309 | MOVING_AVG_Freq_Hz | Moving Average Frequency | float | 2 | R

## Transmission
Power
Transmission Line Supply
0xA800 | 0xA801 | 43008 | 43009 | Transmission Line Supply_P_a_kW | Phase A Active Power | float | 2 | R
0xA802 | 0xA803 | 43010 | 43011 | Transmission Line Supply_P_b_kW | Phase B Active Power | float | 2 | R
0xA804 | 0xA805 | 43012 | 43013 | Transmission Line Supply_P_c_kW | Phase C Active Power | float | 2 | R
0xA806 | 0xA807 | 43014 | 43015 | Transmission Line Supply_P_kW | System Active Power | float | 2 | R
0xA808 | 0xA809 | 43016 | 43017 | Transmission Line Supply_Q_a_kvar | Phase A Reactive Power | float | 2 | R
0xA80A | 0xA80B | 43018 | 43019 | Transmission Line Supply_Q_b_kvar | Phase B Reactive Power | float | 2 | R
0xA80C | 0xA80D | 43020 | 43021 | Transmission Line Supply_Q_c_kvar | Phase C Reactive Power | float | 2 | R
0xA80E | 0xA80F | 43022 | 43023 | Transmission Line Supply_Q_kvar | System Reactive Power | float | 2 | R
Transmission Line load
0xA810 | 0xA811 | 43024 | 43025 | Transmission LineLoad_P_a_kW | Phase A Active Power | float | 2 | R
0xA812 | 0xA813 | 43026 | 43027 | Transmission Line Load_P_b_kW | Phase B Active Power | float | 2 | R
0xA814 | 0xA815 | 43028 | 43029 | Transmission Line Load_P_c_kW | Phase C Active Power | float | 2 | R
0xA816 | 0xA817 | 43030 | 43031 | Transmission Line Load_P_kW | System Active Power | float | 2 | R
0xA818 | 0xA819 | 43032 | 43033 | Transmission Line Load_Q_a_kvar | Phase A Reactive Power | float | 2 | R
0xA81A | 0xA81B | 43034 | 43035 | Transmission Line Load_Q_b_kvar | Phase B Reactive Power | float | 2 | R
0xA81C | 0xA81D | 43036 | 43037 | Transmission Line Load_Q_c_kvar | Phase C Reactive Power | float | 2 | R
0xA81E | 0xA81F | 43038 | 43039 | Transmission Line Load_Q_kvar | System Reactive Power | float | 2 | R
Transformer
0xA820 | 0xA821 | 43040 | 43041 | Transformer_P_a_kW | Phase A Active Power | float | 2 | R
0xA822 | 0xA823 | 43042 | 43043 | Transformer_P_b_kW | Phase B Active Power | float | 2 | R
0xA824 | 0xA825 | 43044 | 43045 | Transformer_P_c_kW | Phase C Active Power | float | 2 | R
0xA826 | 0xA827 | 43046 | 43047 | Transformer_P_kW | System Active Power | float | 2 | R
0xA828 | 0xA829 | 43048 | 43049 | Transformer_Q_a_kvar | Phase A Reactive Power | float | 2 | R
0xA82A | 0xA82B | 43050 | 43051 | Transformer_Q_b_kvar | Phase B Reactive Power | float | 2 | R
0xA82C | 0xA82D | 43052 | 43053 | Transformer_Q_c_kvar | Phase C Reactive Power | float | 2 | R
0xA82E | 0xA82F | 43054 | 43055 | Transformer_Q_kvar | System Reactive Power | float | 2 | R
Total
0xA830 | 0xA831 | 43056 | 43057 | Total_P_a_kW | Phase A Active Power | float | 2 | R
0xA832 | 0xA833 | 43058 | 43059 | Total_P_b_kW | Phase B Active Power | float | 2 | R
0xA834 | 0xA835 | 43060 | 43061 | Total_P_c_kW | Phase C Active Power | float | 2 | R
0xA836 | 0xA837 | 43062 | 43063 | Total_P_kW | System Active Power | float | 2 | R
0xA838 | 0xA839 | 43064 | 43065 | Total_Q_a_kvar | Phase A Reactive Power | float | 2 | R
0xA83A | 0xA83B | 43066 | 43067 | Total_Q_b_kvar | Phase B Reactive Power | float | 2 | R
0xA83C | 0xA83D | 43068 | 43069 | Total_Q_c_kvar | Phase C Reactive Power | float | 2 | R
0xA83E | 0xA83F | 43070 | 43071 | Total_Q_kvar | System Reactive Power | float | 2 | R
Energy(Total)
Transmission Line Supply
0xA840 | 0xA841 | 43072 | 43073 | Transmission Line Supply_EP_a_kWh(Total) | Phase A Active Energy | float | 2 | R
0xA842 | 0xA843 | 43074 | 43075 | Transmission Line Supply_EP_b_kWh(Total) | Phase B Active Energy | float | 2 | R
0xA844 | 0xA845 | 43076 | 43077 | Transmission Line Supply_EP_c_kWh(Total) | Phase C Active Energy | float | 2 | R
0xA846 | 0xA847 | 43078 | 43079 | Transmission Line Supply_EP_kWh(Total) | System Active Energy | float | 2 | R
0xA848 | 0xA849 | 43080 | 43081 | Transmission Line Supply_EQ_a_kvarh(Total) | Phase A Reactive Energy | float | 2 | R
0xA84A | 0xA84B | 43082 | 43083 | Transmission Line Supply_EQ_b_kvarh(Total) | Phase B Reactive Energy | float | 2 | R
0xA84C | 0xA84D | 43084 | 43085 | Transmission Line Supply_EQ_c_kvarh(Total) | Phase C Reactive Energy | float | 2 | R
0xA84E | 0xA84F | 43086 | 43087 | Transmission Line Supply_EQ_kvarh(Total) | System Reactive Energy | float | 2 | R
Transmission Line Load
0xA850 | 0xA851 | 43088 | 43089 | Transmission Line Load_EP_a_kWh(Total) | Phase A Active Energy | float | 2 | R
0xA852 | 0xA853 | 43090 | 43091 | Transmission Line Load_EP_b_kWh(Total) | Phase B Active Energy | float | 2 | R
0xA854 | 0xA855 | 43092 | 43093 | Transmission Line Load_EP_c_kWh(Total) | Phase C Active Energy | float | 2 | R
0xA856 | 0xA857 | 43094 | 43095 | Transmission Line Load_EP_kWh(Total) | System Active Energy | float | 2 | R
0xA858 | 0xA859 | 43096 | 43097 | Transmission Line Load_EQ_a_kvarh(Total) | Phase A Reactive Energy | float | 2 | R
0xA85A | 0xA85B | 43098 | 43099 | Transmission Line Load_EQ_b_kvarh(Total) | Phase B Reactive Energy | float | 2 | R
0xA85C | 0xA85D | 43100 | 43101 | Transmission Line Load_EQ_c_kvarh(Total) | Phase C Reactive Energy | float | 2 | R
0xA85E | 0xA85F | 43102 | 43103 | Transmission Line Load_EQ_kvarh(Total) | System Reactive Energy | float | 2 | R
Transformer
0xA860 | 0xA861 | 43104 | 43105 | Transformer_EP_a_kWh(Total) | Phase A Active Energy | float | 2 | R
0xA862 | 0xA863 | 43106 | 43107 | Transformer_EP_b_kWh(Total) | Phase B Active Energy | float | 2 | R
0xA864 | 0xA865 | 43108 | 43109 | Transformer_EP_c_kWh(Total) | Phase C Active Energy | float | 2 | R
0xA866 | 0xA867 | 43110 | 43111 | Transformer_EP_kWh(Total) | System Active Energy | float | 2 | R
0xA868 | 0xA869 | 43112 | 43113 | Transformer_EQ_a_kvarh(Total) | Phase A Reactive Energy | float | 2 | R
0xA86A | 0xA86B | 43114 | 43115 | Transformer_EQ_b_kvarh(Total) | Phase B Reactive Energy | float | 2 | R
0xA86C | 0xA86D | 43116 | 43117 | Transformer_EQ_c_kvarh(Total) | Phase C Reactive Energy | float | 2 | R
0xA86E | 0xA86F | 43118 | 43119 | Transformer_EQ_kvarh(Total) | System Reactive Energy | float | 2 | R
Total
0xA870 | 0xA871 | 43120 | 43121 | Total_EP_a_kWh(Total) | Phase A Active Energy | float | 2 | R
0xA872 | 0xA873 | 43122 | 43123 | Total_EP_b_kWh(Total) | Phase B Active Energy | float | 2 | R
0xA874 | 0xA875 | 43124 | 43125 | Total_EP_c_kWh(Total) | Phase C Active Energy | float | 2 | R
0xA876 | 0xA877 | 43126 | 43127 | Total_EP_kWh(Total) | System Active Energy | float | 2 | R
0xA878 | 0xA879 | 43128 | 43129 | Total_EQ_a_kvarh(Total) | Phase A Reactive Energy | float | 2 | R
0xA87A | 0xA87B | 43130 | 43131 | Total_EQ_b_kvarh(Total) | Phase B Reactive Energy | float | 2 | R
0xA87C | 0xA87D | 43132 | 43133 | Total_EQ_c_kvarh(Total) | Phase C Reactive Energy | float | 2 | R
0xA87E | 0xA87F | 43134 | 43135 | Total_EQ_kvarh(Total) | System Reactive Energy | float | 2 | R
Energy(Net)
Transmission Line Supply
0xA880 | 0xA881 | 43136 | 43137 | Transmission Line Supply_EP_a_kWh(Net) | Phase A Active Energy | float | 2 | R
0xA882 | 0xA883 | 43138 | 43139 | Transmission Line Supply_EP_b_kWh(Net) | Phase B Active Energy | float | 2 | R
0xA884 | 0xA885 | 43140 | 43141 | Transmission Line Supply_EP_c_kWh(Net) | Phase C Active Energy | float | 2 | R
0xA886 | 0xA887 | 43142 | 43143 | Transmission Line Supply_EP_kWh(Net) | System Active Energy | float | 2 | R
0xA888 | 0xA889 | 43144 | 43145 | Transmission Line Supply_EQ_a_kvarh(Net) | Phase A Reactive Energy | float | 2 | R
0xA88A | 0xA88B | 43146 | 43147 | Transmission Line Supply_EQ_b_kvarh(Net) | Phase B Reactive Energy | float | 2 | R
0xA88C | 0xA88D | 43148 | 43149 | Transmission Line Supply_EQ_c_kvarh(Net) | Phase C Reactive Energy | float | 2 | R
0xA88E | 0xA88F | 43150 | 43151 | Transmission Line Supply_EQ_kvarh(Net) | System Reactive Energy | float | 2 | R
Transmission Line Load
0xA890 | 0xA891 | 43152 | 43153 | Transmission Line Load_EP_a_kWh(Net) | Phase A Active Energy | float | 2 | R
0xA892 | 0xA893 | 43154 | 43155 | Transmission Line Load_EP_b_kWh(Net) | Phase B Active Energy | float | 2 | R
0xA894 | 0xA895 | 43156 | 43157 | Transmission Line Load_EP_c_kWh(Net) | Phase C Active Energy | float | 2 | R
0xA896 | 0xA897 | 43158 | 43159 | Transmission Line Load_EP_kWh(Net) | System Active Energy | float | 2 | R
0xA898 | 0xA899 | 43160 | 43161 | Transmission Line Load_EQ_a_kvarh(Net) | Phase A Reactive Energy | float | 2 | R
0xA89A | 0xA89B | 43162 | 43163 | Transmission Line Load_EQ_b_kvarh(Net) | Phase B Reactive Energy | float | 2 | R
0xA89C | 0xA89D | 43164 | 43165 | Transmission Line Load_EQ_c_kvarh(Net) | Phase C Reactive Energy | float | 2 | R
0xA89E | 0xA89F | 43166 | 43167 | Transmission Line Load_EQ_kvarh(Net) | System Reactive Energy | float | 2 | R
Transformer
0xA8A0 | 0xA8A1 | 43168 | 43169 | Transformer_EP_a_kWh(Net) | Phase A Active Energy | float | 2 | R
0xA8A2 | 0xA8A3 | 43170 | 43171 | Transformer_EP_b_kWh(Net) | Phase B Active Energy | float | 2 | R
0xA8A4 | 0xA8A5 | 43172 | 43173 | Transformer_EP_c_kWh(Net) | Phase C Active Energy | float | 2 | R
0xA8A6 | 0xA8A7 | 43174 | 43175 | Transformer_EP_kWh(Net) | System Active Energy | float | 2 | R
0xA8A8 | 0xA8A9 | 43176 | 43177 | Transformer_EQ_a_kvarh(Net) | Phase A Reactive Energy | float | 2 | R
0xA8AA | 0xA8AB | 43178 | 43179 | Transformer_EQ_b_kvarh(Net) | Phase B Reactive Energy | float | 2 | R
0xA8AC | 0xA8AD | 43180 | 43181 | Transformer_EQ_c_kvarh(Net) | Phase C Reactive Energy | float | 2 | R
0xA8AE | 0xA8AF | 43182 | 43183 | Transformer_EQ_kvarh(Net) | System Reactive Energy | float | 2 | R
Total
0xA8B0 | 0xA8B1 | 43184 | 43185 | Net_EP_a_kWh(Net) | Phase A Active Energy | float | 2 | R
0xA8B2 | 0xA8B3 | 43186 | 43187 | Net_EP_b_kWh(Net) | Phase B Active Energy | float | 2 | R
0xA8B4 | 0xA8B5 | 43188 | 43189 | Net_EP_c_kWh(Net) | Phase C Active Energy | float | 2 | R
0xA8B6 | 0xA8B7 | 43190 | 43191 | Net_EP_kWh(Net) | System Active Energy | float | 2 | R
0xA8B8 | 0xA8B9 | 43192 | 43193 | Net_EQ_a_kvarh(Net) | Phase A Reactive Energy | float | 2 | R
0xA8BA | 0xA8BB | 43194 | 43195 | Net_EQ_b_kvarh(Net) | Phase B Reactive Energy | float | 2 | R
0xA8BC | 0xA8BD | 43196 | 43197 | Net_EQ_c_kvarh(Net) | Phase C Reactive Energy | float | 2 | R
0xA8BE | 0xA8BF | 43198 | 43199 | Net_EQ_kvarh(Net) | System Reactive Energy | float | 2 | R

## 200ms
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x2100 | 0x2103 | 8448 | 8451 | 200MS_RMS_TIMESTAMP | 200ms RMS Param Update Timestamp | double | 4 | R
0x2104 | 0x2105 | 8452 | 8453 | 200MS_RMS_FLAG | 200ms RMS Param Valid Flag | bool | 2 | R
0x2106 | 0x2107 | 8454 | 8455 | 200MS_RMS_BLOCK_NUM | 200ms RMS Param Block Number | uint32 | 2 | R
0x2108 | 0x2109 | 8456 | 8457 | 200MS_RMS_EVENT_FLAG | 200ms RMS Param Event Flag | uint32 | 2 | R
0x210A | 0x210D | 8458 | 8461 | 200MS_FFT_TIMESTAMP | 200ms FFT Param Update Timestamp | double | 4 | R
0x210E | 0x210F | 8462 | 8463 | 200MS_FFT_FLAG | 200ms FFT Param Valid Flag | bool | 2 | R
0x2110 | 0x2111 | 8464 | 8465 | 200MS_FFT_BLOCK_NUM | 200ms FFT Param Block Number | uint32 | 2 | R
0x2112 | 0x2113 | 8466 | 8467 | 200MS_FFT_EVENT_FLAG | 200ms FFT Param Event Flag | uint32 | 2 | R
0x2114 | 0x2115 | 8468 | 8469 | 200MS_Freq_Hz | System Frequency | float | 2 | R
0x2116 | 0x2117 | 8470 | 8471 | 200MS_VLN_a_V | Phase A Line-to-Neutral Voltage | float | 2 | R
0x2118 | 0x2119 | 8472 | 8473 | 200MS_VLN_b_V | Phase B Line-to-Neutral Voltage | float | 2 | R
0x211A | 0x211B | 8474 | 8475 | 200MS_VLN_c_V | Phase C Line-to-Neutral Voltage | float | 2 | R
0x211C | 0x211D | 8476 | 8477 | 200MS_VLN_avg_V | Average Line-to-Neutral Voltage | float | 2 | R
0x211E | 0x211F | 8478 | 8479 | 200MS_VLL_ab_V | Phase AB Line-to-Line Voltage | float | 2 | R
0x2120 | 0x2121 | 8480 | 8481 | 200MS_VLL_bc_V | Phase BC Line-to-Line Voltage | float | 2 | R
0x2122 | 0x2123 | 8482 | 8483 | 200MS_VLL_ca_V | Phase CA Line-to-Line Voltage | float | 2 | R
0x2124 | 0x2125 | 8484 | 8485 | 200MS_VLL_avg_V | Average Line-to-Line Voltage | float | 2 | R
0x2126 | 0x2127 | 8486 | 8487 | 200MS_I_a_A | Phase A Current | float | 2 | R
0x2128 | 0x2129 | 8488 | 8489 | 200MS_I_b_A | Phase B Current | float | 2 | R
0x212A | 0x212B | 8490 | 8491 | 200MS_I_c_A | Phase C Current | float | 2 | R
0x212C | 0x212D | 8492 | 8493 | 200MS_I_n_A | Phase N Current | float | 2 | R
0x212E | 0x212F | 8494 | 8495 | 200MS_I_avg_A | Average Current | float | 2 | R
0x2130 | 0x2131 | 8496 | 8497 | 200MS_P_a_kW | Phase A Active Power | float | 2 | R
0x2132 | 0x2133 | 8498 | 8499 | 200MS_P_b_kW | Phase B Active Power | float | 2 | R
0x2134 | 0x2135 | 8500 | 8501 | 200MS_P_c_kW | Phase C Active Power | float | 2 | R
0x2136 | 0x2137 | 8502 | 8503 | 200MS_P_kW | System Active Power | float | 2 | R
0x2138 | 0x2139 | 8504 | 8505 | 200MS_Q_a_kvar | Phase A Reactive Power | float | 2 | R
0x213A | 0x213B | 8506 | 8507 | 200MS_Q_b_kvar | Phase B Reactive Power | float | 2 | R
0x213C | 0x213D | 8508 | 8509 | 200MS_Q_c_kvar | Phase C Reactive Power | float | 2 | R
0x213E | 0x213F | 8510 | 8511 | 200MS_Q_kvar | System Reactive Power | float | 2 | R
0x2140 | 0x2141 | 8512 | 8513 | 200MS_S_a_kVA | Phase A Apparent Power | float | 2 | R
0x2142 | 0x2143 | 8514 | 8515 | 200MS_S_b_kVA | Phase B Apparent Power | float | 2 | R
0x2144 | 0x2145 | 8516 | 8517 | 200MS_S_c_kVA | Phase C Apparent Power | float | 2 | R
0x2146 | 0x2147 | 8518 | 8519 | 200MS_S_kVA | System Apparent Power | float | 2 | R
0x2148 | 0x2149 | 8520 | 8521 | 200MS_LC_a | Phase A Load Nature | float | 2 | R
0x214A | 0x214B | 8522 | 8523 | 200MS_LC_b | Phase B Load Nature | float | 2 | R
0x214C | 0x214D | 8524 | 8525 | 200MS_LC_c | Phase C Load Nature | float | 2 | R
0x214E | 0x214F | 8526 | 8527 | 200MS_LC | System Load Nature | float | 2 | R
0x2150 | 0x2151 | 8528 | 8529 | 200MS_PF_a | Phase A Power Factor | float | 2 | R
0x2152 | 0x2153 | 8530 | 8531 | 200MS_PF_b | Phase B Power Factor | float | 2 | R
0x2154 | 0x2155 | 8532 | 8533 | 200MS_PF_c | Phase C Power Factor | float | 2 | R
0x2156 | 0x2157 | 8534 | 8535 | 200MS_PF | System Power Factor | float | 2 | R
0x2158 | 0x2159 | 8536 | 8537 | 200MS_LEAD_PF_a | Phase A Leading Power Factor | float | 2 | R
0x215A | 0x215B | 8538 | 8539 | 200MS_LEAD_PF_b | Phase B Leading Power Factor | float | 2 | R
0x215C | 0x215D | 8540 | 8541 | 200MS_LEAD_PF_c | Phase C Leading Power Factor | float | 2 | R
0x215E | 0x215F | 8542 | 8543 | 200MS_LEAD_PF | System Leading Power Factor | float | 2 | R
0x2160 | 0x2161 | 8544 | 8545 | 200MS_LAG_PF_a | Phase A Lagging Power Factor | float | 2 | R
0x2162 | 0x2163 | 8546 | 8547 | 200MS_LAG_PF_b | Phase B Lagging Power Factor | float | 2 | R
0x2164 | 0x2165 | 8548 | 8549 | 200MS_LAG_PF_c | Phase C Lagging Power Factor | float | 2 | R
0x2166 | 0x2167 | 8550 | 8551 | 200MS_LAG_PF | System Lagging Power Factor | float | 2 | R
0x2168 | 0x2169 | 8552 | 8553 | 200MS_PA_VLN_a | Phase A Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x216A | 0x216B | 8554 | 8555 | 200MS_PA_VLN_b | Phase B Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x216C | 0x216D | 8556 | 8557 | 200MS_PA_VLN_c | Phase C Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x216E | 0x216F | 8558 | 8559 | 200MS_PA_VLL_ab | Phase AB Line-to-Line Voltage Phase Angle | float | 2 | R
0x2170 | 0x2171 | 8560 | 8561 | 200MS_PA_VLL_bc | Phase BC Line-to-Line Voltage Phase Angle | float | 2 | R
0x2172 | 0x2173 | 8562 | 8563 | 200MS_PA_VLL_ca | Phase CA Line-to-Line Voltage Phase Angle | float | 2 | R
0x2174 | 0x2175 | 8564 | 8565 | 200MS_PA_I_a | Phase A Current Phase Angle | float | 2 | R
0x2176 | 0x2177 | 8566 | 8567 | 200MS_PA_I_b | Phase B Current Phase Angle | float | 2 | R
0x2178 | 0x2179 | 8568 | 8569 | 200MS_PA_I_c | Phase C Current Phase Angle | float | 2 | R
0x217A | 0x217B | 8570 | 8571 | MAG_200MS_SEQ_POS_V_V | Voltage Positive Sequence Magnitude | float | 2 | R
0x217C | 0x217D | 8572 | 8573 | MAG_200MS_SEQ_ZERO_V_V | Voltage Zero Sequence Magnitude | float | 2 | R
0x217E | 0x217F | 8574 | 8575 | MAG_200MS_SEQ_NEG_V_V | Voltage Negative Sequence Magnitude | float | 2 | R
0x2180 | 0x2181 | 8576 | 8577 | MAG_200MS_SEQ_ZERO_RATIO_V_% | Voltage Zero Sequence Ratio Magnitude | float | 2 | R
0x2182 | 0x2183 | 8578 | 8579 | MAG_200MS_UNBL_V_% | Voltage Unbalance Factor Magnitude | float | 2 | R
0x2184 | 0x2185 | 8580 | 8581 | MAG_200MS_SEQ_POS_I_A | Current Positive Sequence Magnitude | float | 2 | R
0x2186 | 0x2187 | 8582 | 8583 | MAG_200MS_SEQ_ZERO_I_A | Current Zero Sequence Magnitude | float | 2 | R
0x2188 | 0x2189 | 8584 | 8585 | MAG_200MS_SEQ_NEG_I_A | Current Negative Sequence Magnitude | float | 2 | R
0x218A | 0x218B | 8586 | 8587 | MAG_200MS_SEQ_ZERO_RATIO_I_% | Current Zero Sequence Ratio Magnitude | float | 2 | R
0x218C | 0x218D | 8588 | 8589 | MAG_200MS_UNBL_I_% | Current Unbalance Factor Magnitude | float | 2 | R
0x218E | 0x218F | 8590 | 8591 | ANG_200MS_SEQ_POS_V | Voltage Positive Sequence Angle | float | 2 | R
0x2190 | 0x2191 | 8592 | 8593 | ANG_200MS_SEQ_ZERO_V | Voltage Zero Sequence Angle | float | 2 | R
0x2192 | 0x2193 | 8594 | 8595 | ANG_200MS_SEQ_NEG_V | Voltage Negative Sequence Angle | float | 2 | R
0x2194 | 0x2195 | 8596 | 8597 | ANG_200MS_SEQ_POS_I_A | Current Positive Sequence Angle | float | 2 | R
0x2196 | 0x2197 | 8598 | 8599 | ANG_200MS_SEQ_ZERO_I_A | Current Zero Sequence Angle | float | 2 | R
0x2198 | 0x2199 | 8600 | 8601 | ANG_200MS_SEQ_NEG_I_A | Current Negative Sequence Angle | float | 2 | R
0x219A | 0x219B | 8602 | 8603 | 200MS_THD_V_a_% | Phase A Voltage THD | float | 2 | R
0x219C | 0x219D | 8604 | 8605 | 200MS_THD_V_b_% | Phase B Voltage THD | float | 2 | R
0x219E | 0x219F | 8606 | 8607 | 200MS_THD_V_c_% | Phase C Voltage THD | float | 2 | R
0x21A0 | 0x21A1 | 8608 | 8609 | 200MS_OTHD_V_a_% | Phase A Voltage THD Odd | float | 2 | R
0x21A2 | 0x21A3 | 8610 | 8611 | 200MS_OTHD_V_b_% | Phase B Voltage THD Odd | float | 2 | R
0x21A4 | 0x21A5 | 8612 | 8613 | 200MS_OTHD_V_c_% | Phase C Voltage THD Odd | float | 2 | R
0x21A6 | 0x21A7 | 8614 | 8615 | 200MS_ETHD_V_a_% | Phase A Voltage THD Even | float | 2 | R
0x21A8 | 0x21A9 | 8616 | 8617 | 200MS_ETHD_V_b_% | Phase B Voltage THD Even | float | 2 | R
0x21AA | 0x21AB | 8618 | 8619 | 200MS_ETHD_V_c_% | Phase C Voltage THD Even | float | 2 | R
0x21AC | 0x21AD | 8620 | 8621 | 200MS_CF_V_a_% | Phase A Voltage Crest Factor | float | 2 | R
0x21AE | 0x21AF | 8622 | 8623 | 200MS_CF_V_b_% | Phase B Voltage Crest Factor | float | 2 | R
0x21B0 | 0x21B1 | 8624 | 8625 | 200MS_CF_V_c_% | Phase C Voltage Crest Factor | float | 2 | R
0x21B2 | 0x21B3 | 8626 | 8627 | 200MS_THD_I_a_% | Phase A Current THD | float | 2 | R
0x21B4 | 0x21B5 | 8628 | 8629 | 200MS_THD_I_b_% | Phase B Current THD | float | 2 | R
0x21B6 | 0x21B7 | 8630 | 8631 | 200MS_THD_I_c_% | Phase C Current THD | float | 2 | R
0x21B8 | 0x21B9 | 8632 | 8633 | 200MS_THD_I_n_% | Phase N Current THD | float | 2 | R
0x21BA | 0x21BB | 8634 | 8635 | 200MS_OTHD_I_a_% | Phase A Current THD Odd | float | 2 | R
0x21BC | 0x21BD | 8636 | 8637 | 200MS_OTHD_I_b_% | Phase B Current THD Odd | float | 2 | R
0x21BE | 0x21BF | 8638 | 8639 | 200MS_OTHD_I_c_% | Phase C Current THD Odd | float | 2 | R
0x21C0 | 0x21C1 | 8640 | 8641 | 200MS_OTHD_I_n_% | Phase N Current THD Odd | float | 2 | R
0x21C2 | 0x21C3 | 8642 | 8643 | 200MS_ETHD_I_a_% | Phase A Current THD Even | float | 2 | R
0x21C4 | 0x21C5 | 8644 | 8645 | 200MS_ETHD_I_b_% | Phase B Current THD Even | float | 2 | R
0x21C6 | 0x21C7 | 8646 | 8647 | 200MS_ETHD_I_c_% | Phase C Current THD Even | float | 2 | R
0x21C8 | 0x21C9 | 8648 | 8649 | 200MS_ETHD_I_n_% | Phase N Current THD Even | float | 2 | R
0x21CA | 0x21CB | 8650 | 8651 | 200MS_TDD_I_a_% | Phase A Current TDD | float | 2 | R
0x21CC | 0x21CD | 8652 | 8653 | 200MS_TDD_I_b_% | Phase B Current TDD | float | 2 | R
0x21CE | 0x21CF | 8654 | 8655 | 200MS_TDD_I_c_% | Phase C Current TDD | float | 2 | R
0x21D0 | 0x21D1 | 8656 | 8657 | 200MS_TDD_I_n_% | Phase N Current TDD | float | 2 | R
0x21D2 | 0x21D3 | 8658 | 8659 | 200MS_CF_I_a_% | Phase A Current Crest-Factor | float | 2 | R
0x21D4 | 0x21D5 | 8660 | 8661 | 200MS_CF_I_b_% | Phase B Current Crest-Factor | float | 2 | R
0x21D6 | 0x21D7 | 8662 | 8663 | 200MS_CF_I_c_% | Phase C Current Crest-Factor | float | 2 | R
0x21D8 | 0x21D9 | 8664 | 8665 | 200MS_CF_I_n_% | Phase N Current Crest-Factor | float | 2 | R
0x21DA | 0x21DB | 8666 | 8667 | 200MS_KF_I_a_% | Phase A Current K-Factor | float | 2 | R
0x21DC | 0x21DD | 8668 | 8669 | 200MS_KF_I_b_% | Phase B Current K-Factor | float | 2 | R
0x21DE | 0x21DF | 8670 | 8671 | 200MS_KF_I_c_% | Phase C Current K-Factor | float | 2 | R
0x21E0 | 0x21E1 | 8672 | 8673 | 200MS_KF_I_n_% | Phase N Current K-Factor | float | 2 | R
0x21E2 | 0x21E3 | 8674 | 8675 | 200MS_FLICK_V_a | Phase A Voltage Flicker | float | 2 | R
0x21E4 | 0x21E5 | 8676 | 8677 | 200MS_FLICK_V_b | Phase B Voltage Flicker | float | 2 | R
0x21E6 | 0x21E7 | 8678 | 8679 | 200MS_FLICK_V_c | Phase C Voltage Flicker | float | 2 | R
0x21E8 | 0x21E9 | 8680 | 8681 | MAG_200MS_HAR_V_1th_a_% | Phase A 1st Voltage Magnitude Harmonics | float | 2 | R
0x21EA | 0x21EB | 8682 | 8683 | MAG_200MS_HAR_V_1th_b_% | Phase B 1st Voltage Magnitude Harmonics | float | 2 | R
0x21EC | 0x21ED | 8684 | 8685 | MAG_200MS_HAR_V_1th_c_% | Phase C 1st Voltage Magnitude Harmonics | float | 2 | R
0x21EE | 0x21EF | 8686 | 8687 | MAG_200MS_HAR_I_1th_a_% | Phase A 1st Current Magnitude Harmonics | float | 2 | R
0x21F0 | 0x21F1 | 8688 | 8689 | MAG_200MS_HAR_I_1th_b_% | Phase B 1st Current Magnitude Harmonics | float | 2 | R
0x21F2 | 0x21F3 | 8690 | 8691 | MAG_200MS_HAR_I_1th_c_% | Phase C 1st Current Magnitude Harmonics | float | 2 | R
0x21F4 | 0x21F5 | 8692 | 8693 | MAG_200MS_HAR_I_1th_n_% | Phase N 1st Current Magnitude Harmonics | float | 2 | R
0x21F6 | 0x21F7 | 8694 | 8695 | MAG_200MS_HAR_V_2th_a_% | Phase A 2nd Voltage Magnitude Harmonics | float | 2 | R
0x21F8 | 0x21F9 | 8696 | 8697 | MAG_200MS_HAR_V_2th_b_% | Phase B 2nd Voltage Magnitude Harmonics | float | 2 | R
0x21FA | 0x21FB | 8698 | 8699 | MAG_200MS_HAR_V_2th_c_% | Phase C 2nd Voltage Magnitude Harmonics | float | 2 | R
0x21FC | 0x21FD | 8700 | 8701 | MAG_200MS_HAR_I_2th_a_% | Phase A 2nd Current Magnitude Harmonics | float | 2 | R
0x21FE | 0x21FF | 8702 | 8703 | MAG_200MS_HAR_I_2th_b_% | Phase B 2nd Current Magnitude Harmonics | float | 2 | R
0x2200 | 0x2201 | 8704 | 8705 | MAG_200MS_HAR_I_2th_c_% | Phase C 2nd Current Magnitude Harmonics | float | 2 | R
0x2202 | 0x2203 | 8706 | 8707 |  | Phase N 2nd Current Magnitude Harmonics | float | 2 | R
0x2204 | 0x2205 | 8708 | 8709 | MAG_200MS_HAR_V_3th_a_% | Phase A 3rd Voltage Magnitude Harmonics | float | 2 | R
0x2206 | 0x2207 | 8710 | 8711 | MAG_200MS_HAR_V_3th_b_% | Phase B 3rd Voltage Magnitude Harmonics | float | 2 | R
0x2208 | 0x2209 | 8712 | 8713 | MAG_200MS_HAR_V_3th_c_% | Phase C 3rd Voltage Magnitude Harmonics | float | 2 | R
0x220A | 0x220B | 8714 | 8715 | MAG_200MS_HAR_I_3th_a_% | Phase A 3rd Current Magnitude Harmonics | float | 2 | R
0x220C | 0x220D | 8716 | 8717 | MAG_200MS_HAR_I_3th_b_% | Phase B 3rd Current Magnitude Harmonics | float | 2 | R
0x220E | 0x220F | 8718 | 8719 | MAG_200MS_HAR_I_3th_c_% | Phase C 3rd Current Magnitude Harmonics | float | 2 | R
0x2210 | 0x2211 | 8720 | 8721 | MAG_200MS_HAR_I_3th_n_% | Phase N 3rd Current Magnitude Harmonics | float | 2 | R
0x2212 | 0x2213 | 8722 | 8723 | MAG_200MS_HAR_V_4th_a_% | Phase A 4th Voltage Magnitude Harmonics | float | 2 | R
0x2214 | 0x2215 | 8724 | 8725 | MAG_200MS_HAR_V_4th_b_% | Phase B 4th Voltage Magnitude Harmonics | float | 2 | R
0x2216 | 0x2217 | 8726 | 8727 | MAG_200MS_HAR_V_4th_c_% | Phase C 4th Voltage Magnitude Harmonics | float | 2 | R
0x2218 | 0x2219 | 8728 | 8729 | MAG_200MS_HAR_I_4th_a_% | Phase A 4th Current Magnitude Harmonics | float | 2 | R
0x221A | 0x221B | 8730 | 8731 | MAG_200MS_HAR_I_4th_b_% | Phase B 4th Current Magnitude Harmonics | float | 2 | R
0x221C | 0x221D | 8732 | 8733 | MAG_200MS_HAR_I_4th_c_% | Phase C 4th Current Magnitude Harmonics | float | 2 | R
0x221E | 0x221F | 8734 | 8735 | MAG_200MS_HAR_I_4th_n_% | Phase N 4th Current Magnitude Harmonics | float | 2 | R
0x2220 | 0x2221 | 8736 | 8737 | MAG_200MS_HAR_V_5th_a_% | Phase A 5th Voltage Magnitude Harmonics | float | 2 | R
0x2222 | 0x2223 | 8738 | 8739 | MAG_200MS_HAR_V_5th_b_% | Phase B 5th Voltage Magnitude Harmonics | float | 2 | R
0x2224 | 0x2225 | 8740 | 8741 | MAG_200MS_HAR_V_5th_c_% | Phase C 5th Voltage Magnitude Harmonics | float | 2 | R
0x2226 | 0x2227 | 8742 | 8743 | MAG_200MS_HAR_I_5th_a_% | Phase A 5th Current Magnitude Harmonics | float | 2 | R
0x2228 | 0x2229 | 8744 | 8745 | MAG_200MS_HAR_I_5th_b_% | Phase B 5th Current Magnitude Harmonics | float | 2 | R
0x222A | 0x222B | 8746 | 8747 | MAG_200MS_HAR_I_5th_c_% | Phase C 5th Current Magnitude Harmonics | float | 2 | R
0x222C | 0x222D | 8748 | 8749 | MAG_200MS_HAR_I_5th_n_% | Phase N 5th Current Magnitude Harmonics | float | 2 | R
0x222E | 0x222F | 8750 | 8751 | MAG_200MS_HAR_V_6th_a_% | Phase A 6th Voltage Magnitude Harmonics | float | 2 | R
0x2230 | 0x2231 | 8752 | 8753 | MAG_200MS_HAR_V_6th_b_% | Phase B 6th Voltage Magnitude Harmonics | float | 2 | R
0x2232 | 0x2233 | 8754 | 8755 | MAG_200MS_HAR_V_6th_c_% | Phase C 6th Voltage Magnitude Harmonics | float | 2 | R
0x2234 | 0x2235 | 8756 | 8757 | MAG_200MS_HAR_I_6th_a_% | Phase A 6th Current Magnitude Harmonics | float | 2 | R
0x2236 | 0x2237 | 8758 | 8759 | MAG_200MS_HAR_I_6th_b_% | Phase B 6th Current Magnitude Harmonics | float | 2 | R
0x2238 | 0x2239 | 8760 | 8761 | MAG_200MS_HAR_I_6th_c_% | Phase C 6th Current Magnitude Harmonics | float | 2 | R
0x223A | 0x223B | 8762 | 8763 | MAG_200MS_HAR_I_6th_n_% | Phase N 6th Current Magnitude Harmonics | float | 2 | R
0x223C | 0x223D | 8764 | 8765 | MAG_200MS_HAR_V_7th_a_% | Phase A 7th Voltage Magnitude Harmonics | float | 2 | R
0x223E | 0x223F | 8766 | 8767 | MAG_200MS_HAR_V_7th_b_% | Phase B 7th Voltage Magnitude Harmonics | float | 2 | R
0x2240 | 0x2241 | 8768 | 8769 | MAG_200MS_HAR_V_7th_c_% | Phase C 7th Voltage Magnitude Harmonics | float | 2 | R
0x2242 | 0x2243 | 8770 | 8771 | MAG_200MS_HAR_I_7th_a_% | Phase A 7th Current Magnitude Harmonics | float | 2 | R
0x2244 | 0x2245 | 8772 | 8773 | MAG_200MS_HAR_I_7th_b_% | Phase B 7th Current Magnitude Harmonics | float | 2 | R
0x2246 | 0x2247 | 8774 | 8775 | MAG_200MS_HAR_I_7th_c_% | Phase C 7th Current Magnitude Harmonics | float | 2 | R
0x2248 | 0x2249 | 8776 | 8777 | MAG_200MS_HAR_I_7th_n_% | Phase N 7th Current Magnitude Harmonics | float | 2 | R
0x224A | 0x224B | 8778 | 8779 | MAG_200MS_HAR_V_8th_a_% | Phase A 8th Voltage Magnitude Harmonics | float | 2 | R
0x224C | 0x224D | 8780 | 8781 | MAG_200MS_HAR_V_8th_b_% | Phase B 8th Voltage Magnitude Harmonics | float | 2 | R
0x224E | 0x224F | 8782 | 8783 | MAG_200MS_HAR_V_8th_c_% | Phase C 8th Voltage Magnitude Harmonics | float | 2 | R
0x2250 | 0x2251 | 8784 | 8785 | MAG_200MS_HAR_I_8th_a_% | Phase A 8th Current Magnitude Harmonics | float | 2 | R
0x2252 | 0x2253 | 8786 | 8787 | MAG_200MS_HAR_I_8th_b_% | Phase B 8th Current Magnitude Harmonics | float | 2 | R
0x2254 | 0x2255 | 8788 | 8789 | MAG_200MS_HAR_I_8th_c_% | Phase C 8th Current Magnitude Harmonics | float | 2 | R
0x2256 | 0x2257 | 8790 | 8791 | MAG_200MS_HAR_I_8th_n_% | Phase N 8th Current Magnitude Harmonics | float | 2 | R
0x2258 | 0x2259 | 8792 | 8793 | MAG_200MS_HAR_V_9th_a_% | Phase A 9th Voltage Magnitude Harmonics | float | 2 | R
0x225A | 0x225B | 8794 | 8795 | MAG_200MS_HAR_V_9th_b_% | Phase B 9th Voltage Magnitude Harmonics | float | 2 | R
0x225C | 0x225D | 8796 | 8797 | MAG_200MS_HAR_V_9th_c_% | Phase C 9th Voltage Magnitude Harmonics | float | 2 | R
0x225E | 0x225F | 8798 | 8799 | MAG_200MS_HAR_I_9th_a_% | Phase A 9th Current Magnitude Harmonics | float | 2 | R
0x2260 | 0x2261 | 8800 | 8801 | MAG_200MS_HAR_I_9th_b_% | Phase B 9th Current Magnitude Harmonics | float | 2 | R
0x2262 | 0x2263 | 8802 | 8803 | MAG_200MS_HAR_I_9th_c_% | Phase C 9th Current Magnitude Harmonics | float | 2 | R
0x2264 | 0x2265 | 8804 | 8805 | MAG_200MS_HAR_I_9th_n_% | Phase N 9th Current Magnitude Harmonics | float | 2 | R
0x2266 | 0x2267 | 8806 | 8807 | MAG_200MS_HAR_V_10th_a_% | Phase A 10th Voltage Magnitude Harmonics | float | 2 | R
0x2268 | 0x2269 | 8808 | 8809 | MAG_200MS_HAR_V_10th_b_% | Phase B 10th Voltage Magnitude Harmonics | float | 2 | R
0x226A | 0x226B | 8810 | 8811 | MAG_200MS_HAR_V_10th_c_% | Phase C 10th Voltage Magnitude Harmonics | float | 2 | R
0x226C | 0x226D | 8812 | 8813 | MAG_200MS_HAR_I_10th_a_% | Phase A 10th Current Magnitude Harmonics | float | 2 | R
0x226E | 0x226F | 8814 | 8815 | MAG_200MS_HAR_I_10th_b_% | Phase B 10th Current Magnitude Harmonics | float | 2 | R
0x2270 | 0x2271 | 8816 | 8817 | MAG_200MS_HAR_I_10th_c_% | Phase C 10th Current Magnitude Harmonics | float | 2 | R
0x2272 | 0x2273 | 8818 | 8819 | MAG_200MS_HAR_I_10th_n_% | Phase N 10th Current Magnitude Harmonics | float | 2 | R
0x2274 | 0x2275 | 8820 | 8821 | MAG_200MS_HAR_V_11th_a_% | Phase A 11st Voltage Magnitude Harmonics | float | 2 | R
0x2276 | 0x2277 | 8822 | 8823 | MAG_200MS_HAR_V_11th_b_% | Phase B 11st Voltage Magnitude Harmonics | float | 2 | R
0x2278 | 0x2279 | 8824 | 8825 | MAG_200MS_HAR_V_11th_c_% | Phase C 11st Voltage Magnitude Harmonics | float | 2 | R
0x227A | 0x227B | 8826 | 8827 | MAG_200MS_HAR_I_11th_a_% | Phase A 11st Current Magnitude Harmonics | float | 2 | R
0x227C | 0x227D | 8828 | 8829 | MAG_200MS_HAR_I_11th_b_% | Phase B 11st Current Magnitude Harmonics | float | 2 | R
0x227E | 0x227F | 8830 | 8831 | MAG_200MS_HAR_I_11th_c_% | Phase C 11st Current Magnitude Harmonics | float | 2 | R
0x2280 | 0x2281 | 8832 | 8833 | MAG_200MS_HAR_I_11th_n_% | Phase N 11st Current Magnitude Harmonics | float | 2 | R
0x2282 | 0x2283 | 8834 | 8835 | MAG_200MS_HAR_V_12th_a_% | Phase A 12nd Voltage Magnitude Harmonics | float | 2 | R
0x2284 | 0x2285 | 8836 | 8837 | MAG_200MS_HAR_V_12th_b_% | Phase B 12nd Voltage Magnitude Harmonics | float | 2 | R
0x2286 | 0x2287 | 8838 | 8839 | MAG_200MS_HAR_V_12th_c_% | Phase C 12nd Voltage Magnitude Harmonics | float | 2 | R
0x2288 | 0x2289 | 8840 | 8841 | MAG_200MS_HAR_I_12th_a_% | Phase A 12nd Current Magnitude Harmonics | float | 2 | R
0x228A | 0x228B | 8842 | 8843 | MAG_200MS_HAR_I_12th_b_% | Phase B 12nd Current Magnitude Harmonics | float | 2 | R
0x228C | 0x228D | 8844 | 8845 | MAG_200MS_HAR_I_12th_c_% | Phase C 12nd Current Magnitude Harmonics | float | 2 | R
0x228E | 0x228F | 8846 | 8847 | MAG_200MS_HAR_I_12th_n_% | Phase N 12nd Current Magnitude Harmonics | float | 2 | R
0x2290 | 0x2291 | 8848 | 8849 | MAG_200MS_HAR_V_13th_a_% | Phase A 13rd Voltage Magnitude Harmonics | float | 2 | R
0x2292 | 0x2293 | 8850 | 8851 | MAG_200MS_HAR_V_13th_b_% | Phase B 13rd Voltage Magnitude Harmonics | float | 2 | R
0x2294 | 0x2295 | 8852 | 8853 | MAG_200MS_HAR_V_13th_c_% | Phase C 13rd Voltage Magnitude Harmonics | float | 2 | R
0x2296 | 0x2297 | 8854 | 8855 | MAG_200MS_HAR_I_13th_a_% | Phase A 13rd Current Magnitude Harmonics | float | 2 | R
0x2298 | 0x2299 | 8856 | 8857 | MAG_200MS_HAR_I_13th_b_% | Phase B 13rd Current Magnitude Harmonics | float | 2 | R
0x229A | 0x229B | 8858 | 8859 | MAG_200MS_HAR_I_13th_c_% | Phase C 13rd Current Magnitude Harmonics | float | 2 | R
0x229C | 0x229D | 8860 | 8861 | MAG_200MS_HAR_I_13th_n_% | Phase N 13rd Current Magnitude Harmonics | float | 2 | R
0x229E | 0x229F | 8862 | 8863 | MAG_200MS_HAR_V_14th_a_% | Phase A 14th Voltage Magnitude Harmonics | float | 2 | R
0x22A0 | 0x22A1 | 8864 | 8865 | MAG_200MS_HAR_V_14th_b_% | Phase B 14th Voltage Magnitude Harmonics | float | 2 | R
0x22A2 | 0x22A3 | 8866 | 8867 | MAG_200MS_HAR_V_14th_c_% | Phase C 14th Voltage Magnitude Harmonics | float | 2 | R
0x22A4 | 0x22A5 | 8868 | 8869 | MAG_200MS_HAR_I_14th_a_% | Phase A 14th Current Magnitude Harmonics | float | 2 | R
0x22A6 | 0x22A7 | 8870 | 8871 | MAG_200MS_HAR_I_14th_b_% | Phase B 14th Current Magnitude Harmonics | float | 2 | R
0x22A8 | 0x22A9 | 8872 | 8873 | MAG_200MS_HAR_I_14th_c_% | Phase C 14th Current Magnitude Harmonics | float | 2 | R
0x22AA | 0x22AB | 8874 | 8875 | MAG_200MS_HAR_I_14th_n_% | Phase N 14th Current Magnitude Harmonics | float | 2 | R
0x22AC | 0x22AD | 8876 | 8877 | MAG_200MS_HAR_V_15th_a_% | Phase A 15th Voltage Magnitude Harmonics | float | 2 | R
0x22AE | 0x22AF | 8878 | 8879 | MAG_200MS_HAR_V_15th_b_% | Phase B 15th Voltage Magnitude Harmonics | float | 2 | R
0x22B0 | 0x22B1 | 8880 | 8881 | MAG_200MS_HAR_V_15th_c_% | Phase C 15th Voltage Magnitude Harmonics | float | 2 | R
0x22B2 | 0x22B3 | 8882 | 8883 | MAG_200MS_HAR_I_15th_a_% | Phase A 15th Current Magnitude Harmonics | float | 2 | R
0x22B4 | 0x22B5 | 8884 | 8885 | MAG_200MS_HAR_I_15th_b_% | Phase B 15th Current Magnitude Harmonics | float | 2 | R
0x22B6 | 0x22B7 | 8886 | 8887 | MAG_200MS_HAR_I_15th_c_% | Phase C 15th Current Magnitude Harmonics | float | 2 | R
0x22B8 | 0x22B9 | 8888 | 8889 | MAG_200MS_HAR_I_15th_n_% | Phase N 15th Current Magnitude Harmonics | float | 2 | R
0x22BA | 0x22BB | 8890 | 8891 | MAG_200MS_HAR_V_16th_a_% | Phase A 16th Voltage Magnitude Harmonics | float | 2 | R
0x22BC | 0x22BD | 8892 | 8893 | MAG_200MS_HAR_V_16th_b_% | Phase B 16th Voltage Magnitude Harmonics | float | 2 | R
0x22BE | 0x22BF | 8894 | 8895 | MAG_200MS_HAR_V_16th_c_% | Phase C 16th Voltage Magnitude Harmonics | float | 2 | R
0x22C0 | 0x22C1 | 8896 | 8897 | MAG_200MS_HAR_I_16th_a_% | Phase A 16th Current Magnitude Harmonics | float | 2 | R
0x22C2 | 0x22C3 | 8898 | 8899 | MAG_200MS_HAR_I_16th_b_% | Phase B 16th Current Magnitude Harmonics | float | 2 | R
0x22C4 | 0x22C5 | 8900 | 8901 | MAG_200MS_HAR_I_16th_c_% | Phase C 16th Current Magnitude Harmonics | float | 2 | R
0x22C6 | 0x22C7 | 8902 | 8903 | MAG_200MS_HAR_I_16th_n_% | Phase N 16th Current Magnitude Harmonics | float | 2 | R
0x22C8 | 0x22C9 | 8904 | 8905 | MAG_200MS_HAR_V_17th_a_% | Phase A 17th Voltage Magnitude Harmonics | float | 2 | R
0x22CA | 0x22CB | 8906 | 8907 | MAG_200MS_HAR_V_17th_b_% | Phase B 17th Voltage Magnitude Harmonics | float | 2 | R
0x22CC | 0x22CD | 8908 | 8909 | MAG_200MS_HAR_V_17th_c_% | Phase C 17th Voltage Magnitude Harmonics | float | 2 | R
0x22CE | 0x22CF | 8910 | 8911 | MAG_200MS_HAR_I_17th_a_% | Phase A 17th Current Magnitude Harmonics | float | 2 | R
0x22D0 | 0x22D1 | 8912 | 8913 | MAG_200MS_HAR_I_17th_b_% | Phase B 17th Current Magnitude Harmonics | float | 2 | R
0x22D2 | 0x22D3 | 8914 | 8915 | MAG_200MS_HAR_I_17th_c_% | Phase C 17th Current Magnitude Harmonics | float | 2 | R
0x22D4 | 0x22D5 | 8916 | 8917 | MAG_200MS_HAR_I_17th_n_% | Phase N 17th Current Magnitude Harmonics | float | 2 | R
0x22D6 | 0x22D7 | 8918 | 8919 | MAG_200MS_HAR_V_18th_a_% | Phase A 18th Voltage Magnitude Harmonics | float | 2 | R
0x22D8 | 0x22D9 | 8920 | 8921 | MAG_200MS_HAR_V_18th_b_% | Phase B 18th Voltage Magnitude Harmonics | float | 2 | R
0x22DA | 0x22DB | 8922 | 8923 | MAG_200MS_HAR_V_18th_c_% | Phase C 18th Voltage Magnitude Harmonics | float | 2 | R
0x22DC | 0x22DD | 8924 | 8925 | MAG_200MS_HAR_I_18th_a_% | Phase A 18th Current Magnitude Harmonics | float | 2 | R
0x22DE | 0x22DF | 8926 | 8927 | MAG_200MS_HAR_I_18th_b_% | Phase B 18th Current Magnitude Harmonics | float | 2 | R
0x22E0 | 0x22E1 | 8928 | 8929 | MAG_200MS_HAR_I_18th_c_% | Phase C 18th Current Magnitude Harmonics | float | 2 | R
0x22E2 | 0x22E3 | 8930 | 8931 | MAG_200MS_HAR_I_18th_n_% | Phase N 18th Current Magnitude Harmonics | float | 2 | R
0x22E4 | 0x22E5 | 8932 | 8933 | MAG_200MS_HAR_V_19th_a_% | Phase A 19th Voltage Magnitude Harmonics | float | 2 | R
0x22E6 | 0x22E7 | 8934 | 8935 | MAG_200MS_HAR_V_19th_b_% | Phase B 19th Voltage Magnitude Harmonics | float | 2 | R
0x22E8 | 0x22E9 | 8936 | 8937 | MAG_200MS_HAR_V_19th_c_% | Phase C 19th Voltage Magnitude Harmonics | float | 2 | R
0x22EA | 0x22EB | 8938 | 8939 | MAG_200MS_HAR_I_19th_a_% | Phase A 19th Current Magnitude Harmonics | float | 2 | R
0x22EC | 0x22ED | 8940 | 8941 | MAG_200MS_HAR_I_19th_b_% | Phase B 19th Current Magnitude Harmonics | float | 2 | R
0x22EE | 0x22EF | 8942 | 8943 | MAG_200MS_HAR_I_19th_c_% | Phase C 19th Current Magnitude Harmonics | float | 2 | R
0x22F0 | 0x22F1 | 8944 | 8945 | MAG_200MS_HAR_I_19th_n_% | Phase N 19th Current Magnitude Harmonics | float | 2 | R
0x22F2 | 0x22F3 | 8946 | 8947 | MAG_200MS_HAR_V_20th_a_% | Phase A 20th Voltage Magnitude Harmonics | float | 2 | R
0x22F4 | 0x22F5 | 8948 | 8949 | MAG_200MS_HAR_V_20th_b_% | Phase B 20th Voltage Magnitude Harmonics | float | 2 | R
0x22F6 | 0x22F7 | 8950 | 8951 | MAG_200MS_HAR_V_20th_c_% | Phase C 20th Voltage Magnitude Harmonics | float | 2 | R
0x22F8 | 0x22F9 | 8952 | 8953 | MAG_200MS_HAR_I_20th_a_% | Phase A 20th Current Magnitude Harmonics | float | 2 | R
0x22FA | 0x22FB | 8954 | 8955 | MAG_200MS_HAR_I_20th_b_% | Phase B 20th Current Magnitude Harmonics | float | 2 | R
0x22FC | 0x22FD | 8956 | 8957 | MAG_200MS_HAR_I_20th_c_% | Phase C 20th Current Magnitude Harmonics | float | 2 | R
0x22FE | 0x22FF | 8958 | 8959 | MAG_200MS_HAR_I_20th_n_% | Phase N 20th Current Magnitude Harmonics | float | 2 | R
0x2300 | 0x2301 | 8960 | 8961 | MAG_200MS_HAR_V_21th_a_% | Phase A 21st Voltage Magnitude Harmonics | float | 2 | R
0x2302 | 0x2303 | 8962 | 8963 | MAG_200MS_HAR_V_21th_b_% | Phase B 21st Voltage Magnitude Harmonics | float | 2 | R
0x2304 | 0x2305 | 8964 | 8965 | MAG_200MS_HAR_V_21th_c_% | Phase C 21st Voltage Magnitude Harmonics | float | 2 | R
0x2306 | 0x2307 | 8966 | 8967 | MAG_200MS_HAR_I_21th_a_% | Phase A 21st Current Magnitude Harmonics | float | 2 | R
0x2308 | 0x2309 | 8968 | 8969 | MAG_200MS_HAR_I_21th_b_% | Phase B 21st Current Magnitude Harmonics | float | 2 | R
0x230A | 0x230B | 8970 | 8971 | MAG_200MS_HAR_I_21th_c_% | Phase C 21st Current Magnitude Harmonics | float | 2 | R
0x230C | 0x230D | 8972 | 8973 | MAG_200MS_HAR_I_21th_n_% | Phase N 21st Current Magnitude Harmonics | float | 2 | R
0x230E | 0x230F | 8974 | 8975 | MAG_200MS_HAR_V_22th_a_% | Phase A 22nd Voltage Magnitude Harmonics | float | 2 | R
0x2310 | 0x2311 | 8976 | 8977 | MAG_200MS_HAR_V_22th_b_% | Phase B 22nd Voltage Magnitude Harmonics | float | 2 | R
0x2312 | 0x2313 | 8978 | 8979 | MAG_200MS_HAR_V_22th_c_% | Phase C 22nd Voltage Magnitude Harmonics | float | 2 | R
0x2314 | 0x2315 | 8980 | 8981 | MAG_200MS_HAR_I_22th_a_% | Phase A 22nd Current Magnitude Harmonics | float | 2 | R
0x2316 | 0x2317 | 8982 | 8983 | MAG_200MS_HAR_I_22th_b_% | Phase B 22nd Current Magnitude Harmonics | float | 2 | R
0x2318 | 0x2319 | 8984 | 8985 | MAG_200MS_HAR_I_22th_c_% | Phase C 22nd Current Magnitude Harmonics | float | 2 | R
0x231A | 0x231B | 8986 | 8987 | MAG_200MS_HAR_I_22th_n_% | Phase N 22nd Current Magnitude Harmonics | float | 2 | R
0x231C | 0x231D | 8988 | 8989 | MAG_200MS_HAR_V_23th_a_% | Phase A 23rd Voltage Magnitude Harmonics | float | 2 | R
0x231E | 0x231F | 8990 | 8991 | MAG_200MS_HAR_V_23th_b_% | Phase B 23rd Voltage Magnitude Harmonics | float | 2 | R
0x2320 | 0x2321 | 8992 | 8993 | MAG_200MS_HAR_V_23th_c_% | Phase C 23rd Voltage Magnitude Harmonics | float | 2 | R
0x2322 | 0x2323 | 8994 | 8995 | MAG_200MS_HAR_I_23th_a_% | Phase A 23rd Current Magnitude Harmonics | float | 2 | R
0x2324 | 0x2325 | 8996 | 8997 | MAG_200MS_HAR_I_23th_b_% | Phase B 23rd Current Magnitude Harmonics | float | 2 | R
0x2326 | 0x2327 | 8998 | 8999 | MAG_200MS_HAR_I_23th_c_% | Phase C 23rd Current Magnitude Harmonics | float | 2 | R
0x2328 | 0x2329 | 9000 | 9001 | MAG_200MS_HAR_I_23th_n_% | Phase N 23rd Current Magnitude Harmonics | float | 2 | R
0x232A | 0x232B | 9002 | 9003 | MAG_200MS_HAR_V_24th_a_% | Phase A 24th Voltage Magnitude Harmonics | float | 2 | R
0x232C | 0x232D | 9004 | 9005 | MAG_200MS_HAR_V_24th_b_% | Phase B 24th Voltage Magnitude Harmonics | float | 2 | R
0x232E | 0x232F | 9006 | 9007 | MAG_200MS_HAR_V_24th_c_% | Phase C 24th Voltage Magnitude Harmonics | float | 2 | R
0x2330 | 0x2331 | 9008 | 9009 | MAG_200MS_HAR_I_24th_a_% | Phase A 24th Current Magnitude Harmonics | float | 2 | R
0x2332 | 0x2333 | 9010 | 9011 | MAG_200MS_HAR_I_24th_b_% | Phase B 24th Current Magnitude Harmonics | float | 2 | R
0x2334 | 0x2335 | 9012 | 9013 | MAG_200MS_HAR_I_24th_c_% | Phase C 24th Current Magnitude Harmonics | float | 2 | R
0x2336 | 0x2337 | 9014 | 9015 | MAG_200MS_HAR_I_24th_n_% | Phase N 24th Current Magnitude Harmonics | float | 2 | R
0x2338 | 0x2339 | 9016 | 9017 | MAG_200MS_HAR_V_25th_a_% | Phase A 25th Voltage Magnitude Harmonics | float | 2 | R
0x233A | 0x233B | 9018 | 9019 | MAG_200MS_HAR_V_25th_b_% | Phase B 25th Voltage Magnitude Harmonics | float | 2 | R
0x233C | 0x233D | 9020 | 9021 | MAG_200MS_HAR_V_25th_c_% | Phase C 25th Voltage Magnitude Harmonics | float | 2 | R
0x233E | 0x233F | 9022 | 9023 | MAG_200MS_HAR_I_25th_a_% | Phase A 25th Current Magnitude Harmonics | float | 2 | R
0x2340 | 0x2341 | 9024 | 9025 | MAG_200MS_HAR_I_25th_b_% | Phase B 25th Current Magnitude Harmonics | float | 2 | R
0x2342 | 0x2343 | 9026 | 9027 | MAG_200MS_HAR_I_25th_c_% | Phase C 25th Current Magnitude Harmonics | float | 2 | R
0x2344 | 0x2345 | 9028 | 9029 | MAG_200MS_HAR_I_25th_n_% | Phase N 25th Current Magnitude Harmonics | float | 2 | R
0x2346 | 0x2347 | 9030 | 9031 | MAG_200MS_HAR_V_26th_a_% | Phase A 26th Voltage Magnitude Harmonics | float | 2 | R
0x2348 | 0x2349 | 9032 | 9033 | MAG_200MS_HAR_V_26th_b_% | Phase B 26th Voltage Magnitude Harmonics | float | 2 | R
0x234A | 0x234B | 9034 | 9035 | MAG_200MS_HAR_V_26th_c_% | Phase C 26th Voltage Magnitude Harmonics | float | 2 | R
0x234C | 0x234D | 9036 | 9037 | MAG_200MS_HAR_I_26th_a_% | Phase A 26th Current Magnitude Harmonics | float | 2 | R
0x234E | 0x234F | 9038 | 9039 | MAG_200MS_HAR_I_26th_b_% | Phase B 26th Current Magnitude Harmonics | float | 2 | R
0x2350 | 0x2351 | 9040 | 9041 | MAG_200MS_HAR_I_26th_c_% | Phase C 26th Current Magnitude Harmonics | float | 2 | R
0x2352 | 0x2353 | 9042 | 9043 | MAG_200MS_HAR_I_26th_n_% | Phase N 26th Current Magnitude Harmonics | float | 2 | R
0x2354 | 0x2355 | 9044 | 9045 | MAG_200MS_HAR_V_27th_a_% | Phase A 27th Voltage Magnitude Harmonics | float | 2 | R
0x2356 | 0x2357 | 9046 | 9047 | MAG_200MS_HAR_V_27th_b_% | Phase B 27th Voltage Magnitude Harmonics | float | 2 | R
0x2358 | 0x2359 | 9048 | 9049 | MAG_200MS_HAR_V_27th_c_% | Phase C 27th Voltage Magnitude Harmonics | float | 2 | R
0x235A | 0x235B | 9050 | 9051 | MAG_200MS_HAR_I_27th_a_% | Phase A 27th Current Magnitude Harmonics | float | 2 | R
0x235C | 0x235D | 9052 | 9053 | MAG_200MS_HAR_I_27th_b_% | Phase B 27th Current Magnitude Harmonics | float | 2 | R
0x235E | 0x235F | 9054 | 9055 | MAG_200MS_HAR_I_27th_c_% | Phase C 27th Current Magnitude Harmonics | float | 2 | R
0x2360 | 0x2361 | 9056 | 9057 | MAG_200MS_HAR_I_27th_n_% | Phase N 27th Current Magnitude Harmonics | float | 2 | R
0x2362 | 0x2363 | 9058 | 9059 | MAG_200MS_HAR_V_28th_a_% | Phase A 28th Voltage Magnitude Harmonics | float | 2 | R
0x2364 | 0x2365 | 9060 | 9061 | MAG_200MS_HAR_V_28th_b_% | Phase B 28th Voltage Magnitude Harmonics | float | 2 | R
0x2366 | 0x2367 | 9062 | 9063 | MAG_200MS_HAR_V_28th_c_% | Phase C 28th Voltage Magnitude Harmonics | float | 2 | R
0x2368 | 0x2369 | 9064 | 9065 | MAG_200MS_HAR_I_28th_a_% | Phase A 28th Current Magnitude Harmonics | float | 2 | R
0x236A | 0x236B | 9066 | 9067 | MAG_200MS_HAR_I_28th_b_% | Phase B 28th Current Magnitude Harmonics | float | 2 | R
0x236C | 0x236D | 9068 | 9069 | MAG_200MS_HAR_I_28th_c_% | Phase C 28th Current Magnitude Harmonics | float | 2 | R
0x236E | 0x236F | 9070 | 9071 | MAG_200MS_HAR_I_28th_n_% | Phase N 28th Current Magnitude Harmonics | float | 2 | R
0x2370 | 0x2371 | 9072 | 9073 | MAG_200MS_HAR_V_29th_a_% | Phase A 29th Voltage Magnitude Harmonics | float | 2 | R
0x2372 | 0x2373 | 9074 | 9075 | MAG_200MS_HAR_V_29th_b_% | Phase B 29th Voltage Magnitude Harmonics | float | 2 | R
0x2374 | 0x2375 | 9076 | 9077 | MAG_200MS_HAR_V_29th_c_% | Phase C 29th Voltage Magnitude Harmonics | float | 2 | R
0x2376 | 0x2377 | 9078 | 9079 | MAG_200MS_HAR_I_29th_a_% | Phase A 29th Current Magnitude Harmonics | float | 2 | R
0x2378 | 0x2379 | 9080 | 9081 | MAG_200MS_HAR_I_29th_b_% | Phase B 29th Current Magnitude Harmonics | float | 2 | R
0x237A | 0x237B | 9082 | 9083 | MAG_200MS_HAR_I_29th_c_% | Phase C 29th Current Magnitude Harmonics | float | 2 | R
0x237C | 0x237D | 9084 | 9085 | MAG_200MS_HAR_I_29th_n_% | Phase N 29th Current Magnitude Harmonics | float | 2 | R
0x237E | 0x237F | 9086 | 9087 | MAG_200MS_HAR_V_30th_a_% | Phase A 30th Voltage Magnitude Harmonics | float | 2 | R
0x2380 | 0x2381 | 9088 | 9089 | MAG_200MS_HAR_V_30th_b_% | Phase B 30th Voltage Magnitude Harmonics | float | 2 | R
0x2382 | 0x2383 | 9090 | 9091 | MAG_200MS_HAR_V_30th_c_% | Phase C 30th Voltage Magnitude Harmonics | float | 2 | R
0x2384 | 0x2385 | 9092 | 9093 | MAG_200MS_HAR_I_30th_a_% | Phase A 30th Current Magnitude Harmonics | float | 2 | R
0x2386 | 0x2387 | 9094 | 9095 | MAG_200MS_HAR_I_30th_b_% | Phase B 30th Current Magnitude Harmonics | float | 2 | R
0x2388 | 0x2389 | 9096 | 9097 | MAG_200MS_HAR_I_30th_c_% | Phase C 30th Current Magnitude Harmonics | float | 2 | R
0x238A | 0x238B | 9098 | 9099 | MAG_200MS_HAR_I_30th_n_% | Phase N 30th Current Magnitude Harmonics | float | 2 | R
0x238C | 0x238D | 9100 | 9101 | MAG_200MS_HAR_V_31th_a_% | Phase A 31st Voltage Magnitude Harmonics | float | 2 | R
0x238E | 0x238F | 9102 | 9103 | MAG_200MS_HAR_V_31th_b_% | Phase B 31st Voltage Magnitude Harmonics | float | 2 | R
0x2390 | 0x2391 | 9104 | 9105 | MAG_200MS_HAR_V_31th_c_% | Phase C 31st Voltage Magnitude Harmonics | float | 2 | R
0x2392 | 0x2393 | 9106 | 9107 | MAG_200MS_HAR_I_31th_a_% | Phase A 31st Current Magnitude Harmonics | float | 2 | R
0x2394 | 0x2395 | 9108 | 9109 | MAG_200MS_HAR_I_31th_b_% | Phase B 31st Current Magnitude Harmonics | float | 2 | R
0x2396 | 0x2397 | 9110 | 9111 | MAG_200MS_HAR_I_31th_c_% | Phase C 31st Current Magnitude Harmonics | float | 2 | R
0x2398 | 0x2399 | 9112 | 9113 | MAG_200MS_HAR_I_31th_n_% | Phase N 31st Current Magnitude Harmonics | float | 2 | R
0x239A | 0x239B | 9114 | 9115 | MAG_200MS_HAR_V_32th_a_% | Phase A 32nd Voltage Magnitude Harmonics | float | 2 | R
0x239C | 0x239D | 9116 | 9117 | MAG_200MS_HAR_V_32th_b_% | Phase B 32nd Voltage Magnitude Harmonics | float | 2 | R
0x239E | 0x239F | 9118 | 9119 | MAG_200MS_HAR_V_32th_c_% | Phase C 32nd Voltage Magnitude Harmonics | float | 2 | R
0x23A0 | 0x23A1 | 9120 | 9121 | MAG_200MS_HAR_I_32th_a_% | Phase A 32nd Current Magnitude Harmonics | float | 2 | R
0x23A2 | 0x23A3 | 9122 | 9123 | MAG_200MS_HAR_I_32th_b_% | Phase B 32nd Current Magnitude Harmonics | float | 2 | R
0x23A4 | 0x23A5 | 9124 | 9125 | MAG_200MS_HAR_I_32th_c_% | Phase C 32nd Current Magnitude Harmonics | float | 2 | R
0x23A6 | 0x23A7 | 9126 | 9127 | MAG_200MS_HAR_I_32th_n_% | Phase N 32nd Current Magnitude Harmonics | float | 2 | R
0x23A8 | 0x23A9 | 9128 | 9129 | MAG_200MS_HAR_V_33th_a_% | Phase A 33rd Voltage Magnitude Harmonics | float | 2 | R
0x23AA | 0x23AB | 9130 | 9131 | MAG_200MS_HAR_V_33th_b_% | Phase B 33rd Voltage Magnitude Harmonics | float | 2 | R
0x23AC | 0x23AD | 9132 | 9133 | MAG_200MS_HAR_V_33th_c_% | Phase C 33rd Voltage Magnitude Harmonics | float | 2 | R
0x23AE | 0x23AF | 9134 | 9135 | MAG_200MS_HAR_I_33th_a_% | Phase A 33rd Current Magnitude Harmonics | float | 2 | R
0x23B0 | 0x23B1 | 9136 | 9137 | MAG_200MS_HAR_I_33th_b_% | Phase B 33rd Current Magnitude Harmonics | float | 2 | R
0x23B2 | 0x23B3 | 9138 | 9139 | MAG_200MS_HAR_I_33th_c_% | Phase C 33rd Current Magnitude Harmonics | float | 2 | R
0x23B4 | 0x23B5 | 9140 | 9141 | MAG_200MS_HAR_I_33th_n_% | Phase N 33rd Current Magnitude Harmonics | float | 2 | R
0x23B6 | 0x23B7 | 9142 | 9143 | MAG_200MS_HAR_V_34th_a_% | Phase A 34th Voltage Magnitude Harmonics | float | 2 | R
0x23B8 | 0x23B9 | 9144 | 9145 | MAG_200MS_HAR_V_34th_b_% | Phase B 34th Voltage Magnitude Harmonics | float | 2 | R
0x23BA | 0x23BB | 9146 | 9147 | MAG_200MS_HAR_V_34th_c_% | Phase C 34th Voltage Magnitude Harmonics | float | 2 | R
0x23BC | 0x23BD | 9148 | 9149 | MAG_200MS_HAR_I_34th_a_% | Phase A 34th Current Magnitude Harmonics | float | 2 | R
0x23BE | 0x23BF | 9150 | 9151 | MAG_200MS_HAR_I_34th_b_% | Phase B 34th Current Magnitude Harmonics | float | 2 | R
0x23C0 | 0x23C1 | 9152 | 9153 | MAG_200MS_HAR_I_34th_c_% | Phase C 34th Current Magnitude Harmonics | float | 2 | R
0x23C2 | 0x23C3 | 9154 | 9155 | MAG_200MS_HAR_I_34th_n_% | Phase N 34th Current Magnitude Harmonics | float | 2 | R
0x23C4 | 0x23C5 | 9156 | 9157 | MAG_200MS_HAR_V_35th_a_% | Phase A 35th Voltage Magnitude Harmonics | float | 2 | R
0x23C6 | 0x23C7 | 9158 | 9159 | MAG_200MS_HAR_V_35th_b_% | Phase B 35th Voltage Magnitude Harmonics | float | 2 | R
0x23C8 | 0x23C9 | 9160 | 9161 | MAG_200MS_HAR_V_35th_c_% | Phase C 35th Voltage Magnitude Harmonics | float | 2 | R
0x23CA | 0x23CB | 9162 | 9163 | MAG_200MS_HAR_I_35th_a_% | Phase A 35th Current Magnitude Harmonics | float | 2 | R
0x23CC | 0x23CD | 9164 | 9165 | MAG_200MS_HAR_I_35th_b_% | Phase B 35th Current Magnitude Harmonics | float | 2 | R
0x23CE | 0x23CF | 9166 | 9167 | MAG_200MS_HAR_I_35th_c_% | Phase C 35th Current Magnitude Harmonics | float | 2 | R
0x23D0 | 0x23D1 | 9168 | 9169 | MAG_200MS_HAR_I_35th_n_% | Phase N 35th Current Magnitude Harmonics | float | 2 | R
0x23D2 | 0x23D3 | 9170 | 9171 | MAG_200MS_HAR_V_36th_a_% | Phase A 36th Voltage Magnitude Harmonics | float | 2 | R
0x23D4 | 0x23D5 | 9172 | 9173 | MAG_200MS_HAR_V_36th_b_% | Phase B 36th Voltage Magnitude Harmonics | float | 2 | R
0x23D6 | 0x23D7 | 9174 | 9175 | MAG_200MS_HAR_V_36th_c_% | Phase C 36th Voltage Magnitude Harmonics | float | 2 | R
0x23D8 | 0x23D9 | 9176 | 9177 | MAG_200MS_HAR_I_36th_a_% | Phase A 36th Current Magnitude Harmonics | float | 2 | R
0x23DA | 0x23DB | 9178 | 9179 | MAG_200MS_HAR_I_36th_b_% | Phase B 36th Current Magnitude Harmonics | float | 2 | R
0x23DC | 0x23DD | 9180 | 9181 | MAG_200MS_HAR_I_36th_c_% | Phase C 36th Current Magnitude Harmonics | float | 2 | R
0x23DE | 0x23DF | 9182 | 9183 | MAG_200MS_HAR_I_36th_n_% | Phase N 36th Current Magnitude Harmonics | float | 2 | R
0x23E0 | 0x23E1 | 9184 | 9185 | MAG_200MS_HAR_V_37th_a_% | Phase A 37th Voltage Magnitude Harmonics | float | 2 | R
0x23E2 | 0x23E3 | 9186 | 9187 | MAG_200MS_HAR_V_37th_b_% | Phase B 37th Voltage Magnitude Harmonics | float | 2 | R
0x23E4 | 0x23E5 | 9188 | 9189 | MAG_200MS_HAR_V_37th_c_% | Phase C 37th Voltage Magnitude Harmonics | float | 2 | R
0x23E6 | 0x23E7 | 9190 | 9191 | MAG_200MS_HAR_I_37th_a_% | Phase A 37th Current Magnitude Harmonics | float | 2 | R
0x23E8 | 0x23E9 | 9192 | 9193 | MAG_200MS_HAR_I_37th_b_% | Phase B 37th Current Magnitude Harmonics | float | 2 | R
0x23EA | 0x23EB | 9194 | 9195 | MAG_200MS_HAR_I_37th_c_% | Phase C 37th Current Magnitude Harmonics | float | 2 | R
0x23EC | 0x23ED | 9196 | 9197 | MAG_200MS_HAR_I_37th_n_% | Phase N 37th Current Magnitude Harmonics | float | 2 | R
0x23EE | 0x23EF | 9198 | 9199 | MAG_200MS_HAR_V_38th_a_% | Phase A 38th Voltage Magnitude Harmonics | float | 2 | R
0x23F0 | 0x23F1 | 9200 | 9201 | MAG_200MS_HAR_V_38th_b_% | Phase B 38th Voltage Magnitude Harmonics | float | 2 | R
0x23F2 | 0x23F3 | 9202 | 9203 | MAG_200MS_HAR_V_38th_c_% | Phase C 38th Voltage Magnitude Harmonics | float | 2 | R
0x23F4 | 0x23F5 | 9204 | 9205 | MAG_200MS_HAR_I_38th_a_% | Phase A 38th Current Magnitude Harmonics | float | 2 | R
0x23F6 | 0x23F7 | 9206 | 9207 | MAG_200MS_HAR_I_38th_b_% | Phase B 38th Current Magnitude Harmonics | float | 2 | R
0x23F8 | 0x23F9 | 9208 | 9209 | MAG_200MS_HAR_I_38th_c_% | Phase C 38th Current Magnitude Harmonics | float | 2 | R
0x23FA | 0x23FB | 9210 | 9211 | MAG_200MS_HAR_I_38th_n_% | Phase N 38th Current Magnitude Harmonics | float | 2 | R
0x23FC | 0x23FD | 9212 | 9213 | MAG_200MS_HAR_V_39th_a_% | Phase A 39th Voltage Magnitude Harmonics | float | 2 | R
0x23FE | 0x23FF | 9214 | 9215 | MAG_200MS_HAR_V_39th_b_% | Phase B 39th Voltage Magnitude Harmonics | float | 2 | R
0x2400 | 0x2401 | 9216 | 9217 | MAG_200MS_HAR_V_39th_c_% | Phase C 39th Voltage Magnitude Harmonics | float | 2 | R
0x2402 | 0x2403 | 9218 | 9219 | MAG_200MS_HAR_I_39th_a_% | Phase A 39th Current Magnitude Harmonics | float | 2 | R
0x2404 | 0x2405 | 9220 | 9221 | MAG_200MS_HAR_I_39th_b_% | Phase B 39th Current Magnitude Harmonics | float | 2 | R
0x2406 | 0x2407 | 9222 | 9223 | MAG_200MS_HAR_I_39th_c_% | Phase C 39th Current Magnitude Harmonics | float | 2 | R
0x2408 | 0x2409 | 9224 | 9225 | MAG_200MS_HAR_I_39th_n_% | Phase N 39th Current Magnitude Harmonics | float | 2 | R
0x240A | 0x240B | 9226 | 9227 | MAG_200MS_HAR_V_40th_a_% | Phase A 40th Voltage Magnitude Harmonics | float | 2 | R
0x240C | 0x240D | 9228 | 9229 | MAG_200MS_HAR_V_40th_b_% | Phase B 40th Voltage Magnitude Harmonics | float | 2 | R
0x240E | 0x240F | 9230 | 9231 | MAG_200MS_HAR_V_40th_c_% | Phase C 40th Voltage Magnitude Harmonics | float | 2 | R
0x2410 | 0x2411 | 9232 | 9233 | MAG_200MS_HAR_I_40th_a_% | Phase A 40th Current Magnitude Harmonics | float | 2 | R
0x2412 | 0x2413 | 9234 | 9235 | MAG_200MS_HAR_I_40th_b_% | Phase B 40th Current Magnitude Harmonics | float | 2 | R
0x2414 | 0x2415 | 9236 | 9237 | MAG_200MS_HAR_I_40th_c_% | Phase C 40th Current Magnitude Harmonics | float | 2 | R
0x2416 | 0x2417 | 9238 | 9239 | MAG_200MS_HAR_I_40th_n_% | Phase N 40th Current Magnitude Harmonics | float | 2 | R
0x2418 | 0x2419 | 9240 | 9241 | MAG_200MS_HAR_V_41th_a_% | Phase A 41st Voltage Magnitude Harmonics | float | 2 | R
0x241A | 0x241B | 9242 | 9243 | MAG_200MS_HAR_V_41th_b_% | Phase B 41st Voltage Magnitude Harmonics | float | 2 | R
0x241C | 0x241D | 9244 | 9245 | MAG_200MS_HAR_V_41th_c_% | Phase C 41st Voltage Magnitude Harmonics | float | 2 | R
0x241E | 0x241F | 9246 | 9247 | MAG_200MS_HAR_I_41th_a_% | Phase A 41st Current Magnitude Harmonics | float | 2 | R
0x2420 | 0x2421 | 9248 | 9249 | MAG_200MS_HAR_I_41th_b_% | Phase B 41st Current Magnitude Harmonics | float | 2 | R
0x2422 | 0x2423 | 9250 | 9251 | MAG_200MS_HAR_I_41th_c_% | Phase C 41st Current Magnitude Harmonics | float | 2 | R
0x2424 | 0x2425 | 9252 | 9253 | MAG_200MS_HAR_I_41th_n_% | Phase N 41st Current Magnitude Harmonics | float | 2 | R
0x2426 | 0x2427 | 9254 | 9255 | MAG_200MS_HAR_V_42th_a_% | Phase A 42nd Voltage Magnitude Harmonics | float | 2 | R
0x2428 | 0x2429 | 9256 | 9257 | MAG_200MS_HAR_V_42th_b_% | Phase B 42nd Voltage Magnitude Harmonics | float | 2 | R
0x242A | 0x242B | 9258 | 9259 | MAG_200MS_HAR_V_42th_c_% | Phase C 42nd Voltage Magnitude Harmonics | float | 2 | R
0x242C | 0x242D | 9260 | 9261 | MAG_200MS_HAR_I_42th_a_% | Phase A 42nd Current Magnitude Harmonics | float | 2 | R
0x242E | 0x242F | 9262 | 9263 | MAG_200MS_HAR_I_42th_b_% | Phase B 42nd Current Magnitude Harmonics | float | 2 | R
0x2430 | 0x2431 | 9264 | 9265 | MAG_200MS_HAR_I_42th_c_% | Phase C 42nd Current Magnitude Harmonics | float | 2 | R
0x2432 | 0x2433 | 9266 | 9267 | MAG_200MS_HAR_I_42th_n_% | Phase N 42nd Current Magnitude Harmonics | float | 2 | R
0x2434 | 0x2435 | 9268 | 9269 | MAG_200MS_HAR_V_43th_a_% | Phase A 43rd Voltage Magnitude Harmonics | float | 2 | R
0x2436 | 0x2437 | 9270 | 9271 | MAG_200MS_HAR_V_43th_b_% | Phase B 43rd Voltage Magnitude Harmonics | float | 2 | R
0x2438 | 0x2439 | 9272 | 9273 | MAG_200MS_HAR_V_43th_c_% | Phase C 43rd Voltage Magnitude Harmonics | float | 2 | R
0x243A | 0x243B | 9274 | 9275 | MAG_200MS_HAR_I_43th_a_% | Phase A 43rd Current Magnitude Harmonics | float | 2 | R
0x243C | 0x243D | 9276 | 9277 | MAG_200MS_HAR_I_43th_b_% | Phase B 43rd Current Magnitude Harmonics | float | 2 | R
0x243E | 0x243F | 9278 | 9279 | MAG_200MS_HAR_I_43th_c_% | Phase C 43rd Current Magnitude Harmonics | float | 2 | R
0x2440 | 0x2441 | 9280 | 9281 | MAG_200MS_HAR_I_43th_n_% | Phase N 43rd Current Magnitude Harmonics | float | 2 | R
0x2442 | 0x2443 | 9282 | 9283 | MAG_200MS_HAR_V_44th_a_% | Phase A 44th Voltage Magnitude Harmonics | float | 2 | R
0x2444 | 0x2445 | 9284 | 9285 | MAG_200MS_HAR_V_44th_b_% | Phase B 44th Voltage Magnitude Harmonics | float | 2 | R
0x2446 | 0x2447 | 9286 | 9287 | MAG_200MS_HAR_V_44th_c_% | Phase C 44th Voltage Magnitude Harmonics | float | 2 | R
0x2448 | 0x2449 | 9288 | 9289 | MAG_200MS_HAR_I_44th_a_% | Phase A 44th Current Magnitude Harmonics | float | 2 | R
0x244A | 0x244B | 9290 | 9291 | MAG_200MS_HAR_I_44th_b_% | Phase B 44th Current Magnitude Harmonics | float | 2 | R
0x244C | 0x244D | 9292 | 9293 | MAG_200MS_HAR_I_44th_c_% | Phase C 44th Current Magnitude Harmonics | float | 2 | R
0x244E | 0x244F | 9294 | 9295 | MAG_200MS_HAR_I_44th_n_% | Phase N 44th Current Magnitude Harmonics | float | 2 | R
0x2450 | 0x2451 | 9296 | 9297 | MAG_200MS_HAR_V_45th_a_% | Phase A 45th Voltage Magnitude Harmonics | float | 2 | R
0x2452 | 0x2453 | 9298 | 9299 | MAG_200MS_HAR_V_45th_b_% | Phase B 45th Voltage Magnitude Harmonics | float | 2 | R
0x2454 | 0x2455 | 9300 | 9301 | MAG_200MS_HAR_V_45th_c_% | Phase C 45th Voltage Magnitude Harmonics | float | 2 | R
0x2456 | 0x2457 | 9302 | 9303 | MAG_200MS_HAR_I_45th_a_% | Phase A 45th Current Magnitude Harmonics | float | 2 | R
0x2458 | 0x2459 | 9304 | 9305 | MAG_200MS_HAR_I_45th_b_% | Phase B 45th Current Magnitude Harmonics | float | 2 | R
0x245A | 0x245B | 9306 | 9307 | MAG_200MS_HAR_I_45th_c_% | Phase C 45th Current Magnitude Harmonics | float | 2 | R
0x245C | 0x245D | 9308 | 9309 | MAG_200MS_HAR_I_45th_n_% | Phase N 45th Current Magnitude Harmonics | float | 2 | R
0x245E | 0x245F | 9310 | 9311 | MAG_200MS_HAR_V_46th_a_% | Phase A 46th Voltage Magnitude Harmonics | float | 2 | R
0x2460 | 0x2461 | 9312 | 9313 | MAG_200MS_HAR_V_46th_b_% | Phase B 46th Voltage Magnitude Harmonics | float | 2 | R
0x2462 | 0x2463 | 9314 | 9315 | MAG_200MS_HAR_V_46th_c_% | Phase C 46th Voltage Magnitude Harmonics | float | 2 | R
0x2464 | 0x2465 | 9316 | 9317 | MAG_200MS_HAR_I_46th_a_% | Phase A 46th Current Magnitude Harmonics | float | 2 | R
0x2466 | 0x2467 | 9318 | 9319 | MAG_200MS_HAR_I_46th_b_% | Phase B 46th Current Magnitude Harmonics | float | 2 | R
0x2468 | 0x2469 | 9320 | 9321 | MAG_200MS_HAR_I_46th_c_% | Phase C 46th Current Magnitude Harmonics | float | 2 | R
0x246A | 0x246B | 9322 | 9323 | MAG_200MS_HAR_I_46th_n_% | Phase N 46th Current Magnitude Harmonics | float | 2 | R
0x246C | 0x246D | 9324 | 9325 | MAG_200MS_HAR_V_47th_a_% | Phase A 47th Voltage Magnitude Harmonics | float | 2 | R
0x246E | 0x246F | 9326 | 9327 | MAG_200MS_HAR_V_47th_b_% | Phase B 47th Voltage Magnitude Harmonics | float | 2 | R
0x2470 | 0x2471 | 9328 | 9329 | MAG_200MS_HAR_V_47th_c_% | Phase C 47th Voltage Magnitude Harmonics | float | 2 | R
0x2472 | 0x2473 | 9330 | 9331 | MAG_200MS_HAR_I_47th_a_% | Phase A 47th Current Magnitude Harmonics | float | 2 | R
0x2474 | 0x2475 | 9332 | 9333 | MAG_200MS_HAR_I_47th_b_% | Phase B 47th Current Magnitude Harmonics | float | 2 | R
0x2476 | 0x2477 | 9334 | 9335 | MAG_200MS_HAR_I_47th_c_% | Phase C 47th Current Magnitude Harmonics | float | 2 | R
0x2478 | 0x2479 | 9336 | 9337 | MAG_200MS_HAR_I_47th_n_% | Phase N 47th Current Magnitude Harmonics | float | 2 | R
0x247A | 0x247B | 9338 | 9339 | MAG_200MS_HAR_V_48th_a_% | Phase A 48th Voltage Magnitude Harmonics | float | 2 | R
0x247C | 0x247D | 9340 | 9341 | MAG_200MS_HAR_V_48th_b_% | Phase B 48th Voltage Magnitude Harmonics | float | 2 | R
0x247E | 0x247F | 9342 | 9343 | MAG_200MS_HAR_V_48th_c_% | Phase C 48th Voltage Magnitude Harmonics | float | 2 | R
0x2480 | 0x2481 | 9344 | 9345 | MAG_200MS_HAR_I_48th_a_% | Phase A 48th Current Magnitude Harmonics | float | 2 | R
0x2482 | 0x2483 | 9346 | 9347 | MAG_200MS_HAR_I_48th_b_% | Phase B 48th Current Magnitude Harmonics | float | 2 | R
0x2484 | 0x2485 | 9348 | 9349 | MAG_200MS_HAR_I_48th_c_% | Phase C 48th Current Magnitude Harmonics | float | 2 | R
0x2486 | 0x2487 | 9350 | 9351 | MAG_200MS_HAR_I_48th_n_% | Phase N 48th Current Magnitude Harmonics | float | 2 | R
0x2488 | 0x2489 | 9352 | 9353 | MAG_200MS_HAR_V_49th_a_% | Phase A 49th Voltage Magnitude Harmonics | float | 2 | R
0x248A | 0x248B | 9354 | 9355 | MAG_200MS_HAR_V_49th_b_% | Phase B 49th Voltage Magnitude Harmonics | float | 2 | R
0x248C | 0x248D | 9356 | 9357 | MAG_200MS_HAR_V_49th_c_% | Phase C 49th Voltage Magnitude Harmonics | float | 2 | R
0x248E | 0x248F | 9358 | 9359 | MAG_200MS_HAR_I_49th_a_% | Phase A 49th Current Magnitude Harmonics | float | 2 | R
0x2490 | 0x2491 | 9360 | 9361 | MAG_200MS_HAR_I_49th_b_% | Phase B 49th Current Magnitude Harmonics | float | 2 | R
0x2492 | 0x2493 | 9362 | 9363 | MAG_200MS_HAR_I_49th_c_% | Phase C 49th Current Magnitude Harmonics | float | 2 | R
0x2494 | 0x2495 | 9364 | 9365 | MAG_200MS_HAR_I_49th_n_% | Phase N 49th Current Magnitude Harmonics | float | 2 | R
0x2496 | 0x2497 | 9366 | 9367 | MAG_200MS_HAR_V_50th_a_% | Phase A 50th Voltage Magnitude Harmonics | float | 2 | R
0x2498 | 0x2499 | 9368 | 9369 | MAG_200MS_HAR_V_50th_b_% | Phase B 50th Voltage Magnitude Harmonics | float | 2 | R
0x249A | 0x249B | 9370 | 9371 | MAG_200MS_HAR_V_50th_c_% | Phase C 50th Voltage Magnitude Harmonics | float | 2 | R
0x249C | 0x249D | 9372 | 9373 | MAG_200MS_HAR_I_50th_a_% | Phase A 50th Current Magnitude Harmonics | float | 2 | R
0x249E | 0x249F | 9374 | 9375 | MAG_200MS_HAR_I_50th_b_% | Phase B 50th Current Magnitude Harmonics | float | 2 | R
0x24A0 | 0x24A1 | 9376 | 9377 | MAG_200MS_HAR_I_50th_c_% | Phase C 50th Current Magnitude Harmonics | float | 2 | R
0x24A2 | 0x24A3 | 9378 | 9379 | MAG_200MS_HAR_I_50th_n_% | Phase N 50th Current Magnitude Harmonics | float | 2 | R
0x24A4 | 0x24A5 | 9380 | 9381 | MAG_200MS_HAR_V_51th_a_% | Phase A 51st Voltage Magnitude Harmonics | float | 2 | R
0x24A6 | 0x24A7 | 9382 | 9383 | MAG_200MS_HAR_V_51th_b_% | Phase B 51st Voltage Magnitude Harmonics | float | 2 | R
0x24A8 | 0x24A9 | 9384 | 9385 | MAG_200MS_HAR_V_51th_c_% | Phase C 51st Voltage Magnitude Harmonics | float | 2 | R
0x24AA | 0x24AB | 9386 | 9387 | MAG_200MS_HAR_I_51th_a_% | Phase A 51st Current Magnitude Harmonics | float | 2 | R
0x24AC | 0x24AD | 9388 | 9389 | MAG_200MS_HAR_I_51th_b_% | Phase B 51st Current Magnitude Harmonics | float | 2 | R
0x24AE | 0x24AF | 9390 | 9391 | MAG_200MS_HAR_I_51th_c_% | Phase C 51st Current Magnitude Harmonics | float | 2 | R
0x24B0 | 0x24B1 | 9392 | 9393 | MAG_200MS_HAR_I_51th_n_% | Phase N 51st Current Magnitude Harmonics | float | 2 | R
0x24B2 | 0x24B3 | 9394 | 9395 | MAG_200MS_HAR_V_52th_a_% | Phase A 52nd Voltage Magnitude Harmonics | float | 2 | R
0x24B4 | 0x24B5 | 9396 | 9397 | MAG_200MS_HAR_V_52th_b_% | Phase B 52nd Voltage Magnitude Harmonics | float | 2 | R
0x24B6 | 0x24B7 | 9398 | 9399 | MAG_200MS_HAR_V_52th_c_% | Phase C 52nd Voltage Magnitude Harmonics | float | 2 | R
0x24B8 | 0x24B9 | 9400 | 9401 | MAG_200MS_HAR_I_52th_a_% | Phase A 52nd Current Magnitude Harmonics | float | 2 | R
0x24BA | 0x24BB | 9402 | 9403 | MAG_200MS_HAR_I_52th_b_% | Phase B 52nd Current Magnitude Harmonics | float | 2 | R
0x24BC | 0x24BD | 9404 | 9405 | MAG_200MS_HAR_I_52th_c_% | Phase C 52nd Current Magnitude Harmonics | float | 2 | R
0x24BE | 0x24BF | 9406 | 9407 | MAG_200MS_HAR_I_52th_n_% | Phase N 52nd Current Magnitude Harmonics | float | 2 | R
0x24C0 | 0x24C1 | 9408 | 9409 | MAG_200MS_HAR_V_53th_a_% | Phase A 53rd Voltage Magnitude Harmonics | float | 2 | R
0x24C2 | 0x24C3 | 9410 | 9411 | MAG_200MS_HAR_V_53th_b_% | Phase B 53rd Voltage Magnitude Harmonics | float | 2 | R
0x24C4 | 0x24C5 | 9412 | 9413 | MAG_200MS_HAR_V_53th_c_% | Phase C 53rd Voltage Magnitude Harmonics | float | 2 | R
0x24C6 | 0x24C7 | 9414 | 9415 | MAG_200MS_HAR_I_53th_a_% | Phase A 53rd Current Magnitude Harmonics | float | 2 | R
0x24C8 | 0x24C9 | 9416 | 9417 | MAG_200MS_HAR_I_53th_b_% | Phase B 53rd Current Magnitude Harmonics | float | 2 | R
0x24CA | 0x24CB | 9418 | 9419 | MAG_200MS_HAR_I_53th_c_% | Phase C 53rd Current Magnitude Harmonics | float | 2 | R
0x24CC | 0x24CD | 9420 | 9421 | MAG_200MS_HAR_I_53th_n_% | Phase N 53rd Current Magnitude Harmonics | float | 2 | R
0x24CE | 0x24CF | 9422 | 9423 | MAG_200MS_HAR_V_54th_a_% | Phase A 54th Voltage Magnitude Harmonics | float | 2 | R
0x24D0 | 0x24D1 | 9424 | 9425 | MAG_200MS_HAR_V_54th_b_% | Phase B 54th Voltage Magnitude Harmonics | float | 2 | R
0x24D2 | 0x24D3 | 9426 | 9427 | MAG_200MS_HAR_V_54th_c_% | Phase C 54th Voltage Magnitude Harmonics | float | 2 | R
0x24D4 | 0x24D5 | 9428 | 9429 | MAG_200MS_HAR_I_54th_a_% | Phase A 54th Current Magnitude Harmonics | float | 2 | R
0x24D6 | 0x24D7 | 9430 | 9431 | MAG_200MS_HAR_I_54th_b_% | Phase B 54th Current Magnitude Harmonics | float | 2 | R
0x24D8 | 0x24D9 | 9432 | 9433 | MAG_200MS_HAR_I_54th_c_% | Phase C 54th Current Magnitude Harmonics | float | 2 | R
0x24DA | 0x24DB | 9434 | 9435 | MAG_200MS_HAR_I_54th_n_% | Phase N 54th Current Magnitude Harmonics | float | 2 | R
0x24DC | 0x24DD | 9436 | 9437 | MAG_200MS_HAR_V_55th_a_% | Phase A 55th Voltage Magnitude Harmonics | float | 2 | R
0x24DE | 0x24DF | 9438 | 9439 | MAG_200MS_HAR_V_55th_b_% | Phase B 55th Voltage Magnitude Harmonics | float | 2 | R
0x24E0 | 0x24E1 | 9440 | 9441 | MAG_200MS_HAR_V_55th_c_% | Phase C 55th Voltage Magnitude Harmonics | float | 2 | R
0x24E2 | 0x24E3 | 9442 | 9443 | MAG_200MS_HAR_I_55th_a_% | Phase A 55th Current Magnitude Harmonics | float | 2 | R
0x24E4 | 0x24E5 | 9444 | 9445 | MAG_200MS_HAR_I_55th_b_% | Phase B 55th Current Magnitude Harmonics | float | 2 | R
0x24E6 | 0x24E7 | 9446 | 9447 | MAG_200MS_HAR_I_55th_c_% | Phase C 55th Current Magnitude Harmonics | float | 2 | R
0x24E8 | 0x24E9 | 9448 | 9449 | MAG_200MS_HAR_I_55th_n_% | Phase N 55th Current Magnitude Harmonics | float | 2 | R
0x24EA | 0x24EB | 9450 | 9451 | MAG_200MS_HAR_V_56th_a_% | Phase A 56th Voltage Magnitude Harmonics | float | 2 | R
0x24EC | 0x24ED | 9452 | 9453 | MAG_200MS_HAR_V_56th_b_% | Phase B 56th Voltage Magnitude Harmonics | float | 2 | R
0x24EE | 0x24EF | 9454 | 9455 | MAG_200MS_HAR_V_56th_c_% | Phase C 56th Voltage Magnitude Harmonics | float | 2 | R
0x24F0 | 0x24F1 | 9456 | 9457 | MAG_200MS_HAR_I_56th_a_% | Phase A 56th Current Magnitude Harmonics | float | 2 | R
0x24F2 | 0x24F3 | 9458 | 9459 | MAG_200MS_HAR_I_56th_b_% | Phase B 56th Current Magnitude Harmonics | float | 2 | R
0x24F4 | 0x24F5 | 9460 | 9461 | MAG_200MS_HAR_I_56th_c_% | Phase C 56th Current Magnitude Harmonics | float | 2 | R
0x24F6 | 0x24F7 | 9462 | 9463 | MAG_200MS_HAR_I_56th_n_% | Phase N 56th Current Magnitude Harmonics | float | 2 | R
0x24F8 | 0x24F9 | 9464 | 9465 | MAG_200MS_HAR_V_57th_a_% | Phase A 57th Voltage Magnitude Harmonics | float | 2 | R
0x24FA | 0x24FB | 9466 | 9467 | MAG_200MS_HAR_V_57th_b_% | Phase B 57th Voltage Magnitude Harmonics | float | 2 | R
0x24FC | 0x24FD | 9468 | 9469 | MAG_200MS_HAR_V_57th_c_% | Phase C 57th Voltage Magnitude Harmonics | float | 2 | R
0x24FE | 0x24FF | 9470 | 9471 | MAG_200MS_HAR_I_57th_a_% | Phase A 57th Current Magnitude Harmonics | float | 2 | R
0x2500 | 0x2501 | 9472 | 9473 | MAG_200MS_HAR_I_57th_b_% | Phase B 57th Current Magnitude Harmonics | float | 2 | R
0x2502 | 0x2503 | 9474 | 9475 | MAG_200MS_HAR_I_57th_c_% | Phase C 57th Current Magnitude Harmonics | float | 2 | R
0x2504 | 0x2505 | 9476 | 9477 | MAG_200MS_HAR_I_57th_n_% | Phase N 57th Current Magnitude Harmonics | float | 2 | R
0x2506 | 0x2507 | 9478 | 9479 | MAG_200MS_HAR_V_58th_a_% | Phase A 58th Voltage Magnitude Harmonics | float | 2 | R
0x2508 | 0x2509 | 9480 | 9481 | MAG_200MS_HAR_V_58th_b_% | Phase B 58th Voltage Magnitude Harmonics | float | 2 | R
0x250A | 0x250B | 9482 | 9483 | MAG_200MS_HAR_V_58th_c_% | Phase C 58th Voltage Magnitude Harmonics | float | 2 | R
0x250C | 0x250D | 9484 | 9485 | MAG_200MS_HAR_I_58th_a_% | Phase A 58th Current Magnitude Harmonics | float | 2 | R
0x250E | 0x250F | 9486 | 9487 | MAG_200MS_HAR_I_58th_b_% | Phase B 58th Current Magnitude Harmonics | float | 2 | R
0x2510 | 0x2511 | 9488 | 9489 | MAG_200MS_HAR_I_58th_c_% | Phase C 58th Current Magnitude Harmonics | float | 2 | R
0x2512 | 0x2513 | 9490 | 9491 | MAG_200MS_HAR_I_58th_n_% | Phase N 58th Current Magnitude Harmonics | float | 2 | R
0x2514 | 0x2515 | 9492 | 9493 | MAG_200MS_HAR_V_59th_a_% | Phase A 59th Voltage Magnitude Harmonics | float | 2 | R
0x2516 | 0x2517 | 9494 | 9495 | MAG_200MS_HAR_V_59th_b_% | Phase B 59th Voltage Magnitude Harmonics | float | 2 | R
0x2518 | 0x2519 | 9496 | 9497 | MAG_200MS_HAR_V_59th_c_% | Phase C 59th Voltage Magnitude Harmonics | float | 2 | R
0x251A | 0x251B | 9498 | 9499 | MAG_200MS_HAR_I_59th_a_% | Phase A 59th Current Magnitude Harmonics | float | 2 | R
0x251C | 0x251D | 9500 | 9501 | MAG_200MS_HAR_I_59th_b_% | Phase B 59th Current Magnitude Harmonics | float | 2 | R
0x251E | 0x251F | 9502 | 9503 | MAG_200MS_HAR_I_59th_c_% | Phase C 59th Current Magnitude Harmonics | float | 2 | R
0x2520 | 0x2521 | 9504 | 9505 | MAG_200MS_HAR_I_59th_n_% | Phase N 59th Current Magnitude Harmonics | float | 2 | R
0x2522 | 0x2523 | 9506 | 9507 | MAG_200MS_HAR_V_60th_a_% | Phase A 60th Voltage Magnitude Harmonics | float | 2 | R
0x2524 | 0x2525 | 9508 | 9509 | MAG_200MS_HAR_V_60th_b_% | Phase B 60th Voltage Magnitude Harmonics | float | 2 | R
0x2526 | 0x2527 | 9510 | 9511 | MAG_200MS_HAR_V_60th_c_% | Phase C 60th Voltage Magnitude Harmonics | float | 2 | R
0x2528 | 0x2529 | 9512 | 9513 | MAG_200MS_HAR_I_60th_a_% | Phase A 60th Current Magnitude Harmonics | float | 2 | R
0x252A | 0x252B | 9514 | 9515 | MAG_200MS_HAR_I_60th_b_% | Phase B 60th Current Magnitude Harmonics | float | 2 | R
0x252C | 0x252D | 9516 | 9517 | MAG_200MS_HAR_I_60th_c_% | Phase C 60th Current Magnitude Harmonics | float | 2 | R
0x252E | 0x252F | 9518 | 9519 | MAG_200MS_HAR_I_60th_n_% | Phase N 60th Current Magnitude Harmonics | float | 2 | R
0x2530 | 0x2531 | 9520 | 9521 | MAG_200MS_HAR_V_61th_a_% | Phase A 61st Voltage Magnitude Harmonics | float | 2 | R
0x2532 | 0x2533 | 9522 | 9523 | MAG_200MS_HAR_V_61th_b_% | Phase B 61st Voltage Magnitude Harmonics | float | 2 | R
0x2534 | 0x2535 | 9524 | 9525 | MAG_200MS_HAR_V_61th_c_% | Phase C 61st Voltage Magnitude Harmonics | float | 2 | R
0x2536 | 0x2537 | 9526 | 9527 | MAG_200MS_HAR_I_61th_a_% | Phase A 61st Current Magnitude Harmonics | float | 2 | R
0x2538 | 0x2539 | 9528 | 9529 | MAG_200MS_HAR_I_61th_b_% | Phase B 61st Current Magnitude Harmonics | float | 2 | R
0x253A | 0x253B | 9530 | 9531 | MAG_200MS_HAR_I_61th_c_% | Phase C 61st Current Magnitude Harmonics | float | 2 | R
0x253C | 0x253D | 9532 | 9533 | MAG_200MS_HAR_I_61th_n_% | Phase N 61st Current Magnitude Harmonics | float | 2 | R
0x253E | 0x253F | 9534 | 9535 | MAG_200MS_HAR_V_62th_a_% | Phase A 62nd Voltage Magnitude Harmonics | float | 2 | R
0x2540 | 0x2541 | 9536 | 9537 | MAG_200MS_HAR_V_62th_b_% | Phase B 62nd Voltage Magnitude Harmonics | float | 2 | R
0x2542 | 0x2543 | 9538 | 9539 | MAG_200MS_HAR_V_62th_c_% | Phase C 62nd Voltage Magnitude Harmonics | float | 2 | R
0x2544 | 0x2545 | 9540 | 9541 | MAG_200MS_HAR_I_62th_a_% | Phase A 62nd Current Magnitude Harmonics | float | 2 | R
0x2546 | 0x2547 | 9542 | 9543 | MAG_200MS_HAR_I_62th_b_% | Phase B 62nd Current Magnitude Harmonics | float | 2 | R
0x2548 | 0x2549 | 9544 | 9545 | MAG_200MS_HAR_I_62th_c_% | Phase C 62nd Current Magnitude Harmonics | float | 2 | R
0x254A | 0x254B | 9546 | 9547 | MAG_200MS_HAR_I_62th_n_% | Phase N 62nd Current Magnitude Harmonics | float | 2 | R
0x254C | 0x254D | 9548 | 9549 | MAG_200MS_HAR_V_63th_a_% | Phase A 63rd Voltage Magnitude Harmonics | float | 2 | R
0x254E | 0x254F | 9550 | 9551 | MAG_200MS_HAR_V_63th_b_% | Phase B 63rd Voltage Magnitude Harmonics | float | 2 | R
0x2550 | 0x2551 | 9552 | 9553 | MAG_200MS_HAR_V_63th_c_% | Phase C 63rd Voltage Magnitude Harmonics | float | 2 | R
0x2552 | 0x2553 | 9554 | 9555 | MAG_200MS_HAR_I_63th_a_% | Phase A 63rd Current Magnitude Harmonics | float | 2 | R
0x2554 | 0x2555 | 9556 | 9557 | MAG_200MS_HAR_I_63th_b_% | Phase B 63rd Current Magnitude Harmonics | float | 2 | R
0x2556 | 0x2557 | 9558 | 9559 | MAG_200MS_HAR_I_63th_c_% | Phase C 63rd Current Magnitude Harmonics | float | 2 | R
0x2558 | 0x2559 | 9560 | 9561 | MAG_200MS_HAR_I_63th_n_% | Phase N 63rd Current Magnitude Harmonics | float | 2 | R
0x255A | 0x255B | 9562 | 9563 | MAG_200MS_HAR_V_64th_a_% | Phase A 64th Voltage Magnitude Harmonics | float | 2 | R
0x255C | 0x255D | 9564 | 9565 | MAG_200MS_HAR_V_64th_b_% | Phase B 64th Voltage Magnitude Harmonics | float | 2 | R
0x255E | 0x255F | 9566 | 9567 | MAG_200MS_HAR_V_64th_c_% | Phase C 64th Voltage Magnitude Harmonics | float | 2 | R
0x2560 | 0x2561 | 9568 | 9569 | MAG_200MS_HAR_I_64th_a_% | Phase A 64th Current Magnitude Harmonics | float | 2 | R
0x2562 | 0x2563 | 9570 | 9571 | MAG_200MS_HAR_I_64th_b_% | Phase B 64th Current Magnitude Harmonics | float | 2 | R
0x2564 | 0x2565 | 9572 | 9573 | MAG_200MS_HAR_I_64th_c_% | Phase C 64th Current Magnitude Harmonics | float | 2 | R
0x2566 | 0x2567 | 9574 | 9575 | MAG_200MS_HAR_I_64th_n_% | Phase N 64th Current Magnitude Harmonics | float | 2 | R
0x2568 | 0x2569 | 9576 | 9577 | MAG_200MS_HAR_V_65th_a_% | Phase A 65th Voltage Magnitude Harmonics | float | 2 | R
0x256A | 0x256B | 9578 | 9579 | MAG_200MS_HAR_V_65th_b_% | Phase B 65th Voltage Magnitude Harmonics | float | 2 | R
0x256C | 0x256D | 9580 | 9581 | MAG_200MS_HAR_V_65th_c_% | Phase C 65th Voltage Magnitude Harmonics | float | 2 | R
0x256E | 0x256F | 9582 | 9583 | MAG_200MS_HAR_I_65th_a_% | Phase A 65th Current Magnitude Harmonics | float | 2 | R
0x2570 | 0x2571 | 9584 | 9585 | MAG_200MS_HAR_I_65th_b_% | Phase B 65th Current Magnitude Harmonics | float | 2 | R
0x2572 | 0x2573 | 9586 | 9587 | MAG_200MS_HAR_I_65th_c_% | Phase C 65th Current Magnitude Harmonics | float | 2 | R
0x2574 | 0x2575 | 9588 | 9589 | MAG_200MS_HAR_I_65th_n_% | Phase N 65th Current Magnitude Harmonics | float | 2 | R
0x2576 | 0x2577 | 9590 | 9591 | MAG_200MS_HAR_V_66th_a_% | Phase A 66th Voltage Magnitude Harmonics | float | 2 | R
0x2578 | 0x2579 | 9592 | 9593 | MAG_200MS_HAR_V_66th_b_% | Phase B 66th Voltage Magnitude Harmonics | float | 2 | R
0x257A | 0x257B | 9594 | 9595 | MAG_200MS_HAR_V_66th_c_% | Phase C 66th Voltage Magnitude Harmonics | float | 2 | R
0x257C | 0x257D | 9596 | 9597 | MAG_200MS_HAR_I_66th_a_% | Phase A 66th Current Magnitude Harmonics | float | 2 | R
0x257E | 0x257F | 9598 | 9599 | MAG_200MS_HAR_I_66th_b_% | Phase B 66th Current Magnitude Harmonics | float | 2 | R
0x2580 | 0x2581 | 9600 | 9601 | MAG_200MS_HAR_I_66th_c_% | Phase C 66th Current Magnitude Harmonics | float | 2 | R
0x2582 | 0x2583 | 9602 | 9603 | MAG_200MS_HAR_I_66th_n_% | Phase N 66th Current Magnitude Harmonics | float | 2 | R
0x2584 | 0x2585 | 9604 | 9605 | MAG_200MS_HAR_V_67th_a_% | Phase A 67th Voltage Magnitude Harmonics | float | 2 | R
0x2586 | 0x2587 | 9606 | 9607 | MAG_200MS_HAR_V_67th_b_% | Phase B 67th Voltage Magnitude Harmonics | float | 2 | R
0x2588 | 0x2589 | 9608 | 9609 | MAG_200MS_HAR_V_67th_c_% | Phase C 67th Voltage Magnitude Harmonics | float | 2 | R
0x258A | 0x258B | 9610 | 9611 | MAG_200MS_HAR_I_67th_a_% | Phase A 67th Current Magnitude Harmonics | float | 2 | R
0x258C | 0x258D | 9612 | 9613 | MAG_200MS_HAR_I_67th_b_% | Phase B 67th Current Magnitude Harmonics | float | 2 | R
0x258E | 0x258F | 9614 | 9615 | MAG_200MS_HAR_I_67th_c_% | Phase C 67th Current Magnitude Harmonics | float | 2 | R
0x2590 | 0x2591 | 9616 | 9617 | MAG_200MS_HAR_I_67th_n_% | Phase N 67th Current Magnitude Harmonics | float | 2 | R
0x2592 | 0x2593 | 9618 | 9619 | MAG_200MS_HAR_V_68th_a_% | Phase A 68th Voltage Magnitude Harmonics | float | 2 | R
0x2594 | 0x2595 | 9620 | 9621 | MAG_200MS_HAR_V_68th_b_% | Phase B 68th Voltage Magnitude Harmonics | float | 2 | R
0x2596 | 0x2597 | 9622 | 9623 | MAG_200MS_HAR_V_68th_c_% | Phase C 68th Voltage Magnitude Harmonics | float | 2 | R
0x2598 | 0x2599 | 9624 | 9625 | MAG_200MS_HAR_I_68th_a_% | Phase A 68th Current Magnitude Harmonics | float | 2 | R
0x259A | 0x259B | 9626 | 9627 | MAG_200MS_HAR_I_68th_b_% | Phase B 68th Current Magnitude Harmonics | float | 2 | R
0x259C | 0x259D | 9628 | 9629 | MAG_200MS_HAR_I_68th_c_% | Phase C 68th Current Magnitude Harmonics | float | 2 | R
0x259E | 0x259F | 9630 | 9631 | MAG_200MS_HAR_I_68th_n_% | Phase N 68th Current Magnitude Harmonics | float | 2 | R
0x25A0 | 0x25A1 | 9632 | 9633 | MAG_200MS_HAR_V_69th_a_% | Phase A 69th Voltage Magnitude Harmonics | float | 2 | R
0x25A2 | 0x25A3 | 9634 | 9635 | MAG_200MS_HAR_V_69th_b_% | Phase B 69th Voltage Magnitude Harmonics | float | 2 | R
0x25A4 | 0x25A5 | 9636 | 9637 | MAG_200MS_HAR_V_69th_c_% | Phase C 69th Voltage Magnitude Harmonics | float | 2 | R
0x25A6 | 0x25A7 | 9638 | 9639 | MAG_200MS_HAR_I_69th_a_% | Phase A 69th Current Magnitude Harmonics | float | 2 | R
0x25A8 | 0x25A9 | 9640 | 9641 | MAG_200MS_HAR_I_69th_b_% | Phase B 69th Current Magnitude Harmonics | float | 2 | R
0x25AA | 0x25AB | 9642 | 9643 | MAG_200MS_HAR_I_69th_c_% | Phase C 69th Current Magnitude Harmonics | float | 2 | R
0x25AC | 0x25AD | 9644 | 9645 | MAG_200MS_HAR_I_69th_n_% | Phase N 69th Current Magnitude Harmonics | float | 2 | R
0x25AE | 0x25AF | 9646 | 9647 | MAG_200MS_HAR_V_70th_a_% | Phase A 70th Voltage Magnitude Harmonics | float | 2 | R
0x25B0 | 0x25B1 | 9648 | 9649 | MAG_200MS_HAR_V_70th_b_% | Phase B 70th Voltage Magnitude Harmonics | float | 2 | R
0x25B2 | 0x25B3 | 9650 | 9651 | MAG_200MS_HAR_V_70th_c_% | Phase C 70th Voltage Magnitude Harmonics | float | 2 | R
0x25B4 | 0x25B5 | 9652 | 9653 | MAG_200MS_HAR_I_70th_a_% | Phase A 70th Current Magnitude Harmonics | float | 2 | R
0x25B6 | 0x25B7 | 9654 | 9655 | MAG_200MS_HAR_I_70th_b_% | Phase B 70th Current Magnitude Harmonics | float | 2 | R
0x25B8 | 0x25B9 | 9656 | 9657 | MAG_200MS_HAR_I_70th_c_% | Phase C 70th Current Magnitude Harmonics | float | 2 | R
0x25BA | 0x25BB | 9658 | 9659 | MAG_200MS_HAR_I_70th_n_% | Phase N 70th Current Magnitude Harmonics | float | 2 | R
0x25BC | 0x25BD | 9660 | 9661 | MAG_200MS_HAR_V_71th_a_% | Phase A 71st Voltage Magnitude Harmonics | float | 2 | R
0x25BE | 0x25BF | 9662 | 9663 | MAG_200MS_HAR_V_71th_b_% | Phase B 71st Voltage Magnitude Harmonics | float | 2 | R
0x25C0 | 0x25C1 | 9664 | 9665 | MAG_200MS_HAR_V_71th_c_% | Phase C 71st Voltage Magnitude Harmonics | float | 2 | R
0x25C2 | 0x25C3 | 9666 | 9667 | MAG_200MS_HAR_I_71th_a_% | Phase A 71st Current Magnitude Harmonics | float | 2 | R
0x25C4 | 0x25C5 | 9668 | 9669 | MAG_200MS_HAR_I_71th_b_% | Phase B 71st Current Magnitude Harmonics | float | 2 | R
0x25C6 | 0x25C7 | 9670 | 9671 | MAG_200MS_HAR_I_71th_c_% | Phase C 71st Current Magnitude Harmonics | float | 2 | R
0x25C8 | 0x25C9 | 9672 | 9673 | MAG_200MS_HAR_I_71th_n_% | Phase N 71st Current Magnitude Harmonics | float | 2 | R
0x25CA | 0x25CB | 9674 | 9675 | MAG_200MS_HAR_V_72th_a_% | Phase A 72nd Voltage Magnitude Harmonics | float | 2 | R
0x25CC | 0x25CD | 9676 | 9677 | MAG_200MS_HAR_V_72th_b_% | Phase B 72nd Voltage Magnitude Harmonics | float | 2 | R
0x25CE | 0x25CF | 9678 | 9679 | MAG_200MS_HAR_V_72th_c_% | Phase C 72nd Voltage Magnitude Harmonics | float | 2 | R
0x25D0 | 0x25D1 | 9680 | 9681 | MAG_200MS_HAR_I_72th_a_% | Phase A 72nd Current Magnitude Harmonics | float | 2 | R
0x25D2 | 0x25D3 | 9682 | 9683 | MAG_200MS_HAR_I_72th_b_% | Phase B 72nd Current Magnitude Harmonics | float | 2 | R
0x25D4 | 0x25D5 | 9684 | 9685 | MAG_200MS_HAR_I_72th_c_% | Phase C 72nd Current Magnitude Harmonics | float | 2 | R
0x25D6 | 0x25D7 | 9686 | 9687 | MAG_200MS_HAR_I_72th_n_% | Phase N 72nd Current Magnitude Harmonics | float | 2 | R
0x25D8 | 0x25D9 | 9688 | 9689 | MAG_200MS_HAR_V_73th_a_% | Phase A 73rd Voltage Magnitude Harmonics | float | 2 | R
0x25DA | 0x25DB | 9690 | 9691 | MAG_200MS_HAR_V_73th_b_% | Phase B 73rd Voltage Magnitude Harmonics | float | 2 | R
0x25DC | 0x25DD | 9692 | 9693 | MAG_200MS_HAR_V_73th_c_% | Phase C 73rd Voltage Magnitude Harmonics | float | 2 | R
0x25DE | 0x25DF | 9694 | 9695 | MAG_200MS_HAR_I_73th_a_% | Phase A 73rd Current Magnitude Harmonics | float | 2 | R
0x25E0 | 0x25E1 | 9696 | 9697 | MAG_200MS_HAR_I_73th_b_% | Phase B 73rd Current Magnitude Harmonics | float | 2 | R
0x25E2 | 0x25E3 | 9698 | 9699 | MAG_200MS_HAR_I_73th_c_% | Phase C 73rd Current Magnitude Harmonics | float | 2 | R
0x25E4 | 0x25E5 | 9700 | 9701 | MAG_200MS_HAR_I_73th_n_% | Phase N 73rd Current Magnitude Harmonics | float | 2 | R
0x25E6 | 0x25E7 | 9702 | 9703 | MAG_200MS_HAR_V_74th_a_% | Phase A 74th Voltage Magnitude Harmonics | float | 2 | R
0x25E8 | 0x25E9 | 9704 | 9705 | MAG_200MS_HAR_V_74th_b_% | Phase B 74th Voltage Magnitude Harmonics | float | 2 | R
0x25EA | 0x25EB | 9706 | 9707 | MAG_200MS_HAR_V_74th_c_% | Phase C 74th Voltage Magnitude Harmonics | float | 2 | R
0x25EC | 0x25ED | 9708 | 9709 | MAG_200MS_HAR_I_74th_a_% | Phase A 74th Current Magnitude Harmonics | float | 2 | R
0x25EE | 0x25EF | 9710 | 9711 | MAG_200MS_HAR_I_74th_b_% | Phase B 74th Current Magnitude Harmonics | float | 2 | R
0x25F0 | 0x25F1 | 9712 | 9713 | MAG_200MS_HAR_I_74th_c_% | Phase C 74th Current Magnitude Harmonics | float | 2 | R
0x25F2 | 0x25F3 | 9714 | 9715 | MAG_200MS_HAR_I_74th_n_% | Phase N 74th Current Magnitude Harmonics | float | 2 | R
0x25F4 | 0x25F5 | 9716 | 9717 | MAG_200MS_HAR_V_75th_a_% | Phase A 75th Voltage Magnitude Harmonics | float | 2 | R
0x25F6 | 0x25F7 | 9718 | 9719 | MAG_200MS_HAR_V_75th_b_% | Phase B 75th Voltage Magnitude Harmonics | float | 2 | R
0x25F8 | 0x25F9 | 9720 | 9721 | MAG_200MS_HAR_V_75th_c_% | Phase C 75th Voltage Magnitude Harmonics | float | 2 | R
0x25FA | 0x25FB | 9722 | 9723 | MAG_200MS_HAR_I_75th_a_% | Phase A 75th Current Magnitude Harmonics | float | 2 | R
0x25FC | 0x25FD | 9724 | 9725 | MAG_200MS_HAR_I_75th_b_% | Phase B 75th Current Magnitude Harmonics | float | 2 | R
0x25FE | 0x25FF | 9726 | 9727 | MAG_200MS_HAR_I_75th_c_% | Phase C 75th Current Magnitude Harmonics | float | 2 | R
0x2600 | 0x2601 | 9728 | 9729 | MAG_200MS_HAR_I_75th_n_% | Phase N 75th Current Magnitude Harmonics | float | 2 | R
0x2602 | 0x2603 | 9730 | 9731 | MAG_200MS_HAR_V_76th_a_% | Phase A 76th Voltage Magnitude Harmonics | float | 2 | R
0x2604 | 0x2605 | 9732 | 9733 | MAG_200MS_HAR_V_76th_b_% | Phase B 76th Voltage Magnitude Harmonics | float | 2 | R
0x2606 | 0x2607 | 9734 | 9735 | MAG_200MS_HAR_V_76th_c_% | Phase C 76th Voltage Magnitude Harmonics | float | 2 | R
0x2608 | 0x2609 | 9736 | 9737 | MAG_200MS_HAR_I_76th_a_% | Phase A 76th Current Magnitude Harmonics | float | 2 | R
0x260A | 0x260B | 9738 | 9739 | MAG_200MS_HAR_I_76th_b_% | Phase B 76th Current Magnitude Harmonics | float | 2 | R
0x260C | 0x260D | 9740 | 9741 | MAG_200MS_HAR_I_76th_c_% | Phase C 76th Current Magnitude Harmonics | float | 2 | R
0x260E | 0x260F | 9742 | 9743 | MAG_200MS_HAR_I_76th_n_% | Phase N 76th Current Magnitude Harmonics | float | 2 | R
0x2610 | 0x2611 | 9744 | 9745 | MAG_200MS_HAR_V_77th_a_% | Phase A 77th Voltage Magnitude Harmonics | float | 2 | R
0x2612 | 0x2613 | 9746 | 9747 | MAG_200MS_HAR_V_77th_b_% | Phase B 77th Voltage Magnitude Harmonics | float | 2 | R
0x2614 | 0x2615 | 9748 | 9749 | MAG_200MS_HAR_V_77th_c_% | Phase C 77th Voltage Magnitude Harmonics | float | 2 | R
0x2616 | 0x2617 | 9750 | 9751 | MAG_200MS_HAR_I_77th_a_% | Phase A 77th Current Magnitude Harmonics | float | 2 | R
0x2618 | 0x2619 | 9752 | 9753 | MAG_200MS_HAR_I_77th_b_% | Phase B 77th Current Magnitude Harmonics | float | 2 | R
0x261A | 0x261B | 9754 | 9755 | MAG_200MS_HAR_I_77th_c_% | Phase C 77th Current Magnitude Harmonics | float | 2 | R
0x261C | 0x261D | 9756 | 9757 | MAG_200MS_HAR_I_77th_n_% | Phase N 77th Current Magnitude Harmonics | float | 2 | R
0x261E | 0x261F | 9758 | 9759 | MAG_200MS_HAR_V_78th_a_% | Phase A 78th Voltage Magnitude Harmonics | float | 2 | R
0x2620 | 0x2621 | 9760 | 9761 | MAG_200MS_HAR_V_78th_b_% | Phase B 78th Voltage Magnitude Harmonics | float | 2 | R
0x2622 | 0x2623 | 9762 | 9763 | MAG_200MS_HAR_V_78th_c_% | Phase C 78th Voltage Magnitude Harmonics | float | 2 | R
0x2624 | 0x2625 | 9764 | 9765 | MAG_200MS_HAR_I_78th_a_% | Phase A 78th Current Magnitude Harmonics | float | 2 | R
0x2626 | 0x2627 | 9766 | 9767 | MAG_200MS_HAR_I_78th_b_% | Phase B 78th Current Magnitude Harmonics | float | 2 | R
0x2628 | 0x2629 | 9768 | 9769 | MAG_200MS_HAR_I_78th_c_% | Phase C 78th Current Magnitude Harmonics | float | 2 | R
0x262A | 0x262B | 9770 | 9771 | MAG_200MS_HAR_I_78th_n_% | Phase N 78th Current Magnitude Harmonics | float | 2 | R
0x262C | 0x262D | 9772 | 9773 | MAG_200MS_HAR_V_79th_a_% | Phase A 79th Voltage Magnitude Harmonics | float | 2 | R
0x262E | 0x262F | 9774 | 9775 | MAG_200MS_HAR_V_79th_b_% | Phase B 79th Voltage Magnitude Harmonics | float | 2 | R
0x2630 | 0x2631 | 9776 | 9777 | MAG_200MS_HAR_V_79th_c_% | Phase C 79th Voltage Magnitude Harmonics | float | 2 | R
0x2632 | 0x2633 | 9778 | 9779 | MAG_200MS_HAR_I_79th_a_% | Phase A 79th Current Magnitude Harmonics | float | 2 | R
0x2634 | 0x2635 | 9780 | 9781 | MAG_200MS_HAR_I_79th_b_% | Phase B 79th Current Magnitude Harmonics | float | 2 | R
0x2636 | 0x2637 | 9782 | 9783 | MAG_200MS_HAR_I_79th_c_% | Phase C 79th Current Magnitude Harmonics | float | 2 | R
0x2638 | 0x2639 | 9784 | 9785 | MAG_200MS_HAR_I_79th_n_% | Phase N 79th Current Magnitude Harmonics | float | 2 | R
0x263A | 0x263B | 9786 | 9787 | MAG_200MS_HAR_V_80th_a_% | Phase A 80th Voltage Magnitude Harmonics | float | 2 | R
0x263C | 0x263D | 9788 | 9789 | MAG_200MS_HAR_V_80th_b_% | Phase B 80th Voltage Magnitude Harmonics | float | 2 | R
0x263E | 0x263F | 9790 | 9791 | MAG_200MS_HAR_V_80th_c_% | Phase C 80th Voltage Magnitude Harmonics | float | 2 | R
0x2640 | 0x2641 | 9792 | 9793 | MAG_200MS_HAR_I_80th_a_% | Phase A 80th Current Magnitude Harmonics | float | 2 | R
0x2642 | 0x2643 | 9794 | 9795 | MAG_200MS_HAR_I_80th_b_% | Phase B 80th Current Magnitude Harmonics | float | 2 | R
0x2644 | 0x2645 | 9796 | 9797 | MAG_200MS_HAR_I_80th_c_% | Phase C 80th Current Magnitude Harmonics | float | 2 | R
0x2646 | 0x2647 | 9798 | 9799 | MAG_200MS_HAR_I_80th_n_% | Phase N 80th Current Magnitude Harmonics | float | 2 | R
0x2648 | 0x2649 | 9800 | 9801 | MAG_200MS_HAR_V_81th_a_% | Phase A 81st Voltage Magnitude Harmonics | float | 2 | R
0x264A | 0x264B | 9802 | 9803 | MAG_200MS_HAR_V_81th_b_% | Phase B 81st Voltage Magnitude Harmonics | float | 2 | R
0x264C | 0x264D | 9804 | 9805 | MAG_200MS_HAR_V_81th_c_% | Phase C 81st Voltage Magnitude Harmonics | float | 2 | R
0x264E | 0x264F | 9806 | 9807 | MAG_200MS_HAR_I_81th_a_% | Phase A 81st Current Magnitude Harmonics | float | 2 | R
0x2650 | 0x2651 | 9808 | 9809 | MAG_200MS_HAR_I_81th_b_% | Phase B 81st Current Magnitude Harmonics | float | 2 | R
0x2652 | 0x2653 | 9810 | 9811 | MAG_200MS_HAR_I_81th_c_% | Phase C 81st Current Magnitude Harmonics | float | 2 | R
0x2654 | 0x2655 | 9812 | 9813 | MAG_200MS_HAR_I_81th_n_% | Phase N 81st Current Magnitude Harmonics | float | 2 | R
0x2656 | 0x2657 | 9814 | 9815 | MAG_200MS_HAR_V_82th_a_% | Phase A 82nd Voltage Magnitude Harmonics | float | 2 | R
0x2658 | 0x2659 | 9816 | 9817 | MAG_200MS_HAR_V_82th_b_% | Phase B 82nd Voltage Magnitude Harmonics | float | 2 | R
0x265A | 0x265B | 9818 | 9819 | MAG_200MS_HAR_V_82th_c_% | Phase C 82nd Voltage Magnitude Harmonics | float | 2 | R
0x265C | 0x265D | 9820 | 9821 | MAG_200MS_HAR_I_82th_a_% | Phase A 82nd Current Magnitude Harmonics | float | 2 | R
0x265E | 0x265F | 9822 | 9823 | MAG_200MS_HAR_I_82th_b_% | Phase B 82nd Current Magnitude Harmonics | float | 2 | R
0x2660 | 0x2661 | 9824 | 9825 | MAG_200MS_HAR_I_82th_c_% | Phase C 82nd Current Magnitude Harmonics | float | 2 | R
0x2662 | 0x2663 | 9826 | 9827 | MAG_200MS_HAR_I_82th_n_% | Phase N 82nd Current Magnitude Harmonics | float | 2 | R
0x2664 | 0x2665 | 9828 | 9829 | MAG_200MS_HAR_V_83th_a_% | Phase A 83rd Voltage Magnitude Harmonics | float | 2 | R
0x2666 | 0x2667 | 9830 | 9831 | MAG_200MS_HAR_V_83th_b_% | Phase B 83rd Voltage Magnitude Harmonics | float | 2 | R
0x2668 | 0x2669 | 9832 | 9833 | MAG_200MS_HAR_V_83th_c_% | Phase C 83rd Voltage Magnitude Harmonics | float | 2 | R
0x266A | 0x266B | 9834 | 9835 | MAG_200MS_HAR_I_83th_a_% | Phase A 83rd Current Magnitude Harmonics | float | 2 | R
0x266C | 0x266D | 9836 | 9837 | MAG_200MS_HAR_I_83th_b_% | Phase B 83rd Current Magnitude Harmonics | float | 2 | R
0x266E | 0x266F | 9838 | 9839 | MAG_200MS_HAR_I_83th_c_% | Phase C 83rd Current Magnitude Harmonics | float | 2 | R
0x2670 | 0x2671 | 9840 | 9841 | MAG_200MS_HAR_I_83th_n_% | Phase N 83rd Current Magnitude Harmonics | float | 2 | R
0x2672 | 0x2673 | 9842 | 9843 | MAG_200MS_HAR_V_84th_a_% | Phase A 84th Voltage Magnitude Harmonics | float | 2 | R
0x2674 | 0x2675 | 9844 | 9845 | MAG_200MS_HAR_V_84th_b_% | Phase B 84th Voltage Magnitude Harmonics | float | 2 | R
0x2676 | 0x2677 | 9846 | 9847 | MAG_200MS_HAR_V_84th_c_% | Phase C 84th Voltage Magnitude Harmonics | float | 2 | R
0x2678 | 0x2679 | 9848 | 9849 | MAG_200MS_HAR_I_84th_a_% | Phase A 84th Current Magnitude Harmonics | float | 2 | R
0x267A | 0x267B | 9850 | 9851 | MAG_200MS_HAR_I_84th_b_% | Phase B 84th Current Magnitude Harmonics | float | 2 | R
0x267C | 0x267D | 9852 | 9853 | MAG_200MS_HAR_I_84th_c_% | Phase C 84th Current Magnitude Harmonics | float | 2 | R
0x267E | 0x267F | 9854 | 9855 | MAG_200MS_HAR_I_84th_n_% | Phase N 84th Current Magnitude Harmonics | float | 2 | R
0x2680 | 0x2681 | 9856 | 9857 | MAG_200MS_HAR_V_85th_a_% | Phase A 85th Voltage Magnitude Harmonics | float | 2 | R
0x2682 | 0x2683 | 9858 | 9859 | MAG_200MS_HAR_V_85th_b_% | Phase B 85th Voltage Magnitude Harmonics | float | 2 | R
0x2684 | 0x2685 | 9860 | 9861 | MAG_200MS_HAR_V_85th_c_% | Phase C 85th Voltage Magnitude Harmonics | float | 2 | R
0x2686 | 0x2687 | 9862 | 9863 | MAG_200MS_HAR_I_85th_a_% | Phase A 85th Current Magnitude Harmonics | float | 2 | R
0x2688 | 0x2689 | 9864 | 9865 | MAG_200MS_HAR_I_85th_b_% | Phase B 85th Current Magnitude Harmonics | float | 2 | R
0x268A | 0x268B | 9866 | 9867 | MAG_200MS_HAR_I_85th_c_% | Phase C 85th Current Magnitude Harmonics | float | 2 | R
0x268C | 0x268D | 9868 | 9869 | MAG_200MS_HAR_I_85th_n_% | Phase N 85th Current Magnitude Harmonics | float | 2 | R
0x268E | 0x268F | 9870 | 9871 | MAG_200MS_HAR_V_86th_a_% | Phase A 86th Voltage Magnitude Harmonics | float | 2 | R
0x2690 | 0x2691 | 9872 | 9873 | MAG_200MS_HAR_V_86th_b_% | Phase B 86th Voltage Magnitude Harmonics | float | 2 | R
0x2692 | 0x2693 | 9874 | 9875 | MAG_200MS_HAR_V_86th_c_% | Phase C 86th Voltage Magnitude Harmonics | float | 2 | R
0x2694 | 0x2695 | 9876 | 9877 | MAG_200MS_HAR_I_86th_a_% | Phase A 86th Current Magnitude Harmonics | float | 2 | R
0x2696 | 0x2697 | 9878 | 9879 | MAG_200MS_HAR_I_86th_b_% | Phase B 86th Current Magnitude Harmonics | float | 2 | R
0x2698 | 0x2699 | 9880 | 9881 | MAG_200MS_HAR_I_86th_c_% | Phase C 86th Current Magnitude Harmonics | float | 2 | R
0x269A | 0x269B | 9882 | 9883 | MAG_200MS_HAR_I_86th_n_% | Phase N 86th Current Magnitude Harmonics | float | 2 | R
0x269C | 0x269D | 9884 | 9885 | MAG_200MS_HAR_V_87th_a_% | Phase A 87th Voltage Magnitude Harmonics | float | 2 | R
0x269E | 0x269F | 9886 | 9887 | MAG_200MS_HAR_V_87th_b_% | Phase B 87th Voltage Magnitude Harmonics | float | 2 | R
0x26A0 | 0x26A1 | 9888 | 9889 | MAG_200MS_HAR_V_87th_c_% | Phase C 87th Voltage Magnitude Harmonics | float | 2 | R
0x26A2 | 0x26A3 | 9890 | 9891 | MAG_200MS_HAR_I_87th_a_% | Phase A 87th Current Magnitude Harmonics | float | 2 | R
0x26A4 | 0x26A5 | 9892 | 9893 | MAG_200MS_HAR_I_87th_b_% | Phase B 87th Current Magnitude Harmonics | float | 2 | R
0x26A6 | 0x26A7 | 9894 | 9895 | MAG_200MS_HAR_I_87th_c_% | Phase C 87th Current Magnitude Harmonics | float | 2 | R
0x26A8 | 0x26A9 | 9896 | 9897 | MAG_200MS_HAR_I_87th_n_% | Phase N 87th Current Magnitude Harmonics | float | 2 | R
0x26AA | 0x26AB | 9898 | 9899 | MAG_200MS_HAR_V_88th_a_% | Phase A 88th Voltage Magnitude Harmonics | float | 2 | R
0x26AC | 0x26AD | 9900 | 9901 | MAG_200MS_HAR_V_88th_b_% | Phase B 88th Voltage Magnitude Harmonics | float | 2 | R
0x26AE | 0x26AF | 9902 | 9903 | MAG_200MS_HAR_V_88th_c_% | Phase C 88th Voltage Magnitude Harmonics | float | 2 | R
0x26B0 | 0x26B1 | 9904 | 9905 | MAG_200MS_HAR_I_88th_a_% | Phase A 88th Current Magnitude Harmonics | float | 2 | R
0x26B2 | 0x26B3 | 9906 | 9907 | MAG_200MS_HAR_I_88th_b_% | Phase B 88th Current Magnitude Harmonics | float | 2 | R
0x26B4 | 0x26B5 | 9908 | 9909 | MAG_200MS_HAR_I_88th_c_% | Phase C 88th Current Magnitude Harmonics | float | 2 | R
0x26B6 | 0x26B7 | 9910 | 9911 | MAG_200MS_HAR_I_88th_n_% | Phase N 88th Current Magnitude Harmonics | float | 2 | R
0x26B8 | 0x26B9 | 9912 | 9913 | MAG_200MS_HAR_V_89th_a_% | Phase A 89th Voltage Magnitude Harmonics | float | 2 | R
0x26BA | 0x26BB | 9914 | 9915 | MAG_200MS_HAR_V_89th_b_% | Phase B 89th Voltage Magnitude Harmonics | float | 2 | R
0x26BC | 0x26BD | 9916 | 9917 | MAG_200MS_HAR_V_89th_c_% | Phase C 89th Voltage Magnitude Harmonics | float | 2 | R
0x26BE | 0x26BF | 9918 | 9919 | MAG_200MS_HAR_I_89th_a_% | Phase A 89th Current Magnitude Harmonics | float | 2 | R
0x26C0 | 0x26C1 | 9920 | 9921 | MAG_200MS_HAR_I_89th_b_% | Phase B 89th Current Magnitude Harmonics | float | 2 | R
0x26C2 | 0x26C3 | 9922 | 9923 | MAG_200MS_HAR_I_89th_c_% | Phase C 89th Current Magnitude Harmonics | float | 2 | R
0x26C4 | 0x26C5 | 9924 | 9925 | MAG_200MS_HAR_I_89th_n_% | Phase N 89th Current Magnitude Harmonics | float | 2 | R
0x26C6 | 0x26C7 | 9926 | 9927 | MAG_200MS_HAR_V_90th_a_% | Phase A 90th Voltage Magnitude Harmonics | float | 2 | R
0x26C8 | 0x26C9 | 9928 | 9929 | MAG_200MS_HAR_V_90th_b_% | Phase B 90th Voltage Magnitude Harmonics | float | 2 | R
0x26CA | 0x26CB | 9930 | 9931 | MAG_200MS_HAR_V_90th_c_% | Phase C 90th Voltage Magnitude Harmonics | float | 2 | R
0x26CC | 0x26CD | 9932 | 9933 | MAG_200MS_HAR_I_90th_a_% | Phase A 90th Current Magnitude Harmonics | float | 2 | R
0x26CE | 0x26CF | 9934 | 9935 | MAG_200MS_HAR_I_90th_b_% | Phase B 90th Current Magnitude Harmonics | float | 2 | R
0x26D0 | 0x26D1 | 9936 | 9937 | MAG_200MS_HAR_I_90th_c_% | Phase C 90th Current Magnitude Harmonics | float | 2 | R
0x26D2 | 0x26D3 | 9938 | 9939 | MAG_200MS_HAR_I_90th_n_% | Phase N 90th Current Magnitude Harmonics | float | 2 | R
0x26D4 | 0x26D5 | 9940 | 9941 | MAG_200MS_HAR_V_91th_a_% | Phase A 91st Voltage Magnitude Harmonics | float | 2 | R
0x26D6 | 0x26D7 | 9942 | 9943 | MAG_200MS_HAR_V_91th_b_% | Phase B 91st Voltage Magnitude Harmonics | float | 2 | R
0x26D8 | 0x26D9 | 9944 | 9945 | MAG_200MS_HAR_V_91th_c_% | Phase C 91st Voltage Magnitude Harmonics | float | 2 | R
0x26DA | 0x26DB | 9946 | 9947 | MAG_200MS_HAR_I_91th_a_% | Phase A 91st Current Magnitude Harmonics | float | 2 | R
0x26DC | 0x26DD | 9948 | 9949 | MAG_200MS_HAR_I_91th_b_% | Phase B 91st Current Magnitude Harmonics | float | 2 | R
0x26DE | 0x26DF | 9950 | 9951 | MAG_200MS_HAR_I_91th_c_% | Phase C 91st Current Magnitude Harmonics | float | 2 | R
0x26E0 | 0x26E1 | 9952 | 9953 | MAG_200MS_HAR_I_91th_n_% | Phase N 91st Current Magnitude Harmonics | float | 2 | R
0x26E2 | 0x26E3 | 9954 | 9955 | MAG_200MS_HAR_V_92th_a_% | Phase A 92nd Voltage Magnitude Harmonics | float | 2 | R
0x26E4 | 0x26E5 | 9956 | 9957 | MAG_200MS_HAR_V_92th_b_% | Phase B 92nd Voltage Magnitude Harmonics | float | 2 | R
0x26E6 | 0x26E7 | 9958 | 9959 | MAG_200MS_HAR_V_92th_c_% | Phase C 92nd Voltage Magnitude Harmonics | float | 2 | R
0x26E8 | 0x26E9 | 9960 | 9961 | MAG_200MS_HAR_I_92th_a_% | Phase A 92nd Current Magnitude Harmonics | float | 2 | R
0x26EA | 0x26EB | 9962 | 9963 | MAG_200MS_HAR_I_92th_b_% | Phase B 92nd Current Magnitude Harmonics | float | 2 | R
0x26EC | 0x26ED | 9964 | 9965 | MAG_200MS_HAR_I_92th_c_% | Phase C 92nd Current Magnitude Harmonics | float | 2 | R
0x26EE | 0x26EF | 9966 | 9967 | MAG_200MS_HAR_I_92th_n_% | Phase N 92nd Current Magnitude Harmonics | float | 2 | R
0x26F0 | 0x26F1 | 9968 | 9969 | MAG_200MS_HAR_V_93th_a_% | Phase A 93rd Voltage Magnitude Harmonics | float | 2 | R
0x26F2 | 0x26F3 | 9970 | 9971 | MAG_200MS_HAR_V_93th_b_% | Phase B 93rd Voltage Magnitude Harmonics | float | 2 | R
0x26F4 | 0x26F5 | 9972 | 9973 | MAG_200MS_HAR_V_93th_c_% | Phase C 93rd Voltage Magnitude Harmonics | float | 2 | R
0x26F6 | 0x26F7 | 9974 | 9975 | MAG_200MS_HAR_I_93th_a_% | Phase A 93rd Current Magnitude Harmonics | float | 2 | R
0x26F8 | 0x26F9 | 9976 | 9977 | MAG_200MS_HAR_I_93th_b_% | Phase B 93rd Current Magnitude Harmonics | float | 2 | R
0x26FA | 0x26FB | 9978 | 9979 | MAG_200MS_HAR_I_93th_c_% | Phase C 93rd Current Magnitude Harmonics | float | 2 | R
0x26FC | 0x26FD | 9980 | 9981 | MAG_200MS_HAR_I_93th_n_% | Phase N 93rd Current Magnitude Harmonics | float | 2 | R
0x26FE | 0x26FF | 9982 | 9983 | MAG_200MS_HAR_V_94th_a_% | Phase A 94th Voltage Magnitude Harmonics | float | 2 | R
0x2700 | 0x2701 | 9984 | 9985 | MAG_200MS_HAR_V_94th_b_% | Phase B 94th Voltage Magnitude Harmonics | float | 2 | R
0x2702 | 0x2703 | 9986 | 9987 | MAG_200MS_HAR_V_94th_c_% | Phase C 94th Voltage Magnitude Harmonics | float | 2 | R
0x2704 | 0x2705 | 9988 | 9989 | MAG_200MS_HAR_I_94th_a_% | Phase A 94th Current Magnitude Harmonics | float | 2 | R
0x2706 | 0x2707 | 9990 | 9991 | MAG_200MS_HAR_I_94th_b_% | Phase B 94th Current Magnitude Harmonics | float | 2 | R
0x2708 | 0x2709 | 9992 | 9993 | MAG_200MS_HAR_I_94th_c_% | Phase C 94th Current Magnitude Harmonics | float | 2 | R
0x270A | 0x270B | 9994 | 9995 | MAG_200MS_HAR_I_94th_n_% | Phase N 94th Current Magnitude Harmonics | float | 2 | R
0x270C | 0x270D | 9996 | 9997 | MAG_200MS_HAR_V_95th_a_% | Phase A 95th Voltage Magnitude Harmonics | float | 2 | R
0x270E | 0x270F | 9998 | 9999 | MAG_200MS_HAR_V_95th_b_% | Phase B 95th Voltage Magnitude Harmonics | float | 2 | R
0x2710 | 0x2711 | 10000 | 10001 | MAG_200MS_HAR_V_95th_c_% | Phase C 95th Voltage Magnitude Harmonics | float | 2 | R
0x2712 | 0x2713 | 10002 | 10003 | MAG_200MS_HAR_I_95th_a_% | Phase A 95th Current Magnitude Harmonics | float | 2 | R
0x2714 | 0x2715 | 10004 | 10005 | MAG_200MS_HAR_I_95th_b_% | Phase B 95th Current Magnitude Harmonics | float | 2 | R
0x2716 | 0x2717 | 10006 | 10007 | MAG_200MS_HAR_I_95th_c_% | Phase C 95th Current Magnitude Harmonics | float | 2 | R
0x2718 | 0x2719 | 10008 | 10009 | MAG_200MS_HAR_I_95th_n_% | Phase N 95th Current Magnitude Harmonics | float | 2 | R
0x271A | 0x271B | 10010 | 10011 | MAG_200MS_HAR_V_96th_a_% | Phase A 96th Voltage Magnitude Harmonics | float | 2 | R
0x271C | 0x271D | 10012 | 10013 | MAG_200MS_HAR_V_96th_b_% | Phase B 96th Voltage Magnitude Harmonics | float | 2 | R
0x271E | 0x271F | 10014 | 10015 | MAG_200MS_HAR_V_96th_c_% | Phase C 96th Voltage Magnitude Harmonics | float | 2 | R
0x2720 | 0x2721 | 10016 | 10017 | MAG_200MS_HAR_I_96th_a_% | Phase A 96th Current Magnitude Harmonics | float | 2 | R
0x2722 | 0x2723 | 10018 | 10019 | MAG_200MS_HAR_I_96th_b_% | Phase B 96th Current Magnitude Harmonics | float | 2 | R
0x2724 | 0x2725 | 10020 | 10021 | MAG_200MS_HAR_I_96th_c_% | Phase C 96th Current Magnitude Harmonics | float | 2 | R
0x2726 | 0x2727 | 10022 | 10023 | MAG_200MS_HAR_I_96th_n_% | Phase N 96th Current Magnitude Harmonics | float | 2 | R
0x2728 | 0x2729 | 10024 | 10025 | MAG_200MS_HAR_V_97th_a_% | Phase A 97th Voltage Magnitude Harmonics | float | 2 | R
0x272A | 0x272B | 10026 | 10027 | MAG_200MS_HAR_V_97th_b_% | Phase B 97th Voltage Magnitude Harmonics | float | 2 | R
0x272C | 0x272D | 10028 | 10029 | MAG_200MS_HAR_V_97th_c_% | Phase C 97th Voltage Magnitude Harmonics | float | 2 | R
0x272E | 0x272F | 10030 | 10031 | MAG_200MS_HAR_I_97th_a_% | Phase A 97th Current Magnitude Harmonics | float | 2 | R
0x2730 | 0x2731 | 10032 | 10033 | MAG_200MS_HAR_I_97th_b_% | Phase B 97th Current Magnitude Harmonics | float | 2 | R
0x2732 | 0x2733 | 10034 | 10035 | MAG_200MS_HAR_I_97th_c_% | Phase C 97th Current Magnitude Harmonics | float | 2 | R
0x2734 | 0x2735 | 10036 | 10037 | MAG_200MS_HAR_I_97th_n_% | Phase N 97th Current Magnitude Harmonics | float | 2 | R
0x2736 | 0x2737 | 10038 | 10039 | MAG_200MS_HAR_V_98th_a_% | Phase A 98th Voltage Magnitude Harmonics | float | 2 | R
0x2738 | 0x2739 | 10040 | 10041 | MAG_200MS_HAR_V_98th_b_% | Phase B 98th Voltage Magnitude Harmonics | float | 2 | R
0x273A | 0x273B | 10042 | 10043 | MAG_200MS_HAR_V_98th_c_% | Phase C 98th Voltage Magnitude Harmonics | float | 2 | R
0x273C | 0x273D | 10044 | 10045 | MAG_200MS_HAR_I_98th_a_% | Phase A 98th Current Magnitude Harmonics | float | 2 | R
0x273E | 0x273F | 10046 | 10047 | MAG_200MS_HAR_I_98th_b_% | Phase B 98th Current Magnitude Harmonics | float | 2 | R
0x2740 | 0x2741 | 10048 | 10049 | MAG_200MS_HAR_I_98th_c_% | Phase C 98th Current Magnitude Harmonics | float | 2 | R
0x2742 | 0x2743 | 10050 | 10051 | MAG_200MS_HAR_I_98th_n_% | Phase N 98th Current Magnitude Harmonics | float | 2 | R
0x2744 | 0x2745 | 10052 | 10053 | MAG_200MS_HAR_V_99th_a_% | Phase A 99th Voltage Magnitude Harmonics | float | 2 | R
0x2746 | 0x2747 | 10054 | 10055 | MAG_200MS_HAR_V_99th_b_% | Phase B 99th Voltage Magnitude Harmonics | float | 2 | R
0x2748 | 0x2749 | 10056 | 10057 | MAG_200MS_HAR_V_99th_c_% | Phase C 99th Voltage Magnitude Harmonics | float | 2 | R
0x274A | 0x274B | 10058 | 10059 | MAG_200MS_HAR_I_99th_a_% | Phase A 99th Current Magnitude Harmonics | float | 2 | R
0x274C | 0x274D | 10060 | 10061 | MAG_200MS_HAR_I_99th_b_% | Phase B 99th Current Magnitude Harmonics | float | 2 | R
0x274E | 0x274F | 10062 | 10063 | MAG_200MS_HAR_I_99th_c_% | Phase C 99th Current Magnitude Harmonics | float | 2 | R
0x2750 | 0x2751 | 10064 | 10065 | MAG_200MS_HAR_I_99th_n_% | Phase N 99th Current Magnitude Harmonics | float | 2 | R
0x2752 | 0x2753 | 10066 | 10067 | MAG_200MS_HAR_V_100th_a_% | Phase A 100th Voltage Magnitude Harmonics | float | 2 | R
0x2754 | 0x2755 | 10068 | 10069 | MAG_200MS_HAR_V_100th_b_% | Phase B 100th Voltage Magnitude Harmonics | float | 2 | R
0x2756 | 0x2757 | 10070 | 10071 | MAG_200MS_HAR_V_100th_c_% | Phase C 100th Voltage Magnitude Harmonics | float | 2 | R
0x2758 | 0x2759 | 10072 | 10073 | MAG_200MS_HAR_I_100th_a_% | Phase A 100th Current Magnitude Harmonics | float | 2 | R
0x275A | 0x275B | 10074 | 10075 | MAG_200MS_HAR_I_100th_b_% | Phase B 100th Current Magnitude Harmonics | float | 2 | R
0x275C | 0x275D | 10076 | 10077 | MAG_200MS_HAR_I_100th_c_% | Phase C 100th Current Magnitude Harmonics | float | 2 | R
0x275E | 0x275F | 10078 | 10079 | MAG_200MS_HAR_I_100th_n_% | Phase N 100th Current Magnitude Harmonics | float | 2 | R
0x2760 | 0x2761 | 10080 | 10081 | MAG_200MS_HAR_V_101th_a_% | Phase A 101st Voltage Magnitude Harmonics | float | 2 | R
0x2762 | 0x2763 | 10082 | 10083 | MAG_200MS_HAR_V_101th_b_% | Phase B 101st Voltage Magnitude Harmonics | float | 2 | R
0x2764 | 0x2765 | 10084 | 10085 | MAG_200MS_HAR_V_101th_c_% | Phase C 101st Voltage Magnitude Harmonics | float | 2 | R
0x2766 | 0x2767 | 10086 | 10087 | MAG_200MS_HAR_I_101th_a_% | Phase A 101st Current Magnitude Harmonics | float | 2 | R
0x2768 | 0x2769 | 10088 | 10089 | MAG_200MS_HAR_I_101th_b_% | Phase B 101st Current Magnitude Harmonics | float | 2 | R
0x276A | 0x276B | 10090 | 10091 | MAG_200MS_HAR_I_101th_c_% | Phase C 101st Current Magnitude Harmonics | float | 2 | R
0x276C | 0x276D | 10092 | 10093 | MAG_200MS_HAR_I_101th_n_% | Phase N 101st Current Magnitude Harmonics | float | 2 | R
0x276E | 0x276F | 10094 | 10095 | MAG_200MS_HAR_V_102th_a_% | Phase A 102nd Voltage Magnitude Harmonics | float | 2 | R
0x2770 | 0x2771 | 10096 | 10097 | MAG_200MS_HAR_V_102th_b_% | Phase B 102nd Voltage Magnitude Harmonics | float | 2 | R
0x2772 | 0x2773 | 10098 | 10099 | MAG_200MS_HAR_V_102th_c_% | Phase C 102nd Voltage Magnitude Harmonics | float | 2 | R
0x2774 | 0x2775 | 10100 | 10101 | MAG_200MS_HAR_I_102th_a_% | Phase A 102nd Current Magnitude Harmonics | float | 2 | R
0x2776 | 0x2777 | 10102 | 10103 | MAG_200MS_HAR_I_102th_b_% | Phase B 102nd Current Magnitude Harmonics | float | 2 | R
0x2778 | 0x2779 | 10104 | 10105 | MAG_200MS_HAR_I_102th_c_% | Phase C 102nd Current Magnitude Harmonics | float | 2 | R
0x277A | 0x277B | 10106 | 10107 | MAG_200MS_HAR_I_102th_n_% | Phase N 102nd Current Magnitude Harmonics | float | 2 | R
0x277C | 0x277D | 10108 | 10109 | MAG_200MS_HAR_V_103th_a_% | Phase A 103rd Voltage Magnitude Harmonics | float | 2 | R
0x277E | 0x277F | 10110 | 10111 | MAG_200MS_HAR_V_103th_b_% | Phase B 103rd Voltage Magnitude Harmonics | float | 2 | R
0x2780 | 0x2781 | 10112 | 10113 | MAG_200MS_HAR_V_103th_c_% | Phase C 103rd Voltage Magnitude Harmonics | float | 2 | R
0x2782 | 0x2783 | 10114 | 10115 | MAG_200MS_HAR_I_103th_a_% | Phase A 103rd Current Magnitude Harmonics | float | 2 | R
0x2784 | 0x2785 | 10116 | 10117 | MAG_200MS_HAR_I_103th_b_% | Phase B 103rd Current Magnitude Harmonics | float | 2 | R
0x2786 | 0x2787 | 10118 | 10119 | MAG_200MS_HAR_I_103th_c_% | Phase C 103rd Current Magnitude Harmonics | float | 2 | R
0x2788 | 0x2789 | 10120 | 10121 | MAG_200MS_HAR_I_103th_n_% | Phase N 103rd Current Magnitude Harmonics | float | 2 | R
0x278A | 0x278B | 10122 | 10123 | MAG_200MS_HAR_V_104th_a_% | Phase A 104th Voltage Magnitude Harmonics | float | 2 | R
0x278C | 0x278D | 10124 | 10125 | MAG_200MS_HAR_V_104th_b_% | Phase B 104th Voltage Magnitude Harmonics | float | 2 | R
0x278E | 0x278F | 10126 | 10127 | MAG_200MS_HAR_V_104th_c_% | Phase C 104th Voltage Magnitude Harmonics | float | 2 | R
0x2790 | 0x2791 | 10128 | 10129 | MAG_200MS_HAR_I_104th_a_% | Phase A 104th Current Magnitude Harmonics | float | 2 | R
0x2792 | 0x2793 | 10130 | 10131 | MAG_200MS_HAR_I_104th_b_% | Phase B 104th Current Magnitude Harmonics | float | 2 | R
0x2794 | 0x2795 | 10132 | 10133 | MAG_200MS_HAR_I_104th_c_% | Phase C 104th Current Magnitude Harmonics | float | 2 | R
0x2796 | 0x2797 | 10134 | 10135 | MAG_200MS_HAR_I_104th_n_% | Phase N 104th Current Magnitude Harmonics | float | 2 | R
0x2798 | 0x2799 | 10136 | 10137 | MAG_200MS_HAR_V_105th_a_% | Phase A 105th Voltage Magnitude Harmonics | float | 2 | R
0x279A | 0x279B | 10138 | 10139 | MAG_200MS_HAR_V_105th_b_% | Phase B 105th Voltage Magnitude Harmonics | float | 2 | R
0x279C | 0x279D | 10140 | 10141 | MAG_200MS_HAR_V_105th_c_% | Phase C 105th Voltage Magnitude Harmonics | float | 2 | R
0x279E | 0x279F | 10142 | 10143 | MAG_200MS_HAR_I_105th_a_% | Phase A 105th Current Magnitude Harmonics | float | 2 | R
0x27A0 | 0x27A1 | 10144 | 10145 | MAG_200MS_HAR_I_105th_b_% | Phase B 105th Current Magnitude Harmonics | float | 2 | R
0x27A2 | 0x27A3 | 10146 | 10147 | MAG_200MS_HAR_I_105th_c_% | Phase C 105th Current Magnitude Harmonics | float | 2 | R
0x27A4 | 0x27A5 | 10148 | 10149 | MAG_200MS_HAR_I_105th_n_% | Phase N 105th Current Magnitude Harmonics | float | 2 | R
0x27A6 | 0x27A7 | 10150 | 10151 | MAG_200MS_HAR_V_106th_a_% | Phase A 106th Voltage Magnitude Harmonics | float | 2 | R
0x27A8 | 0x27A9 | 10152 | 10153 | MAG_200MS_HAR_V_106th_b_% | Phase B 106th Voltage Magnitude Harmonics | float | 2 | R
0x27AA | 0x27AB | 10154 | 10155 | MAG_200MS_HAR_V_106th_c_% | Phase C 106th Voltage Magnitude Harmonics | float | 2 | R
0x27AC | 0x27AD | 10156 | 10157 | MAG_200MS_HAR_I_106th_a_% | Phase A 106th Current Magnitude Harmonics | float | 2 | R
0x27AE | 0x27AF | 10158 | 10159 | MAG_200MS_HAR_I_106th_b_% | Phase B 106th Current Magnitude Harmonics | float | 2 | R
0x27B0 | 0x27B1 | 10160 | 10161 | MAG_200MS_HAR_I_106th_c_% | Phase C 106th Current Magnitude Harmonics | float | 2 | R
0x27B2 | 0x27B3 | 10162 | 10163 | MAG_200MS_HAR_I_106th_n_% | Phase N 106th Current Magnitude Harmonics | float | 2 | R
0x27B4 | 0x27B5 | 10164 | 10165 | MAG_200MS_HAR_V_107th_a_% | Phase A 107th Voltage Magnitude Harmonics | float | 2 | R
0x27B6 | 0x27B7 | 10166 | 10167 | MAG_200MS_HAR_V_107th_b_% | Phase B 107th Voltage Magnitude Harmonics | float | 2 | R
0x27B8 | 0x27B9 | 10168 | 10169 | MAG_200MS_HAR_V_107th_c_% | Phase C 107th Voltage Magnitude Harmonics | float | 2 | R
0x27BA | 0x27BB | 10170 | 10171 | MAG_200MS_HAR_I_107th_a_% | Phase A 107th Current Magnitude Harmonics | float | 2 | R
0x27BC | 0x27BD | 10172 | 10173 | MAG_200MS_HAR_I_107th_b_% | Phase B 107th Current Magnitude Harmonics | float | 2 | R
0x27BE | 0x27BF | 10174 | 10175 | MAG_200MS_HAR_I_107th_c_% | Phase C 107th Current Magnitude Harmonics | float | 2 | R
0x27C0 | 0x27C1 | 10176 | 10177 | MAG_200MS_HAR_I_107th_n_% | Phase N 107th Current Magnitude Harmonics | float | 2 | R
0x27C2 | 0x27C3 | 10178 | 10179 | MAG_200MS_HAR_V_108th_a_% | Phase A 108th Voltage Magnitude Harmonics | float | 2 | R
0x27C4 | 0x27C5 | 10180 | 10181 | MAG_200MS_HAR_V_108th_b_% | Phase B 108th Voltage Magnitude Harmonics | float | 2 | R
0x27C6 | 0x27C7 | 10182 | 10183 | MAG_200MS_HAR_V_108th_c_% | Phase C 108th Voltage Magnitude Harmonics | float | 2 | R
0x27C8 | 0x27C9 | 10184 | 10185 | MAG_200MS_HAR_I_108th_a_% | Phase A 108th Current Magnitude Harmonics | float | 2 | R
0x27CA | 0x27CB | 10186 | 10187 | MAG_200MS_HAR_I_108th_b_% | Phase B 108th Current Magnitude Harmonics | float | 2 | R
0x27CC | 0x27CD | 10188 | 10189 | MAG_200MS_HAR_I_108th_c_% | Phase C 108th Current Magnitude Harmonics | float | 2 | R
0x27CE | 0x27CF | 10190 | 10191 | MAG_200MS_HAR_I_108th_n_% | Phase N 108th Current Magnitude Harmonics | float | 2 | R
0x27D0 | 0x27D1 | 10192 | 10193 | MAG_200MS_HAR_V_109th_a_% | Phase A 109th Voltage Magnitude Harmonics | float | 2 | R
0x27D2 | 0x27D3 | 10194 | 10195 | MAG_200MS_HAR_V_109th_b_% | Phase B 109th Voltage Magnitude Harmonics | float | 2 | R
0x27D4 | 0x27D5 | 10196 | 10197 | MAG_200MS_HAR_V_109th_c_% | Phase C 109th Voltage Magnitude Harmonics | float | 2 | R
0x27D6 | 0x27D7 | 10198 | 10199 | MAG_200MS_HAR_I_109th_a_% | Phase A 109th Current Magnitude Harmonics | float | 2 | R
0x27D8 | 0x27D9 | 10200 | 10201 | MAG_200MS_HAR_I_109th_b_% | Phase B 109th Current Magnitude Harmonics | float | 2 | R
0x27DA | 0x27DB | 10202 | 10203 | MAG_200MS_HAR_I_109th_c_% | Phase C 109th Current Magnitude Harmonics | float | 2 | R
0x27DC | 0x27DD | 10204 | 10205 | MAG_200MS_HAR_I_109th_n_% | Phase N 109th Current Magnitude Harmonics | float | 2 | R
0x27DE | 0x27DF | 10206 | 10207 | MAG_200MS_HAR_V_110th_a_% | Phase A 110th Voltage Magnitude Harmonics | float | 2 | R
0x27E0 | 0x27E1 | 10208 | 10209 | MAG_200MS_HAR_V_110th_b_% | Phase B 110th Voltage Magnitude Harmonics | float | 2 | R
0x27E2 | 0x27E3 | 10210 | 10211 | MAG_200MS_HAR_V_110th_c_% | Phase C 110th Voltage Magnitude Harmonics | float | 2 | R
0x27E4 | 0x27E5 | 10212 | 10213 | MAG_200MS_HAR_I_110th_a_% | Phase A 110th Current Magnitude Harmonics | float | 2 | R
0x27E6 | 0x27E7 | 10214 | 10215 | MAG_200MS_HAR_I_110th_b_% | Phase B 110th Current Magnitude Harmonics | float | 2 | R
0x27E8 | 0x27E9 | 10216 | 10217 | MAG_200MS_HAR_I_110th_c_% | Phase C 110th Current Magnitude Harmonics | float | 2 | R
0x27EA | 0x27EB | 10218 | 10219 | MAG_200MS_HAR_I_110th_n_% | Phase N 110th Current Magnitude Harmonics | float | 2 | R
0x27EC | 0x27ED | 10220 | 10221 | MAG_200MS_HAR_V_111th_a_% | Phase A 111st Voltage Magnitude Harmonics | float | 2 | R
0x27EE | 0x27EF | 10222 | 10223 | MAG_200MS_HAR_V_111th_b_% | Phase B 111st Voltage Magnitude Harmonics | float | 2 | R
0x27F0 | 0x27F1 | 10224 | 10225 | MAG_200MS_HAR_V_111th_c_% | Phase C 111st Voltage Magnitude Harmonics | float | 2 | R
0x27F2 | 0x27F3 | 10226 | 10227 | MAG_200MS_HAR_I_111th_a_% | Phase A 111st Current Magnitude Harmonics | float | 2 | R
0x27F4 | 0x27F5 | 10228 | 10229 | MAG_200MS_HAR_I_111th_b_% | Phase B 111st Current Magnitude Harmonics | float | 2 | R
0x27F6 | 0x27F7 | 10230 | 10231 | MAG_200MS_HAR_I_111th_c_% | Phase C 111st Current Magnitude Harmonics | float | 2 | R
0x27F8 | 0x27F9 | 10232 | 10233 | MAG_200MS_HAR_I_111th_n_% | Phase N 111st Current Magnitude Harmonics | float | 2 | R
0x27FA | 0x27FB | 10234 | 10235 | MAG_200MS_HAR_V_112th_a_% | Phase A 112nd Voltage Magnitude Harmonics | float | 2 | R
0x27FC | 0x27FD | 10236 | 10237 | MAG_200MS_HAR_V_112th_b_% | Phase B 112nd Voltage Magnitude Harmonics | float | 2 | R
0x27FE | 0x27FF | 10238 | 10239 | MAG_200MS_HAR_V_112th_c_% | Phase C 112nd Voltage Magnitude Harmonics | float | 2 | R
0x2800 | 0x2801 | 10240 | 10241 | MAG_200MS_HAR_I_112th_a_% | Phase A 112nd Current Magnitude Harmonics | float | 2 | R
0x2802 | 0x2803 | 10242 | 10243 | MAG_200MS_HAR_I_112th_b_% | Phase B 112nd Current Magnitude Harmonics | float | 2 | R
0x2804 | 0x2805 | 10244 | 10245 | MAG_200MS_HAR_I_112th_c_% | Phase C 112nd Current Magnitude Harmonics | float | 2 | R
0x2806 | 0x2807 | 10246 | 10247 | MAG_200MS_HAR_I_112th_n_% | Phase N 112nd Current Magnitude Harmonics | float | 2 | R
0x2808 | 0x2809 | 10248 | 10249 | MAG_200MS_HAR_V_113th_a_% | Phase A 113rd Voltage Magnitude Harmonics | float | 2 | R
0x280A | 0x280B | 10250 | 10251 | MAG_200MS_HAR_V_113th_b_% | Phase B 113rd Voltage Magnitude Harmonics | float | 2 | R
0x280C | 0x280D | 10252 | 10253 | MAG_200MS_HAR_V_113th_c_% | Phase C 113rd Voltage Magnitude Harmonics | float | 2 | R
0x280E | 0x280F | 10254 | 10255 | MAG_200MS_HAR_I_113th_a_% | Phase A 113rd Current Magnitude Harmonics | float | 2 | R
0x2810 | 0x2811 | 10256 | 10257 | MAG_200MS_HAR_I_113th_b_% | Phase B 113rd Current Magnitude Harmonics | float | 2 | R
0x2812 | 0x2813 | 10258 | 10259 | MAG_200MS_HAR_I_113th_c_% | Phase C 113rd Current Magnitude Harmonics | float | 2 | R
0x2814 | 0x2815 | 10260 | 10261 | MAG_200MS_HAR_I_113th_n_% | Phase N 113rd Current Magnitude Harmonics | float | 2 | R
0x2816 | 0x2817 | 10262 | 10263 | MAG_200MS_HAR_V_114th_a_% | Phase A 114th Voltage Magnitude Harmonics | float | 2 | R
0x2818 | 0x2819 | 10264 | 10265 | MAG_200MS_HAR_V_114th_b_% | Phase B 114th Voltage Magnitude Harmonics | float | 2 | R
0x281A | 0x281B | 10266 | 10267 | MAG_200MS_HAR_V_114th_c_% | Phase C 114th Voltage Magnitude Harmonics | float | 2 | R
0x281C | 0x281D | 10268 | 10269 | MAG_200MS_HAR_I_114th_a_% | Phase A 114th Current Magnitude Harmonics | float | 2 | R
0x281E | 0x281F | 10270 | 10271 | MAG_200MS_HAR_I_114th_b_% | Phase B 114th Current Magnitude Harmonics | float | 2 | R
0x2820 | 0x2821 | 10272 | 10273 | MAG_200MS_HAR_I_114th_c_% | Phase C 114th Current Magnitude Harmonics | float | 2 | R
0x2822 | 0x2823 | 10274 | 10275 | MAG_200MS_HAR_I_114th_n_% | Phase N 114th Current Magnitude Harmonics | float | 2 | R
0x2824 | 0x2825 | 10276 | 10277 | MAG_200MS_HAR_V_115th_a_% | Phase A 115th Voltage Magnitude Harmonics | float | 2 | R
0x2826 | 0x2827 | 10278 | 10279 | MAG_200MS_HAR_V_115th_b_% | Phase B 115th Voltage Magnitude Harmonics | float | 2 | R
0x2828 | 0x2829 | 10280 | 10281 | MAG_200MS_HAR_V_115th_c_% | Phase C 115th Voltage Magnitude Harmonics | float | 2 | R
0x282A | 0x282B | 10282 | 10283 | MAG_200MS_HAR_I_115th_a_% | Phase A 115th Current Magnitude Harmonics | float | 2 | R
0x282C | 0x282D | 10284 | 10285 | MAG_200MS_HAR_I_115th_b_% | Phase B 115th Current Magnitude Harmonics | float | 2 | R
0x282E | 0x282F | 10286 | 10287 | MAG_200MS_HAR_I_115th_c_% | Phase C 115th Current Magnitude Harmonics | float | 2 | R
0x2830 | 0x2831 | 10288 | 10289 | MAG_200MS_HAR_I_115th_n_% | Phase N 115th Current Magnitude Harmonics | float | 2 | R
0x2832 | 0x2833 | 10290 | 10291 | MAG_200MS_HAR_V_116th_a_% | Phase A 116th Voltage Magnitude Harmonics | float | 2 | R
0x2834 | 0x2835 | 10292 | 10293 | MAG_200MS_HAR_V_116th_b_% | Phase B 116th Voltage Magnitude Harmonics | float | 2 | R
0x2836 | 0x2837 | 10294 | 10295 | MAG_200MS_HAR_V_116th_c_% | Phase C 116th Voltage Magnitude Harmonics | float | 2 | R
0x2838 | 0x2839 | 10296 | 10297 | MAG_200MS_HAR_I_116th_a_% | Phase A 116th Current Magnitude Harmonics | float | 2 | R
0x283A | 0x283B | 10298 | 10299 | MAG_200MS_HAR_I_116th_b_% | Phase B 116th Current Magnitude Harmonics | float | 2 | R
0x283C | 0x283D | 10300 | 10301 | MAG_200MS_HAR_I_116th_c_% | Phase C 116th Current Magnitude Harmonics | float | 2 | R
0x283E | 0x283F | 10302 | 10303 | MAG_200MS_HAR_I_116th_n_% | Phase N 116th Current Magnitude Harmonics | float | 2 | R
0x2840 | 0x2841 | 10304 | 10305 | MAG_200MS_HAR_V_117th_a_% | Phase A 117th Voltage Magnitude Harmonics | float | 2 | R
0x2842 | 0x2843 | 10306 | 10307 | MAG_200MS_HAR_V_117th_b_% | Phase B 117th Voltage Magnitude Harmonics | float | 2 | R
0x2844 | 0x2845 | 10308 | 10309 | MAG_200MS_HAR_V_117th_c_% | Phase C 117th Voltage Magnitude Harmonics | float | 2 | R
0x2846 | 0x2847 | 10310 | 10311 | MAG_200MS_HAR_I_117th_a_% | Phase A 117th Current Magnitude Harmonics | float | 2 | R
0x2848 | 0x2849 | 10312 | 10313 | MAG_200MS_HAR_I_117th_b_% | Phase B 117th Current Magnitude Harmonics | float | 2 | R
0x284A | 0x284B | 10314 | 10315 | MAG_200MS_HAR_I_117th_c_% | Phase C 117th Current Magnitude Harmonics | float | 2 | R
0x284C | 0x284D | 10316 | 10317 | MAG_200MS_HAR_I_117th_n_% | Phase N 117th Current Magnitude Harmonics | float | 2 | R
0x284E | 0x284F | 10318 | 10319 | MAG_200MS_HAR_V_118th_a_% | Phase A 118th Voltage Magnitude Harmonics | float | 2 | R
0x2850 | 0x2851 | 10320 | 10321 | MAG_200MS_HAR_V_118th_b_% | Phase B 118th Voltage Magnitude Harmonics | float | 2 | R
0x2852 | 0x2853 | 10322 | 10323 | MAG_200MS_HAR_V_118th_c_% | Phase C 118th Voltage Magnitude Harmonics | float | 2 | R
0x2854 | 0x2855 | 10324 | 10325 | MAG_200MS_HAR_I_118th_a_% | Phase A 118th Current Magnitude Harmonics | float | 2 | R
0x2856 | 0x2857 | 10326 | 10327 | MAG_200MS_HAR_I_118th_b_% | Phase B 118th Current Magnitude Harmonics | float | 2 | R
0x2858 | 0x2859 | 10328 | 10329 | MAG_200MS_HAR_I_118th_c_% | Phase C 118th Current Magnitude Harmonics | float | 2 | R
0x285A | 0x285B | 10330 | 10331 | MAG_200MS_HAR_I_118th_n_% | Phase N 118th Current Magnitude Harmonics | float | 2 | R
0x285C | 0x285D | 10332 | 10333 | MAG_200MS_HAR_V_119th_a_% | Phase A 119th Voltage Magnitude Harmonics | float | 2 | R
0x285E | 0x285F | 10334 | 10335 | MAG_200MS_HAR_V_119th_b_% | Phase B 119th Voltage Magnitude Harmonics | float | 2 | R
0x2860 | 0x2861 | 10336 | 10337 | MAG_200MS_HAR_V_119th_c_% | Phase C 119th Voltage Magnitude Harmonics | float | 2 | R
0x2862 | 0x2863 | 10338 | 10339 | MAG_200MS_HAR_I_119th_a_% | Phase A 119th Current Magnitude Harmonics | float | 2 | R
0x2864 | 0x2865 | 10340 | 10341 | MAG_200MS_HAR_I_119th_b_% | Phase B 119th Current Magnitude Harmonics | float | 2 | R
0x2866 | 0x2867 | 10342 | 10343 | MAG_200MS_HAR_I_119th_c_% | Phase C 119th Current Magnitude Harmonics | float | 2 | R
0x2868 | 0x2869 | 10344 | 10345 | MAG_200MS_HAR_I_119th_n_% | Phase N 119th Current Magnitude Harmonics | float | 2 | R
0x286A | 0x286B | 10346 | 10347 | MAG_200MS_HAR_V_120th_a_% | Phase A 120th Voltage Magnitude Harmonics | float | 2 | R
0x286C | 0x286D | 10348 | 10349 | MAG_200MS_HAR_V_120th_b_% | Phase B 120th Voltage Magnitude Harmonics | float | 2 | R
0x286E | 0x286F | 10350 | 10351 | MAG_200MS_HAR_V_120th_c_% | Phase C 120th Voltage Magnitude Harmonics | float | 2 | R
0x2870 | 0x2871 | 10352 | 10353 | MAG_200MS_HAR_I_120th_a_% | Phase A 120th Current Magnitude Harmonics | float | 2 | R
0x2872 | 0x2873 | 10354 | 10355 | MAG_200MS_HAR_I_120th_b_% | Phase B 120th Current Magnitude Harmonics | float | 2 | R
0x2874 | 0x2875 | 10356 | 10357 | MAG_200MS_HAR_I_120th_c_% | Phase C 120th Current Magnitude Harmonics | float | 2 | R
0x2876 | 0x2877 | 10358 | 10359 | MAG_200MS_HAR_I_120th_n_% | Phase N 120th Current Magnitude Harmonics | float | 2 | R
0x2878 | 0x2879 | 10360 | 10361 | MAG_200MS_HAR_V_121th_a_% | Phase A 121st Voltage Magnitude Harmonics | float | 2 | R
0x287A | 0x287B | 10362 | 10363 | MAG_200MS_HAR_V_121th_b_% | Phase B 121st Voltage Magnitude Harmonics | float | 2 | R
0x287C | 0x287D | 10364 | 10365 | MAG_200MS_HAR_V_121th_c_% | Phase C 121st Voltage Magnitude Harmonics | float | 2 | R
0x287E | 0x287F | 10366 | 10367 | MAG_200MS_HAR_I_121th_a_% | Phase A 121st Current Magnitude Harmonics | float | 2 | R
0x2880 | 0x2881 | 10368 | 10369 | MAG_200MS_HAR_I_121th_b_% | Phase B 121st Current Magnitude Harmonics | float | 2 | R
0x2882 | 0x2883 | 10370 | 10371 | MAG_200MS_HAR_I_121th_c_% | Phase C 121st Current Magnitude Harmonics | float | 2 | R
0x2884 | 0x2885 | 10372 | 10373 | MAG_200MS_HAR_I_121th_n_% | Phase N 121st Current Magnitude Harmonics | float | 2 | R
0x2886 | 0x2887 | 10374 | 10375 | MAG_200MS_HAR_V_122th_a_% | Phase A 122nd Voltage Magnitude Harmonics | float | 2 | R
0x2888 | 0x2889 | 10376 | 10377 | MAG_200MS_HAR_V_122th_b_% | Phase B 122nd Voltage Magnitude Harmonics | float | 2 | R
0x288A | 0x288B | 10378 | 10379 | MAG_200MS_HAR_V_122th_c_% | Phase C 122nd Voltage Magnitude Harmonics | float | 2 | R
0x288C | 0x288D | 10380 | 10381 | MAG_200MS_HAR_I_122th_a_% | Phase A 122nd Current Magnitude Harmonics | float | 2 | R
0x288E | 0x288F | 10382 | 10383 | MAG_200MS_HAR_I_122th_b_% | Phase B 122nd Current Magnitude Harmonics | float | 2 | R
0x2890 | 0x2891 | 10384 | 10385 | MAG_200MS_HAR_I_122th_c_% | Phase C 122nd Current Magnitude Harmonics | float | 2 | R
0x2892 | 0x2893 | 10386 | 10387 | MAG_200MS_HAR_I_122th_n_% | Phase N 122nd Current Magnitude Harmonics | float | 2 | R
0x2894 | 0x2895 | 10388 | 10389 | MAG_200MS_HAR_V_123th_a_% | Phase A 123rd Voltage Magnitude Harmonics | float | 2 | R
0x2896 | 0x2897 | 10390 | 10391 | MAG_200MS_HAR_V_123th_b_% | Phase B 123rd Voltage Magnitude Harmonics | float | 2 | R
0x2898 | 0x2899 | 10392 | 10393 | MAG_200MS_HAR_V_123th_c_% | Phase C 123rd Voltage Magnitude Harmonics | float | 2 | R
0x289A | 0x289B | 10394 | 10395 | MAG_200MS_HAR_I_123th_a_% | Phase A 123rd Current Magnitude Harmonics | float | 2 | R
0x289C | 0x289D | 10396 | 10397 | MAG_200MS_HAR_I_123th_b_% | Phase B 123rd Current Magnitude Harmonics | float | 2 | R
0x289E | 0x289F | 10398 | 10399 | MAG_200MS_HAR_I_123th_c_% | Phase C 123rd Current Magnitude Harmonics | float | 2 | R
0x28A0 | 0x28A1 | 10400 | 10401 | MAG_200MS_HAR_I_123th_n_% | Phase N 123rd Current Magnitude Harmonics | float | 2 | R
0x28A2 | 0x28A3 | 10402 | 10403 | MAG_200MS_HAR_V_124th_a_% | Phase A 124th Voltage Magnitude Harmonics | float | 2 | R
0x28A4 | 0x28A5 | 10404 | 10405 | MAG_200MS_HAR_V_124th_b_% | Phase B 124th Voltage Magnitude Harmonics | float | 2 | R
0x28A6 | 0x28A7 | 10406 | 10407 | MAG_200MS_HAR_V_124th_c_% | Phase C 124th Voltage Magnitude Harmonics | float | 2 | R
0x28A8 | 0x28A9 | 10408 | 10409 | MAG_200MS_HAR_I_124th_a_% | Phase A 124th Current Magnitude Harmonics | float | 2 | R
0x28AA | 0x28AB | 10410 | 10411 | MAG_200MS_HAR_I_124th_b_% | Phase B 124th Current Magnitude Harmonics | float | 2 | R
0x28AC | 0x28AD | 10412 | 10413 | MAG_200MS_HAR_I_124th_c_% | Phase C 124th Current Magnitude Harmonics | float | 2 | R
0x28AE | 0x28AF | 10414 | 10415 | MAG_200MS_HAR_I_124th_n_% | Phase N 124th Current Magnitude Harmonics | float | 2 | R
0x28B0 | 0x28B1 | 10416 | 10417 | MAG_200MS_HAR_V_125th_a_% | Phase A 125th Voltage Magnitude Harmonics | float | 2 | R
0x28B2 | 0x28B3 | 10418 | 10419 | MAG_200MS_HAR_V_125th_b_% | Phase B 125th Voltage Magnitude Harmonics | float | 2 | R
0x28B4 | 0x28B5 | 10420 | 10421 | MAG_200MS_HAR_V_125th_c_% | Phase C 125th Voltage Magnitude Harmonics | float | 2 | R
0x28B6 | 0x28B7 | 10422 | 10423 | MAG_200MS_HAR_I_125th_a_% | Phase A 125th Current Magnitude Harmonics | float | 2 | R
0x28B8 | 0x28B9 | 10424 | 10425 | MAG_200MS_HAR_I_125th_b_% | Phase B 125th Current Magnitude Harmonics | float | 2 | R
0x28BA | 0x28BB | 10426 | 10427 | MAG_200MS_HAR_I_125th_c_% | Phase C 125th Current Magnitude Harmonics | float | 2 | R
0x28BC | 0x28BD | 10428 | 10429 | MAG_200MS_HAR_I_125th_n_% | Phase N 125th Current Magnitude Harmonics | float | 2 | R
0x28BE | 0x28BF | 10430 | 10431 | MAG_200MS_HAR_V_126th_a_% | Phase A 126th Voltage Magnitude Harmonics | float | 2 | R
0x28C0 | 0x28C1 | 10432 | 10433 | MAG_200MS_HAR_V_126th_b_% | Phase B 126th Voltage Magnitude Harmonics | float | 2 | R
0x28C2 | 0x28C3 | 10434 | 10435 | MAG_200MS_HAR_V_126th_c_% | Phase C 126th Voltage Magnitude Harmonics | float | 2 | R
0x28C4 | 0x28C5 | 10436 | 10437 | MAG_200MS_HAR_I_126th_a_% | Phase A 126th Current Magnitude Harmonics | float | 2 | R
0x28C6 | 0x28C7 | 10438 | 10439 | MAG_200MS_HAR_I_126th_b_% | Phase B 126th Current Magnitude Harmonics | float | 2 | R
0x28C8 | 0x28C9 | 10440 | 10441 | MAG_200MS_HAR_I_126th_c_% | Phase C 126th Current Magnitude Harmonics | float | 2 | R
0x28CA | 0x28CB | 10442 | 10443 | MAG_200MS_HAR_I_126th_n_% | Phase N 126th Current Magnitude Harmonics | float | 2 | R
0x28CC | 0x28CD | 10444 | 10445 | MAG_200MS_HAR_V_127th_a_% | Phase A 127th Voltage Magnitude Harmonics | float | 2 | R
0x28CE | 0x28CF | 10446 | 10447 | MAG_200MS_HAR_V_127th_b_% | Phase B 127th Voltage Magnitude Harmonics | float | 2 | R
0x28D0 | 0x28D1 | 10448 | 10449 | MAG_200MS_HAR_V_127th_c_% | Phase C 127th Voltage Magnitude Harmonics | float | 2 | R
0x28D2 | 0x28D3 | 10450 | 10451 | MAG_200MS_HAR_I_127th_a_% | Phase A 127th Current Magnitude Harmonics | float | 2 | R
0x28D4 | 0x28D5 | 10452 | 10453 | MAG_200MS_HAR_I_127th_b_% | Phase B 127th Current Magnitude Harmonics | float | 2 | R
0x28D6 | 0x28D7 | 10454 | 10455 | MAG_200MS_HAR_I_127th_c_% | Phase C 127th Current Magnitude Harmonics | float | 2 | R
0x28D8 | 0x28D9 | 10456 | 10457 | MAG_200MS_HAR_I_127th_n_% | Phase N 127th Current Magnitude Harmonics | float | 2 | R
0x28DA | 0x28DB | 10458 | 10459 | ANG_200MS_HAR_V_1th_a | Phase A 1st Voltage Angle Harmonics | float | 2 | R
0x28DC | 0x28DD | 10460 | 10461 | ANG_200MS_HAR_V_1th_b | Phase B 1st Voltage Angle Harmonics | float | 2 | R
0x28DE | 0x28DF | 10462 | 10463 | ANG_200MS_HAR_V_1th_c | Phase C 1st Voltage Angle Harmonics | float | 2 | R
0x28E0 | 0x28E1 | 10464 | 10465 | ANG_200MS_HAR_I_1th_a | Phase A 1st Current Angle Harmonics | float | 2 | R
0x28E2 | 0x28E3 | 10466 | 10467 | ANG_200MS_HAR_I_1th_b | Phase B 1st Current Angle Harmonics | float | 2 | R
0x28E4 | 0x28E5 | 10468 | 10469 | ANG_200MS_HAR_I_1th_c | Phase C 1st Current Angle Harmonics | float | 2 | R
0x28E6 | 0x28E7 | 10470 | 10471 | ANG_200MS_HAR_I_1th_n | Phase N 1st Current Angle Harmonics | float | 2 | R
0x28E8 | 0x28E9 | 10472 | 10473 | ANG_200MS_HAR_V_2th_a | Phase A 2nd Voltage Angle Harmonics | float | 2 | R
0x28EA | 0x28EB | 10474 | 10475 | ANG_200MS_HAR_V_2th_b | Phase B 2nd Voltage Angle Harmonics | float | 2 | R
0x28EC | 0x28ED | 10476 | 10477 | ANG_200MS_HAR_V_2th_c | Phase C 2nd Voltage Angle Harmonics | float | 2 | R
0x28EE | 0x28EF | 10478 | 10479 | ANG_200MS_HAR_I_2th_a | Phase A 2nd Current Angle Harmonics | float | 2 | R
0x28F0 | 0x28F1 | 10480 | 10481 | ANG_200MS_HAR_I_2th_b | Phase B 2nd Current Angle Harmonics | float | 2 | R
0x28F2 | 0x28F3 | 10482 | 10483 | ANG_200MS_HAR_I_2th_c | Phase C 2nd Current Angle Harmonics | float | 2 | R
0x28F4 | 0x28F5 | 10484 | 10485 | ANG_200MS_HAR_I_2th_n | Phase N 2nd Current Angle Harmonics | float | 2 | R
0x28F6 | 0x28F7 | 10486 | 10487 | ANG_200MS_HAR_V_3th_a | Phase A 3rd Voltage Angle Harmonics | float | 2 | R
0x28F8 | 0x28F9 | 10488 | 10489 | ANG_200MS_HAR_V_3th_b | Phase B 3rd Voltage Angle Harmonics | float | 2 | R
0x28FA | 0x28FB | 10490 | 10491 | ANG_200MS_HAR_V_3th_c | Phase C 3rd Voltage Angle Harmonics | float | 2 | R
0x28FC | 0x28FD | 10492 | 10493 | ANG_200MS_HAR_I_3th_a | Phase A 3rd Current Angle Harmonics | float | 2 | R
0x28FE | 0x28FF | 10494 | 10495 | ANG_200MS_HAR_I_3th_b | Phase B 3rd Current Angle Harmonics | float | 2 | R
0x2900 | 0x2901 | 10496 | 10497 | ANG_200MS_HAR_I_3th_c | Phase C 3rd Current Angle Harmonics | float | 2 | R
0x2902 | 0x2903 | 10498 | 10499 | ANG_200MS_HAR_I_3th_n | Phase N 3rd Current Angle Harmonics | float | 2 | R
0x2904 | 0x2905 | 10500 | 10501 | ANG_200MS_HAR_V_4th_a | Phase A 4th Voltage Angle Harmonics | float | 2 | R
0x2906 | 0x2907 | 10502 | 10503 | ANG_200MS_HAR_V_4th_b | Phase B 4th Voltage Angle Harmonics | float | 2 | R
0x2908 | 0x2909 | 10504 | 10505 | ANG_200MS_HAR_V_4th_c | Phase C 4th Voltage Angle Harmonics | float | 2 | R
0x290A | 0x290B | 10506 | 10507 | ANG_200MS_HAR_I_4th_a | Phase A 4th Current Angle Harmonics | float | 2 | R
0x290C | 0x290D | 10508 | 10509 | ANG_200MS_HAR_I_4th_b | Phase B 4th Current Angle Harmonics | float | 2 | R
0x290E | 0x290F | 10510 | 10511 | ANG_200MS_HAR_I_4th_c | Phase C 4th Current Angle Harmonics | float | 2 | R
0x2910 | 0x2911 | 10512 | 10513 | ANG_200MS_HAR_I_4th_n | Phase N 4th Current Angle Harmonics | float | 2 | R
0x2912 | 0x2913 | 10514 | 10515 | ANG_200MS_HAR_V_5th_a | Phase A 5th Voltage Angle Harmonics | float | 2 | R
0x2914 | 0x2915 | 10516 | 10517 | ANG_200MS_HAR_V_5th_b | Phase B 5th Voltage Angle Harmonics | float | 2 | R
0x2916 | 0x2917 | 10518 | 10519 | ANG_200MS_HAR_V_5th_c | Phase C 5th Voltage Angle Harmonics | float | 2 | R
0x2918 | 0x2919 | 10520 | 10521 | ANG_200MS_HAR_I_5th_a | Phase A 5th Current Angle Harmonics | float | 2 | R
0x291A | 0x291B | 10522 | 10523 | ANG_200MS_HAR_I_5th_b | Phase B 5th Current Angle Harmonics | float | 2 | R
0x291C | 0x291D | 10524 | 10525 | ANG_200MS_HAR_I_5th_c | Phase C 5th Current Angle Harmonics | float | 2 | R
0x291E | 0x291F | 10526 | 10527 | ANG_200MS_HAR_I_5th_n | Phase N 5th Current Angle Harmonics | float | 2 | R
0x2920 | 0x2921 | 10528 | 10529 | ANG_200MS_HAR_V_6th_a | Phase A 6th Voltage Angle Harmonics | float | 2 | R
0x2922 | 0x2923 | 10530 | 10531 | ANG_200MS_HAR_V_6th_b | Phase B 6th Voltage Angle Harmonics | float | 2 | R
0x2924 | 0x2925 | 10532 | 10533 | ANG_200MS_HAR_V_6th_c | Phase C 6th Voltage Angle Harmonics | float | 2 | R
0x2926 | 0x2927 | 10534 | 10535 | ANG_200MS_HAR_I_6th_a | Phase A 6th Current Angle Harmonics | float | 2 | R
0x2928 | 0x2929 | 10536 | 10537 | ANG_200MS_HAR_I_6th_b | Phase B 6th Current Angle Harmonics | float | 2 | R
0x292A | 0x292B | 10538 | 10539 | ANG_200MS_HAR_I_6th_c | Phase C 6th Current Angle Harmonics | float | 2 | R
0x292C | 0x292D | 10540 | 10541 | ANG_200MS_HAR_I_6th_n | Phase N 6th Current Angle Harmonics | float | 2 | R
0x292E | 0x292F | 10542 | 10543 | ANG_200MS_HAR_V_7th_a | Phase A 7th Voltage Angle Harmonics | float | 2 | R
0x2930 | 0x2931 | 10544 | 10545 | ANG_200MS_HAR_V_7th_b | Phase B 7th Voltage Angle Harmonics | float | 2 | R
0x2932 | 0x2933 | 10546 | 10547 | ANG_200MS_HAR_V_7th_c | Phase C 7th Voltage Angle Harmonics | float | 2 | R
0x2934 | 0x2935 | 10548 | 10549 | ANG_200MS_HAR_I_7th_a | Phase A 7th Current Angle Harmonics | float | 2 | R
0x2936 | 0x2937 | 10550 | 10551 | ANG_200MS_HAR_I_7th_b | Phase B 7th Current Angle Harmonics | float | 2 | R
0x2938 | 0x2939 | 10552 | 10553 | ANG_200MS_HAR_I_7th_c | Phase C 7th Current Angle Harmonics | float | 2 | R
0x293A | 0x293B | 10554 | 10555 | ANG_200MS_HAR_I_7th_n | Phase N 7th Current Angle Harmonics | float | 2 | R
0x293C | 0x293D | 10556 | 10557 | ANG_200MS_HAR_V_8th_a | Phase A 8th Voltage Angle Harmonics | float | 2 | R
0x293E | 0x293F | 10558 | 10559 | ANG_200MS_HAR_V_8th_b | Phase B 8th Voltage Angle Harmonics | float | 2 | R
0x2940 | 0x2941 | 10560 | 10561 | ANG_200MS_HAR_V_8th_c | Phase C 8th Voltage Angle Harmonics | float | 2 | R
0x2942 | 0x2943 | 10562 | 10563 | ANG_200MS_HAR_I_8th_a | Phase A 8th Current Angle Harmonics | float | 2 | R
0x2944 | 0x2945 | 10564 | 10565 | ANG_200MS_HAR_I_8th_b | Phase B 8th Current Angle Harmonics | float | 2 | R
0x2946 | 0x2947 | 10566 | 10567 | ANG_200MS_HAR_I_8th_c | Phase C 8th Current Angle Harmonics | float | 2 | R
0x2948 | 0x2949 | 10568 | 10569 | ANG_200MS_HAR_I_8th_n | Phase N 8th Current Angle Harmonics | float | 2 | R
0x294A | 0x294B | 10570 | 10571 | ANG_200MS_HAR_V_9th_a | Phase A 9th Voltage Angle Harmonics | float | 2 | R
0x294C | 0x294D | 10572 | 10573 | ANG_200MS_HAR_V_9th_b | Phase B 9th Voltage Angle Harmonics | float | 2 | R
0x294E | 0x294F | 10574 | 10575 | ANG_200MS_HAR_V_9th_c | Phase C 9th Voltage Angle Harmonics | float | 2 | R
0x2950 | 0x2951 | 10576 | 10577 | ANG_200MS_HAR_I_9th_a | Phase A 9th Current Angle Harmonics | float | 2 | R
0x2952 | 0x2953 | 10578 | 10579 | ANG_200MS_HAR_I_9th_b | Phase B 9th Current Angle Harmonics | float | 2 | R
0x2954 | 0x2955 | 10580 | 10581 | ANG_200MS_HAR_I_9th_c | Phase C 9th Current Angle Harmonics | float | 2 | R
0x2956 | 0x2957 | 10582 | 10583 | ANG_200MS_HAR_I_9th_n | Phase N 9th Current Angle Harmonics | float | 2 | R
0x2958 | 0x2959 | 10584 | 10585 | ANG_200MS_HAR_V_10th_a | Phase A 10th Voltage Angle Harmonics | float | 2 | R
0x295A | 0x295B | 10586 | 10587 | ANG_200MS_HAR_V_10th_b | Phase B 10th Voltage Angle Harmonics | float | 2 | R
0x295C | 0x295D | 10588 | 10589 | ANG_200MS_HAR_V_10th_c | Phase C 10th Voltage Angle Harmonics | float | 2 | R
0x295E | 0x295F | 10590 | 10591 | ANG_200MS_HAR_I_10th_a | Phase A 10th Current Angle Harmonics | float | 2 | R
0x2960 | 0x2961 | 10592 | 10593 | ANG_200MS_HAR_I_10th_b | Phase B 10th Current Angle Harmonics | float | 2 | R
0x2962 | 0x2963 | 10594 | 10595 | ANG_200MS_HAR_I_10th_c | Phase C 10th Current Angle Harmonics | float | 2 | R
0x2964 | 0x2965 | 10596 | 10597 | ANG_200MS_HAR_I_10th_n | Phase N 10th Current Angle Harmonics | float | 2 | R
0x2966 | 0x2967 | 10598 | 10599 | ANG_200MS_HAR_V_11th_a | Phase A 11st Voltage Angle Harmonics | float | 2 | R
0x2968 | 0x2969 | 10600 | 10601 | ANG_200MS_HAR_V_11th_b | Phase B 11st Voltage Angle Harmonics | float | 2 | R
0x296A | 0x296B | 10602 | 10603 | ANG_200MS_HAR_V_11th_c | Phase C 11st Voltage Angle Harmonics | float | 2 | R
0x296C | 0x296D | 10604 | 10605 | ANG_200MS_HAR_I_11th_a | Phase A 11st Current Angle Harmonics | float | 2 | R
0x296E | 0x296F | 10606 | 10607 | ANG_200MS_HAR_I_11th_b | Phase B 11st Current Angle Harmonics | float | 2 | R
0x2970 | 0x2971 | 10608 | 10609 | ANG_200MS_HAR_I_11th_c | Phase C 11st Current Angle Harmonics | float | 2 | R
0x2972 | 0x2973 | 10610 | 10611 | ANG_200MS_HAR_I_11th_n | Phase N 11st Current Angle Harmonics | float | 2 | R
0x2974 | 0x2975 | 10612 | 10613 | ANG_200MS_HAR_V_12th_a | Phase A 12nd Voltage Angle Harmonics | float | 2 | R
0x2976 | 0x2977 | 10614 | 10615 | ANG_200MS_HAR_V_12th_b | Phase B 12nd Voltage Angle Harmonics | float | 2 | R
0x2978 | 0x2979 | 10616 | 10617 | ANG_200MS_HAR_V_12th_c | Phase C 12nd Voltage Angle Harmonics | float | 2 | R
0x297A | 0x297B | 10618 | 10619 | ANG_200MS_HAR_I_12th_a | Phase A 12nd Current Angle Harmonics | float | 2 | R
0x297C | 0x297D | 10620 | 10621 | ANG_200MS_HAR_I_12th_b | Phase B 12nd Current Angle Harmonics | float | 2 | R
0x297E | 0x297F | 10622 | 10623 | ANG_200MS_HAR_I_12th_c | Phase C 12nd Current Angle Harmonics | float | 2 | R
0x2980 | 0x2981 | 10624 | 10625 | ANG_200MS_HAR_I_12th_n | Phase N 12nd Current Angle Harmonics | float | 2 | R
0x2982 | 0x2983 | 10626 | 10627 | ANG_200MS_HAR_V_13th_a | Phase A 13rd Voltage Angle Harmonics | float | 2 | R
0x2984 | 0x2985 | 10628 | 10629 | ANG_200MS_HAR_V_13th_b | Phase B 13rd Voltage Angle Harmonics | float | 2 | R
0x2986 | 0x2987 | 10630 | 10631 | ANG_200MS_HAR_V_13th_c | Phase C 13rd Voltage Angle Harmonics | float | 2 | R
0x2988 | 0x2989 | 10632 | 10633 | ANG_200MS_HAR_I_13th_a | Phase A 13rd Current Angle Harmonics | float | 2 | R
0x298A | 0x298B | 10634 | 10635 | ANG_200MS_HAR_I_13th_b | Phase B 13rd Current Angle Harmonics | float | 2 | R
0x298C | 0x298D | 10636 | 10637 | ANG_200MS_HAR_I_13th_c | Phase C 13rd Current Angle Harmonics | float | 2 | R
0x298E | 0x298F | 10638 | 10639 | ANG_200MS_HAR_I_13th_n | Phase N 13rd Current Angle Harmonics | float | 2 | R
0x2990 | 0x2991 | 10640 | 10641 | ANG_200MS_HAR_V_14th_a | Phase A 14th Voltage Angle Harmonics | float | 2 | R
0x2992 | 0x2993 | 10642 | 10643 | ANG_200MS_HAR_V_14th_b | Phase B 14th Voltage Angle Harmonics | float | 2 | R
0x2994 | 0x2995 | 10644 | 10645 | ANG_200MS_HAR_V_14th_c | Phase C 14th Voltage Angle Harmonics | float | 2 | R
0x2996 | 0x2997 | 10646 | 10647 | ANG_200MS_HAR_I_14th_a | Phase A 14th Current Angle Harmonics | float | 2 | R
0x2998 | 0x2999 | 10648 | 10649 | ANG_200MS_HAR_I_14th_b | Phase B 14th Current Angle Harmonics | float | 2 | R
0x299A | 0x299B | 10650 | 10651 | ANG_200MS_HAR_I_14th_c | Phase C 14th Current Angle Harmonics | float | 2 | R
0x299C | 0x299D | 10652 | 10653 | ANG_200MS_HAR_I_14th_n | Phase N 14th Current Angle Harmonics | float | 2 | R
0x299E | 0x299F | 10654 | 10655 | ANG_200MS_HAR_V_15th_a | Phase A 15th Voltage Angle Harmonics | float | 2 | R
0x29A0 | 0x29A1 | 10656 | 10657 | ANG_200MS_HAR_V_15th_b | Phase B 15th Voltage Angle Harmonics | float | 2 | R
0x29A2 | 0x29A3 | 10658 | 10659 | ANG_200MS_HAR_V_15th_c | Phase C 15th Voltage Angle Harmonics | float | 2 | R
0x29A4 | 0x29A5 | 10660 | 10661 | ANG_200MS_HAR_I_15th_a | Phase A 15th Current Angle Harmonics | float | 2 | R
0x29A6 | 0x29A7 | 10662 | 10663 | ANG_200MS_HAR_I_15th_b | Phase B 15th Current Angle Harmonics | float | 2 | R
0x29A8 | 0x29A9 | 10664 | 10665 | ANG_200MS_HAR_I_15th_c | Phase C 15th Current Angle Harmonics | float | 2 | R
0x29AA | 0x29AB | 10666 | 10667 | ANG_200MS_HAR_I_15th_n | Phase N 15th Current Angle Harmonics | float | 2 | R
0x29AC | 0x29AD | 10668 | 10669 | ANG_200MS_HAR_V_16th_a | Phase A 16th Voltage Angle Harmonics | float | 2 | R
0x29AE | 0x29AF | 10670 | 10671 | ANG_200MS_HAR_V_16th_b | Phase B 16th Voltage Angle Harmonics | float | 2 | R
0x29B0 | 0x29B1 | 10672 | 10673 | ANG_200MS_HAR_V_16th_c | Phase C 16th Voltage Angle Harmonics | float | 2 | R
0x29B2 | 0x29B3 | 10674 | 10675 | ANG_200MS_HAR_I_16th_a | Phase A 16th Current Angle Harmonics | float | 2 | R
0x29B4 | 0x29B5 | 10676 | 10677 | ANG_200MS_HAR_I_16th_b | Phase B 16th Current Angle Harmonics | float | 2 | R
0x29B6 | 0x29B7 | 10678 | 10679 | ANG_200MS_HAR_I_16th_c | Phase C 16th Current Angle Harmonics | float | 2 | R
0x29B8 | 0x29B9 | 10680 | 10681 | ANG_200MS_HAR_I_16th_n | Phase N 16th Current Angle Harmonics | float | 2 | R
0x29BA | 0x29BB | 10682 | 10683 | ANG_200MS_HAR_V_17th_a | Phase A 17th Voltage Angle Harmonics | float | 2 | R
0x29BC | 0x29BD | 10684 | 10685 | ANG_200MS_HAR_V_17th_b | Phase B 17th Voltage Angle Harmonics | float | 2 | R
0x29BE | 0x29BF | 10686 | 10687 | ANG_200MS_HAR_V_17th_c | Phase C 17th Voltage Angle Harmonics | float | 2 | R
0x29C0 | 0x29C1 | 10688 | 10689 | ANG_200MS_HAR_I_17th_a | Phase A 17th Current Angle Harmonics | float | 2 | R
0x29C2 | 0x29C3 | 10690 | 10691 | ANG_200MS_HAR_I_17th_b | Phase B 17th Current Angle Harmonics | float | 2 | R
0x29C4 | 0x29C5 | 10692 | 10693 | ANG_200MS_HAR_I_17th_c | Phase C 17th Current Angle Harmonics | float | 2 | R
0x29C6 | 0x29C7 | 10694 | 10695 | ANG_200MS_HAR_I_17th_n | Phase N 17th Current Angle Harmonics | float | 2 | R
0x29C8 | 0x29C9 | 10696 | 10697 | ANG_200MS_HAR_V_18th_a | Phase A 18th Voltage Angle Harmonics | float | 2 | R
0x29CA | 0x29CB | 10698 | 10699 | ANG_200MS_HAR_V_18th_b | Phase B 18th Voltage Angle Harmonics | float | 2 | R
0x29CC | 0x29CD | 10700 | 10701 | ANG_200MS_HAR_V_18th_c | Phase C 18th Voltage Angle Harmonics | float | 2 | R
0x29CE | 0x29CF | 10702 | 10703 | ANG_200MS_HAR_I_18th_a | Phase A 18th Current Angle Harmonics | float | 2 | R
0x29D0 | 0x29D1 | 10704 | 10705 | ANG_200MS_HAR_I_18th_b | Phase B 18th Current Angle Harmonics | float | 2 | R
0x29D2 | 0x29D3 | 10706 | 10707 | ANG_200MS_HAR_I_18th_c | Phase C 18th Current Angle Harmonics | float | 2 | R
0x29D4 | 0x29D5 | 10708 | 10709 | ANG_200MS_HAR_I_18th_n | Phase N 18th Current Angle Harmonics | float | 2 | R
0x29D6 | 0x29D7 | 10710 | 10711 | ANG_200MS_HAR_V_19th_a | Phase A 19th Voltage Angle Harmonics | float | 2 | R
0x29D8 | 0x29D9 | 10712 | 10713 | ANG_200MS_HAR_V_19th_b | Phase B 19th Voltage Angle Harmonics | float | 2 | R
0x29DA | 0x29DB | 10714 | 10715 | ANG_200MS_HAR_V_19th_c | Phase C 19th Voltage Angle Harmonics | float | 2 | R
0x29DC | 0x29DD | 10716 | 10717 | ANG_200MS_HAR_I_19th_a | Phase A 19th Current Angle Harmonics | float | 2 | R
0x29DE | 0x29DF | 10718 | 10719 | ANG_200MS_HAR_I_19th_b | Phase B 19th Current Angle Harmonics | float | 2 | R
0x29E0 | 0x29E1 | 10720 | 10721 | ANG_200MS_HAR_I_19th_c | Phase C 19th Current Angle Harmonics | float | 2 | R
0x29E2 | 0x29E3 | 10722 | 10723 | ANG_200MS_HAR_I_19th_n | Phase N 19th Current Angle Harmonics | float | 2 | R
0x29E4 | 0x29E5 | 10724 | 10725 | ANG_200MS_HAR_V_20th_a | Phase A 20th Voltage Angle Harmonics | float | 2 | R
0x29E6 | 0x29E7 | 10726 | 10727 | ANG_200MS_HAR_V_20th_b | Phase B 20th Voltage Angle Harmonics | float | 2 | R
0x29E8 | 0x29E9 | 10728 | 10729 | ANG_200MS_HAR_V_20th_c | Phase C 20th Voltage Angle Harmonics | float | 2 | R
0x29EA | 0x29EB | 10730 | 10731 | ANG_200MS_HAR_I_20th_a | Phase A 20th Current Angle Harmonics | float | 2 | R
0x29EC | 0x29ED | 10732 | 10733 | ANG_200MS_HAR_I_20th_b | Phase B 20th Current Angle Harmonics | float | 2 | R
0x29EE | 0x29EF | 10734 | 10735 | ANG_200MS_HAR_I_20th_c | Phase C 20th Current Angle Harmonics | float | 2 | R
0x29F0 | 0x29F1 | 10736 | 10737 | ANG_200MS_HAR_I_20th_n | Phase N 20th Current Angle Harmonics | float | 2 | R
0x29F2 | 0x29F3 | 10738 | 10739 | ANG_200MS_HAR_V_21th_a | Phase A 21st Voltage Angle Harmonics | float | 2 | R
0x29F4 | 0x29F5 | 10740 | 10741 | ANG_200MS_HAR_V_21th_b | Phase B 21st Voltage Angle Harmonics | float | 2 | R
0x29F6 | 0x29F7 | 10742 | 10743 | ANG_200MS_HAR_V_21th_c | Phase C 21st Voltage Angle Harmonics | float | 2 | R
0x29F8 | 0x29F9 | 10744 | 10745 | ANG_200MS_HAR_I_21th_a | Phase A 21st Current Angle Harmonics | float | 2 | R
0x29FA | 0x29FB | 10746 | 10747 | ANG_200MS_HAR_I_21th_b | Phase B 21st Current Angle Harmonics | float | 2 | R
0x29FC | 0x29FD | 10748 | 10749 | ANG_200MS_HAR_I_21th_c | Phase C 21st Current Angle Harmonics | float | 2 | R
0x29FE | 0x29FF | 10750 | 10751 | ANG_200MS_HAR_I_21th_n | Phase N 21st Current Angle Harmonics | float | 2 | R
0x2A00 | 0x2A01 | 10752 | 10753 | ANG_200MS_HAR_V_22th_a | Phase A 22nd Voltage Angle Harmonics | float | 2 | R
0x2A02 | 0x2A03 | 10754 | 10755 | ANG_200MS_HAR_V_22th_b | Phase B 22nd Voltage Angle Harmonics | float | 2 | R
0x2A04 | 0x2A05 | 10756 | 10757 | ANG_200MS_HAR_V_22th_c | Phase C 22nd Voltage Angle Harmonics | float | 2 | R
0x2A06 | 0x2A07 | 10758 | 10759 | ANG_200MS_HAR_I_22th_a | Phase A 22nd Current Angle Harmonics | float | 2 | R
0x2A08 | 0x2A09 | 10760 | 10761 | ANG_200MS_HAR_I_22th_b | Phase B 22nd Current Angle Harmonics | float | 2 | R
0x2A0A | 0x2A0B | 10762 | 10763 | ANG_200MS_HAR_I_22th_c | Phase C 22nd Current Angle Harmonics | float | 2 | R
0x2A0C | 0x2A0D | 10764 | 10765 | ANG_200MS_HAR_I_22th_n | Phase N 22nd Current Angle Harmonics | float | 2 | R
0x2A0E | 0x2A0F | 10766 | 10767 | ANG_200MS_HAR_V_23th_a | Phase A 23rd Voltage Angle Harmonics | float | 2 | R
0x2A10 | 0x2A11 | 10768 | 10769 | ANG_200MS_HAR_V_23th_b | Phase B 23rd Voltage Angle Harmonics | float | 2 | R
0x2A12 | 0x2A13 | 10770 | 10771 | ANG_200MS_HAR_V_23th_c | Phase C 23rd Voltage Angle Harmonics | float | 2 | R
0x2A14 | 0x2A15 | 10772 | 10773 | ANG_200MS_HAR_I_23th_a | Phase A 23rd Current Angle Harmonics | float | 2 | R
0x2A16 | 0x2A17 | 10774 | 10775 | ANG_200MS_HAR_I_23th_b | Phase B 23rd Current Angle Harmonics | float | 2 | R
0x2A18 | 0x2A19 | 10776 | 10777 | ANG_200MS_HAR_I_23th_c | Phase C 23rd Current Angle Harmonics | float | 2 | R
0x2A1A | 0x2A1B | 10778 | 10779 | ANG_200MS_HAR_I_23th_n | Phase N 23rd Current Angle Harmonics | float | 2 | R
0x2A1C | 0x2A1D | 10780 | 10781 | ANG_200MS_HAR_V_24th_a | Phase A 24th Voltage Angle Harmonics | float | 2 | R
0x2A1E | 0x2A1F | 10782 | 10783 | ANG_200MS_HAR_V_24th_b | Phase B 24th Voltage Angle Harmonics | float | 2 | R
0x2A20 | 0x2A21 | 10784 | 10785 | ANG_200MS_HAR_V_24th_c | Phase C 24th Voltage Angle Harmonics | float | 2 | R
0x2A22 | 0x2A23 | 10786 | 10787 | ANG_200MS_HAR_I_24th_a | Phase A 24th Current Angle Harmonics | float | 2 | R
0x2A24 | 0x2A25 | 10788 | 10789 | ANG_200MS_HAR_I_24th_b | Phase B 24th Current Angle Harmonics | float | 2 | R
0x2A26 | 0x2A27 | 10790 | 10791 | ANG_200MS_HAR_I_24th_c | Phase C 24th Current Angle Harmonics | float | 2 | R
0x2A28 | 0x2A29 | 10792 | 10793 | ANG_200MS_HAR_I_24th_n | Phase N 24th Current Angle Harmonics | float | 2 | R
0x2A2A | 0x2A2B | 10794 | 10795 | ANG_200MS_HAR_V_25th_a | Phase A 25th Voltage Angle Harmonics | float | 2 | R
0x2A2C | 0x2A2D | 10796 | 10797 | ANG_200MS_HAR_V_25th_b | Phase B 25th Voltage Angle Harmonics | float | 2 | R
0x2A2E | 0x2A2F | 10798 | 10799 | ANG_200MS_HAR_V_25th_c | Phase C 25th Voltage Angle Harmonics | float | 2 | R
0x2A30 | 0x2A31 | 10800 | 10801 | ANG_200MS_HAR_I_25th_a | Phase A 25th Current Angle Harmonics | float | 2 | R
0x2A32 | 0x2A33 | 10802 | 10803 | ANG_200MS_HAR_I_25th_b | Phase B 25th Current Angle Harmonics | float | 2 | R
0x2A34 | 0x2A35 | 10804 | 10805 | ANG_200MS_HAR_I_25th_c | Phase C 25th Current Angle Harmonics | float | 2 | R
0x2A36 | 0x2A37 | 10806 | 10807 | ANG_200MS_HAR_I_25th_n | Phase N 25th Current Angle Harmonics | float | 2 | R
0x2A38 | 0x2A39 | 10808 | 10809 | ANG_200MS_HAR_V_26th_a | Phase A 26th Voltage Angle Harmonics | float | 2 | R
0x2A3A | 0x2A3B | 10810 | 10811 | ANG_200MS_HAR_V_26th_b | Phase B 26th Voltage Angle Harmonics | float | 2 | R
0x2A3C | 0x2A3D | 10812 | 10813 | ANG_200MS_HAR_V_26th_c | Phase C 26th Voltage Angle Harmonics | float | 2 | R
0x2A3E | 0x2A3F | 10814 | 10815 | ANG_200MS_HAR_I_26th_a | Phase A 26th Current Angle Harmonics | float | 2 | R
0x2A40 | 0x2A41 | 10816 | 10817 | ANG_200MS_HAR_I_26th_b | Phase B 26th Current Angle Harmonics | float | 2 | R
0x2A42 | 0x2A43 | 10818 | 10819 | ANG_200MS_HAR_I_26th_c | Phase C 26th Current Angle Harmonics | float | 2 | R
0x2A44 | 0x2A45 | 10820 | 10821 | ANG_200MS_HAR_I_26th_n | Phase N 26th Current Angle Harmonics | float | 2 | R
0x2A46 | 0x2A47 | 10822 | 10823 | ANG_200MS_HAR_V_27th_a | Phase A 27th Voltage Angle Harmonics | float | 2 | R
0x2A48 | 0x2A49 | 10824 | 10825 | ANG_200MS_HAR_V_27th_b | Phase B 27th Voltage Angle Harmonics | float | 2 | R
0x2A4A | 0x2A4B | 10826 | 10827 | ANG_200MS_HAR_V_27th_c | Phase C 27th Voltage Angle Harmonics | float | 2 | R
0x2A4C | 0x2A4D | 10828 | 10829 | ANG_200MS_HAR_I_27th_a | Phase A 27th Current Angle Harmonics | float | 2 | R
0x2A4E | 0x2A4F | 10830 | 10831 | ANG_200MS_HAR_I_27th_b | Phase B 27th Current Angle Harmonics | float | 2 | R
0x2A50 | 0x2A51 | 10832 | 10833 | ANG_200MS_HAR_I_27th_c | Phase C 27th Current Angle Harmonics | float | 2 | R
0x2A52 | 0x2A53 | 10834 | 10835 | ANG_200MS_HAR_I_27th_n | Phase N 27th Current Angle Harmonics | float | 2 | R
0x2A54 | 0x2A55 | 10836 | 10837 | ANG_200MS_HAR_V_28th_a | Phase A 28th Voltage Angle Harmonics | float | 2 | R
0x2A56 | 0x2A57 | 10838 | 10839 | ANG_200MS_HAR_V_28th_b | Phase B 28th Voltage Angle Harmonics | float | 2 | R
0x2A58 | 0x2A59 | 10840 | 10841 | ANG_200MS_HAR_V_28th_c | Phase C 28th Voltage Angle Harmonics | float | 2 | R
0x2A5A | 0x2A5B | 10842 | 10843 | ANG_200MS_HAR_I_28th_a | Phase A 28th Current Angle Harmonics | float | 2 | R
0x2A5C | 0x2A5D | 10844 | 10845 | ANG_200MS_HAR_I_28th_b | Phase B 28th Current Angle Harmonics | float | 2 | R
0x2A5E | 0x2A5F | 10846 | 10847 | ANG_200MS_HAR_I_28th_c | Phase C 28th Current Angle Harmonics | float | 2 | R
0x2A60 | 0x2A61 | 10848 | 10849 | ANG_200MS_HAR_I_28th_n | Phase N 28th Current Angle Harmonics | float | 2 | R
0x2A62 | 0x2A63 | 10850 | 10851 | ANG_200MS_HAR_V_29th_a | Phase A 29th Voltage Angle Harmonics | float | 2 | R
0x2A64 | 0x2A65 | 10852 | 10853 | ANG_200MS_HAR_V_29th_b | Phase B 29th Voltage Angle Harmonics | float | 2 | R
0x2A66 | 0x2A67 | 10854 | 10855 | ANG_200MS_HAR_V_29th_c | Phase C 29th Voltage Angle Harmonics | float | 2 | R
0x2A68 | 0x2A69 | 10856 | 10857 | ANG_200MS_HAR_I_29th_a | Phase A 29th Current Angle Harmonics | float | 2 | R
0x2A6A | 0x2A6B | 10858 | 10859 | ANG_200MS_HAR_I_29th_b | Phase B 29th Current Angle Harmonics | float | 2 | R
0x2A6C | 0x2A6D | 10860 | 10861 | ANG_200MS_HAR_I_29th_c | Phase C 29th Current Angle Harmonics | float | 2 | R
0x2A6E | 0x2A6F | 10862 | 10863 | ANG_200MS_HAR_I_29th_n | Phase N 29th Current Angle Harmonics | float | 2 | R
0x2A70 | 0x2A71 | 10864 | 10865 | ANG_200MS_HAR_V_30th_a | Phase A 30th Voltage Angle Harmonics | float | 2 | R
0x2A72 | 0x2A73 | 10866 | 10867 | ANG_200MS_HAR_V_30th_b | Phase B 30th Voltage Angle Harmonics | float | 2 | R
0x2A74 | 0x2A75 | 10868 | 10869 | ANG_200MS_HAR_V_30th_c | Phase C 30th Voltage Angle Harmonics | float | 2 | R
0x2A76 | 0x2A77 | 10870 | 10871 | ANG_200MS_HAR_I_30th_a | Phase A 30th Current Angle Harmonics | float | 2 | R
0x2A78 | 0x2A79 | 10872 | 10873 | ANG_200MS_HAR_I_30th_b | Phase B 30th Current Angle Harmonics | float | 2 | R
0x2A7A | 0x2A7B | 10874 | 10875 | ANG_200MS_HAR_I_30th_c | Phase C 30th Current Angle Harmonics | float | 2 | R
0x2A7C | 0x2A7D | 10876 | 10877 | ANG_200MS_HAR_I_30th_n | Phase N 30th Current Angle Harmonics | float | 2 | R
0x2A7E | 0x2A7F | 10878 | 10879 | ANG_200MS_HAR_V_31th_a | Phase A 31st Voltage Angle Harmonics | float | 2 | R
0x2A80 | 0x2A81 | 10880 | 10881 | ANG_200MS_HAR_V_31th_b | Phase B 31st Voltage Angle Harmonics | float | 2 | R
0x2A82 | 0x2A83 | 10882 | 10883 | ANG_200MS_HAR_V_31th_c | Phase C 31st Voltage Angle Harmonics | float | 2 | R
0x2A84 | 0x2A85 | 10884 | 10885 | ANG_200MS_HAR_I_31th_a | Phase A 31st Current Angle Harmonics | float | 2 | R
0x2A86 | 0x2A87 | 10886 | 10887 | ANG_200MS_HAR_I_31th_b | Phase B 31st Current Angle Harmonics | float | 2 | R
0x2A88 | 0x2A89 | 10888 | 10889 | ANG_200MS_HAR_I_31th_c | Phase C 31st Current Angle Harmonics | float | 2 | R
0x2A8A | 0x2A8B | 10890 | 10891 | ANG_200MS_HAR_I_31th_n | Phase N 31st Current Angle Harmonics | float | 2 | R
0x2A8C | 0x2A8D | 10892 | 10893 | ANG_200MS_HAR_V_32th_a | Phase A 32nd Voltage Angle Harmonics | float | 2 | R
0x2A8E | 0x2A8F | 10894 | 10895 | ANG_200MS_HAR_V_32th_b | Phase B 32nd Voltage Angle Harmonics | float | 2 | R
0x2A90 | 0x2A91 | 10896 | 10897 | ANG_200MS_HAR_V_32th_c | Phase C 32nd Voltage Angle Harmonics | float | 2 | R
0x2A92 | 0x2A93 | 10898 | 10899 | ANG_200MS_HAR_I_32th_a | Phase A 32nd Current Angle Harmonics | float | 2 | R
0x2A94 | 0x2A95 | 10900 | 10901 | ANG_200MS_HAR_I_32th_b | Phase B 32nd Current Angle Harmonics | float | 2 | R
0x2A96 | 0x2A97 | 10902 | 10903 | ANG_200MS_HAR_I_32th_c | Phase C 32nd Current Angle Harmonics | float | 2 | R
0x2A98 | 0x2A99 | 10904 | 10905 | ANG_200MS_HAR_I_32th_n | Phase N 32nd Current Angle Harmonics | float | 2 | R
0x2A9A | 0x2A9B | 10906 | 10907 | ANG_200MS_HAR_V_33th_a | Phase A 33rd Voltage Angle Harmonics | float | 2 | R
0x2A9C | 0x2A9D | 10908 | 10909 | ANG_200MS_HAR_V_33th_b | Phase B 33rd Voltage Angle Harmonics | float | 2 | R
0x2A9E | 0x2A9F | 10910 | 10911 | ANG_200MS_HAR_V_33th_c | Phase C 33rd Voltage Angle Harmonics | float | 2 | R
0x2AA0 | 0x2AA1 | 10912 | 10913 | ANG_200MS_HAR_I_33th_a | Phase A 33rd Current Angle Harmonics | float | 2 | R
0x2AA2 | 0x2AA3 | 10914 | 10915 | ANG_200MS_HAR_I_33th_b | Phase B 33rd Current Angle Harmonics | float | 2 | R
0x2AA4 | 0x2AA5 | 10916 | 10917 | ANG_200MS_HAR_I_33th_c | Phase C 33rd Current Angle Harmonics | float | 2 | R
0x2AA6 | 0x2AA7 | 10918 | 10919 | ANG_200MS_HAR_I_33th_n | Phase N 33rd Current Angle Harmonics | float | 2 | R
0x2AA8 | 0x2AA9 | 10920 | 10921 | ANG_200MS_HAR_V_34th_a | Phase A 34th Voltage Angle Harmonics | float | 2 | R
0x2AAA | 0x2AAB | 10922 | 10923 | ANG_200MS_HAR_V_34th_b | Phase B 34th Voltage Angle Harmonics | float | 2 | R
0x2AAC | 0x2AAD | 10924 | 10925 | ANG_200MS_HAR_V_34th_c | Phase C 34th Voltage Angle Harmonics | float | 2 | R
0x2AAE | 0x2AAF | 10926 | 10927 | ANG_200MS_HAR_I_34th_a | Phase A 34th Current Angle Harmonics | float | 2 | R
0x2AB0 | 0x2AB1 | 10928 | 10929 | ANG_200MS_HAR_I_34th_b | Phase B 34th Current Angle Harmonics | float | 2 | R
0x2AB2 | 0x2AB3 | 10930 | 10931 | ANG_200MS_HAR_I_34th_c | Phase C 34th Current Angle Harmonics | float | 2 | R
0x2AB4 | 0x2AB5 | 10932 | 10933 | ANG_200MS_HAR_I_34th_n | Phase N 34th Current Angle Harmonics | float | 2 | R
0x2AB6 | 0x2AB7 | 10934 | 10935 | ANG_200MS_HAR_V_35th_a | Phase A 35th Voltage Angle Harmonics | float | 2 | R
0x2AB8 | 0x2AB9 | 10936 | 10937 | ANG_200MS_HAR_V_35th_b | Phase B 35th Voltage Angle Harmonics | float | 2 | R
0x2ABA | 0x2ABB | 10938 | 10939 | ANG_200MS_HAR_V_35th_c | Phase C 35th Voltage Angle Harmonics | float | 2 | R
0x2ABC | 0x2ABD | 10940 | 10941 | ANG_200MS_HAR_I_35th_a | Phase A 35th Current Angle Harmonics | float | 2 | R
0x2ABE | 0x2ABF | 10942 | 10943 | ANG_200MS_HAR_I_35th_b | Phase B 35th Current Angle Harmonics | float | 2 | R
0x2AC0 | 0x2AC1 | 10944 | 10945 | ANG_200MS_HAR_I_35th_c | Phase C 35th Current Angle Harmonics | float | 2 | R
0x2AC2 | 0x2AC3 | 10946 | 10947 | ANG_200MS_HAR_I_35th_n | Phase N 35th Current Angle Harmonics | float | 2 | R
0x2AC4 | 0x2AC5 | 10948 | 10949 | ANG_200MS_HAR_V_36th_a | Phase A 36th Voltage Angle Harmonics | float | 2 | R
0x2AC6 | 0x2AC7 | 10950 | 10951 | ANG_200MS_HAR_V_36th_b | Phase B 36th Voltage Angle Harmonics | float | 2 | R
0x2AC8 | 0x2AC9 | 10952 | 10953 | ANG_200MS_HAR_V_36th_c | Phase C 36th Voltage Angle Harmonics | float | 2 | R
0x2ACA | 0x2ACB | 10954 | 10955 | ANG_200MS_HAR_I_36th_a | Phase A 36th Current Angle Harmonics | float | 2 | R
0x2ACC | 0x2ACD | 10956 | 10957 | ANG_200MS_HAR_I_36th_b | Phase B 36th Current Angle Harmonics | float | 2 | R
0x2ACE | 0x2ACF | 10958 | 10959 | ANG_200MS_HAR_I_36th_c | Phase C 36th Current Angle Harmonics | float | 2 | R
0x2AD0 | 0x2AD1 | 10960 | 10961 | ANG_200MS_HAR_I_36th_n | Phase N 36th Current Angle Harmonics | float | 2 | R
0x2AD2 | 0x2AD3 | 10962 | 10963 | ANG_200MS_HAR_V_37th_a | Phase A 37th Voltage Angle Harmonics | float | 2 | R
0x2AD4 | 0x2AD5 | 10964 | 10965 | ANG_200MS_HAR_V_37th_b | Phase B 37th Voltage Angle Harmonics | float | 2 | R
0x2AD6 | 0x2AD7 | 10966 | 10967 | ANG_200MS_HAR_V_37th_c | Phase C 37th Voltage Angle Harmonics | float | 2 | R
0x2AD8 | 0x2AD9 | 10968 | 10969 | ANG_200MS_HAR_I_37th_a | Phase A 37th Current Angle Harmonics | float | 2 | R
0x2ADA | 0x2ADB | 10970 | 10971 | ANG_200MS_HAR_I_37th_b | Phase B 37th Current Angle Harmonics | float | 2 | R
0x2ADC | 0x2ADD | 10972 | 10973 | ANG_200MS_HAR_I_37th_c | Phase C 37th Current Angle Harmonics | float | 2 | R
0x2ADE | 0x2ADF | 10974 | 10975 | ANG_200MS_HAR_I_37th_n | Phase N 37th Current Angle Harmonics | float | 2 | R
0x2AE0 | 0x2AE1 | 10976 | 10977 | ANG_200MS_HAR_V_38th_a | Phase A 38th Voltage Angle Harmonics | float | 2 | R
0x2AE2 | 0x2AE3 | 10978 | 10979 | ANG_200MS_HAR_V_38th_b | Phase B 38th Voltage Angle Harmonics | float | 2 | R
0x2AE4 | 0x2AE5 | 10980 | 10981 | ANG_200MS_HAR_V_38th_c | Phase C 38th Voltage Angle Harmonics | float | 2 | R
0x2AE6 | 0x2AE7 | 10982 | 10983 | ANG_200MS_HAR_I_38th_a | Phase A 38th Current Angle Harmonics | float | 2 | R
0x2AE8 | 0x2AE9 | 10984 | 10985 | ANG_200MS_HAR_I_38th_b | Phase B 38th Current Angle Harmonics | float | 2 | R
0x2AEA | 0x2AEB | 10986 | 10987 | ANG_200MS_HAR_I_38th_c | Phase C 38th Current Angle Harmonics | float | 2 | R
0x2AEC | 0x2AED | 10988 | 10989 | ANG_200MS_HAR_I_38th_n | Phase N 38th Current Angle Harmonics | float | 2 | R
0x2AEE | 0x2AEF | 10990 | 10991 | ANG_200MS_HAR_V_39th_a | Phase A 39th Voltage Angle Harmonics | float | 2 | R
0x2AF0 | 0x2AF1 | 10992 | 10993 | ANG_200MS_HAR_V_39th_b | Phase B 39th Voltage Angle Harmonics | float | 2 | R
0x2AF2 | 0x2AF3 | 10994 | 10995 | ANG_200MS_HAR_V_39th_c | Phase C 39th Voltage Angle Harmonics | float | 2 | R
0x2AF4 | 0x2AF5 | 10996 | 10997 | ANG_200MS_HAR_I_39th_a | Phase A 39th Current Angle Harmonics | float | 2 | R
0x2AF6 | 0x2AF7 | 10998 | 10999 | ANG_200MS_HAR_I_39th_b | Phase B 39th Current Angle Harmonics | float | 2 | R
0x2AF8 | 0x2AF9 | 11000 | 11001 | ANG_200MS_HAR_I_39th_c | Phase C 39th Current Angle Harmonics | float | 2 | R
0x2AFA | 0x2AFB | 11002 | 11003 | ANG_200MS_HAR_I_39th_n | Phase N 39th Current Angle Harmonics | float | 2 | R
0x2AFC | 0x2AFD | 11004 | 11005 | ANG_200MS_HAR_V_40th_a | Phase A 40th Voltage Angle Harmonics | float | 2 | R
0x2AFE | 0x2AFF | 11006 | 11007 | ANG_200MS_HAR_V_40th_b | Phase B 40th Voltage Angle Harmonics | float | 2 | R
0x2B00 | 0x2B01 | 11008 | 11009 | ANG_200MS_HAR_V_40th_c | Phase C 40th Voltage Angle Harmonics | float | 2 | R
0x2B02 | 0x2B03 | 11010 | 11011 | ANG_200MS_HAR_I_40th_a | Phase A 40th Current Angle Harmonics | float | 2 | R
0x2B04 | 0x2B05 | 11012 | 11013 | ANG_200MS_HAR_I_40th_b | Phase B 40th Current Angle Harmonics | float | 2 | R
0x2B06 | 0x2B07 | 11014 | 11015 | ANG_200MS_HAR_I_40th_c | Phase C 40th Current Angle Harmonics | float | 2 | R
0x2B08 | 0x2B09 | 11016 | 11017 | ANG_200MS_HAR_I_40th_n | Phase N 40th Current Angle Harmonics | float | 2 | R
0x2B0A | 0x2B0B | 11018 | 11019 | ANG_200MS_HAR_V_41th_a | Phase A 41st Voltage Angle Harmonics | float | 2 | R
0x2B0C | 0x2B0D | 11020 | 11021 | ANG_200MS_HAR_V_41th_b | Phase B 41st Voltage Angle Harmonics | float | 2 | R
0x2B0E | 0x2B0F | 11022 | 11023 | ANG_200MS_HAR_V_41th_c | Phase C 41st Voltage Angle Harmonics | float | 2 | R
0x2B10 | 0x2B11 | 11024 | 11025 | ANG_200MS_HAR_I_41th_a | Phase A 41st Current Angle Harmonics | float | 2 | R
0x2B12 | 0x2B13 | 11026 | 11027 | ANG_200MS_HAR_I_41th_b | Phase B 41st Current Angle Harmonics | float | 2 | R
0x2B14 | 0x2B15 | 11028 | 11029 | ANG_200MS_HAR_I_41th_c | Phase C 41st Current Angle Harmonics | float | 2 | R
0x2B16 | 0x2B17 | 11030 | 11031 | ANG_200MS_HAR_I_41th_n | Phase N 41st Current Angle Harmonics | float | 2 | R
0x2B18 | 0x2B19 | 11032 | 11033 | ANG_200MS_HAR_V_42th_a | Phase A 42nd Voltage Angle Harmonics | float | 2 | R
0x2B1A | 0x2B1B | 11034 | 11035 | ANG_200MS_HAR_V_42th_b | Phase B 42nd Voltage Angle Harmonics | float | 2 | R
0x2B1C | 0x2B1D | 11036 | 11037 | ANG_200MS_HAR_V_42th_c | Phase C 42nd Voltage Angle Harmonics | float | 2 | R
0x2B1E | 0x2B1F | 11038 | 11039 | ANG_200MS_HAR_I_42th_a | Phase A 42nd Current Angle Harmonics | float | 2 | R
0x2B20 | 0x2B21 | 11040 | 11041 | ANG_200MS_HAR_I_42th_b | Phase B 42nd Current Angle Harmonics | float | 2 | R
0x2B22 | 0x2B23 | 11042 | 11043 | ANG_200MS_HAR_I_42th_c | Phase C 42nd Current Angle Harmonics | float | 2 | R
0x2B24 | 0x2B25 | 11044 | 11045 | ANG_200MS_HAR_I_42th_n | Phase N 42nd Current Angle Harmonics | float | 2 | R
0x2B26 | 0x2B27 | 11046 | 11047 | ANG_200MS_HAR_V_43th_a | Phase A 43rd Voltage Angle Harmonics | float | 2 | R
0x2B28 | 0x2B29 | 11048 | 11049 | ANG_200MS_HAR_V_43th_b | Phase B 43rd Voltage Angle Harmonics | float | 2 | R
0x2B2A | 0x2B2B | 11050 | 11051 | ANG_200MS_HAR_V_43th_c | Phase C 43rd Voltage Angle Harmonics | float | 2 | R
0x2B2C | 0x2B2D | 11052 | 11053 | ANG_200MS_HAR_I_43th_a | Phase A 43rd Current Angle Harmonics | float | 2 | R
0x2B2E | 0x2B2F | 11054 | 11055 | ANG_200MS_HAR_I_43th_b | Phase B 43rd Current Angle Harmonics | float | 2 | R
0x2B30 | 0x2B31 | 11056 | 11057 | ANG_200MS_HAR_I_43th_c | Phase C 43rd Current Angle Harmonics | float | 2 | R
0x2B32 | 0x2B33 | 11058 | 11059 | ANG_200MS_HAR_I_43th_n | Phase N 43rd Current Angle Harmonics | float | 2 | R
0x2B34 | 0x2B35 | 11060 | 11061 | ANG_200MS_HAR_V_44th_a | Phase A 44th Voltage Angle Harmonics | float | 2 | R
0x2B36 | 0x2B37 | 11062 | 11063 | ANG_200MS_HAR_V_44th_b | Phase B 44th Voltage Angle Harmonics | float | 2 | R
0x2B38 | 0x2B39 | 11064 | 11065 | ANG_200MS_HAR_V_44th_c | Phase C 44th Voltage Angle Harmonics | float | 2 | R
0x2B3A | 0x2B3B | 11066 | 11067 | ANG_200MS_HAR_I_44th_a | Phase A 44th Current Angle Harmonics | float | 2 | R
0x2B3C | 0x2B3D | 11068 | 11069 | ANG_200MS_HAR_I_44th_b | Phase B 44th Current Angle Harmonics | float | 2 | R
0x2B3E | 0x2B3F | 11070 | 11071 | ANG_200MS_HAR_I_44th_c | Phase C 44th Current Angle Harmonics | float | 2 | R
0x2B40 | 0x2B41 | 11072 | 11073 | ANG_200MS_HAR_I_44th_n | Phase N 44th Current Angle Harmonics | float | 2 | R
0x2B42 | 0x2B43 | 11074 | 11075 | ANG_200MS_HAR_V_45th_a | Phase A 45th Voltage Angle Harmonics | float | 2 | R
0x2B44 | 0x2B45 | 11076 | 11077 | ANG_200MS_HAR_V_45th_b | Phase B 45th Voltage Angle Harmonics | float | 2 | R
0x2B46 | 0x2B47 | 11078 | 11079 | ANG_200MS_HAR_V_45th_c | Phase C 45th Voltage Angle Harmonics | float | 2 | R
0x2B48 | 0x2B49 | 11080 | 11081 | ANG_200MS_HAR_I_45th_a | Phase A 45th Current Angle Harmonics | float | 2 | R
0x2B4A | 0x2B4B | 11082 | 11083 | ANG_200MS_HAR_I_45th_b | Phase B 45th Current Angle Harmonics | float | 2 | R
0x2B4C | 0x2B4D | 11084 | 11085 | ANG_200MS_HAR_I_45th_c | Phase C 45th Current Angle Harmonics | float | 2 | R
0x2B4E | 0x2B4F | 11086 | 11087 | ANG_200MS_HAR_I_45th_n | Phase N 45th Current Angle Harmonics | float | 2 | R
0x2B50 | 0x2B51 | 11088 | 11089 | ANG_200MS_HAR_V_46th_a | Phase A 46th Voltage Angle Harmonics | float | 2 | R
0x2B52 | 0x2B53 | 11090 | 11091 | ANG_200MS_HAR_V_46th_b | Phase B 46th Voltage Angle Harmonics | float | 2 | R
0x2B54 | 0x2B55 | 11092 | 11093 | ANG_200MS_HAR_V_46th_c | Phase C 46th Voltage Angle Harmonics | float | 2 | R
0x2B56 | 0x2B57 | 11094 | 11095 | ANG_200MS_HAR_I_46th_a | Phase A 46th Current Angle Harmonics | float | 2 | R
0x2B58 | 0x2B59 | 11096 | 11097 | ANG_200MS_HAR_I_46th_b | Phase B 46th Current Angle Harmonics | float | 2 | R
0x2B5A | 0x2B5B | 11098 | 11099 | ANG_200MS_HAR_I_46th_c | Phase C 46th Current Angle Harmonics | float | 2 | R
0x2B5C | 0x2B5D | 11100 | 11101 | ANG_200MS_HAR_I_46th_n | Phase N 46th Current Angle Harmonics | float | 2 | R
0x2B5E | 0x2B5F | 11102 | 11103 | ANG_200MS_HAR_V_47th_a | Phase A 47th Voltage Angle Harmonics | float | 2 | R
0x2B60 | 0x2B61 | 11104 | 11105 | ANG_200MS_HAR_V_47th_b | Phase B 47th Voltage Angle Harmonics | float | 2 | R
0x2B62 | 0x2B63 | 11106 | 11107 | ANG_200MS_HAR_V_47th_c | Phase C 47th Voltage Angle Harmonics | float | 2 | R
0x2B64 | 0x2B65 | 11108 | 11109 | ANG_200MS_HAR_I_47th_a | Phase A 47th Current Angle Harmonics | float | 2 | R
0x2B66 | 0x2B67 | 11110 | 11111 | ANG_200MS_HAR_I_47th_b | Phase B 47th Current Angle Harmonics | float | 2 | R
0x2B68 | 0x2B69 | 11112 | 11113 | ANG_200MS_HAR_I_47th_c | Phase C 47th Current Angle Harmonics | float | 2 | R
0x2B6A | 0x2B6B | 11114 | 11115 | ANG_200MS_HAR_I_47th_n | Phase N 47th Current Angle Harmonics | float | 2 | R
0x2B6C | 0x2B6D | 11116 | 11117 | ANG_200MS_HAR_V_48th_a | Phase A 48th Voltage Angle Harmonics | float | 2 | R
0x2B6E | 0x2B6F | 11118 | 11119 | ANG_200MS_HAR_V_48th_b | Phase B 48th Voltage Angle Harmonics | float | 2 | R
0x2B70 | 0x2B71 | 11120 | 11121 | ANG_200MS_HAR_V_48th_c | Phase C 48th Voltage Angle Harmonics | float | 2 | R
0x2B72 | 0x2B73 | 11122 | 11123 | ANG_200MS_HAR_I_48th_a | Phase A 48th Current Angle Harmonics | float | 2 | R
0x2B74 | 0x2B75 | 11124 | 11125 | ANG_200MS_HAR_I_48th_b | Phase B 48th Current Angle Harmonics | float | 2 | R
0x2B76 | 0x2B77 | 11126 | 11127 | ANG_200MS_HAR_I_48th_c | Phase C 48th Current Angle Harmonics | float | 2 | R
0x2B78 | 0x2B79 | 11128 | 11129 | ANG_200MS_HAR_I_48th_n | Phase N 48th Current Angle Harmonics | float | 2 | R
0x2B7A | 0x2B7B | 11130 | 11131 | ANG_200MS_HAR_V_49th_a | Phase A 49th Voltage Angle Harmonics | float | 2 | R
0x2B7C | 0x2B7D | 11132 | 11133 | ANG_200MS_HAR_V_49th_b | Phase B 49th Voltage Angle Harmonics | float | 2 | R
0x2B7E | 0x2B7F | 11134 | 11135 | ANG_200MS_HAR_V_49th_c | Phase C 49th Voltage Angle Harmonics | float | 2 | R
0x2B80 | 0x2B81 | 11136 | 11137 | ANG_200MS_HAR_I_49th_a | Phase A 49th Current Angle Harmonics | float | 2 | R
0x2B82 | 0x2B83 | 11138 | 11139 | ANG_200MS_HAR_I_49th_b | Phase B 49th Current Angle Harmonics | float | 2 | R
0x2B84 | 0x2B85 | 11140 | 11141 | ANG_200MS_HAR_I_49th_c | Phase C 49th Current Angle Harmonics | float | 2 | R
0x2B86 | 0x2B87 | 11142 | 11143 | ANG_200MS_HAR_I_49th_n | Phase N 49th Current Angle Harmonics | float | 2 | R
0x2B88 | 0x2B89 | 11144 | 11145 | ANG_200MS_HAR_V_50th_a | Phase A 50th Voltage Angle Harmonics | float | 2 | R
0x2B8A | 0x2B8B | 11146 | 11147 | ANG_200MS_HAR_V_50th_b | Phase B 50th Voltage Angle Harmonics | float | 2 | R
0x2B8C | 0x2B8D | 11148 | 11149 | ANG_200MS_HAR_V_50th_c | Phase C 50th Voltage Angle Harmonics | float | 2 | R
0x2B8E | 0x2B8F | 11150 | 11151 | ANG_200MS_HAR_I_50th_a | Phase A 50th Current Angle Harmonics | float | 2 | R
0x2B90 | 0x2B91 | 11152 | 11153 | ANG_200MS_HAR_I_50th_b | Phase B 50th Current Angle Harmonics | float | 2 | R
0x2B92 | 0x2B93 | 11154 | 11155 | ANG_200MS_HAR_I_50th_c | Phase C 50th Current Angle Harmonics | float | 2 | R
0x2B94 | 0x2B95 | 11156 | 11157 | ANG_200MS_HAR_I_50th_n | Phase N 50th Current Angle Harmonics | float | 2 | R
0x2B96 | 0x2B97 | 11158 | 11159 | ANG_200MS_HAR_V_51th_a | Phase A 51st Voltage Angle Harmonics | float | 2 | R
0x2B98 | 0x2B99 | 11160 | 11161 | ANG_200MS_HAR_V_51th_b | Phase B 51st Voltage Angle Harmonics | float | 2 | R
0x2B9A | 0x2B9B | 11162 | 11163 | ANG_200MS_HAR_V_51th_c | Phase C 51st Voltage Angle Harmonics | float | 2 | R
0x2B9C | 0x2B9D | 11164 | 11165 | ANG_200MS_HAR_I_51th_a | Phase A 51st Current Angle Harmonics | float | 2 | R
0x2B9E | 0x2B9F | 11166 | 11167 | ANG_200MS_HAR_I_51th_b | Phase B 51st Current Angle Harmonics | float | 2 | R
0x2BA0 | 0x2BA1 | 11168 | 11169 | ANG_200MS_HAR_I_51th_c | Phase C 51st Current Angle Harmonics | float | 2 | R
0x2BA2 | 0x2BA3 | 11170 | 11171 | ANG_200MS_HAR_I_51th_n | Phase N 51st Current Angle Harmonics | float | 2 | R
0x2BA4 | 0x2BA5 | 11172 | 11173 | ANG_200MS_HAR_V_52th_a | Phase A 52nd Voltage Angle Harmonics | float | 2 | R
0x2BA6 | 0x2BA7 | 11174 | 11175 | ANG_200MS_HAR_V_52th_b | Phase B 52nd Voltage Angle Harmonics | float | 2 | R
0x2BA8 | 0x2BA9 | 11176 | 11177 | ANG_200MS_HAR_V_52th_c | Phase C 52nd Voltage Angle Harmonics | float | 2 | R
0x2BAA | 0x2BAB | 11178 | 11179 | ANG_200MS_HAR_I_52th_a | Phase A 52nd Current Angle Harmonics | float | 2 | R
0x2BAC | 0x2BAD | 11180 | 11181 | ANG_200MS_HAR_I_52th_b | Phase B 52nd Current Angle Harmonics | float | 2 | R
0x2BAE | 0x2BAF | 11182 | 11183 | ANG_200MS_HAR_I_52th_c | Phase C 52nd Current Angle Harmonics | float | 2 | R
0x2BB0 | 0x2BB1 | 11184 | 11185 | ANG_200MS_HAR_I_52th_n | Phase N 52nd Current Angle Harmonics | float | 2 | R
0x2BB2 | 0x2BB3 | 11186 | 11187 | ANG_200MS_HAR_V_53th_a | Phase A 53rd Voltage Angle Harmonics | float | 2 | R
0x2BB4 | 0x2BB5 | 11188 | 11189 | ANG_200MS_HAR_V_53th_b | Phase B 53rd Voltage Angle Harmonics | float | 2 | R
0x2BB6 | 0x2BB7 | 11190 | 11191 | ANG_200MS_HAR_V_53th_c | Phase C 53rd Voltage Angle Harmonics | float | 2 | R
0x2BB8 | 0x2BB9 | 11192 | 11193 | ANG_200MS_HAR_I_53th_a | Phase A 53rd Current Angle Harmonics | float | 2 | R
0x2BBA | 0x2BBB | 11194 | 11195 | ANG_200MS_HAR_I_53th_b | Phase B 53rd Current Angle Harmonics | float | 2 | R
0x2BBC | 0x2BBD | 11196 | 11197 | ANG_200MS_HAR_I_53th_c | Phase C 53rd Current Angle Harmonics | float | 2 | R
0x2BBE | 0x2BBF | 11198 | 11199 | ANG_200MS_HAR_I_53th_n | Phase N 53rd Current Angle Harmonics | float | 2 | R
0x2BC0 | 0x2BC1 | 11200 | 11201 | ANG_200MS_HAR_V_54th_a | Phase A 54th Voltage Angle Harmonics | float | 2 | R
0x2BC2 | 0x2BC3 | 11202 | 11203 | ANG_200MS_HAR_V_54th_b | Phase B 54th Voltage Angle Harmonics | float | 2 | R
0x2BC4 | 0x2BC5 | 11204 | 11205 | ANG_200MS_HAR_V_54th_c | Phase C 54th Voltage Angle Harmonics | float | 2 | R
0x2BC6 | 0x2BC7 | 11206 | 11207 | ANG_200MS_HAR_I_54th_a | Phase A 54th Current Angle Harmonics | float | 2 | R
0x2BC8 | 0x2BC9 | 11208 | 11209 | ANG_200MS_HAR_I_54th_b | Phase B 54th Current Angle Harmonics | float | 2 | R
0x2BCA | 0x2BCB | 11210 | 11211 | ANG_200MS_HAR_I_54th_c | Phase C 54th Current Angle Harmonics | float | 2 | R
0x2BCC | 0x2BCD | 11212 | 11213 | ANG_200MS_HAR_I_54th_n | Phase N 54th Current Angle Harmonics | float | 2 | R
0x2BCE | 0x2BCF | 11214 | 11215 | ANG_200MS_HAR_V_55th_a | Phase A 55th Voltage Angle Harmonics | float | 2 | R
0x2BD0 | 0x2BD1 | 11216 | 11217 | ANG_200MS_HAR_V_55th_b | Phase B 55th Voltage Angle Harmonics | float | 2 | R
0x2BD2 | 0x2BD3 | 11218 | 11219 | ANG_200MS_HAR_V_55th_c | Phase C 55th Voltage Angle Harmonics | float | 2 | R
0x2BD4 | 0x2BD5 | 11220 | 11221 | ANG_200MS_HAR_I_55th_a | Phase A 55th Current Angle Harmonics | float | 2 | R
0x2BD6 | 0x2BD7 | 11222 | 11223 | ANG_200MS_HAR_I_55th_b | Phase B 55th Current Angle Harmonics | float | 2 | R
0x2BD8 | 0x2BD9 | 11224 | 11225 | ANG_200MS_HAR_I_55th_c | Phase C 55th Current Angle Harmonics | float | 2 | R
0x2BDA | 0x2BDB | 11226 | 11227 | ANG_200MS_HAR_I_55th_n | Phase N 55th Current Angle Harmonics | float | 2 | R
0x2BDC | 0x2BDD | 11228 | 11229 | ANG_200MS_HAR_V_56th_a | Phase A 56th Voltage Angle Harmonics | float | 2 | R
0x2BDE | 0x2BDF | 11230 | 11231 | ANG_200MS_HAR_V_56th_b | Phase B 56th Voltage Angle Harmonics | float | 2 | R
0x2BE0 | 0x2BE1 | 11232 | 11233 | ANG_200MS_HAR_V_56th_c | Phase C 56th Voltage Angle Harmonics | float | 2 | R
0x2BE2 | 0x2BE3 | 11234 | 11235 | ANG_200MS_HAR_I_56th_a | Phase A 56th Current Angle Harmonics | float | 2 | R
0x2BE4 | 0x2BE5 | 11236 | 11237 | ANG_200MS_HAR_I_56th_b | Phase B 56th Current Angle Harmonics | float | 2 | R
0x2BE6 | 0x2BE7 | 11238 | 11239 | ANG_200MS_HAR_I_56th_c | Phase C 56th Current Angle Harmonics | float | 2 | R
0x2BE8 | 0x2BE9 | 11240 | 11241 | ANG_200MS_HAR_I_56th_n | Phase N 56th Current Angle Harmonics | float | 2 | R
0x2BEA | 0x2BEB | 11242 | 11243 | ANG_200MS_HAR_V_57th_a | Phase A 57th Voltage Angle Harmonics | float | 2 | R
0x2BEC | 0x2BED | 11244 | 11245 | ANG_200MS_HAR_V_57th_b | Phase B 57th Voltage Angle Harmonics | float | 2 | R
0x2BEE | 0x2BEF | 11246 | 11247 | ANG_200MS_HAR_V_57th_c | Phase C 57th Voltage Angle Harmonics | float | 2 | R
0x2BF0 | 0x2BF1 | 11248 | 11249 | ANG_200MS_HAR_I_57th_a | Phase A 57th Current Angle Harmonics | float | 2 | R
0x2BF2 | 0x2BF3 | 11250 | 11251 | ANG_200MS_HAR_I_57th_b | Phase B 57th Current Angle Harmonics | float | 2 | R
0x2BF4 | 0x2BF5 | 11252 | 11253 | ANG_200MS_HAR_I_57th_c | Phase C 57th Current Angle Harmonics | float | 2 | R
0x2BF6 | 0x2BF7 | 11254 | 11255 | ANG_200MS_HAR_I_57th_n | Phase N 57th Current Angle Harmonics | float | 2 | R
0x2BF8 | 0x2BF9 | 11256 | 11257 | ANG_200MS_HAR_V_58th_a | Phase A 58th Voltage Angle Harmonics | float | 2 | R
0x2BFA | 0x2BFB | 11258 | 11259 | ANG_200MS_HAR_V_58th_b | Phase B 58th Voltage Angle Harmonics | float | 2 | R
0x2BFC | 0x2BFD | 11260 | 11261 | ANG_200MS_HAR_V_58th_c | Phase C 58th Voltage Angle Harmonics | float | 2 | R
0x2BFE | 0x2BFF | 11262 | 11263 | ANG_200MS_HAR_I_58th_a | Phase A 58th Current Angle Harmonics | float | 2 | R
0x2C00 | 0x2C01 | 11264 | 11265 | ANG_200MS_HAR_I_58th_b | Phase B 58th Current Angle Harmonics | float | 2 | R
0x2C02 | 0x2C03 | 11266 | 11267 | ANG_200MS_HAR_I_58th_c | Phase C 58th Current Angle Harmonics | float | 2 | R
0x2C04 | 0x2C05 | 11268 | 11269 | ANG_200MS_HAR_I_58th_n | Phase N 58th Current Angle Harmonics | float | 2 | R
0x2C06 | 0x2C07 | 11270 | 11271 | ANG_200MS_HAR_V_59th_a | Phase A 59th Voltage Angle Harmonics | float | 2 | R
0x2C08 | 0x2C09 | 11272 | 11273 | ANG_200MS_HAR_V_59th_b | Phase B 59th Voltage Angle Harmonics | float | 2 | R
0x2C0A | 0x2C0B | 11274 | 11275 | ANG_200MS_HAR_V_59th_c | Phase C 59th Voltage Angle Harmonics | float | 2 | R
0x2C0C | 0x2C0D | 11276 | 11277 | ANG_200MS_HAR_I_59th_a | Phase A 59th Current Angle Harmonics | float | 2 | R
0x2C0E | 0x2C0F | 11278 | 11279 | ANG_200MS_HAR_I_59th_b | Phase B 59th Current Angle Harmonics | float | 2 | R
0x2C10 | 0x2C11 | 11280 | 11281 | ANG_200MS_HAR_I_59th_c | Phase C 59th Current Angle Harmonics | float | 2 | R
0x2C12 | 0x2C13 | 11282 | 11283 | ANG_200MS_HAR_I_59th_n | Phase N 59th Current Angle Harmonics | float | 2 | R
0x2C14 | 0x2C15 | 11284 | 11285 | ANG_200MS_HAR_V_60th_a | Phase A 60th Voltage Angle Harmonics | float | 2 | R
0x2C16 | 0x2C17 | 11286 | 11287 | ANG_200MS_HAR_V_60th_b | Phase B 60th Voltage Angle Harmonics | float | 2 | R
0x2C18 | 0x2C19 | 11288 | 11289 | ANG_200MS_HAR_V_60th_c | Phase C 60th Voltage Angle Harmonics | float | 2 | R
0x2C1A | 0x2C1B | 11290 | 11291 | ANG_200MS_HAR_I_60th_a | Phase A 60th Current Angle Harmonics | float | 2 | R
0x2C1C | 0x2C1D | 11292 | 11293 | ANG_200MS_HAR_I_60th_b | Phase B 60th Current Angle Harmonics | float | 2 | R
0x2C1E | 0x2C1F | 11294 | 11295 | ANG_200MS_HAR_I_60th_c | Phase C 60th Current Angle Harmonics | float | 2 | R
0x2C20 | 0x2C21 | 11296 | 11297 | ANG_200MS_HAR_I_60th_n | Phase N 60th Current Angle Harmonics | float | 2 | R
0x2C22 | 0x2C23 | 11298 | 11299 | ANG_200MS_HAR_V_61th_a | Phase A 61st Voltage Angle Harmonics | float | 2 | R
0x2C24 | 0x2C25 | 11300 | 11301 | ANG_200MS_HAR_V_61th_b | Phase B 61st Voltage Angle Harmonics | float | 2 | R
0x2C26 | 0x2C27 | 11302 | 11303 | ANG_200MS_HAR_V_61th_c | Phase C 61st Voltage Angle Harmonics | float | 2 | R
0x2C28 | 0x2C29 | 11304 | 11305 | ANG_200MS_HAR_I_61th_a | Phase A 61st Current Angle Harmonics | float | 2 | R
0x2C2A | 0x2C2B | 11306 | 11307 | ANG_200MS_HAR_I_61th_b | Phase B 61st Current Angle Harmonics | float | 2 | R
0x2C2C | 0x2C2D | 11308 | 11309 | ANG_200MS_HAR_I_61th_c | Phase C 61st Current Angle Harmonics | float | 2 | R
0x2C2E | 0x2C2F | 11310 | 11311 | ANG_200MS_HAR_I_61th_n | Phase N 61st Current Angle Harmonics | float | 2 | R
0x2C30 | 0x2C31 | 11312 | 11313 | ANG_200MS_HAR_V_62th_a | Phase A 62nd Voltage Angle Harmonics | float | 2 | R
0x2C32 | 0x2C33 | 11314 | 11315 | ANG_200MS_HAR_V_62th_b | Phase B 62nd Voltage Angle Harmonics | float | 2 | R
0x2C34 | 0x2C35 | 11316 | 11317 | ANG_200MS_HAR_V_62th_c | Phase C 62nd Voltage Angle Harmonics | float | 2 | R
0x2C36 | 0x2C37 | 11318 | 11319 | ANG_200MS_HAR_I_62th_a | Phase A 62nd Current Angle Harmonics | float | 2 | R
0x2C38 | 0x2C39 | 11320 | 11321 | ANG_200MS_HAR_I_62th_b | Phase B 62nd Current Angle Harmonics | float | 2 | R
0x2C3A | 0x2C3B | 11322 | 11323 | ANG_200MS_HAR_I_62th_c | Phase C 62nd Current Angle Harmonics | float | 2 | R
0x2C3C | 0x2C3D | 11324 | 11325 | ANG_200MS_HAR_I_62th_n | Phase N 62nd Current Angle Harmonics | float | 2 | R
0x2C3E | 0x2C3F | 11326 | 11327 | ANG_200MS_HAR_V_63th_a | Phase A 63rd Voltage Angle Harmonics | float | 2 | R
0x2C40 | 0x2C41 | 11328 | 11329 | ANG_200MS_HAR_V_63th_b | Phase B 63rd Voltage Angle Harmonics | float | 2 | R
0x2C42 | 0x2C43 | 11330 | 11331 | ANG_200MS_HAR_V_63th_c | Phase C 63rd Voltage Angle Harmonics | float | 2 | R
0x2C44 | 0x2C45 | 11332 | 11333 | ANG_200MS_HAR_I_63th_a | Phase A 63rd Current Angle Harmonics | float | 2 | R
0x2C46 | 0x2C47 | 11334 | 11335 | ANG_200MS_HAR_I_63th_b | Phase B 63rd Current Angle Harmonics | float | 2 | R
0x2C48 | 0x2C49 | 11336 | 11337 | ANG_200MS_HAR_I_63th_c | Phase C 63rd Current Angle Harmonics | float | 2 | R
0x2C4A | 0x2C4B | 11338 | 11339 | ANG_200MS_HAR_I_63th_n | Phase N 63rd Current Angle Harmonics | float | 2 | R
0x2C4C | 0x2C4D | 11340 | 11341 | ANG_200MS_HAR_V_64th_a | Phase A 64th Voltage Angle Harmonics | float | 2 | R
0x2C4E | 0x2C4F | 11342 | 11343 | ANG_200MS_HAR_V_64th_b | Phase B 64th Voltage Angle Harmonics | float | 2 | R
0x2C50 | 0x2C51 | 11344 | 11345 | ANG_200MS_HAR_V_64th_c | Phase C 64th Voltage Angle Harmonics | float | 2 | R
0x2C52 | 0x2C53 | 11346 | 11347 | ANG_200MS_HAR_I_64th_a | Phase A 64th Current Angle Harmonics | float | 2 | R
0x2C54 | 0x2C55 | 11348 | 11349 | ANG_200MS_HAR_I_64th_b | Phase B 64th Current Angle Harmonics | float | 2 | R
0x2C56 | 0x2C57 | 11350 | 11351 | ANG_200MS_HAR_I_64th_c | Phase C 64th Current Angle Harmonics | float | 2 | R
0x2C58 | 0x2C59 | 11352 | 11353 | ANG_200MS_HAR_I_64th_n | Phase N 64th Current Angle Harmonics | float | 2 | R
0x2C5A | 0x2C5B | 11354 | 11355 | ANG_200MS_HAR_V_65th_a | Phase A 65th Voltage Angle Harmonics | float | 2 | R
0x2C5C | 0x2C5D | 11356 | 11357 | ANG_200MS_HAR_V_65th_b | Phase B 65th Voltage Angle Harmonics | float | 2 | R
0x2C5E | 0x2C5F | 11358 | 11359 | ANG_200MS_HAR_V_65th_c | Phase C 65th Voltage Angle Harmonics | float | 2 | R
0x2C60 | 0x2C61 | 11360 | 11361 | ANG_200MS_HAR_I_65th_a | Phase A 65th Current Angle Harmonics | float | 2 | R
0x2C62 | 0x2C63 | 11362 | 11363 | ANG_200MS_HAR_I_65th_b | Phase B 65th Current Angle Harmonics | float | 2 | R
0x2C64 | 0x2C65 | 11364 | 11365 | ANG_200MS_HAR_I_65th_c | Phase C 65th Current Angle Harmonics | float | 2 | R
0x2C66 | 0x2C67 | 11366 | 11367 | ANG_200MS_HAR_I_65th_n | Phase N 65th Current Angle Harmonics | float | 2 | R
0x2C68 | 0x2C69 | 11368 | 11369 | ANG_200MS_HAR_V_66th_a | Phase A 66th Voltage Angle Harmonics | float | 2 | R
0x2C6A | 0x2C6B | 11370 | 11371 | ANG_200MS_HAR_V_66th_b | Phase B 66th Voltage Angle Harmonics | float | 2 | R
0x2C6C | 0x2C6D | 11372 | 11373 | ANG_200MS_HAR_V_66th_c | Phase C 66th Voltage Angle Harmonics | float | 2 | R
0x2C6E | 0x2C6F | 11374 | 11375 | ANG_200MS_HAR_I_66th_a | Phase A 66th Current Angle Harmonics | float | 2 | R
0x2C70 | 0x2C71 | 11376 | 11377 | ANG_200MS_HAR_I_66th_b | Phase B 66th Current Angle Harmonics | float | 2 | R
0x2C72 | 0x2C73 | 11378 | 11379 | ANG_200MS_HAR_I_66th_c | Phase C 66th Current Angle Harmonics | float | 2 | R
0x2C74 | 0x2C75 | 11380 | 11381 | ANG_200MS_HAR_I_66th_n | Phase N 66th Current Angle Harmonics | float | 2 | R
0x2C76 | 0x2C77 | 11382 | 11383 | ANG_200MS_HAR_V_67th_a | Phase A 67th Voltage Angle Harmonics | float | 2 | R
0x2C78 | 0x2C79 | 11384 | 11385 | ANG_200MS_HAR_V_67th_b | Phase B 67th Voltage Angle Harmonics | float | 2 | R
0x2C7A | 0x2C7B | 11386 | 11387 | ANG_200MS_HAR_V_67th_c | Phase C 67th Voltage Angle Harmonics | float | 2 | R
0x2C7C | 0x2C7D | 11388 | 11389 | ANG_200MS_HAR_I_67th_a | Phase A 67th Current Angle Harmonics | float | 2 | R
0x2C7E | 0x2C7F | 11390 | 11391 | ANG_200MS_HAR_I_67th_b | Phase B 67th Current Angle Harmonics | float | 2 | R
0x2C80 | 0x2C81 | 11392 | 11393 | ANG_200MS_HAR_I_67th_c | Phase C 67th Current Angle Harmonics | float | 2 | R
0x2C82 | 0x2C83 | 11394 | 11395 | ANG_200MS_HAR_I_67th_n | Phase N 67th Current Angle Harmonics | float | 2 | R
0x2C84 | 0x2C85 | 11396 | 11397 | ANG_200MS_HAR_V_68th_a | Phase A 68th Voltage Angle Harmonics | float | 2 | R
0x2C86 | 0x2C87 | 11398 | 11399 | ANG_200MS_HAR_V_68th_b | Phase B 68th Voltage Angle Harmonics | float | 2 | R
0x2C88 | 0x2C89 | 11400 | 11401 | ANG_200MS_HAR_V_68th_c | Phase C 68th Voltage Angle Harmonics | float | 2 | R
0x2C8A | 0x2C8B | 11402 | 11403 | ANG_200MS_HAR_I_68th_a | Phase A 68th Current Angle Harmonics | float | 2 | R
0x2C8C | 0x2C8D | 11404 | 11405 | ANG_200MS_HAR_I_68th_b | Phase B 68th Current Angle Harmonics | float | 2 | R
0x2C8E | 0x2C8F | 11406 | 11407 | ANG_200MS_HAR_I_68th_c | Phase C 68th Current Angle Harmonics | float | 2 | R
0x2C90 | 0x2C91 | 11408 | 11409 | ANG_200MS_HAR_I_68th_n | Phase N 68th Current Angle Harmonics | float | 2 | R
0x2C92 | 0x2C93 | 11410 | 11411 | ANG_200MS_HAR_V_69th_a | Phase A 69th Voltage Angle Harmonics | float | 2 | R
0x2C94 | 0x2C95 | 11412 | 11413 | ANG_200MS_HAR_V_69th_b | Phase B 69th Voltage Angle Harmonics | float | 2 | R
0x2C96 | 0x2C97 | 11414 | 11415 | ANG_200MS_HAR_V_69th_c | Phase C 69th Voltage Angle Harmonics | float | 2 | R
0x2C98 | 0x2C99 | 11416 | 11417 | ANG_200MS_HAR_I_69th_a | Phase A 69th Current Angle Harmonics | float | 2 | R
0x2C9A | 0x2C9B | 11418 | 11419 | ANG_200MS_HAR_I_69th_b | Phase B 69th Current Angle Harmonics | float | 2 | R
0x2C9C | 0x2C9D | 11420 | 11421 | ANG_200MS_HAR_I_69th_c | Phase C 69th Current Angle Harmonics | float | 2 | R
0x2C9E | 0x2C9F | 11422 | 11423 | ANG_200MS_HAR_I_69th_n | Phase N 69th Current Angle Harmonics | float | 2 | R
0x2CA0 | 0x2CA1 | 11424 | 11425 | ANG_200MS_HAR_V_70th_a | Phase A 70th Voltage Angle Harmonics | float | 2 | R
0x2CA2 | 0x2CA3 | 11426 | 11427 | ANG_200MS_HAR_V_70th_b | Phase B 70th Voltage Angle Harmonics | float | 2 | R
0x2CA4 | 0x2CA5 | 11428 | 11429 | ANG_200MS_HAR_V_70th_c | Phase C 70th Voltage Angle Harmonics | float | 2 | R
0x2CA6 | 0x2CA7 | 11430 | 11431 | ANG_200MS_HAR_I_70th_a | Phase A 70th Current Angle Harmonics | float | 2 | R
0x2CA8 | 0x2CA9 | 11432 | 11433 | ANG_200MS_HAR_I_70th_b | Phase B 70th Current Angle Harmonics | float | 2 | R
0x2CAA | 0x2CAB | 11434 | 11435 | ANG_200MS_HAR_I_70th_c | Phase C 70th Current Angle Harmonics | float | 2 | R
0x2CAC | 0x2CAD | 11436 | 11437 | ANG_200MS_HAR_I_70th_n | Phase N 70th Current Angle Harmonics | float | 2 | R
0x2CAE | 0x2CAF | 11438 | 11439 | ANG_200MS_HAR_V_71th_a | Phase A 71st Voltage Angle Harmonics | float | 2 | R
0x2CB0 | 0x2CB1 | 11440 | 11441 | ANG_200MS_HAR_V_71th_b | Phase B 71st Voltage Angle Harmonics | float | 2 | R
0x2CB2 | 0x2CB3 | 11442 | 11443 | ANG_200MS_HAR_V_71th_c | Phase C 71st Voltage Angle Harmonics | float | 2 | R
0x2CB4 | 0x2CB5 | 11444 | 11445 | ANG_200MS_HAR_I_71th_a | Phase A 71st Current Angle Harmonics | float | 2 | R
0x2CB6 | 0x2CB7 | 11446 | 11447 | ANG_200MS_HAR_I_71th_b | Phase B 71st Current Angle Harmonics | float | 2 | R
0x2CB8 | 0x2CB9 | 11448 | 11449 | ANG_200MS_HAR_I_71th_c | Phase C 71st Current Angle Harmonics | float | 2 | R
0x2CBA | 0x2CBB | 11450 | 11451 | ANG_200MS_HAR_I_71th_n | Phase N 71st Current Angle Harmonics | float | 2 | R
0x2CBC | 0x2CBD | 11452 | 11453 | ANG_200MS_HAR_V_72th_a | Phase A 72nd Voltage Angle Harmonics | float | 2 | R
0x2CBE | 0x2CBF | 11454 | 11455 | ANG_200MS_HAR_V_72th_b | Phase B 72nd Voltage Angle Harmonics | float | 2 | R
0x2CC0 | 0x2CC1 | 11456 | 11457 | ANG_200MS_HAR_V_72th_c | Phase C 72nd Voltage Angle Harmonics | float | 2 | R
0x2CC2 | 0x2CC3 | 11458 | 11459 | ANG_200MS_HAR_I_72th_a | Phase A 72nd Current Angle Harmonics | float | 2 | R
0x2CC4 | 0x2CC5 | 11460 | 11461 | ANG_200MS_HAR_I_72th_b | Phase B 72nd Current Angle Harmonics | float | 2 | R
0x2CC6 | 0x2CC7 | 11462 | 11463 | ANG_200MS_HAR_I_72th_c | Phase C 72nd Current Angle Harmonics | float | 2 | R
0x2CC8 | 0x2CC9 | 11464 | 11465 | ANG_200MS_HAR_I_72th_n | Phase N 72nd Current Angle Harmonics | float | 2 | R
0x2CCA | 0x2CCB | 11466 | 11467 | ANG_200MS_HAR_V_73th_a | Phase A 73rd Voltage Angle Harmonics | float | 2 | R
0x2CCC | 0x2CCD | 11468 | 11469 | ANG_200MS_HAR_V_73th_b | Phase B 73rd Voltage Angle Harmonics | float | 2 | R
0x2CCE | 0x2CCF | 11470 | 11471 | ANG_200MS_HAR_V_73th_c | Phase C 73rd Voltage Angle Harmonics | float | 2 | R
0x2CD0 | 0x2CD1 | 11472 | 11473 | ANG_200MS_HAR_I_73th_a | Phase A 73rd Current Angle Harmonics | float | 2 | R
0x2CD2 | 0x2CD3 | 11474 | 11475 | ANG_200MS_HAR_I_73th_b | Phase B 73rd Current Angle Harmonics | float | 2 | R
0x2CD4 | 0x2CD5 | 11476 | 11477 | ANG_200MS_HAR_I_73th_c | Phase C 73rd Current Angle Harmonics | float | 2 | R
0x2CD6 | 0x2CD7 | 11478 | 11479 | ANG_200MS_HAR_I_73th_n | Phase N 73rd Current Angle Harmonics | float | 2 | R
0x2CD8 | 0x2CD9 | 11480 | 11481 | ANG_200MS_HAR_V_74th_a | Phase A 74th Voltage Angle Harmonics | float | 2 | R
0x2CDA | 0x2CDB | 11482 | 11483 | ANG_200MS_HAR_V_74th_b | Phase B 74th Voltage Angle Harmonics | float | 2 | R
0x2CDC | 0x2CDD | 11484 | 11485 | ANG_200MS_HAR_V_74th_c | Phase C 74th Voltage Angle Harmonics | float | 2 | R
0x2CDE | 0x2CDF | 11486 | 11487 | ANG_200MS_HAR_I_74th_a | Phase A 74th Current Angle Harmonics | float | 2 | R
0x2CE0 | 0x2CE1 | 11488 | 11489 | ANG_200MS_HAR_I_74th_b | Phase B 74th Current Angle Harmonics | float | 2 | R
0x2CE2 | 0x2CE3 | 11490 | 11491 | ANG_200MS_HAR_I_74th_c | Phase C 74th Current Angle Harmonics | float | 2 | R
0x2CE4 | 0x2CE5 | 11492 | 11493 | ANG_200MS_HAR_I_74th_n | Phase N 74th Current Angle Harmonics | float | 2 | R
0x2CE6 | 0x2CE7 | 11494 | 11495 | ANG_200MS_HAR_V_75th_a | Phase A 75th Voltage Angle Harmonics | float | 2 | R
0x2CE8 | 0x2CE9 | 11496 | 11497 | ANG_200MS_HAR_V_75th_b | Phase B 75th Voltage Angle Harmonics | float | 2 | R
0x2CEA | 0x2CEB | 11498 | 11499 | ANG_200MS_HAR_V_75th_c | Phase C 75th Voltage Angle Harmonics | float | 2 | R
0x2CEC | 0x2CED | 11500 | 11501 | ANG_200MS_HAR_I_75th_a | Phase A 75th Current Angle Harmonics | float | 2 | R
0x2CEE | 0x2CEF | 11502 | 11503 | ANG_200MS_HAR_I_75th_b | Phase B 75th Current Angle Harmonics | float | 2 | R
0x2CF0 | 0x2CF1 | 11504 | 11505 | ANG_200MS_HAR_I_75th_c | Phase C 75th Current Angle Harmonics | float | 2 | R
0x2CF2 | 0x2CF3 | 11506 | 11507 | ANG_200MS_HAR_I_75th_n | Phase N 75th Current Angle Harmonics | float | 2 | R
0x2CF4 | 0x2CF5 | 11508 | 11509 | ANG_200MS_HAR_V_76th_a | Phase A 76th Voltage Angle Harmonics | float | 2 | R
0x2CF6 | 0x2CF7 | 11510 | 11511 | ANG_200MS_HAR_V_76th_b | Phase B 76th Voltage Angle Harmonics | float | 2 | R
0x2CF8 | 0x2CF9 | 11512 | 11513 | ANG_200MS_HAR_V_76th_c | Phase C 76th Voltage Angle Harmonics | float | 2 | R
0x2CFA | 0x2CFB | 11514 | 11515 | ANG_200MS_HAR_I_76th_a | Phase A 76th Current Angle Harmonics | float | 2 | R
0x2CFC | 0x2CFD | 11516 | 11517 | ANG_200MS_HAR_I_76th_b | Phase B 76th Current Angle Harmonics | float | 2 | R
0x2CFE | 0x2CFF | 11518 | 11519 | ANG_200MS_HAR_I_76th_c | Phase C 76th Current Angle Harmonics | float | 2 | R
0x2D00 | 0x2D01 | 11520 | 11521 | ANG_200MS_HAR_I_76th_n | Phase N 76th Current Angle Harmonics | float | 2 | R
0x2D02 | 0x2D03 | 11522 | 11523 | ANG_200MS_HAR_V_77th_a | Phase A 77th Voltage Angle Harmonics | float | 2 | R
0x2D04 | 0x2D05 | 11524 | 11525 | ANG_200MS_HAR_V_77th_b | Phase B 77th Voltage Angle Harmonics | float | 2 | R
0x2D06 | 0x2D07 | 11526 | 11527 | ANG_200MS_HAR_V_77th_c | Phase C 77th Voltage Angle Harmonics | float | 2 | R
0x2D08 | 0x2D09 | 11528 | 11529 | ANG_200MS_HAR_I_77th_a | Phase A 77th Current Angle Harmonics | float | 2 | R
0x2D0A | 0x2D0B | 11530 | 11531 | ANG_200MS_HAR_I_77th_b | Phase B 77th Current Angle Harmonics | float | 2 | R
0x2D0C | 0x2D0D | 11532 | 11533 | ANG_200MS_HAR_I_77th_c | Phase C 77th Current Angle Harmonics | float | 2 | R
0x2D0E | 0x2D0F | 11534 | 11535 | ANG_200MS_HAR_I_77th_n | Phase N 77th Current Angle Harmonics | float | 2 | R
0x2D10 | 0x2D11 | 11536 | 11537 | ANG_200MS_HAR_V_78th_a | Phase A 78th Voltage Angle Harmonics | float | 2 | R
0x2D12 | 0x2D13 | 11538 | 11539 | ANG_200MS_HAR_V_78th_b | Phase B 78th Voltage Angle Harmonics | float | 2 | R
0x2D14 | 0x2D15 | 11540 | 11541 | ANG_200MS_HAR_V_78th_c | Phase C 78th Voltage Angle Harmonics | float | 2 | R
0x2D16 | 0x2D17 | 11542 | 11543 | ANG_200MS_HAR_I_78th_a | Phase A 78th Current Angle Harmonics | float | 2 | R
0x2D18 | 0x2D19 | 11544 | 11545 | ANG_200MS_HAR_I_78th_b | Phase B 78th Current Angle Harmonics | float | 2 | R
0x2D1A | 0x2D1B | 11546 | 11547 | ANG_200MS_HAR_I_78th_c | Phase C 78th Current Angle Harmonics | float | 2 | R
0x2D1C | 0x2D1D | 11548 | 11549 | ANG_200MS_HAR_I_78th_n | Phase N 78th Current Angle Harmonics | float | 2 | R
0x2D1E | 0x2D1F | 11550 | 11551 | ANG_200MS_HAR_V_79th_a | Phase A 79th Voltage Angle Harmonics | float | 2 | R
0x2D20 | 0x2D21 | 11552 | 11553 | ANG_200MS_HAR_V_79th_b | Phase B 79th Voltage Angle Harmonics | float | 2 | R
0x2D22 | 0x2D23 | 11554 | 11555 | ANG_200MS_HAR_V_79th_c | Phase C 79th Voltage Angle Harmonics | float | 2 | R
0x2D24 | 0x2D25 | 11556 | 11557 | ANG_200MS_HAR_I_79th_a | Phase A 79th Current Angle Harmonics | float | 2 | R
0x2D26 | 0x2D27 | 11558 | 11559 | ANG_200MS_HAR_I_79th_b | Phase B 79th Current Angle Harmonics | float | 2 | R
0x2D28 | 0x2D29 | 11560 | 11561 | ANG_200MS_HAR_I_79th_c | Phase C 79th Current Angle Harmonics | float | 2 | R
0x2D2A | 0x2D2B | 11562 | 11563 | ANG_200MS_HAR_I_79th_n | Phase N 79th Current Angle Harmonics | float | 2 | R
0x2D2C | 0x2D2D | 11564 | 11565 | ANG_200MS_HAR_V_80th_a | Phase A 80th Voltage Angle Harmonics | float | 2 | R
0x2D2E | 0x2D2F | 11566 | 11567 | ANG_200MS_HAR_V_80th_b | Phase B 80th Voltage Angle Harmonics | float | 2 | R
0x2D30 | 0x2D31 | 11568 | 11569 | ANG_200MS_HAR_V_80th_c | Phase C 80th Voltage Angle Harmonics | float | 2 | R
0x2D32 | 0x2D33 | 11570 | 11571 | ANG_200MS_HAR_I_80th_a | Phase A 80th Current Angle Harmonics | float | 2 | R
0x2D34 | 0x2D35 | 11572 | 11573 | ANG_200MS_HAR_I_80th_b | Phase B 80th Current Angle Harmonics | float | 2 | R
0x2D36 | 0x2D37 | 11574 | 11575 | ANG_200MS_HAR_I_80th_c | Phase C 80th Current Angle Harmonics | float | 2 | R
0x2D38 | 0x2D39 | 11576 | 11577 | ANG_200MS_HAR_I_80th_n | Phase N 80th Current Angle Harmonics | float | 2 | R
0x2D3A | 0x2D3B | 11578 | 11579 | ANG_200MS_HAR_V_81th_a | Phase A 81st Voltage Angle Harmonics | float | 2 | R
0x2D3C | 0x2D3D | 11580 | 11581 | ANG_200MS_HAR_V_81th_b | Phase B 81st Voltage Angle Harmonics | float | 2 | R
0x2D3E | 0x2D3F | 11582 | 11583 | ANG_200MS_HAR_V_81th_c | Phase C 81st Voltage Angle Harmonics | float | 2 | R
0x2D40 | 0x2D41 | 11584 | 11585 | ANG_200MS_HAR_I_81th_a | Phase A 81st Current Angle Harmonics | float | 2 | R
0x2D42 | 0x2D43 | 11586 | 11587 | ANG_200MS_HAR_I_81th_b | Phase B 81st Current Angle Harmonics | float | 2 | R
0x2D44 | 0x2D45 | 11588 | 11589 | ANG_200MS_HAR_I_81th_c | Phase C 81st Current Angle Harmonics | float | 2 | R
0x2D46 | 0x2D47 | 11590 | 11591 | ANG_200MS_HAR_I_81th_n | Phase N 81st Current Angle Harmonics | float | 2 | R
0x2D48 | 0x2D49 | 11592 | 11593 | ANG_200MS_HAR_V_82th_a | Phase A 82nd Voltage Angle Harmonics | float | 2 | R
0x2D4A | 0x2D4B | 11594 | 11595 | ANG_200MS_HAR_V_82th_b | Phase B 82nd Voltage Angle Harmonics | float | 2 | R
0x2D4C | 0x2D4D | 11596 | 11597 | ANG_200MS_HAR_V_82th_c | Phase C 82nd Voltage Angle Harmonics | float | 2 | R
0x2D4E | 0x2D4F | 11598 | 11599 | ANG_200MS_HAR_I_82th_a | Phase A 82nd Current Angle Harmonics | float | 2 | R
0x2D50 | 0x2D51 | 11600 | 11601 | ANG_200MS_HAR_I_82th_b | Phase B 82nd Current Angle Harmonics | float | 2 | R
0x2D52 | 0x2D53 | 11602 | 11603 | ANG_200MS_HAR_I_82th_c | Phase C 82nd Current Angle Harmonics | float | 2 | R
0x2D54 | 0x2D55 | 11604 | 11605 | ANG_200MS_HAR_I_82th_n | Phase N 82nd Current Angle Harmonics | float | 2 | R
0x2D56 | 0x2D57 | 11606 | 11607 | ANG_200MS_HAR_V_83th_a | Phase A 83rd Voltage Angle Harmonics | float | 2 | R
0x2D58 | 0x2D59 | 11608 | 11609 | ANG_200MS_HAR_V_83th_b | Phase B 83rd Voltage Angle Harmonics | float | 2 | R
0x2D5A | 0x2D5B | 11610 | 11611 | ANG_200MS_HAR_V_83th_c | Phase C 83rd Voltage Angle Harmonics | float | 2 | R
0x2D5C | 0x2D5D | 11612 | 11613 | ANG_200MS_HAR_I_83th_a | Phase A 83rd Current Angle Harmonics | float | 2 | R
0x2D5E | 0x2D5F | 11614 | 11615 | ANG_200MS_HAR_I_83th_b | Phase B 83rd Current Angle Harmonics | float | 2 | R
0x2D60 | 0x2D61 | 11616 | 11617 | ANG_200MS_HAR_I_83th_c | Phase C 83rd Current Angle Harmonics | float | 2 | R
0x2D62 | 0x2D63 | 11618 | 11619 | ANG_200MS_HAR_I_83th_n | Phase N 83rd Current Angle Harmonics | float | 2 | R
0x2D64 | 0x2D65 | 11620 | 11621 | ANG_200MS_HAR_V_84th_a | Phase A 84th Voltage Angle Harmonics | float | 2 | R
0x2D66 | 0x2D67 | 11622 | 11623 | ANG_200MS_HAR_V_84th_b | Phase B 84th Voltage Angle Harmonics | float | 2 | R
0x2D68 | 0x2D69 | 11624 | 11625 | ANG_200MS_HAR_V_84th_c | Phase C 84th Voltage Angle Harmonics | float | 2 | R
0x2D6A | 0x2D6B | 11626 | 11627 | ANG_200MS_HAR_I_84th_a | Phase A 84th Current Angle Harmonics | float | 2 | R
0x2D6C | 0x2D6D | 11628 | 11629 | ANG_200MS_HAR_I_84th_b | Phase B 84th Current Angle Harmonics | float | 2 | R
0x2D6E | 0x2D6F | 11630 | 11631 | ANG_200MS_HAR_I_84th_c | Phase C 84th Current Angle Harmonics | float | 2 | R
0x2D70 | 0x2D71 | 11632 | 11633 | ANG_200MS_HAR_I_84th_n | Phase N 84th Current Angle Harmonics | float | 2 | R
0x2D72 | 0x2D73 | 11634 | 11635 | ANG_200MS_HAR_V_85th_a | Phase A 85th Voltage Angle Harmonics | float | 2 | R
0x2D74 | 0x2D75 | 11636 | 11637 | ANG_200MS_HAR_V_85th_b | Phase B 85th Voltage Angle Harmonics | float | 2 | R
0x2D76 | 0x2D77 | 11638 | 11639 | ANG_200MS_HAR_V_85th_c | Phase C 85th Voltage Angle Harmonics | float | 2 | R
0x2D78 | 0x2D79 | 11640 | 11641 | ANG_200MS_HAR_I_85th_a | Phase A 85th Current Angle Harmonics | float | 2 | R
0x2D7A | 0x2D7B | 11642 | 11643 | ANG_200MS_HAR_I_85th_b | Phase B 85th Current Angle Harmonics | float | 2 | R
0x2D7C | 0x2D7D | 11644 | 11645 | ANG_200MS_HAR_I_85th_c | Phase C 85th Current Angle Harmonics | float | 2 | R
0x2D7E | 0x2D7F | 11646 | 11647 | ANG_200MS_HAR_I_85th_n | Phase N 85th Current Angle Harmonics | float | 2 | R
0x2D80 | 0x2D81 | 11648 | 11649 | ANG_200MS_HAR_V_86th_a | Phase A 86th Voltage Angle Harmonics | float | 2 | R
0x2D82 | 0x2D83 | 11650 | 11651 | ANG_200MS_HAR_V_86th_b | Phase B 86th Voltage Angle Harmonics | float | 2 | R
0x2D84 | 0x2D85 | 11652 | 11653 | ANG_200MS_HAR_V_86th_c | Phase C 86th Voltage Angle Harmonics | float | 2 | R
0x2D86 | 0x2D87 | 11654 | 11655 | ANG_200MS_HAR_I_86th_a | Phase A 86th Current Angle Harmonics | float | 2 | R
0x2D88 | 0x2D89 | 11656 | 11657 | ANG_200MS_HAR_I_86th_b | Phase B 86th Current Angle Harmonics | float | 2 | R
0x2D8A | 0x2D8B | 11658 | 11659 | ANG_200MS_HAR_I_86th_c | Phase C 86th Current Angle Harmonics | float | 2 | R
0x2D8C | 0x2D8D | 11660 | 11661 | ANG_200MS_HAR_I_86th_n | Phase N 86th Current Angle Harmonics | float | 2 | R
0x2D8E | 0x2D8F | 11662 | 11663 | ANG_200MS_HAR_V_87th_a | Phase A 87th Voltage Angle Harmonics | float | 2 | R
0x2D90 | 0x2D91 | 11664 | 11665 | ANG_200MS_HAR_V_87th_b | Phase B 87th Voltage Angle Harmonics | float | 2 | R
0x2D92 | 0x2D93 | 11666 | 11667 | ANG_200MS_HAR_V_87th_c | Phase C 87th Voltage Angle Harmonics | float | 2 | R
0x2D94 | 0x2D95 | 11668 | 11669 | ANG_200MS_HAR_I_87th_a | Phase A 87th Current Angle Harmonics | float | 2 | R
0x2D96 | 0x2D97 | 11670 | 11671 | ANG_200MS_HAR_I_87th_b | Phase B 87th Current Angle Harmonics | float | 2 | R
0x2D98 | 0x2D99 | 11672 | 11673 | ANG_200MS_HAR_I_87th_c | Phase C 87th Current Angle Harmonics | float | 2 | R
0x2D9A | 0x2D9B | 11674 | 11675 | ANG_200MS_HAR_I_87th_n | Phase N 87th Current Angle Harmonics | float | 2 | R
0x2D9C | 0x2D9D | 11676 | 11677 | ANG_200MS_HAR_V_88th_a | Phase A 88th Voltage Angle Harmonics | float | 2 | R
0x2D9E | 0x2D9F | 11678 | 11679 | ANG_200MS_HAR_V_88th_b | Phase B 88th Voltage Angle Harmonics | float | 2 | R
0x2DA0 | 0x2DA1 | 11680 | 11681 | ANG_200MS_HAR_V_88th_c | Phase C 88th Voltage Angle Harmonics | float | 2 | R
0x2DA2 | 0x2DA3 | 11682 | 11683 | ANG_200MS_HAR_I_88th_a | Phase A 88th Current Angle Harmonics | float | 2 | R
0x2DA4 | 0x2DA5 | 11684 | 11685 | ANG_200MS_HAR_I_88th_b | Phase B 88th Current Angle Harmonics | float | 2 | R
0x2DA6 | 0x2DA7 | 11686 | 11687 | ANG_200MS_HAR_I_88th_c | Phase C 88th Current Angle Harmonics | float | 2 | R
0x2DA8 | 0x2DA9 | 11688 | 11689 | ANG_200MS_HAR_I_88th_n | Phase N 88th Current Angle Harmonics | float | 2 | R
0x2DAA | 0x2DAB | 11690 | 11691 | ANG_200MS_HAR_V_89th_a | Phase A 89th Voltage Angle Harmonics | float | 2 | R
0x2DAC | 0x2DAD | 11692 | 11693 | ANG_200MS_HAR_V_89th_b | Phase B 89th Voltage Angle Harmonics | float | 2 | R
0x2DAE | 0x2DAF | 11694 | 11695 | ANG_200MS_HAR_V_89th_c | Phase C 89th Voltage Angle Harmonics | float | 2 | R
0x2DB0 | 0x2DB1 | 11696 | 11697 | ANG_200MS_HAR_I_89th_a | Phase A 89th Current Angle Harmonics | float | 2 | R
0x2DB2 | 0x2DB3 | 11698 | 11699 | ANG_200MS_HAR_I_89th_b | Phase B 89th Current Angle Harmonics | float | 2 | R
0x2DB4 | 0x2DB5 | 11700 | 11701 | ANG_200MS_HAR_I_89th_c | Phase C 89th Current Angle Harmonics | float | 2 | R
0x2DB6 | 0x2DB7 | 11702 | 11703 | ANG_200MS_HAR_I_89th_n | Phase N 89th Current Angle Harmonics | float | 2 | R
0x2DB8 | 0x2DB9 | 11704 | 11705 | ANG_200MS_HAR_V_90th_a | Phase A 90th Voltage Angle Harmonics | float | 2 | R
0x2DBA | 0x2DBB | 11706 | 11707 | ANG_200MS_HAR_V_90th_b | Phase B 90th Voltage Angle Harmonics | float | 2 | R
0x2DBC | 0x2DBD | 11708 | 11709 | ANG_200MS_HAR_V_90th_c | Phase C 90th Voltage Angle Harmonics | float | 2 | R
0x2DBE | 0x2DBF | 11710 | 11711 | ANG_200MS_HAR_I_90th_a | Phase A 90th Current Angle Harmonics | float | 2 | R
0x2DC0 | 0x2DC1 | 11712 | 11713 | ANG_200MS_HAR_I_90th_b | Phase B 90th Current Angle Harmonics | float | 2 | R
0x2DC2 | 0x2DC3 | 11714 | 11715 | ANG_200MS_HAR_I_90th_c | Phase C 90th Current Angle Harmonics | float | 2 | R
0x2DC4 | 0x2DC5 | 11716 | 11717 | ANG_200MS_HAR_I_90th_n | Phase N 90th Current Angle Harmonics | float | 2 | R
0x2DC6 | 0x2DC7 | 11718 | 11719 | ANG_200MS_HAR_V_91th_a | Phase A 91st Voltage Angle Harmonics | float | 2 | R
0x2DC8 | 0x2DC9 | 11720 | 11721 | ANG_200MS_HAR_V_91th_b | Phase B 91st Voltage Angle Harmonics | float | 2 | R
0x2DCA | 0x2DCB | 11722 | 11723 | ANG_200MS_HAR_V_91th_c | Phase C 91st Voltage Angle Harmonics | float | 2 | R
0x2DCC | 0x2DCD | 11724 | 11725 | ANG_200MS_HAR_I_91th_a | Phase A 91st Current Angle Harmonics | float | 2 | R
0x2DCE | 0x2DCF | 11726 | 11727 | ANG_200MS_HAR_I_91th_b | Phase B 91st Current Angle Harmonics | float | 2 | R
0x2DD0 | 0x2DD1 | 11728 | 11729 | ANG_200MS_HAR_I_91th_c | Phase C 91st Current Angle Harmonics | float | 2 | R
0x2DD2 | 0x2DD3 | 11730 | 11731 | ANG_200MS_HAR_I_91th_n | Phase N 91st Current Angle Harmonics | float | 2 | R
0x2DD4 | 0x2DD5 | 11732 | 11733 | ANG_200MS_HAR_V_92th_a | Phase A 92nd Voltage Angle Harmonics | float | 2 | R
0x2DD6 | 0x2DD7 | 11734 | 11735 | ANG_200MS_HAR_V_92th_b | Phase B 92nd Voltage Angle Harmonics | float | 2 | R
0x2DD8 | 0x2DD9 | 11736 | 11737 | ANG_200MS_HAR_V_92th_c | Phase C 92nd Voltage Angle Harmonics | float | 2 | R
0x2DDA | 0x2DDB | 11738 | 11739 | ANG_200MS_HAR_I_92th_a | Phase A 92nd Current Angle Harmonics | float | 2 | R
0x2DDC | 0x2DDD | 11740 | 11741 | ANG_200MS_HAR_I_92th_b | Phase B 92nd Current Angle Harmonics | float | 2 | R
0x2DDE | 0x2DDF | 11742 | 11743 | ANG_200MS_HAR_I_92th_c | Phase C 92nd Current Angle Harmonics | float | 2 | R
0x2DE0 | 0x2DE1 | 11744 | 11745 | ANG_200MS_HAR_I_92th_n | Phase N 92nd Current Angle Harmonics | float | 2 | R
0x2DE2 | 0x2DE3 | 11746 | 11747 | ANG_200MS_HAR_V_93th_a | Phase A 93rd Voltage Angle Harmonics | float | 2 | R
0x2DE4 | 0x2DE5 | 11748 | 11749 | ANG_200MS_HAR_V_93th_b | Phase B 93rd Voltage Angle Harmonics | float | 2 | R
0x2DE6 | 0x2DE7 | 11750 | 11751 | ANG_200MS_HAR_V_93th_c | Phase C 93rd Voltage Angle Harmonics | float | 2 | R
0x2DE8 | 0x2DE9 | 11752 | 11753 | ANG_200MS_HAR_I_93th_a | Phase A 93rd Current Angle Harmonics | float | 2 | R
0x2DEA | 0x2DEB | 11754 | 11755 | ANG_200MS_HAR_I_93th_b | Phase B 93rd Current Angle Harmonics | float | 2 | R
0x2DEC | 0x2DED | 11756 | 11757 | ANG_200MS_HAR_I_93th_c | Phase C 93rd Current Angle Harmonics | float | 2 | R
0x2DEE | 0x2DEF | 11758 | 11759 | ANG_200MS_HAR_I_93th_n | Phase N 93rd Current Angle Harmonics | float | 2 | R
0x2DF0 | 0x2DF1 | 11760 | 11761 | ANG_200MS_HAR_V_94th_a | Phase A 94th Voltage Angle Harmonics | float | 2 | R
0x2DF2 | 0x2DF3 | 11762 | 11763 | ANG_200MS_HAR_V_94th_b | Phase B 94th Voltage Angle Harmonics | float | 2 | R
0x2DF4 | 0x2DF5 | 11764 | 11765 | ANG_200MS_HAR_V_94th_c | Phase C 94th Voltage Angle Harmonics | float | 2 | R
0x2DF6 | 0x2DF7 | 11766 | 11767 | ANG_200MS_HAR_I_94th_a | Phase A 94th Current Angle Harmonics | float | 2 | R
0x2DF8 | 0x2DF9 | 11768 | 11769 | ANG_200MS_HAR_I_94th_b | Phase B 94th Current Angle Harmonics | float | 2 | R
0x2DFA | 0x2DFB | 11770 | 11771 | ANG_200MS_HAR_I_94th_c | Phase C 94th Current Angle Harmonics | float | 2 | R
0x2DFC | 0x2DFD | 11772 | 11773 | ANG_200MS_HAR_I_94th_n | Phase N 94th Current Angle Harmonics | float | 2 | R
0x2DFE | 0x2DFF | 11774 | 11775 | ANG_200MS_HAR_V_95th_a | Phase A 95th Voltage Angle Harmonics | float | 2 | R
0x2E00 | 0x2E01 | 11776 | 11777 | ANG_200MS_HAR_V_95th_b | Phase B 95th Voltage Angle Harmonics | float | 2 | R
0x2E02 | 0x2E03 | 11778 | 11779 | ANG_200MS_HAR_V_95th_c | Phase C 95th Voltage Angle Harmonics | float | 2 | R
0x2E04 | 0x2E05 | 11780 | 11781 | ANG_200MS_HAR_I_95th_a | Phase A 95th Current Angle Harmonics | float | 2 | R
0x2E06 | 0x2E07 | 11782 | 11783 | ANG_200MS_HAR_I_95th_b | Phase B 95th Current Angle Harmonics | float | 2 | R
0x2E08 | 0x2E09 | 11784 | 11785 | ANG_200MS_HAR_I_95th_c | Phase C 95th Current Angle Harmonics | float | 2 | R
0x2E0A | 0x2E0B | 11786 | 11787 | ANG_200MS_HAR_I_95th_n | Phase N 95th Current Angle Harmonics | float | 2 | R
0x2E0C | 0x2E0D | 11788 | 11789 | ANG_200MS_HAR_V_96th_a | Phase A 96th Voltage Angle Harmonics | float | 2 | R
0x2E0E | 0x2E0F | 11790 | 11791 | ANG_200MS_HAR_V_96th_b | Phase B 96th Voltage Angle Harmonics | float | 2 | R
0x2E10 | 0x2E11 | 11792 | 11793 | ANG_200MS_HAR_V_96th_c | Phase C 96th Voltage Angle Harmonics | float | 2 | R
0x2E12 | 0x2E13 | 11794 | 11795 | ANG_200MS_HAR_I_96th_a | Phase A 96th Current Angle Harmonics | float | 2 | R
0x2E14 | 0x2E15 | 11796 | 11797 | ANG_200MS_HAR_I_96th_b | Phase B 96th Current Angle Harmonics | float | 2 | R
0x2E16 | 0x2E17 | 11798 | 11799 | ANG_200MS_HAR_I_96th_c | Phase C 96th Current Angle Harmonics | float | 2 | R
0x2E18 | 0x2E19 | 11800 | 11801 | ANG_200MS_HAR_I_96th_n | Phase N 96th Current Angle Harmonics | float | 2 | R
0x2E1A | 0x2E1B | 11802 | 11803 | ANG_200MS_HAR_V_97th_a | Phase A 97th Voltage Angle Harmonics | float | 2 | R
0x2E1C | 0x2E1D | 11804 | 11805 | ANG_200MS_HAR_V_97th_b | Phase B 97th Voltage Angle Harmonics | float | 2 | R
0x2E1E | 0x2E1F | 11806 | 11807 | ANG_200MS_HAR_V_97th_c | Phase C 97th Voltage Angle Harmonics | float | 2 | R
0x2E20 | 0x2E21 | 11808 | 11809 | ANG_200MS_HAR_I_97th_a | Phase A 97th Current Angle Harmonics | float | 2 | R
0x2E22 | 0x2E23 | 11810 | 11811 | ANG_200MS_HAR_I_97th_b | Phase B 97th Current Angle Harmonics | float | 2 | R
0x2E24 | 0x2E25 | 11812 | 11813 | ANG_200MS_HAR_I_97th_c | Phase C 97th Current Angle Harmonics | float | 2 | R
0x2E26 | 0x2E27 | 11814 | 11815 | ANG_200MS_HAR_I_97th_n | Phase N 97th Current Angle Harmonics | float | 2 | R
0x2E28 | 0x2E29 | 11816 | 11817 | ANG_200MS_HAR_V_98th_a | Phase A 98th Voltage Angle Harmonics | float | 2 | R
0x2E2A | 0x2E2B | 11818 | 11819 | ANG_200MS_HAR_V_98th_b | Phase B 98th Voltage Angle Harmonics | float | 2 | R
0x2E2C | 0x2E2D | 11820 | 11821 | ANG_200MS_HAR_V_98th_c | Phase C 98th Voltage Angle Harmonics | float | 2 | R
0x2E2E | 0x2E2F | 11822 | 11823 | ANG_200MS_HAR_I_98th_a | Phase A 98th Current Angle Harmonics | float | 2 | R
0x2E30 | 0x2E31 | 11824 | 11825 | ANG_200MS_HAR_I_98th_b | Phase B 98th Current Angle Harmonics | float | 2 | R
0x2E32 | 0x2E33 | 11826 | 11827 | ANG_200MS_HAR_I_98th_c | Phase C 98th Current Angle Harmonics | float | 2 | R
0x2E34 | 0x2E35 | 11828 | 11829 | ANG_200MS_HAR_I_98th_n | Phase N 98th Current Angle Harmonics | float | 2 | R
0x2E36 | 0x2E37 | 11830 | 11831 | ANG_200MS_HAR_V_99th_a | Phase A 99th Voltage Angle Harmonics | float | 2 | R
0x2E38 | 0x2E39 | 11832 | 11833 | ANG_200MS_HAR_V_99th_b | Phase B 99th Voltage Angle Harmonics | float | 2 | R
0x2E3A | 0x2E3B | 11834 | 11835 | ANG_200MS_HAR_V_99th_c | Phase C 99th Voltage Angle Harmonics | float | 2 | R
0x2E3C | 0x2E3D | 11836 | 11837 | ANG_200MS_HAR_I_99th_a | Phase A 99th Current Angle Harmonics | float | 2 | R
0x2E3E | 0x2E3F | 11838 | 11839 | ANG_200MS_HAR_I_99th_b | Phase B 99th Current Angle Harmonics | float | 2 | R
0x2E40 | 0x2E41 | 11840 | 11841 | ANG_200MS_HAR_I_99th_c | Phase C 99th Current Angle Harmonics | float | 2 | R
0x2E42 | 0x2E43 | 11842 | 11843 | ANG_200MS_HAR_I_99th_n | Phase N 99th Current Angle Harmonics | float | 2 | R
0x2E44 | 0x2E45 | 11844 | 11845 | ANG_200MS_HAR_V_100th_a | Phase A 100th Voltage Angle Harmonics | float | 2 | R
0x2E46 | 0x2E47 | 11846 | 11847 | ANG_200MS_HAR_V_100th_b | Phase B 100th Voltage Angle Harmonics | float | 2 | R
0x2E48 | 0x2E49 | 11848 | 11849 | ANG_200MS_HAR_V_100th_c | Phase C 100th Voltage Angle Harmonics | float | 2 | R
0x2E4A | 0x2E4B | 11850 | 11851 | ANG_200MS_HAR_I_100th_a | Phase A 100th Current Angle Harmonics | float | 2 | R
0x2E4C | 0x2E4D | 11852 | 11853 | ANG_200MS_HAR_I_100th_b | Phase B 100th Current Angle Harmonics | float | 2 | R
0x2E4E | 0x2E4F | 11854 | 11855 | ANG_200MS_HAR_I_100th_c | Phase C 100th Current Angle Harmonics | float | 2 | R
0x2E50 | 0x2E51 | 11856 | 11857 | ANG_200MS_HAR_I_100th_n | Phase N 100th Current Angle Harmonics | float | 2 | R
0x2E52 | 0x2E53 | 11858 | 11859 | ANG_200MS_HAR_V_101th_a | Phase A 101st Voltage Angle Harmonics | float | 2 | R
0x2E54 | 0x2E55 | 11860 | 11861 | ANG_200MS_HAR_V_101th_b | Phase B 101st Voltage Angle Harmonics | float | 2 | R
0x2E56 | 0x2E57 | 11862 | 11863 | ANG_200MS_HAR_V_101th_c | Phase C 101st Voltage Angle Harmonics | float | 2 | R
0x2E58 | 0x2E59 | 11864 | 11865 | ANG_200MS_HAR_I_101th_a | Phase A 101st Current Angle Harmonics | float | 2 | R
0x2E5A | 0x2E5B | 11866 | 11867 | ANG_200MS_HAR_I_101th_b | Phase B 101st Current Angle Harmonics | float | 2 | R
0x2E5C | 0x2E5D | 11868 | 11869 | ANG_200MS_HAR_I_101th_c | Phase C 101st Current Angle Harmonics | float | 2 | R
0x2E5E | 0x2E5F | 11870 | 11871 | ANG_200MS_HAR_I_101th_n | Phase N 101st Current Angle Harmonics | float | 2 | R
0x2E60 | 0x2E61 | 11872 | 11873 | ANG_200MS_HAR_V_102th_a | Phase A 102nd Voltage Angle Harmonics | float | 2 | R
0x2E62 | 0x2E63 | 11874 | 11875 | ANG_200MS_HAR_V_102th_b | Phase B 102nd Voltage Angle Harmonics | float | 2 | R
0x2E64 | 0x2E65 | 11876 | 11877 | ANG_200MS_HAR_V_102th_c | Phase C 102nd Voltage Angle Harmonics | float | 2 | R
0x2E66 | 0x2E67 | 11878 | 11879 | ANG_200MS_HAR_I_102th_a | Phase A 102nd Current Angle Harmonics | float | 2 | R
0x2E68 | 0x2E69 | 11880 | 11881 | ANG_200MS_HAR_I_102th_b | Phase B 102nd Current Angle Harmonics | float | 2 | R
0x2E6A | 0x2E6B | 11882 | 11883 | ANG_200MS_HAR_I_102th_c | Phase C 102nd Current Angle Harmonics | float | 2 | R
0x2E6C | 0x2E6D | 11884 | 11885 | ANG_200MS_HAR_I_102th_n | Phase N 102nd Current Angle Harmonics | float | 2 | R
0x2E6E | 0x2E6F | 11886 | 11887 | ANG_200MS_HAR_V_103th_a | Phase A 103rd Voltage Angle Harmonics | float | 2 | R
0x2E70 | 0x2E71 | 11888 | 11889 | ANG_200MS_HAR_V_103th_b | Phase B 103rd Voltage Angle Harmonics | float | 2 | R
0x2E72 | 0x2E73 | 11890 | 11891 | ANG_200MS_HAR_V_103th_c | Phase C 103rd Voltage Angle Harmonics | float | 2 | R
0x2E74 | 0x2E75 | 11892 | 11893 | ANG_200MS_HAR_I_103th_a | Phase A 103rd Current Angle Harmonics | float | 2 | R
0x2E76 | 0x2E77 | 11894 | 11895 | ANG_200MS_HAR_I_103th_b | Phase B 103rd Current Angle Harmonics | float | 2 | R
0x2E78 | 0x2E79 | 11896 | 11897 | ANG_200MS_HAR_I_103th_c | Phase C 103rd Current Angle Harmonics | float | 2 | R
0x2E7A | 0x2E7B | 11898 | 11899 | ANG_200MS_HAR_I_103th_n | Phase N 103rd Current Angle Harmonics | float | 2 | R
0x2E7C | 0x2E7D | 11900 | 11901 | ANG_200MS_HAR_V_104th_a | Phase A 104th Voltage Angle Harmonics | float | 2 | R
0x2E7E | 0x2E7F | 11902 | 11903 | ANG_200MS_HAR_V_104th_b | Phase B 104th Voltage Angle Harmonics | float | 2 | R
0x2E80 | 0x2E81 | 11904 | 11905 | ANG_200MS_HAR_V_104th_c | Phase C 104th Voltage Angle Harmonics | float | 2 | R
0x2E82 | 0x2E83 | 11906 | 11907 | ANG_200MS_HAR_I_104th_a | Phase A 104th Current Angle Harmonics | float | 2 | R
0x2E84 | 0x2E85 | 11908 | 11909 | ANG_200MS_HAR_I_104th_b | Phase B 104th Current Angle Harmonics | float | 2 | R
0x2E86 | 0x2E87 | 11910 | 11911 | ANG_200MS_HAR_I_104th_c | Phase C 104th Current Angle Harmonics | float | 2 | R
0x2E88 | 0x2E89 | 11912 | 11913 | ANG_200MS_HAR_I_104th_n | Phase N 104th Current Angle Harmonics | float | 2 | R
0x2E8A | 0x2E8B | 11914 | 11915 | ANG_200MS_HAR_V_105th_a | Phase A 105th Voltage Angle Harmonics | float | 2 | R
0x2E8C | 0x2E8D | 11916 | 11917 | ANG_200MS_HAR_V_105th_b | Phase B 105th Voltage Angle Harmonics | float | 2 | R
0x2E8E | 0x2E8F | 11918 | 11919 | ANG_200MS_HAR_V_105th_c | Phase C 105th Voltage Angle Harmonics | float | 2 | R
0x2E90 | 0x2E91 | 11920 | 11921 | ANG_200MS_HAR_I_105th_a | Phase A 105th Current Angle Harmonics | float | 2 | R
0x2E92 | 0x2E93 | 11922 | 11923 | ANG_200MS_HAR_I_105th_b | Phase B 105th Current Angle Harmonics | float | 2 | R
0x2E94 | 0x2E95 | 11924 | 11925 | ANG_200MS_HAR_I_105th_c | Phase C 105th Current Angle Harmonics | float | 2 | R
0x2E96 | 0x2E97 | 11926 | 11927 | ANG_200MS_HAR_I_105th_n | Phase N 105th Current Angle Harmonics | float | 2 | R
0x2E98 | 0x2E99 | 11928 | 11929 | ANG_200MS_HAR_V_106th_a | Phase A 106th Voltage Angle Harmonics | float | 2 | R
0x2E9A | 0x2E9B | 11930 | 11931 | ANG_200MS_HAR_V_106th_b | Phase B 106th Voltage Angle Harmonics | float | 2 | R
0x2E9C | 0x2E9D | 11932 | 11933 | ANG_200MS_HAR_V_106th_c | Phase C 106th Voltage Angle Harmonics | float | 2 | R
0x2E9E | 0x2E9F | 11934 | 11935 | ANG_200MS_HAR_I_106th_a | Phase A 106th Current Angle Harmonics | float | 2 | R
0x2EA0 | 0x2EA1 | 11936 | 11937 | ANG_200MS_HAR_I_106th_b | Phase B 106th Current Angle Harmonics | float | 2 | R
0x2EA2 | 0x2EA3 | 11938 | 11939 | ANG_200MS_HAR_I_106th_c | Phase C 106th Current Angle Harmonics | float | 2 | R
0x2EA4 | 0x2EA5 | 11940 | 11941 | ANG_200MS_HAR_I_106th_n | Phase N 106th Current Angle Harmonics | float | 2 | R
0x2EA6 | 0x2EA7 | 11942 | 11943 | ANG_200MS_HAR_V_107th_a | Phase A 107th Voltage Angle Harmonics | float | 2 | R
0x2EA8 | 0x2EA9 | 11944 | 11945 | ANG_200MS_HAR_V_107th_b | Phase B 107th Voltage Angle Harmonics | float | 2 | R
0x2EAA | 0x2EAB | 11946 | 11947 | ANG_200MS_HAR_V_107th_c | Phase C 107th Voltage Angle Harmonics | float | 2 | R
0x2EAC | 0x2EAD | 11948 | 11949 | ANG_200MS_HAR_I_107th_a | Phase A 107th Current Angle Harmonics | float | 2 | R
0x2EAE | 0x2EAF | 11950 | 11951 | ANG_200MS_HAR_I_107th_b | Phase B 107th Current Angle Harmonics | float | 2 | R
0x2EB0 | 0x2EB1 | 11952 | 11953 | ANG_200MS_HAR_I_107th_c | Phase C 107th Current Angle Harmonics | float | 2 | R
0x2EB2 | 0x2EB3 | 11954 | 11955 | ANG_200MS_HAR_I_107th_n | Phase N 107th Current Angle Harmonics | float | 2 | R
0x2EB4 | 0x2EB5 | 11956 | 11957 | ANG_200MS_HAR_V_108th_a | Phase A 108th Voltage Angle Harmonics | float | 2 | R
0x2EB6 | 0x2EB7 | 11958 | 11959 | ANG_200MS_HAR_V_108th_b | Phase B 108th Voltage Angle Harmonics | float | 2 | R
0x2EB8 | 0x2EB9 | 11960 | 11961 | ANG_200MS_HAR_V_108th_c | Phase C 108th Voltage Angle Harmonics | float | 2 | R
0x2EBA | 0x2EBB | 11962 | 11963 | ANG_200MS_HAR_I_108th_a | Phase A 108th Current Angle Harmonics | float | 2 | R
0x2EBC | 0x2EBD | 11964 | 11965 | ANG_200MS_HAR_I_108th_b | Phase B 108th Current Angle Harmonics | float | 2 | R
0x2EBE | 0x2EBF | 11966 | 11967 | ANG_200MS_HAR_I_108th_c | Phase C 108th Current Angle Harmonics | float | 2 | R
0x2EC0 | 0x2EC1 | 11968 | 11969 | ANG_200MS_HAR_I_108th_n | Phase N 108th Current Angle Harmonics | float | 2 | R
0x2EC2 | 0x2EC3 | 11970 | 11971 | ANG_200MS_HAR_V_109th_a | Phase A 109th Voltage Angle Harmonics | float | 2 | R
0x2EC4 | 0x2EC5 | 11972 | 11973 | ANG_200MS_HAR_V_109th_b | Phase B 109th Voltage Angle Harmonics | float | 2 | R
0x2EC6 | 0x2EC7 | 11974 | 11975 | ANG_200MS_HAR_V_109th_c | Phase C 109th Voltage Angle Harmonics | float | 2 | R
0x2EC8 | 0x2EC9 | 11976 | 11977 | ANG_200MS_HAR_I_109th_a | Phase A 109th Current Angle Harmonics | float | 2 | R
0x2ECA | 0x2ECB | 11978 | 11979 | ANG_200MS_HAR_I_109th_b | Phase B 109th Current Angle Harmonics | float | 2 | R
0x2ECC | 0x2ECD | 11980 | 11981 | ANG_200MS_HAR_I_109th_c | Phase C 109th Current Angle Harmonics | float | 2 | R
0x2ECE | 0x2ECF | 11982 | 11983 | ANG_200MS_HAR_I_109th_n | Phase N 109th Current Angle Harmonics | float | 2 | R
0x2ED0 | 0x2ED1 | 11984 | 11985 | ANG_200MS_HAR_V_110th_a | Phase A 110th Voltage Angle Harmonics | float | 2 | R
0x2ED2 | 0x2ED3 | 11986 | 11987 | ANG_200MS_HAR_V_110th_b | Phase B 110th Voltage Angle Harmonics | float | 2 | R
0x2ED4 | 0x2ED5 | 11988 | 11989 | ANG_200MS_HAR_V_110th_c | Phase C 110th Voltage Angle Harmonics | float | 2 | R
0x2ED6 | 0x2ED7 | 11990 | 11991 | ANG_200MS_HAR_I_110th_a | Phase A 110th Current Angle Harmonics | float | 2 | R
0x2ED8 | 0x2ED9 | 11992 | 11993 | ANG_200MS_HAR_I_110th_b | Phase B 110th Current Angle Harmonics | float | 2 | R
0x2EDA | 0x2EDB | 11994 | 11995 | ANG_200MS_HAR_I_110th_c | Phase C 110th Current Angle Harmonics | float | 2 | R
0x2EDC | 0x2EDD | 11996 | 11997 | ANG_200MS_HAR_I_110th_n | Phase N 110th Current Angle Harmonics | float | 2 | R
0x2EDE | 0x2EDF | 11998 | 11999 | ANG_200MS_HAR_V_111th_a | Phase A 111st Voltage Angle Harmonics | float | 2 | R
0x2EE0 | 0x2EE1 | 12000 | 12001 | ANG_200MS_HAR_V_111th_b | Phase B 111st Voltage Angle Harmonics | float | 2 | R
0x2EE2 | 0x2EE3 | 12002 | 12003 | ANG_200MS_HAR_V_111th_c | Phase C 111st Voltage Angle Harmonics | float | 2 | R
0x2EE4 | 0x2EE5 | 12004 | 12005 | ANG_200MS_HAR_I_111th_a | Phase A 111st Current Angle Harmonics | float | 2 | R
0x2EE6 | 0x2EE7 | 12006 | 12007 | ANG_200MS_HAR_I_111th_b | Phase B 111st Current Angle Harmonics | float | 2 | R
0x2EE8 | 0x2EE9 | 12008 | 12009 | ANG_200MS_HAR_I_111th_c | Phase C 111st Current Angle Harmonics | float | 2 | R
0x2EEA | 0x2EEB | 12010 | 12011 | ANG_200MS_HAR_I_111th_n | Phase N 111st Current Angle Harmonics | float | 2 | R
0x2EEC | 0x2EED | 12012 | 12013 | ANG_200MS_HAR_V_112th_a | Phase A 112nd Voltage Angle Harmonics | float | 2 | R
0x2EEE | 0x2EEF | 12014 | 12015 | ANG_200MS_HAR_V_112th_b | Phase B 112nd Voltage Angle Harmonics | float | 2 | R
0x2EF0 | 0x2EF1 | 12016 | 12017 | ANG_200MS_HAR_V_112th_c | Phase C 112nd Voltage Angle Harmonics | float | 2 | R
0x2EF2 | 0x2EF3 | 12018 | 12019 | ANG_200MS_HAR_I_112th_a | Phase A 112nd Current Angle Harmonics | float | 2 | R
0x2EF4 | 0x2EF5 | 12020 | 12021 | ANG_200MS_HAR_I_112th_b | Phase B 112nd Current Angle Harmonics | float | 2 | R
0x2EF6 | 0x2EF7 | 12022 | 12023 | ANG_200MS_HAR_I_112th_c | Phase C 112nd Current Angle Harmonics | float | 2 | R
0x2EF8 | 0x2EF9 | 12024 | 12025 | ANG_200MS_HAR_I_112th_n | Phase N 112nd Current Angle Harmonics | float | 2 | R
0x2EFA | 0x2EFB | 12026 | 12027 | ANG_200MS_HAR_V_113th_a | Phase A 113rd Voltage Angle Harmonics | float | 2 | R
0x2EFC | 0x2EFD | 12028 | 12029 | ANG_200MS_HAR_V_113th_b | Phase B 113rd Voltage Angle Harmonics | float | 2 | R
0x2EFE | 0x2EFF | 12030 | 12031 | ANG_200MS_HAR_V_113th_c | Phase C 113rd Voltage Angle Harmonics | float | 2 | R
0x2F00 | 0x2F01 | 12032 | 12033 | ANG_200MS_HAR_I_113th_a | Phase A 113rd Current Angle Harmonics | float | 2 | R
0x2F02 | 0x2F03 | 12034 | 12035 | ANG_200MS_HAR_I_113th_b | Phase B 113rd Current Angle Harmonics | float | 2 | R
0x2F04 | 0x2F05 | 12036 | 12037 | ANG_200MS_HAR_I_113th_c | Phase C 113rd Current Angle Harmonics | float | 2 | R
0x2F06 | 0x2F07 | 12038 | 12039 | ANG_200MS_HAR_I_113th_n | Phase N 113rd Current Angle Harmonics | float | 2 | R
0x2F08 | 0x2F09 | 12040 | 12041 | ANG_200MS_HAR_V_114th_a | Phase A 114th Voltage Angle Harmonics | float | 2 | R
0x2F0A | 0x2F0B | 12042 | 12043 | ANG_200MS_HAR_V_114th_b | Phase B 114th Voltage Angle Harmonics | float | 2 | R
0x2F0C | 0x2F0D | 12044 | 12045 | ANG_200MS_HAR_V_114th_c | Phase C 114th Voltage Angle Harmonics | float | 2 | R
0x2F0E | 0x2F0F | 12046 | 12047 | ANG_200MS_HAR_I_114th_a | Phase A 114th Current Angle Harmonics | float | 2 | R
0x2F10 | 0x2F11 | 12048 | 12049 | ANG_200MS_HAR_I_114th_b | Phase B 114th Current Angle Harmonics | float | 2 | R
0x2F12 | 0x2F13 | 12050 | 12051 | ANG_200MS_HAR_I_114th_c | Phase C 114th Current Angle Harmonics | float | 2 | R
0x2F14 | 0x2F15 | 12052 | 12053 | ANG_200MS_HAR_I_114th_n | Phase N 114th Current Angle Harmonics | float | 2 | R
0x2F16 | 0x2F17 | 12054 | 12055 | ANG_200MS_HAR_V_115th_a | Phase A 115th Voltage Angle Harmonics | float | 2 | R
0x2F18 | 0x2F19 | 12056 | 12057 | ANG_200MS_HAR_V_115th_b | Phase B 115th Voltage Angle Harmonics | float | 2 | R
0x2F1A | 0x2F1B | 12058 | 12059 | ANG_200MS_HAR_V_115th_c | Phase C 115th Voltage Angle Harmonics | float | 2 | R
0x2F1C | 0x2F1D | 12060 | 12061 | ANG_200MS_HAR_I_115th_a | Phase A 115th Current Angle Harmonics | float | 2 | R
0x2F1E | 0x2F1F | 12062 | 12063 | ANG_200MS_HAR_I_115th_b | Phase B 115th Current Angle Harmonics | float | 2 | R
0x2F20 | 0x2F21 | 12064 | 12065 | ANG_200MS_HAR_I_115th_c | Phase C 115th Current Angle Harmonics | float | 2 | R
0x2F22 | 0x2F23 | 12066 | 12067 | ANG_200MS_HAR_I_115th_n | Phase N 115th Current Angle Harmonics | float | 2 | R
0x2F24 | 0x2F25 | 12068 | 12069 | ANG_200MS_HAR_V_116th_a | Phase A 116th Voltage Angle Harmonics | float | 2 | R
0x2F26 | 0x2F27 | 12070 | 12071 | ANG_200MS_HAR_V_116th_b | Phase B 116th Voltage Angle Harmonics | float | 2 | R
0x2F28 | 0x2F29 | 12072 | 12073 | ANG_200MS_HAR_V_116th_c | Phase C 116th Voltage Angle Harmonics | float | 2 | R
0x2F2A | 0x2F2B | 12074 | 12075 | ANG_200MS_HAR_I_116th_a | Phase A 116th Current Angle Harmonics | float | 2 | R
0x2F2C | 0x2F2D | 12076 | 12077 | ANG_200MS_HAR_I_116th_b | Phase B 116th Current Angle Harmonics | float | 2 | R
0x2F2E | 0x2F2F | 12078 | 12079 | ANG_200MS_HAR_I_116th_c | Phase C 116th Current Angle Harmonics | float | 2 | R
0x2F30 | 0x2F31 | 12080 | 12081 | ANG_200MS_HAR_I_116th_n | Phase N 116th Current Angle Harmonics | float | 2 | R
0x2F32 | 0x2F33 | 12082 | 12083 | ANG_200MS_HAR_V_117th_a | Phase A 117th Voltage Angle Harmonics | float | 2 | R
0x2F34 | 0x2F35 | 12084 | 12085 | ANG_200MS_HAR_V_117th_b | Phase B 117th Voltage Angle Harmonics | float | 2 | R
0x2F36 | 0x2F37 | 12086 | 12087 | ANG_200MS_HAR_V_117th_c | Phase C 117th Voltage Angle Harmonics | float | 2 | R
0x2F38 | 0x2F39 | 12088 | 12089 | ANG_200MS_HAR_I_117th_a | Phase A 117th Current Angle Harmonics | float | 2 | R
0x2F3A | 0x2F3B | 12090 | 12091 | ANG_200MS_HAR_I_117th_b | Phase B 117th Current Angle Harmonics | float | 2 | R
0x2F3C | 0x2F3D | 12092 | 12093 | ANG_200MS_HAR_I_117th_c | Phase C 117th Current Angle Harmonics | float | 2 | R
0x2F3E | 0x2F3F | 12094 | 12095 | ANG_200MS_HAR_I_117th_n | Phase N 117th Current Angle Harmonics | float | 2 | R
0x2F40 | 0x2F41 | 12096 | 12097 | ANG_200MS_HAR_V_118th_a | Phase A 118th Voltage Angle Harmonics | float | 2 | R
0x2F42 | 0x2F43 | 12098 | 12099 | ANG_200MS_HAR_V_118th_b | Phase B 118th Voltage Angle Harmonics | float | 2 | R
0x2F44 | 0x2F45 | 12100 | 12101 | ANG_200MS_HAR_V_118th_c | Phase C 118th Voltage Angle Harmonics | float | 2 | R
0x2F46 | 0x2F47 | 12102 | 12103 | ANG_200MS_HAR_I_118th_a | Phase A 118th Current Angle Harmonics | float | 2 | R
0x2F48 | 0x2F49 | 12104 | 12105 | ANG_200MS_HAR_I_118th_b | Phase B 118th Current Angle Harmonics | float | 2 | R
0x2F4A | 0x2F4B | 12106 | 12107 | ANG_200MS_HAR_I_118th_c | Phase C 118th Current Angle Harmonics | float | 2 | R
0x2F4C | 0x2F4D | 12108 | 12109 | ANG_200MS_HAR_I_118th_n | Phase N 118th Current Angle Harmonics | float | 2 | R
0x2F4E | 0x2F4F | 12110 | 12111 | ANG_200MS_HAR_V_119th_a | Phase A 119th Voltage Angle Harmonics | float | 2 | R
0x2F50 | 0x2F51 | 12112 | 12113 | ANG_200MS_HAR_V_119th_b | Phase B 119th Voltage Angle Harmonics | float | 2 | R
0x2F52 | 0x2F53 | 12114 | 12115 | ANG_200MS_HAR_V_119th_c | Phase C 119th Voltage Angle Harmonics | float | 2 | R
0x2F54 | 0x2F55 | 12116 | 12117 | ANG_200MS_HAR_I_119th_a | Phase A 119th Current Angle Harmonics | float | 2 | R
0x2F56 | 0x2F57 | 12118 | 12119 | ANG_200MS_HAR_I_119th_b | Phase B 119th Current Angle Harmonics | float | 2 | R
0x2F58 | 0x2F59 | 12120 | 12121 | ANG_200MS_HAR_I_119th_c | Phase C 119th Current Angle Harmonics | float | 2 | R
0x2F5A | 0x2F5B | 12122 | 12123 | ANG_200MS_HAR_I_119th_n | Phase N 119th Current Angle Harmonics | float | 2 | R
0x2F5C | 0x2F5D | 12124 | 12125 | ANG_200MS_HAR_V_120th_a | Phase A 120th Voltage Angle Harmonics | float | 2 | R
0x2F5E | 0x2F5F | 12126 | 12127 | ANG_200MS_HAR_V_120th_b | Phase B 120th Voltage Angle Harmonics | float | 2 | R
0x2F60 | 0x2F61 | 12128 | 12129 | ANG_200MS_HAR_V_120th_c | Phase C 120th Voltage Angle Harmonics | float | 2 | R
0x2F62 | 0x2F63 | 12130 | 12131 | ANG_200MS_HAR_I_120th_a | Phase A 120th Current Angle Harmonics | float | 2 | R
0x2F64 | 0x2F65 | 12132 | 12133 | ANG_200MS_HAR_I_120th_b | Phase B 120th Current Angle Harmonics | float | 2 | R
0x2F66 | 0x2F67 | 12134 | 12135 | ANG_200MS_HAR_I_120th_c | Phase C 120th Current Angle Harmonics | float | 2 | R
0x2F68 | 0x2F69 | 12136 | 12137 | ANG_200MS_HAR_I_120th_n | Phase N 120th Current Angle Harmonics | float | 2 | R
0x2F6A | 0x2F6B | 12138 | 12139 | ANG_200MS_HAR_V_121th_a | Phase A 121st Voltage Angle Harmonics | float | 2 | R
0x2F6C | 0x2F6D | 12140 | 12141 | ANG_200MS_HAR_V_121th_b | Phase B 121st Voltage Angle Harmonics | float | 2 | R
0x2F6E | 0x2F6F | 12142 | 12143 | ANG_200MS_HAR_V_121th_c | Phase C 121st Voltage Angle Harmonics | float | 2 | R
0x2F70 | 0x2F71 | 12144 | 12145 | ANG_200MS_HAR_I_121th_a | Phase A 121st Current Angle Harmonics | float | 2 | R
0x2F72 | 0x2F73 | 12146 | 12147 | ANG_200MS_HAR_I_121th_b | Phase B 121st Current Angle Harmonics | float | 2 | R
0x2F74 | 0x2F75 | 12148 | 12149 | ANG_200MS_HAR_I_121th_c | Phase C 121st Current Angle Harmonics | float | 2 | R
0x2F76 | 0x2F77 | 12150 | 12151 | ANG_200MS_HAR_I_121th_n | Phase N 121st Current Angle Harmonics | float | 2 | R
0x2F78 | 0x2F79 | 12152 | 12153 | ANG_200MS_HAR_V_122th_a | Phase A 122nd Voltage Angle Harmonics | float | 2 | R
0x2F7A | 0x2F7B | 12154 | 12155 | ANG_200MS_HAR_V_122th_b | Phase B 122nd Voltage Angle Harmonics | float | 2 | R
0x2F7C | 0x2F7D | 12156 | 12157 | ANG_200MS_HAR_V_122th_c | Phase C 122nd Voltage Angle Harmonics | float | 2 | R
0x2F7E | 0x2F7F | 12158 | 12159 | ANG_200MS_HAR_I_122th_a | Phase A 122nd Current Angle Harmonics | float | 2 | R
0x2F80 | 0x2F81 | 12160 | 12161 | ANG_200MS_HAR_I_122th_b | Phase B 122nd Current Angle Harmonics | float | 2 | R
0x2F82 | 0x2F83 | 12162 | 12163 | ANG_200MS_HAR_I_122th_c | Phase C 122nd Current Angle Harmonics | float | 2 | R
0x2F84 | 0x2F85 | 12164 | 12165 | ANG_200MS_HAR_I_122th_n | Phase N 122nd Current Angle Harmonics | float | 2 | R
0x2F86 | 0x2F87 | 12166 | 12167 | ANG_200MS_HAR_V_123th_a | Phase A 123rd Voltage Angle Harmonics | float | 2 | R
0x2F88 | 0x2F89 | 12168 | 12169 | ANG_200MS_HAR_V_123th_b | Phase B 123rd Voltage Angle Harmonics | float | 2 | R
0x2F8A | 0x2F8B | 12170 | 12171 | ANG_200MS_HAR_V_123th_c | Phase C 123rd Voltage Angle Harmonics | float | 2 | R
0x2F8C | 0x2F8D | 12172 | 12173 | ANG_200MS_HAR_I_123th_a | Phase A 123rd Current Angle Harmonics | float | 2 | R
0x2F8E | 0x2F8F | 12174 | 12175 | ANG_200MS_HAR_I_123th_b | Phase B 123rd Current Angle Harmonics | float | 2 | R
0x2F90 | 0x2F91 | 12176 | 12177 | ANG_200MS_HAR_I_123th_c | Phase C 123rd Current Angle Harmonics | float | 2 | R
0x2F92 | 0x2F93 | 12178 | 12179 | ANG_200MS_HAR_I_123th_n | Phase N 123rd Current Angle Harmonics | float | 2 | R
0x2F94 | 0x2F95 | 12180 | 12181 | ANG_200MS_HAR_V_124th_a | Phase A 124th Voltage Angle Harmonics | float | 2 | R
0x2F96 | 0x2F97 | 12182 | 12183 | ANG_200MS_HAR_V_124th_b | Phase B 124th Voltage Angle Harmonics | float | 2 | R
0x2F98 | 0x2F99 | 12184 | 12185 | ANG_200MS_HAR_V_124th_c | Phase C 124th Voltage Angle Harmonics | float | 2 | R
0x2F9A | 0x2F9B | 12186 | 12187 | ANG_200MS_HAR_I_124th_a | Phase A 124th Current Angle Harmonics | float | 2 | R
0x2F9C | 0x2F9D | 12188 | 12189 | ANG_200MS_HAR_I_124th_b | Phase B 124th Current Angle Harmonics | float | 2 | R
0x2F9E | 0x2F9F | 12190 | 12191 | ANG_200MS_HAR_I_124th_c | Phase C 124th Current Angle Harmonics | float | 2 | R
0x2FA0 | 0x2FA1 | 12192 | 12193 | ANG_200MS_HAR_I_124th_n | Phase N 124th Current Angle Harmonics | float | 2 | R
0x2FA2 | 0x2FA3 | 12194 | 12195 | ANG_200MS_HAR_V_125th_a | Phase A 125th Voltage Angle Harmonics | float | 2 | R
0x2FA4 | 0x2FA5 | 12196 | 12197 | ANG_200MS_HAR_V_125th_b | Phase B 125th Voltage Angle Harmonics | float | 2 | R
0x2FA6 | 0x2FA7 | 12198 | 12199 | ANG_200MS_HAR_V_125th_c | Phase C 125th Voltage Angle Harmonics | float | 2 | R
0x2FA8 | 0x2FA9 | 12200 | 12201 | ANG_200MS_HAR_I_125th_a | Phase A 125th Current Angle Harmonics | float | 2 | R
0x2FAA | 0x2FAB | 12202 | 12203 | ANG_200MS_HAR_I_125th_b | Phase B 125th Current Angle Harmonics | float | 2 | R
0x2FAC | 0x2FAD | 12204 | 12205 | ANG_200MS_HAR_I_125th_c | Phase C 125th Current Angle Harmonics | float | 2 | R
0x2FAE | 0x2FAF | 12206 | 12207 | ANG_200MS_HAR_I_125th_n | Phase N 125th Current Angle Harmonics | float | 2 | R
0x2FB0 | 0x2FB1 | 12208 | 12209 | ANG_200MS_HAR_V_126th_a | Phase A 126th Voltage Angle Harmonics | float | 2 | R
0x2FB2 | 0x2FB3 | 12210 | 12211 | ANG_200MS_HAR_V_126th_b | Phase B 126th Voltage Angle Harmonics | float | 2 | R
0x2FB4 | 0x2FB5 | 12212 | 12213 | ANG_200MS_HAR_V_126th_c | Phase C 126th Voltage Angle Harmonics | float | 2 | R
0x2FB6 | 0x2FB7 | 12214 | 12215 | ANG_200MS_HAR_I_126th_a | Phase A 126th Current Angle Harmonics | float | 2 | R
0x2FB8 | 0x2FB9 | 12216 | 12217 | ANG_200MS_HAR_I_126th_b | Phase B 126th Current Angle Harmonics | float | 2 | R
0x2FBA | 0x2FBB | 12218 | 12219 | ANG_200MS_HAR_I_126th_c | Phase C 126th Current Angle Harmonics | float | 2 | R
0x2FBC | 0x2FBD | 12220 | 12221 | ANG_200MS_HAR_I_126th_n | Phase N 126th Current Angle Harmonics | float | 2 | R
0x2FBE | 0x2FBF | 12222 | 12223 | ANG_200MS_HAR_V_127th_a | Phase A 127th Voltage Angle Harmonics | float | 2 | R
0x2FC0 | 0x2FC1 | 12224 | 12225 | ANG_200MS_HAR_V_127th_b | Phase B 127th Voltage Angle Harmonics | float | 2 | R
0x2FC2 | 0x2FC3 | 12226 | 12227 | ANG_200MS_HAR_V_127th_c | Phase C 127th Voltage Angle Harmonics | float | 2 | R
0x2FC4 | 0x2FC5 | 12228 | 12229 | ANG_200MS_HAR_I_127th_a | Phase A 127th Current Angle Harmonics | float | 2 | R
0x2FC6 | 0x2FC7 | 12230 | 12231 | ANG_200MS_HAR_I_127th_b | Phase B 127th Current Angle Harmonics | float | 2 | R
0x2FC8 | 0x2FC9 | 12232 | 12233 | ANG_200MS_HAR_I_127th_c | Phase C 127th Current Angle Harmonics | float | 2 | R
0x2FCA | 0x2FCB | 12234 | 12235 | ANG_200MS_HAR_I_127th_n | Phase N 127th Current Angle Harmonics | float | 2 | R
0x2FCC | 0x2FCD | 12236 | 12237 | 200MS_MAINS_SIGNAL_V_a | Phase A Mains Signaling Voltage | float | 2 | R
0x2FCE | 0x2FCF | 12238 | 12239 | 200MS_MAINS_SIGNAL_V_b | Phase B Mains Signaling Voltage | float | 2 | R
0x2FD0 | 0x2FD1 | 12240 | 12241 | 200MS_MAINS_SIGNAL_V_c | Phase C Mains Signaling Voltage | float | 2 | R

## 10min Aggregation
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x4000 | 0x4003 | 16384 | 16387 | 10M_TIMESTAMP | Aggr 10min Param Update Time Stamp | double | 4 | R
0x4004 | 0x4005 | 16388 | 16389 | 10M_FLAG | Aggr 10min Param Valid Flag | bool | 2 | R
0x4006 | 0x4007 | 16390 | 16391 | 10M_EVENT_FLAG | Aggr 10min Param Event Flag | uint32 | 2 | R
0x4008 | 0x4009 | 16392 | 16393 | 10M_Freq_Hz | Aggr 10min System Frequency | float | 2 | R
0x400A | 0x400B | 16394 | 16395 | 10M_VLN_a_V | Aggr 10min Phase A Line-to-Neutral Voltage | float | 2 | R
0x400C | 0x400D | 16396 | 16397 | 10M_VLN_b_V | Aggr 10min Phase B Line-to-Neutral Voltage | float | 2 | R
0x400E | 0x400F | 16398 | 16399 | 10M_VLN_c_V | Aggr 10min Phase C Line-to-Neutral Voltage | float | 2 | R
0x4010 | 0x4011 | 16400 | 16401 | 10M_VLN_avg_V | Aggr 10min Average Line-to-Neutral Voltage | float | 2 | R
0x4012 | 0x4013 | 16402 | 16403 | 10M_VLL_ab_V | Aggr 10min Phase AB Line-to-Line Voltage | float | 2 | R
0x4014 | 0x4015 | 16404 | 16405 | 10M_VLL_bc_V | Aggr 10min Phase BC Line-to-Line Voltage | float | 2 | R
0x4016 | 0x4017 | 16406 | 16407 | 10M_VLL_ca_V | Aggr 10min Phase CA Line-to-Line Voltage | float | 2 | R
0x4018 | 0x4019 | 16408 | 16409 | 10M_VLL_avg_V | Aggr 10min Average Line-to-Line Voltage | float | 2 | R
0x401A | 0x401B | 16410 | 16411 | 10M_I_a_A | Aggr 10min Phase A Current | float | 2 | R
0x401C | 0x401D | 16412 | 16413 | 10M_I_b_A | Aggr 10min Phase B Current | float | 2 | R
0x401E | 0x401F | 16414 | 16415 | 10M_I_c_A | Aggr 10min Phase C Current | float | 2 | R
0x4020 | 0x4021 | 16416 | 16417 | 10M_I_n_A | Aggr 10min Phase N Current | float | 2 | R
0x4022 | 0x4023 | 16418 | 16419 | 10M_I_avg_A | Aggr 10min Average Current | float | 2 | R
0x4024 | 0x4025 | 16420 | 16421 | 10M_P_a_kW | Aggr 10min Phase A Active Power | float | 2 | R
0x4026 | 0x4027 | 16422 | 16423 | 10M_P_b_kW | Aggr 10min Phase B Active Power | float | 2 | R
0x4028 | 0x4029 | 16424 | 16425 | 10M_P_c_kW | Aggr 10min Phase C Active Power | float | 2 | R
0x402A | 0x402B | 16426 | 16427 | 10M_P_kW | Aggr 10min System Active Power | float | 2 | R
0x402C | 0x402D | 16428 | 16429 | 10M_Q_a_kvar | Aggr 10min Phase A Reactive Power | float | 2 | R
0x402E | 0x402F | 16430 | 16431 | 10M_Q_b_kvar | Aggr 10min Phase B Reactive Power | float | 2 | R
0x4030 | 0x4031 | 16432 | 16433 | 10M_Q_c_kvar | Aggr 10min Phase C Reactive Power | float | 2 | R
0x4032 | 0x4033 | 16434 | 16435 | 10M_Q_kvar | Aggr 10min System Reactive Power | float | 2 | R
0x4034 | 0x4035 | 16436 | 16437 | 10M_S_a_kVA | Aggr 10min Phase A Apparent Power | float | 2 | R
0x4036 | 0x4037 | 16438 | 16439 | 10M_S_b_kVA | Aggr 10min Phase B Apparent Power | float | 2 | R
0x4038 | 0x4039 | 16440 | 16441 | 10M_S_c_kVA | Aggr 10min Phase C Apparent Power | float | 2 | R
0x403A | 0x403B | 16442 | 16443 | 10M_S_kVA | Aggr 10min System Apparent Power | float | 2 | R
0x403C | 0x403D | 16444 | 16445 | 10M_LC_a | Aggr 10min Phase A Load Nature | float | 2 | R
0x403E | 0x403F | 16446 | 16447 | 10M_LC_b | Aggr 10min Phase B Load Nature | float | 2 | R
0x4040 | 0x4041 | 16448 | 16449 | 10M_LC_c | Aggr 10min Phase C Load Nature | float | 2 | R
0x4042 | 0x4043 | 16450 | 16451 | 10M_LC | Aggr 10min System Load Nature | float | 2 | R
0x4044 | 0x4045 | 16452 | 16453 | 10M_PF_a | Aggr 10min Phase A Power Factor | float | 2 | R
0x4046 | 0x4047 | 16454 | 16455 | 10M_PF_b | Aggr 10min Phase B Power Factor | float | 2 | R
0x4048 | 0x4049 | 16456 | 16457 | 10M_PF_c | Aggr 10min Phase C Power Factor | float | 2 | R
0x404A | 0x404B | 16458 | 16459 | 10M_PF | Aggr 10min System Power Factor | float | 2 | R
0x404C | 0x404D | 16460 | 16461 | 10M_LEAD_PF_a | Aggr 10min Phase A Leading Power Factor | float | 2 | R
0x404E | 0x404F | 16462 | 16463 | 10M_LEAD_PF_b | Aggr 10min Phase B Leading Power Factor | float | 2 | R
0x4050 | 0x4051 | 16464 | 16465 | 10M_LEAD_PF_c | Aggr 10min Phase C Leading Power Factor | float | 2 | R
0x4052 | 0x4053 | 16466 | 16467 | 10M_LEAD_PF | Aggr 10min System Leading Power Factor | float | 2 | R
0x4054 | 0x4055 | 16468 | 16469 | 10M_LAG_PF_a | Aggr 10min Phase A Lagging Power Factor | float | 2 | R
0x4056 | 0x4057 | 16470 | 16471 | 10M_LAG_PF_b | Aggr 10min Phase B Lagging Power Factor | float | 2 | R
0x4058 | 0x4059 | 16472 | 16473 | 10M_LAG_PF_c | Aggr 10min Phase C Lagging Power Factor | float | 2 | R
0x405A | 0x405B | 16474 | 16475 | 10M_LAG_PF | Aggr 10min System Lagging Power Factor | float | 2 | R
0x405C | 0x405D | 16476 | 16477 | 10M_PA_VLN_a | Aggr 10min Phase A Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x405E | 0x405F | 16478 | 16479 | 10M_PA_VLN_b | Aggr 10min Phase B Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x4060 | 0x4061 | 16480 | 16481 | 10M_PA_VLN_c | Aggr 10min Phase C Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x4062 | 0x4063 | 16482 | 16483 | 10M_PA_VLL_ab | Aggr 10min Phase AB Line-to-Line Voltage Phase Angle | float | 2 | R
0x4064 | 0x4065 | 16484 | 16485 | 10M_PA_VLL_bc | Aggr 10min Phase BC Line-to-Line Voltage Phase Angle | float | 2 | R
0x4066 | 0x4067 | 16486 | 16487 | 10M_PA_VLL_ca | Aggr 10min Phase CA Line-to-Line Voltage Phase Angle | float | 2 | R
0x4068 | 0x4069 | 16488 | 16489 | 10M_PA_I_a | Aggr 10min Phase A Current Phase Angle | float | 2 | R
0x406A | 0x406B | 16490 | 16491 | 10M_PA_I_b | Aggr 10min Phase B Current Phase Angle | float | 2 | R
0x406C | 0x406D | 16492 | 16493 | 10M_PA_I_c | Aggr 10min Phase C Current Phase Angle | float | 2 | R
0x406E | 0x406F | 16494 | 16495 | MAG_10M_SEQ_POS_V_V | Aggr 10min Voltage Positive Sequence Magnitude | float | 2 | R
0x4070 | 0x4071 | 16496 | 16497 | MAG_10M_SEQ_ZERO_V_V | Aggr 10min Voltage Zero Sequence Magnitude | float | 2 | R
0x4072 | 0x4073 | 16498 | 16499 | MAG_10M_SEQ_NEG_V_V | Aggr 10min Voltage Negative Sequence Magnitude | float | 2 | R
0x4074 | 0x4075 | 16500 | 16501 | MAG_10M_SEQ_ZERO_RATIO_V_% | Aggr 10min Voltage Zero Sequence Ratio Magnitude | float | 2 | R
0x4076 | 0x4077 | 16502 | 16503 | MAG_10M_UNBL_V_% | Aggr 10min Voltage Unbalance Factor Magnitude | float | 2 | R
0x4078 | 0x4079 | 16504 | 16505 | MAG_10M_SEQ_POS_I_A | Aggr 10min Current Positive Sequence Magnitude | float | 2 | R
0x407A | 0x407B | 16506 | 16507 | MAG_10M_SEQ_ZERO_I_A | Aggr 10min Current Zero Sequence Magnitude | float | 2 | R
0x407C | 0x407D | 16508 | 16509 | MAG_10M_SEQ_NEG_I_A | Aggr 10min Current Negative Sequence Magnitude | float | 2 | R
0x407E | 0x407F | 16510 | 16511 | MAG_10M_SEQ_ZERO_RATIO_I_% | Aggr 10min Current Zero Sequence Ratio Magnitude | float | 2 | R
0x4080 | 0x4081 | 16512 | 16513 | MAG_10M_UNBL_I_% | Aggr 10min Current Unbalance Factor Magnitude | float | 2 | R
0x4082 | 0x4083 | 16514 | 16515 | ANG_10M_SEQ_POS_V | Aggr 10min Voltage Positive Sequence Angle | float | 2 | R
0x4084 | 0x4085 | 16516 | 16517 | ANG_10M_SEQ_ZERO_V | Aggr 10min Voltage Zero Sequence Angle | float | 2 | R
0x4086 | 0x4087 | 16518 | 16519 | ANG_10M_SEQ_NEG_V | Aggr 10min Voltage Negative Sequence Angle | float | 2 | R
0x4088 | 0x4089 | 16520 | 16521 | ANG_10M_SEQ_POS_I_A | Aggr 10min Current Positive Sequence Angle | float | 2 | R
0x408A | 0x408B | 16522 | 16523 | ANG_10M_SEQ_ZERO_I_A | Aggr 10min Current Zero Sequence Angle | float | 2 | R
0x408C | 0x408D | 16524 | 16525 | ANG_10M_SEQ_NEG_I_A | Aggr 10min Current Negative Sequence Angle | float | 2 | R
0x408E | 0x408F | 16526 | 16527 | 10M_THD_V_a_% | Aggr 10min Phase A Voltage THD | float | 2 | R
0x4090 | 0x4091 | 16528 | 16529 | 10M_THD_V_b_% | Aggr 10min Phase B Voltage THD | float | 2 | R
0x4092 | 0x4093 | 16530 | 16531 | 10M_THD_V_c_% | Aggr 10min Phase C Voltage THD | float | 2 | R
0x4094 | 0x4095 | 16532 | 16533 | 10M_OTHD_V_a_% | Aggr 10min Phase A Voltage THD Odd | float | 2 | R
0x4096 | 0x4097 | 16534 | 16535 | 10M_OTHD_V_b_% | Aggr 10min Phase B Voltage THD Odd | float | 2 | R
0x4098 | 0x4099 | 16536 | 16537 | 10M_OTHD_V_c_% | Aggr 10min Phase C Voltage THD Odd | float | 2 | R
0x409A | 0x409B | 16538 | 16539 | 10M_ETHD_V_a_% | Aggr 10min Phase A Voltage THD Even | float | 2 | R
0x409C | 0x409D | 16540 | 16541 | 10M_ETHD_V_b_% | Aggr 10min Phase B Voltage THD Even | float | 2 | R
0x409E | 0x409F | 16542 | 16543 | 10M_ETHD_V_c_% | Aggr 10min Phase C Voltage THD Even | float | 2 | R
0x40A0 | 0x40A1 | 16544 | 16545 | 10M_CF_V_a_% | Aggr 10min Phase A Voltage Crest Factor | float | 2 | R
0x40A2 | 0x40A3 | 16546 | 16547 | 10M_CF_V_b_% | Aggr 10min Phase B Voltage Crest Factor | float | 2 | R
0x40A4 | 0x40A5 | 16548 | 16549 | 10M_CF_V_c_% | Aggr 10min Phase C Voltage Crest Factor | float | 2 | R
0x40A6 | 0x40A7 | 16550 | 16551 | 10M_THD_I_a_% | Aggr 10min Phase A Current THD | float | 2 | R
0x40A8 | 0x40A9 | 16552 | 16553 | 10M_THD_I_b_% | Aggr 10min Phase B Current THD | float | 2 | R
0x40AA | 0x40AB | 16554 | 16555 | 10M_THD_I_c_% | Aggr 10min Phase C Current THD | float | 2 | R
0x40AC | 0x40AD | 16556 | 16557 | 10M_THD_I_n_% | Aggr 10min Phase N Current THD | float | 2 | R
0x40AE | 0x40AF | 16558 | 16559 | 10M_OTHD_I_a_% | Aggr 10min Phase A Current THD Odd | float | 2 | R
0x40B0 | 0x40B1 | 16560 | 16561 | 10M_OTHD_I_b_% | Aggr 10min Phase B Current THD Odd | float | 2 | R
0x40B2 | 0x40B3 | 16562 | 16563 | 10M_OTHD_I_c_% | Aggr 10min Phase C Current THD Odd | float | 2 | R
0x40B4 | 0x40B5 | 16564 | 16565 | 10M_OTHD_I_n_% | Aggr 10min Phase N Current THD Odd | float | 2 | R
0x40B6 | 0x40B7 | 16566 | 16567 | 10M_ETHD_I_a_% | Aggr 10min Phase A Current THD Even | float | 2 | R
0x40B8 | 0x40B9 | 16568 | 16569 | 10M_ETHD_I_b_% | Aggr 10min Phase B Current THD Even | float | 2 | R
0x40BA | 0x40BB | 16570 | 16571 | 10M_ETHD_I_c_% | Aggr 10min Phase C Current THD Even | float | 2 | R
0x40BC | 0x40BD | 16572 | 16573 | 10M_ETHD_I_n_% | Aggr 10min Phase N Current THD Even | float | 2 | R
0x40BE | 0x40BF | 16574 | 16575 | 10M_TDD_I_a_% | Aggr 10min Phase A Current TDD | float | 2 | R
0x40C0 | 0x40C1 | 16576 | 16577 | 10M_TDD_I_b_% | Aggr 10min Phase B Current TDD | float | 2 | R
0x40C2 | 0x40C3 | 16578 | 16579 | 10M_TDD_I_c_% | Aggr 10min Phase C Current TDD | float | 2 | R
0x40C4 | 0x40C5 | 16580 | 16581 | 10M_TDD_I_n_% | Aggr 10min Phase N Current TDD | float | 2 | R
0x40C6 | 0x40C7 | 16582 | 16583 | 10M_CF_I_a_% | Aggr 10min Phase A Current Crest-Factor | float | 2 | R
0x40C8 | 0x40C9 | 16584 | 16585 | 10M_CF_I_b_% | Aggr 10min Phase B Current Crest-Factor | float | 2 | R
0x40CA | 0x40CB | 16586 | 16587 | 10M_CF_I_c_% | Aggr 10min Phase C Current Crest-Factor | float | 2 | R
0x40CC | 0x40CD | 16588 | 16589 | 10M_CF_I_n_% | Aggr 10min Phase N Current Crest-Factor | float | 2 | R
0x40CE | 0x40CF | 16590 | 16591 | 10M_KF_I_a_% | Aggr 10min Phase A Current K-Factor | float | 2 | R
0x40D0 | 0x40D1 | 16592 | 16593 | 10M_KF_I_b_% | Aggr 10min Phase B Current K-Factor | float | 2 | R
0x40D2 | 0x40D3 | 16594 | 16595 | 10M_KF_I_c_% | Aggr 10min Phase C Current K-Factor | float | 2 | R
0x40D4 | 0x40D5 | 16596 | 16597 | 10M_KF_I_n_% | Aggr 10min Phase N Current K-Factor | float | 2 | R
0x40D6 | 0x40D7 | 16598 | 16599 | 10M_FLICK_V_a | Aggr 10min Phase A Voltage Flicker | float | 2 | R
0x40D8 | 0x40D9 | 16600 | 16601 | 10M_FLICK_V_b | Aggr 10min Phase B Voltage Flicker | float | 2 | R
0x40DA | 0x40DB | 16602 | 16603 | 10M_FLICK_V_c | Aggr 10min Phase C Voltage Flicker | float | 2 | R
0x40DC | 0x40DD | 16604 | 16605 | MAG_10M_HAR_V_1th_a_% | Aggr 10min Phase A 1st Voltage Magnitude Harmonics | float | 2 | R
0x40DE | 0x40DF | 16606 | 16607 | MAG_10M_HAR_V_1th_b_% | Aggr 10min Phase B 1st Voltage Magnitude Harmonics | float | 2 | R
0x40E0 | 0x40E1 | 16608 | 16609 | MAG_10M_HAR_V_1th_c_% | Aggr 10min Phase C 1st Voltage Magnitude Harmonics | float | 2 | R
0x40E2 | 0x40E3 | 16610 | 16611 | MAG_10M_HAR_I_1th_a_% | Aggr 10min Phase A 1st Current Magnitude Harmonics | float | 2 | R
0x40E4 | 0x40E5 | 16612 | 16613 | MAG_10M_HAR_I_1th_b_% | Aggr 10min Phase B 1st Current Magnitude Harmonics | float | 2 | R
0x40E6 | 0x40E7 | 16614 | 16615 | MAG_10M_HAR_I_1th_c_% | Aggr 10min Phase C 1st Current Magnitude Harmonics | float | 2 | R
0x40E8 | 0x40E9 | 16616 | 16617 | MAG_10M_HAR_I_1th_n_% | Aggr 10min Phase N 1st Current Magnitude Harmonics | float | 2 | R
0x40EA | 0x40EB | 16618 | 16619 | MAG_10M_HAR_V_2th_a_% | Aggr 10min Phase A 2nd Voltage Magnitude Harmonics | float | 2 | R
0x40EC | 0x40ED | 16620 | 16621 | MAG_10M_HAR_V_2th_b_% | Aggr 10min Phase B 2nd Voltage Magnitude Harmonics | float | 2 | R
0x40EE | 0x40EF | 16622 | 16623 | MAG_10M_HAR_V_2th_c_% | Aggr 10min Phase C 2nd Voltage Magnitude Harmonics | float | 2 | R
0x40F0 | 0x40F1 | 16624 | 16625 | MAG_10M_HAR_I_2th_a_% | Aggr 10min Phase A 2nd Current Magnitude Harmonics | float | 2 | R
0x40F2 | 0x40F3 | 16626 | 16627 | MAG_10M_HAR_I_2th_b_% | Aggr 10min Phase B 2nd Current Magnitude Harmonics | float | 2 | R
0x40F4 | 0x40F5 | 16628 | 16629 | MAG_10M_HAR_I_2th_c_% | Aggr 10min Phase C 2nd Current Magnitude Harmonics | float | 2 | R
0x40F6 | 0x40F7 | 16630 | 16631 | MAG_10M_HAR_I_2th_n_% | Aggr 10min Phase N 2nd Current Magnitude Harmonics | float | 2 | R
0x40F8 | 0x40F9 | 16632 | 16633 | MAG_10M_HAR_V_3th_a_% | Aggr 10min Phase A 3rd Voltage Magnitude Harmonics | float | 2 | R
0x40FA | 0x40FB | 16634 | 16635 | MAG_10M_HAR_V_3th_b_% | Aggr 10min Phase B 3rd Voltage Magnitude Harmonics | float | 2 | R
0x40FC | 0x40FD | 16636 | 16637 | MAG_10M_HAR_V_3th_c_% | Aggr 10min Phase C 3rd Voltage Magnitude Harmonics | float | 2 | R
0x40FE | 0x40FF | 16638 | 16639 | MAG_10M_HAR_I_3th_a_% | Aggr 10min Phase A 3rd Current Magnitude Harmonics | float | 2 | R
0x4100 | 0x4101 | 16640 | 16641 | MAG_10M_HAR_I_3th_b_% | Aggr 10min Phase B 3rd Current Magnitude Harmonics | float | 2 | R
0x4102 | 0x4103 | 16642 | 16643 | MAG_10M_HAR_I_3th_c_% | Aggr 10min Phase C 3rd Current Magnitude Harmonics | float | 2 | R
0x4104 | 0x4105 | 16644 | 16645 | MAG_10M_HAR_I_3th_n_% | Aggr 10min Phase N 3rd Current Magnitude Harmonics | float | 2 | R
0x4106 | 0x4107 | 16646 | 16647 | MAG_10M_HAR_V_4th_a_% | Aggr 10min Phase A 4th Voltage Magnitude Harmonics | float | 2 | R
0x4108 | 0x4109 | 16648 | 16649 | MAG_10M_HAR_V_4th_b_% | Aggr 10min Phase B 4th Voltage Magnitude Harmonics | float | 2 | R
0x410A | 0x410B | 16650 | 16651 | MAG_10M_HAR_V_4th_c_% | Aggr 10min Phase C 4th Voltage Magnitude Harmonics | float | 2 | R
0x410C | 0x410D | 16652 | 16653 | MAG_10M_HAR_I_4th_a_% | Aggr 10min Phase A 4th Current Magnitude Harmonics | float | 2 | R
0x410E | 0x410F | 16654 | 16655 | MAG_10M_HAR_I_4th_b_% | Aggr 10min Phase B 4th Current Magnitude Harmonics | float | 2 | R
0x4110 | 0x4111 | 16656 | 16657 | MAG_10M_HAR_I_4th_c_% | Aggr 10min Phase C 4th Current Magnitude Harmonics | float | 2 | R
0x4112 | 0x4113 | 16658 | 16659 | MAG_10M_HAR_I_4th_n_% | Aggr 10min Phase N 4th Current Magnitude Harmonics | float | 2 | R
0x4114 | 0x4115 | 16660 | 16661 | MAG_10M_HAR_V_5th_a_% | Aggr 10min Phase A 5th Voltage Magnitude Harmonics | float | 2 | R
0x4116 | 0x4117 | 16662 | 16663 | MAG_10M_HAR_V_5th_b_% | Aggr 10min Phase B 5th Voltage Magnitude Harmonics | float | 2 | R
0x4118 | 0x4119 | 16664 | 16665 | MAG_10M_HAR_V_5th_c_% | Aggr 10min Phase C 5th Voltage Magnitude Harmonics | float | 2 | R
0x411A | 0x411B | 16666 | 16667 | MAG_10M_HAR_I_5th_a_% | Aggr 10min Phase A 5th Current Magnitude Harmonics | float | 2 | R
0x411C | 0x411D | 16668 | 16669 | MAG_10M_HAR_I_5th_b_% | Aggr 10min Phase B 5th Current Magnitude Harmonics | float | 2 | R
0x411E | 0x411F | 16670 | 16671 | MAG_10M_HAR_I_5th_c_% | Aggr 10min Phase C 5th Current Magnitude Harmonics | float | 2 | R
0x4120 | 0x4121 | 16672 | 16673 | MAG_10M_HAR_I_5th_n_% | Aggr 10min Phase N 5th Current Magnitude Harmonics | float | 2 | R
0x4122 | 0x4123 | 16674 | 16675 | MAG_10M_HAR_V_6th_a_% | Aggr 10min Phase A 6th Voltage Magnitude Harmonics | float | 2 | R
0x4124 | 0x4125 | 16676 | 16677 | MAG_10M_HAR_V_6th_b_% | Aggr 10min Phase B 6th Voltage Magnitude Harmonics | float | 2 | R
0x4126 | 0x4127 | 16678 | 16679 | MAG_10M_HAR_V_6th_c_% | Aggr 10min Phase C 6th Voltage Magnitude Harmonics | float | 2 | R
0x4128 | 0x4129 | 16680 | 16681 | MAG_10M_HAR_I_6th_a_% | Aggr 10min Phase A 6th Current Magnitude Harmonics | float | 2 | R
0x412A | 0x412B | 16682 | 16683 | MAG_10M_HAR_I_6th_b_% | Aggr 10min Phase B 6th Current Magnitude Harmonics | float | 2 | R
0x412C | 0x412D | 16684 | 16685 | MAG_10M_HAR_I_6th_c_% | Aggr 10min Phase C 6th Current Magnitude Harmonics | float | 2 | R
0x412E | 0x412F | 16686 | 16687 | MAG_10M_HAR_I_6th_n_% | Aggr 10min Phase N 6th Current Magnitude Harmonics | float | 2 | R
0x4130 | 0x4131 | 16688 | 16689 | MAG_10M_HAR_V_7th_a_% | Aggr 10min Phase A 7th Voltage Magnitude Harmonics | float | 2 | R
0x4132 | 0x4133 | 16690 | 16691 | MAG_10M_HAR_V_7th_b_% | Aggr 10min Phase B 7th Voltage Magnitude Harmonics | float | 2 | R
0x4134 | 0x4135 | 16692 | 16693 | MAG_10M_HAR_V_7th_c_% | Aggr 10min Phase C 7th Voltage Magnitude Harmonics | float | 2 | R
0x4136 | 0x4137 | 16694 | 16695 | MAG_10M_HAR_I_7th_a_% | Aggr 10min Phase A 7th Current Magnitude Harmonics | float | 2 | R
0x4138 | 0x4139 | 16696 | 16697 | MAG_10M_HAR_I_7th_b_% | Aggr 10min Phase B 7th Current Magnitude Harmonics | float | 2 | R
0x413A | 0x413B | 16698 | 16699 | MAG_10M_HAR_I_7th_c_% | Aggr 10min Phase C 7th Current Magnitude Harmonics | float | 2 | R
0x413C | 0x413D | 16700 | 16701 | MAG_10M_HAR_I_7th_n_% | Aggr 10min Phase N 7th Current Magnitude Harmonics | float | 2 | R
0x413E | 0x413F | 16702 | 16703 | MAG_10M_HAR_V_8th_a_% | Aggr 10min Phase A 8th Voltage Magnitude Harmonics | float | 2 | R
0x4140 | 0x4141 | 16704 | 16705 | MAG_10M_HAR_V_8th_b_% | Aggr 10min Phase B 8th Voltage Magnitude Harmonics | float | 2 | R
0x4142 | 0x4143 | 16706 | 16707 | MAG_10M_HAR_V_8th_c_% | Aggr 10min Phase C 8th Voltage Magnitude Harmonics | float | 2 | R
0x4144 | 0x4145 | 16708 | 16709 | MAG_10M_HAR_I_8th_a_% | Aggr 10min Phase A 8th Current Magnitude Harmonics | float | 2 | R
0x4146 | 0x4147 | 16710 | 16711 | MAG_10M_HAR_I_8th_b_% | Aggr 10min Phase B 8th Current Magnitude Harmonics | float | 2 | R
0x4148 | 0x4149 | 16712 | 16713 | MAG_10M_HAR_I_8th_c_% | Aggr 10min Phase C 8th Current Magnitude Harmonics | float | 2 | R
0x414A | 0x414B | 16714 | 16715 | MAG_10M_HAR_I_8th_n_% | Aggr 10min Phase N 8th Current Magnitude Harmonics | float | 2 | R
0x414C | 0x414D | 16716 | 16717 | MAG_10M_HAR_V_9th_a_% | Aggr 10min Phase A 9th Voltage Magnitude Harmonics | float | 2 | R
0x414E | 0x414F | 16718 | 16719 | MAG_10M_HAR_V_9th_b_% | Aggr 10min Phase B 9th Voltage Magnitude Harmonics | float | 2 | R
0x4150 | 0x4151 | 16720 | 16721 | MAG_10M_HAR_V_9th_c_% | Aggr 10min Phase C 9th Voltage Magnitude Harmonics | float | 2 | R
0x4152 | 0x4153 | 16722 | 16723 | MAG_10M_HAR_I_9th_a_% | Aggr 10min Phase A 9th Current Magnitude Harmonics | float | 2 | R
0x4154 | 0x4155 | 16724 | 16725 | MAG_10M_HAR_I_9th_b_% | Aggr 10min Phase B 9th Current Magnitude Harmonics | float | 2 | R
0x4156 | 0x4157 | 16726 | 16727 | MAG_10M_HAR_I_9th_c_% | Aggr 10min Phase C 9th Current Magnitude Harmonics | float | 2 | R
0x4158 | 0x4159 | 16728 | 16729 | MAG_10M_HAR_I_9th_n_% | Aggr 10min Phase N 9th Current Magnitude Harmonics | float | 2 | R
0x415A | 0x415B | 16730 | 16731 | MAG_10M_HAR_V_10th_a_% | Aggr 10min Phase A 10th Voltage Magnitude Harmonics | float | 2 | R
0x415C | 0x415D | 16732 | 16733 | MAG_10M_HAR_V_10th_b_% | Aggr 10min Phase B 10th Voltage Magnitude Harmonics | float | 2 | R
0x415E | 0x415F | 16734 | 16735 | MAG_10M_HAR_V_10th_c_% | Aggr 10min Phase C 10th Voltage Magnitude Harmonics | float | 2 | R
0x4160 | 0x4161 | 16736 | 16737 | MAG_10M_HAR_I_10th_a_% | Aggr 10min Phase A 10th Current Magnitude Harmonics | float | 2 | R
0x4162 | 0x4163 | 16738 | 16739 | MAG_10M_HAR_I_10th_b_% | Aggr 10min Phase B 10th Current Magnitude Harmonics | float | 2 | R
0x4164 | 0x4165 | 16740 | 16741 | MAG_10M_HAR_I_10th_c_% | Aggr 10min Phase C 10th Current Magnitude Harmonics | float | 2 | R
0x4166 | 0x4167 | 16742 | 16743 | MAG_10M_HAR_I_10th_n_% | Aggr 10min Phase N 10th Current Magnitude Harmonics | float | 2 | R
0x4168 | 0x4169 | 16744 | 16745 | MAG_10M_HAR_V_11th_a_% | Aggr 10min Phase A 11st Voltage Magnitude Harmonics | float | 2 | R
0x416A | 0x416B | 16746 | 16747 | MAG_10M_HAR_V_11th_b_% | Aggr 10min Phase B 11st Voltage Magnitude Harmonics | float | 2 | R
0x416C | 0x416D | 16748 | 16749 | MAG_10M_HAR_V_11th_c_% | Aggr 10min Phase C 11st Voltage Magnitude Harmonics | float | 2 | R
0x416E | 0x416F | 16750 | 16751 | MAG_10M_HAR_I_11th_a_% | Aggr 10min Phase A 11st Current Magnitude Harmonics | float | 2 | R
0x4170 | 0x4171 | 16752 | 16753 | MAG_10M_HAR_I_11th_b_% | Aggr 10min Phase B 11st Current Magnitude Harmonics | float | 2 | R
0x4172 | 0x4173 | 16754 | 16755 | MAG_10M_HAR_I_11th_c_% | Aggr 10min Phase C 11st Current Magnitude Harmonics | float | 2 | R
0x4174 | 0x4175 | 16756 | 16757 | MAG_10M_HAR_I_11th_n_% | Aggr 10min Phase N 11st Current Magnitude Harmonics | float | 2 | R
0x4176 | 0x4177 | 16758 | 16759 | MAG_10M_HAR_V_12th_a_% | Aggr 10min Phase A 12nd Voltage Magnitude Harmonics | float | 2 | R
0x4178 | 0x4179 | 16760 | 16761 | MAG_10M_HAR_V_12th_b_% | Aggr 10min Phase B 12nd Voltage Magnitude Harmonics | float | 2 | R
0x417A | 0x417B | 16762 | 16763 | MAG_10M_HAR_V_12th_c_% | Aggr 10min Phase C 12nd Voltage Magnitude Harmonics | float | 2 | R
0x417C | 0x417D | 16764 | 16765 | MAG_10M_HAR_I_12th_a_% | Aggr 10min Phase A 12nd Current Magnitude Harmonics | float | 2 | R
0x417E | 0x417F | 16766 | 16767 | MAG_10M_HAR_I_12th_b_% | Aggr 10min Phase B 12nd Current Magnitude Harmonics | float | 2 | R
0x4180 | 0x4181 | 16768 | 16769 | MAG_10M_HAR_I_12th_c_% | Aggr 10min Phase C 12nd Current Magnitude Harmonics | float | 2 | R
0x4182 | 0x4183 | 16770 | 16771 | MAG_10M_HAR_I_12th_n_% | Aggr 10min Phase N 12nd Current Magnitude Harmonics | float | 2 | R
0x4184 | 0x4185 | 16772 | 16773 | MAG_10M_HAR_V_13th_a_% | Aggr 10min Phase A 13rd Voltage Magnitude Harmonics | float | 2 | R
0x4186 | 0x4187 | 16774 | 16775 | MAG_10M_HAR_V_13th_b_% | Aggr 10min Phase B 13rd Voltage Magnitude Harmonics | float | 2 | R
0x4188 | 0x4189 | 16776 | 16777 | MAG_10M_HAR_V_13th_c_% | Aggr 10min Phase C 13rd Voltage Magnitude Harmonics | float | 2 | R
0x418A | 0x418B | 16778 | 16779 | MAG_10M_HAR_I_13th_a_% | Aggr 10min Phase A 13rd Current Magnitude Harmonics | float | 2 | R
0x418C | 0x418D | 16780 | 16781 | MAG_10M_HAR_I_13th_b_% | Aggr 10min Phase B 13rd Current Magnitude Harmonics | float | 2 | R
0x418E | 0x418F | 16782 | 16783 | MAG_10M_HAR_I_13th_c_% | Aggr 10min Phase C 13rd Current Magnitude Harmonics | float | 2 | R
0x4190 | 0x4191 | 16784 | 16785 | MAG_10M_HAR_I_13th_n_% | Aggr 10min Phase N 13rd Current Magnitude Harmonics | float | 2 | R
0x4192 | 0x4193 | 16786 | 16787 | MAG_10M_HAR_V_14th_a_% | Aggr 10min Phase A 14th Voltage Magnitude Harmonics | float | 2 | R
0x4194 | 0x4195 | 16788 | 16789 | MAG_10M_HAR_V_14th_b_% | Aggr 10min Phase B 14th Voltage Magnitude Harmonics | float | 2 | R
0x4196 | 0x4197 | 16790 | 16791 | MAG_10M_HAR_V_14th_c_% | Aggr 10min Phase C 14th Voltage Magnitude Harmonics | float | 2 | R
0x4198 | 0x4199 | 16792 | 16793 | MAG_10M_HAR_I_14th_a_% | Aggr 10min Phase A 14th Current Magnitude Harmonics | float | 2 | R
0x419A | 0x419B | 16794 | 16795 | MAG_10M_HAR_I_14th_b_% | Aggr 10min Phase B 14th Current Magnitude Harmonics | float | 2 | R
0x419C | 0x419D | 16796 | 16797 | MAG_10M_HAR_I_14th_c_% | Aggr 10min Phase C 14th Current Magnitude Harmonics | float | 2 | R
0x419E | 0x419F | 16798 | 16799 | MAG_10M_HAR_I_14th_n_% | Aggr 10min Phase N 14th Current Magnitude Harmonics | float | 2 | R
0x41A0 | 0x41A1 | 16800 | 16801 | MAG_10M_HAR_V_15th_a_% | Aggr 10min Phase A 15th Voltage Magnitude Harmonics | float | 2 | R
0x41A2 | 0x41A3 | 16802 | 16803 | MAG_10M_HAR_V_15th_b_% | Aggr 10min Phase B 15th Voltage Magnitude Harmonics | float | 2 | R
0x41A4 | 0x41A5 | 16804 | 16805 | MAG_10M_HAR_V_15th_c_% | Aggr 10min Phase C 15th Voltage Magnitude Harmonics | float | 2 | R
0x41A6 | 0x41A7 | 16806 | 16807 | MAG_10M_HAR_I_15th_a_% | Aggr 10min Phase A 15th Current Magnitude Harmonics | float | 2 | R
0x41A8 | 0x41A9 | 16808 | 16809 | MAG_10M_HAR_I_15th_b_% | Aggr 10min Phase B 15th Current Magnitude Harmonics | float | 2 | R
0x41AA | 0x41AB | 16810 | 16811 | MAG_10M_HAR_I_15th_c_% | Aggr 10min Phase C 15th Current Magnitude Harmonics | float | 2 | R
0x41AC | 0x41AD | 16812 | 16813 | MAG_10M_HAR_I_15th_n_% | Aggr 10min Phase N 15th Current Magnitude Harmonics | float | 2 | R
0x41AE | 0x41AF | 16814 | 16815 | MAG_10M_HAR_V_16th_a_% | Aggr 10min Phase A 16th Voltage Magnitude Harmonics | float | 2 | R
0x41B0 | 0x41B1 | 16816 | 16817 | MAG_10M_HAR_V_16th_b_% | Aggr 10min Phase B 16th Voltage Magnitude Harmonics | float | 2 | R
0x41B2 | 0x41B3 | 16818 | 16819 | MAG_10M_HAR_V_16th_c_% | Aggr 10min Phase C 16th Voltage Magnitude Harmonics | float | 2 | R
0x41B4 | 0x41B5 | 16820 | 16821 | MAG_10M_HAR_I_16th_a_% | Aggr 10min Phase A 16th Current Magnitude Harmonics | float | 2 | R
0x41B6 | 0x41B7 | 16822 | 16823 | MAG_10M_HAR_I_16th_b_% | Aggr 10min Phase B 16th Current Magnitude Harmonics | float | 2 | R
0x41B8 | 0x41B9 | 16824 | 16825 | MAG_10M_HAR_I_16th_c_% | Aggr 10min Phase C 16th Current Magnitude Harmonics | float | 2 | R
0x41BA | 0x41BB | 16826 | 16827 | MAG_10M_HAR_I_16th_n_% | Aggr 10min Phase N 16th Current Magnitude Harmonics | float | 2 | R
0x41BC | 0x41BD | 16828 | 16829 | MAG_10M_HAR_V_17th_a_% | Aggr 10min Phase A 17th Voltage Magnitude Harmonics | float | 2 | R
0x41BE | 0x41BF | 16830 | 16831 | MAG_10M_HAR_V_17th_b_% | Aggr 10min Phase B 17th Voltage Magnitude Harmonics | float | 2 | R
0x41C0 | 0x41C1 | 16832 | 16833 | MAG_10M_HAR_V_17th_c_% | Aggr 10min Phase C 17th Voltage Magnitude Harmonics | float | 2 | R
0x41C2 | 0x41C3 | 16834 | 16835 | MAG_10M_HAR_I_17th_a_% | Aggr 10min Phase A 17th Current Magnitude Harmonics | float | 2 | R
0x41C4 | 0x41C5 | 16836 | 16837 | MAG_10M_HAR_I_17th_b_% | Aggr 10min Phase B 17th Current Magnitude Harmonics | float | 2 | R
0x41C6 | 0x41C7 | 16838 | 16839 | MAG_10M_HAR_I_17th_c_% | Aggr 10min Phase C 17th Current Magnitude Harmonics | float | 2 | R
0x41C8 | 0x41C9 | 16840 | 16841 | MAG_10M_HAR_I_17th_n_% | Aggr 10min Phase N 17th Current Magnitude Harmonics | float | 2 | R
0x41CA | 0x41CB | 16842 | 16843 | MAG_10M_HAR_V_18th_a_% | Aggr 10min Phase A 18th Voltage Magnitude Harmonics | float | 2 | R
0x41CC | 0x41CD | 16844 | 16845 | MAG_10M_HAR_V_18th_b_% | Aggr 10min Phase B 18th Voltage Magnitude Harmonics | float | 2 | R
0x41CE | 0x41CF | 16846 | 16847 | MAG_10M_HAR_V_18th_c_% | Aggr 10min Phase C 18th Voltage Magnitude Harmonics | float | 2 | R
0x41D0 | 0x41D1 | 16848 | 16849 | MAG_10M_HAR_I_18th_a_% | Aggr 10min Phase A 18th Current Magnitude Harmonics | float | 2 | R
0x41D2 | 0x41D3 | 16850 | 16851 | MAG_10M_HAR_I_18th_b_% | Aggr 10min Phase B 18th Current Magnitude Harmonics | float | 2 | R
0x41D4 | 0x41D5 | 16852 | 16853 | MAG_10M_HAR_I_18th_c_% | Aggr 10min Phase C 18th Current Magnitude Harmonics | float | 2 | R
0x41D6 | 0x41D7 | 16854 | 16855 | MAG_10M_HAR_I_18th_n_% | Aggr 10min Phase N 18th Current Magnitude Harmonics | float | 2 | R
0x41D8 | 0x41D9 | 16856 | 16857 | MAG_10M_HAR_V_19th_a_% | Aggr 10min Phase A 19th Voltage Magnitude Harmonics | float | 2 | R
0x41DA | 0x41DB | 16858 | 16859 | MAG_10M_HAR_V_19th_b_% | Aggr 10min Phase B 19th Voltage Magnitude Harmonics | float | 2 | R
0x41DC | 0x41DD | 16860 | 16861 | MAG_10M_HAR_V_19th_c_% | Aggr 10min Phase C 19th Voltage Magnitude Harmonics | float | 2 | R
0x41DE | 0x41DF | 16862 | 16863 | MAG_10M_HAR_I_19th_a_% | Aggr 10min Phase A 19th Current Magnitude Harmonics | float | 2 | R
0x41E0 | 0x41E1 | 16864 | 16865 | MAG_10M_HAR_I_19th_b_% | Aggr 10min Phase B 19th Current Magnitude Harmonics | float | 2 | R
0x41E2 | 0x41E3 | 16866 | 16867 | MAG_10M_HAR_I_19th_c_% | Aggr 10min Phase C 19th Current Magnitude Harmonics | float | 2 | R
0x41E4 | 0x41E5 | 16868 | 16869 | MAG_10M_HAR_I_19th_n_% | Aggr 10min Phase N 19th Current Magnitude Harmonics | float | 2 | R
0x41E6 | 0x41E7 | 16870 | 16871 | MAG_10M_HAR_V_20th_a_% | Aggr 10min Phase A 20th Voltage Magnitude Harmonics | float | 2 | R
0x41E8 | 0x41E9 | 16872 | 16873 | MAG_10M_HAR_V_20th_b_% | Aggr 10min Phase B 20th Voltage Magnitude Harmonics | float | 2 | R
0x41EA | 0x41EB | 16874 | 16875 | MAG_10M_HAR_V_20th_c_% | Aggr 10min Phase C 20th Voltage Magnitude Harmonics | float | 2 | R
0x41EC | 0x41ED | 16876 | 16877 | MAG_10M_HAR_I_20th_a_% | Aggr 10min Phase A 20th Current Magnitude Harmonics | float | 2 | R
0x41EE | 0x41EF | 16878 | 16879 | MAG_10M_HAR_I_20th_b_% | Aggr 10min Phase B 20th Current Magnitude Harmonics | float | 2 | R
0x41F0 | 0x41F1 | 16880 | 16881 | MAG_10M_HAR_I_20th_c_% | Aggr 10min Phase C 20th Current Magnitude Harmonics | float | 2 | R
0x41F2 | 0x41F3 | 16882 | 16883 | MAG_10M_HAR_I_20th_n_% | Aggr 10min Phase N 20th Current Magnitude Harmonics | float | 2 | R
0x41F4 | 0x41F5 | 16884 | 16885 | MAG_10M_HAR_V_21th_a_% | Aggr 10min Phase A 21st Voltage Magnitude Harmonics | float | 2 | R
0x41F6 | 0x41F7 | 16886 | 16887 | MAG_10M_HAR_V_21th_b_% | Aggr 10min Phase B 21st Voltage Magnitude Harmonics | float | 2 | R
0x41F8 | 0x41F9 | 16888 | 16889 | MAG_10M_HAR_V_21th_c_% | Aggr 10min Phase C 21st Voltage Magnitude Harmonics | float | 2 | R
0x41FA | 0x41FB | 16890 | 16891 | MAG_10M_HAR_I_21th_a_% | Aggr 10min Phase A 21st Current Magnitude Harmonics | float | 2 | R
0x41FC | 0x41FD | 16892 | 16893 | MAG_10M_HAR_I_21th_b_% | Aggr 10min Phase B 21st Current Magnitude Harmonics | float | 2 | R
0x41FE | 0x41FF | 16894 | 16895 | MAG_10M_HAR_I_21th_c_% | Aggr 10min Phase C 21st Current Magnitude Harmonics | float | 2 | R
0x4200 | 0x4201 | 16896 | 16897 | MAG_10M_HAR_I_21th_n_% | Aggr 10min Phase N 21st Current Magnitude Harmonics | float | 2 | R
0x4202 | 0x4203 | 16898 | 16899 | MAG_10M_HAR_V_22th_a_% | Aggr 10min Phase A 22nd Voltage Magnitude Harmonics | float | 2 | R
0x4204 | 0x4205 | 16900 | 16901 | MAG_10M_HAR_V_22th_b_% | Aggr 10min Phase B 22nd Voltage Magnitude Harmonics | float | 2 | R
0x4206 | 0x4207 | 16902 | 16903 | MAG_10M_HAR_V_22th_c_% | Aggr 10min Phase C 22nd Voltage Magnitude Harmonics | float | 2 | R
0x4208 | 0x4209 | 16904 | 16905 | MAG_10M_HAR_I_22th_a_% | Aggr 10min Phase A 22nd Current Magnitude Harmonics | float | 2 | R
0x420A | 0x420B | 16906 | 16907 | MAG_10M_HAR_I_22th_b_% | Aggr 10min Phase B 22nd Current Magnitude Harmonics | float | 2 | R
0x420C | 0x420D | 16908 | 16909 | MAG_10M_HAR_I_22th_c_% | Aggr 10min Phase C 22nd Current Magnitude Harmonics | float | 2 | R
0x420E | 0x420F | 16910 | 16911 | MAG_10M_HAR_I_22th_n_% | Aggr 10min Phase N 22nd Current Magnitude Harmonics | float | 2 | R
0x4210 | 0x4211 | 16912 | 16913 | MAG_10M_HAR_V_23th_a_% | Aggr 10min Phase A 23rd Voltage Magnitude Harmonics | float | 2 | R
0x4212 | 0x4213 | 16914 | 16915 | MAG_10M_HAR_V_23th_b_% | Aggr 10min Phase B 23rd Voltage Magnitude Harmonics | float | 2 | R
0x4214 | 0x4215 | 16916 | 16917 | MAG_10M_HAR_V_23th_c_% | Aggr 10min Phase C 23rd Voltage Magnitude Harmonics | float | 2 | R
0x4216 | 0x4217 | 16918 | 16919 | MAG_10M_HAR_I_23th_a_% | Aggr 10min Phase A 23rd Current Magnitude Harmonics | float | 2 | R
0x4218 | 0x4219 | 16920 | 16921 | MAG_10M_HAR_I_23th_b_% | Aggr 10min Phase B 23rd Current Magnitude Harmonics | float | 2 | R
0x421A | 0x421B | 16922 | 16923 | MAG_10M_HAR_I_23th_c_% | Aggr 10min Phase C 23rd Current Magnitude Harmonics | float | 2 | R
0x421C | 0x421D | 16924 | 16925 | MAG_10M_HAR_I_23th_n_% | Aggr 10min Phase N 23rd Current Magnitude Harmonics | float | 2 | R
0x421E | 0x421F | 16926 | 16927 | MAG_10M_HAR_V_24th_a_% | Aggr 10min Phase A 24th Voltage Magnitude Harmonics | float | 2 | R
0x4220 | 0x4221 | 16928 | 16929 | MAG_10M_HAR_V_24th_b_% | Aggr 10min Phase B 24th Voltage Magnitude Harmonics | float | 2 | R
0x4222 | 0x4223 | 16930 | 16931 | MAG_10M_HAR_V_24th_c_% | Aggr 10min Phase C 24th Voltage Magnitude Harmonics | float | 2 | R
0x4224 | 0x4225 | 16932 | 16933 | MAG_10M_HAR_I_24th_a_% | Aggr 10min Phase A 24th Current Magnitude Harmonics | float | 2 | R
0x4226 | 0x4227 | 16934 | 16935 | MAG_10M_HAR_I_24th_b_% | Aggr 10min Phase B 24th Current Magnitude Harmonics | float | 2 | R
0x4228 | 0x4229 | 16936 | 16937 | MAG_10M_HAR_I_24th_c_% | Aggr 10min Phase C 24th Current Magnitude Harmonics | float | 2 | R
0x422A | 0x422B | 16938 | 16939 | MAG_10M_HAR_I_24th_n_% | Aggr 10min Phase N 24th Current Magnitude Harmonics | float | 2 | R
0x422C | 0x422D | 16940 | 16941 | MAG_10M_HAR_V_25th_a_% | Aggr 10min Phase A 25th Voltage Magnitude Harmonics | float | 2 | R
0x422E | 0x422F | 16942 | 16943 | MAG_10M_HAR_V_25th_b_% | Aggr 10min Phase B 25th Voltage Magnitude Harmonics | float | 2 | R
0x4230 | 0x4231 | 16944 | 16945 | MAG_10M_HAR_V_25th_c_% | Aggr 10min Phase C 25th Voltage Magnitude Harmonics | float | 2 | R
0x4232 | 0x4233 | 16946 | 16947 | MAG_10M_HAR_I_25th_a_% | Aggr 10min Phase A 25th Current Magnitude Harmonics | float | 2 | R
0x4234 | 0x4235 | 16948 | 16949 | MAG_10M_HAR_I_25th_b_% | Aggr 10min Phase B 25th Current Magnitude Harmonics | float | 2 | R
0x4236 | 0x4237 | 16950 | 16951 | MAG_10M_HAR_I_25th_c_% | Aggr 10min Phase C 25th Current Magnitude Harmonics | float | 2 | R
0x4238 | 0x4239 | 16952 | 16953 | MAG_10M_HAR_I_25th_n_% | Aggr 10min Phase N 25th Current Magnitude Harmonics | float | 2 | R
0x423A | 0x423B | 16954 | 16955 | MAG_10M_HAR_V_26th_a_% | Aggr 10min Phase A 26th Voltage Magnitude Harmonics | float | 2 | R
0x423C | 0x423D | 16956 | 16957 | MAG_10M_HAR_V_26th_b_% | Aggr 10min Phase B 26th Voltage Magnitude Harmonics | float | 2 | R
0x423E | 0x423F | 16958 | 16959 | MAG_10M_HAR_V_26th_c_% | Aggr 10min Phase C 26th Voltage Magnitude Harmonics | float | 2 | R
0x4240 | 0x4241 | 16960 | 16961 | MAG_10M_HAR_I_26th_a_% | Aggr 10min Phase A 26th Current Magnitude Harmonics | float | 2 | R
0x4242 | 0x4243 | 16962 | 16963 | MAG_10M_HAR_I_26th_b_% | Aggr 10min Phase B 26th Current Magnitude Harmonics | float | 2 | R
0x4244 | 0x4245 | 16964 | 16965 | MAG_10M_HAR_I_26th_c_% | Aggr 10min Phase C 26th Current Magnitude Harmonics | float | 2 | R
0x4246 | 0x4247 | 16966 | 16967 | MAG_10M_HAR_I_26th_n_% | Aggr 10min Phase N 26th Current Magnitude Harmonics | float | 2 | R
0x4248 | 0x4249 | 16968 | 16969 | MAG_10M_HAR_V_27th_a_% | Aggr 10min Phase A 27th Voltage Magnitude Harmonics | float | 2 | R
0x424A | 0x424B | 16970 | 16971 | MAG_10M_HAR_V_27th_b_% | Aggr 10min Phase B 27th Voltage Magnitude Harmonics | float | 2 | R
0x424C | 0x424D | 16972 | 16973 | MAG_10M_HAR_V_27th_c_% | Aggr 10min Phase C 27th Voltage Magnitude Harmonics | float | 2 | R
0x424E | 0x424F | 16974 | 16975 | MAG_10M_HAR_I_27th_a_% | Aggr 10min Phase A 27th Current Magnitude Harmonics | float | 2 | R
0x4250 | 0x4251 | 16976 | 16977 | MAG_10M_HAR_I_27th_b_% | Aggr 10min Phase B 27th Current Magnitude Harmonics | float | 2 | R
0x4252 | 0x4253 | 16978 | 16979 | MAG_10M_HAR_I_27th_c_% | Aggr 10min Phase C 27th Current Magnitude Harmonics | float | 2 | R
0x4254 | 0x4255 | 16980 | 16981 | MAG_10M_HAR_I_27th_n_% | Aggr 10min Phase N 27th Current Magnitude Harmonics | float | 2 | R
0x4256 | 0x4257 | 16982 | 16983 | MAG_10M_HAR_V_28th_a_% | Aggr 10min Phase A 28th Voltage Magnitude Harmonics | float | 2 | R
0x4258 | 0x4259 | 16984 | 16985 | MAG_10M_HAR_V_28th_b_% | Aggr 10min Phase B 28th Voltage Magnitude Harmonics | float | 2 | R
0x425A | 0x425B | 16986 | 16987 | MAG_10M_HAR_V_28th_c_% | Aggr 10min Phase C 28th Voltage Magnitude Harmonics | float | 2 | R
0x425C | 0x425D | 16988 | 16989 | MAG_10M_HAR_I_28th_a_% | Aggr 10min Phase A 28th Current Magnitude Harmonics | float | 2 | R
0x425E | 0x425F | 16990 | 16991 | MAG_10M_HAR_I_28th_b_% | Aggr 10min Phase B 28th Current Magnitude Harmonics | float | 2 | R
0x4260 | 0x4261 | 16992 | 16993 | MAG_10M_HAR_I_28th_c_% | Aggr 10min Phase C 28th Current Magnitude Harmonics | float | 2 | R
0x4262 | 0x4263 | 16994 | 16995 | MAG_10M_HAR_I_28th_n_% | Aggr 10min Phase N 28th Current Magnitude Harmonics | float | 2 | R
0x4264 | 0x4265 | 16996 | 16997 | MAG_10M_HAR_V_29th_a_% | Aggr 10min Phase A 29th Voltage Magnitude Harmonics | float | 2 | R
0x4266 | 0x4267 | 16998 | 16999 | MAG_10M_HAR_V_29th_b_% | Aggr 10min Phase B 29th Voltage Magnitude Harmonics | float | 2 | R
0x4268 | 0x4269 | 17000 | 17001 | MAG_10M_HAR_V_29th_c_% | Aggr 10min Phase C 29th Voltage Magnitude Harmonics | float | 2 | R
0x426A | 0x426B | 17002 | 17003 | MAG_10M_HAR_I_29th_a_% | Aggr 10min Phase A 29th Current Magnitude Harmonics | float | 2 | R
0x426C | 0x426D | 17004 | 17005 | MAG_10M_HAR_I_29th_b_% | Aggr 10min Phase B 29th Current Magnitude Harmonics | float | 2 | R
0x426E | 0x426F | 17006 | 17007 | MAG_10M_HAR_I_29th_c_% | Aggr 10min Phase C 29th Current Magnitude Harmonics | float | 2 | R
0x4270 | 0x4271 | 17008 | 17009 | MAG_10M_HAR_I_29th_n_% | Aggr 10min Phase N 29th Current Magnitude Harmonics | float | 2 | R
0x4272 | 0x4273 | 17010 | 17011 | MAG_10M_HAR_V_30th_a_% | Aggr 10min Phase A 30th Voltage Magnitude Harmonics | float | 2 | R
0x4274 | 0x4275 | 17012 | 17013 | MAG_10M_HAR_V_30th_b_% | Aggr 10min Phase B 30th Voltage Magnitude Harmonics | float | 2 | R
0x4276 | 0x4277 | 17014 | 17015 | MAG_10M_HAR_V_30th_c_% | Aggr 10min Phase C 30th Voltage Magnitude Harmonics | float | 2 | R
0x4278 | 0x4279 | 17016 | 17017 | MAG_10M_HAR_I_30th_a_% | Aggr 10min Phase A 30th Current Magnitude Harmonics | float | 2 | R
0x427A | 0x427B | 17018 | 17019 | MAG_10M_HAR_I_30th_b_% | Aggr 10min Phase B 30th Current Magnitude Harmonics | float | 2 | R
0x427C | 0x427D | 17020 | 17021 | MAG_10M_HAR_I_30th_c_% | Aggr 10min Phase C 30th Current Magnitude Harmonics | float | 2 | R
0x427E | 0x427F | 17022 | 17023 | MAG_10M_HAR_I_30th_n_% | Aggr 10min Phase N 30th Current Magnitude Harmonics | float | 2 | R
0x4280 | 0x4281 | 17024 | 17025 | MAG_10M_HAR_V_31th_a_% | Aggr 10min Phase A 31st Voltage Magnitude Harmonics | float | 2 | R
0x4282 | 0x4283 | 17026 | 17027 | MAG_10M_HAR_V_31th_b_% | Aggr 10min Phase B 31st Voltage Magnitude Harmonics | float | 2 | R
0x4284 | 0x4285 | 17028 | 17029 | MAG_10M_HAR_V_31th_c_% | Aggr 10min Phase C 31st Voltage Magnitude Harmonics | float | 2 | R
0x4286 | 0x4287 | 17030 | 17031 | MAG_10M_HAR_I_31th_a_% | Aggr 10min Phase A 31st Current Magnitude Harmonics | float | 2 | R
0x4288 | 0x4289 | 17032 | 17033 | MAG_10M_HAR_I_31th_b_% | Aggr 10min Phase B 31st Current Magnitude Harmonics | float | 2 | R
0x428A | 0x428B | 17034 | 17035 | MAG_10M_HAR_I_31th_c_% | Aggr 10min Phase C 31st Current Magnitude Harmonics | float | 2 | R
0x428C | 0x428D | 17036 | 17037 | MAG_10M_HAR_I_31th_n_% | Aggr 10min Phase N 31st Current Magnitude Harmonics | float | 2 | R
0x428E | 0x428F | 17038 | 17039 | MAG_10M_HAR_V_32th_a_% | Aggr 10min Phase A 32nd Voltage Magnitude Harmonics | float | 2 | R
0x4290 | 0x4291 | 17040 | 17041 | MAG_10M_HAR_V_32th_b_% | Aggr 10min Phase B 32nd Voltage Magnitude Harmonics | float | 2 | R
0x4292 | 0x4293 | 17042 | 17043 | MAG_10M_HAR_V_32th_c_% | Aggr 10min Phase C 32nd Voltage Magnitude Harmonics | float | 2 | R
0x4294 | 0x4295 | 17044 | 17045 | MAG_10M_HAR_I_32th_a_% | Aggr 10min Phase A 32nd Current Magnitude Harmonics | float | 2 | R
0x4296 | 0x4297 | 17046 | 17047 | MAG_10M_HAR_I_32th_b_% | Aggr 10min Phase B 32nd Current Magnitude Harmonics | float | 2 | R
0x4298 | 0x4299 | 17048 | 17049 | MAG_10M_HAR_I_32th_c_% | Aggr 10min Phase C 32nd Current Magnitude Harmonics | float | 2 | R
0x429A | 0x429B | 17050 | 17051 | MAG_10M_HAR_I_32th_n_% | Aggr 10min Phase N 32nd Current Magnitude Harmonics | float | 2 | R
0x429C | 0x429D | 17052 | 17053 | MAG_10M_HAR_V_33th_a_% | Aggr 10min Phase A 33rd Voltage Magnitude Harmonics | float | 2 | R
0x429E | 0x429F | 17054 | 17055 | MAG_10M_HAR_V_33th_b_% | Aggr 10min Phase B 33rd Voltage Magnitude Harmonics | float | 2 | R
0x42A0 | 0x42A1 | 17056 | 17057 | MAG_10M_HAR_V_33th_c_% | Aggr 10min Phase C 33rd Voltage Magnitude Harmonics | float | 2 | R
0x42A2 | 0x42A3 | 17058 | 17059 | MAG_10M_HAR_I_33th_a_% | Aggr 10min Phase A 33rd Current Magnitude Harmonics | float | 2 | R
0x42A4 | 0x42A5 | 17060 | 17061 | MAG_10M_HAR_I_33th_b_% | Aggr 10min Phase B 33rd Current Magnitude Harmonics | float | 2 | R
0x42A6 | 0x42A7 | 17062 | 17063 | MAG_10M_HAR_I_33th_c_% | Aggr 10min Phase C 33rd Current Magnitude Harmonics | float | 2 | R
0x42A8 | 0x42A9 | 17064 | 17065 | MAG_10M_HAR_I_33th_n_% | Aggr 10min Phase N 33rd Current Magnitude Harmonics | float | 2 | R
0x42AA | 0x42AB | 17066 | 17067 | MAG_10M_HAR_V_34th_a_% | Aggr 10min Phase A 34th Voltage Magnitude Harmonics | float | 2 | R
0x42AC | 0x42AD | 17068 | 17069 | MAG_10M_HAR_V_34th_b_% | Aggr 10min Phase B 34th Voltage Magnitude Harmonics | float | 2 | R
0x42AE | 0x42AF | 17070 | 17071 | MAG_10M_HAR_V_34th_c_% | Aggr 10min Phase C 34th Voltage Magnitude Harmonics | float | 2 | R
0x42B0 | 0x42B1 | 17072 | 17073 | MAG_10M_HAR_I_34th_a_% | Aggr 10min Phase A 34th Current Magnitude Harmonics | float | 2 | R
0x42B2 | 0x42B3 | 17074 | 17075 | MAG_10M_HAR_I_34th_b_% | Aggr 10min Phase B 34th Current Magnitude Harmonics | float | 2 | R
0x42B4 | 0x42B5 | 17076 | 17077 | MAG_10M_HAR_I_34th_c_% | Aggr 10min Phase C 34th Current Magnitude Harmonics | float | 2 | R
0x42B6 | 0x42B7 | 17078 | 17079 | MAG_10M_HAR_I_34th_n_% | Aggr 10min Phase N 34th Current Magnitude Harmonics | float | 2 | R
0x42B8 | 0x42B9 | 17080 | 17081 | MAG_10M_HAR_V_35th_a_% | Aggr 10min Phase A 35th Voltage Magnitude Harmonics | float | 2 | R
0x42BA | 0x42BB | 17082 | 17083 | MAG_10M_HAR_V_35th_b_% | Aggr 10min Phase B 35th Voltage Magnitude Harmonics | float | 2 | R
0x42BC | 0x42BD | 17084 | 17085 | MAG_10M_HAR_V_35th_c_% | Aggr 10min Phase C 35th Voltage Magnitude Harmonics | float | 2 | R
0x42BE | 0x42BF | 17086 | 17087 | MAG_10M_HAR_I_35th_a_% | Aggr 10min Phase A 35th Current Magnitude Harmonics | float | 2 | R
0x42C0 | 0x42C1 | 17088 | 17089 | MAG_10M_HAR_I_35th_b_% | Aggr 10min Phase B 35th Current Magnitude Harmonics | float | 2 | R
0x42C2 | 0x42C3 | 17090 | 17091 | MAG_10M_HAR_I_35th_c_% | Aggr 10min Phase C 35th Current Magnitude Harmonics | float | 2 | R
0x42C4 | 0x42C5 | 17092 | 17093 | MAG_10M_HAR_I_35th_n_% | Aggr 10min Phase N 35th Current Magnitude Harmonics | float | 2 | R
0x42C6 | 0x42C7 | 17094 | 17095 | MAG_10M_HAR_V_36th_a_% | Aggr 10min Phase A 36th Voltage Magnitude Harmonics | float | 2 | R
0x42C8 | 0x42C9 | 17096 | 17097 | MAG_10M_HAR_V_36th_b_% | Aggr 10min Phase B 36th Voltage Magnitude Harmonics | float | 2 | R
0x42CA | 0x42CB | 17098 | 17099 | MAG_10M_HAR_V_36th_c_% | Aggr 10min Phase C 36th Voltage Magnitude Harmonics | float | 2 | R
0x42CC | 0x42CD | 17100 | 17101 | MAG_10M_HAR_I_36th_a_% | Aggr 10min Phase A 36th Current Magnitude Harmonics | float | 2 | R
0x42CE | 0x42CF | 17102 | 17103 | MAG_10M_HAR_I_36th_b_% | Aggr 10min Phase B 36th Current Magnitude Harmonics | float | 2 | R
0x42D0 | 0x42D1 | 17104 | 17105 | MAG_10M_HAR_I_36th_c_% | Aggr 10min Phase C 36th Current Magnitude Harmonics | float | 2 | R
0x42D2 | 0x42D3 | 17106 | 17107 | MAG_10M_HAR_I_36th_n_% | Aggr 10min Phase N 36th Current Magnitude Harmonics | float | 2 | R
0x42D4 | 0x42D5 | 17108 | 17109 | MAG_10M_HAR_V_37th_a_% | Aggr 10min Phase A 37th Voltage Magnitude Harmonics | float | 2 | R
0x42D6 | 0x42D7 | 17110 | 17111 | MAG_10M_HAR_V_37th_b_% | Aggr 10min Phase B 37th Voltage Magnitude Harmonics | float | 2 | R
0x42D8 | 0x42D9 | 17112 | 17113 | MAG_10M_HAR_V_37th_c_% | Aggr 10min Phase C 37th Voltage Magnitude Harmonics | float | 2 | R
0x42DA | 0x42DB | 17114 | 17115 | MAG_10M_HAR_I_37th_a_% | Aggr 10min Phase A 37th Current Magnitude Harmonics | float | 2 | R
0x42DC | 0x42DD | 17116 | 17117 | MAG_10M_HAR_I_37th_b_% | Aggr 10min Phase B 37th Current Magnitude Harmonics | float | 2 | R
0x42DE | 0x42DF | 17118 | 17119 | MAG_10M_HAR_I_37th_c_% | Aggr 10min Phase C 37th Current Magnitude Harmonics | float | 2 | R
0x42E0 | 0x42E1 | 17120 | 17121 | MAG_10M_HAR_I_37th_n_% | Aggr 10min Phase N 37th Current Magnitude Harmonics | float | 2 | R
0x42E2 | 0x42E3 | 17122 | 17123 | MAG_10M_HAR_V_38th_a_% | Aggr 10min Phase A 38th Voltage Magnitude Harmonics | float | 2 | R
0x42E4 | 0x42E5 | 17124 | 17125 | MAG_10M_HAR_V_38th_b_% | Aggr 10min Phase B 38th Voltage Magnitude Harmonics | float | 2 | R
0x42E6 | 0x42E7 | 17126 | 17127 | MAG_10M_HAR_V_38th_c_% | Aggr 10min Phase C 38th Voltage Magnitude Harmonics | float | 2 | R
0x42E8 | 0x42E9 | 17128 | 17129 | MAG_10M_HAR_I_38th_a_% | Aggr 10min Phase A 38th Current Magnitude Harmonics | float | 2 | R
0x42EA | 0x42EB | 17130 | 17131 | MAG_10M_HAR_I_38th_b_% | Aggr 10min Phase B 38th Current Magnitude Harmonics | float | 2 | R
0x42EC | 0x42ED | 17132 | 17133 | MAG_10M_HAR_I_38th_c_% | Aggr 10min Phase C 38th Current Magnitude Harmonics | float | 2 | R
0x42EE | 0x42EF | 17134 | 17135 | MAG_10M_HAR_I_38th_n_% | Aggr 10min Phase N 38th Current Magnitude Harmonics | float | 2 | R
0x42F0 | 0x42F1 | 17136 | 17137 | MAG_10M_HAR_V_39th_a_% | Aggr 10min Phase A 39th Voltage Magnitude Harmonics | float | 2 | R
0x42F2 | 0x42F3 | 17138 | 17139 | MAG_10M_HAR_V_39th_b_% | Aggr 10min Phase B 39th Voltage Magnitude Harmonics | float | 2 | R
0x42F4 | 0x42F5 | 17140 | 17141 | MAG_10M_HAR_V_39th_c_% | Aggr 10min Phase C 39th Voltage Magnitude Harmonics | float | 2 | R
0x42F6 | 0x42F7 | 17142 | 17143 | MAG_10M_HAR_I_39th_a_% | Aggr 10min Phase A 39th Current Magnitude Harmonics | float | 2 | R
0x42F8 | 0x42F9 | 17144 | 17145 | MAG_10M_HAR_I_39th_b_% | Aggr 10min Phase B 39th Current Magnitude Harmonics | float | 2 | R
0x42FA | 0x42FB | 17146 | 17147 | MAG_10M_HAR_I_39th_c_% | Aggr 10min Phase C 39th Current Magnitude Harmonics | float | 2 | R
0x42FC | 0x42FD | 17148 | 17149 | MAG_10M_HAR_I_39th_n_% | Aggr 10min Phase N 39th Current Magnitude Harmonics | float | 2 | R
0x42FE | 0x42FF | 17150 | 17151 | MAG_10M_HAR_V_40th_a_% | Aggr 10min Phase A 40th Voltage Magnitude Harmonics | float | 2 | R
0x4300 | 0x4301 | 17152 | 17153 | MAG_10M_HAR_V_40th_b_% | Aggr 10min Phase B 40th Voltage Magnitude Harmonics | float | 2 | R
0x4302 | 0x4303 | 17154 | 17155 | MAG_10M_HAR_V_40th_c_% | Aggr 10min Phase C 40th Voltage Magnitude Harmonics | float | 2 | R
0x4304 | 0x4305 | 17156 | 17157 | MAG_10M_HAR_I_40th_a_% | Aggr 10min Phase A 40th Current Magnitude Harmonics | float | 2 | R
0x4306 | 0x4307 | 17158 | 17159 | MAG_10M_HAR_I_40th_b_% | Aggr 10min Phase B 40th Current Magnitude Harmonics | float | 2 | R
0x4308 | 0x4309 | 17160 | 17161 | MAG_10M_HAR_I_40th_c_% | Aggr 10min Phase C 40th Current Magnitude Harmonics | float | 2 | R
0x430A | 0x430B | 17162 | 17163 | MAG_10M_HAR_I_40th_n_% | Aggr 10min Phase N 40th Current Magnitude Harmonics | float | 2 | R
0x430C | 0x430D | 17164 | 17165 | MAG_10M_HAR_V_41th_a_% | Aggr 10min Phase A 41st Voltage Magnitude Harmonics | float | 2 | R
0x430E | 0x430F | 17166 | 17167 | MAG_10M_HAR_V_41th_b_% | Aggr 10min Phase B 41st Voltage Magnitude Harmonics | float | 2 | R
0x4310 | 0x4311 | 17168 | 17169 | MAG_10M_HAR_V_41th_c_% | Aggr 10min Phase C 41st Voltage Magnitude Harmonics | float | 2 | R
0x4312 | 0x4313 | 17170 | 17171 | MAG_10M_HAR_I_41th_a_% | Aggr 10min Phase A 41st Current Magnitude Harmonics | float | 2 | R
0x4314 | 0x4315 | 17172 | 17173 | MAG_10M_HAR_I_41th_b_% | Aggr 10min Phase B 41st Current Magnitude Harmonics | float | 2 | R
0x4316 | 0x4317 | 17174 | 17175 | MAG_10M_HAR_I_41th_c_% | Aggr 10min Phase C 41st Current Magnitude Harmonics | float | 2 | R
0x4318 | 0x4319 | 17176 | 17177 | MAG_10M_HAR_I_41th_n_% | Aggr 10min Phase N 41st Current Magnitude Harmonics | float | 2 | R
0x431A | 0x431B | 17178 | 17179 | MAG_10M_HAR_V_42th_a_% | Aggr 10min Phase A 42nd Voltage Magnitude Harmonics | float | 2 | R
0x431C | 0x431D | 17180 | 17181 | MAG_10M_HAR_V_42th_b_% | Aggr 10min Phase B 42nd Voltage Magnitude Harmonics | float | 2 | R
0x431E | 0x431F | 17182 | 17183 | MAG_10M_HAR_V_42th_c_% | Aggr 10min Phase C 42nd Voltage Magnitude Harmonics | float | 2 | R
0x4320 | 0x4321 | 17184 | 17185 | MAG_10M_HAR_I_42th_a_% | Aggr 10min Phase A 42nd Current Magnitude Harmonics | float | 2 | R
0x4322 | 0x4323 | 17186 | 17187 | MAG_10M_HAR_I_42th_b_% | Aggr 10min Phase B 42nd Current Magnitude Harmonics | float | 2 | R
0x4324 | 0x4325 | 17188 | 17189 | MAG_10M_HAR_I_42th_c_% | Aggr 10min Phase C 42nd Current Magnitude Harmonics | float | 2 | R
0x4326 | 0x4327 | 17190 | 17191 | MAG_10M_HAR_I_42th_n_% | Aggr 10min Phase N 42nd Current Magnitude Harmonics | float | 2 | R
0x4328 | 0x4329 | 17192 | 17193 | MAG_10M_HAR_V_43th_a_% | Aggr 10min Phase A 43rd Voltage Magnitude Harmonics | float | 2 | R
0x432A | 0x432B | 17194 | 17195 | MAG_10M_HAR_V_43th_b_% | Aggr 10min Phase B 43rd Voltage Magnitude Harmonics | float | 2 | R
0x432C | 0x432D | 17196 | 17197 | MAG_10M_HAR_V_43th_c_% | Aggr 10min Phase C 43rd Voltage Magnitude Harmonics | float | 2 | R
0x432E | 0x432F | 17198 | 17199 | MAG_10M_HAR_I_43th_a_% | Aggr 10min Phase A 43rd Current Magnitude Harmonics | float | 2 | R
0x4330 | 0x4331 | 17200 | 17201 | MAG_10M_HAR_I_43th_b_% | Aggr 10min Phase B 43rd Current Magnitude Harmonics | float | 2 | R
0x4332 | 0x4333 | 17202 | 17203 | MAG_10M_HAR_I_43th_c_% | Aggr 10min Phase C 43rd Current Magnitude Harmonics | float | 2 | R
0x4334 | 0x4335 | 17204 | 17205 | MAG_10M_HAR_I_43th_n_% | Aggr 10min Phase N 43rd Current Magnitude Harmonics | float | 2 | R
0x4336 | 0x4337 | 17206 | 17207 | MAG_10M_HAR_V_44th_a_% | Aggr 10min Phase A 44th Voltage Magnitude Harmonics | float | 2 | R
0x4338 | 0x4339 | 17208 | 17209 | MAG_10M_HAR_V_44th_b_% | Aggr 10min Phase B 44th Voltage Magnitude Harmonics | float | 2 | R
0x433A | 0x433B | 17210 | 17211 | MAG_10M_HAR_V_44th_c_% | Aggr 10min Phase C 44th Voltage Magnitude Harmonics | float | 2 | R
0x433C | 0x433D | 17212 | 17213 | MAG_10M_HAR_I_44th_a_% | Aggr 10min Phase A 44th Current Magnitude Harmonics | float | 2 | R
0x433E | 0x433F | 17214 | 17215 | MAG_10M_HAR_I_44th_b_% | Aggr 10min Phase B 44th Current Magnitude Harmonics | float | 2 | R
0x4340 | 0x4341 | 17216 | 17217 | MAG_10M_HAR_I_44th_c_% | Aggr 10min Phase C 44th Current Magnitude Harmonics | float | 2 | R
0x4342 | 0x4343 | 17218 | 17219 | MAG_10M_HAR_I_44th_n_% | Aggr 10min Phase N 44th Current Magnitude Harmonics | float | 2 | R
0x4344 | 0x4345 | 17220 | 17221 | MAG_10M_HAR_V_45th_a_% | Aggr 10min Phase A 45th Voltage Magnitude Harmonics | float | 2 | R
0x4346 | 0x4347 | 17222 | 17223 | MAG_10M_HAR_V_45th_b_% | Aggr 10min Phase B 45th Voltage Magnitude Harmonics | float | 2 | R
0x4348 | 0x4349 | 17224 | 17225 | MAG_10M_HAR_V_45th_c_% | Aggr 10min Phase C 45th Voltage Magnitude Harmonics | float | 2 | R
0x434A | 0x434B | 17226 | 17227 | MAG_10M_HAR_I_45th_a_% | Aggr 10min Phase A 45th Current Magnitude Harmonics | float | 2 | R
0x434C | 0x434D | 17228 | 17229 | MAG_10M_HAR_I_45th_b_% | Aggr 10min Phase B 45th Current Magnitude Harmonics | float | 2 | R
0x434E | 0x434F | 17230 | 17231 | MAG_10M_HAR_I_45th_c_% | Aggr 10min Phase C 45th Current Magnitude Harmonics | float | 2 | R
0x4350 | 0x4351 | 17232 | 17233 | MAG_10M_HAR_I_45th_n_% | Aggr 10min Phase N 45th Current Magnitude Harmonics | float | 2 | R
0x4352 | 0x4353 | 17234 | 17235 | MAG_10M_HAR_V_46th_a_% | Aggr 10min Phase A 46th Voltage Magnitude Harmonics | float | 2 | R
0x4354 | 0x4355 | 17236 | 17237 | MAG_10M_HAR_V_46th_b_% | Aggr 10min Phase B 46th Voltage Magnitude Harmonics | float | 2 | R
0x4356 | 0x4357 | 17238 | 17239 | MAG_10M_HAR_V_46th_c_% | Aggr 10min Phase C 46th Voltage Magnitude Harmonics | float | 2 | R
0x4358 | 0x4359 | 17240 | 17241 | MAG_10M_HAR_I_46th_a_% | Aggr 10min Phase A 46th Current Magnitude Harmonics | float | 2 | R
0x435A | 0x435B | 17242 | 17243 | MAG_10M_HAR_I_46th_b_% | Aggr 10min Phase B 46th Current Magnitude Harmonics | float | 2 | R
0x435C | 0x435D | 17244 | 17245 | MAG_10M_HAR_I_46th_c_% | Aggr 10min Phase C 46th Current Magnitude Harmonics | float | 2 | R
0x435E | 0x435F | 17246 | 17247 | MAG_10M_HAR_I_46th_n_% | Aggr 10min Phase N 46th Current Magnitude Harmonics | float | 2 | R
0x4360 | 0x4361 | 17248 | 17249 | MAG_10M_HAR_V_47th_a_% | Aggr 10min Phase A 47th Voltage Magnitude Harmonics | float | 2 | R
0x4362 | 0x4363 | 17250 | 17251 | MAG_10M_HAR_V_47th_b_% | Aggr 10min Phase B 47th Voltage Magnitude Harmonics | float | 2 | R
0x4364 | 0x4365 | 17252 | 17253 | MAG_10M_HAR_V_47th_c_% | Aggr 10min Phase C 47th Voltage Magnitude Harmonics | float | 2 | R
0x4366 | 0x4367 | 17254 | 17255 | MAG_10M_HAR_I_47th_a_% | Aggr 10min Phase A 47th Current Magnitude Harmonics | float | 2 | R
0x4368 | 0x4369 | 17256 | 17257 | MAG_10M_HAR_I_47th_b_% | Aggr 10min Phase B 47th Current Magnitude Harmonics | float | 2 | R
0x436A | 0x436B | 17258 | 17259 | MAG_10M_HAR_I_47th_c_% | Aggr 10min Phase C 47th Current Magnitude Harmonics | float | 2 | R
0x436C | 0x436D | 17260 | 17261 | MAG_10M_HAR_I_47th_n_% | Aggr 10min Phase N 47th Current Magnitude Harmonics | float | 2 | R
0x436E | 0x436F | 17262 | 17263 | MAG_10M_HAR_V_48th_a_% | Aggr 10min Phase A 48th Voltage Magnitude Harmonics | float | 2 | R
0x4370 | 0x4371 | 17264 | 17265 | MAG_10M_HAR_V_48th_b_% | Aggr 10min Phase B 48th Voltage Magnitude Harmonics | float | 2 | R
0x4372 | 0x4373 | 17266 | 17267 | MAG_10M_HAR_V_48th_c_% | Aggr 10min Phase C 48th Voltage Magnitude Harmonics | float | 2 | R
0x4374 | 0x4375 | 17268 | 17269 | MAG_10M_HAR_I_48th_a_% | Aggr 10min Phase A 48th Current Magnitude Harmonics | float | 2 | R
0x4376 | 0x4377 | 17270 | 17271 | MAG_10M_HAR_I_48th_b_% | Aggr 10min Phase B 48th Current Magnitude Harmonics | float | 2 | R
0x4378 | 0x4379 | 17272 | 17273 | MAG_10M_HAR_I_48th_c_% | Aggr 10min Phase C 48th Current Magnitude Harmonics | float | 2 | R
0x437A | 0x437B | 17274 | 17275 | MAG_10M_HAR_I_48th_n_% | Aggr 10min Phase N 48th Current Magnitude Harmonics | float | 2 | R
0x437C | 0x437D | 17276 | 17277 | MAG_10M_HAR_V_49th_a_% | Aggr 10min Phase A 49th Voltage Magnitude Harmonics | float | 2 | R
0x437E | 0x437F | 17278 | 17279 | MAG_10M_HAR_V_49th_b_% | Aggr 10min Phase B 49th Voltage Magnitude Harmonics | float | 2 | R
0x4380 | 0x4381 | 17280 | 17281 | MAG_10M_HAR_V_49th_c_% | Aggr 10min Phase C 49th Voltage Magnitude Harmonics | float | 2 | R
0x4382 | 0x4383 | 17282 | 17283 | MAG_10M_HAR_I_49th_a_% | Aggr 10min Phase A 49th Current Magnitude Harmonics | float | 2 | R
0x4384 | 0x4385 | 17284 | 17285 | MAG_10M_HAR_I_49th_b_% | Aggr 10min Phase B 49th Current Magnitude Harmonics | float | 2 | R
0x4386 | 0x4387 | 17286 | 17287 | MAG_10M_HAR_I_49th_c_% | Aggr 10min Phase C 49th Current Magnitude Harmonics | float | 2 | R
0x4388 | 0x4389 | 17288 | 17289 | MAG_10M_HAR_I_49th_n_% | Aggr 10min Phase N 49th Current Magnitude Harmonics | float | 2 | R
0x438A | 0x438B | 17290 | 17291 | MAG_10M_HAR_V_50th_a_% | Aggr 10min Phase A 50th Voltage Magnitude Harmonics | float | 2 | R
0x438C | 0x438D | 17292 | 17293 | MAG_10M_HAR_V_50th_b_% | Aggr 10min Phase B 50th Voltage Magnitude Harmonics | float | 2 | R
0x438E | 0x438F | 17294 | 17295 | MAG_10M_HAR_V_50th_c_% | Aggr 10min Phase C 50th Voltage Magnitude Harmonics | float | 2 | R
0x4390 | 0x4391 | 17296 | 17297 | MAG_10M_HAR_I_50th_a_% | Aggr 10min Phase A 50th Current Magnitude Harmonics | float | 2 | R
0x4392 | 0x4393 | 17298 | 17299 | MAG_10M_HAR_I_50th_b_% | Aggr 10min Phase B 50th Current Magnitude Harmonics | float | 2 | R
0x4394 | 0x4395 | 17300 | 17301 | MAG_10M_HAR_I_50th_c_% | Aggr 10min Phase C 50th Current Magnitude Harmonics | float | 2 | R
0x4396 | 0x4397 | 17302 | 17303 | MAG_10M_HAR_I_50th_n_% | Aggr 10min Phase N 50th Current Magnitude Harmonics | float | 2 | R
0x4398 | 0x4399 | 17304 | 17305 | MAG_10M_HAR_V_51th_a_% | Aggr 10min Phase A 51st Voltage Magnitude Harmonics | float | 2 | R
0x439A | 0x439B | 17306 | 17307 | MAG_10M_HAR_V_51th_b_% | Aggr 10min Phase B 51st Voltage Magnitude Harmonics | float | 2 | R
0x439C | 0x439D | 17308 | 17309 | MAG_10M_HAR_V_51th_c_% | Aggr 10min Phase C 51st Voltage Magnitude Harmonics | float | 2 | R
0x439E | 0x439F | 17310 | 17311 | MAG_10M_HAR_I_51th_a_% | Aggr 10min Phase A 51st Current Magnitude Harmonics | float | 2 | R
0x43A0 | 0x43A1 | 17312 | 17313 | MAG_10M_HAR_I_51th_b_% | Aggr 10min Phase B 51st Current Magnitude Harmonics | float | 2 | R
0x43A2 | 0x43A3 | 17314 | 17315 | MAG_10M_HAR_I_51th_c_% | Aggr 10min Phase C 51st Current Magnitude Harmonics | float | 2 | R
0x43A4 | 0x43A5 | 17316 | 17317 | MAG_10M_HAR_I_51th_n_% | Aggr 10min Phase N 51st Current Magnitude Harmonics | float | 2 | R
0x43A6 | 0x43A7 | 17318 | 17319 | MAG_10M_HAR_V_52th_a_% | Aggr 10min Phase A 52nd Voltage Magnitude Harmonics | float | 2 | R
0x43A8 | 0x43A9 | 17320 | 17321 | MAG_10M_HAR_V_52th_b_% | Aggr 10min Phase B 52nd Voltage Magnitude Harmonics | float | 2 | R
0x43AA | 0x43AB | 17322 | 17323 | MAG_10M_HAR_V_52th_c_% | Aggr 10min Phase C 52nd Voltage Magnitude Harmonics | float | 2 | R
0x43AC | 0x43AD | 17324 | 17325 | MAG_10M_HAR_I_52th_a_% | Aggr 10min Phase A 52nd Current Magnitude Harmonics | float | 2 | R
0x43AE | 0x43AF | 17326 | 17327 | MAG_10M_HAR_I_52th_b_% | Aggr 10min Phase B 52nd Current Magnitude Harmonics | float | 2 | R
0x43B0 | 0x43B1 | 17328 | 17329 | MAG_10M_HAR_I_52th_c_% | Aggr 10min Phase C 52nd Current Magnitude Harmonics | float | 2 | R
0x43B2 | 0x43B3 | 17330 | 17331 | MAG_10M_HAR_I_52th_n_% | Aggr 10min Phase N 52nd Current Magnitude Harmonics | float | 2 | R
0x43B4 | 0x43B5 | 17332 | 17333 | MAG_10M_HAR_V_53th_a_% | Aggr 10min Phase A 53rd Voltage Magnitude Harmonics | float | 2 | R
0x43B6 | 0x43B7 | 17334 | 17335 | MAG_10M_HAR_V_53th_b_% | Aggr 10min Phase B 53rd Voltage Magnitude Harmonics | float | 2 | R
0x43B8 | 0x43B9 | 17336 | 17337 | MAG_10M_HAR_V_53th_c_% | Aggr 10min Phase C 53rd Voltage Magnitude Harmonics | float | 2 | R
0x43BA | 0x43BB | 17338 | 17339 | MAG_10M_HAR_I_53th_a_% | Aggr 10min Phase A 53rd Current Magnitude Harmonics | float | 2 | R
0x43BC | 0x43BD | 17340 | 17341 | MAG_10M_HAR_I_53th_b_% | Aggr 10min Phase B 53rd Current Magnitude Harmonics | float | 2 | R
0x43BE | 0x43BF | 17342 | 17343 | MAG_10M_HAR_I_53th_c_% | Aggr 10min Phase C 53rd Current Magnitude Harmonics | float | 2 | R
0x43C0 | 0x43C1 | 17344 | 17345 | MAG_10M_HAR_I_53th_n_% | Aggr 10min Phase N 53rd Current Magnitude Harmonics | float | 2 | R
0x43C2 | 0x43C3 | 17346 | 17347 | MAG_10M_HAR_V_54th_a_% | Aggr 10min Phase A 54th Voltage Magnitude Harmonics | float | 2 | R
0x43C4 | 0x43C5 | 17348 | 17349 | MAG_10M_HAR_V_54th_b_% | Aggr 10min Phase B 54th Voltage Magnitude Harmonics | float | 2 | R
0x43C6 | 0x43C7 | 17350 | 17351 | MAG_10M_HAR_V_54th_c_% | Aggr 10min Phase C 54th Voltage Magnitude Harmonics | float | 2 | R
0x43C8 | 0x43C9 | 17352 | 17353 | MAG_10M_HAR_I_54th_a_% | Aggr 10min Phase A 54th Current Magnitude Harmonics | float | 2 | R
0x43CA | 0x43CB | 17354 | 17355 | MAG_10M_HAR_I_54th_b_% | Aggr 10min Phase B 54th Current Magnitude Harmonics | float | 2 | R
0x43CC | 0x43CD | 17356 | 17357 | MAG_10M_HAR_I_54th_c_% | Aggr 10min Phase C 54th Current Magnitude Harmonics | float | 2 | R
0x43CE | 0x43CF | 17358 | 17359 | MAG_10M_HAR_I_54th_n_% | Aggr 10min Phase N 54th Current Magnitude Harmonics | float | 2 | R
0x43D0 | 0x43D1 | 17360 | 17361 | MAG_10M_HAR_V_55th_a_% | Aggr 10min Phase A 55th Voltage Magnitude Harmonics | float | 2 | R
0x43D2 | 0x43D3 | 17362 | 17363 | MAG_10M_HAR_V_55th_b_% | Aggr 10min Phase B 55th Voltage Magnitude Harmonics | float | 2 | R
0x43D4 | 0x43D5 | 17364 | 17365 | MAG_10M_HAR_V_55th_c_% | Aggr 10min Phase C 55th Voltage Magnitude Harmonics | float | 2 | R
0x43D6 | 0x43D7 | 17366 | 17367 | MAG_10M_HAR_I_55th_a_% | Aggr 10min Phase A 55th Current Magnitude Harmonics | float | 2 | R
0x43D8 | 0x43D9 | 17368 | 17369 | MAG_10M_HAR_I_55th_b_% | Aggr 10min Phase B 55th Current Magnitude Harmonics | float | 2 | R
0x43DA | 0x43DB | 17370 | 17371 | MAG_10M_HAR_I_55th_c_% | Aggr 10min Phase C 55th Current Magnitude Harmonics | float | 2 | R
0x43DC | 0x43DD | 17372 | 17373 | MAG_10M_HAR_I_55th_n_% | Aggr 10min Phase N 55th Current Magnitude Harmonics | float | 2 | R
0x43DE | 0x43DF | 17374 | 17375 | MAG_10M_HAR_V_56th_a_% | Aggr 10min Phase A 56th Voltage Magnitude Harmonics | float | 2 | R
0x43E0 | 0x43E1 | 17376 | 17377 | MAG_10M_HAR_V_56th_b_% | Aggr 10min Phase B 56th Voltage Magnitude Harmonics | float | 2 | R
0x43E2 | 0x43E3 | 17378 | 17379 | MAG_10M_HAR_V_56th_c_% | Aggr 10min Phase C 56th Voltage Magnitude Harmonics | float | 2 | R
0x43E4 | 0x43E5 | 17380 | 17381 | MAG_10M_HAR_I_56th_a_% | Aggr 10min Phase A 56th Current Magnitude Harmonics | float | 2 | R
0x43E6 | 0x43E7 | 17382 | 17383 | MAG_10M_HAR_I_56th_b_% | Aggr 10min Phase B 56th Current Magnitude Harmonics | float | 2 | R
0x43E8 | 0x43E9 | 17384 | 17385 | MAG_10M_HAR_I_56th_c_% | Aggr 10min Phase C 56th Current Magnitude Harmonics | float | 2 | R
0x43EA | 0x43EB | 17386 | 17387 | MAG_10M_HAR_I_56th_n_% | Aggr 10min Phase N 56th Current Magnitude Harmonics | float | 2 | R
0x43EC | 0x43ED | 17388 | 17389 | MAG_10M_HAR_V_57th_a_% | Aggr 10min Phase A 57th Voltage Magnitude Harmonics | float | 2 | R
0x43EE | 0x43EF | 17390 | 17391 | MAG_10M_HAR_V_57th_b_% | Aggr 10min Phase B 57th Voltage Magnitude Harmonics | float | 2 | R
0x43F0 | 0x43F1 | 17392 | 17393 | MAG_10M_HAR_V_57th_c_% | Aggr 10min Phase C 57th Voltage Magnitude Harmonics | float | 2 | R
0x43F2 | 0x43F3 | 17394 | 17395 | MAG_10M_HAR_I_57th_a_% | Aggr 10min Phase A 57th Current Magnitude Harmonics | float | 2 | R
0x43F4 | 0x43F5 | 17396 | 17397 | MAG_10M_HAR_I_57th_b_% | Aggr 10min Phase B 57th Current Magnitude Harmonics | float | 2 | R
0x43F6 | 0x43F7 | 17398 | 17399 | MAG_10M_HAR_I_57th_c_% | Aggr 10min Phase C 57th Current Magnitude Harmonics | float | 2 | R
0x43F8 | 0x43F9 | 17400 | 17401 | MAG_10M_HAR_I_57th_n_% | Aggr 10min Phase N 57th Current Magnitude Harmonics | float | 2 | R
0x43FA | 0x43FB | 17402 | 17403 | MAG_10M_HAR_V_58th_a_% | Aggr 10min Phase A 58th Voltage Magnitude Harmonics | float | 2 | R
0x43FC | 0x43FD | 17404 | 17405 | MAG_10M_HAR_V_58th_b_% | Aggr 10min Phase B 58th Voltage Magnitude Harmonics | float | 2 | R
0x43FE | 0x43FF | 17406 | 17407 | MAG_10M_HAR_V_58th_c_% | Aggr 10min Phase C 58th Voltage Magnitude Harmonics | float | 2 | R
0x4400 | 0x4401 | 17408 | 17409 | MAG_10M_HAR_I_58th_a_% | Aggr 10min Phase A 58th Current Magnitude Harmonics | float | 2 | R
0x4402 | 0x4403 | 17410 | 17411 | MAG_10M_HAR_I_58th_b_% | Aggr 10min Phase B 58th Current Magnitude Harmonics | float | 2 | R
0x4404 | 0x4405 | 17412 | 17413 | MAG_10M_HAR_I_58th_c_% | Aggr 10min Phase C 58th Current Magnitude Harmonics | float | 2 | R
0x4406 | 0x4407 | 17414 | 17415 | MAG_10M_HAR_I_58th_n_% | Aggr 10min Phase N 58th Current Magnitude Harmonics | float | 2 | R
0x4408 | 0x4409 | 17416 | 17417 | MAG_10M_HAR_V_59th_a_% | Aggr 10min Phase A 59th Voltage Magnitude Harmonics | float | 2 | R
0x440A | 0x440B | 17418 | 17419 | MAG_10M_HAR_V_59th_b_% | Aggr 10min Phase B 59th Voltage Magnitude Harmonics | float | 2 | R
0x440C | 0x440D | 17420 | 17421 | MAG_10M_HAR_V_59th_c_% | Aggr 10min Phase C 59th Voltage Magnitude Harmonics | float | 2 | R
0x440E | 0x440F | 17422 | 17423 | MAG_10M_HAR_I_59th_a_% | Aggr 10min Phase A 59th Current Magnitude Harmonics | float | 2 | R
0x4410 | 0x4411 | 17424 | 17425 | MAG_10M_HAR_I_59th_b_% | Aggr 10min Phase B 59th Current Magnitude Harmonics | float | 2 | R
0x4412 | 0x4413 | 17426 | 17427 | MAG_10M_HAR_I_59th_c_% | Aggr 10min Phase C 59th Current Magnitude Harmonics | float | 2 | R
0x4414 | 0x4415 | 17428 | 17429 | MAG_10M_HAR_I_59th_n_% | Aggr 10min Phase N 59th Current Magnitude Harmonics | float | 2 | R
0x4416 | 0x4417 | 17430 | 17431 | MAG_10M_HAR_V_60th_a_% | Aggr 10min Phase A 60th Voltage Magnitude Harmonics | float | 2 | R
0x4418 | 0x4419 | 17432 | 17433 | MAG_10M_HAR_V_60th_b_% | Aggr 10min Phase B 60th Voltage Magnitude Harmonics | float | 2 | R
0x441A | 0x441B | 17434 | 17435 | MAG_10M_HAR_V_60th_c_% | Aggr 10min Phase C 60th Voltage Magnitude Harmonics | float | 2 | R
0x441C | 0x441D | 17436 | 17437 | MAG_10M_HAR_I_60th_a_% | Aggr 10min Phase A 60th Current Magnitude Harmonics | float | 2 | R
0x441E | 0x441F | 17438 | 17439 | MAG_10M_HAR_I_60th_b_% | Aggr 10min Phase B 60th Current Magnitude Harmonics | float | 2 | R
0x4420 | 0x4421 | 17440 | 17441 | MAG_10M_HAR_I_60th_c_% | Aggr 10min Phase C 60th Current Magnitude Harmonics | float | 2 | R
0x4422 | 0x4423 | 17442 | 17443 | MAG_10M_HAR_I_60th_n_% | Aggr 10min Phase N 60th Current Magnitude Harmonics | float | 2 | R
0x4424 | 0x4425 | 17444 | 17445 | MAG_10M_HAR_V_61th_a_% | Aggr 10min Phase A 61st Voltage Magnitude Harmonics | float | 2 | R
0x4426 | 0x4427 | 17446 | 17447 | MAG_10M_HAR_V_61th_b_% | Aggr 10min Phase B 61st Voltage Magnitude Harmonics | float | 2 | R
0x4428 | 0x4429 | 17448 | 17449 | MAG_10M_HAR_V_61th_c_% | Aggr 10min Phase C 61st Voltage Magnitude Harmonics | float | 2 | R
0x442A | 0x442B | 17450 | 17451 | MAG_10M_HAR_I_61th_a_% | Aggr 10min Phase A 61st Current Magnitude Harmonics | float | 2 | R
0x442C | 0x442D | 17452 | 17453 | MAG_10M_HAR_I_61th_b_% | Aggr 10min Phase B 61st Current Magnitude Harmonics | float | 2 | R
0x442E | 0x442F | 17454 | 17455 | MAG_10M_HAR_I_61th_c_% | Aggr 10min Phase C 61st Current Magnitude Harmonics | float | 2 | R
0x4430 | 0x4431 | 17456 | 17457 | MAG_10M_HAR_I_61th_n_% | Aggr 10min Phase N 61st Current Magnitude Harmonics | float | 2 | R
0x4432 | 0x4433 | 17458 | 17459 | MAG_10M_HAR_V_62th_a_% | Aggr 10min Phase A 62nd Voltage Magnitude Harmonics | float | 2 | R
0x4434 | 0x4435 | 17460 | 17461 | MAG_10M_HAR_V_62th_b_% | Aggr 10min Phase B 62nd Voltage Magnitude Harmonics | float | 2 | R
0x4436 | 0x4437 | 17462 | 17463 | MAG_10M_HAR_V_62th_c_% | Aggr 10min Phase C 62nd Voltage Magnitude Harmonics | float | 2 | R
0x4438 | 0x4439 | 17464 | 17465 | MAG_10M_HAR_I_62th_a_% | Aggr 10min Phase A 62nd Current Magnitude Harmonics | float | 2 | R
0x443A | 0x443B | 17466 | 17467 | MAG_10M_HAR_I_62th_b_% | Aggr 10min Phase B 62nd Current Magnitude Harmonics | float | 2 | R
0x443C | 0x443D | 17468 | 17469 | MAG_10M_HAR_I_62th_c_% | Aggr 10min Phase C 62nd Current Magnitude Harmonics | float | 2 | R
0x443E | 0x443F | 17470 | 17471 | MAG_10M_HAR_I_62th_n_% | Aggr 10min Phase N 62nd Current Magnitude Harmonics | float | 2 | R
0x4440 | 0x4441 | 17472 | 17473 | MAG_10M_HAR_V_63th_a_% | Aggr 10min Phase A 63rd Voltage Magnitude Harmonics | float | 2 | R
0x4442 | 0x4443 | 17474 | 17475 | MAG_10M_HAR_V_63th_b_% | Aggr 10min Phase B 63rd Voltage Magnitude Harmonics | float | 2 | R
0x4444 | 0x4445 | 17476 | 17477 | MAG_10M_HAR_V_63th_c_% | Aggr 10min Phase C 63rd Voltage Magnitude Harmonics | float | 2 | R
0x4446 | 0x4447 | 17478 | 17479 | MAG_10M_HAR_I_63th_a_% | Aggr 10min Phase A 63rd Current Magnitude Harmonics | float | 2 | R
0x4448 | 0x4449 | 17480 | 17481 | MAG_10M_HAR_I_63th_b_% | Aggr 10min Phase B 63rd Current Magnitude Harmonics | float | 2 | R
0x444A | 0x444B | 17482 | 17483 | MAG_10M_HAR_I_63th_c_% | Aggr 10min Phase C 63rd Current Magnitude Harmonics | float | 2 | R
0x444C | 0x444D | 17484 | 17485 | MAG_10M_HAR_I_63th_n_% | Aggr 10min Phase N 63rd Current Magnitude Harmonics | float | 2 | R
0x444E | 0x444F | 17486 | 17487 | MAG_10M_HAR_V_64th_a_% | Aggr 10min Phase A 64th Voltage Magnitude Harmonics | float | 2 | R
0x4450 | 0x4451 | 17488 | 17489 | MAG_10M_HAR_V_64th_b_% | Aggr 10min Phase B 64th Voltage Magnitude Harmonics | float | 2 | R
0x4452 | 0x4453 | 17490 | 17491 | MAG_10M_HAR_V_64th_c_% | Aggr 10min Phase C 64th Voltage Magnitude Harmonics | float | 2 | R
0x4454 | 0x4455 | 17492 | 17493 | MAG_10M_HAR_I_64th_a_% | Aggr 10min Phase A 64th Current Magnitude Harmonics | float | 2 | R
0x4456 | 0x4457 | 17494 | 17495 | MAG_10M_HAR_I_64th_b_% | Aggr 10min Phase B 64th Current Magnitude Harmonics | float | 2 | R
0x4458 | 0x4459 | 17496 | 17497 | MAG_10M_HAR_I_64th_c_% | Aggr 10min Phase C 64th Current Magnitude Harmonics | float | 2 | R
0x445A | 0x445B | 17498 | 17499 | MAG_10M_HAR_I_64th_n_% | Aggr 10min Phase N 64th Current Magnitude Harmonics | float | 2 | R
0x445C | 0x445D | 17500 | 17501 | MAG_10M_HAR_V_65th_a_% | Aggr 10min Phase A 65th Voltage Magnitude Harmonics | float | 2 | R
0x445E | 0x445F | 17502 | 17503 | MAG_10M_HAR_V_65th_b_% | Aggr 10min Phase B 65th Voltage Magnitude Harmonics | float | 2 | R
0x4460 | 0x4461 | 17504 | 17505 | MAG_10M_HAR_V_65th_c_% | Aggr 10min Phase C 65th Voltage Magnitude Harmonics | float | 2 | R
0x4462 | 0x4463 | 17506 | 17507 | MAG_10M_HAR_I_65th_a_% | Aggr 10min Phase A 65th Current Magnitude Harmonics | float | 2 | R
0x4464 | 0x4465 | 17508 | 17509 | MAG_10M_HAR_I_65th_b_% | Aggr 10min Phase B 65th Current Magnitude Harmonics | float | 2 | R
0x4466 | 0x4467 | 17510 | 17511 | MAG_10M_HAR_I_65th_c_% | Aggr 10min Phase C 65th Current Magnitude Harmonics | float | 2 | R
0x4468 | 0x4469 | 17512 | 17513 | MAG_10M_HAR_I_65th_n_% | Aggr 10min Phase N 65th Current Magnitude Harmonics | float | 2 | R
0x446A | 0x446B | 17514 | 17515 | MAG_10M_HAR_V_66th_a_% | Aggr 10min Phase A 66th Voltage Magnitude Harmonics | float | 2 | R
0x446C | 0x446D | 17516 | 17517 | MAG_10M_HAR_V_66th_b_% | Aggr 10min Phase B 66th Voltage Magnitude Harmonics | float | 2 | R
0x446E | 0x446F | 17518 | 17519 | MAG_10M_HAR_V_66th_c_% | Aggr 10min Phase C 66th Voltage Magnitude Harmonics | float | 2 | R
0x4470 | 0x4471 | 17520 | 17521 | MAG_10M_HAR_I_66th_a_% | Aggr 10min Phase A 66th Current Magnitude Harmonics | float | 2 | R
0x4472 | 0x4473 | 17522 | 17523 | MAG_10M_HAR_I_66th_b_% | Aggr 10min Phase B 66th Current Magnitude Harmonics | float | 2 | R
0x4474 | 0x4475 | 17524 | 17525 | MAG_10M_HAR_I_66th_c_% | Aggr 10min Phase C 66th Current Magnitude Harmonics | float | 2 | R
0x4476 | 0x4477 | 17526 | 17527 | MAG_10M_HAR_I_66th_n_% | Aggr 10min Phase N 66th Current Magnitude Harmonics | float | 2 | R
0x4478 | 0x4479 | 17528 | 17529 | MAG_10M_HAR_V_67th_a_% | Aggr 10min Phase A 67th Voltage Magnitude Harmonics | float | 2 | R
0x447A | 0x447B | 17530 | 17531 | MAG_10M_HAR_V_67th_b_% | Aggr 10min Phase B 67th Voltage Magnitude Harmonics | float | 2 | R
0x447C | 0x447D | 17532 | 17533 | MAG_10M_HAR_V_67th_c_% | Aggr 10min Phase C 67th Voltage Magnitude Harmonics | float | 2 | R
0x447E | 0x447F | 17534 | 17535 | MAG_10M_HAR_I_67th_a_% | Aggr 10min Phase A 67th Current Magnitude Harmonics | float | 2 | R
0x4480 | 0x4481 | 17536 | 17537 | MAG_10M_HAR_I_67th_b_% | Aggr 10min Phase B 67th Current Magnitude Harmonics | float | 2 | R
0x4482 | 0x4483 | 17538 | 17539 | MAG_10M_HAR_I_67th_c_% | Aggr 10min Phase C 67th Current Magnitude Harmonics | float | 2 | R
0x4484 | 0x4485 | 17540 | 17541 | MAG_10M_HAR_I_67th_n_% | Aggr 10min Phase N 67th Current Magnitude Harmonics | float | 2 | R
0x4486 | 0x4487 | 17542 | 17543 | MAG_10M_HAR_V_68th_a_% | Aggr 10min Phase A 68th Voltage Magnitude Harmonics | float | 2 | R
0x4488 | 0x4489 | 17544 | 17545 | MAG_10M_HAR_V_68th_b_% | Aggr 10min Phase B 68th Voltage Magnitude Harmonics | float | 2 | R
0x448A | 0x448B | 17546 | 17547 | MAG_10M_HAR_V_68th_c_% | Aggr 10min Phase C 68th Voltage Magnitude Harmonics | float | 2 | R
0x448C | 0x448D | 17548 | 17549 | MAG_10M_HAR_I_68th_a_% | Aggr 10min Phase A 68th Current Magnitude Harmonics | float | 2 | R
0x448E | 0x448F | 17550 | 17551 | MAG_10M_HAR_I_68th_b_% | Aggr 10min Phase B 68th Current Magnitude Harmonics | float | 2 | R
0x4490 | 0x4491 | 17552 | 17553 | MAG_10M_HAR_I_68th_c_% | Aggr 10min Phase C 68th Current Magnitude Harmonics | float | 2 | R
0x4492 | 0x4493 | 17554 | 17555 | MAG_10M_HAR_I_68th_n_% | Aggr 10min Phase N 68th Current Magnitude Harmonics | float | 2 | R
0x4494 | 0x4495 | 17556 | 17557 | MAG_10M_HAR_V_69th_a_% | Aggr 10min Phase A 69th Voltage Magnitude Harmonics | float | 2 | R
0x4496 | 0x4497 | 17558 | 17559 | MAG_10M_HAR_V_69th_b_% | Aggr 10min Phase B 69th Voltage Magnitude Harmonics | float | 2 | R
0x4498 | 0x4499 | 17560 | 17561 | MAG_10M_HAR_V_69th_c_% | Aggr 10min Phase C 69th Voltage Magnitude Harmonics | float | 2 | R
0x449A | 0x449B | 17562 | 17563 | MAG_10M_HAR_I_69th_a_% | Aggr 10min Phase A 69th Current Magnitude Harmonics | float | 2 | R
0x449C | 0x449D | 17564 | 17565 | MAG_10M_HAR_I_69th_b_% | Aggr 10min Phase B 69th Current Magnitude Harmonics | float | 2 | R
0x449E | 0x449F | 17566 | 17567 | MAG_10M_HAR_I_69th_c_% | Aggr 10min Phase C 69th Current Magnitude Harmonics | float | 2 | R
0x44A0 | 0x44A1 | 17568 | 17569 | MAG_10M_HAR_I_69th_n_% | Aggr 10min Phase N 69th Current Magnitude Harmonics | float | 2 | R
0x44A2 | 0x44A3 | 17570 | 17571 | MAG_10M_HAR_V_70th_a_% | Aggr 10min Phase A 70th Voltage Magnitude Harmonics | float | 2 | R
0x44A4 | 0x44A5 | 17572 | 17573 | MAG_10M_HAR_V_70th_b_% | Aggr 10min Phase B 70th Voltage Magnitude Harmonics | float | 2 | R
0x44A6 | 0x44A7 | 17574 | 17575 | MAG_10M_HAR_V_70th_c_% | Aggr 10min Phase C 70th Voltage Magnitude Harmonics | float | 2 | R
0x44A8 | 0x44A9 | 17576 | 17577 | MAG_10M_HAR_I_70th_a_% | Aggr 10min Phase A 70th Current Magnitude Harmonics | float | 2 | R
0x44AA | 0x44AB | 17578 | 17579 | MAG_10M_HAR_I_70th_b_% | Aggr 10min Phase B 70th Current Magnitude Harmonics | float | 2 | R
0x44AC | 0x44AD | 17580 | 17581 | MAG_10M_HAR_I_70th_c_% | Aggr 10min Phase C 70th Current Magnitude Harmonics | float | 2 | R
0x44AE | 0x44AF | 17582 | 17583 | MAG_10M_HAR_I_70th_n_% | Aggr 10min Phase N 70th Current Magnitude Harmonics | float | 2 | R
0x44B0 | 0x44B1 | 17584 | 17585 | MAG_10M_HAR_V_71th_a_% | Aggr 10min Phase A 71st Voltage Magnitude Harmonics | float | 2 | R
0x44B2 | 0x44B3 | 17586 | 17587 | MAG_10M_HAR_V_71th_b_% | Aggr 10min Phase B 71st Voltage Magnitude Harmonics | float | 2 | R
0x44B4 | 0x44B5 | 17588 | 17589 | MAG_10M_HAR_V_71th_c_% | Aggr 10min Phase C 71st Voltage Magnitude Harmonics | float | 2 | R
0x44B6 | 0x44B7 | 17590 | 17591 | MAG_10M_HAR_I_71th_a_% | Aggr 10min Phase A 71st Current Magnitude Harmonics | float | 2 | R
0x44B8 | 0x44B9 | 17592 | 17593 | MAG_10M_HAR_I_71th_b_% | Aggr 10min Phase B 71st Current Magnitude Harmonics | float | 2 | R
0x44BA | 0x44BB | 17594 | 17595 | MAG_10M_HAR_I_71th_c_% | Aggr 10min Phase C 71st Current Magnitude Harmonics | float | 2 | R
0x44BC | 0x44BD | 17596 | 17597 | MAG_10M_HAR_I_71th_n_% | Aggr 10min Phase N 71st Current Magnitude Harmonics | float | 2 | R
0x44BE | 0x44BF | 17598 | 17599 | MAG_10M_HAR_V_72th_a_% | Aggr 10min Phase A 72nd Voltage Magnitude Harmonics | float | 2 | R
0x44C0 | 0x44C1 | 17600 | 17601 | MAG_10M_HAR_V_72th_b_% | Aggr 10min Phase B 72nd Voltage Magnitude Harmonics | float | 2 | R
0x44C2 | 0x44C3 | 17602 | 17603 | MAG_10M_HAR_V_72th_c_% | Aggr 10min Phase C 72nd Voltage Magnitude Harmonics | float | 2 | R
0x44C4 | 0x44C5 | 17604 | 17605 | MAG_10M_HAR_I_72th_a_% | Aggr 10min Phase A 72nd Current Magnitude Harmonics | float | 2 | R
0x44C6 | 0x44C7 | 17606 | 17607 | MAG_10M_HAR_I_72th_b_% | Aggr 10min Phase B 72nd Current Magnitude Harmonics | float | 2 | R
0x44C8 | 0x44C9 | 17608 | 17609 | MAG_10M_HAR_I_72th_c_% | Aggr 10min Phase C 72nd Current Magnitude Harmonics | float | 2 | R
0x44CA | 0x44CB | 17610 | 17611 | MAG_10M_HAR_I_72th_n_% | Aggr 10min Phase N 72nd Current Magnitude Harmonics | float | 2 | R
0x44CC | 0x44CD | 17612 | 17613 | MAG_10M_HAR_V_73th_a_% | Aggr 10min Phase A 73rd Voltage Magnitude Harmonics | float | 2 | R
0x44CE | 0x44CF | 17614 | 17615 | MAG_10M_HAR_V_73th_b_% | Aggr 10min Phase B 73rd Voltage Magnitude Harmonics | float | 2 | R
0x44D0 | 0x44D1 | 17616 | 17617 | MAG_10M_HAR_V_73th_c_% | Aggr 10min Phase C 73rd Voltage Magnitude Harmonics | float | 2 | R
0x44D2 | 0x44D3 | 17618 | 17619 | MAG_10M_HAR_I_73th_a_% | Aggr 10min Phase A 73rd Current Magnitude Harmonics | float | 2 | R
0x44D4 | 0x44D5 | 17620 | 17621 | MAG_10M_HAR_I_73th_b_% | Aggr 10min Phase B 73rd Current Magnitude Harmonics | float | 2 | R
0x44D6 | 0x44D7 | 17622 | 17623 | MAG_10M_HAR_I_73th_c_% | Aggr 10min Phase C 73rd Current Magnitude Harmonics | float | 2 | R
0x44D8 | 0x44D9 | 17624 | 17625 | MAG_10M_HAR_I_73th_n_% | Aggr 10min Phase N 73rd Current Magnitude Harmonics | float | 2 | R
0x44DA | 0x44DB | 17626 | 17627 | MAG_10M_HAR_V_74th_a_% | Aggr 10min Phase A 74th Voltage Magnitude Harmonics | float | 2 | R
0x44DC | 0x44DD | 17628 | 17629 | MAG_10M_HAR_V_74th_b_% | Aggr 10min Phase B 74th Voltage Magnitude Harmonics | float | 2 | R
0x44DE | 0x44DF | 17630 | 17631 | MAG_10M_HAR_V_74th_c_% | Aggr 10min Phase C 74th Voltage Magnitude Harmonics | float | 2 | R
0x44E0 | 0x44E1 | 17632 | 17633 | MAG_10M_HAR_I_74th_a_% | Aggr 10min Phase A 74th Current Magnitude Harmonics | float | 2 | R
0x44E2 | 0x44E3 | 17634 | 17635 | MAG_10M_HAR_I_74th_b_% | Aggr 10min Phase B 74th Current Magnitude Harmonics | float | 2 | R
0x44E4 | 0x44E5 | 17636 | 17637 | MAG_10M_HAR_I_74th_c_% | Aggr 10min Phase C 74th Current Magnitude Harmonics | float | 2 | R
0x44E6 | 0x44E7 | 17638 | 17639 | MAG_10M_HAR_I_74th_n_% | Aggr 10min Phase N 74th Current Magnitude Harmonics | float | 2 | R
0x44E8 | 0x44E9 | 17640 | 17641 | MAG_10M_HAR_V_75th_a_% | Aggr 10min Phase A 75th Voltage Magnitude Harmonics | float | 2 | R
0x44EA | 0x44EB | 17642 | 17643 | MAG_10M_HAR_V_75th_b_% | Aggr 10min Phase B 75th Voltage Magnitude Harmonics | float | 2 | R
0x44EC | 0x44ED | 17644 | 17645 | MAG_10M_HAR_V_75th_c_% | Aggr 10min Phase C 75th Voltage Magnitude Harmonics | float | 2 | R
0x44EE | 0x44EF | 17646 | 17647 | MAG_10M_HAR_I_75th_a_% | Aggr 10min Phase A 75th Current Magnitude Harmonics | float | 2 | R
0x44F0 | 0x44F1 | 17648 | 17649 | MAG_10M_HAR_I_75th_b_% | Aggr 10min Phase B 75th Current Magnitude Harmonics | float | 2 | R
0x44F2 | 0x44F3 | 17650 | 17651 | MAG_10M_HAR_I_75th_c_% | Aggr 10min Phase C 75th Current Magnitude Harmonics | float | 2 | R
0x44F4 | 0x44F5 | 17652 | 17653 | MAG_10M_HAR_I_75th_n_% | Aggr 10min Phase N 75th Current Magnitude Harmonics | float | 2 | R
0x44F6 | 0x44F7 | 17654 | 17655 | MAG_10M_HAR_V_76th_a_% | Aggr 10min Phase A 76th Voltage Magnitude Harmonics | float | 2 | R
0x44F8 | 0x44F9 | 17656 | 17657 | MAG_10M_HAR_V_76th_b_% | Aggr 10min Phase B 76th Voltage Magnitude Harmonics | float | 2 | R
0x44FA | 0x44FB | 17658 | 17659 | MAG_10M_HAR_V_76th_c_% | Aggr 10min Phase C 76th Voltage Magnitude Harmonics | float | 2 | R
0x44FC | 0x44FD | 17660 | 17661 | MAG_10M_HAR_I_76th_a_% | Aggr 10min Phase A 76th Current Magnitude Harmonics | float | 2 | R
0x44FE | 0x44FF | 17662 | 17663 | MAG_10M_HAR_I_76th_b_% | Aggr 10min Phase B 76th Current Magnitude Harmonics | float | 2 | R
0x4500 | 0x4501 | 17664 | 17665 | MAG_10M_HAR_I_76th_c_% | Aggr 10min Phase C 76th Current Magnitude Harmonics | float | 2 | R
0x4502 | 0x4503 | 17666 | 17667 | MAG_10M_HAR_I_76th_n_% | Aggr 10min Phase N 76th Current Magnitude Harmonics | float | 2 | R
0x4504 | 0x4505 | 17668 | 17669 | MAG_10M_HAR_V_77th_a_% | Aggr 10min Phase A 77th Voltage Magnitude Harmonics | float | 2 | R
0x4506 | 0x4507 | 17670 | 17671 | MAG_10M_HAR_V_77th_b_% | Aggr 10min Phase B 77th Voltage Magnitude Harmonics | float | 2 | R
0x4508 | 0x4509 | 17672 | 17673 | MAG_10M_HAR_V_77th_c_% | Aggr 10min Phase C 77th Voltage Magnitude Harmonics | float | 2 | R
0x450A | 0x450B | 17674 | 17675 | MAG_10M_HAR_I_77th_a_% | Aggr 10min Phase A 77th Current Magnitude Harmonics | float | 2 | R
0x450C | 0x450D | 17676 | 17677 | MAG_10M_HAR_I_77th_b_% | Aggr 10min Phase B 77th Current Magnitude Harmonics | float | 2 | R
0x450E | 0x450F | 17678 | 17679 | MAG_10M_HAR_I_77th_c_% | Aggr 10min Phase C 77th Current Magnitude Harmonics | float | 2 | R
0x4510 | 0x4511 | 17680 | 17681 | MAG_10M_HAR_I_77th_n_% | Aggr 10min Phase N 77th Current Magnitude Harmonics | float | 2 | R
0x4512 | 0x4513 | 17682 | 17683 | MAG_10M_HAR_V_78th_a_% | Aggr 10min Phase A 78th Voltage Magnitude Harmonics | float | 2 | R
0x4514 | 0x4515 | 17684 | 17685 | MAG_10M_HAR_V_78th_b_% | Aggr 10min Phase B 78th Voltage Magnitude Harmonics | float | 2 | R
0x4516 | 0x4517 | 17686 | 17687 | MAG_10M_HAR_V_78th_c_% | Aggr 10min Phase C 78th Voltage Magnitude Harmonics | float | 2 | R
0x4518 | 0x4519 | 17688 | 17689 | MAG_10M_HAR_I_78th_a_% | Aggr 10min Phase A 78th Current Magnitude Harmonics | float | 2 | R
0x451A | 0x451B | 17690 | 17691 | MAG_10M_HAR_I_78th_b_% | Aggr 10min Phase B 78th Current Magnitude Harmonics | float | 2 | R
0x451C | 0x451D | 17692 | 17693 | MAG_10M_HAR_I_78th_c_% | Aggr 10min Phase C 78th Current Magnitude Harmonics | float | 2 | R
0x451E | 0x451F | 17694 | 17695 | MAG_10M_HAR_I_78th_n_% | Aggr 10min Phase N 78th Current Magnitude Harmonics | float | 2 | R
0x4520 | 0x4521 | 17696 | 17697 | MAG_10M_HAR_V_79th_a_% | Aggr 10min Phase A 79th Voltage Magnitude Harmonics | float | 2 | R
0x4522 | 0x4523 | 17698 | 17699 | MAG_10M_HAR_V_79th_b_% | Aggr 10min Phase B 79th Voltage Magnitude Harmonics | float | 2 | R
0x4524 | 0x4525 | 17700 | 17701 | MAG_10M_HAR_V_79th_c_% | Aggr 10min Phase C 79th Voltage Magnitude Harmonics | float | 2 | R
0x4526 | 0x4527 | 17702 | 17703 | MAG_10M_HAR_I_79th_a_% | Aggr 10min Phase A 79th Current Magnitude Harmonics | float | 2 | R
0x4528 | 0x4529 | 17704 | 17705 | MAG_10M_HAR_I_79th_b_% | Aggr 10min Phase B 79th Current Magnitude Harmonics | float | 2 | R
0x452A | 0x452B | 17706 | 17707 | MAG_10M_HAR_I_79th_c_% | Aggr 10min Phase C 79th Current Magnitude Harmonics | float | 2 | R
0x452C | 0x452D | 17708 | 17709 | MAG_10M_HAR_I_79th_n_% | Aggr 10min Phase N 79th Current Magnitude Harmonics | float | 2 | R
0x452E | 0x452F | 17710 | 17711 | MAG_10M_HAR_V_80th_a_% | Aggr 10min Phase A 80th Voltage Magnitude Harmonics | float | 2 | R
0x4530 | 0x4531 | 17712 | 17713 | MAG_10M_HAR_V_80th_b_% | Aggr 10min Phase B 80th Voltage Magnitude Harmonics | float | 2 | R
0x4532 | 0x4533 | 17714 | 17715 | MAG_10M_HAR_V_80th_c_% | Aggr 10min Phase C 80th Voltage Magnitude Harmonics | float | 2 | R
0x4534 | 0x4535 | 17716 | 17717 | MAG_10M_HAR_I_80th_a_% | Aggr 10min Phase A 80th Current Magnitude Harmonics | float | 2 | R
0x4536 | 0x4537 | 17718 | 17719 | MAG_10M_HAR_I_80th_b_% | Aggr 10min Phase B 80th Current Magnitude Harmonics | float | 2 | R
0x4538 | 0x4539 | 17720 | 17721 | MAG_10M_HAR_I_80th_c_% | Aggr 10min Phase C 80th Current Magnitude Harmonics | float | 2 | R
0x453A | 0x453B | 17722 | 17723 | MAG_10M_HAR_I_80th_n_% | Aggr 10min Phase N 80th Current Magnitude Harmonics | float | 2 | R
0x453C | 0x453D | 17724 | 17725 | MAG_10M_HAR_V_81th_a_% | Aggr 10min Phase A 81st Voltage Magnitude Harmonics | float | 2 | R
0x453E | 0x453F | 17726 | 17727 | MAG_10M_HAR_V_81th_b_% | Aggr 10min Phase B 81st Voltage Magnitude Harmonics | float | 2 | R
0x4540 | 0x4541 | 17728 | 17729 | MAG_10M_HAR_V_81th_c_% | Aggr 10min Phase C 81st Voltage Magnitude Harmonics | float | 2 | R
0x4542 | 0x4543 | 17730 | 17731 | MAG_10M_HAR_I_81th_a_% | Aggr 10min Phase A 81st Current Magnitude Harmonics | float | 2 | R
0x4544 | 0x4545 | 17732 | 17733 | MAG_10M_HAR_I_81th_b_% | Aggr 10min Phase B 81st Current Magnitude Harmonics | float | 2 | R
0x4546 | 0x4547 | 17734 | 17735 | MAG_10M_HAR_I_81th_c_% | Aggr 10min Phase C 81st Current Magnitude Harmonics | float | 2 | R
0x4548 | 0x4549 | 17736 | 17737 | MAG_10M_HAR_I_81th_n_% | Aggr 10min Phase N 81st Current Magnitude Harmonics | float | 2 | R
0x454A | 0x454B | 17738 | 17739 | MAG_10M_HAR_V_82th_a_% | Aggr 10min Phase A 82nd Voltage Magnitude Harmonics | float | 2 | R
0x454C | 0x454D | 17740 | 17741 | MAG_10M_HAR_V_82th_b_% | Aggr 10min Phase B 82nd Voltage Magnitude Harmonics | float | 2 | R
0x454E | 0x454F | 17742 | 17743 | MAG_10M_HAR_V_82th_c_% | Aggr 10min Phase C 82nd Voltage Magnitude Harmonics | float | 2 | R
0x4550 | 0x4551 | 17744 | 17745 | MAG_10M_HAR_I_82th_a_% | Aggr 10min Phase A 82nd Current Magnitude Harmonics | float | 2 | R
0x4552 | 0x4553 | 17746 | 17747 | MAG_10M_HAR_I_82th_b_% | Aggr 10min Phase B 82nd Current Magnitude Harmonics | float | 2 | R
0x4554 | 0x4555 | 17748 | 17749 | MAG_10M_HAR_I_82th_c_% | Aggr 10min Phase C 82nd Current Magnitude Harmonics | float | 2 | R
0x4556 | 0x4557 | 17750 | 17751 | MAG_10M_HAR_I_82th_n_% | Aggr 10min Phase N 82nd Current Magnitude Harmonics | float | 2 | R
0x4558 | 0x4559 | 17752 | 17753 | MAG_10M_HAR_V_83th_a_% | Aggr 10min Phase A 83rd Voltage Magnitude Harmonics | float | 2 | R
0x455A | 0x455B | 17754 | 17755 | MAG_10M_HAR_V_83th_b_% | Aggr 10min Phase B 83rd Voltage Magnitude Harmonics | float | 2 | R
0x455C | 0x455D | 17756 | 17757 | MAG_10M_HAR_V_83th_c_% | Aggr 10min Phase C 83rd Voltage Magnitude Harmonics | float | 2 | R
0x455E | 0x455F | 17758 | 17759 | MAG_10M_HAR_I_83th_a_% | Aggr 10min Phase A 83rd Current Magnitude Harmonics | float | 2 | R
0x4560 | 0x4561 | 17760 | 17761 | MAG_10M_HAR_I_83th_b_% | Aggr 10min Phase B 83rd Current Magnitude Harmonics | float | 2 | R
0x4562 | 0x4563 | 17762 | 17763 | MAG_10M_HAR_I_83th_c_% | Aggr 10min Phase C 83rd Current Magnitude Harmonics | float | 2 | R
0x4564 | 0x4565 | 17764 | 17765 | MAG_10M_HAR_I_83th_n_% | Aggr 10min Phase N 83rd Current Magnitude Harmonics | float | 2 | R
0x4566 | 0x4567 | 17766 | 17767 | MAG_10M_HAR_V_84th_a_% | Aggr 10min Phase A 84th Voltage Magnitude Harmonics | float | 2 | R
0x4568 | 0x4569 | 17768 | 17769 | MAG_10M_HAR_V_84th_b_% | Aggr 10min Phase B 84th Voltage Magnitude Harmonics | float | 2 | R
0x456A | 0x456B | 17770 | 17771 | MAG_10M_HAR_V_84th_c_% | Aggr 10min Phase C 84th Voltage Magnitude Harmonics | float | 2 | R
0x456C | 0x456D | 17772 | 17773 | MAG_10M_HAR_I_84th_a_% | Aggr 10min Phase A 84th Current Magnitude Harmonics | float | 2 | R
0x456E | 0x456F | 17774 | 17775 | MAG_10M_HAR_I_84th_b_% | Aggr 10min Phase B 84th Current Magnitude Harmonics | float | 2 | R
0x4570 | 0x4571 | 17776 | 17777 | MAG_10M_HAR_I_84th_c_% | Aggr 10min Phase C 84th Current Magnitude Harmonics | float | 2 | R
0x4572 | 0x4573 | 17778 | 17779 | MAG_10M_HAR_I_84th_n_% | Aggr 10min Phase N 84th Current Magnitude Harmonics | float | 2 | R
0x4574 | 0x4575 | 17780 | 17781 | MAG_10M_HAR_V_85th_a_% | Aggr 10min Phase A 85th Voltage Magnitude Harmonics | float | 2 | R
0x4576 | 0x4577 | 17782 | 17783 | MAG_10M_HAR_V_85th_b_% | Aggr 10min Phase B 85th Voltage Magnitude Harmonics | float | 2 | R
0x4578 | 0x4579 | 17784 | 17785 | MAG_10M_HAR_V_85th_c_% | Aggr 10min Phase C 85th Voltage Magnitude Harmonics | float | 2 | R
0x457A | 0x457B | 17786 | 17787 | MAG_10M_HAR_I_85th_a_% | Aggr 10min Phase A 85th Current Magnitude Harmonics | float | 2 | R
0x457C | 0x457D | 17788 | 17789 | MAG_10M_HAR_I_85th_b_% | Aggr 10min Phase B 85th Current Magnitude Harmonics | float | 2 | R
0x457E | 0x457F | 17790 | 17791 | MAG_10M_HAR_I_85th_c_% | Aggr 10min Phase C 85th Current Magnitude Harmonics | float | 2 | R
0x4580 | 0x4581 | 17792 | 17793 | MAG_10M_HAR_I_85th_n_% | Aggr 10min Phase N 85th Current Magnitude Harmonics | float | 2 | R
0x4582 | 0x4583 | 17794 | 17795 | MAG_10M_HAR_V_86th_a_% | Aggr 10min Phase A 86th Voltage Magnitude Harmonics | float | 2 | R
0x4584 | 0x4585 | 17796 | 17797 | MAG_10M_HAR_V_86th_b_% | Aggr 10min Phase B 86th Voltage Magnitude Harmonics | float | 2 | R
0x4586 | 0x4587 | 17798 | 17799 | MAG_10M_HAR_V_86th_c_% | Aggr 10min Phase C 86th Voltage Magnitude Harmonics | float | 2 | R
0x4588 | 0x4589 | 17800 | 17801 | MAG_10M_HAR_I_86th_a_% | Aggr 10min Phase A 86th Current Magnitude Harmonics | float | 2 | R
0x458A | 0x458B | 17802 | 17803 | MAG_10M_HAR_I_86th_b_% | Aggr 10min Phase B 86th Current Magnitude Harmonics | float | 2 | R
0x458C | 0x458D | 17804 | 17805 | MAG_10M_HAR_I_86th_c_% | Aggr 10min Phase C 86th Current Magnitude Harmonics | float | 2 | R
0x458E | 0x458F | 17806 | 17807 | MAG_10M_HAR_I_86th_n_% | Aggr 10min Phase N 86th Current Magnitude Harmonics | float | 2 | R
0x4590 | 0x4591 | 17808 | 17809 | MAG_10M_HAR_V_87th_a_% | Aggr 10min Phase A 87th Voltage Magnitude Harmonics | float | 2 | R
0x4592 | 0x4593 | 17810 | 17811 | MAG_10M_HAR_V_87th_b_% | Aggr 10min Phase B 87th Voltage Magnitude Harmonics | float | 2 | R
0x4594 | 0x4595 | 17812 | 17813 | MAG_10M_HAR_V_87th_c_% | Aggr 10min Phase C 87th Voltage Magnitude Harmonics | float | 2 | R
0x4596 | 0x4597 | 17814 | 17815 | MAG_10M_HAR_I_87th_a_% | Aggr 10min Phase A 87th Current Magnitude Harmonics | float | 2 | R
0x4598 | 0x4599 | 17816 | 17817 | MAG_10M_HAR_I_87th_b_% | Aggr 10min Phase B 87th Current Magnitude Harmonics | float | 2 | R
0x459A | 0x459B | 17818 | 17819 | MAG_10M_HAR_I_87th_c_% | Aggr 10min Phase C 87th Current Magnitude Harmonics | float | 2 | R
0x459C | 0x459D | 17820 | 17821 | MAG_10M_HAR_I_87th_n_% | Aggr 10min Phase N 87th Current Magnitude Harmonics | float | 2 | R
0x459E | 0x459F | 17822 | 17823 | MAG_10M_HAR_V_88th_a_% | Aggr 10min Phase A 88th Voltage Magnitude Harmonics | float | 2 | R
0x45A0 | 0x45A1 | 17824 | 17825 | MAG_10M_HAR_V_88th_b_% | Aggr 10min Phase B 88th Voltage Magnitude Harmonics | float | 2 | R
0x45A2 | 0x45A3 | 17826 | 17827 | MAG_10M_HAR_V_88th_c_% | Aggr 10min Phase C 88th Voltage Magnitude Harmonics | float | 2 | R
0x45A4 | 0x45A5 | 17828 | 17829 | MAG_10M_HAR_I_88th_a_% | Aggr 10min Phase A 88th Current Magnitude Harmonics | float | 2 | R
0x45A6 | 0x45A7 | 17830 | 17831 | MAG_10M_HAR_I_88th_b_% | Aggr 10min Phase B 88th Current Magnitude Harmonics | float | 2 | R
0x45A8 | 0x45A9 | 17832 | 17833 | MAG_10M_HAR_I_88th_c_% | Aggr 10min Phase C 88th Current Magnitude Harmonics | float | 2 | R
0x45AA | 0x45AB | 17834 | 17835 | MAG_10M_HAR_I_88th_n_% | Aggr 10min Phase N 88th Current Magnitude Harmonics | float | 2 | R
0x45AC | 0x45AD | 17836 | 17837 | MAG_10M_HAR_V_89th_a_% | Aggr 10min Phase A 89th Voltage Magnitude Harmonics | float | 2 | R
0x45AE | 0x45AF | 17838 | 17839 | MAG_10M_HAR_V_89th_b_% | Aggr 10min Phase B 89th Voltage Magnitude Harmonics | float | 2 | R
0x45B0 | 0x45B1 | 17840 | 17841 | MAG_10M_HAR_V_89th_c_% | Aggr 10min Phase C 89th Voltage Magnitude Harmonics | float | 2 | R
0x45B2 | 0x45B3 | 17842 | 17843 | MAG_10M_HAR_I_89th_a_% | Aggr 10min Phase A 89th Current Magnitude Harmonics | float | 2 | R
0x45B4 | 0x45B5 | 17844 | 17845 | MAG_10M_HAR_I_89th_b_% | Aggr 10min Phase B 89th Current Magnitude Harmonics | float | 2 | R
0x45B6 | 0x45B7 | 17846 | 17847 | MAG_10M_HAR_I_89th_c_% | Aggr 10min Phase C 89th Current Magnitude Harmonics | float | 2 | R
0x45B8 | 0x45B9 | 17848 | 17849 | MAG_10M_HAR_I_89th_n_% | Aggr 10min Phase N 89th Current Magnitude Harmonics | float | 2 | R
0x45BA | 0x45BB | 17850 | 17851 | MAG_10M_HAR_V_90th_a_% | Aggr 10min Phase A 90th Voltage Magnitude Harmonics | float | 2 | R
0x45BC | 0x45BD | 17852 | 17853 | MAG_10M_HAR_V_90th_b_% | Aggr 10min Phase B 90th Voltage Magnitude Harmonics | float | 2 | R
0x45BE | 0x45BF | 17854 | 17855 | MAG_10M_HAR_V_90th_c_% | Aggr 10min Phase C 90th Voltage Magnitude Harmonics | float | 2 | R
0x45C0 | 0x45C1 | 17856 | 17857 | MAG_10M_HAR_I_90th_a_% | Aggr 10min Phase A 90th Current Magnitude Harmonics | float | 2 | R
0x45C2 | 0x45C3 | 17858 | 17859 | MAG_10M_HAR_I_90th_b_% | Aggr 10min Phase B 90th Current Magnitude Harmonics | float | 2 | R
0x45C4 | 0x45C5 | 17860 | 17861 | MAG_10M_HAR_I_90th_c_% | Aggr 10min Phase C 90th Current Magnitude Harmonics | float | 2 | R
0x45C6 | 0x45C7 | 17862 | 17863 | MAG_10M_HAR_I_90th_n_% | Aggr 10min Phase N 90th Current Magnitude Harmonics | float | 2 | R
0x45C8 | 0x45C9 | 17864 | 17865 | MAG_10M_HAR_V_91th_a_% | Aggr 10min Phase A 91st Voltage Magnitude Harmonics | float | 2 | R
0x45CA | 0x45CB | 17866 | 17867 | MAG_10M_HAR_V_91th_b_% | Aggr 10min Phase B 91st Voltage Magnitude Harmonics | float | 2 | R
0x45CC | 0x45CD | 17868 | 17869 | MAG_10M_HAR_V_91th_c_% | Aggr 10min Phase C 91st Voltage Magnitude Harmonics | float | 2 | R
0x45CE | 0x45CF | 17870 | 17871 | MAG_10M_HAR_I_91th_a_% | Aggr 10min Phase A 91st Current Magnitude Harmonics | float | 2 | R
0x45D0 | 0x45D1 | 17872 | 17873 | MAG_10M_HAR_I_91th_b_% | Aggr 10min Phase B 91st Current Magnitude Harmonics | float | 2 | R
0x45D2 | 0x45D3 | 17874 | 17875 | MAG_10M_HAR_I_91th_c_% | Aggr 10min Phase C 91st Current Magnitude Harmonics | float | 2 | R
0x45D4 | 0x45D5 | 17876 | 17877 | MAG_10M_HAR_I_91th_n_% | Aggr 10min Phase N 91st Current Magnitude Harmonics | float | 2 | R
0x45D6 | 0x45D7 | 17878 | 17879 | MAG_10M_HAR_V_92th_a_% | Aggr 10min Phase A 92nd Voltage Magnitude Harmonics | float | 2 | R
0x45D8 | 0x45D9 | 17880 | 17881 | MAG_10M_HAR_V_92th_b_% | Aggr 10min Phase B 92nd Voltage Magnitude Harmonics | float | 2 | R
0x45DA | 0x45DB | 17882 | 17883 | MAG_10M_HAR_V_92th_c_% | Aggr 10min Phase C 92nd Voltage Magnitude Harmonics | float | 2 | R
0x45DC | 0x45DD | 17884 | 17885 | MAG_10M_HAR_I_92th_a_% | Aggr 10min Phase A 92nd Current Magnitude Harmonics | float | 2 | R
0x45DE | 0x45DF | 17886 | 17887 | MAG_10M_HAR_I_92th_b_% | Aggr 10min Phase B 92nd Current Magnitude Harmonics | float | 2 | R
0x45E0 | 0x45E1 | 17888 | 17889 | MAG_10M_HAR_I_92th_c_% | Aggr 10min Phase C 92nd Current Magnitude Harmonics | float | 2 | R
0x45E2 | 0x45E3 | 17890 | 17891 | MAG_10M_HAR_I_92th_n_% | Aggr 10min Phase N 92nd Current Magnitude Harmonics | float | 2 | R
0x45E4 | 0x45E5 | 17892 | 17893 | MAG_10M_HAR_V_93th_a_% | Aggr 10min Phase A 93rd Voltage Magnitude Harmonics | float | 2 | R
0x45E6 | 0x45E7 | 17894 | 17895 | MAG_10M_HAR_V_93th_b_% | Aggr 10min Phase B 93rd Voltage Magnitude Harmonics | float | 2 | R
0x45E8 | 0x45E9 | 17896 | 17897 | MAG_10M_HAR_V_93th_c_% | Aggr 10min Phase C 93rd Voltage Magnitude Harmonics | float | 2 | R
0x45EA | 0x45EB | 17898 | 17899 | MAG_10M_HAR_I_93th_a_% | Aggr 10min Phase A 93rd Current Magnitude Harmonics | float | 2 | R
0x45EC | 0x45ED | 17900 | 17901 | MAG_10M_HAR_I_93th_b_% | Aggr 10min Phase B 93rd Current Magnitude Harmonics | float | 2 | R
0x45EE | 0x45EF | 17902 | 17903 | MAG_10M_HAR_I_93th_c_% | Aggr 10min Phase C 93rd Current Magnitude Harmonics | float | 2 | R
0x45F0 | 0x45F1 | 17904 | 17905 | MAG_10M_HAR_I_93th_n_% | Aggr 10min Phase N 93rd Current Magnitude Harmonics | float | 2 | R
0x45F2 | 0x45F3 | 17906 | 17907 | MAG_10M_HAR_V_94th_a_% | Aggr 10min Phase A 94th Voltage Magnitude Harmonics | float | 2 | R
0x45F4 | 0x45F5 | 17908 | 17909 | MAG_10M_HAR_V_94th_b_% | Aggr 10min Phase B 94th Voltage Magnitude Harmonics | float | 2 | R
0x45F6 | 0x45F7 | 17910 | 17911 | MAG_10M_HAR_V_94th_c_% | Aggr 10min Phase C 94th Voltage Magnitude Harmonics | float | 2 | R
0x45F8 | 0x45F9 | 17912 | 17913 | MAG_10M_HAR_I_94th_a_% | Aggr 10min Phase A 94th Current Magnitude Harmonics | float | 2 | R
0x45FA | 0x45FB | 17914 | 17915 | MAG_10M_HAR_I_94th_b_% | Aggr 10min Phase B 94th Current Magnitude Harmonics | float | 2 | R
0x45FC | 0x45FD | 17916 | 17917 | MAG_10M_HAR_I_94th_c_% | Aggr 10min Phase C 94th Current Magnitude Harmonics | float | 2 | R
0x45FE | 0x45FF | 17918 | 17919 | MAG_10M_HAR_I_94th_n_% | Aggr 10min Phase N 94th Current Magnitude Harmonics | float | 2 | R
0x4600 | 0x4601 | 17920 | 17921 | MAG_10M_HAR_V_95th_a_% | Aggr 10min Phase A 95th Voltage Magnitude Harmonics | float | 2 | R
0x4602 | 0x4603 | 17922 | 17923 | MAG_10M_HAR_V_95th_b_% | Aggr 10min Phase B 95th Voltage Magnitude Harmonics | float | 2 | R
0x4604 | 0x4605 | 17924 | 17925 | MAG_10M_HAR_V_95th_c_% | Aggr 10min Phase C 95th Voltage Magnitude Harmonics | float | 2 | R
0x4606 | 0x4607 | 17926 | 17927 | MAG_10M_HAR_I_95th_a_% | Aggr 10min Phase A 95th Current Magnitude Harmonics | float | 2 | R
0x4608 | 0x4609 | 17928 | 17929 | MAG_10M_HAR_I_95th_b_% | Aggr 10min Phase B 95th Current Magnitude Harmonics | float | 2 | R
0x460A | 0x460B | 17930 | 17931 | MAG_10M_HAR_I_95th_c_% | Aggr 10min Phase C 95th Current Magnitude Harmonics | float | 2 | R
0x460C | 0x460D | 17932 | 17933 | MAG_10M_HAR_I_95th_n_% | Aggr 10min Phase N 95th Current Magnitude Harmonics | float | 2 | R
0x460E | 0x460F | 17934 | 17935 | MAG_10M_HAR_V_96th_a_% | Aggr 10min Phase A 96th Voltage Magnitude Harmonics | float | 2 | R
0x4610 | 0x4611 | 17936 | 17937 | MAG_10M_HAR_V_96th_b_% | Aggr 10min Phase B 96th Voltage Magnitude Harmonics | float | 2 | R
0x4612 | 0x4613 | 17938 | 17939 | MAG_10M_HAR_V_96th_c_% | Aggr 10min Phase C 96th Voltage Magnitude Harmonics | float | 2 | R
0x4614 | 0x4615 | 17940 | 17941 | MAG_10M_HAR_I_96th_a_% | Aggr 10min Phase A 96th Current Magnitude Harmonics | float | 2 | R
0x4616 | 0x4617 | 17942 | 17943 | MAG_10M_HAR_I_96th_b_% | Aggr 10min Phase B 96th Current Magnitude Harmonics | float | 2 | R
0x4618 | 0x4619 | 17944 | 17945 | MAG_10M_HAR_I_96th_c_% | Aggr 10min Phase C 96th Current Magnitude Harmonics | float | 2 | R
0x461A | 0x461B | 17946 | 17947 | MAG_10M_HAR_I_96th_n_% | Aggr 10min Phase N 96th Current Magnitude Harmonics | float | 2 | R
0x461C | 0x461D | 17948 | 17949 | MAG_10M_HAR_V_97th_a_% | Aggr 10min Phase A 97th Voltage Magnitude Harmonics | float | 2 | R
0x461E | 0x461F | 17950 | 17951 | MAG_10M_HAR_V_97th_b_% | Aggr 10min Phase B 97th Voltage Magnitude Harmonics | float | 2 | R
0x4620 | 0x4621 | 17952 | 17953 | MAG_10M_HAR_V_97th_c_% | Aggr 10min Phase C 97th Voltage Magnitude Harmonics | float | 2 | R
0x4622 | 0x4623 | 17954 | 17955 | MAG_10M_HAR_I_97th_a_% | Aggr 10min Phase A 97th Current Magnitude Harmonics | float | 2 | R
0x4624 | 0x4625 | 17956 | 17957 | MAG_10M_HAR_I_97th_b_% | Aggr 10min Phase B 97th Current Magnitude Harmonics | float | 2 | R
0x4626 | 0x4627 | 17958 | 17959 | MAG_10M_HAR_I_97th_c_% | Aggr 10min Phase C 97th Current Magnitude Harmonics | float | 2 | R
0x4628 | 0x4629 | 17960 | 17961 | MAG_10M_HAR_I_97th_n_% | Aggr 10min Phase N 97th Current Magnitude Harmonics | float | 2 | R
0x462A | 0x462B | 17962 | 17963 | MAG_10M_HAR_V_98th_a_% | Aggr 10min Phase A 98th Voltage Magnitude Harmonics | float | 2 | R
0x462C | 0x462D | 17964 | 17965 | MAG_10M_HAR_V_98th_b_% | Aggr 10min Phase B 98th Voltage Magnitude Harmonics | float | 2 | R
0x462E | 0x462F | 17966 | 17967 | MAG_10M_HAR_V_98th_c_% | Aggr 10min Phase C 98th Voltage Magnitude Harmonics | float | 2 | R
0x4630 | 0x4631 | 17968 | 17969 | MAG_10M_HAR_I_98th_a_% | Aggr 10min Phase A 98th Current Magnitude Harmonics | float | 2 | R
0x4632 | 0x4633 | 17970 | 17971 | MAG_10M_HAR_I_98th_b_% | Aggr 10min Phase B 98th Current Magnitude Harmonics | float | 2 | R
0x4634 | 0x4635 | 17972 | 17973 | MAG_10M_HAR_I_98th_c_% | Aggr 10min Phase C 98th Current Magnitude Harmonics | float | 2 | R
0x4636 | 0x4637 | 17974 | 17975 | MAG_10M_HAR_I_98th_n_% | Aggr 10min Phase N 98th Current Magnitude Harmonics | float | 2 | R
0x4638 | 0x4639 | 17976 | 17977 | MAG_10M_HAR_V_99th_a_% | Aggr 10min Phase A 99th Voltage Magnitude Harmonics | float | 2 | R
0x463A | 0x463B | 17978 | 17979 | MAG_10M_HAR_V_99th_b_% | Aggr 10min Phase B 99th Voltage Magnitude Harmonics | float | 2 | R
0x463C | 0x463D | 17980 | 17981 | MAG_10M_HAR_V_99th_c_% | Aggr 10min Phase C 99th Voltage Magnitude Harmonics | float | 2 | R
0x463E | 0x463F | 17982 | 17983 | MAG_10M_HAR_I_99th_a_% | Aggr 10min Phase A 99th Current Magnitude Harmonics | float | 2 | R
0x4640 | 0x4641 | 17984 | 17985 | MAG_10M_HAR_I_99th_b_% | Aggr 10min Phase B 99th Current Magnitude Harmonics | float | 2 | R
0x4642 | 0x4643 | 17986 | 17987 | MAG_10M_HAR_I_99th_c_% | Aggr 10min Phase C 99th Current Magnitude Harmonics | float | 2 | R
0x4644 | 0x4645 | 17988 | 17989 | MAG_10M_HAR_I_99th_n_% | Aggr 10min Phase N 99th Current Magnitude Harmonics | float | 2 | R
0x4646 | 0x4647 | 17990 | 17991 | MAG_10M_HAR_V_100th_a_% | Aggr 10min Phase A 100th Voltage Magnitude Harmonics | float | 2 | R
0x4648 | 0x4649 | 17992 | 17993 | MAG_10M_HAR_V_100th_b_% | Aggr 10min Phase B 100th Voltage Magnitude Harmonics | float | 2 | R
0x464A | 0x464B | 17994 | 17995 | MAG_10M_HAR_V_100th_c_% | Aggr 10min Phase C 100th Voltage Magnitude Harmonics | float | 2 | R
0x464C | 0x464D | 17996 | 17997 | MAG_10M_HAR_I_100th_a_% | Aggr 10min Phase A 100th Current Magnitude Harmonics | float | 2 | R
0x464E | 0x464F | 17998 | 17999 | MAG_10M_HAR_I_100th_b_% | Aggr 10min Phase B 100th Current Magnitude Harmonics | float | 2 | R
0x4650 | 0x4651 | 18000 | 18001 | MAG_10M_HAR_I_100th_c_% | Aggr 10min Phase C 100th Current Magnitude Harmonics | float | 2 | R
0x4652 | 0x4653 | 18002 | 18003 | MAG_10M_HAR_I_100th_n_% | Aggr 10min Phase N 100th Current Magnitude Harmonics | float | 2 | R
0x4654 | 0x4655 | 18004 | 18005 | MAG_10M_HAR_V_101th_a_% | Aggr 10min Phase A 101st Voltage Magnitude Harmonics | float | 2 | R
0x4656 | 0x4657 | 18006 | 18007 | MAG_10M_HAR_V_101th_b_% | Aggr 10min Phase B 101st Voltage Magnitude Harmonics | float | 2 | R
0x4658 | 0x4659 | 18008 | 18009 | MAG_10M_HAR_V_101th_c_% | Aggr 10min Phase C 101st Voltage Magnitude Harmonics | float | 2 | R
0x465A | 0x465B | 18010 | 18011 | MAG_10M_HAR_I_101th_a_% | Aggr 10min Phase A 101st Current Magnitude Harmonics | float | 2 | R
0x465C | 0x465D | 18012 | 18013 | MAG_10M_HAR_I_101th_b_% | Aggr 10min Phase B 101st Current Magnitude Harmonics | float | 2 | R
0x465E | 0x465F | 18014 | 18015 | MAG_10M_HAR_I_101th_c_% | Aggr 10min Phase C 101st Current Magnitude Harmonics | float | 2 | R
0x4660 | 0x4661 | 18016 | 18017 | MAG_10M_HAR_I_101th_n_% | Aggr 10min Phase N 101st Current Magnitude Harmonics | float | 2 | R
0x4662 | 0x4663 | 18018 | 18019 | MAG_10M_HAR_V_102th_a_% | Aggr 10min Phase A 102nd Voltage Magnitude Harmonics | float | 2 | R
0x4664 | 0x4665 | 18020 | 18021 | MAG_10M_HAR_V_102th_b_% | Aggr 10min Phase B 102nd Voltage Magnitude Harmonics | float | 2 | R
0x4666 | 0x4667 | 18022 | 18023 | MAG_10M_HAR_V_102th_c_% | Aggr 10min Phase C 102nd Voltage Magnitude Harmonics | float | 2 | R
0x4668 | 0x4669 | 18024 | 18025 | MAG_10M_HAR_I_102th_a_% | Aggr 10min Phase A 102nd Current Magnitude Harmonics | float | 2 | R
0x466A | 0x466B | 18026 | 18027 | MAG_10M_HAR_I_102th_b_% | Aggr 10min Phase B 102nd Current Magnitude Harmonics | float | 2 | R
0x466C | 0x466D | 18028 | 18029 | MAG_10M_HAR_I_102th_c_% | Aggr 10min Phase C 102nd Current Magnitude Harmonics | float | 2 | R
0x466E | 0x466F | 18030 | 18031 | MAG_10M_HAR_I_102th_n_% | Aggr 10min Phase N 102nd Current Magnitude Harmonics | float | 2 | R
0x4670 | 0x4671 | 18032 | 18033 | MAG_10M_HAR_V_103th_a_% | Aggr 10min Phase A 103rd Voltage Magnitude Harmonics | float | 2 | R
0x4672 | 0x4673 | 18034 | 18035 | MAG_10M_HAR_V_103th_b_% | Aggr 10min Phase B 103rd Voltage Magnitude Harmonics | float | 2 | R
0x4674 | 0x4675 | 18036 | 18037 | MAG_10M_HAR_V_103th_c_% | Aggr 10min Phase C 103rd Voltage Magnitude Harmonics | float | 2 | R
0x4676 | 0x4677 | 18038 | 18039 | MAG_10M_HAR_I_103th_a_% | Aggr 10min Phase A 103rd Current Magnitude Harmonics | float | 2 | R
0x4678 | 0x4679 | 18040 | 18041 | MAG_10M_HAR_I_103th_b_% | Aggr 10min Phase B 103rd Current Magnitude Harmonics | float | 2 | R
0x467A | 0x467B | 18042 | 18043 | MAG_10M_HAR_I_103th_c_% | Aggr 10min Phase C 103rd Current Magnitude Harmonics | float | 2 | R
0x467C | 0x467D | 18044 | 18045 | MAG_10M_HAR_I_103th_n_% | Aggr 10min Phase N 103rd Current Magnitude Harmonics | float | 2 | R
0x467E | 0x467F | 18046 | 18047 | MAG_10M_HAR_V_104th_a_% | Aggr 10min Phase A 104th Voltage Magnitude Harmonics | float | 2 | R
0x4680 | 0x4681 | 18048 | 18049 | MAG_10M_HAR_V_104th_b_% | Aggr 10min Phase B 104th Voltage Magnitude Harmonics | float | 2 | R
0x4682 | 0x4683 | 18050 | 18051 | MAG_10M_HAR_V_104th_c_% | Aggr 10min Phase C 104th Voltage Magnitude Harmonics | float | 2 | R
0x4684 | 0x4685 | 18052 | 18053 | MAG_10M_HAR_I_104th_a_% | Aggr 10min Phase A 104th Current Magnitude Harmonics | float | 2 | R
0x4686 | 0x4687 | 18054 | 18055 | MAG_10M_HAR_I_104th_b_% | Aggr 10min Phase B 104th Current Magnitude Harmonics | float | 2 | R
0x4688 | 0x4689 | 18056 | 18057 | MAG_10M_HAR_I_104th_c_% | Aggr 10min Phase C 104th Current Magnitude Harmonics | float | 2 | R
0x468A | 0x468B | 18058 | 18059 | MAG_10M_HAR_I_104th_n_% | Aggr 10min Phase N 104th Current Magnitude Harmonics | float | 2 | R
0x468C | 0x468D | 18060 | 18061 | MAG_10M_HAR_V_105th_a_% | Aggr 10min Phase A 105th Voltage Magnitude Harmonics | float | 2 | R
0x468E | 0x468F | 18062 | 18063 | MAG_10M_HAR_V_105th_b_% | Aggr 10min Phase B 105th Voltage Magnitude Harmonics | float | 2 | R
0x4690 | 0x4691 | 18064 | 18065 | MAG_10M_HAR_V_105th_c_% | Aggr 10min Phase C 105th Voltage Magnitude Harmonics | float | 2 | R
0x4692 | 0x4693 | 18066 | 18067 | MAG_10M_HAR_I_105th_a_% | Aggr 10min Phase A 105th Current Magnitude Harmonics | float | 2 | R
0x4694 | 0x4695 | 18068 | 18069 | MAG_10M_HAR_I_105th_b_% | Aggr 10min Phase B 105th Current Magnitude Harmonics | float | 2 | R
0x4696 | 0x4697 | 18070 | 18071 | MAG_10M_HAR_I_105th_c_% | Aggr 10min Phase C 105th Current Magnitude Harmonics | float | 2 | R
0x4698 | 0x4699 | 18072 | 18073 | MAG_10M_HAR_I_105th_n_% | Aggr 10min Phase N 105th Current Magnitude Harmonics | float | 2 | R
0x469A | 0x469B | 18074 | 18075 | MAG_10M_HAR_V_106th_a_% | Aggr 10min Phase A 106th Voltage Magnitude Harmonics | float | 2 | R
0x469C | 0x469D | 18076 | 18077 | MAG_10M_HAR_V_106th_b_% | Aggr 10min Phase B 106th Voltage Magnitude Harmonics | float | 2 | R
0x469E | 0x469F | 18078 | 18079 | MAG_10M_HAR_V_106th_c_% | Aggr 10min Phase C 106th Voltage Magnitude Harmonics | float | 2 | R
0x46A0 | 0x46A1 | 18080 | 18081 | MAG_10M_HAR_I_106th_a_% | Aggr 10min Phase A 106th Current Magnitude Harmonics | float | 2 | R
0x46A2 | 0x46A3 | 18082 | 18083 | MAG_10M_HAR_I_106th_b_% | Aggr 10min Phase B 106th Current Magnitude Harmonics | float | 2 | R
0x46A4 | 0x46A5 | 18084 | 18085 | MAG_10M_HAR_I_106th_c_% | Aggr 10min Phase C 106th Current Magnitude Harmonics | float | 2 | R
0x46A6 | 0x46A7 | 18086 | 18087 | MAG_10M_HAR_I_106th_n_% | Aggr 10min Phase N 106th Current Magnitude Harmonics | float | 2 | R
0x46A8 | 0x46A9 | 18088 | 18089 | MAG_10M_HAR_V_107th_a_% | Aggr 10min Phase A 107th Voltage Magnitude Harmonics | float | 2 | R
0x46AA | 0x46AB | 18090 | 18091 | MAG_10M_HAR_V_107th_b_% | Aggr 10min Phase B 107th Voltage Magnitude Harmonics | float | 2 | R
0x46AC | 0x46AD | 18092 | 18093 | MAG_10M_HAR_V_107th_c_% | Aggr 10min Phase C 107th Voltage Magnitude Harmonics | float | 2 | R
0x46AE | 0x46AF | 18094 | 18095 | MAG_10M_HAR_I_107th_a_% | Aggr 10min Phase A 107th Current Magnitude Harmonics | float | 2 | R
0x46B0 | 0x46B1 | 18096 | 18097 | MAG_10M_HAR_I_107th_b_% | Aggr 10min Phase B 107th Current Magnitude Harmonics | float | 2 | R
0x46B2 | 0x46B3 | 18098 | 18099 | MAG_10M_HAR_I_107th_c_% | Aggr 10min Phase C 107th Current Magnitude Harmonics | float | 2 | R
0x46B4 | 0x46B5 | 18100 | 18101 | MAG_10M_HAR_I_107th_n_% | Aggr 10min Phase N 107th Current Magnitude Harmonics | float | 2 | R
0x46B6 | 0x46B7 | 18102 | 18103 | MAG_10M_HAR_V_108th_a_% | Aggr 10min Phase A 108th Voltage Magnitude Harmonics | float | 2 | R
0x46B8 | 0x46B9 | 18104 | 18105 | MAG_10M_HAR_V_108th_b_% | Aggr 10min Phase B 108th Voltage Magnitude Harmonics | float | 2 | R
0x46BA | 0x46BB | 18106 | 18107 | MAG_10M_HAR_V_108th_c_% | Aggr 10min Phase C 108th Voltage Magnitude Harmonics | float | 2 | R
0x46BC | 0x46BD | 18108 | 18109 | MAG_10M_HAR_I_108th_a_% | Aggr 10min Phase A 108th Current Magnitude Harmonics | float | 2 | R
0x46BE | 0x46BF | 18110 | 18111 | MAG_10M_HAR_I_108th_b_% | Aggr 10min Phase B 108th Current Magnitude Harmonics | float | 2 | R
0x46C0 | 0x46C1 | 18112 | 18113 | MAG_10M_HAR_I_108th_c_% | Aggr 10min Phase C 108th Current Magnitude Harmonics | float | 2 | R
0x46C2 | 0x46C3 | 18114 | 18115 | MAG_10M_HAR_I_108th_n_% | Aggr 10min Phase N 108th Current Magnitude Harmonics | float | 2 | R
0x46C4 | 0x46C5 | 18116 | 18117 | MAG_10M_HAR_V_109th_a_% | Aggr 10min Phase A 109th Voltage Magnitude Harmonics | float | 2 | R
0x46C6 | 0x46C7 | 18118 | 18119 | MAG_10M_HAR_V_109th_b_% | Aggr 10min Phase B 109th Voltage Magnitude Harmonics | float | 2 | R
0x46C8 | 0x46C9 | 18120 | 18121 | MAG_10M_HAR_V_109th_c_% | Aggr 10min Phase C 109th Voltage Magnitude Harmonics | float | 2 | R
0x46CA | 0x46CB | 18122 | 18123 | MAG_10M_HAR_I_109th_a_% | Aggr 10min Phase A 109th Current Magnitude Harmonics | float | 2 | R
0x46CC | 0x46CD | 18124 | 18125 | MAG_10M_HAR_I_109th_b_% | Aggr 10min Phase B 109th Current Magnitude Harmonics | float | 2 | R
0x46CE | 0x46CF | 18126 | 18127 | MAG_10M_HAR_I_109th_c_% | Aggr 10min Phase C 109th Current Magnitude Harmonics | float | 2 | R
0x46D0 | 0x46D1 | 18128 | 18129 | MAG_10M_HAR_I_109th_n_% | Aggr 10min Phase N 109th Current Magnitude Harmonics | float | 2 | R
0x46D2 | 0x46D3 | 18130 | 18131 | MAG_10M_HAR_V_110th_a_% | Aggr 10min Phase A 110th Voltage Magnitude Harmonics | float | 2 | R
0x46D4 | 0x46D5 | 18132 | 18133 | MAG_10M_HAR_V_110th_b_% | Aggr 10min Phase B 110th Voltage Magnitude Harmonics | float | 2 | R
0x46D6 | 0x46D7 | 18134 | 18135 | MAG_10M_HAR_V_110th_c_% | Aggr 10min Phase C 110th Voltage Magnitude Harmonics | float | 2 | R
0x46D8 | 0x46D9 | 18136 | 18137 | MAG_10M_HAR_I_110th_a_% | Aggr 10min Phase A 110th Current Magnitude Harmonics | float | 2 | R
0x46DA | 0x46DB | 18138 | 18139 | MAG_10M_HAR_I_110th_b_% | Aggr 10min Phase B 110th Current Magnitude Harmonics | float | 2 | R
0x46DC | 0x46DD | 18140 | 18141 | MAG_10M_HAR_I_110th_c_% | Aggr 10min Phase C 110th Current Magnitude Harmonics | float | 2 | R
0x46DE | 0x46DF | 18142 | 18143 | MAG_10M_HAR_I_110th_n_% | Aggr 10min Phase N 110th Current Magnitude Harmonics | float | 2 | R
0x46E0 | 0x46E1 | 18144 | 18145 | MAG_10M_HAR_V_111th_a_% | Aggr 10min Phase A 111st Voltage Magnitude Harmonics | float | 2 | R
0x46E2 | 0x46E3 | 18146 | 18147 | MAG_10M_HAR_V_111th_b_% | Aggr 10min Phase B 111st Voltage Magnitude Harmonics | float | 2 | R
0x46E4 | 0x46E5 | 18148 | 18149 | MAG_10M_HAR_V_111th_c_% | Aggr 10min Phase C 111st Voltage Magnitude Harmonics | float | 2 | R
0x46E6 | 0x46E7 | 18150 | 18151 | MAG_10M_HAR_I_111th_a_% | Aggr 10min Phase A 111st Current Magnitude Harmonics | float | 2 | R
0x46E8 | 0x46E9 | 18152 | 18153 | MAG_10M_HAR_I_111th_b_% | Aggr 10min Phase B 111st Current Magnitude Harmonics | float | 2 | R
0x46EA | 0x46EB | 18154 | 18155 | MAG_10M_HAR_I_111th_c_% | Aggr 10min Phase C 111st Current Magnitude Harmonics | float | 2 | R
0x46EC | 0x46ED | 18156 | 18157 | MAG_10M_HAR_I_111th_n_% | Aggr 10min Phase N 111st Current Magnitude Harmonics | float | 2 | R
0x46EE | 0x46EF | 18158 | 18159 | MAG_10M_HAR_V_112th_a_% | Aggr 10min Phase A 112nd Voltage Magnitude Harmonics | float | 2 | R
0x46F0 | 0x46F1 | 18160 | 18161 | MAG_10M_HAR_V_112th_b_% | Aggr 10min Phase B 112nd Voltage Magnitude Harmonics | float | 2 | R
0x46F2 | 0x46F3 | 18162 | 18163 | MAG_10M_HAR_V_112th_c_% | Aggr 10min Phase C 112nd Voltage Magnitude Harmonics | float | 2 | R
0x46F4 | 0x46F5 | 18164 | 18165 | MAG_10M_HAR_I_112th_a_% | Aggr 10min Phase A 112nd Current Magnitude Harmonics | float | 2 | R
0x46F6 | 0x46F7 | 18166 | 18167 | MAG_10M_HAR_I_112th_b_% | Aggr 10min Phase B 112nd Current Magnitude Harmonics | float | 2 | R
0x46F8 | 0x46F9 | 18168 | 18169 | MAG_10M_HAR_I_112th_c_% | Aggr 10min Phase C 112nd Current Magnitude Harmonics | float | 2 | R
0x46FA | 0x46FB | 18170 | 18171 | MAG_10M_HAR_I_112th_n_% | Aggr 10min Phase N 112nd Current Magnitude Harmonics | float | 2 | R
0x46FC | 0x46FD | 18172 | 18173 | MAG_10M_HAR_V_113th_a_% | Aggr 10min Phase A 113rd Voltage Magnitude Harmonics | float | 2 | R
0x46FE | 0x46FF | 18174 | 18175 | MAG_10M_HAR_V_113th_b_% | Aggr 10min Phase B 113rd Voltage Magnitude Harmonics | float | 2 | R
0x4700 | 0x4701 | 18176 | 18177 | MAG_10M_HAR_V_113th_c_% | Aggr 10min Phase C 113rd Voltage Magnitude Harmonics | float | 2 | R
0x4702 | 0x4703 | 18178 | 18179 | MAG_10M_HAR_I_113th_a_% | Aggr 10min Phase A 113rd Current Magnitude Harmonics | float | 2 | R
0x4704 | 0x4705 | 18180 | 18181 | MAG_10M_HAR_I_113th_b_% | Aggr 10min Phase B 113rd Current Magnitude Harmonics | float | 2 | R
0x4706 | 0x4707 | 18182 | 18183 | MAG_10M_HAR_I_113th_c_% | Aggr 10min Phase C 113rd Current Magnitude Harmonics | float | 2 | R
0x4708 | 0x4709 | 18184 | 18185 | MAG_10M_HAR_I_113th_n_% | Aggr 10min Phase N 113rd Current Magnitude Harmonics | float | 2 | R
0x470A | 0x470B | 18186 | 18187 | MAG_10M_HAR_V_114th_a_% | Aggr 10min Phase A 114th Voltage Magnitude Harmonics | float | 2 | R
0x470C | 0x470D | 18188 | 18189 | MAG_10M_HAR_V_114th_b_% | Aggr 10min Phase B 114th Voltage Magnitude Harmonics | float | 2 | R
0x470E | 0x470F | 18190 | 18191 | MAG_10M_HAR_V_114th_c_% | Aggr 10min Phase C 114th Voltage Magnitude Harmonics | float | 2 | R
0x4710 | 0x4711 | 18192 | 18193 | MAG_10M_HAR_I_114th_a_% | Aggr 10min Phase A 114th Current Magnitude Harmonics | float | 2 | R
0x4712 | 0x4713 | 18194 | 18195 | MAG_10M_HAR_I_114th_b_% | Aggr 10min Phase B 114th Current Magnitude Harmonics | float | 2 | R
0x4714 | 0x4715 | 18196 | 18197 | MAG_10M_HAR_I_114th_c_% | Aggr 10min Phase C 114th Current Magnitude Harmonics | float | 2 | R
0x4716 | 0x4717 | 18198 | 18199 | MAG_10M_HAR_I_114th_n_% | Aggr 10min Phase N 114th Current Magnitude Harmonics | float | 2 | R
0x4718 | 0x4719 | 18200 | 18201 | MAG_10M_HAR_V_115th_a_% | Aggr 10min Phase A 115th Voltage Magnitude Harmonics | float | 2 | R
0x471A | 0x471B | 18202 | 18203 | MAG_10M_HAR_V_115th_b_% | Aggr 10min Phase B 115th Voltage Magnitude Harmonics | float | 2 | R
0x471C | 0x471D | 18204 | 18205 | MAG_10M_HAR_V_115th_c_% | Aggr 10min Phase C 115th Voltage Magnitude Harmonics | float | 2 | R
0x471E | 0x471F | 18206 | 18207 | MAG_10M_HAR_I_115th_a_% | Aggr 10min Phase A 115th Current Magnitude Harmonics | float | 2 | R
0x4720 | 0x4721 | 18208 | 18209 | MAG_10M_HAR_I_115th_b_% | Aggr 10min Phase B 115th Current Magnitude Harmonics | float | 2 | R
0x4722 | 0x4723 | 18210 | 18211 | MAG_10M_HAR_I_115th_c_% | Aggr 10min Phase C 115th Current Magnitude Harmonics | float | 2 | R
0x4724 | 0x4725 | 18212 | 18213 | MAG_10M_HAR_I_115th_n_% | Aggr 10min Phase N 115th Current Magnitude Harmonics | float | 2 | R
0x4726 | 0x4727 | 18214 | 18215 | MAG_10M_HAR_V_116th_a_% | Aggr 10min Phase A 116th Voltage Magnitude Harmonics | float | 2 | R
0x4728 | 0x4729 | 18216 | 18217 | MAG_10M_HAR_V_116th_b_% | Aggr 10min Phase B 116th Voltage Magnitude Harmonics | float | 2 | R
0x472A | 0x472B | 18218 | 18219 | MAG_10M_HAR_V_116th_c_% | Aggr 10min Phase C 116th Voltage Magnitude Harmonics | float | 2 | R
0x472C | 0x472D | 18220 | 18221 | MAG_10M_HAR_I_116th_a_% | Aggr 10min Phase A 116th Current Magnitude Harmonics | float | 2 | R
0x472E | 0x472F | 18222 | 18223 | MAG_10M_HAR_I_116th_b_% | Aggr 10min Phase B 116th Current Magnitude Harmonics | float | 2 | R
0x4730 | 0x4731 | 18224 | 18225 | MAG_10M_HAR_I_116th_c_% | Aggr 10min Phase C 116th Current Magnitude Harmonics | float | 2 | R
0x4732 | 0x4733 | 18226 | 18227 | MAG_10M_HAR_I_116th_n_% | Aggr 10min Phase N 116th Current Magnitude Harmonics | float | 2 | R
0x4734 | 0x4735 | 18228 | 18229 | MAG_10M_HAR_V_117th_a_% | Aggr 10min Phase A 117th Voltage Magnitude Harmonics | float | 2 | R
0x4736 | 0x4737 | 18230 | 18231 | MAG_10M_HAR_V_117th_b_% | Aggr 10min Phase B 117th Voltage Magnitude Harmonics | float | 2 | R
0x4738 | 0x4739 | 18232 | 18233 | MAG_10M_HAR_V_117th_c_% | Aggr 10min Phase C 117th Voltage Magnitude Harmonics | float | 2 | R
0x473A | 0x473B | 18234 | 18235 | MAG_10M_HAR_I_117th_a_% | Aggr 10min Phase A 117th Current Magnitude Harmonics | float | 2 | R
0x473C | 0x473D | 18236 | 18237 | MAG_10M_HAR_I_117th_b_% | Aggr 10min Phase B 117th Current Magnitude Harmonics | float | 2 | R
0x473E | 0x473F | 18238 | 18239 | MAG_10M_HAR_I_117th_c_% | Aggr 10min Phase C 117th Current Magnitude Harmonics | float | 2 | R
0x4740 | 0x4741 | 18240 | 18241 | MAG_10M_HAR_I_117th_n_% | Aggr 10min Phase N 117th Current Magnitude Harmonics | float | 2 | R
0x4742 | 0x4743 | 18242 | 18243 | MAG_10M_HAR_V_118th_a_% | Aggr 10min Phase A 118th Voltage Magnitude Harmonics | float | 2 | R
0x4744 | 0x4745 | 18244 | 18245 | MAG_10M_HAR_V_118th_b_% | Aggr 10min Phase B 118th Voltage Magnitude Harmonics | float | 2 | R
0x4746 | 0x4747 | 18246 | 18247 | MAG_10M_HAR_V_118th_c_% | Aggr 10min Phase C 118th Voltage Magnitude Harmonics | float | 2 | R
0x4748 | 0x4749 | 18248 | 18249 | MAG_10M_HAR_I_118th_a_% | Aggr 10min Phase A 118th Current Magnitude Harmonics | float | 2 | R
0x474A | 0x474B | 18250 | 18251 | MAG_10M_HAR_I_118th_b_% | Aggr 10min Phase B 118th Current Magnitude Harmonics | float | 2 | R
0x474C | 0x474D | 18252 | 18253 | MAG_10M_HAR_I_118th_c_% | Aggr 10min Phase C 118th Current Magnitude Harmonics | float | 2 | R
0x474E | 0x474F | 18254 | 18255 | MAG_10M_HAR_I_118th_n_% | Aggr 10min Phase N 118th Current Magnitude Harmonics | float | 2 | R
0x4750 | 0x4751 | 18256 | 18257 | MAG_10M_HAR_V_119th_a_% | Aggr 10min Phase A 119th Voltage Magnitude Harmonics | float | 2 | R
0x4752 | 0x4753 | 18258 | 18259 | MAG_10M_HAR_V_119th_b_% | Aggr 10min Phase B 119th Voltage Magnitude Harmonics | float | 2 | R
0x4754 | 0x4755 | 18260 | 18261 | MAG_10M_HAR_V_119th_c_% | Aggr 10min Phase C 119th Voltage Magnitude Harmonics | float | 2 | R
0x4756 | 0x4757 | 18262 | 18263 | MAG_10M_HAR_I_119th_a_% | Aggr 10min Phase A 119th Current Magnitude Harmonics | float | 2 | R
0x4758 | 0x4759 | 18264 | 18265 | MAG_10M_HAR_I_119th_b_% | Aggr 10min Phase B 119th Current Magnitude Harmonics | float | 2 | R
0x475A | 0x475B | 18266 | 18267 | MAG_10M_HAR_I_119th_c_% | Aggr 10min Phase C 119th Current Magnitude Harmonics | float | 2 | R
0x475C | 0x475D | 18268 | 18269 | MAG_10M_HAR_I_119th_n_% | Aggr 10min Phase N 119th Current Magnitude Harmonics | float | 2 | R
0x475E | 0x475F | 18270 | 18271 | MAG_10M_HAR_V_120th_a_% | Aggr 10min Phase A 120th Voltage Magnitude Harmonics | float | 2 | R
0x4760 | 0x4761 | 18272 | 18273 | MAG_10M_HAR_V_120th_b_% | Aggr 10min Phase B 120th Voltage Magnitude Harmonics | float | 2 | R
0x4762 | 0x4763 | 18274 | 18275 | MAG_10M_HAR_V_120th_c_% | Aggr 10min Phase C 120th Voltage Magnitude Harmonics | float | 2 | R
0x4764 | 0x4765 | 18276 | 18277 | MAG_10M_HAR_I_120th_a_% | Aggr 10min Phase A 120th Current Magnitude Harmonics | float | 2 | R
0x4766 | 0x4767 | 18278 | 18279 | MAG_10M_HAR_I_120th_b_% | Aggr 10min Phase B 120th Current Magnitude Harmonics | float | 2 | R
0x4768 | 0x4769 | 18280 | 18281 | MAG_10M_HAR_I_120th_c_% | Aggr 10min Phase C 120th Current Magnitude Harmonics | float | 2 | R
0x476A | 0x476B | 18282 | 18283 | MAG_10M_HAR_I_120th_n_% | Aggr 10min Phase N 120th Current Magnitude Harmonics | float | 2 | R
0x476C | 0x476D | 18284 | 18285 | MAG_10M_HAR_V_121th_a_% | Aggr 10min Phase A 121st Voltage Magnitude Harmonics | float | 2 | R
0x476E | 0x476F | 18286 | 18287 | MAG_10M_HAR_V_121th_b_% | Aggr 10min Phase B 121st Voltage Magnitude Harmonics | float | 2 | R
0x4770 | 0x4771 | 18288 | 18289 | MAG_10M_HAR_V_121th_c_% | Aggr 10min Phase C 121st Voltage Magnitude Harmonics | float | 2 | R
0x4772 | 0x4773 | 18290 | 18291 | MAG_10M_HAR_I_121th_a_% | Aggr 10min Phase A 121st Current Magnitude Harmonics | float | 2 | R
0x4774 | 0x4775 | 18292 | 18293 | MAG_10M_HAR_I_121th_b_% | Aggr 10min Phase B 121st Current Magnitude Harmonics | float | 2 | R
0x4776 | 0x4777 | 18294 | 18295 | MAG_10M_HAR_I_121th_c_% | Aggr 10min Phase C 121st Current Magnitude Harmonics | float | 2 | R
0x4778 | 0x4779 | 18296 | 18297 | MAG_10M_HAR_I_121th_n_% | Aggr 10min Phase N 121st Current Magnitude Harmonics | float | 2 | R
0x477A | 0x477B | 18298 | 18299 | MAG_10M_HAR_V_122th_a_% | Aggr 10min Phase A 122nd Voltage Magnitude Harmonics | float | 2 | R
0x477C | 0x477D | 18300 | 18301 | MAG_10M_HAR_V_122th_b_% | Aggr 10min Phase B 122nd Voltage Magnitude Harmonics | float | 2 | R
0x477E | 0x477F | 18302 | 18303 | MAG_10M_HAR_V_122th_c_% | Aggr 10min Phase C 122nd Voltage Magnitude Harmonics | float | 2 | R
0x4780 | 0x4781 | 18304 | 18305 | MAG_10M_HAR_I_122th_a_% | Aggr 10min Phase A 122nd Current Magnitude Harmonics | float | 2 | R
0x4782 | 0x4783 | 18306 | 18307 | MAG_10M_HAR_I_122th_b_% | Aggr 10min Phase B 122nd Current Magnitude Harmonics | float | 2 | R
0x4784 | 0x4785 | 18308 | 18309 | MAG_10M_HAR_I_122th_c_% | Aggr 10min Phase C 122nd Current Magnitude Harmonics | float | 2 | R
0x4786 | 0x4787 | 18310 | 18311 | MAG_10M_HAR_I_122th_n_% | Aggr 10min Phase N 122nd Current Magnitude Harmonics | float | 2 | R
0x4788 | 0x4789 | 18312 | 18313 | MAG_10M_HAR_V_123th_a_% | Aggr 10min Phase A 123rd Voltage Magnitude Harmonics | float | 2 | R
0x478A | 0x478B | 18314 | 18315 | MAG_10M_HAR_V_123th_b_% | Aggr 10min Phase B 123rd Voltage Magnitude Harmonics | float | 2 | R
0x478C | 0x478D | 18316 | 18317 | MAG_10M_HAR_V_123th_c_% | Aggr 10min Phase C 123rd Voltage Magnitude Harmonics | float | 2 | R
0x478E | 0x478F | 18318 | 18319 | MAG_10M_HAR_I_123th_a_% | Aggr 10min Phase A 123rd Current Magnitude Harmonics | float | 2 | R
0x4790 | 0x4791 | 18320 | 18321 | MAG_10M_HAR_I_123th_b_% | Aggr 10min Phase B 123rd Current Magnitude Harmonics | float | 2 | R
0x4792 | 0x4793 | 18322 | 18323 | MAG_10M_HAR_I_123th_c_% | Aggr 10min Phase C 123rd Current Magnitude Harmonics | float | 2 | R
0x4794 | 0x4795 | 18324 | 18325 | MAG_10M_HAR_I_123th_n_% | Aggr 10min Phase N 123rd Current Magnitude Harmonics | float | 2 | R
0x4796 | 0x4797 | 18326 | 18327 | MAG_10M_HAR_V_124th_a_% | Aggr 10min Phase A 124th Voltage Magnitude Harmonics | float | 2 | R
0x4798 | 0x4799 | 18328 | 18329 | MAG_10M_HAR_V_124th_b_% | Aggr 10min Phase B 124th Voltage Magnitude Harmonics | float | 2 | R
0x479A | 0x479B | 18330 | 18331 | MAG_10M_HAR_V_124th_c_% | Aggr 10min Phase C 124th Voltage Magnitude Harmonics | float | 2 | R
0x479C | 0x479D | 18332 | 18333 | MAG_10M_HAR_I_124th_a_% | Aggr 10min Phase A 124th Current Magnitude Harmonics | float | 2 | R
0x479E | 0x479F | 18334 | 18335 | MAG_10M_HAR_I_124th_b_% | Aggr 10min Phase B 124th Current Magnitude Harmonics | float | 2 | R
0x47A0 | 0x47A1 | 18336 | 18337 | MAG_10M_HAR_I_124th_c_% | Aggr 10min Phase C 124th Current Magnitude Harmonics | float | 2 | R
0x47A2 | 0x47A3 | 18338 | 18339 | MAG_10M_HAR_I_124th_n_% | Aggr 10min Phase N 124th Current Magnitude Harmonics | float | 2 | R
0x47A4 | 0x47A5 | 18340 | 18341 | MAG_10M_HAR_V_125th_a_% | Aggr 10min Phase A 125th Voltage Magnitude Harmonics | float | 2 | R
0x47A6 | 0x47A7 | 18342 | 18343 | MAG_10M_HAR_V_125th_b_% | Aggr 10min Phase B 125th Voltage Magnitude Harmonics | float | 2 | R
0x47A8 | 0x47A9 | 18344 | 18345 | MAG_10M_HAR_V_125th_c_% | Aggr 10min Phase C 125th Voltage Magnitude Harmonics | float | 2 | R
0x47AA | 0x47AB | 18346 | 18347 | MAG_10M_HAR_I_125th_a_% | Aggr 10min Phase A 125th Current Magnitude Harmonics | float | 2 | R
0x47AC | 0x47AD | 18348 | 18349 | MAG_10M_HAR_I_125th_b_% | Aggr 10min Phase B 125th Current Magnitude Harmonics | float | 2 | R
0x47AE | 0x47AF | 18350 | 18351 | MAG_10M_HAR_I_125th_c_% | Aggr 10min Phase C 125th Current Magnitude Harmonics | float | 2 | R
0x47B0 | 0x47B1 | 18352 | 18353 | MAG_10M_HAR_I_125th_n_% | Aggr 10min Phase N 125th Current Magnitude Harmonics | float | 2 | R
0x47B2 | 0x47B3 | 18354 | 18355 | MAG_10M_HAR_V_126th_a_% | Aggr 10min Phase A 126th Voltage Magnitude Harmonics | float | 2 | R
0x47B4 | 0x47B5 | 18356 | 18357 | MAG_10M_HAR_V_126th_b_% | Aggr 10min Phase B 126th Voltage Magnitude Harmonics | float | 2 | R
0x47B6 | 0x47B7 | 18358 | 18359 | MAG_10M_HAR_V_126th_c_% | Aggr 10min Phase C 126th Voltage Magnitude Harmonics | float | 2 | R
0x47B8 | 0x47B9 | 18360 | 18361 | MAG_10M_HAR_I_126th_a_% | Aggr 10min Phase A 126th Current Magnitude Harmonics | float | 2 | R
0x47BA | 0x47BB | 18362 | 18363 | MAG_10M_HAR_I_126th_b_% | Aggr 10min Phase B 126th Current Magnitude Harmonics | float | 2 | R
0x47BC | 0x47BD | 18364 | 18365 | MAG_10M_HAR_I_126th_c_% | Aggr 10min Phase C 126th Current Magnitude Harmonics | float | 2 | R
0x47BE | 0x47BF | 18366 | 18367 | MAG_10M_HAR_I_126th_n_% | Aggr 10min Phase N 126th Current Magnitude Harmonics | float | 2 | R
0x47C0 | 0x47C1 | 18368 | 18369 | MAG_10M_HAR_V_127th_a_% | Aggr 10min Phase A 127th Voltage Magnitude Harmonics | float | 2 | R
0x47C2 | 0x47C3 | 18370 | 18371 | MAG_10M_HAR_V_127th_b_% | Aggr 10min Phase B 127th Voltage Magnitude Harmonics | float | 2 | R
0x47C4 | 0x47C5 | 18372 | 18373 | MAG_10M_HAR_V_127th_c_% | Aggr 10min Phase C 127th Voltage Magnitude Harmonics | float | 2 | R
0x47C6 | 0x47C7 | 18374 | 18375 | MAG_10M_HAR_I_127th_a_% | Aggr 10min Phase A 127th Current Magnitude Harmonics | float | 2 | R
0x47C8 | 0x47C9 | 18376 | 18377 | MAG_10M_HAR_I_127th_b_% | Aggr 10min Phase B 127th Current Magnitude Harmonics | float | 2 | R
0x47CA | 0x47CB | 18378 | 18379 | MAG_10M_HAR_I_127th_c_% | Aggr 10min Phase C 127th Current Magnitude Harmonics | float | 2 | R
0x47CC | 0x47CD | 18380 | 18381 | MAG_10M_HAR_I_127th_n_% | Aggr 10min Phase N 127th Current Magnitude Harmonics | float | 2 | R
0x47CE | 0x47CF | 18382 | 18383 | ANG_10M_HAR_V_1th_a | Aggr 10min Phase A 1st Voltage Angle Harmonics | float | 2 | R
0x47D0 | 0x47D1 | 18384 | 18385 | ANG_10M_HAR_V_1th_b | Aggr 10min Phase B 1st Voltage Angle Harmonics | float | 2 | R
0x47D2 | 0x47D3 | 18386 | 18387 | ANG_10M_HAR_V_1th_c | Aggr 10min Phase C 1st Voltage Angle Harmonics | float | 2 | R
0x47D4 | 0x47D5 | 18388 | 18389 | ANG_10M_HAR_I_1th_a | Aggr 10min Phase A 1st Current Angle Harmonics | float | 2 | R
0x47D6 | 0x47D7 | 18390 | 18391 | ANG_10M_HAR_I_1th_b | Aggr 10min Phase B 1st Current Angle Harmonics | float | 2 | R
0x47D8 | 0x47D9 | 18392 | 18393 | ANG_10M_HAR_I_1th_c | Aggr 10min Phase C 1st Current Angle Harmonics | float | 2 | R
0x47DA | 0x47DB | 18394 | 18395 | ANG_10M_HAR_I_1th_n | Aggr 10min Phase N 1st Current Angle Harmonics | float | 2 | R
0x47DC | 0x47DD | 18396 | 18397 | ANG_10M_HAR_V_2th_a | Aggr 10min Phase A 2nd Voltage Angle Harmonics | float | 2 | R
0x47DE | 0x47DF | 18398 | 18399 | ANG_10M_HAR_V_2th_b | Aggr 10min Phase B 2nd Voltage Angle Harmonics | float | 2 | R
0x47E0 | 0x47E1 | 18400 | 18401 | ANG_10M_HAR_V_2th_c | Aggr 10min Phase C 2nd Voltage Angle Harmonics | float | 2 | R
0x47E2 | 0x47E3 | 18402 | 18403 | ANG_10M_HAR_I_2th_a | Aggr 10min Phase A 2nd Current Angle Harmonics | float | 2 | R
0x47E4 | 0x47E5 | 18404 | 18405 | ANG_10M_HAR_I_2th_b | Aggr 10min Phase B 2nd Current Angle Harmonics | float | 2 | R
0x47E6 | 0x47E7 | 18406 | 18407 | ANG_10M_HAR_I_2th_c | Aggr 10min Phase C 2nd Current Angle Harmonics | float | 2 | R
0x47E8 | 0x47E9 | 18408 | 18409 | ANG_10M_HAR_I_2th_n | Aggr 10min Phase N 2nd Current Angle Harmonics | float | 2 | R
0x47EA | 0x47EB | 18410 | 18411 | ANG_10M_HAR_V_3th_a | Aggr 10min Phase A 3rd Voltage Angle Harmonics | float | 2 | R
0x47EC | 0x47ED | 18412 | 18413 | ANG_10M_HAR_V_3th_b | Aggr 10min Phase B 3rd Voltage Angle Harmonics | float | 2 | R
0x47EE | 0x47EF | 18414 | 18415 | ANG_10M_HAR_V_3th_c | Aggr 10min Phase C 3rd Voltage Angle Harmonics | float | 2 | R
0x47F0 | 0x47F1 | 18416 | 18417 | ANG_10M_HAR_I_3th_a | Aggr 10min Phase A 3rd Current Angle Harmonics | float | 2 | R
0x47F2 | 0x47F3 | 18418 | 18419 | ANG_10M_HAR_I_3th_b | Aggr 10min Phase B 3rd Current Angle Harmonics | float | 2 | R
0x47F4 | 0x47F5 | 18420 | 18421 | ANG_10M_HAR_I_3th_c | Aggr 10min Phase C 3rd Current Angle Harmonics | float | 2 | R
0x47F6 | 0x47F7 | 18422 | 18423 | ANG_10M_HAR_I_3th_n | Aggr 10min Phase N 3rd Current Angle Harmonics | float | 2 | R
0x47F8 | 0x47F9 | 18424 | 18425 | ANG_10M_HAR_V_4th_a | Aggr 10min Phase A 4th Voltage Angle Harmonics | float | 2 | R
0x47FA | 0x47FB | 18426 | 18427 | ANG_10M_HAR_V_4th_b | Aggr 10min Phase B 4th Voltage Angle Harmonics | float | 2 | R
0x47FC | 0x47FD | 18428 | 18429 | ANG_10M_HAR_V_4th_c | Aggr 10min Phase C 4th Voltage Angle Harmonics | float | 2 | R
0x47FE | 0x47FF | 18430 | 18431 | ANG_10M_HAR_I_4th_a | Aggr 10min Phase A 4th Current Angle Harmonics | float | 2 | R
0x4800 | 0x4801 | 18432 | 18433 | ANG_10M_HAR_I_4th_b | Aggr 10min Phase B 4th Current Angle Harmonics | float | 2 | R
0x4802 | 0x4803 | 18434 | 18435 | ANG_10M_HAR_I_4th_c | Aggr 10min Phase C 4th Current Angle Harmonics | float | 2 | R
0x4804 | 0x4805 | 18436 | 18437 | ANG_10M_HAR_I_4th_n | Aggr 10min Phase N 4th Current Angle Harmonics | float | 2 | R
0x4806 | 0x4807 | 18438 | 18439 | ANG_10M_HAR_V_5th_a | Aggr 10min Phase A 5th Voltage Angle Harmonics | float | 2 | R
0x4808 | 0x4809 | 18440 | 18441 | ANG_10M_HAR_V_5th_b | Aggr 10min Phase B 5th Voltage Angle Harmonics | float | 2 | R
0x480A | 0x480B | 18442 | 18443 | ANG_10M_HAR_V_5th_c | Aggr 10min Phase C 5th Voltage Angle Harmonics | float | 2 | R
0x480C | 0x480D | 18444 | 18445 | ANG_10M_HAR_I_5th_a | Aggr 10min Phase A 5th Current Angle Harmonics | float | 2 | R
0x480E | 0x480F | 18446 | 18447 | ANG_10M_HAR_I_5th_b | Aggr 10min Phase B 5th Current Angle Harmonics | float | 2 | R
0x4810 | 0x4811 | 18448 | 18449 | ANG_10M_HAR_I_5th_c | Aggr 10min Phase C 5th Current Angle Harmonics | float | 2 | R
0x4812 | 0x4813 | 18450 | 18451 | ANG_10M_HAR_I_5th_n | Aggr 10min Phase N 5th Current Angle Harmonics | float | 2 | R
0x4814 | 0x4815 | 18452 | 18453 | ANG_10M_HAR_V_6th_a | Aggr 10min Phase A 6th Voltage Angle Harmonics | float | 2 | R
0x4816 | 0x4817 | 18454 | 18455 | ANG_10M_HAR_V_6th_b | Aggr 10min Phase B 6th Voltage Angle Harmonics | float | 2 | R
0x4818 | 0x4819 | 18456 | 18457 | ANG_10M_HAR_V_6th_c | Aggr 10min Phase C 6th Voltage Angle Harmonics | float | 2 | R
0x481A | 0x481B | 18458 | 18459 | ANG_10M_HAR_I_6th_a | Aggr 10min Phase A 6th Current Angle Harmonics | float | 2 | R
0x481C | 0x481D | 18460 | 18461 | ANG_10M_HAR_I_6th_b | Aggr 10min Phase B 6th Current Angle Harmonics | float | 2 | R
0x481E | 0x481F | 18462 | 18463 | ANG_10M_HAR_I_6th_c | Aggr 10min Phase C 6th Current Angle Harmonics | float | 2 | R
0x4820 | 0x4821 | 18464 | 18465 | ANG_10M_HAR_I_6th_n | Aggr 10min Phase N 6th Current Angle Harmonics | float | 2 | R
0x4822 | 0x4823 | 18466 | 18467 | ANG_10M_HAR_V_7th_a | Aggr 10min Phase A 7th Voltage Angle Harmonics | float | 2 | R
0x4824 | 0x4825 | 18468 | 18469 | ANG_10M_HAR_V_7th_b | Aggr 10min Phase B 7th Voltage Angle Harmonics | float | 2 | R
0x4826 | 0x4827 | 18470 | 18471 | ANG_10M_HAR_V_7th_c | Aggr 10min Phase C 7th Voltage Angle Harmonics | float | 2 | R
0x4828 | 0x4829 | 18472 | 18473 | ANG_10M_HAR_I_7th_a | Aggr 10min Phase A 7th Current Angle Harmonics | float | 2 | R
0x482A | 0x482B | 18474 | 18475 | ANG_10M_HAR_I_7th_b | Aggr 10min Phase B 7th Current Angle Harmonics | float | 2 | R
0x482C | 0x482D | 18476 | 18477 | ANG_10M_HAR_I_7th_c | Aggr 10min Phase C 7th Current Angle Harmonics | float | 2 | R
0x482E | 0x482F | 18478 | 18479 | ANG_10M_HAR_I_7th_n | Aggr 10min Phase N 7th Current Angle Harmonics | float | 2 | R
0x4830 | 0x4831 | 18480 | 18481 | ANG_10M_HAR_V_8th_a | Aggr 10min Phase A 8th Voltage Angle Harmonics | float | 2 | R
0x4832 | 0x4833 | 18482 | 18483 | ANG_10M_HAR_V_8th_b | Aggr 10min Phase B 8th Voltage Angle Harmonics | float | 2 | R
0x4834 | 0x4835 | 18484 | 18485 | ANG_10M_HAR_V_8th_c | Aggr 10min Phase C 8th Voltage Angle Harmonics | float | 2 | R
0x4836 | 0x4837 | 18486 | 18487 | ANG_10M_HAR_I_8th_a | Aggr 10min Phase A 8th Current Angle Harmonics | float | 2 | R
0x4838 | 0x4839 | 18488 | 18489 | ANG_10M_HAR_I_8th_b | Aggr 10min Phase B 8th Current Angle Harmonics | float | 2 | R
0x483A | 0x483B | 18490 | 18491 | ANG_10M_HAR_I_8th_c | Aggr 10min Phase C 8th Current Angle Harmonics | float | 2 | R
0x483C | 0x483D | 18492 | 18493 | ANG_10M_HAR_I_8th_n | Aggr 10min Phase N 8th Current Angle Harmonics | float | 2 | R
0x483E | 0x483F | 18494 | 18495 | ANG_10M_HAR_V_9th_a | Aggr 10min Phase A 9th Voltage Angle Harmonics | float | 2 | R
0x4840 | 0x4841 | 18496 | 18497 | ANG_10M_HAR_V_9th_b | Aggr 10min Phase B 9th Voltage Angle Harmonics | float | 2 | R
0x4842 | 0x4843 | 18498 | 18499 | ANG_10M_HAR_V_9th_c | Aggr 10min Phase C 9th Voltage Angle Harmonics | float | 2 | R
0x4844 | 0x4845 | 18500 | 18501 | ANG_10M_HAR_I_9th_a | Aggr 10min Phase A 9th Current Angle Harmonics | float | 2 | R
0x4846 | 0x4847 | 18502 | 18503 | ANG_10M_HAR_I_9th_b | Aggr 10min Phase B 9th Current Angle Harmonics | float | 2 | R
0x4848 | 0x4849 | 18504 | 18505 | ANG_10M_HAR_I_9th_c | Aggr 10min Phase C 9th Current Angle Harmonics | float | 2 | R
0x484A | 0x484B | 18506 | 18507 | ANG_10M_HAR_I_9th_n | Aggr 10min Phase N 9th Current Angle Harmonics | float | 2 | R
0x484C | 0x484D | 18508 | 18509 | ANG_10M_HAR_V_10th_a | Aggr 10min Phase A 10th Voltage Angle Harmonics | float | 2 | R
0x484E | 0x484F | 18510 | 18511 | ANG_10M_HAR_V_10th_b | Aggr 10min Phase B 10th Voltage Angle Harmonics | float | 2 | R
0x4850 | 0x4851 | 18512 | 18513 | ANG_10M_HAR_V_10th_c | Aggr 10min Phase C 10th Voltage Angle Harmonics | float | 2 | R
0x4852 | 0x4853 | 18514 | 18515 | ANG_10M_HAR_I_10th_a | Aggr 10min Phase A 10th Current Angle Harmonics | float | 2 | R
0x4854 | 0x4855 | 18516 | 18517 | ANG_10M_HAR_I_10th_b | Aggr 10min Phase B 10th Current Angle Harmonics | float | 2 | R
0x4856 | 0x4857 | 18518 | 18519 | ANG_10M_HAR_I_10th_c | Aggr 10min Phase C 10th Current Angle Harmonics | float | 2 | R
0x4858 | 0x4859 | 18520 | 18521 | ANG_10M_HAR_I_10th_n | Aggr 10min Phase N 10th Current Angle Harmonics | float | 2 | R
0x485A | 0x485B | 18522 | 18523 | ANG_10M_HAR_V_11th_a | Aggr 10min Phase A 11st Voltage Angle Harmonics | float | 2 | R
0x485C | 0x485D | 18524 | 18525 | ANG_10M_HAR_V_11th_b | Aggr 10min Phase B 11st Voltage Angle Harmonics | float | 2 | R
0x485E | 0x485F | 18526 | 18527 | ANG_10M_HAR_V_11th_c | Aggr 10min Phase C 11st Voltage Angle Harmonics | float | 2 | R
0x4860 | 0x4861 | 18528 | 18529 | ANG_10M_HAR_I_11th_a | Aggr 10min Phase A 11st Current Angle Harmonics | float | 2 | R
0x4862 | 0x4863 | 18530 | 18531 | ANG_10M_HAR_I_11th_b | Aggr 10min Phase B 11st Current Angle Harmonics | float | 2 | R
0x4864 | 0x4865 | 18532 | 18533 | ANG_10M_HAR_I_11th_c | Aggr 10min Phase C 11st Current Angle Harmonics | float | 2 | R
0x4866 | 0x4867 | 18534 | 18535 | ANG_10M_HAR_I_11th_n | Aggr 10min Phase N 11st Current Angle Harmonics | float | 2 | R
0x4868 | 0x4869 | 18536 | 18537 | ANG_10M_HAR_V_12th_a | Aggr 10min Phase A 12nd Voltage Angle Harmonics | float | 2 | R
0x486A | 0x486B | 18538 | 18539 | ANG_10M_HAR_V_12th_b | Aggr 10min Phase B 12nd Voltage Angle Harmonics | float | 2 | R
0x486C | 0x486D | 18540 | 18541 | ANG_10M_HAR_V_12th_c | Aggr 10min Phase C 12nd Voltage Angle Harmonics | float | 2 | R
0x486E | 0x486F | 18542 | 18543 | ANG_10M_HAR_I_12th_a | Aggr 10min Phase A 12nd Current Angle Harmonics | float | 2 | R
0x4870 | 0x4871 | 18544 | 18545 | ANG_10M_HAR_I_12th_b | Aggr 10min Phase B 12nd Current Angle Harmonics | float | 2 | R
0x4872 | 0x4873 | 18546 | 18547 | ANG_10M_HAR_I_12th_c | Aggr 10min Phase C 12nd Current Angle Harmonics | float | 2 | R
0x4874 | 0x4875 | 18548 | 18549 | ANG_10M_HAR_I_12th_n | Aggr 10min Phase N 12nd Current Angle Harmonics | float | 2 | R
0x4876 | 0x4877 | 18550 | 18551 | ANG_10M_HAR_V_13th_a | Aggr 10min Phase A 13rd Voltage Angle Harmonics | float | 2 | R
0x4878 | 0x4879 | 18552 | 18553 | ANG_10M_HAR_V_13th_b | Aggr 10min Phase B 13rd Voltage Angle Harmonics | float | 2 | R
0x487A | 0x487B | 18554 | 18555 | ANG_10M_HAR_V_13th_c | Aggr 10min Phase C 13rd Voltage Angle Harmonics | float | 2 | R
0x487C | 0x487D | 18556 | 18557 | ANG_10M_HAR_I_13th_a | Aggr 10min Phase A 13rd Current Angle Harmonics | float | 2 | R
0x487E | 0x487F | 18558 | 18559 | ANG_10M_HAR_I_13th_b | Aggr 10min Phase B 13rd Current Angle Harmonics | float | 2 | R
0x4880 | 0x4881 | 18560 | 18561 | ANG_10M_HAR_I_13th_c | Aggr 10min Phase C 13rd Current Angle Harmonics | float | 2 | R
0x4882 | 0x4883 | 18562 | 18563 | ANG_10M_HAR_I_13th_n | Aggr 10min Phase N 13rd Current Angle Harmonics | float | 2 | R
0x4884 | 0x4885 | 18564 | 18565 | ANG_10M_HAR_V_14th_a | Aggr 10min Phase A 14th Voltage Angle Harmonics | float | 2 | R
0x4886 | 0x4887 | 18566 | 18567 | ANG_10M_HAR_V_14th_b | Aggr 10min Phase B 14th Voltage Angle Harmonics | float | 2 | R
0x4888 | 0x4889 | 18568 | 18569 | ANG_10M_HAR_V_14th_c | Aggr 10min Phase C 14th Voltage Angle Harmonics | float | 2 | R
0x488A | 0x488B | 18570 | 18571 | ANG_10M_HAR_I_14th_a | Aggr 10min Phase A 14th Current Angle Harmonics | float | 2 | R
0x488C | 0x488D | 18572 | 18573 | ANG_10M_HAR_I_14th_b | Aggr 10min Phase B 14th Current Angle Harmonics | float | 2 | R
0x488E | 0x488F | 18574 | 18575 | ANG_10M_HAR_I_14th_c | Aggr 10min Phase C 14th Current Angle Harmonics | float | 2 | R
0x4890 | 0x4891 | 18576 | 18577 | ANG_10M_HAR_I_14th_n | Aggr 10min Phase N 14th Current Angle Harmonics | float | 2 | R
0x4892 | 0x4893 | 18578 | 18579 | ANG_10M_HAR_V_15th_a | Aggr 10min Phase A 15th Voltage Angle Harmonics | float | 2 | R
0x4894 | 0x4895 | 18580 | 18581 | ANG_10M_HAR_V_15th_b | Aggr 10min Phase B 15th Voltage Angle Harmonics | float | 2 | R
0x4896 | 0x4897 | 18582 | 18583 | ANG_10M_HAR_V_15th_c | Aggr 10min Phase C 15th Voltage Angle Harmonics | float | 2 | R
0x4898 | 0x4899 | 18584 | 18585 | ANG_10M_HAR_I_15th_a | Aggr 10min Phase A 15th Current Angle Harmonics | float | 2 | R
0x489A | 0x489B | 18586 | 18587 | ANG_10M_HAR_I_15th_b | Aggr 10min Phase B 15th Current Angle Harmonics | float | 2 | R
0x489C | 0x489D | 18588 | 18589 | ANG_10M_HAR_I_15th_c | Aggr 10min Phase C 15th Current Angle Harmonics | float | 2 | R
0x489E | 0x489F | 18590 | 18591 | ANG_10M_HAR_I_15th_n | Aggr 10min Phase N 15th Current Angle Harmonics | float | 2 | R
0x48A0 | 0x48A1 | 18592 | 18593 | ANG_10M_HAR_V_16th_a | Aggr 10min Phase A 16th Voltage Angle Harmonics | float | 2 | R
0x48A2 | 0x48A3 | 18594 | 18595 | ANG_10M_HAR_V_16th_b | Aggr 10min Phase B 16th Voltage Angle Harmonics | float | 2 | R
0x48A4 | 0x48A5 | 18596 | 18597 | ANG_10M_HAR_V_16th_c | Aggr 10min Phase C 16th Voltage Angle Harmonics | float | 2 | R
0x48A6 | 0x48A7 | 18598 | 18599 | ANG_10M_HAR_I_16th_a | Aggr 10min Phase A 16th Current Angle Harmonics | float | 2 | R
0x48A8 | 0x48A9 | 18600 | 18601 | ANG_10M_HAR_I_16th_b | Aggr 10min Phase B 16th Current Angle Harmonics | float | 2 | R
0x48AA | 0x48AB | 18602 | 18603 | ANG_10M_HAR_I_16th_c | Aggr 10min Phase C 16th Current Angle Harmonics | float | 2 | R
0x48AC | 0x48AD | 18604 | 18605 | ANG_10M_HAR_I_16th_n | Aggr 10min Phase N 16th Current Angle Harmonics | float | 2 | R
0x48AE | 0x48AF | 18606 | 18607 | ANG_10M_HAR_V_17th_a | Aggr 10min Phase A 17th Voltage Angle Harmonics | float | 2 | R
0x48B0 | 0x48B1 | 18608 | 18609 | ANG_10M_HAR_V_17th_b | Aggr 10min Phase B 17th Voltage Angle Harmonics | float | 2 | R
0x48B2 | 0x48B3 | 18610 | 18611 | ANG_10M_HAR_V_17th_c | Aggr 10min Phase C 17th Voltage Angle Harmonics | float | 2 | R
0x48B4 | 0x48B5 | 18612 | 18613 | ANG_10M_HAR_I_17th_a | Aggr 10min Phase A 17th Current Angle Harmonics | float | 2 | R
0x48B6 | 0x48B7 | 18614 | 18615 | ANG_10M_HAR_I_17th_b | Aggr 10min Phase B 17th Current Angle Harmonics | float | 2 | R
0x48B8 | 0x48B9 | 18616 | 18617 | ANG_10M_HAR_I_17th_c | Aggr 10min Phase C 17th Current Angle Harmonics | float | 2 | R
0x48BA | 0x48BB | 18618 | 18619 | ANG_10M_HAR_I_17th_n | Aggr 10min Phase N 17th Current Angle Harmonics | float | 2 | R
0x48BC | 0x48BD | 18620 | 18621 | ANG_10M_HAR_V_18th_a | Aggr 10min Phase A 18th Voltage Angle Harmonics | float | 2 | R
0x48BE | 0x48BF | 18622 | 18623 | ANG_10M_HAR_V_18th_b | Aggr 10min Phase B 18th Voltage Angle Harmonics | float | 2 | R
0x48C0 | 0x48C1 | 18624 | 18625 | ANG_10M_HAR_V_18th_c | Aggr 10min Phase C 18th Voltage Angle Harmonics | float | 2 | R
0x48C2 | 0x48C3 | 18626 | 18627 | ANG_10M_HAR_I_18th_a | Aggr 10min Phase A 18th Current Angle Harmonics | float | 2 | R
0x48C4 | 0x48C5 | 18628 | 18629 | ANG_10M_HAR_I_18th_b | Aggr 10min Phase B 18th Current Angle Harmonics | float | 2 | R
0x48C6 | 0x48C7 | 18630 | 18631 | ANG_10M_HAR_I_18th_c | Aggr 10min Phase C 18th Current Angle Harmonics | float | 2 | R
0x48C8 | 0x48C9 | 18632 | 18633 | ANG_10M_HAR_I_18th_n | Aggr 10min Phase N 18th Current Angle Harmonics | float | 2 | R
0x48CA | 0x48CB | 18634 | 18635 | ANG_10M_HAR_V_19th_a | Aggr 10min Phase A 19th Voltage Angle Harmonics | float | 2 | R
0x48CC | 0x48CD | 18636 | 18637 | ANG_10M_HAR_V_19th_b | Aggr 10min Phase B 19th Voltage Angle Harmonics | float | 2 | R
0x48CE | 0x48CF | 18638 | 18639 | ANG_10M_HAR_V_19th_c | Aggr 10min Phase C 19th Voltage Angle Harmonics | float | 2 | R
0x48D0 | 0x48D1 | 18640 | 18641 | ANG_10M_HAR_I_19th_a | Aggr 10min Phase A 19th Current Angle Harmonics | float | 2 | R
0x48D2 | 0x48D3 | 18642 | 18643 | ANG_10M_HAR_I_19th_b | Aggr 10min Phase B 19th Current Angle Harmonics | float | 2 | R
0x48D4 | 0x48D5 | 18644 | 18645 | ANG_10M_HAR_I_19th_c | Aggr 10min Phase C 19th Current Angle Harmonics | float | 2 | R
0x48D6 | 0x48D7 | 18646 | 18647 | ANG_10M_HAR_I_19th_n | Aggr 10min Phase N 19th Current Angle Harmonics | float | 2 | R
0x48D8 | 0x48D9 | 18648 | 18649 | ANG_10M_HAR_V_20th_a | Aggr 10min Phase A 20th Voltage Angle Harmonics | float | 2 | R
0x48DA | 0x48DB | 18650 | 18651 | ANG_10M_HAR_V_20th_b | Aggr 10min Phase B 20th Voltage Angle Harmonics | float | 2 | R
0x48DC | 0x48DD | 18652 | 18653 | ANG_10M_HAR_V_20th_c | Aggr 10min Phase C 20th Voltage Angle Harmonics | float | 2 | R
0x48DE | 0x48DF | 18654 | 18655 | ANG_10M_HAR_I_20th_a | Aggr 10min Phase A 20th Current Angle Harmonics | float | 2 | R
0x48E0 | 0x48E1 | 18656 | 18657 | ANG_10M_HAR_I_20th_b | Aggr 10min Phase B 20th Current Angle Harmonics | float | 2 | R
0x48E2 | 0x48E3 | 18658 | 18659 | ANG_10M_HAR_I_20th_c | Aggr 10min Phase C 20th Current Angle Harmonics | float | 2 | R
0x48E4 | 0x48E5 | 18660 | 18661 | ANG_10M_HAR_I_20th_n | Aggr 10min Phase N 20th Current Angle Harmonics | float | 2 | R
0x48E6 | 0x48E7 | 18662 | 18663 | ANG_10M_HAR_V_21th_a | Aggr 10min Phase A 21st Voltage Angle Harmonics | float | 2 | R
0x48E8 | 0x48E9 | 18664 | 18665 | ANG_10M_HAR_V_21th_b | Aggr 10min Phase B 21st Voltage Angle Harmonics | float | 2 | R
0x48EA | 0x48EB | 18666 | 18667 | ANG_10M_HAR_V_21th_c | Aggr 10min Phase C 21st Voltage Angle Harmonics | float | 2 | R
0x48EC | 0x48ED | 18668 | 18669 | ANG_10M_HAR_I_21th_a | Aggr 10min Phase A 21st Current Angle Harmonics | float | 2 | R
0x48EE | 0x48EF | 18670 | 18671 | ANG_10M_HAR_I_21th_b | Aggr 10min Phase B 21st Current Angle Harmonics | float | 2 | R
0x48F0 | 0x48F1 | 18672 | 18673 | ANG_10M_HAR_I_21th_c | Aggr 10min Phase C 21st Current Angle Harmonics | float | 2 | R
0x48F2 | 0x48F3 | 18674 | 18675 | ANG_10M_HAR_I_21th_n | Aggr 10min Phase N 21st Current Angle Harmonics | float | 2 | R
0x48F4 | 0x48F5 | 18676 | 18677 | ANG_10M_HAR_V_22th_a | Aggr 10min Phase A 22nd Voltage Angle Harmonics | float | 2 | R
0x48F6 | 0x48F7 | 18678 | 18679 | ANG_10M_HAR_V_22th_b | Aggr 10min Phase B 22nd Voltage Angle Harmonics | float | 2 | R
0x48F8 | 0x48F9 | 18680 | 18681 | ANG_10M_HAR_V_22th_c | Aggr 10min Phase C 22nd Voltage Angle Harmonics | float | 2 | R
0x48FA | 0x48FB | 18682 | 18683 | ANG_10M_HAR_I_22th_a | Aggr 10min Phase A 22nd Current Angle Harmonics | float | 2 | R
0x48FC | 0x48FD | 18684 | 18685 | ANG_10M_HAR_I_22th_b | Aggr 10min Phase B 22nd Current Angle Harmonics | float | 2 | R
0x48FE | 0x48FF | 18686 | 18687 | ANG_10M_HAR_I_22th_c | Aggr 10min Phase C 22nd Current Angle Harmonics | float | 2 | R
0x4900 | 0x4901 | 18688 | 18689 | ANG_10M_HAR_I_22th_n | Aggr 10min Phase N 22nd Current Angle Harmonics | float | 2 | R
0x4902 | 0x4903 | 18690 | 18691 | ANG_10M_HAR_V_23th_a | Aggr 10min Phase A 23rd Voltage Angle Harmonics | float | 2 | R
0x4904 | 0x4905 | 18692 | 18693 | ANG_10M_HAR_V_23th_b | Aggr 10min Phase B 23rd Voltage Angle Harmonics | float | 2 | R
0x4906 | 0x4907 | 18694 | 18695 | ANG_10M_HAR_V_23th_c | Aggr 10min Phase C 23rd Voltage Angle Harmonics | float | 2 | R
0x4908 | 0x4909 | 18696 | 18697 | ANG_10M_HAR_I_23th_a | Aggr 10min Phase A 23rd Current Angle Harmonics | float | 2 | R
0x490A | 0x490B | 18698 | 18699 | ANG_10M_HAR_I_23th_b | Aggr 10min Phase B 23rd Current Angle Harmonics | float | 2 | R
0x490C | 0x490D | 18700 | 18701 | ANG_10M_HAR_I_23th_c | Aggr 10min Phase C 23rd Current Angle Harmonics | float | 2 | R
0x490E | 0x490F | 18702 | 18703 | ANG_10M_HAR_I_23th_n | Aggr 10min Phase N 23rd Current Angle Harmonics | float | 2 | R
0x4910 | 0x4911 | 18704 | 18705 | ANG_10M_HAR_V_24th_a | Aggr 10min Phase A 24th Voltage Angle Harmonics | float | 2 | R
0x4912 | 0x4913 | 18706 | 18707 | ANG_10M_HAR_V_24th_b | Aggr 10min Phase B 24th Voltage Angle Harmonics | float | 2 | R
0x4914 | 0x4915 | 18708 | 18709 | ANG_10M_HAR_V_24th_c | Aggr 10min Phase C 24th Voltage Angle Harmonics | float | 2 | R
0x4916 | 0x4917 | 18710 | 18711 | ANG_10M_HAR_I_24th_a | Aggr 10min Phase A 24th Current Angle Harmonics | float | 2 | R
0x4918 | 0x4919 | 18712 | 18713 | ANG_10M_HAR_I_24th_b | Aggr 10min Phase B 24th Current Angle Harmonics | float | 2 | R
0x491A | 0x491B | 18714 | 18715 | ANG_10M_HAR_I_24th_c | Aggr 10min Phase C 24th Current Angle Harmonics | float | 2 | R
0x491C | 0x491D | 18716 | 18717 | ANG_10M_HAR_I_24th_n | Aggr 10min Phase N 24th Current Angle Harmonics | float | 2 | R
0x491E | 0x491F | 18718 | 18719 | ANG_10M_HAR_V_25th_a | Aggr 10min Phase A 25th Voltage Angle Harmonics | float | 2 | R
0x4920 | 0x4921 | 18720 | 18721 | ANG_10M_HAR_V_25th_b | Aggr 10min Phase B 25th Voltage Angle Harmonics | float | 2 | R
0x4922 | 0x4923 | 18722 | 18723 | ANG_10M_HAR_V_25th_c | Aggr 10min Phase C 25th Voltage Angle Harmonics | float | 2 | R
0x4924 | 0x4925 | 18724 | 18725 | ANG_10M_HAR_I_25th_a | Aggr 10min Phase A 25th Current Angle Harmonics | float | 2 | R
0x4926 | 0x4927 | 18726 | 18727 | ANG_10M_HAR_I_25th_b | Aggr 10min Phase B 25th Current Angle Harmonics | float | 2 | R
0x4928 | 0x4929 | 18728 | 18729 | ANG_10M_HAR_I_25th_c | Aggr 10min Phase C 25th Current Angle Harmonics | float | 2 | R
0x492A | 0x492B | 18730 | 18731 | ANG_10M_HAR_I_25th_n | Aggr 10min Phase N 25th Current Angle Harmonics | float | 2 | R
0x492C | 0x492D | 18732 | 18733 | ANG_10M_HAR_V_26th_a | Aggr 10min Phase A 26th Voltage Angle Harmonics | float | 2 | R
0x492E | 0x492F | 18734 | 18735 | ANG_10M_HAR_V_26th_b | Aggr 10min Phase B 26th Voltage Angle Harmonics | float | 2 | R
0x4930 | 0x4931 | 18736 | 18737 | ANG_10M_HAR_V_26th_c | Aggr 10min Phase C 26th Voltage Angle Harmonics | float | 2 | R
0x4932 | 0x4933 | 18738 | 18739 | ANG_10M_HAR_I_26th_a | Aggr 10min Phase A 26th Current Angle Harmonics | float | 2 | R
0x4934 | 0x4935 | 18740 | 18741 | ANG_10M_HAR_I_26th_b | Aggr 10min Phase B 26th Current Angle Harmonics | float | 2 | R
0x4936 | 0x4937 | 18742 | 18743 | ANG_10M_HAR_I_26th_c | Aggr 10min Phase C 26th Current Angle Harmonics | float | 2 | R
0x4938 | 0x4939 | 18744 | 18745 | ANG_10M_HAR_I_26th_n | Aggr 10min Phase N 26th Current Angle Harmonics | float | 2 | R
0x493A | 0x493B | 18746 | 18747 | ANG_10M_HAR_V_27th_a | Aggr 10min Phase A 27th Voltage Angle Harmonics | float | 2 | R
0x493C | 0x493D | 18748 | 18749 | ANG_10M_HAR_V_27th_b | Aggr 10min Phase B 27th Voltage Angle Harmonics | float | 2 | R
0x493E | 0x493F | 18750 | 18751 | ANG_10M_HAR_V_27th_c | Aggr 10min Phase C 27th Voltage Angle Harmonics | float | 2 | R
0x4940 | 0x4941 | 18752 | 18753 | ANG_10M_HAR_I_27th_a | Aggr 10min Phase A 27th Current Angle Harmonics | float | 2 | R
0x4942 | 0x4943 | 18754 | 18755 | ANG_10M_HAR_I_27th_b | Aggr 10min Phase B 27th Current Angle Harmonics | float | 2 | R
0x4944 | 0x4945 | 18756 | 18757 | ANG_10M_HAR_I_27th_c | Aggr 10min Phase C 27th Current Angle Harmonics | float | 2 | R
0x4946 | 0x4947 | 18758 | 18759 | ANG_10M_HAR_I_27th_n | Aggr 10min Phase N 27th Current Angle Harmonics | float | 2 | R
0x4948 | 0x4949 | 18760 | 18761 | ANG_10M_HAR_V_28th_a | Aggr 10min Phase A 28th Voltage Angle Harmonics | float | 2 | R
0x494A | 0x494B | 18762 | 18763 | ANG_10M_HAR_V_28th_b | Aggr 10min Phase B 28th Voltage Angle Harmonics | float | 2 | R
0x494C | 0x494D | 18764 | 18765 | ANG_10M_HAR_V_28th_c | Aggr 10min Phase C 28th Voltage Angle Harmonics | float | 2 | R
0x494E | 0x494F | 18766 | 18767 | ANG_10M_HAR_I_28th_a | Aggr 10min Phase A 28th Current Angle Harmonics | float | 2 | R
0x4950 | 0x4951 | 18768 | 18769 | ANG_10M_HAR_I_28th_b | Aggr 10min Phase B 28th Current Angle Harmonics | float | 2 | R
0x4952 | 0x4953 | 18770 | 18771 | ANG_10M_HAR_I_28th_c | Aggr 10min Phase C 28th Current Angle Harmonics | float | 2 | R
0x4954 | 0x4955 | 18772 | 18773 | ANG_10M_HAR_I_28th_n | Aggr 10min Phase N 28th Current Angle Harmonics | float | 2 | R
0x4956 | 0x4957 | 18774 | 18775 | ANG_10M_HAR_V_29th_a | Aggr 10min Phase A 29th Voltage Angle Harmonics | float | 2 | R
0x4958 | 0x4959 | 18776 | 18777 | ANG_10M_HAR_V_29th_b | Aggr 10min Phase B 29th Voltage Angle Harmonics | float | 2 | R
0x495A | 0x495B | 18778 | 18779 | ANG_10M_HAR_V_29th_c | Aggr 10min Phase C 29th Voltage Angle Harmonics | float | 2 | R
0x495C | 0x495D | 18780 | 18781 | ANG_10M_HAR_I_29th_a | Aggr 10min Phase A 29th Current Angle Harmonics | float | 2 | R
0x495E | 0x495F | 18782 | 18783 | ANG_10M_HAR_I_29th_b | Aggr 10min Phase B 29th Current Angle Harmonics | float | 2 | R
0x4960 | 0x4961 | 18784 | 18785 | ANG_10M_HAR_I_29th_c | Aggr 10min Phase C 29th Current Angle Harmonics | float | 2 | R
0x4962 | 0x4963 | 18786 | 18787 | ANG_10M_HAR_I_29th_n | Aggr 10min Phase N 29th Current Angle Harmonics | float | 2 | R
0x4964 | 0x4965 | 18788 | 18789 | ANG_10M_HAR_V_30th_a | Aggr 10min Phase A 30th Voltage Angle Harmonics | float | 2 | R
0x4966 | 0x4967 | 18790 | 18791 | ANG_10M_HAR_V_30th_b | Aggr 10min Phase B 30th Voltage Angle Harmonics | float | 2 | R
0x4968 | 0x4969 | 18792 | 18793 | ANG_10M_HAR_V_30th_c | Aggr 10min Phase C 30th Voltage Angle Harmonics | float | 2 | R
0x496A | 0x496B | 18794 | 18795 | ANG_10M_HAR_I_30th_a | Aggr 10min Phase A 30th Current Angle Harmonics | float | 2 | R
0x496C | 0x496D | 18796 | 18797 | ANG_10M_HAR_I_30th_b | Aggr 10min Phase B 30th Current Angle Harmonics | float | 2 | R
0x496E | 0x496F | 18798 | 18799 | ANG_10M_HAR_I_30th_c | Aggr 10min Phase C 30th Current Angle Harmonics | float | 2 | R
0x4970 | 0x4971 | 18800 | 18801 | ANG_10M_HAR_I_30th_n | Aggr 10min Phase N 30th Current Angle Harmonics | float | 2 | R
0x4972 | 0x4973 | 18802 | 18803 | ANG_10M_HAR_V_31th_a | Aggr 10min Phase A 31st Voltage Angle Harmonics | float | 2 | R
0x4974 | 0x4975 | 18804 | 18805 | ANG_10M_HAR_V_31th_b | Aggr 10min Phase B 31st Voltage Angle Harmonics | float | 2 | R
0x4976 | 0x4977 | 18806 | 18807 | ANG_10M_HAR_V_31th_c | Aggr 10min Phase C 31st Voltage Angle Harmonics | float | 2 | R
0x4978 | 0x4979 | 18808 | 18809 | ANG_10M_HAR_I_31th_a | Aggr 10min Phase A 31st Current Angle Harmonics | float | 2 | R
0x497A | 0x497B | 18810 | 18811 | ANG_10M_HAR_I_31th_b | Aggr 10min Phase B 31st Current Angle Harmonics | float | 2 | R
0x497C | 0x497D | 18812 | 18813 | ANG_10M_HAR_I_31th_c | Aggr 10min Phase C 31st Current Angle Harmonics | float | 2 | R
0x497E | 0x497F | 18814 | 18815 | ANG_10M_HAR_I_31th_n | Aggr 10min Phase N 31st Current Angle Harmonics | float | 2 | R
0x4980 | 0x4981 | 18816 | 18817 | ANG_10M_HAR_V_32th_a | Aggr 10min Phase A 32nd Voltage Angle Harmonics | float | 2 | R
0x4982 | 0x4983 | 18818 | 18819 | ANG_10M_HAR_V_32th_b | Aggr 10min Phase B 32nd Voltage Angle Harmonics | float | 2 | R
0x4984 | 0x4985 | 18820 | 18821 | ANG_10M_HAR_V_32th_c | Aggr 10min Phase C 32nd Voltage Angle Harmonics | float | 2 | R
0x4986 | 0x4987 | 18822 | 18823 | ANG_10M_HAR_I_32th_a | Aggr 10min Phase A 32nd Current Angle Harmonics | float | 2 | R
0x4988 | 0x4989 | 18824 | 18825 | ANG_10M_HAR_I_32th_b | Aggr 10min Phase B 32nd Current Angle Harmonics | float | 2 | R
0x498A | 0x498B | 18826 | 18827 | ANG_10M_HAR_I_32th_c | Aggr 10min Phase C 32nd Current Angle Harmonics | float | 2 | R
0x498C | 0x498D | 18828 | 18829 | ANG_10M_HAR_I_32th_n | Aggr 10min Phase N 32nd Current Angle Harmonics | float | 2 | R
0x498E | 0x498F | 18830 | 18831 | ANG_10M_HAR_V_33th_a | Aggr 10min Phase A 33rd Voltage Angle Harmonics | float | 2 | R
0x4990 | 0x4991 | 18832 | 18833 | ANG_10M_HAR_V_33th_b | Aggr 10min Phase B 33rd Voltage Angle Harmonics | float | 2 | R
0x4992 | 0x4993 | 18834 | 18835 | ANG_10M_HAR_V_33th_c | Aggr 10min Phase C 33rd Voltage Angle Harmonics | float | 2 | R
0x4994 | 0x4995 | 18836 | 18837 | ANG_10M_HAR_I_33th_a | Aggr 10min Phase A 33rd Current Angle Harmonics | float | 2 | R
0x4996 | 0x4997 | 18838 | 18839 | ANG_10M_HAR_I_33th_b | Aggr 10min Phase B 33rd Current Angle Harmonics | float | 2 | R
0x4998 | 0x4999 | 18840 | 18841 | ANG_10M_HAR_I_33th_c | Aggr 10min Phase C 33rd Current Angle Harmonics | float | 2 | R
0x499A | 0x499B | 18842 | 18843 | ANG_10M_HAR_I_33th_n | Aggr 10min Phase N 33rd Current Angle Harmonics | float | 2 | R
0x499C | 0x499D | 18844 | 18845 | ANG_10M_HAR_V_34th_a | Aggr 10min Phase A 34th Voltage Angle Harmonics | float | 2 | R
0x499E | 0x499F | 18846 | 18847 | ANG_10M_HAR_V_34th_b | Aggr 10min Phase B 34th Voltage Angle Harmonics | float | 2 | R
0x49A0 | 0x49A1 | 18848 | 18849 | ANG_10M_HAR_V_34th_c | Aggr 10min Phase C 34th Voltage Angle Harmonics | float | 2 | R
0x49A2 | 0x49A3 | 18850 | 18851 | ANG_10M_HAR_I_34th_a | Aggr 10min Phase A 34th Current Angle Harmonics | float | 2 | R
0x49A4 | 0x49A5 | 18852 | 18853 | ANG_10M_HAR_I_34th_b | Aggr 10min Phase B 34th Current Angle Harmonics | float | 2 | R
0x49A6 | 0x49A7 | 18854 | 18855 | ANG_10M_HAR_I_34th_c | Aggr 10min Phase C 34th Current Angle Harmonics | float | 2 | R
0x49A8 | 0x49A9 | 18856 | 18857 | ANG_10M_HAR_I_34th_n | Aggr 10min Phase N 34th Current Angle Harmonics | float | 2 | R
0x49AA | 0x49AB | 18858 | 18859 | ANG_10M_HAR_V_35th_a | Aggr 10min Phase A 35th Voltage Angle Harmonics | float | 2 | R
0x49AC | 0x49AD | 18860 | 18861 | ANG_10M_HAR_V_35th_b | Aggr 10min Phase B 35th Voltage Angle Harmonics | float | 2 | R
0x49AE | 0x49AF | 18862 | 18863 | ANG_10M_HAR_V_35th_c | Aggr 10min Phase C 35th Voltage Angle Harmonics | float | 2 | R
0x49B0 | 0x49B1 | 18864 | 18865 | ANG_10M_HAR_I_35th_a | Aggr 10min Phase A 35th Current Angle Harmonics | float | 2 | R
0x49B2 | 0x49B3 | 18866 | 18867 | ANG_10M_HAR_I_35th_b | Aggr 10min Phase B 35th Current Angle Harmonics | float | 2 | R
0x49B4 | 0x49B5 | 18868 | 18869 | ANG_10M_HAR_I_35th_c | Aggr 10min Phase C 35th Current Angle Harmonics | float | 2 | R
0x49B6 | 0x49B7 | 18870 | 18871 | ANG_10M_HAR_I_35th_n | Aggr 10min Phase N 35th Current Angle Harmonics | float | 2 | R
0x49B8 | 0x49B9 | 18872 | 18873 | ANG_10M_HAR_V_36th_a | Aggr 10min Phase A 36th Voltage Angle Harmonics | float | 2 | R
0x49BA | 0x49BB | 18874 | 18875 | ANG_10M_HAR_V_36th_b | Aggr 10min Phase B 36th Voltage Angle Harmonics | float | 2 | R
0x49BC | 0x49BD | 18876 | 18877 | ANG_10M_HAR_V_36th_c | Aggr 10min Phase C 36th Voltage Angle Harmonics | float | 2 | R
0x49BE | 0x49BF | 18878 | 18879 | ANG_10M_HAR_I_36th_a | Aggr 10min Phase A 36th Current Angle Harmonics | float | 2 | R
0x49C0 | 0x49C1 | 18880 | 18881 | ANG_10M_HAR_I_36th_b | Aggr 10min Phase B 36th Current Angle Harmonics | float | 2 | R
0x49C2 | 0x49C3 | 18882 | 18883 | ANG_10M_HAR_I_36th_c | Aggr 10min Phase C 36th Current Angle Harmonics | float | 2 | R
0x49C4 | 0x49C5 | 18884 | 18885 | ANG_10M_HAR_I_36th_n | Aggr 10min Phase N 36th Current Angle Harmonics | float | 2 | R
0x49C6 | 0x49C7 | 18886 | 18887 | ANG_10M_HAR_V_37th_a | Aggr 10min Phase A 37th Voltage Angle Harmonics | float | 2 | R
0x49C8 | 0x49C9 | 18888 | 18889 | ANG_10M_HAR_V_37th_b | Aggr 10min Phase B 37th Voltage Angle Harmonics | float | 2 | R
0x49CA | 0x49CB | 18890 | 18891 | ANG_10M_HAR_V_37th_c | Aggr 10min Phase C 37th Voltage Angle Harmonics | float | 2 | R
0x49CC | 0x49CD | 18892 | 18893 | ANG_10M_HAR_I_37th_a | Aggr 10min Phase A 37th Current Angle Harmonics | float | 2 | R
0x49CE | 0x49CF | 18894 | 18895 | ANG_10M_HAR_I_37th_b | Aggr 10min Phase B 37th Current Angle Harmonics | float | 2 | R
0x49D0 | 0x49D1 | 18896 | 18897 | ANG_10M_HAR_I_37th_c | Aggr 10min Phase C 37th Current Angle Harmonics | float | 2 | R
0x49D2 | 0x49D3 | 18898 | 18899 | ANG_10M_HAR_I_37th_n | Aggr 10min Phase N 37th Current Angle Harmonics | float | 2 | R
0x49D4 | 0x49D5 | 18900 | 18901 | ANG_10M_HAR_V_38th_a | Aggr 10min Phase A 38th Voltage Angle Harmonics | float | 2 | R
0x49D6 | 0x49D7 | 18902 | 18903 | ANG_10M_HAR_V_38th_b | Aggr 10min Phase B 38th Voltage Angle Harmonics | float | 2 | R
0x49D8 | 0x49D9 | 18904 | 18905 | ANG_10M_HAR_V_38th_c | Aggr 10min Phase C 38th Voltage Angle Harmonics | float | 2 | R
0x49DA | 0x49DB | 18906 | 18907 | ANG_10M_HAR_I_38th_a | Aggr 10min Phase A 38th Current Angle Harmonics | float | 2 | R
0x49DC | 0x49DD | 18908 | 18909 | ANG_10M_HAR_I_38th_b | Aggr 10min Phase B 38th Current Angle Harmonics | float | 2 | R
0x49DE | 0x49DF | 18910 | 18911 | ANG_10M_HAR_I_38th_c | Aggr 10min Phase C 38th Current Angle Harmonics | float | 2 | R
0x49E0 | 0x49E1 | 18912 | 18913 | ANG_10M_HAR_I_38th_n | Aggr 10min Phase N 38th Current Angle Harmonics | float | 2 | R
0x49E2 | 0x49E3 | 18914 | 18915 | ANG_10M_HAR_V_39th_a | Aggr 10min Phase A 39th Voltage Angle Harmonics | float | 2 | R
0x49E4 | 0x49E5 | 18916 | 18917 | ANG_10M_HAR_V_39th_b | Aggr 10min Phase B 39th Voltage Angle Harmonics | float | 2 | R
0x49E6 | 0x49E7 | 18918 | 18919 | ANG_10M_HAR_V_39th_c | Aggr 10min Phase C 39th Voltage Angle Harmonics | float | 2 | R
0x49E8 | 0x49E9 | 18920 | 18921 | ANG_10M_HAR_I_39th_a | Aggr 10min Phase A 39th Current Angle Harmonics | float | 2 | R
0x49EA | 0x49EB | 18922 | 18923 | ANG_10M_HAR_I_39th_b | Aggr 10min Phase B 39th Current Angle Harmonics | float | 2 | R
0x49EC | 0x49ED | 18924 | 18925 | ANG_10M_HAR_I_39th_c | Aggr 10min Phase C 39th Current Angle Harmonics | float | 2 | R
0x49EE | 0x49EF | 18926 | 18927 | ANG_10M_HAR_I_39th_n | Aggr 10min Phase N 39th Current Angle Harmonics | float | 2 | R
0x49F0 | 0x49F1 | 18928 | 18929 | ANG_10M_HAR_V_40th_a | Aggr 10min Phase A 40th Voltage Angle Harmonics | float | 2 | R
0x49F2 | 0x49F3 | 18930 | 18931 | ANG_10M_HAR_V_40th_b | Aggr 10min Phase B 40th Voltage Angle Harmonics | float | 2 | R
0x49F4 | 0x49F5 | 18932 | 18933 | ANG_10M_HAR_V_40th_c | Aggr 10min Phase C 40th Voltage Angle Harmonics | float | 2 | R
0x49F6 | 0x49F7 | 18934 | 18935 | ANG_10M_HAR_I_40th_a | Aggr 10min Phase A 40th Current Angle Harmonics | float | 2 | R
0x49F8 | 0x49F9 | 18936 | 18937 | ANG_10M_HAR_I_40th_b | Aggr 10min Phase B 40th Current Angle Harmonics | float | 2 | R
0x49FA | 0x49FB | 18938 | 18939 | ANG_10M_HAR_I_40th_c | Aggr 10min Phase C 40th Current Angle Harmonics | float | 2 | R
0x49FC | 0x49FD | 18940 | 18941 | ANG_10M_HAR_I_40th_n | Aggr 10min Phase N 40th Current Angle Harmonics | float | 2 | R
0x49FE | 0x49FF | 18942 | 18943 | ANG_10M_HAR_V_41th_a | Aggr 10min Phase A 41st Voltage Angle Harmonics | float | 2 | R
0x4A00 | 0x4A01 | 18944 | 18945 | ANG_10M_HAR_V_41th_b | Aggr 10min Phase B 41st Voltage Angle Harmonics | float | 2 | R
0x4A02 | 0x4A03 | 18946 | 18947 | ANG_10M_HAR_V_41th_c | Aggr 10min Phase C 41st Voltage Angle Harmonics | float | 2 | R
0x4A04 | 0x4A05 | 18948 | 18949 | ANG_10M_HAR_I_41th_a | Aggr 10min Phase A 41st Current Angle Harmonics | float | 2 | R
0x4A06 | 0x4A07 | 18950 | 18951 | ANG_10M_HAR_I_41th_b | Aggr 10min Phase B 41st Current Angle Harmonics | float | 2 | R
0x4A08 | 0x4A09 | 18952 | 18953 | ANG_10M_HAR_I_41th_c | Aggr 10min Phase C 41st Current Angle Harmonics | float | 2 | R
0x4A0A | 0x4A0B | 18954 | 18955 | ANG_10M_HAR_I_41th_n | Aggr 10min Phase N 41st Current Angle Harmonics | float | 2 | R
0x4A0C | 0x4A0D | 18956 | 18957 | ANG_10M_HAR_V_42th_a | Aggr 10min Phase A 42nd Voltage Angle Harmonics | float | 2 | R
0x4A0E | 0x4A0F | 18958 | 18959 | ANG_10M_HAR_V_42th_b | Aggr 10min Phase B 42nd Voltage Angle Harmonics | float | 2 | R
0x4A10 | 0x4A11 | 18960 | 18961 | ANG_10M_HAR_V_42th_c | Aggr 10min Phase C 42nd Voltage Angle Harmonics | float | 2 | R
0x4A12 | 0x4A13 | 18962 | 18963 | ANG_10M_HAR_I_42th_a | Aggr 10min Phase A 42nd Current Angle Harmonics | float | 2 | R
0x4A14 | 0x4A15 | 18964 | 18965 | ANG_10M_HAR_I_42th_b | Aggr 10min Phase B 42nd Current Angle Harmonics | float | 2 | R
0x4A16 | 0x4A17 | 18966 | 18967 | ANG_10M_HAR_I_42th_c | Aggr 10min Phase C 42nd Current Angle Harmonics | float | 2 | R
0x4A18 | 0x4A19 | 18968 | 18969 | ANG_10M_HAR_I_42th_n | Aggr 10min Phase N 42nd Current Angle Harmonics | float | 2 | R
0x4A1A | 0x4A1B | 18970 | 18971 | ANG_10M_HAR_V_43th_a | Aggr 10min Phase A 43rd Voltage Angle Harmonics | float | 2 | R
0x4A1C | 0x4A1D | 18972 | 18973 | ANG_10M_HAR_V_43th_b | Aggr 10min Phase B 43rd Voltage Angle Harmonics | float | 2 | R
0x4A1E | 0x4A1F | 18974 | 18975 | ANG_10M_HAR_V_43th_c | Aggr 10min Phase C 43rd Voltage Angle Harmonics | float | 2 | R
0x4A20 | 0x4A21 | 18976 | 18977 | ANG_10M_HAR_I_43th_a | Aggr 10min Phase A 43rd Current Angle Harmonics | float | 2 | R
0x4A22 | 0x4A23 | 18978 | 18979 | ANG_10M_HAR_I_43th_b | Aggr 10min Phase B 43rd Current Angle Harmonics | float | 2 | R
0x4A24 | 0x4A25 | 18980 | 18981 | ANG_10M_HAR_I_43th_c | Aggr 10min Phase C 43rd Current Angle Harmonics | float | 2 | R
0x4A26 | 0x4A27 | 18982 | 18983 | ANG_10M_HAR_I_43th_n | Aggr 10min Phase N 43rd Current Angle Harmonics | float | 2 | R
0x4A28 | 0x4A29 | 18984 | 18985 | ANG_10M_HAR_V_44th_a | Aggr 10min Phase A 44th Voltage Angle Harmonics | float | 2 | R
0x4A2A | 0x4A2B | 18986 | 18987 | ANG_10M_HAR_V_44th_b | Aggr 10min Phase B 44th Voltage Angle Harmonics | float | 2 | R
0x4A2C | 0x4A2D | 18988 | 18989 | ANG_10M_HAR_V_44th_c | Aggr 10min Phase C 44th Voltage Angle Harmonics | float | 2 | R
0x4A2E | 0x4A2F | 18990 | 18991 | ANG_10M_HAR_I_44th_a | Aggr 10min Phase A 44th Current Angle Harmonics | float | 2 | R
0x4A30 | 0x4A31 | 18992 | 18993 | ANG_10M_HAR_I_44th_b | Aggr 10min Phase B 44th Current Angle Harmonics | float | 2 | R
0x4A32 | 0x4A33 | 18994 | 18995 | ANG_10M_HAR_I_44th_c | Aggr 10min Phase C 44th Current Angle Harmonics | float | 2 | R
0x4A34 | 0x4A35 | 18996 | 18997 | ANG_10M_HAR_I_44th_n | Aggr 10min Phase N 44th Current Angle Harmonics | float | 2 | R
0x4A36 | 0x4A37 | 18998 | 18999 | ANG_10M_HAR_V_45th_a | Aggr 10min Phase A 45th Voltage Angle Harmonics | float | 2 | R
0x4A38 | 0x4A39 | 19000 | 19001 | ANG_10M_HAR_V_45th_b | Aggr 10min Phase B 45th Voltage Angle Harmonics | float | 2 | R
0x4A3A | 0x4A3B | 19002 | 19003 | ANG_10M_HAR_V_45th_c | Aggr 10min Phase C 45th Voltage Angle Harmonics | float | 2 | R
0x4A3C | 0x4A3D | 19004 | 19005 | ANG_10M_HAR_I_45th_a | Aggr 10min Phase A 45th Current Angle Harmonics | float | 2 | R
0x4A3E | 0x4A3F | 19006 | 19007 | ANG_10M_HAR_I_45th_b | Aggr 10min Phase B 45th Current Angle Harmonics | float | 2 | R
0x4A40 | 0x4A41 | 19008 | 19009 | ANG_10M_HAR_I_45th_c | Aggr 10min Phase C 45th Current Angle Harmonics | float | 2 | R
0x4A42 | 0x4A43 | 19010 | 19011 | ANG_10M_HAR_I_45th_n | Aggr 10min Phase N 45th Current Angle Harmonics | float | 2 | R
0x4A44 | 0x4A45 | 19012 | 19013 | ANG_10M_HAR_V_46th_a | Aggr 10min Phase A 46th Voltage Angle Harmonics | float | 2 | R
0x4A46 | 0x4A47 | 19014 | 19015 | ANG_10M_HAR_V_46th_b | Aggr 10min Phase B 46th Voltage Angle Harmonics | float | 2 | R
0x4A48 | 0x4A49 | 19016 | 19017 | ANG_10M_HAR_V_46th_c | Aggr 10min Phase C 46th Voltage Angle Harmonics | float | 2 | R
0x4A4A | 0x4A4B | 19018 | 19019 | ANG_10M_HAR_I_46th_a | Aggr 10min Phase A 46th Current Angle Harmonics | float | 2 | R
0x4A4C | 0x4A4D | 19020 | 19021 | ANG_10M_HAR_I_46th_b | Aggr 10min Phase B 46th Current Angle Harmonics | float | 2 | R
0x4A4E | 0x4A4F | 19022 | 19023 | ANG_10M_HAR_I_46th_c | Aggr 10min Phase C 46th Current Angle Harmonics | float | 2 | R
0x4A50 | 0x4A51 | 19024 | 19025 | ANG_10M_HAR_I_46th_n | Aggr 10min Phase N 46th Current Angle Harmonics | float | 2 | R
0x4A52 | 0x4A53 | 19026 | 19027 | ANG_10M_HAR_V_47th_a | Aggr 10min Phase A 47th Voltage Angle Harmonics | float | 2 | R
0x4A54 | 0x4A55 | 19028 | 19029 | ANG_10M_HAR_V_47th_b | Aggr 10min Phase B 47th Voltage Angle Harmonics | float | 2 | R
0x4A56 | 0x4A57 | 19030 | 19031 | ANG_10M_HAR_V_47th_c | Aggr 10min Phase C 47th Voltage Angle Harmonics | float | 2 | R
0x4A58 | 0x4A59 | 19032 | 19033 | ANG_10M_HAR_I_47th_a | Aggr 10min Phase A 47th Current Angle Harmonics | float | 2 | R
0x4A5A | 0x4A5B | 19034 | 19035 | ANG_10M_HAR_I_47th_b | Aggr 10min Phase B 47th Current Angle Harmonics | float | 2 | R
0x4A5C | 0x4A5D | 19036 | 19037 | ANG_10M_HAR_I_47th_c | Aggr 10min Phase C 47th Current Angle Harmonics | float | 2 | R
0x4A5E | 0x4A5F | 19038 | 19039 | ANG_10M_HAR_I_47th_n | Aggr 10min Phase N 47th Current Angle Harmonics | float | 2 | R
0x4A60 | 0x4A61 | 19040 | 19041 | ANG_10M_HAR_V_48th_a | Aggr 10min Phase A 48th Voltage Angle Harmonics | float | 2 | R
0x4A62 | 0x4A63 | 19042 | 19043 | ANG_10M_HAR_V_48th_b | Aggr 10min Phase B 48th Voltage Angle Harmonics | float | 2 | R
0x4A64 | 0x4A65 | 19044 | 19045 | ANG_10M_HAR_V_48th_c | Aggr 10min Phase C 48th Voltage Angle Harmonics | float | 2 | R
0x4A66 | 0x4A67 | 19046 | 19047 | ANG_10M_HAR_I_48th_a | Aggr 10min Phase A 48th Current Angle Harmonics | float | 2 | R
0x4A68 | 0x4A69 | 19048 | 19049 | ANG_10M_HAR_I_48th_b | Aggr 10min Phase B 48th Current Angle Harmonics | float | 2 | R
0x4A6A | 0x4A6B | 19050 | 19051 | ANG_10M_HAR_I_48th_c | Aggr 10min Phase C 48th Current Angle Harmonics | float | 2 | R
0x4A6C | 0x4A6D | 19052 | 19053 | ANG_10M_HAR_I_48th_n | Aggr 10min Phase N 48th Current Angle Harmonics | float | 2 | R
0x4A6E | 0x4A6F | 19054 | 19055 | ANG_10M_HAR_V_49th_a | Aggr 10min Phase A 49th Voltage Angle Harmonics | float | 2 | R
0x4A70 | 0x4A71 | 19056 | 19057 | ANG_10M_HAR_V_49th_b | Aggr 10min Phase B 49th Voltage Angle Harmonics | float | 2 | R
0x4A72 | 0x4A73 | 19058 | 19059 | ANG_10M_HAR_V_49th_c | Aggr 10min Phase C 49th Voltage Angle Harmonics | float | 2 | R
0x4A74 | 0x4A75 | 19060 | 19061 | ANG_10M_HAR_I_49th_a | Aggr 10min Phase A 49th Current Angle Harmonics | float | 2 | R
0x4A76 | 0x4A77 | 19062 | 19063 | ANG_10M_HAR_I_49th_b | Aggr 10min Phase B 49th Current Angle Harmonics | float | 2 | R
0x4A78 | 0x4A79 | 19064 | 19065 | ANG_10M_HAR_I_49th_c | Aggr 10min Phase C 49th Current Angle Harmonics | float | 2 | R
0x4A7A | 0x4A7B | 19066 | 19067 | ANG_10M_HAR_I_49th_n | Aggr 10min Phase N 49th Current Angle Harmonics | float | 2 | R
0x4A7C | 0x4A7D | 19068 | 19069 | ANG_10M_HAR_V_50th_a | Aggr 10min Phase A 50th Voltage Angle Harmonics | float | 2 | R
0x4A7E | 0x4A7F | 19070 | 19071 | ANG_10M_HAR_V_50th_b | Aggr 10min Phase B 50th Voltage Angle Harmonics | float | 2 | R
0x4A80 | 0x4A81 | 19072 | 19073 | ANG_10M_HAR_V_50th_c | Aggr 10min Phase C 50th Voltage Angle Harmonics | float | 2 | R
0x4A82 | 0x4A83 | 19074 | 19075 | ANG_10M_HAR_I_50th_a | Aggr 10min Phase A 50th Current Angle Harmonics | float | 2 | R
0x4A84 | 0x4A85 | 19076 | 19077 | ANG_10M_HAR_I_50th_b | Aggr 10min Phase B 50th Current Angle Harmonics | float | 2 | R
0x4A86 | 0x4A87 | 19078 | 19079 | ANG_10M_HAR_I_50th_c | Aggr 10min Phase C 50th Current Angle Harmonics | float | 2 | R
0x4A88 | 0x4A89 | 19080 | 19081 | ANG_10M_HAR_I_50th_n | Aggr 10min Phase N 50th Current Angle Harmonics | float | 2 | R
0x4A8A | 0x4A8B | 19082 | 19083 | ANG_10M_HAR_V_51th_a | Aggr 10min Phase A 51st Voltage Angle Harmonics | float | 2 | R
0x4A8C | 0x4A8D | 19084 | 19085 | ANG_10M_HAR_V_51th_b | Aggr 10min Phase B 51st Voltage Angle Harmonics | float | 2 | R
0x4A8E | 0x4A8F | 19086 | 19087 | ANG_10M_HAR_V_51th_c | Aggr 10min Phase C 51st Voltage Angle Harmonics | float | 2 | R
0x4A90 | 0x4A91 | 19088 | 19089 | ANG_10M_HAR_I_51th_a | Aggr 10min Phase A 51st Current Angle Harmonics | float | 2 | R
0x4A92 | 0x4A93 | 19090 | 19091 | ANG_10M_HAR_I_51th_b | Aggr 10min Phase B 51st Current Angle Harmonics | float | 2 | R
0x4A94 | 0x4A95 | 19092 | 19093 | ANG_10M_HAR_I_51th_c | Aggr 10min Phase C 51st Current Angle Harmonics | float | 2 | R
0x4A96 | 0x4A97 | 19094 | 19095 | ANG_10M_HAR_I_51th_n | Aggr 10min Phase N 51st Current Angle Harmonics | float | 2 | R
0x4A98 | 0x4A99 | 19096 | 19097 | ANG_10M_HAR_V_52th_a | Aggr 10min Phase A 52nd Voltage Angle Harmonics | float | 2 | R
0x4A9A | 0x4A9B | 19098 | 19099 | ANG_10M_HAR_V_52th_b | Aggr 10min Phase B 52nd Voltage Angle Harmonics | float | 2 | R
0x4A9C | 0x4A9D | 19100 | 19101 | ANG_10M_HAR_V_52th_c | Aggr 10min Phase C 52nd Voltage Angle Harmonics | float | 2 | R
0x4A9E | 0x4A9F | 19102 | 19103 | ANG_10M_HAR_I_52th_a | Aggr 10min Phase A 52nd Current Angle Harmonics | float | 2 | R
0x4AA0 | 0x4AA1 | 19104 | 19105 | ANG_10M_HAR_I_52th_b | Aggr 10min Phase B 52nd Current Angle Harmonics | float | 2 | R
0x4AA2 | 0x4AA3 | 19106 | 19107 | ANG_10M_HAR_I_52th_c | Aggr 10min Phase C 52nd Current Angle Harmonics | float | 2 | R
0x4AA4 | 0x4AA5 | 19108 | 19109 | ANG_10M_HAR_I_52th_n | Aggr 10min Phase N 52nd Current Angle Harmonics | float | 2 | R
0x4AA6 | 0x4AA7 | 19110 | 19111 | ANG_10M_HAR_V_53th_a | Aggr 10min Phase A 53rd Voltage Angle Harmonics | float | 2 | R
0x4AA8 | 0x4AA9 | 19112 | 19113 | ANG_10M_HAR_V_53th_b | Aggr 10min Phase B 53rd Voltage Angle Harmonics | float | 2 | R
0x4AAA | 0x4AAB | 19114 | 19115 | ANG_10M_HAR_V_53th_c | Aggr 10min Phase C 53rd Voltage Angle Harmonics | float | 2 | R
0x4AAC | 0x4AAD | 19116 | 19117 | ANG_10M_HAR_I_53th_a | Aggr 10min Phase A 53rd Current Angle Harmonics | float | 2 | R
0x4AAE | 0x4AAF | 19118 | 19119 | ANG_10M_HAR_I_53th_b | Aggr 10min Phase B 53rd Current Angle Harmonics | float | 2 | R
0x4AB0 | 0x4AB1 | 19120 | 19121 | ANG_10M_HAR_I_53th_c | Aggr 10min Phase C 53rd Current Angle Harmonics | float | 2 | R
0x4AB2 | 0x4AB3 | 19122 | 19123 | ANG_10M_HAR_I_53th_n | Aggr 10min Phase N 53rd Current Angle Harmonics | float | 2 | R
0x4AB4 | 0x4AB5 | 19124 | 19125 | ANG_10M_HAR_V_54th_a | Aggr 10min Phase A 54th Voltage Angle Harmonics | float | 2 | R
0x4AB6 | 0x4AB7 | 19126 | 19127 | ANG_10M_HAR_V_54th_b | Aggr 10min Phase B 54th Voltage Angle Harmonics | float | 2 | R
0x4AB8 | 0x4AB9 | 19128 | 19129 | ANG_10M_HAR_V_54th_c | Aggr 10min Phase C 54th Voltage Angle Harmonics | float | 2 | R
0x4ABA | 0x4ABB | 19130 | 19131 | ANG_10M_HAR_I_54th_a | Aggr 10min Phase A 54th Current Angle Harmonics | float | 2 | R
0x4ABC | 0x4ABD | 19132 | 19133 | ANG_10M_HAR_I_54th_b | Aggr 10min Phase B 54th Current Angle Harmonics | float | 2 | R
0x4ABE | 0x4ABF | 19134 | 19135 | ANG_10M_HAR_I_54th_c | Aggr 10min Phase C 54th Current Angle Harmonics | float | 2 | R
0x4AC0 | 0x4AC1 | 19136 | 19137 | ANG_10M_HAR_I_54th_n | Aggr 10min Phase N 54th Current Angle Harmonics | float | 2 | R
0x4AC2 | 0x4AC3 | 19138 | 19139 | ANG_10M_HAR_V_55th_a | Aggr 10min Phase A 55th Voltage Angle Harmonics | float | 2 | R
0x4AC4 | 0x4AC5 | 19140 | 19141 | ANG_10M_HAR_V_55th_b | Aggr 10min Phase B 55th Voltage Angle Harmonics | float | 2 | R
0x4AC6 | 0x4AC7 | 19142 | 19143 | ANG_10M_HAR_V_55th_c | Aggr 10min Phase C 55th Voltage Angle Harmonics | float | 2 | R
0x4AC8 | 0x4AC9 | 19144 | 19145 | ANG_10M_HAR_I_55th_a | Aggr 10min Phase A 55th Current Angle Harmonics | float | 2 | R
0x4ACA | 0x4ACB | 19146 | 19147 | ANG_10M_HAR_I_55th_b | Aggr 10min Phase B 55th Current Angle Harmonics | float | 2 | R
0x4ACC | 0x4ACD | 19148 | 19149 | ANG_10M_HAR_I_55th_c | Aggr 10min Phase C 55th Current Angle Harmonics | float | 2 | R
0x4ACE | 0x4ACF | 19150 | 19151 | ANG_10M_HAR_I_55th_n | Aggr 10min Phase N 55th Current Angle Harmonics | float | 2 | R
0x4AD0 | 0x4AD1 | 19152 | 19153 | ANG_10M_HAR_V_56th_a | Aggr 10min Phase A 56th Voltage Angle Harmonics | float | 2 | R
0x4AD2 | 0x4AD3 | 19154 | 19155 | ANG_10M_HAR_V_56th_b | Aggr 10min Phase B 56th Voltage Angle Harmonics | float | 2 | R
0x4AD4 | 0x4AD5 | 19156 | 19157 | ANG_10M_HAR_V_56th_c | Aggr 10min Phase C 56th Voltage Angle Harmonics | float | 2 | R
0x4AD6 | 0x4AD7 | 19158 | 19159 | ANG_10M_HAR_I_56th_a | Aggr 10min Phase A 56th Current Angle Harmonics | float | 2 | R
0x4AD8 | 0x4AD9 | 19160 | 19161 | ANG_10M_HAR_I_56th_b | Aggr 10min Phase B 56th Current Angle Harmonics | float | 2 | R
0x4ADA | 0x4ADB | 19162 | 19163 | ANG_10M_HAR_I_56th_c | Aggr 10min Phase C 56th Current Angle Harmonics | float | 2 | R
0x4ADC | 0x4ADD | 19164 | 19165 | ANG_10M_HAR_I_56th_n | Aggr 10min Phase N 56th Current Angle Harmonics | float | 2 | R
0x4ADE | 0x4ADF | 19166 | 19167 | ANG_10M_HAR_V_57th_a | Aggr 10min Phase A 57th Voltage Angle Harmonics | float | 2 | R
0x4AE0 | 0x4AE1 | 19168 | 19169 | ANG_10M_HAR_V_57th_b | Aggr 10min Phase B 57th Voltage Angle Harmonics | float | 2 | R
0x4AE2 | 0x4AE3 | 19170 | 19171 | ANG_10M_HAR_V_57th_c | Aggr 10min Phase C 57th Voltage Angle Harmonics | float | 2 | R
0x4AE4 | 0x4AE5 | 19172 | 19173 | ANG_10M_HAR_I_57th_a | Aggr 10min Phase A 57th Current Angle Harmonics | float | 2 | R
0x4AE6 | 0x4AE7 | 19174 | 19175 | ANG_10M_HAR_I_57th_b | Aggr 10min Phase B 57th Current Angle Harmonics | float | 2 | R
0x4AE8 | 0x4AE9 | 19176 | 19177 | ANG_10M_HAR_I_57th_c | Aggr 10min Phase C 57th Current Angle Harmonics | float | 2 | R
0x4AEA | 0x4AEB | 19178 | 19179 | ANG_10M_HAR_I_57th_n | Aggr 10min Phase N 57th Current Angle Harmonics | float | 2 | R
0x4AEC | 0x4AED | 19180 | 19181 | ANG_10M_HAR_V_58th_a | Aggr 10min Phase A 58th Voltage Angle Harmonics | float | 2 | R
0x4AEE | 0x4AEF | 19182 | 19183 | ANG_10M_HAR_V_58th_b | Aggr 10min Phase B 58th Voltage Angle Harmonics | float | 2 | R
0x4AF0 | 0x4AF1 | 19184 | 19185 | ANG_10M_HAR_V_58th_c | Aggr 10min Phase C 58th Voltage Angle Harmonics | float | 2 | R
0x4AF2 | 0x4AF3 | 19186 | 19187 | ANG_10M_HAR_I_58th_a | Aggr 10min Phase A 58th Current Angle Harmonics | float | 2 | R
0x4AF4 | 0x4AF5 | 19188 | 19189 | ANG_10M_HAR_I_58th_b | Aggr 10min Phase B 58th Current Angle Harmonics | float | 2 | R
0x4AF6 | 0x4AF7 | 19190 | 19191 | ANG_10M_HAR_I_58th_c | Aggr 10min Phase C 58th Current Angle Harmonics | float | 2 | R
0x4AF8 | 0x4AF9 | 19192 | 19193 | ANG_10M_HAR_I_58th_n | Aggr 10min Phase N 58th Current Angle Harmonics | float | 2 | R
0x4AFA | 0x4AFB | 19194 | 19195 | ANG_10M_HAR_V_59th_a | Aggr 10min Phase A 59th Voltage Angle Harmonics | float | 2 | R
0x4AFC | 0x4AFD | 19196 | 19197 | ANG_10M_HAR_V_59th_b | Aggr 10min Phase B 59th Voltage Angle Harmonics | float | 2 | R
0x4AFE | 0x4AFF | 19198 | 19199 | ANG_10M_HAR_V_59th_c | Aggr 10min Phase C 59th Voltage Angle Harmonics | float | 2 | R
0x4B00 | 0x4B01 | 19200 | 19201 | ANG_10M_HAR_I_59th_a | Aggr 10min Phase A 59th Current Angle Harmonics | float | 2 | R
0x4B02 | 0x4B03 | 19202 | 19203 | ANG_10M_HAR_I_59th_b | Aggr 10min Phase B 59th Current Angle Harmonics | float | 2 | R
0x4B04 | 0x4B05 | 19204 | 19205 | ANG_10M_HAR_I_59th_c | Aggr 10min Phase C 59th Current Angle Harmonics | float | 2 | R
0x4B06 | 0x4B07 | 19206 | 19207 | ANG_10M_HAR_I_59th_n | Aggr 10min Phase N 59th Current Angle Harmonics | float | 2 | R
0x4B08 | 0x4B09 | 19208 | 19209 | ANG_10M_HAR_V_60th_a | Aggr 10min Phase A 60th Voltage Angle Harmonics | float | 2 | R
0x4B0A | 0x4B0B | 19210 | 19211 | ANG_10M_HAR_V_60th_b | Aggr 10min Phase B 60th Voltage Angle Harmonics | float | 2 | R
0x4B0C | 0x4B0D | 19212 | 19213 | ANG_10M_HAR_V_60th_c | Aggr 10min Phase C 60th Voltage Angle Harmonics | float | 2 | R
0x4B0E | 0x4B0F | 19214 | 19215 | ANG_10M_HAR_I_60th_a | Aggr 10min Phase A 60th Current Angle Harmonics | float | 2 | R
0x4B10 | 0x4B11 | 19216 | 19217 | ANG_10M_HAR_I_60th_b | Aggr 10min Phase B 60th Current Angle Harmonics | float | 2 | R
0x4B12 | 0x4B13 | 19218 | 19219 | ANG_10M_HAR_I_60th_c | Aggr 10min Phase C 60th Current Angle Harmonics | float | 2 | R
0x4B14 | 0x4B15 | 19220 | 19221 | ANG_10M_HAR_I_60th_n | Aggr 10min Phase N 60th Current Angle Harmonics | float | 2 | R
0x4B16 | 0x4B17 | 19222 | 19223 | ANG_10M_HAR_V_61th_a | Aggr 10min Phase A 61st Voltage Angle Harmonics | float | 2 | R
0x4B18 | 0x4B19 | 19224 | 19225 | ANG_10M_HAR_V_61th_b | Aggr 10min Phase B 61st Voltage Angle Harmonics | float | 2 | R
0x4B1A | 0x4B1B | 19226 | 19227 | ANG_10M_HAR_V_61th_c | Aggr 10min Phase C 61st Voltage Angle Harmonics | float | 2 | R
0x4B1C | 0x4B1D | 19228 | 19229 | ANG_10M_HAR_I_61th_a | Aggr 10min Phase A 61st Current Angle Harmonics | float | 2 | R
0x4B1E | 0x4B1F | 19230 | 19231 | ANG_10M_HAR_I_61th_b | Aggr 10min Phase B 61st Current Angle Harmonics | float | 2 | R
0x4B20 | 0x4B21 | 19232 | 19233 | ANG_10M_HAR_I_61th_c | Aggr 10min Phase C 61st Current Angle Harmonics | float | 2 | R
0x4B22 | 0x4B23 | 19234 | 19235 | ANG_10M_HAR_I_61th_n | Aggr 10min Phase N 61st Current Angle Harmonics | float | 2 | R
0x4B24 | 0x4B25 | 19236 | 19237 | ANG_10M_HAR_V_62th_a | Aggr 10min Phase A 62nd Voltage Angle Harmonics | float | 2 | R
0x4B26 | 0x4B27 | 19238 | 19239 | ANG_10M_HAR_V_62th_b | Aggr 10min Phase B 62nd Voltage Angle Harmonics | float | 2 | R
0x4B28 | 0x4B29 | 19240 | 19241 | ANG_10M_HAR_V_62th_c | Aggr 10min Phase C 62nd Voltage Angle Harmonics | float | 2 | R
0x4B2A | 0x4B2B | 19242 | 19243 | ANG_10M_HAR_I_62th_a | Aggr 10min Phase A 62nd Current Angle Harmonics | float | 2 | R
0x4B2C | 0x4B2D | 19244 | 19245 | ANG_10M_HAR_I_62th_b | Aggr 10min Phase B 62nd Current Angle Harmonics | float | 2 | R
0x4B2E | 0x4B2F | 19246 | 19247 | ANG_10M_HAR_I_62th_c | Aggr 10min Phase C 62nd Current Angle Harmonics | float | 2 | R
0x4B30 | 0x4B31 | 19248 | 19249 | ANG_10M_HAR_I_62th_n | Aggr 10min Phase N 62nd Current Angle Harmonics | float | 2 | R
0x4B32 | 0x4B33 | 19250 | 19251 | ANG_10M_HAR_V_63th_a | Aggr 10min Phase A 63rd Voltage Angle Harmonics | float | 2 | R
0x4B34 | 0x4B35 | 19252 | 19253 | ANG_10M_HAR_V_63th_b | Aggr 10min Phase B 63rd Voltage Angle Harmonics | float | 2 | R
0x4B36 | 0x4B37 | 19254 | 19255 | ANG_10M_HAR_V_63th_c | Aggr 10min Phase C 63rd Voltage Angle Harmonics | float | 2 | R
0x4B38 | 0x4B39 | 19256 | 19257 | ANG_10M_HAR_I_63th_a | Aggr 10min Phase A 63rd Current Angle Harmonics | float | 2 | R
0x4B3A | 0x4B3B | 19258 | 19259 | ANG_10M_HAR_I_63th_b | Aggr 10min Phase B 63rd Current Angle Harmonics | float | 2 | R
0x4B3C | 0x4B3D | 19260 | 19261 | ANG_10M_HAR_I_63th_c | Aggr 10min Phase C 63rd Current Angle Harmonics | float | 2 | R
0x4B3E | 0x4B3F | 19262 | 19263 | ANG_10M_HAR_I_63th_n | Aggr 10min Phase N 63rd Current Angle Harmonics | float | 2 | R
0x4B40 | 0x4B41 | 19264 | 19265 | ANG_10M_HAR_V_64th_a | Aggr 10min Phase A 64th Voltage Angle Harmonics | float | 2 | R
0x4B42 | 0x4B43 | 19266 | 19267 | ANG_10M_HAR_V_64th_b | Aggr 10min Phase B 64th Voltage Angle Harmonics | float | 2 | R
0x4B44 | 0x4B45 | 19268 | 19269 | ANG_10M_HAR_V_64th_c | Aggr 10min Phase C 64th Voltage Angle Harmonics | float | 2 | R
0x4B46 | 0x4B47 | 19270 | 19271 | ANG_10M_HAR_I_64th_a | Aggr 10min Phase A 64th Current Angle Harmonics | float | 2 | R
0x4B48 | 0x4B49 | 19272 | 19273 | ANG_10M_HAR_I_64th_b | Aggr 10min Phase B 64th Current Angle Harmonics | float | 2 | R
0x4B4A | 0x4B4B | 19274 | 19275 | ANG_10M_HAR_I_64th_c | Aggr 10min Phase C 64th Current Angle Harmonics | float | 2 | R
0x4B4C | 0x4B4D | 19276 | 19277 | ANG_10M_HAR_I_64th_n | Aggr 10min Phase N 64th Current Angle Harmonics | float | 2 | R
0x4B4E | 0x4B4F | 19278 | 19279 | ANG_10M_HAR_V_65th_a | Aggr 10min Phase A 65th Voltage Angle Harmonics | float | 2 | R
0x4B50 | 0x4B51 | 19280 | 19281 | ANG_10M_HAR_V_65th_b | Aggr 10min Phase B 65th Voltage Angle Harmonics | float | 2 | R
0x4B52 | 0x4B53 | 19282 | 19283 | ANG_10M_HAR_V_65th_c | Aggr 10min Phase C 65th Voltage Angle Harmonics | float | 2 | R
0x4B54 | 0x4B55 | 19284 | 19285 | ANG_10M_HAR_I_65th_a | Aggr 10min Phase A 65th Current Angle Harmonics | float | 2 | R
0x4B56 | 0x4B57 | 19286 | 19287 | ANG_10M_HAR_I_65th_b | Aggr 10min Phase B 65th Current Angle Harmonics | float | 2 | R
0x4B58 | 0x4B59 | 19288 | 19289 | ANG_10M_HAR_I_65th_c | Aggr 10min Phase C 65th Current Angle Harmonics | float | 2 | R
0x4B5A | 0x4B5B | 19290 | 19291 | ANG_10M_HAR_I_65th_n | Aggr 10min Phase N 65th Current Angle Harmonics | float | 2 | R
0x4B5C | 0x4B5D | 19292 | 19293 | ANG_10M_HAR_V_66th_a | Aggr 10min Phase A 66th Voltage Angle Harmonics | float | 2 | R
0x4B5E | 0x4B5F | 19294 | 19295 | ANG_10M_HAR_V_66th_b | Aggr 10min Phase B 66th Voltage Angle Harmonics | float | 2 | R
0x4B60 | 0x4B61 | 19296 | 19297 | ANG_10M_HAR_V_66th_c | Aggr 10min Phase C 66th Voltage Angle Harmonics | float | 2 | R
0x4B62 | 0x4B63 | 19298 | 19299 | ANG_10M_HAR_I_66th_a | Aggr 10min Phase A 66th Current Angle Harmonics | float | 2 | R
0x4B64 | 0x4B65 | 19300 | 19301 | ANG_10M_HAR_I_66th_b | Aggr 10min Phase B 66th Current Angle Harmonics | float | 2 | R
0x4B66 | 0x4B67 | 19302 | 19303 | ANG_10M_HAR_I_66th_c | Aggr 10min Phase C 66th Current Angle Harmonics | float | 2 | R
0x4B68 | 0x4B69 | 19304 | 19305 | ANG_10M_HAR_I_66th_n | Aggr 10min Phase N 66th Current Angle Harmonics | float | 2 | R
0x4B6A | 0x4B6B | 19306 | 19307 | ANG_10M_HAR_V_67th_a | Aggr 10min Phase A 67th Voltage Angle Harmonics | float | 2 | R
0x4B6C | 0x4B6D | 19308 | 19309 | ANG_10M_HAR_V_67th_b | Aggr 10min Phase B 67th Voltage Angle Harmonics | float | 2 | R
0x4B6E | 0x4B6F | 19310 | 19311 | ANG_10M_HAR_V_67th_c | Aggr 10min Phase C 67th Voltage Angle Harmonics | float | 2 | R
0x4B70 | 0x4B71 | 19312 | 19313 | ANG_10M_HAR_I_67th_a | Aggr 10min Phase A 67th Current Angle Harmonics | float | 2 | R
0x4B72 | 0x4B73 | 19314 | 19315 | ANG_10M_HAR_I_67th_b | Aggr 10min Phase B 67th Current Angle Harmonics | float | 2 | R
0x4B74 | 0x4B75 | 19316 | 19317 | ANG_10M_HAR_I_67th_c | Aggr 10min Phase C 67th Current Angle Harmonics | float | 2 | R
0x4B76 | 0x4B77 | 19318 | 19319 | ANG_10M_HAR_I_67th_n | Aggr 10min Phase N 67th Current Angle Harmonics | float | 2 | R
0x4B78 | 0x4B79 | 19320 | 19321 | ANG_10M_HAR_V_68th_a | Aggr 10min Phase A 68th Voltage Angle Harmonics | float | 2 | R
0x4B7A | 0x4B7B | 19322 | 19323 | ANG_10M_HAR_V_68th_b | Aggr 10min Phase B 68th Voltage Angle Harmonics | float | 2 | R
0x4B7C | 0x4B7D | 19324 | 19325 | ANG_10M_HAR_V_68th_c | Aggr 10min Phase C 68th Voltage Angle Harmonics | float | 2 | R
0x4B7E | 0x4B7F | 19326 | 19327 | ANG_10M_HAR_I_68th_a | Aggr 10min Phase A 68th Current Angle Harmonics | float | 2 | R
0x4B80 | 0x4B81 | 19328 | 19329 | ANG_10M_HAR_I_68th_b | Aggr 10min Phase B 68th Current Angle Harmonics | float | 2 | R
0x4B82 | 0x4B83 | 19330 | 19331 | ANG_10M_HAR_I_68th_c | Aggr 10min Phase C 68th Current Angle Harmonics | float | 2 | R
0x4B84 | 0x4B85 | 19332 | 19333 | ANG_10M_HAR_I_68th_n | Aggr 10min Phase N 68th Current Angle Harmonics | float | 2 | R
0x4B86 | 0x4B87 | 19334 | 19335 | ANG_10M_HAR_V_69th_a | Aggr 10min Phase A 69th Voltage Angle Harmonics | float | 2 | R
0x4B88 | 0x4B89 | 19336 | 19337 | ANG_10M_HAR_V_69th_b | Aggr 10min Phase B 69th Voltage Angle Harmonics | float | 2 | R
0x4B8A | 0x4B8B | 19338 | 19339 | ANG_10M_HAR_V_69th_c | Aggr 10min Phase C 69th Voltage Angle Harmonics | float | 2 | R
0x4B8C | 0x4B8D | 19340 | 19341 | ANG_10M_HAR_I_69th_a | Aggr 10min Phase A 69th Current Angle Harmonics | float | 2 | R
0x4B8E | 0x4B8F | 19342 | 19343 | ANG_10M_HAR_I_69th_b | Aggr 10min Phase B 69th Current Angle Harmonics | float | 2 | R
0x4B90 | 0x4B91 | 19344 | 19345 | ANG_10M_HAR_I_69th_c | Aggr 10min Phase C 69th Current Angle Harmonics | float | 2 | R
0x4B92 | 0x4B93 | 19346 | 19347 | ANG_10M_HAR_I_69th_n | Aggr 10min Phase N 69th Current Angle Harmonics | float | 2 | R
0x4B94 | 0x4B95 | 19348 | 19349 | ANG_10M_HAR_V_70th_a | Aggr 10min Phase A 70th Voltage Angle Harmonics | float | 2 | R
0x4B96 | 0x4B97 | 19350 | 19351 | ANG_10M_HAR_V_70th_b | Aggr 10min Phase B 70th Voltage Angle Harmonics | float | 2 | R
0x4B98 | 0x4B99 | 19352 | 19353 | ANG_10M_HAR_V_70th_c | Aggr 10min Phase C 70th Voltage Angle Harmonics | float | 2 | R
0x4B9A | 0x4B9B | 19354 | 19355 | ANG_10M_HAR_I_70th_a | Aggr 10min Phase A 70th Current Angle Harmonics | float | 2 | R
0x4B9C | 0x4B9D | 19356 | 19357 | ANG_10M_HAR_I_70th_b | Aggr 10min Phase B 70th Current Angle Harmonics | float | 2 | R
0x4B9E | 0x4B9F | 19358 | 19359 | ANG_10M_HAR_I_70th_c | Aggr 10min Phase C 70th Current Angle Harmonics | float | 2 | R
0x4BA0 | 0x4BA1 | 19360 | 19361 | ANG_10M_HAR_I_70th_n | Aggr 10min Phase N 70th Current Angle Harmonics | float | 2 | R
0x4BA2 | 0x4BA3 | 19362 | 19363 | ANG_10M_HAR_V_71th_a | Aggr 10min Phase A 71st Voltage Angle Harmonics | float | 2 | R
0x4BA4 | 0x4BA5 | 19364 | 19365 | ANG_10M_HAR_V_71th_b | Aggr 10min Phase B 71st Voltage Angle Harmonics | float | 2 | R
0x4BA6 | 0x4BA7 | 19366 | 19367 | ANG_10M_HAR_V_71th_c | Aggr 10min Phase C 71st Voltage Angle Harmonics | float | 2 | R
0x4BA8 | 0x4BA9 | 19368 | 19369 | ANG_10M_HAR_I_71th_a | Aggr 10min Phase A 71st Current Angle Harmonics | float | 2 | R
0x4BAA | 0x4BAB | 19370 | 19371 | ANG_10M_HAR_I_71th_b | Aggr 10min Phase B 71st Current Angle Harmonics | float | 2 | R
0x4BAC | 0x4BAD | 19372 | 19373 | ANG_10M_HAR_I_71th_c | Aggr 10min Phase C 71st Current Angle Harmonics | float | 2 | R
0x4BAE | 0x4BAF | 19374 | 19375 | ANG_10M_HAR_I_71th_n | Aggr 10min Phase N 71st Current Angle Harmonics | float | 2 | R
0x4BB0 | 0x4BB1 | 19376 | 19377 | ANG_10M_HAR_V_72th_a | Aggr 10min Phase A 72nd Voltage Angle Harmonics | float | 2 | R
0x4BB2 | 0x4BB3 | 19378 | 19379 | ANG_10M_HAR_V_72th_b | Aggr 10min Phase B 72nd Voltage Angle Harmonics | float | 2 | R
0x4BB4 | 0x4BB5 | 19380 | 19381 | ANG_10M_HAR_V_72th_c | Aggr 10min Phase C 72nd Voltage Angle Harmonics | float | 2 | R
0x4BB6 | 0x4BB7 | 19382 | 19383 | ANG_10M_HAR_I_72th_a | Aggr 10min Phase A 72nd Current Angle Harmonics | float | 2 | R
0x4BB8 | 0x4BB9 | 19384 | 19385 | ANG_10M_HAR_I_72th_b | Aggr 10min Phase B 72nd Current Angle Harmonics | float | 2 | R
0x4BBA | 0x4BBB | 19386 | 19387 | ANG_10M_HAR_I_72th_c | Aggr 10min Phase C 72nd Current Angle Harmonics | float | 2 | R
0x4BBC | 0x4BBD | 19388 | 19389 | ANG_10M_HAR_I_72th_n | Aggr 10min Phase N 72nd Current Angle Harmonics | float | 2 | R
0x4BBE | 0x4BBF | 19390 | 19391 | ANG_10M_HAR_V_73th_a | Aggr 10min Phase A 73rd Voltage Angle Harmonics | float | 2 | R
0x4BC0 | 0x4BC1 | 19392 | 19393 | ANG_10M_HAR_V_73th_b | Aggr 10min Phase B 73rd Voltage Angle Harmonics | float | 2 | R
0x4BC2 | 0x4BC3 | 19394 | 19395 | ANG_10M_HAR_V_73th_c | Aggr 10min Phase C 73rd Voltage Angle Harmonics | float | 2 | R
0x4BC4 | 0x4BC5 | 19396 | 19397 | ANG_10M_HAR_I_73th_a | Aggr 10min Phase A 73rd Current Angle Harmonics | float | 2 | R
0x4BC6 | 0x4BC7 | 19398 | 19399 | ANG_10M_HAR_I_73th_b | Aggr 10min Phase B 73rd Current Angle Harmonics | float | 2 | R
0x4BC8 | 0x4BC9 | 19400 | 19401 | ANG_10M_HAR_I_73th_c | Aggr 10min Phase C 73rd Current Angle Harmonics | float | 2 | R
0x4BCA | 0x4BCB | 19402 | 19403 | ANG_10M_HAR_I_73th_n | Aggr 10min Phase N 73rd Current Angle Harmonics | float | 2 | R
0x4BCC | 0x4BCD | 19404 | 19405 | ANG_10M_HAR_V_74th_a | Aggr 10min Phase A 74th Voltage Angle Harmonics | float | 2 | R
0x4BCE | 0x4BCF | 19406 | 19407 | ANG_10M_HAR_V_74th_b | Aggr 10min Phase B 74th Voltage Angle Harmonics | float | 2 | R
0x4BD0 | 0x4BD1 | 19408 | 19409 | ANG_10M_HAR_V_74th_c | Aggr 10min Phase C 74th Voltage Angle Harmonics | float | 2 | R
0x4BD2 | 0x4BD3 | 19410 | 19411 | ANG_10M_HAR_I_74th_a | Aggr 10min Phase A 74th Current Angle Harmonics | float | 2 | R
0x4BD4 | 0x4BD5 | 19412 | 19413 | ANG_10M_HAR_I_74th_b | Aggr 10min Phase B 74th Current Angle Harmonics | float | 2 | R
0x4BD6 | 0x4BD7 | 19414 | 19415 | ANG_10M_HAR_I_74th_c | Aggr 10min Phase C 74th Current Angle Harmonics | float | 2 | R
0x4BD8 | 0x4BD9 | 19416 | 19417 | ANG_10M_HAR_I_74th_n | Aggr 10min Phase N 74th Current Angle Harmonics | float | 2 | R
0x4BDA | 0x4BDB | 19418 | 19419 | ANG_10M_HAR_V_75th_a | Aggr 10min Phase A 75th Voltage Angle Harmonics | float | 2 | R
0x4BDC | 0x4BDD | 19420 | 19421 | ANG_10M_HAR_V_75th_b | Aggr 10min Phase B 75th Voltage Angle Harmonics | float | 2 | R
0x4BDE | 0x4BDF | 19422 | 19423 | ANG_10M_HAR_V_75th_c | Aggr 10min Phase C 75th Voltage Angle Harmonics | float | 2 | R
0x4BE0 | 0x4BE1 | 19424 | 19425 | ANG_10M_HAR_I_75th_a | Aggr 10min Phase A 75th Current Angle Harmonics | float | 2 | R
0x4BE2 | 0x4BE3 | 19426 | 19427 | ANG_10M_HAR_I_75th_b | Aggr 10min Phase B 75th Current Angle Harmonics | float | 2 | R
0x4BE4 | 0x4BE5 | 19428 | 19429 | ANG_10M_HAR_I_75th_c | Aggr 10min Phase C 75th Current Angle Harmonics | float | 2 | R
0x4BE6 | 0x4BE7 | 19430 | 19431 | ANG_10M_HAR_I_75th_n | Aggr 10min Phase N 75th Current Angle Harmonics | float | 2 | R
0x4BE8 | 0x4BE9 | 19432 | 19433 | ANG_10M_HAR_V_76th_a | Aggr 10min Phase A 76th Voltage Angle Harmonics | float | 2 | R
0x4BEA | 0x4BEB | 19434 | 19435 | ANG_10M_HAR_V_76th_b | Aggr 10min Phase B 76th Voltage Angle Harmonics | float | 2 | R
0x4BEC | 0x4BED | 19436 | 19437 | ANG_10M_HAR_V_76th_c | Aggr 10min Phase C 76th Voltage Angle Harmonics | float | 2 | R
0x4BEE | 0x4BEF | 19438 | 19439 | ANG_10M_HAR_I_76th_a | Aggr 10min Phase A 76th Current Angle Harmonics | float | 2 | R
0x4BF0 | 0x4BF1 | 19440 | 19441 | ANG_10M_HAR_I_76th_b | Aggr 10min Phase B 76th Current Angle Harmonics | float | 2 | R
0x4BF2 | 0x4BF3 | 19442 | 19443 | ANG_10M_HAR_I_76th_c | Aggr 10min Phase C 76th Current Angle Harmonics | float | 2 | R
0x4BF4 | 0x4BF5 | 19444 | 19445 | ANG_10M_HAR_I_76th_n | Aggr 10min Phase N 76th Current Angle Harmonics | float | 2 | R
0x4BF6 | 0x4BF7 | 19446 | 19447 | ANG_10M_HAR_V_77th_a | Aggr 10min Phase A 77th Voltage Angle Harmonics | float | 2 | R
0x4BF8 | 0x4BF9 | 19448 | 19449 | ANG_10M_HAR_V_77th_b | Aggr 10min Phase B 77th Voltage Angle Harmonics | float | 2 | R
0x4BFA | 0x4BFB | 19450 | 19451 | ANG_10M_HAR_V_77th_c | Aggr 10min Phase C 77th Voltage Angle Harmonics | float | 2 | R
0x4BFC | 0x4BFD | 19452 | 19453 | ANG_10M_HAR_I_77th_a | Aggr 10min Phase A 77th Current Angle Harmonics | float | 2 | R
0x4BFE | 0x4BFF | 19454 | 19455 | ANG_10M_HAR_I_77th_b | Aggr 10min Phase B 77th Current Angle Harmonics | float | 2 | R
0x4C00 | 0x4C01 | 19456 | 19457 | ANG_10M_HAR_I_77th_c | Aggr 10min Phase C 77th Current Angle Harmonics | float | 2 | R
0x4C02 | 0x4C03 | 19458 | 19459 | ANG_10M_HAR_I_77th_n | Aggr 10min Phase N 77th Current Angle Harmonics | float | 2 | R
0x4C04 | 0x4C05 | 19460 | 19461 | ANG_10M_HAR_V_78th_a | Aggr 10min Phase A 78th Voltage Angle Harmonics | float | 2 | R
0x4C06 | 0x4C07 | 19462 | 19463 | ANG_10M_HAR_V_78th_b | Aggr 10min Phase B 78th Voltage Angle Harmonics | float | 2 | R
0x4C08 | 0x4C09 | 19464 | 19465 | ANG_10M_HAR_V_78th_c | Aggr 10min Phase C 78th Voltage Angle Harmonics | float | 2 | R
0x4C0A | 0x4C0B | 19466 | 19467 | ANG_10M_HAR_I_78th_a | Aggr 10min Phase A 78th Current Angle Harmonics | float | 2 | R
0x4C0C | 0x4C0D | 19468 | 19469 | ANG_10M_HAR_I_78th_b | Aggr 10min Phase B 78th Current Angle Harmonics | float | 2 | R
0x4C0E | 0x4C0F | 19470 | 19471 | ANG_10M_HAR_I_78th_c | Aggr 10min Phase C 78th Current Angle Harmonics | float | 2 | R
0x4C10 | 0x4C11 | 19472 | 19473 | ANG_10M_HAR_I_78th_n | Aggr 10min Phase N 78th Current Angle Harmonics | float | 2 | R
0x4C12 | 0x4C13 | 19474 | 19475 | ANG_10M_HAR_V_79th_a | Aggr 10min Phase A 79th Voltage Angle Harmonics | float | 2 | R
0x4C14 | 0x4C15 | 19476 | 19477 | ANG_10M_HAR_V_79th_b | Aggr 10min Phase B 79th Voltage Angle Harmonics | float | 2 | R
0x4C16 | 0x4C17 | 19478 | 19479 | ANG_10M_HAR_V_79th_c | Aggr 10min Phase C 79th Voltage Angle Harmonics | float | 2 | R
0x4C18 | 0x4C19 | 19480 | 19481 | ANG_10M_HAR_I_79th_a | Aggr 10min Phase A 79th Current Angle Harmonics | float | 2 | R
0x4C1A | 0x4C1B | 19482 | 19483 | ANG_10M_HAR_I_79th_b | Aggr 10min Phase B 79th Current Angle Harmonics | float | 2 | R
0x4C1C | 0x4C1D | 19484 | 19485 | ANG_10M_HAR_I_79th_c | Aggr 10min Phase C 79th Current Angle Harmonics | float | 2 | R
0x4C1E | 0x4C1F | 19486 | 19487 | ANG_10M_HAR_I_79th_n | Aggr 10min Phase N 79th Current Angle Harmonics | float | 2 | R
0x4C20 | 0x4C21 | 19488 | 19489 | ANG_10M_HAR_V_80th_a | Aggr 10min Phase A 80th Voltage Angle Harmonics | float | 2 | R
0x4C22 | 0x4C23 | 19490 | 19491 | ANG_10M_HAR_V_80th_b | Aggr 10min Phase B 80th Voltage Angle Harmonics | float | 2 | R
0x4C24 | 0x4C25 | 19492 | 19493 | ANG_10M_HAR_V_80th_c | Aggr 10min Phase C 80th Voltage Angle Harmonics | float | 2 | R
0x4C26 | 0x4C27 | 19494 | 19495 | ANG_10M_HAR_I_80th_a | Aggr 10min Phase A 80th Current Angle Harmonics | float | 2 | R
0x4C28 | 0x4C29 | 19496 | 19497 | ANG_10M_HAR_I_80th_b | Aggr 10min Phase B 80th Current Angle Harmonics | float | 2 | R
0x4C2A | 0x4C2B | 19498 | 19499 | ANG_10M_HAR_I_80th_c | Aggr 10min Phase C 80th Current Angle Harmonics | float | 2 | R
0x4C2C | 0x4C2D | 19500 | 19501 | ANG_10M_HAR_I_80th_n | Aggr 10min Phase N 80th Current Angle Harmonics | float | 2 | R
0x4C2E | 0x4C2F | 19502 | 19503 | ANG_10M_HAR_V_81th_a | Aggr 10min Phase A 81st Voltage Angle Harmonics | float | 2 | R
0x4C30 | 0x4C31 | 19504 | 19505 | ANG_10M_HAR_V_81th_b | Aggr 10min Phase B 81st Voltage Angle Harmonics | float | 2 | R
0x4C32 | 0x4C33 | 19506 | 19507 | ANG_10M_HAR_V_81th_c | Aggr 10min Phase C 81st Voltage Angle Harmonics | float | 2 | R
0x4C34 | 0x4C35 | 19508 | 19509 | ANG_10M_HAR_I_81th_a | Aggr 10min Phase A 81st Current Angle Harmonics | float | 2 | R
0x4C36 | 0x4C37 | 19510 | 19511 | ANG_10M_HAR_I_81th_b | Aggr 10min Phase B 81st Current Angle Harmonics | float | 2 | R
0x4C38 | 0x4C39 | 19512 | 19513 | ANG_10M_HAR_I_81th_c | Aggr 10min Phase C 81st Current Angle Harmonics | float | 2 | R
0x4C3A | 0x4C3B | 19514 | 19515 | ANG_10M_HAR_I_81th_n | Aggr 10min Phase N 81st Current Angle Harmonics | float | 2 | R
0x4C3C | 0x4C3D | 19516 | 19517 | ANG_10M_HAR_V_82th_a | Aggr 10min Phase A 82nd Voltage Angle Harmonics | float | 2 | R
0x4C3E | 0x4C3F | 19518 | 19519 | ANG_10M_HAR_V_82th_b | Aggr 10min Phase B 82nd Voltage Angle Harmonics | float | 2 | R
0x4C40 | 0x4C41 | 19520 | 19521 | ANG_10M_HAR_V_82th_c | Aggr 10min Phase C 82nd Voltage Angle Harmonics | float | 2 | R
0x4C42 | 0x4C43 | 19522 | 19523 | ANG_10M_HAR_I_82th_a | Aggr 10min Phase A 82nd Current Angle Harmonics | float | 2 | R
0x4C44 | 0x4C45 | 19524 | 19525 | ANG_10M_HAR_I_82th_b | Aggr 10min Phase B 82nd Current Angle Harmonics | float | 2 | R
0x4C46 | 0x4C47 | 19526 | 19527 | ANG_10M_HAR_I_82th_c | Aggr 10min Phase C 82nd Current Angle Harmonics | float | 2 | R
0x4C48 | 0x4C49 | 19528 | 19529 | ANG_10M_HAR_I_82th_n | Aggr 10min Phase N 82nd Current Angle Harmonics | float | 2 | R
0x4C4A | 0x4C4B | 19530 | 19531 | ANG_10M_HAR_V_83th_a | Aggr 10min Phase A 83rd Voltage Angle Harmonics | float | 2 | R
0x4C4C | 0x4C4D | 19532 | 19533 | ANG_10M_HAR_V_83th_b | Aggr 10min Phase B 83rd Voltage Angle Harmonics | float | 2 | R
0x4C4E | 0x4C4F | 19534 | 19535 | ANG_10M_HAR_V_83th_c | Aggr 10min Phase C 83rd Voltage Angle Harmonics | float | 2 | R
0x4C50 | 0x4C51 | 19536 | 19537 | ANG_10M_HAR_I_83th_a | Aggr 10min Phase A 83rd Current Angle Harmonics | float | 2 | R
0x4C52 | 0x4C53 | 19538 | 19539 | ANG_10M_HAR_I_83th_b | Aggr 10min Phase B 83rd Current Angle Harmonics | float | 2 | R
0x4C54 | 0x4C55 | 19540 | 19541 | ANG_10M_HAR_I_83th_c | Aggr 10min Phase C 83rd Current Angle Harmonics | float | 2 | R
0x4C56 | 0x4C57 | 19542 | 19543 | ANG_10M_HAR_I_83th_n | Aggr 10min Phase N 83rd Current Angle Harmonics | float | 2 | R
0x4C58 | 0x4C59 | 19544 | 19545 | ANG_10M_HAR_V_84th_a | Aggr 10min Phase A 84th Voltage Angle Harmonics | float | 2 | R
0x4C5A | 0x4C5B | 19546 | 19547 | ANG_10M_HAR_V_84th_b | Aggr 10min Phase B 84th Voltage Angle Harmonics | float | 2 | R
0x4C5C | 0x4C5D | 19548 | 19549 | ANG_10M_HAR_V_84th_c | Aggr 10min Phase C 84th Voltage Angle Harmonics | float | 2 | R
0x4C5E | 0x4C5F | 19550 | 19551 | ANG_10M_HAR_I_84th_a | Aggr 10min Phase A 84th Current Angle Harmonics | float | 2 | R
0x4C60 | 0x4C61 | 19552 | 19553 | ANG_10M_HAR_I_84th_b | Aggr 10min Phase B 84th Current Angle Harmonics | float | 2 | R
0x4C62 | 0x4C63 | 19554 | 19555 | ANG_10M_HAR_I_84th_c | Aggr 10min Phase C 84th Current Angle Harmonics | float | 2 | R
0x4C64 | 0x4C65 | 19556 | 19557 | ANG_10M_HAR_I_84th_n | Aggr 10min Phase N 84th Current Angle Harmonics | float | 2 | R
0x4C66 | 0x4C67 | 19558 | 19559 | ANG_10M_HAR_V_85th_a | Aggr 10min Phase A 85th Voltage Angle Harmonics | float | 2 | R
0x4C68 | 0x4C69 | 19560 | 19561 | ANG_10M_HAR_V_85th_b | Aggr 10min Phase B 85th Voltage Angle Harmonics | float | 2 | R
0x4C6A | 0x4C6B | 19562 | 19563 | ANG_10M_HAR_V_85th_c | Aggr 10min Phase C 85th Voltage Angle Harmonics | float | 2 | R
0x4C6C | 0x4C6D | 19564 | 19565 | ANG_10M_HAR_I_85th_a | Aggr 10min Phase A 85th Current Angle Harmonics | float | 2 | R
0x4C6E | 0x4C6F | 19566 | 19567 | ANG_10M_HAR_I_85th_b | Aggr 10min Phase B 85th Current Angle Harmonics | float | 2 | R
0x4C70 | 0x4C71 | 19568 | 19569 | ANG_10M_HAR_I_85th_c | Aggr 10min Phase C 85th Current Angle Harmonics | float | 2 | R
0x4C72 | 0x4C73 | 19570 | 19571 | ANG_10M_HAR_I_85th_n | Aggr 10min Phase N 85th Current Angle Harmonics | float | 2 | R
0x4C74 | 0x4C75 | 19572 | 19573 | ANG_10M_HAR_V_86th_a | Aggr 10min Phase A 86th Voltage Angle Harmonics | float | 2 | R
0x4C76 | 0x4C77 | 19574 | 19575 | ANG_10M_HAR_V_86th_b | Aggr 10min Phase B 86th Voltage Angle Harmonics | float | 2 | R
0x4C78 | 0x4C79 | 19576 | 19577 | ANG_10M_HAR_V_86th_c | Aggr 10min Phase C 86th Voltage Angle Harmonics | float | 2 | R
0x4C7A | 0x4C7B | 19578 | 19579 | ANG_10M_HAR_I_86th_a | Aggr 10min Phase A 86th Current Angle Harmonics | float | 2 | R
0x4C7C | 0x4C7D | 19580 | 19581 | ANG_10M_HAR_I_86th_b | Aggr 10min Phase B 86th Current Angle Harmonics | float | 2 | R
0x4C7E | 0x4C7F | 19582 | 19583 | ANG_10M_HAR_I_86th_c | Aggr 10min Phase C 86th Current Angle Harmonics | float | 2 | R
0x4C80 | 0x4C81 | 19584 | 19585 | ANG_10M_HAR_I_86th_n | Aggr 10min Phase N 86th Current Angle Harmonics | float | 2 | R
0x4C82 | 0x4C83 | 19586 | 19587 | ANG_10M_HAR_V_87th_a | Aggr 10min Phase A 87th Voltage Angle Harmonics | float | 2 | R
0x4C84 | 0x4C85 | 19588 | 19589 | ANG_10M_HAR_V_87th_b | Aggr 10min Phase B 87th Voltage Angle Harmonics | float | 2 | R
0x4C86 | 0x4C87 | 19590 | 19591 | ANG_10M_HAR_V_87th_c | Aggr 10min Phase C 87th Voltage Angle Harmonics | float | 2 | R
0x4C88 | 0x4C89 | 19592 | 19593 | ANG_10M_HAR_I_87th_a | Aggr 10min Phase A 87th Current Angle Harmonics | float | 2 | R
0x4C8A | 0x4C8B | 19594 | 19595 | ANG_10M_HAR_I_87th_b | Aggr 10min Phase B 87th Current Angle Harmonics | float | 2 | R
0x4C8C | 0x4C8D | 19596 | 19597 | ANG_10M_HAR_I_87th_c | Aggr 10min Phase C 87th Current Angle Harmonics | float | 2 | R
0x4C8E | 0x4C8F | 19598 | 19599 | ANG_10M_HAR_I_87th_n | Aggr 10min Phase N 87th Current Angle Harmonics | float | 2 | R
0x4C90 | 0x4C91 | 19600 | 19601 | ANG_10M_HAR_V_88th_a | Aggr 10min Phase A 88th Voltage Angle Harmonics | float | 2 | R
0x4C92 | 0x4C93 | 19602 | 19603 | ANG_10M_HAR_V_88th_b | Aggr 10min Phase B 88th Voltage Angle Harmonics | float | 2 | R
0x4C94 | 0x4C95 | 19604 | 19605 | ANG_10M_HAR_V_88th_c | Aggr 10min Phase C 88th Voltage Angle Harmonics | float | 2 | R
0x4C96 | 0x4C97 | 19606 | 19607 | ANG_10M_HAR_I_88th_a | Aggr 10min Phase A 88th Current Angle Harmonics | float | 2 | R
0x4C98 | 0x4C99 | 19608 | 19609 | ANG_10M_HAR_I_88th_b | Aggr 10min Phase B 88th Current Angle Harmonics | float | 2 | R
0x4C9A | 0x4C9B | 19610 | 19611 | ANG_10M_HAR_I_88th_c | Aggr 10min Phase C 88th Current Angle Harmonics | float | 2 | R
0x4C9C | 0x4C9D | 19612 | 19613 | ANG_10M_HAR_I_88th_n | Aggr 10min Phase N 88th Current Angle Harmonics | float | 2 | R
0x4C9E | 0x4C9F | 19614 | 19615 | ANG_10M_HAR_V_89th_a | Aggr 10min Phase A 89th Voltage Angle Harmonics | float | 2 | R
0x4CA0 | 0x4CA1 | 19616 | 19617 | ANG_10M_HAR_V_89th_b | Aggr 10min Phase B 89th Voltage Angle Harmonics | float | 2 | R
0x4CA2 | 0x4CA3 | 19618 | 19619 | ANG_10M_HAR_V_89th_c | Aggr 10min Phase C 89th Voltage Angle Harmonics | float | 2 | R
0x4CA4 | 0x4CA5 | 19620 | 19621 | ANG_10M_HAR_I_89th_a | Aggr 10min Phase A 89th Current Angle Harmonics | float | 2 | R
0x4CA6 | 0x4CA7 | 19622 | 19623 | ANG_10M_HAR_I_89th_b | Aggr 10min Phase B 89th Current Angle Harmonics | float | 2 | R
0x4CA8 | 0x4CA9 | 19624 | 19625 | ANG_10M_HAR_I_89th_c | Aggr 10min Phase C 89th Current Angle Harmonics | float | 2 | R
0x4CAA | 0x4CAB | 19626 | 19627 | ANG_10M_HAR_I_89th_n | Aggr 10min Phase N 89th Current Angle Harmonics | float | 2 | R
0x4CAC | 0x4CAD | 19628 | 19629 | ANG_10M_HAR_V_90th_a | Aggr 10min Phase A 90th Voltage Angle Harmonics | float | 2 | R
0x4CAE | 0x4CAF | 19630 | 19631 | ANG_10M_HAR_V_90th_b | Aggr 10min Phase B 90th Voltage Angle Harmonics | float | 2 | R
0x4CB0 | 0x4CB1 | 19632 | 19633 | ANG_10M_HAR_V_90th_c | Aggr 10min Phase C 90th Voltage Angle Harmonics | float | 2 | R
0x4CB2 | 0x4CB3 | 19634 | 19635 | ANG_10M_HAR_I_90th_a | Aggr 10min Phase A 90th Current Angle Harmonics | float | 2 | R
0x4CB4 | 0x4CB5 | 19636 | 19637 | ANG_10M_HAR_I_90th_b | Aggr 10min Phase B 90th Current Angle Harmonics | float | 2 | R
0x4CB6 | 0x4CB7 | 19638 | 19639 | ANG_10M_HAR_I_90th_c | Aggr 10min Phase C 90th Current Angle Harmonics | float | 2 | R
0x4CB8 | 0x4CB9 | 19640 | 19641 | ANG_10M_HAR_I_90th_n | Aggr 10min Phase N 90th Current Angle Harmonics | float | 2 | R
0x4CBA | 0x4CBB | 19642 | 19643 | ANG_10M_HAR_V_91th_a | Aggr 10min Phase A 91st Voltage Angle Harmonics | float | 2 | R
0x4CBC | 0x4CBD | 19644 | 19645 | ANG_10M_HAR_V_91th_b | Aggr 10min Phase B 91st Voltage Angle Harmonics | float | 2 | R
0x4CBE | 0x4CBF | 19646 | 19647 | ANG_10M_HAR_V_91th_c | Aggr 10min Phase C 91st Voltage Angle Harmonics | float | 2 | R
0x4CC0 | 0x4CC1 | 19648 | 19649 | ANG_10M_HAR_I_91th_a | Aggr 10min Phase A 91st Current Angle Harmonics | float | 2 | R
0x4CC2 | 0x4CC3 | 19650 | 19651 | ANG_10M_HAR_I_91th_b | Aggr 10min Phase B 91st Current Angle Harmonics | float | 2 | R
0x4CC4 | 0x4CC5 | 19652 | 19653 | ANG_10M_HAR_I_91th_c | Aggr 10min Phase C 91st Current Angle Harmonics | float | 2 | R
0x4CC6 | 0x4CC7 | 19654 | 19655 | ANG_10M_HAR_I_91th_n | Aggr 10min Phase N 91st Current Angle Harmonics | float | 2 | R
0x4CC8 | 0x4CC9 | 19656 | 19657 | ANG_10M_HAR_V_92th_a | Aggr 10min Phase A 92nd Voltage Angle Harmonics | float | 2 | R
0x4CCA | 0x4CCB | 19658 | 19659 | ANG_10M_HAR_V_92th_b | Aggr 10min Phase B 92nd Voltage Angle Harmonics | float | 2 | R
0x4CCC | 0x4CCD | 19660 | 19661 | ANG_10M_HAR_V_92th_c | Aggr 10min Phase C 92nd Voltage Angle Harmonics | float | 2 | R
0x4CCE | 0x4CCF | 19662 | 19663 | ANG_10M_HAR_I_92th_a | Aggr 10min Phase A 92nd Current Angle Harmonics | float | 2 | R
0x4CD0 | 0x4CD1 | 19664 | 19665 | ANG_10M_HAR_I_92th_b | Aggr 10min Phase B 92nd Current Angle Harmonics | float | 2 | R
0x4CD2 | 0x4CD3 | 19666 | 19667 | ANG_10M_HAR_I_92th_c | Aggr 10min Phase C 92nd Current Angle Harmonics | float | 2 | R
0x4CD4 | 0x4CD5 | 19668 | 19669 | ANG_10M_HAR_I_92th_n | Aggr 10min Phase N 92nd Current Angle Harmonics | float | 2 | R
0x4CD6 | 0x4CD7 | 19670 | 19671 | ANG_10M_HAR_V_93th_a | Aggr 10min Phase A 93rd Voltage Angle Harmonics | float | 2 | R
0x4CD8 | 0x4CD9 | 19672 | 19673 | ANG_10M_HAR_V_93th_b | Aggr 10min Phase B 93rd Voltage Angle Harmonics | float | 2 | R
0x4CDA | 0x4CDB | 19674 | 19675 | ANG_10M_HAR_V_93th_c | Aggr 10min Phase C 93rd Voltage Angle Harmonics | float | 2 | R
0x4CDC | 0x4CDD | 19676 | 19677 | ANG_10M_HAR_I_93th_a | Aggr 10min Phase A 93rd Current Angle Harmonics | float | 2 | R
0x4CDE | 0x4CDF | 19678 | 19679 | ANG_10M_HAR_I_93th_b | Aggr 10min Phase B 93rd Current Angle Harmonics | float | 2 | R
0x4CE0 | 0x4CE1 | 19680 | 19681 | ANG_10M_HAR_I_93th_c | Aggr 10min Phase C 93rd Current Angle Harmonics | float | 2 | R
0x4CE2 | 0x4CE3 | 19682 | 19683 | ANG_10M_HAR_I_93th_n | Aggr 10min Phase N 93rd Current Angle Harmonics | float | 2 | R
0x4CE4 | 0x4CE5 | 19684 | 19685 | ANG_10M_HAR_V_94th_a | Aggr 10min Phase A 94th Voltage Angle Harmonics | float | 2 | R
0x4CE6 | 0x4CE7 | 19686 | 19687 | ANG_10M_HAR_V_94th_b | Aggr 10min Phase B 94th Voltage Angle Harmonics | float | 2 | R
0x4CE8 | 0x4CE9 | 19688 | 19689 | ANG_10M_HAR_V_94th_c | Aggr 10min Phase C 94th Voltage Angle Harmonics | float | 2 | R
0x4CEA | 0x4CEB | 19690 | 19691 | ANG_10M_HAR_I_94th_a | Aggr 10min Phase A 94th Current Angle Harmonics | float | 2 | R
0x4CEC | 0x4CED | 19692 | 19693 | ANG_10M_HAR_I_94th_b | Aggr 10min Phase B 94th Current Angle Harmonics | float | 2 | R
0x4CEE | 0x4CEF | 19694 | 19695 | ANG_10M_HAR_I_94th_c | Aggr 10min Phase C 94th Current Angle Harmonics | float | 2 | R
0x4CF0 | 0x4CF1 | 19696 | 19697 | ANG_10M_HAR_I_94th_n | Aggr 10min Phase N 94th Current Angle Harmonics | float | 2 | R
0x4CF2 | 0x4CF3 | 19698 | 19699 | ANG_10M_HAR_V_95th_a | Aggr 10min Phase A 95th Voltage Angle Harmonics | float | 2 | R
0x4CF4 | 0x4CF5 | 19700 | 19701 | ANG_10M_HAR_V_95th_b | Aggr 10min Phase B 95th Voltage Angle Harmonics | float | 2 | R
0x4CF6 | 0x4CF7 | 19702 | 19703 | ANG_10M_HAR_V_95th_c | Aggr 10min Phase C 95th Voltage Angle Harmonics | float | 2 | R
0x4CF8 | 0x4CF9 | 19704 | 19705 | ANG_10M_HAR_I_95th_a | Aggr 10min Phase A 95th Current Angle Harmonics | float | 2 | R
0x4CFA | 0x4CFB | 19706 | 19707 | ANG_10M_HAR_I_95th_b | Aggr 10min Phase B 95th Current Angle Harmonics | float | 2 | R
0x4CFC | 0x4CFD | 19708 | 19709 | ANG_10M_HAR_I_95th_c | Aggr 10min Phase C 95th Current Angle Harmonics | float | 2 | R
0x4CFE | 0x4CFF | 19710 | 19711 | ANG_10M_HAR_I_95th_n | Aggr 10min Phase N 95th Current Angle Harmonics | float | 2 | R
0x4D00 | 0x4D01 | 19712 | 19713 | ANG_10M_HAR_V_96th_a | Aggr 10min Phase A 96th Voltage Angle Harmonics | float | 2 | R
0x4D02 | 0x4D03 | 19714 | 19715 | ANG_10M_HAR_V_96th_b | Aggr 10min Phase B 96th Voltage Angle Harmonics | float | 2 | R
0x4D04 | 0x4D05 | 19716 | 19717 | ANG_10M_HAR_V_96th_c | Aggr 10min Phase C 96th Voltage Angle Harmonics | float | 2 | R
0x4D06 | 0x4D07 | 19718 | 19719 | ANG_10M_HAR_I_96th_a | Aggr 10min Phase A 96th Current Angle Harmonics | float | 2 | R
0x4D08 | 0x4D09 | 19720 | 19721 | ANG_10M_HAR_I_96th_b | Aggr 10min Phase B 96th Current Angle Harmonics | float | 2 | R
0x4D0A | 0x4D0B | 19722 | 19723 | ANG_10M_HAR_I_96th_c | Aggr 10min Phase C 96th Current Angle Harmonics | float | 2 | R
0x4D0C | 0x4D0D | 19724 | 19725 | ANG_10M_HAR_I_96th_n | Aggr 10min Phase N 96th Current Angle Harmonics | float | 2 | R
0x4D0E | 0x4D0F | 19726 | 19727 | ANG_10M_HAR_V_97th_a | Aggr 10min Phase A 97th Voltage Angle Harmonics | float | 2 | R
0x4D10 | 0x4D11 | 19728 | 19729 | ANG_10M_HAR_V_97th_b | Aggr 10min Phase B 97th Voltage Angle Harmonics | float | 2 | R
0x4D12 | 0x4D13 | 19730 | 19731 | ANG_10M_HAR_V_97th_c | Aggr 10min Phase C 97th Voltage Angle Harmonics | float | 2 | R
0x4D14 | 0x4D15 | 19732 | 19733 | ANG_10M_HAR_I_97th_a | Aggr 10min Phase A 97th Current Angle Harmonics | float | 2 | R
0x4D16 | 0x4D17 | 19734 | 19735 | ANG_10M_HAR_I_97th_b | Aggr 10min Phase B 97th Current Angle Harmonics | float | 2 | R
0x4D18 | 0x4D19 | 19736 | 19737 | ANG_10M_HAR_I_97th_c | Aggr 10min Phase C 97th Current Angle Harmonics | float | 2 | R
0x4D1A | 0x4D1B | 19738 | 19739 | ANG_10M_HAR_I_97th_n | Aggr 10min Phase N 97th Current Angle Harmonics | float | 2 | R
0x4D1C | 0x4D1D | 19740 | 19741 | ANG_10M_HAR_V_98th_a | Aggr 10min Phase A 98th Voltage Angle Harmonics | float | 2 | R
0x4D1E | 0x4D1F | 19742 | 19743 | ANG_10M_HAR_V_98th_b | Aggr 10min Phase B 98th Voltage Angle Harmonics | float | 2 | R
0x4D20 | 0x4D21 | 19744 | 19745 | ANG_10M_HAR_V_98th_c | Aggr 10min Phase C 98th Voltage Angle Harmonics | float | 2 | R
0x4D22 | 0x4D23 | 19746 | 19747 | ANG_10M_HAR_I_98th_a | Aggr 10min Phase A 98th Current Angle Harmonics | float | 2 | R
0x4D24 | 0x4D25 | 19748 | 19749 | ANG_10M_HAR_I_98th_b | Aggr 10min Phase B 98th Current Angle Harmonics | float | 2 | R
0x4D26 | 0x4D27 | 19750 | 19751 | ANG_10M_HAR_I_98th_c | Aggr 10min Phase C 98th Current Angle Harmonics | float | 2 | R
0x4D28 | 0x4D29 | 19752 | 19753 | ANG_10M_HAR_I_98th_n | Aggr 10min Phase N 98th Current Angle Harmonics | float | 2 | R
0x4D2A | 0x4D2B | 19754 | 19755 | ANG_10M_HAR_V_99th_a | Aggr 10min Phase A 99th Voltage Angle Harmonics | float | 2 | R
0x4D2C | 0x4D2D | 19756 | 19757 | ANG_10M_HAR_V_99th_b | Aggr 10min Phase B 99th Voltage Angle Harmonics | float | 2 | R
0x4D2E | 0x4D2F | 19758 | 19759 | ANG_10M_HAR_V_99th_c | Aggr 10min Phase C 99th Voltage Angle Harmonics | float | 2 | R
0x4D30 | 0x4D31 | 19760 | 19761 | ANG_10M_HAR_I_99th_a | Aggr 10min Phase A 99th Current Angle Harmonics | float | 2 | R
0x4D32 | 0x4D33 | 19762 | 19763 | ANG_10M_HAR_I_99th_b | Aggr 10min Phase B 99th Current Angle Harmonics | float | 2 | R
0x4D34 | 0x4D35 | 19764 | 19765 | ANG_10M_HAR_I_99th_c | Aggr 10min Phase C 99th Current Angle Harmonics | float | 2 | R
0x4D36 | 0x4D37 | 19766 | 19767 | ANG_10M_HAR_I_99th_n | Aggr 10min Phase N 99th Current Angle Harmonics | float | 2 | R
0x4D38 | 0x4D39 | 19768 | 19769 | ANG_10M_HAR_V_100th_a | Aggr 10min Phase A 100th Voltage Angle Harmonics | float | 2 | R
0x4D3A | 0x4D3B | 19770 | 19771 | ANG_10M_HAR_V_100th_b | Aggr 10min Phase B 100th Voltage Angle Harmonics | float | 2 | R
0x4D3C | 0x4D3D | 19772 | 19773 | ANG_10M_HAR_V_100th_c | Aggr 10min Phase C 100th Voltage Angle Harmonics | float | 2 | R
0x4D3E | 0x4D3F | 19774 | 19775 | ANG_10M_HAR_I_100th_a | Aggr 10min Phase A 100th Current Angle Harmonics | float | 2 | R
0x4D40 | 0x4D41 | 19776 | 19777 | ANG_10M_HAR_I_100th_b | Aggr 10min Phase B 100th Current Angle Harmonics | float | 2 | R
0x4D42 | 0x4D43 | 19778 | 19779 | ANG_10M_HAR_I_100th_c | Aggr 10min Phase C 100th Current Angle Harmonics | float | 2 | R
0x4D44 | 0x4D45 | 19780 | 19781 | ANG_10M_HAR_I_100th_n | Aggr 10min Phase N 100th Current Angle Harmonics | float | 2 | R
0x4D46 | 0x4D47 | 19782 | 19783 | ANG_10M_HAR_V_101th_a | Aggr 10min Phase A 101st Voltage Angle Harmonics | float | 2 | R
0x4D48 | 0x4D49 | 19784 | 19785 | ANG_10M_HAR_V_101th_b | Aggr 10min Phase B 101st Voltage Angle Harmonics | float | 2 | R
0x4D4A | 0x4D4B | 19786 | 19787 | ANG_10M_HAR_V_101th_c | Aggr 10min Phase C 101st Voltage Angle Harmonics | float | 2 | R
0x4D4C | 0x4D4D | 19788 | 19789 | ANG_10M_HAR_I_101th_a | Aggr 10min Phase A 101st Current Angle Harmonics | float | 2 | R
0x4D4E | 0x4D4F | 19790 | 19791 | ANG_10M_HAR_I_101th_b | Aggr 10min Phase B 101st Current Angle Harmonics | float | 2 | R
0x4D50 | 0x4D51 | 19792 | 19793 | ANG_10M_HAR_I_101th_c | Aggr 10min Phase C 101st Current Angle Harmonics | float | 2 | R
0x4D52 | 0x4D53 | 19794 | 19795 | ANG_10M_HAR_I_101th_n | Aggr 10min Phase N 101st Current Angle Harmonics | float | 2 | R
0x4D54 | 0x4D55 | 19796 | 19797 | ANG_10M_HAR_V_102th_a | Aggr 10min Phase A 102nd Voltage Angle Harmonics | float | 2 | R
0x4D56 | 0x4D57 | 19798 | 19799 | ANG_10M_HAR_V_102th_b | Aggr 10min Phase B 102nd Voltage Angle Harmonics | float | 2 | R
0x4D58 | 0x4D59 | 19800 | 19801 | ANG_10M_HAR_V_102th_c | Aggr 10min Phase C 102nd Voltage Angle Harmonics | float | 2 | R
0x4D5A | 0x4D5B | 19802 | 19803 | ANG_10M_HAR_I_102th_a | Aggr 10min Phase A 102nd Current Angle Harmonics | float | 2 | R
0x4D5C | 0x4D5D | 19804 | 19805 | ANG_10M_HAR_I_102th_b | Aggr 10min Phase B 102nd Current Angle Harmonics | float | 2 | R
0x4D5E | 0x4D5F | 19806 | 19807 | ANG_10M_HAR_I_102th_c | Aggr 10min Phase C 102nd Current Angle Harmonics | float | 2 | R
0x4D60 | 0x4D61 | 19808 | 19809 | ANG_10M_HAR_I_102th_n | Aggr 10min Phase N 102nd Current Angle Harmonics | float | 2 | R
0x4D62 | 0x4D63 | 19810 | 19811 | ANG_10M_HAR_V_103th_a | Aggr 10min Phase A 103rd Voltage Angle Harmonics | float | 2 | R
0x4D64 | 0x4D65 | 19812 | 19813 | ANG_10M_HAR_V_103th_b | Aggr 10min Phase B 103rd Voltage Angle Harmonics | float | 2 | R
0x4D66 | 0x4D67 | 19814 | 19815 | ANG_10M_HAR_V_103th_c | Aggr 10min Phase C 103rd Voltage Angle Harmonics | float | 2 | R
0x4D68 | 0x4D69 | 19816 | 19817 | ANG_10M_HAR_I_103th_a | Aggr 10min Phase A 103rd Current Angle Harmonics | float | 2 | R
0x4D6A | 0x4D6B | 19818 | 19819 | ANG_10M_HAR_I_103th_b | Aggr 10min Phase B 103rd Current Angle Harmonics | float | 2 | R
0x4D6C | 0x4D6D | 19820 | 19821 | ANG_10M_HAR_I_103th_c | Aggr 10min Phase C 103rd Current Angle Harmonics | float | 2 | R
0x4D6E | 0x4D6F | 19822 | 19823 | ANG_10M_HAR_I_103th_n | Aggr 10min Phase N 103rd Current Angle Harmonics | float | 2 | R
0x4D70 | 0x4D71 | 19824 | 19825 | ANG_10M_HAR_V_104th_a | Aggr 10min Phase A 104th Voltage Angle Harmonics | float | 2 | R
0x4D72 | 0x4D73 | 19826 | 19827 | ANG_10M_HAR_V_104th_b | Aggr 10min Phase B 104th Voltage Angle Harmonics | float | 2 | R
0x4D74 | 0x4D75 | 19828 | 19829 | ANG_10M_HAR_V_104th_c | Aggr 10min Phase C 104th Voltage Angle Harmonics | float | 2 | R
0x4D76 | 0x4D77 | 19830 | 19831 | ANG_10M_HAR_I_104th_a | Aggr 10min Phase A 104th Current Angle Harmonics | float | 2 | R
0x4D78 | 0x4D79 | 19832 | 19833 | ANG_10M_HAR_I_104th_b | Aggr 10min Phase B 104th Current Angle Harmonics | float | 2 | R
0x4D7A | 0x4D7B | 19834 | 19835 | ANG_10M_HAR_I_104th_c | Aggr 10min Phase C 104th Current Angle Harmonics | float | 2 | R
0x4D7C | 0x4D7D | 19836 | 19837 | ANG_10M_HAR_I_104th_n | Aggr 10min Phase N 104th Current Angle Harmonics | float | 2 | R
0x4D7E | 0x4D7F | 19838 | 19839 | ANG_10M_HAR_V_105th_a | Aggr 10min Phase A 105th Voltage Angle Harmonics | float | 2 | R
0x4D80 | 0x4D81 | 19840 | 19841 | ANG_10M_HAR_V_105th_b | Aggr 10min Phase B 105th Voltage Angle Harmonics | float | 2 | R
0x4D82 | 0x4D83 | 19842 | 19843 | ANG_10M_HAR_V_105th_c | Aggr 10min Phase C 105th Voltage Angle Harmonics | float | 2 | R
0x4D84 | 0x4D85 | 19844 | 19845 | ANG_10M_HAR_I_105th_a | Aggr 10min Phase A 105th Current Angle Harmonics | float | 2 | R
0x4D86 | 0x4D87 | 19846 | 19847 | ANG_10M_HAR_I_105th_b | Aggr 10min Phase B 105th Current Angle Harmonics | float | 2 | R
0x4D88 | 0x4D89 | 19848 | 19849 | ANG_10M_HAR_I_105th_c | Aggr 10min Phase C 105th Current Angle Harmonics | float | 2 | R
0x4D8A | 0x4D8B | 19850 | 19851 | ANG_10M_HAR_I_105th_n | Aggr 10min Phase N 105th Current Angle Harmonics | float | 2 | R
0x4D8C | 0x4D8D | 19852 | 19853 | ANG_10M_HAR_V_106th_a | Aggr 10min Phase A 106th Voltage Angle Harmonics | float | 2 | R
0x4D8E | 0x4D8F | 19854 | 19855 | ANG_10M_HAR_V_106th_b | Aggr 10min Phase B 106th Voltage Angle Harmonics | float | 2 | R
0x4D90 | 0x4D91 | 19856 | 19857 | ANG_10M_HAR_V_106th_c | Aggr 10min Phase C 106th Voltage Angle Harmonics | float | 2 | R
0x4D92 | 0x4D93 | 19858 | 19859 | ANG_10M_HAR_I_106th_a | Aggr 10min Phase A 106th Current Angle Harmonics | float | 2 | R
0x4D94 | 0x4D95 | 19860 | 19861 | ANG_10M_HAR_I_106th_b | Aggr 10min Phase B 106th Current Angle Harmonics | float | 2 | R
0x4D96 | 0x4D97 | 19862 | 19863 | ANG_10M_HAR_I_106th_c | Aggr 10min Phase C 106th Current Angle Harmonics | float | 2 | R
0x4D98 | 0x4D99 | 19864 | 19865 | ANG_10M_HAR_I_106th_n | Aggr 10min Phase N 106th Current Angle Harmonics | float | 2 | R
0x4D9A | 0x4D9B | 19866 | 19867 | ANG_10M_HAR_V_107th_a | Aggr 10min Phase A 107th Voltage Angle Harmonics | float | 2 | R
0x4D9C | 0x4D9D | 19868 | 19869 | ANG_10M_HAR_V_107th_b | Aggr 10min Phase B 107th Voltage Angle Harmonics | float | 2 | R
0x4D9E | 0x4D9F | 19870 | 19871 | ANG_10M_HAR_V_107th_c | Aggr 10min Phase C 107th Voltage Angle Harmonics | float | 2 | R
0x4DA0 | 0x4DA1 | 19872 | 19873 | ANG_10M_HAR_I_107th_a | Aggr 10min Phase A 107th Current Angle Harmonics | float | 2 | R
0x4DA2 | 0x4DA3 | 19874 | 19875 | ANG_10M_HAR_I_107th_b | Aggr 10min Phase B 107th Current Angle Harmonics | float | 2 | R
0x4DA4 | 0x4DA5 | 19876 | 19877 | ANG_10M_HAR_I_107th_c | Aggr 10min Phase C 107th Current Angle Harmonics | float | 2 | R
0x4DA6 | 0x4DA7 | 19878 | 19879 | ANG_10M_HAR_I_107th_n | Aggr 10min Phase N 107th Current Angle Harmonics | float | 2 | R
0x4DA8 | 0x4DA9 | 19880 | 19881 | ANG_10M_HAR_V_108th_a | Aggr 10min Phase A 108th Voltage Angle Harmonics | float | 2 | R
0x4DAA | 0x4DAB | 19882 | 19883 | ANG_10M_HAR_V_108th_b | Aggr 10min Phase B 108th Voltage Angle Harmonics | float | 2 | R
0x4DAC | 0x4DAD | 19884 | 19885 | ANG_10M_HAR_V_108th_c | Aggr 10min Phase C 108th Voltage Angle Harmonics | float | 2 | R
0x4DAE | 0x4DAF | 19886 | 19887 | ANG_10M_HAR_I_108th_a | Aggr 10min Phase A 108th Current Angle Harmonics | float | 2 | R
0x4DB0 | 0x4DB1 | 19888 | 19889 | ANG_10M_HAR_I_108th_b | Aggr 10min Phase B 108th Current Angle Harmonics | float | 2 | R
0x4DB2 | 0x4DB3 | 19890 | 19891 | ANG_10M_HAR_I_108th_c | Aggr 10min Phase C 108th Current Angle Harmonics | float | 2 | R
0x4DB4 | 0x4DB5 | 19892 | 19893 | ANG_10M_HAR_I_108th_n | Aggr 10min Phase N 108th Current Angle Harmonics | float | 2 | R
0x4DB6 | 0x4DB7 | 19894 | 19895 | ANG_10M_HAR_V_109th_a | Aggr 10min Phase A 109th Voltage Angle Harmonics | float | 2 | R
0x4DB8 | 0x4DB9 | 19896 | 19897 | ANG_10M_HAR_V_109th_b | Aggr 10min Phase B 109th Voltage Angle Harmonics | float | 2 | R
0x4DBA | 0x4DBB | 19898 | 19899 | ANG_10M_HAR_V_109th_c | Aggr 10min Phase C 109th Voltage Angle Harmonics | float | 2 | R
0x4DBC | 0x4DBD | 19900 | 19901 | ANG_10M_HAR_I_109th_a | Aggr 10min Phase A 109th Current Angle Harmonics | float | 2 | R
0x4DBE | 0x4DBF | 19902 | 19903 | ANG_10M_HAR_I_109th_b | Aggr 10min Phase B 109th Current Angle Harmonics | float | 2 | R
0x4DC0 | 0x4DC1 | 19904 | 19905 | ANG_10M_HAR_I_109th_c | Aggr 10min Phase C 109th Current Angle Harmonics | float | 2 | R
0x4DC2 | 0x4DC3 | 19906 | 19907 | ANG_10M_HAR_I_109th_n | Aggr 10min Phase N 109th Current Angle Harmonics | float | 2 | R
0x4DC4 | 0x4DC5 | 19908 | 19909 | ANG_10M_HAR_V_110th_a | Aggr 10min Phase A 110th Voltage Angle Harmonics | float | 2 | R
0x4DC6 | 0x4DC7 | 19910 | 19911 | ANG_10M_HAR_V_110th_b | Aggr 10min Phase B 110th Voltage Angle Harmonics | float | 2 | R
0x4DC8 | 0x4DC9 | 19912 | 19913 | ANG_10M_HAR_V_110th_c | Aggr 10min Phase C 110th Voltage Angle Harmonics | float | 2 | R
0x4DCA | 0x4DCB | 19914 | 19915 | ANG_10M_HAR_I_110th_a | Aggr 10min Phase A 110th Current Angle Harmonics | float | 2 | R
0x4DCC | 0x4DCD | 19916 | 19917 | ANG_10M_HAR_I_110th_b | Aggr 10min Phase B 110th Current Angle Harmonics | float | 2 | R
0x4DCE | 0x4DCF | 19918 | 19919 | ANG_10M_HAR_I_110th_c | Aggr 10min Phase C 110th Current Angle Harmonics | float | 2 | R
0x4DD0 | 0x4DD1 | 19920 | 19921 | ANG_10M_HAR_I_110th_n | Aggr 10min Phase N 110th Current Angle Harmonics | float | 2 | R
0x4DD2 | 0x4DD3 | 19922 | 19923 | ANG_10M_HAR_V_111th_a | Aggr 10min Phase A 111st Voltage Angle Harmonics | float | 2 | R
0x4DD4 | 0x4DD5 | 19924 | 19925 | ANG_10M_HAR_V_111th_b | Aggr 10min Phase B 111st Voltage Angle Harmonics | float | 2 | R
0x4DD6 | 0x4DD7 | 19926 | 19927 | ANG_10M_HAR_V_111th_c | Aggr 10min Phase C 111st Voltage Angle Harmonics | float | 2 | R
0x4DD8 | 0x4DD9 | 19928 | 19929 | ANG_10M_HAR_I_111th_a | Aggr 10min Phase A 111st Current Angle Harmonics | float | 2 | R
0x4DDA | 0x4DDB | 19930 | 19931 | ANG_10M_HAR_I_111th_b | Aggr 10min Phase B 111st Current Angle Harmonics | float | 2 | R
0x4DDC | 0x4DDD | 19932 | 19933 | ANG_10M_HAR_I_111th_c | Aggr 10min Phase C 111st Current Angle Harmonics | float | 2 | R
0x4DDE | 0x4DDF | 19934 | 19935 | ANG_10M_HAR_I_111th_n | Aggr 10min Phase N 111st Current Angle Harmonics | float | 2 | R
0x4DE0 | 0x4DE1 | 19936 | 19937 | ANG_10M_HAR_V_112th_a | Aggr 10min Phase A 112nd Voltage Angle Harmonics | float | 2 | R
0x4DE2 | 0x4DE3 | 19938 | 19939 | ANG_10M_HAR_V_112th_b | Aggr 10min Phase B 112nd Voltage Angle Harmonics | float | 2 | R
0x4DE4 | 0x4DE5 | 19940 | 19941 | ANG_10M_HAR_V_112th_c | Aggr 10min Phase C 112nd Voltage Angle Harmonics | float | 2 | R
0x4DE6 | 0x4DE7 | 19942 | 19943 | ANG_10M_HAR_I_112th_a | Aggr 10min Phase A 112nd Current Angle Harmonics | float | 2 | R
0x4DE8 | 0x4DE9 | 19944 | 19945 | ANG_10M_HAR_I_112th_b | Aggr 10min Phase B 112nd Current Angle Harmonics | float | 2 | R
0x4DEA | 0x4DEB | 19946 | 19947 | ANG_10M_HAR_I_112th_c | Aggr 10min Phase C 112nd Current Angle Harmonics | float | 2 | R
0x4DEC | 0x4DED | 19948 | 19949 | ANG_10M_HAR_I_112th_n | Aggr 10min Phase N 112nd Current Angle Harmonics | float | 2 | R
0x4DEE | 0x4DEF | 19950 | 19951 | ANG_10M_HAR_V_113th_a | Aggr 10min Phase A 113rd Voltage Angle Harmonics | float | 2 | R
0x4DF0 | 0x4DF1 | 19952 | 19953 | ANG_10M_HAR_V_113th_b | Aggr 10min Phase B 113rd Voltage Angle Harmonics | float | 2 | R
0x4DF2 | 0x4DF3 | 19954 | 19955 | ANG_10M_HAR_V_113th_c | Aggr 10min Phase C 113rd Voltage Angle Harmonics | float | 2 | R
0x4DF4 | 0x4DF5 | 19956 | 19957 | ANG_10M_HAR_I_113th_a | Aggr 10min Phase A 113rd Current Angle Harmonics | float | 2 | R
0x4DF6 | 0x4DF7 | 19958 | 19959 | ANG_10M_HAR_I_113th_b | Aggr 10min Phase B 113rd Current Angle Harmonics | float | 2 | R
0x4DF8 | 0x4DF9 | 19960 | 19961 | ANG_10M_HAR_I_113th_c | Aggr 10min Phase C 113rd Current Angle Harmonics | float | 2 | R
0x4DFA | 0x4DFB | 19962 | 19963 | ANG_10M_HAR_I_113th_n | Aggr 10min Phase N 113rd Current Angle Harmonics | float | 2 | R
0x4DFC | 0x4DFD | 19964 | 19965 | ANG_10M_HAR_V_114th_a | Aggr 10min Phase A 114th Voltage Angle Harmonics | float | 2 | R
0x4DFE | 0x4DFF | 19966 | 19967 | ANG_10M_HAR_V_114th_b | Aggr 10min Phase B 114th Voltage Angle Harmonics | float | 2 | R
0x4E00 | 0x4E01 | 19968 | 19969 | ANG_10M_HAR_V_114th_c | Aggr 10min Phase C 114th Voltage Angle Harmonics | float | 2 | R
0x4E02 | 0x4E03 | 19970 | 19971 | ANG_10M_HAR_I_114th_a | Aggr 10min Phase A 114th Current Angle Harmonics | float | 2 | R
0x4E04 | 0x4E05 | 19972 | 19973 | ANG_10M_HAR_I_114th_b | Aggr 10min Phase B 114th Current Angle Harmonics | float | 2 | R
0x4E06 | 0x4E07 | 19974 | 19975 | ANG_10M_HAR_I_114th_c | Aggr 10min Phase C 114th Current Angle Harmonics | float | 2 | R
0x4E08 | 0x4E09 | 19976 | 19977 | ANG_10M_HAR_I_114th_n | Aggr 10min Phase N 114th Current Angle Harmonics | float | 2 | R
0x4E0A | 0x4E0B | 19978 | 19979 | ANG_10M_HAR_V_115th_a | Aggr 10min Phase A 115th Voltage Angle Harmonics | float | 2 | R
0x4E0C | 0x4E0D | 19980 | 19981 | ANG_10M_HAR_V_115th_b | Aggr 10min Phase B 115th Voltage Angle Harmonics | float | 2 | R
0x4E0E | 0x4E0F | 19982 | 19983 | ANG_10M_HAR_V_115th_c | Aggr 10min Phase C 115th Voltage Angle Harmonics | float | 2 | R
0x4E10 | 0x4E11 | 19984 | 19985 | ANG_10M_HAR_I_115th_a | Aggr 10min Phase A 115th Current Angle Harmonics | float | 2 | R
0x4E12 | 0x4E13 | 19986 | 19987 | ANG_10M_HAR_I_115th_b | Aggr 10min Phase B 115th Current Angle Harmonics | float | 2 | R
0x4E14 | 0x4E15 | 19988 | 19989 | ANG_10M_HAR_I_115th_c | Aggr 10min Phase C 115th Current Angle Harmonics | float | 2 | R
0x4E16 | 0x4E17 | 19990 | 19991 | ANG_10M_HAR_I_115th_n | Aggr 10min Phase N 115th Current Angle Harmonics | float | 2 | R
0x4E18 | 0x4E19 | 19992 | 19993 | ANG_10M_HAR_V_116th_a | Aggr 10min Phase A 116th Voltage Angle Harmonics | float | 2 | R
0x4E1A | 0x4E1B | 19994 | 19995 | ANG_10M_HAR_V_116th_b | Aggr 10min Phase B 116th Voltage Angle Harmonics | float | 2 | R
0x4E1C | 0x4E1D | 19996 | 19997 | ANG_10M_HAR_V_116th_c | Aggr 10min Phase C 116th Voltage Angle Harmonics | float | 2 | R
0x4E1E | 0x4E1F | 19998 | 19999 | ANG_10M_HAR_I_116th_a | Aggr 10min Phase A 116th Current Angle Harmonics | float | 2 | R
0x4E20 | 0x4E21 | 20000 | 20001 | ANG_10M_HAR_I_116th_b | Aggr 10min Phase B 116th Current Angle Harmonics | float | 2 | R
0x4E22 | 0x4E23 | 20002 | 20003 | ANG_10M_HAR_I_116th_c | Aggr 10min Phase C 116th Current Angle Harmonics | float | 2 | R
0x4E24 | 0x4E25 | 20004 | 20005 | ANG_10M_HAR_I_116th_n | Aggr 10min Phase N 116th Current Angle Harmonics | float | 2 | R
0x4E26 | 0x4E27 | 20006 | 20007 | ANG_10M_HAR_V_117th_a | Aggr 10min Phase A 117th Voltage Angle Harmonics | float | 2 | R
0x4E28 | 0x4E29 | 20008 | 20009 | ANG_10M_HAR_V_117th_b | Aggr 10min Phase B 117th Voltage Angle Harmonics | float | 2 | R
0x4E2A | 0x4E2B | 20010 | 20011 | ANG_10M_HAR_V_117th_c | Aggr 10min Phase C 117th Voltage Angle Harmonics | float | 2 | R
0x4E2C | 0x4E2D | 20012 | 20013 | ANG_10M_HAR_I_117th_a | Aggr 10min Phase A 117th Current Angle Harmonics | float | 2 | R
0x4E2E | 0x4E2F | 20014 | 20015 | ANG_10M_HAR_I_117th_b | Aggr 10min Phase B 117th Current Angle Harmonics | float | 2 | R
0x4E30 | 0x4E31 | 20016 | 20017 | ANG_10M_HAR_I_117th_c | Aggr 10min Phase C 117th Current Angle Harmonics | float | 2 | R
0x4E32 | 0x4E33 | 20018 | 20019 | ANG_10M_HAR_I_117th_n | Aggr 10min Phase N 117th Current Angle Harmonics | float | 2 | R
0x4E34 | 0x4E35 | 20020 | 20021 | ANG_10M_HAR_V_118th_a | Aggr 10min Phase A 118th Voltage Angle Harmonics | float | 2 | R
0x4E36 | 0x4E37 | 20022 | 20023 | ANG_10M_HAR_V_118th_b | Aggr 10min Phase B 118th Voltage Angle Harmonics | float | 2 | R
0x4E38 | 0x4E39 | 20024 | 20025 | ANG_10M_HAR_V_118th_c | Aggr 10min Phase C 118th Voltage Angle Harmonics | float | 2 | R
0x4E3A | 0x4E3B | 20026 | 20027 | ANG_10M_HAR_I_118th_a | Aggr 10min Phase A 118th Current Angle Harmonics | float | 2 | R
0x4E3C | 0x4E3D | 20028 | 20029 | ANG_10M_HAR_I_118th_b | Aggr 10min Phase B 118th Current Angle Harmonics | float | 2 | R
0x4E3E | 0x4E3F | 20030 | 20031 | ANG_10M_HAR_I_118th_c | Aggr 10min Phase C 118th Current Angle Harmonics | float | 2 | R
0x4E40 | 0x4E41 | 20032 | 20033 | ANG_10M_HAR_I_118th_n | Aggr 10min Phase N 118th Current Angle Harmonics | float | 2 | R
0x4E42 | 0x4E43 | 20034 | 20035 | ANG_10M_HAR_V_119th_a | Aggr 10min Phase A 119th Voltage Angle Harmonics | float | 2 | R
0x4E44 | 0x4E45 | 20036 | 20037 | ANG_10M_HAR_V_119th_b | Aggr 10min Phase B 119th Voltage Angle Harmonics | float | 2 | R
0x4E46 | 0x4E47 | 20038 | 20039 | ANG_10M_HAR_V_119th_c | Aggr 10min Phase C 119th Voltage Angle Harmonics | float | 2 | R
0x4E48 | 0x4E49 | 20040 | 20041 | ANG_10M_HAR_I_119th_a | Aggr 10min Phase A 119th Current Angle Harmonics | float | 2 | R
0x4E4A | 0x4E4B | 20042 | 20043 | ANG_10M_HAR_I_119th_b | Aggr 10min Phase B 119th Current Angle Harmonics | float | 2 | R
0x4E4C | 0x4E4D | 20044 | 20045 | ANG_10M_HAR_I_119th_c | Aggr 10min Phase C 119th Current Angle Harmonics | float | 2 | R
0x4E4E | 0x4E4F | 20046 | 20047 | ANG_10M_HAR_I_119th_n | Aggr 10min Phase N 119th Current Angle Harmonics | float | 2 | R
0x4E50 | 0x4E51 | 20048 | 20049 | ANG_10M_HAR_V_120th_a | Aggr 10min Phase A 120th Voltage Angle Harmonics | float | 2 | R
0x4E52 | 0x4E53 | 20050 | 20051 | ANG_10M_HAR_V_120th_b | Aggr 10min Phase B 120th Voltage Angle Harmonics | float | 2 | R
0x4E54 | 0x4E55 | 20052 | 20053 | ANG_10M_HAR_V_120th_c | Aggr 10min Phase C 120th Voltage Angle Harmonics | float | 2 | R
0x4E56 | 0x4E57 | 20054 | 20055 | ANG_10M_HAR_I_120th_a | Aggr 10min Phase A 120th Current Angle Harmonics | float | 2 | R
0x4E58 | 0x4E59 | 20056 | 20057 | ANG_10M_HAR_I_120th_b | Aggr 10min Phase B 120th Current Angle Harmonics | float | 2 | R
0x4E5A | 0x4E5B | 20058 | 20059 | ANG_10M_HAR_I_120th_c | Aggr 10min Phase C 120th Current Angle Harmonics | float | 2 | R
0x4E5C | 0x4E5D | 20060 | 20061 | ANG_10M_HAR_I_120th_n | Aggr 10min Phase N 120th Current Angle Harmonics | float | 2 | R
0x4E5E | 0x4E5F | 20062 | 20063 | ANG_10M_HAR_V_121th_a | Aggr 10min Phase A 121st Voltage Angle Harmonics | float | 2 | R
0x4E60 | 0x4E61 | 20064 | 20065 | ANG_10M_HAR_V_121th_b | Aggr 10min Phase B 121st Voltage Angle Harmonics | float | 2 | R
0x4E62 | 0x4E63 | 20066 | 20067 | ANG_10M_HAR_V_121th_c | Aggr 10min Phase C 121st Voltage Angle Harmonics | float | 2 | R
0x4E64 | 0x4E65 | 20068 | 20069 | ANG_10M_HAR_I_121th_a | Aggr 10min Phase A 121st Current Angle Harmonics | float | 2 | R
0x4E66 | 0x4E67 | 20070 | 20071 | ANG_10M_HAR_I_121th_b | Aggr 10min Phase B 121st Current Angle Harmonics | float | 2 | R
0x4E68 | 0x4E69 | 20072 | 20073 | ANG_10M_HAR_I_121th_c | Aggr 10min Phase C 121st Current Angle Harmonics | float | 2 | R
0x4E6A | 0x4E6B | 20074 | 20075 | ANG_10M_HAR_I_121th_n | Aggr 10min Phase N 121st Current Angle Harmonics | float | 2 | R
0x4E6C | 0x4E6D | 20076 | 20077 | ANG_10M_HAR_V_122th_a | Aggr 10min Phase A 122nd Voltage Angle Harmonics | float | 2 | R
0x4E6E | 0x4E6F | 20078 | 20079 | ANG_10M_HAR_V_122th_b | Aggr 10min Phase B 122nd Voltage Angle Harmonics | float | 2 | R
0x4E70 | 0x4E71 | 20080 | 20081 | ANG_10M_HAR_V_122th_c | Aggr 10min Phase C 122nd Voltage Angle Harmonics | float | 2 | R
0x4E72 | 0x4E73 | 20082 | 20083 | ANG_10M_HAR_I_122th_a | Aggr 10min Phase A 122nd Current Angle Harmonics | float | 2 | R
0x4E74 | 0x4E75 | 20084 | 20085 | ANG_10M_HAR_I_122th_b | Aggr 10min Phase B 122nd Current Angle Harmonics | float | 2 | R
0x4E76 | 0x4E77 | 20086 | 20087 | ANG_10M_HAR_I_122th_c | Aggr 10min Phase C 122nd Current Angle Harmonics | float | 2 | R
0x4E78 | 0x4E79 | 20088 | 20089 | ANG_10M_HAR_I_122th_n | Aggr 10min Phase N 122nd Current Angle Harmonics | float | 2 | R
0x4E7A | 0x4E7B | 20090 | 20091 | ANG_10M_HAR_V_123th_a | Aggr 10min Phase A 123rd Voltage Angle Harmonics | float | 2 | R
0x4E7C | 0x4E7D | 20092 | 20093 | ANG_10M_HAR_V_123th_b | Aggr 10min Phase B 123rd Voltage Angle Harmonics | float | 2 | R
0x4E7E | 0x4E7F | 20094 | 20095 | ANG_10M_HAR_V_123th_c | Aggr 10min Phase C 123rd Voltage Angle Harmonics | float | 2 | R
0x4E80 | 0x4E81 | 20096 | 20097 | ANG_10M_HAR_I_123th_a | Aggr 10min Phase A 123rd Current Angle Harmonics | float | 2 | R
0x4E82 | 0x4E83 | 20098 | 20099 | ANG_10M_HAR_I_123th_b | Aggr 10min Phase B 123rd Current Angle Harmonics | float | 2 | R
0x4E84 | 0x4E85 | 20100 | 20101 | ANG_10M_HAR_I_123th_c | Aggr 10min Phase C 123rd Current Angle Harmonics | float | 2 | R
0x4E86 | 0x4E87 | 20102 | 20103 | ANG_10M_HAR_I_123th_n | Aggr 10min Phase N 123rd Current Angle Harmonics | float | 2 | R
0x4E88 | 0x4E89 | 20104 | 20105 | ANG_10M_HAR_V_124th_a | Aggr 10min Phase A 124th Voltage Angle Harmonics | float | 2 | R
0x4E8A | 0x4E8B | 20106 | 20107 | ANG_10M_HAR_V_124th_b | Aggr 10min Phase B 124th Voltage Angle Harmonics | float | 2 | R
0x4E8C | 0x4E8D | 20108 | 20109 | ANG_10M_HAR_V_124th_c | Aggr 10min Phase C 124th Voltage Angle Harmonics | float | 2 | R
0x4E8E | 0x4E8F | 20110 | 20111 | ANG_10M_HAR_I_124th_a | Aggr 10min Phase A 124th Current Angle Harmonics | float | 2 | R
0x4E90 | 0x4E91 | 20112 | 20113 | ANG_10M_HAR_I_124th_b | Aggr 10min Phase B 124th Current Angle Harmonics | float | 2 | R
0x4E92 | 0x4E93 | 20114 | 20115 | ANG_10M_HAR_I_124th_c | Aggr 10min Phase C 124th Current Angle Harmonics | float | 2 | R
0x4E94 | 0x4E95 | 20116 | 20117 | ANG_10M_HAR_I_124th_n | Aggr 10min Phase N 124th Current Angle Harmonics | float | 2 | R
0x4E96 | 0x4E97 | 20118 | 20119 | ANG_10M_HAR_V_125th_a | Aggr 10min Phase A 125th Voltage Angle Harmonics | float | 2 | R
0x4E98 | 0x4E99 | 20120 | 20121 | ANG_10M_HAR_V_125th_b | Aggr 10min Phase B 125th Voltage Angle Harmonics | float | 2 | R
0x4E9A | 0x4E9B | 20122 | 20123 | ANG_10M_HAR_V_125th_c | Aggr 10min Phase C 125th Voltage Angle Harmonics | float | 2 | R
0x4E9C | 0x4E9D | 20124 | 20125 | ANG_10M_HAR_I_125th_a | Aggr 10min Phase A 125th Current Angle Harmonics | float | 2 | R
0x4E9E | 0x4E9F | 20126 | 20127 | ANG_10M_HAR_I_125th_b | Aggr 10min Phase B 125th Current Angle Harmonics | float | 2 | R
0x4EA0 | 0x4EA1 | 20128 | 20129 | ANG_10M_HAR_I_125th_c | Aggr 10min Phase C 125th Current Angle Harmonics | float | 2 | R
0x4EA2 | 0x4EA3 | 20130 | 20131 | ANG_10M_HAR_I_125th_n | Aggr 10min Phase N 125th Current Angle Harmonics | float | 2 | R
0x4EA4 | 0x4EA5 | 20132 | 20133 | ANG_10M_HAR_V_126th_a | Aggr 10min Phase A 126th Voltage Angle Harmonics | float | 2 | R
0x4EA6 | 0x4EA7 | 20134 | 20135 | ANG_10M_HAR_V_126th_b | Aggr 10min Phase B 126th Voltage Angle Harmonics | float | 2 | R
0x4EA8 | 0x4EA9 | 20136 | 20137 | ANG_10M_HAR_V_126th_c | Aggr 10min Phase C 126th Voltage Angle Harmonics | float | 2 | R
0x4EAA | 0x4EAB | 20138 | 20139 | ANG_10M_HAR_I_126th_a | Aggr 10min Phase A 126th Current Angle Harmonics | float | 2 | R
0x4EAC | 0x4EAD | 20140 | 20141 | ANG_10M_HAR_I_126th_b | Aggr 10min Phase B 126th Current Angle Harmonics | float | 2 | R
0x4EAE | 0x4EAF | 20142 | 20143 | ANG_10M_HAR_I_126th_c | Aggr 10min Phase C 126th Current Angle Harmonics | float | 2 | R
0x4EB0 | 0x4EB1 | 20144 | 20145 | ANG_10M_HAR_I_126th_n | Aggr 10min Phase N 126th Current Angle Harmonics | float | 2 | R
0x4EB2 | 0x4EB3 | 20146 | 20147 | ANG_10M_HAR_V_127th_a | Aggr 10min Phase A 127th Voltage Angle Harmonics | float | 2 | R
0x4EB4 | 0x4EB5 | 20148 | 20149 | ANG_10M_HAR_V_127th_b | Aggr 10min Phase B 127th Voltage Angle Harmonics | float | 2 | R
0x4EB6 | 0x4EB7 | 20150 | 20151 | ANG_10M_HAR_V_127th_c | Aggr 10min Phase C 127th Voltage Angle Harmonics | float | 2 | R
0x4EB8 | 0x4EB9 | 20152 | 20153 | ANG_10M_HAR_I_127th_a | Aggr 10min Phase A 127th Current Angle Harmonics | float | 2 | R
0x4EBA | 0x4EBB | 20154 | 20155 | ANG_10M_HAR_I_127th_b | Aggr 10min Phase B 127th Current Angle Harmonics | float | 2 | R
0x4EBC | 0x4EBD | 20156 | 20157 | ANG_10M_HAR_I_127th_c | Aggr 10min Phase C 127th Current Angle Harmonics | float | 2 | R
0x4EBE | 0x4EBF | 20158 | 20159 | ANG_10M_HAR_I_127th_n | Aggr 10min Phase N 127th Current Angle Harmonics | float | 2 | R
0x4EC0 | 0x4EC1 | 20160 | 20161 | FUND_HAR_Va_V | Aggr 10min Phase A Fundamental Voltage | float | 2 | R
0x4EC2 | 0x4EC3 | 20162 | 20163 | FUND_HAR_Vb_V | Aggr 10min Phase B Fundamental Voltage | float | 2 | R
0x4EC4 | 0x4EC5 | 20164 | 20165 | FUND_HAR_Vc_V | Aggr 10min Phase C Fundamental Voltage | float | 2 | R
0x4EC6 | 0x4EC7 | 20166 | 20167 | FUND_HAR_Ia_A | Aggr 10min Phase A Fundamental Current | float | 2 | R
0x4EC8 | 0x4EC9 | 20168 | 20169 | FUND_HAR_Ib_A | Aggr 10min Phase B Fundamental Current | float | 2 | R
0x4ECA | 0x4ECB | 20170 | 20171 | FUND_HAR_Ic_A | Aggr 10min Phase C Fundamental Current | float | 2 | R
0x4ECC | 0x4ECD | 20172 | 20173 | FUND_HAR_In_A | Aggr 10min Phase N Fundamental Current | float | 2 | R

## 2hr Aggregation
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x5000 | 0x5003 | 20480 | 20483 | 2HR_TIMESTAMP | Aggr 2hr Param Update Time Stamp | double | 4 | R
0x5004 | 0x5005 | 20484 | 20485 | 2HR_FLAG | Aggr 2hr Param Valid Flag | bool | 2 | R
0x5006 | 0x5007 | 20486 | 20487 | 2HR_EVENT_FLAG | Aggr 2hr Param Event Flag | uint32 | 2 | R
0x5008 | 0x5009 | 20488 | 20489 | 2HR_Freq_Hz | Aggr 2hr System Frequency | float | 2 | R
0x500A | 0x500B | 20490 | 20491 | 2HR_VLN_a_V | Aggr 2hr Phase A Line-to-Neutral Voltage | float | 2 | R
0x500C | 0x500D | 20492 | 20493 | 2HR_VLN_b_V | Aggr 2hr Phase B Line-to-Neutral Voltage | float | 2 | R
0x500E | 0x500F | 20494 | 20495 | 2HR_VLN_c_V | Aggr 2hr Phase C Line-to-Neutral Voltage | float | 2 | R
0x5010 | 0x5011 | 20496 | 20497 | 2HR_VLN_avg_V | Aggr 2hr Average Line-to-Neutral Voltage | float | 2 | R
0x5012 | 0x5013 | 20498 | 20499 | 2HR_VLL_ab_V | Aggr 2hr Phase AB Line-to-Line Voltage | float | 2 | R
0x5014 | 0x5015 | 20500 | 20501 | 2HR_VLL_bc_V | Aggr 2hr Phase BC Line-to-Line Voltage | float | 2 | R
0x5016 | 0x5017 | 20502 | 20503 | 2HR_VLL_ca_V | Aggr 2hr Phase CA Line-to-Line Voltage | float | 2 | R
0x5018 | 0x5019 | 20504 | 20505 | 2HR_VLL_avg_V | Aggr 2hr Average Line-to-Line Voltage | float | 2 | R
0x501A | 0x501B | 20506 | 20507 | 2HR_I_a_A | Aggr 2hr Phase A Current | float | 2 | R
0x501C | 0x501D | 20508 | 20509 | 2HR_I_b_A | Aggr 2hr Phase B Current | float | 2 | R
0x501E | 0x501F | 20510 | 20511 | 2HR_I_c_A | Aggr 2hr Phase C Current | float | 2 | R
0x5020 | 0x5021 | 20512 | 20513 | 2HR_I_n_A | Aggr 2hr Phase N Current | float | 2 | R
0x5022 | 0x5023 | 20514 | 20515 | 2HR_I_avg_A | Aggr 2hr Average Current | float | 2 | R
0x5024 | 0x5025 | 20516 | 20517 | 2HR_P_a_kW | Aggr 2hr Phase A Active Power | float | 2 | R
0x5026 | 0x5027 | 20518 | 20519 | 2HR_P_b_kW | Aggr 2hr Phase B Active Power | float | 2 | R
0x5028 | 0x5029 | 20520 | 20521 | 2HR_P_c_kW | Aggr 2hr Phase C Active Power | float | 2 | R
0x502A | 0x502B | 20522 | 20523 | 2HR_P_kW | Aggr 2hr System Active Power | float | 2 | R
0x502C | 0x502D | 20524 | 20525 | 2HR_Q_a_kvar | Aggr 2hr Phase A Reactive Power | float | 2 | R
0x502E | 0x502F | 20526 | 20527 | 2HR_Q_b_kvar | Aggr 2hr Phase B Reactive Power | float | 2 | R
0x5030 | 0x5031 | 20528 | 20529 | 2HR_Q_c_kvar | Aggr 2hr Phase C Reactive Power | float | 2 | R
0x5032 | 0x5033 | 20530 | 20531 | 2HR_Q_kvar | Aggr 2hr System Reactive Power | float | 2 | R
0x5034 | 0x5035 | 20532 | 20533 | 2HR_S_a_kVA | Aggr 2hr Phase A Apparent Power | float | 2 | R
0x5036 | 0x5037 | 20534 | 20535 | 2HR_S_b_kVA | Aggr 2hr Phase B Apparent Power | float | 2 | R
0x5038 | 0x5039 | 20536 | 20537 | 2HR_S_c_kVA | Aggr 2hr Phase C Apparent Power | float | 2 | R
0x503A | 0x503B | 20538 | 20539 | 2HR_S_kVA | Aggr 2hr System Apparent Power | float | 2 | R
0x503C | 0x503D | 20540 | 20541 | 2HR_LC_a | Aggr 2hr Phase A Load Nature | float | 2 | R
0x503E | 0x503F | 20542 | 20543 | 2HR_LC_b | Aggr 2hr Phase B Load Nature | float | 2 | R
0x5040 | 0x5041 | 20544 | 20545 | 2HR_LC_c | Aggr 2hr Phase C Load Nature | float | 2 | R
0x5042 | 0x5043 | 20546 | 20547 | 2HR_LC | Aggr 2hr System Load Nature | float | 2 | R
0x5044 | 0x5045 | 20548 | 20549 | 2HR_PF_a | Aggr 2hr Phase A Power Factor | float | 2 | R
0x5046 | 0x5047 | 20550 | 20551 | 2HR_PF_b | Aggr 2hr Phase B Power Factor | float | 2 | R
0x5048 | 0x5049 | 20552 | 20553 | 2HR_PF_c | Aggr 2hr Phase C Power Factor | float | 2 | R
0x504A | 0x504B | 20554 | 20555 | 2HR_PF | Aggr 2hr System Power Factor | float | 2 | R
0x504C | 0x504D | 20556 | 20557 | 2HR_LEAD_PF_a | Aggr 2hr Phase A Leading Power Factor | float | 2 | R
0x504E | 0x504F | 20558 | 20559 | 2HR_LEAD_PF_b | Aggr 2hr Phase B Leading Power Factor | float | 2 | R
0x5050 | 0x5051 | 20560 | 20561 | 2HR_LEAD_PF_c | Aggr 2hr Phase C Leading Power Factor | float | 2 | R
0x5052 | 0x5053 | 20562 | 20563 | 2HR_LEAD_PF | Aggr 2hr System Leading Power Factor | float | 2 | R
0x5054 | 0x5055 | 20564 | 20565 | 2HR_LAG_PF_a | Aggr 2hr Phase A Lagging Power Factor | float | 2 | R
0x5056 | 0x5057 | 20566 | 20567 | 2HR_LAG_PF_b | Aggr 2hr Phase B Lagging Power Factor | float | 2 | R
0x5058 | 0x5059 | 20568 | 20569 | 2HR_LAG_PF_c | Aggr 2hr Phase C Lagging Power Factor | float | 2 | R
0x505A | 0x505B | 20570 | 20571 | 2HR_LAG_PF | Aggr 2hr System Lagging Power Factor | float | 2 | R
0x505C | 0x505D | 20572 | 20573 | 2HR_PA_VLN_a | Aggr 2hr Phase A Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x505E | 0x505F | 20574 | 20575 | 2HR_PA_VLN_b | Aggr 2hr Phase B Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x5060 | 0x5061 | 20576 | 20577 | 2HR_PA_VLN_c | Aggr 2hr Phase C Line-to-Neutral Voltage Phase Angle | float | 2 | R
0x5062 | 0x5063 | 20578 | 20579 | 2HR_PA_VLL_ab | Aggr 2hr Phase AB Line-to-Line Voltage Phase Angle | float | 2 | R
0x5064 | 0x5065 | 20580 | 20581 | 2HR_PA_VLL_bc | Aggr 2hr Phase BC Line-to-Line Voltage Phase Angle | float | 2 | R
0x5066 | 0x5067 | 20582 | 20583 | 2HR_PA_VLL_ca | Aggr 2hr Phase CA Line-to-Line Voltage Phase Angle | float | 2 | R
0x5068 | 0x5069 | 20584 | 20585 | 2HR_PA_I_a | Aggr 2hr Phase A Current Phase Angle | float | 2 | R
0x506A | 0x506B | 20586 | 20587 | 2HR_PA_I_b | Aggr 2hr Phase B Current Phase Angle | float | 2 | R
0x506C | 0x506D | 20588 | 20589 | 2HR_PA_I_c | Aggr 2hr Phase C Current Phase Angle | float | 2 | R
0x506E | 0x506F | 20590 | 20591 | MAG_2HR_SEQ_POS_V_V | Aggr 2hr Voltage Positive Sequence Magnitude | float | 2 | R
0x5070 | 0x5071 | 20592 | 20593 | MAG_2HR_SEQ_ZERO_V_V | Aggr 2hr Voltage Zero Sequence Magnitude | float | 2 | R
0x5072 | 0x5073 | 20594 | 20595 | MAG_2HR_SEQ_NEG_V_V | Aggr 2hr Voltage Negative Sequence Magnitude | float | 2 | R
0x5074 | 0x5075 | 20596 | 20597 | MAG_2HR_SEQ_ZERO_RATIO_V_% | Aggr 2hr Voltage Zero Sequence Ratio Magnitude | float | 2 | R
0x5076 | 0x5077 | 20598 | 20599 | MAG_2HR_UNBL_V_% | Aggr 2hr Voltage Unbalance Factor Magnitude | float | 2 | R
0x5078 | 0x5079 | 20600 | 20601 | MAG_2HR_SEQ_POS_I_A | Aggr 2hr Current Positive Sequence Magnitude | float | 2 | R
0x507A | 0x507B | 20602 | 20603 | MAG_2HR_SEQ_ZERO_I_A | Aggr 2hr Current Zero Sequence Magnitude | float | 2 | R
0x507C | 0x507D | 20604 | 20605 | MAG_2HR_SEQ_NEG_I_A | Aggr 2hr Current Negative Sequence Magnitude | float | 2 | R
0x507E | 0x507F | 20606 | 20607 | MAG_2HR_SEQ_ZERO_RATIO_I_% | Aggr 2hr Current Zero Sequence Ratio Magnitude | float | 2 | R
0x5080 | 0x5081 | 20608 | 20609 | MAG_2HR_UNBL_I_% | Aggr 2hr Current Unbalance Factor Magnitude | float | 2 | R
0x5082 | 0x5083 | 20610 | 20611 | ANG_2HR_SEQ_POS_V | Aggr 2hr Voltage Positive Sequence Angle | float | 2 | R
0x5084 | 0x5085 | 20612 | 20613 | ANG_2HR_SEQ_ZERO_V | Aggr 2hr Voltage Zero Sequence Angle | float | 2 | R
0x5086 | 0x5087 | 20614 | 20615 | ANG_2HR_SEQ_NEG_V | Aggr 2hr Voltage Negative Sequence Angle | float | 2 | R
0x5088 | 0x5089 | 20616 | 20617 | ANG_2HR_SEQ_POS_I_A | Aggr 2hr Current Positive Sequence Angle | float | 2 | R
0x508A | 0x508B | 20618 | 20619 | ANG_2HR_SEQ_ZERO_I_A | Aggr 2hr Current Zero Sequence Angle | float | 2 | R
0x508C | 0x508D | 20620 | 20621 | ANG_2HR_SEQ_NEG_I_A | Aggr 2hr Current Negative Sequence Angle | float | 2 | R
0x508E | 0x508F | 20622 | 20623 | 2HR_THD_V_a_% | Aggr 2hr Phase A Voltage THD | float | 2 | R
0x5090 | 0x5091 | 20624 | 20625 | 2HR_THD_V_b_% | Aggr 2hr Phase B Voltage THD | float | 2 | R
0x5092 | 0x5093 | 20626 | 20627 | 2HR_THD_V_c_% | Aggr 2hr Phase C Voltage THD | float | 2 | R
0x5094 | 0x5095 | 20628 | 20629 | 2HR_OTHD_V_a_% | Aggr 2hr Phase A Voltage THD Odd | float | 2 | R
0x5096 | 0x5097 | 20630 | 20631 | 2HR_OTHD_V_b_% | Aggr 2hr Phase B Voltage THD Odd | float | 2 | R
0x5098 | 0x5099 | 20632 | 20633 | 2HR_OTHD_V_c_% | Aggr 2hr Phase C Voltage THD Odd | float | 2 | R
0x509A | 0x509B | 20634 | 20635 | 2HR_ETHD_V_a_% | Aggr 2hr Phase A Voltage THD Even | float | 2 | R
0x509C | 0x509D | 20636 | 20637 | 2HR_ETHD_V_b_% | Aggr 2hr Phase B Voltage THD Even | float | 2 | R
0x509E | 0x509F | 20638 | 20639 | 2HR_ETHD_V_c_% | Aggr 2hr Phase C Voltage THD Even | float | 2 | R
0x50A0 | 0x50A1 | 20640 | 20641 | 2HR_CF_V_a_% | Aggr 2hr Phase A Voltage Crest Factor | float | 2 | R
0x50A2 | 0x50A3 | 20642 | 20643 | 2HR_CF_V_b_% | Aggr 2hr Phase B Voltage Crest Factor | float | 2 | R
0x50A4 | 0x50A5 | 20644 | 20645 | 2HR_CF_V_c_% | Aggr 2hr Phase C Voltage Crest Factor | float | 2 | R
0x50A6 | 0x50A7 | 20646 | 20647 | 2HR_THD_I_a_% | Aggr 2hr Phase A Current THD | float | 2 | R
0x50A8 | 0x50A9 | 20648 | 20649 | 2HR_THD_I_b_% | Aggr 2hr Phase B Current THD | float | 2 | R
0x50AA | 0x50AB | 20650 | 20651 | 2HR_THD_I_c_% | Aggr 2hr Phase C Current THD | float | 2 | R
0x50AC | 0x50AD | 20652 | 20653 | 2HR_THD_I_n_% | Aggr 2hr Phase N Current THD | float | 2 | R
0x50AE | 0x50AF | 20654 | 20655 | 2HR_OTHD_I_a_% | Aggr 2hr Phase A Current THD Odd | float | 2 | R
0x50B0 | 0x50B1 | 20656 | 20657 | 2HR_OTHD_I_b_% | Aggr 2hr Phase B Current THD Odd | float | 2 | R
0x50B2 | 0x50B3 | 20658 | 20659 | 2HR_OTHD_I_c_% | Aggr 2hr Phase C Current THD Odd | float | 2 | R
0x50B4 | 0x50B5 | 20660 | 20661 | 2HR_OTHD_I_n_% | Aggr 2hr Phase N Current THD Odd | float | 2 | R
0x50B6 | 0x50B7 | 20662 | 20663 | 2HR_ETHD_I_a_% | Aggr 2hr Phase A Current THD Even | float | 2 | R
0x50B8 | 0x50B9 | 20664 | 20665 | 2HR_ETHD_I_b_% | Aggr 2hr Phase B Current THD Even | float | 2 | R
0x50BA | 0x50BB | 20666 | 20667 | 2HR_ETHD_I_c_% | Aggr 2hr Phase C Current THD Even | float | 2 | R
0x50BC | 0x50BD | 20668 | 20669 | 2HR_ETHD_I_n_% | Aggr 2hr Phase N Current THD Even | float | 2 | R
0x50BE | 0x50BF | 20670 | 20671 | 2HR_TDD_I_a_% | Aggr 2hr Phase A Current TDD | float | 2 | R
0x50C0 | 0x50C1 | 20672 | 20673 | 2HR_TDD_I_b_% | Aggr 2hr Phase B Current TDD | float | 2 | R
0x50C2 | 0x50C3 | 20674 | 20675 | 2HR_TDD_I_c_% | Aggr 2hr Phase C Current TDD | float | 2 | R
0x50C4 | 0x50C5 | 20676 | 20677 | 2HR_TDD_I_n_% | Aggr 2hr Phase N Current TDD | float | 2 | R
0x50C6 | 0x50C7 | 20678 | 20679 | 2HR_CF_I_a_% | Aggr 2hr Phase A Current Crest-Factor | float | 2 | R
0x50C8 | 0x50C9 | 20680 | 20681 | 2HR_CF_I_b_% | Aggr 2hr Phase B Current Crest-Factor | float | 2 | R
0x50CA | 0x50CB | 20682 | 20683 | 2HR_CF_I_c_% | Aggr 2hr Phase C Current Crest-Factor | float | 2 | R
0x50CC | 0x50CD | 20684 | 20685 | 2HR_CF_I_n_% | Aggr 2hr Phase N Current Crest-Factor | float | 2 | R
0x50CE | 0x50CF | 20686 | 20687 | 2HR_KF_I_a_% | Aggr 2hr Phase A Current K-Factor | float | 2 | R
0x50D0 | 0x50D1 | 20688 | 20689 | 2HR_KF_I_b_% | Aggr 2hr Phase B Current K-Factor | float | 2 | R
0x50D2 | 0x50D3 | 20690 | 20691 | 2HR_KF_I_c_% | Aggr 2hr Phase C Current K-Factor | float | 2 | R
0x50D4 | 0x50D5 | 20692 | 20693 | 2HR_KF_I_n_% | Aggr 2hr Phase N Current K-Factor | float | 2 | R
0x50D6 | 0x50D7 | 20694 | 20695 | 2HR_FLICK_V_a | Aggr 2hr Phase A Voltage Flicker | float | 2 | R
0x50D8 | 0x50D9 | 20696 | 20697 | 2HR_FLICK_V_b | Aggr 2hr Phase B Voltage Flicker | float | 2 | R
0x50DA | 0x50DB | 20698 | 20699 | 2HR_FLICK_V_c | Aggr 2hr Phase C Voltage Flicker | float | 2 | R
0x50DC | 0x50DD | 20700 | 20701 | MAG_2HR_HAR_V_1th_a_% | Aggr 2hr Phase A 1st Voltage Magnitude Harmonics | float | 2 | R
0x50DE | 0x50DF | 20702 | 20703 | MAG_2HR_HAR_V_1th_b_% | Aggr 2hr Phase B 1st Voltage Magnitude Harmonics | float | 2 | R
0x50E0 | 0x50E1 | 20704 | 20705 | MAG_2HR_HAR_V_1th_c_% | Aggr 2hr Phase C 1st Voltage Magnitude Harmonics | float | 2 | R
0x50E2 | 0x50E3 | 20706 | 20707 | MAG_2HR_HAR_I_1th_a_% | Aggr 2hr Phase A 1st Current Magnitude Harmonics | float | 2 | R
0x50E4 | 0x50E5 | 20708 | 20709 | MAG_2HR_HAR_I_1th_b_% | Aggr 2hr Phase B 1st Current Magnitude Harmonics | float | 2 | R
0x50E6 | 0x50E7 | 20710 | 20711 | MAG_2HR_HAR_I_1th_c_% | Aggr 2hr Phase C 1st Current Magnitude Harmonics | float | 2 | R
0x50E8 | 0x50E9 | 20712 | 20713 | MAG_2HR_HAR_I_1th_n_% | Aggr 2hr Phase N 1st Current Magnitude Harmonics | float | 2 | R
0x50EA | 0x50EB | 20714 | 20715 | MAG_2HR_HAR_V_2th_a_% | Aggr 2hr Phase A 2nd Voltage Magnitude Harmonics | float | 2 | R
0x50EC | 0x50ED | 20716 | 20717 | MAG_2HR_HAR_V_2th_b_% | Aggr 2hr Phase B 2nd Voltage Magnitude Harmonics | float | 2 | R
0x50EE | 0x50EF | 20718 | 20719 | MAG_2HR_HAR_V_2th_c_% | Aggr 2hr Phase C 2nd Voltage Magnitude Harmonics | float | 2 | R
0x50F0 | 0x50F1 | 20720 | 20721 | MAG_2HR_HAR_I_2th_a_% | Aggr 2hr Phase A 2nd Current Magnitude Harmonics | float | 2 | R
0x50F2 | 0x50F3 | 20722 | 20723 | MAG_2HR_HAR_I_2th_b_% | Aggr 2hr Phase B 2nd Current Magnitude Harmonics | float | 2 | R
0x50F4 | 0x50F5 | 20724 | 20725 | MAG_2HR_HAR_I_2th_c_% | Aggr 2hr Phase C 2nd Current Magnitude Harmonics | float | 2 | R
0x50F6 | 0x50F7 | 20726 | 20727 | MAG_2HR_HAR_I_2th_n_% | Aggr 2hr Phase N 2nd Current Magnitude Harmonics | float | 2 | R
0x50F8 | 0x50F9 | 20728 | 20729 | MAG_2HR_HAR_V_3th_a_% | Aggr 2hr Phase A 3rd Voltage Magnitude Harmonics | float | 2 | R
0x50FA | 0x50FB | 20730 | 20731 | MAG_2HR_HAR_V_3th_b_% | Aggr 2hr Phase B 3rd Voltage Magnitude Harmonics | float | 2 | R
0x50FC | 0x50FD | 20732 | 20733 | MAG_2HR_HAR_V_3th_c_% | Aggr 2hr Phase C 3rd Voltage Magnitude Harmonics | float | 2 | R
0x50FE | 0x50FF | 20734 | 20735 | MAG_2HR_HAR_I_3th_a_% | Aggr 2hr Phase A 3rd Current Magnitude Harmonics | float | 2 | R
0x5100 | 0x5101 | 20736 | 20737 | MAG_2HR_HAR_I_3th_b_% | Aggr 2hr Phase B 3rd Current Magnitude Harmonics | float | 2 | R
0x5102 | 0x5103 | 20738 | 20739 | MAG_2HR_HAR_I_3th_c_% | Aggr 2hr Phase C 3rd Current Magnitude Harmonics | float | 2 | R
0x5104 | 0x5105 | 20740 | 20741 | MAG_2HR_HAR_I_3th_n_% | Aggr 2hr Phase N 3rd Current Magnitude Harmonics | float | 2 | R
0x5106 | 0x5107 | 20742 | 20743 | MAG_2HR_HAR_V_4th_a_% | Aggr 2hr Phase A 4th Voltage Magnitude Harmonics | float | 2 | R
0x5108 | 0x5109 | 20744 | 20745 | MAG_2HR_HAR_V_4th_b_% | Aggr 2hr Phase B 4th Voltage Magnitude Harmonics | float | 2 | R
0x510A | 0x510B | 20746 | 20747 | MAG_2HR_HAR_V_4th_c_% | Aggr 2hr Phase C 4th Voltage Magnitude Harmonics | float | 2 | R
0x510C | 0x510D | 20748 | 20749 | MAG_2HR_HAR_I_4th_a_% | Aggr 2hr Phase A 4th Current Magnitude Harmonics | float | 2 | R
0x510E | 0x510F | 20750 | 20751 | MAG_2HR_HAR_I_4th_b_% | Aggr 2hr Phase B 4th Current Magnitude Harmonics | float | 2 | R
0x5110 | 0x5111 | 20752 | 20753 | MAG_2HR_HAR_I_4th_c_% | Aggr 2hr Phase C 4th Current Magnitude Harmonics | float | 2 | R
0x5112 | 0x5113 | 20754 | 20755 | MAG_2HR_HAR_I_4th_n_% | Aggr 2hr Phase N 4th Current Magnitude Harmonics | float | 2 | R
0x5114 | 0x5115 | 20756 | 20757 | MAG_2HR_HAR_V_5th_a_% | Aggr 2hr Phase A 5th Voltage Magnitude Harmonics | float | 2 | R
0x5116 | 0x5117 | 20758 | 20759 | MAG_2HR_HAR_V_5th_b_% | Aggr 2hr Phase B 5th Voltage Magnitude Harmonics | float | 2 | R
0x5118 | 0x5119 | 20760 | 20761 | MAG_2HR_HAR_V_5th_c_% | Aggr 2hr Phase C 5th Voltage Magnitude Harmonics | float | 2 | R
0x511A | 0x511B | 20762 | 20763 | MAG_2HR_HAR_I_5th_a_% | Aggr 2hr Phase A 5th Current Magnitude Harmonics | float | 2 | R
0x511C | 0x511D | 20764 | 20765 | MAG_2HR_HAR_I_5th_b_% | Aggr 2hr Phase B 5th Current Magnitude Harmonics | float | 2 | R
0x511E | 0x511F | 20766 | 20767 | MAG_2HR_HAR_I_5th_c_% | Aggr 2hr Phase C 5th Current Magnitude Harmonics | float | 2 | R
0x5120 | 0x5121 | 20768 | 20769 | MAG_2HR_HAR_I_5th_n_% | Aggr 2hr Phase N 5th Current Magnitude Harmonics | float | 2 | R
0x5122 | 0x5123 | 20770 | 20771 | MAG_2HR_HAR_V_6th_a_% | Aggr 2hr Phase A 6th Voltage Magnitude Harmonics | float | 2 | R
0x5124 | 0x5125 | 20772 | 20773 | MAG_2HR_HAR_V_6th_b_% | Aggr 2hr Phase B 6th Voltage Magnitude Harmonics | float | 2 | R
0x5126 | 0x5127 | 20774 | 20775 | MAG_2HR_HAR_V_6th_c_% | Aggr 2hr Phase C 6th Voltage Magnitude Harmonics | float | 2 | R
0x5128 | 0x5129 | 20776 | 20777 | MAG_2HR_HAR_I_6th_a_% | Aggr 2hr Phase A 6th Current Magnitude Harmonics | float | 2 | R
0x512A | 0x512B | 20778 | 20779 | MAG_2HR_HAR_I_6th_b_% | Aggr 2hr Phase B 6th Current Magnitude Harmonics | float | 2 | R
0x512C | 0x512D | 20780 | 20781 | MAG_2HR_HAR_I_6th_c_% | Aggr 2hr Phase C 6th Current Magnitude Harmonics | float | 2 | R
0x512E | 0x512F | 20782 | 20783 | MAG_2HR_HAR_I_6th_n_% | Aggr 2hr Phase N 6th Current Magnitude Harmonics | float | 2 | R
0x5130 | 0x5131 | 20784 | 20785 | MAG_2HR_HAR_V_7th_a_% | Aggr 2hr Phase A 7th Voltage Magnitude Harmonics | float | 2 | R
0x5132 | 0x5133 | 20786 | 20787 | MAG_2HR_HAR_V_7th_b_% | Aggr 2hr Phase B 7th Voltage Magnitude Harmonics | float | 2 | R
0x5134 | 0x5135 | 20788 | 20789 | MAG_2HR_HAR_V_7th_c_% | Aggr 2hr Phase C 7th Voltage Magnitude Harmonics | float | 2 | R
0x5136 | 0x5137 | 20790 | 20791 | MAG_2HR_HAR_I_7th_a_% | Aggr 2hr Phase A 7th Current Magnitude Harmonics | float | 2 | R
0x5138 | 0x5139 | 20792 | 20793 | MAG_2HR_HAR_I_7th_b_% | Aggr 2hr Phase B 7th Current Magnitude Harmonics | float | 2 | R
0x513A | 0x513B | 20794 | 20795 | MAG_2HR_HAR_I_7th_c_% | Aggr 2hr Phase C 7th Current Magnitude Harmonics | float | 2 | R
0x513C | 0x513D | 20796 | 20797 | MAG_2HR_HAR_I_7th_n_% | Aggr 2hr Phase N 7th Current Magnitude Harmonics | float | 2 | R
0x513E | 0x513F | 20798 | 20799 | MAG_2HR_HAR_V_8th_a_% | Aggr 2hr Phase A 8th Voltage Magnitude Harmonics | float | 2 | R
0x5140 | 0x5141 | 20800 | 20801 | MAG_2HR_HAR_V_8th_b_% | Aggr 2hr Phase B 8th Voltage Magnitude Harmonics | float | 2 | R
0x5142 | 0x5143 | 20802 | 20803 | MAG_2HR_HAR_V_8th_c_% | Aggr 2hr Phase C 8th Voltage Magnitude Harmonics | float | 2 | R
0x5144 | 0x5145 | 20804 | 20805 | MAG_2HR_HAR_I_8th_a_% | Aggr 2hr Phase A 8th Current Magnitude Harmonics | float | 2 | R
0x5146 | 0x5147 | 20806 | 20807 | MAG_2HR_HAR_I_8th_b_% | Aggr 2hr Phase B 8th Current Magnitude Harmonics | float | 2 | R
0x5148 | 0x5149 | 20808 | 20809 | MAG_2HR_HAR_I_8th_c_% | Aggr 2hr Phase C 8th Current Magnitude Harmonics | float | 2 | R
0x514A | 0x514B | 20810 | 20811 | MAG_2HR_HAR_I_8th_n_% | Aggr 2hr Phase N 8th Current Magnitude Harmonics | float | 2 | R
0x514C | 0x514D | 20812 | 20813 | MAG_2HR_HAR_V_9th_a_% | Aggr 2hr Phase A 9th Voltage Magnitude Harmonics | float | 2 | R
0x514E | 0x514F | 20814 | 20815 | MAG_2HR_HAR_V_9th_b_% | Aggr 2hr Phase B 9th Voltage Magnitude Harmonics | float | 2 | R
0x5150 | 0x5151 | 20816 | 20817 | MAG_2HR_HAR_V_9th_c_% | Aggr 2hr Phase C 9th Voltage Magnitude Harmonics | float | 2 | R
0x5152 | 0x5153 | 20818 | 20819 | MAG_2HR_HAR_I_9th_a_% | Aggr 2hr Phase A 9th Current Magnitude Harmonics | float | 2 | R
0x5154 | 0x5155 | 20820 | 20821 | MAG_2HR_HAR_I_9th_b_% | Aggr 2hr Phase B 9th Current Magnitude Harmonics | float | 2 | R
0x5156 | 0x5157 | 20822 | 20823 | MAG_2HR_HAR_I_9th_c_% | Aggr 2hr Phase C 9th Current Magnitude Harmonics | float | 2 | R
0x5158 | 0x5159 | 20824 | 20825 | MAG_2HR_HAR_I_9th_n_% | Aggr 2hr Phase N 9th Current Magnitude Harmonics | float | 2 | R
0x515A | 0x515B | 20826 | 20827 | MAG_2HR_HAR_V_10th_a_% | Aggr 2hr Phase A 10th Voltage Magnitude Harmonics | float | 2 | R
0x515C | 0x515D | 20828 | 20829 | MAG_2HR_HAR_V_10th_b_% | Aggr 2hr Phase B 10th Voltage Magnitude Harmonics | float | 2 | R
0x515E | 0x515F | 20830 | 20831 | MAG_2HR_HAR_V_10th_c_% | Aggr 2hr Phase C 10th Voltage Magnitude Harmonics | float | 2 | R
0x5160 | 0x5161 | 20832 | 20833 | MAG_2HR_HAR_I_10th_a_% | Aggr 2hr Phase A 10th Current Magnitude Harmonics | float | 2 | R
0x5162 | 0x5163 | 20834 | 20835 | MAG_2HR_HAR_I_10th_b_% | Aggr 2hr Phase B 10th Current Magnitude Harmonics | float | 2 | R
0x5164 | 0x5165 | 20836 | 20837 | MAG_2HR_HAR_I_10th_c_% | Aggr 2hr Phase C 10th Current Magnitude Harmonics | float | 2 | R
0x5166 | 0x5167 | 20838 | 20839 | MAG_2HR_HAR_I_10th_n_% | Aggr 2hr Phase N 10th Current Magnitude Harmonics | float | 2 | R
0x5168 | 0x5169 | 20840 | 20841 | MAG_2HR_HAR_V_11th_a_% | Aggr 2hr Phase A 11st Voltage Magnitude Harmonics | float | 2 | R
0x516A | 0x516B | 20842 | 20843 | MAG_2HR_HAR_V_11th_b_% | Aggr 2hr Phase B 11st Voltage Magnitude Harmonics | float | 2 | R
0x516C | 0x516D | 20844 | 20845 | MAG_2HR_HAR_V_11th_c_% | Aggr 2hr Phase C 11st Voltage Magnitude Harmonics | float | 2 | R
0x516E | 0x516F | 20846 | 20847 | MAG_2HR_HAR_I_11th_a_% | Aggr 2hr Phase A 11st Current Magnitude Harmonics | float | 2 | R
0x5170 | 0x5171 | 20848 | 20849 | MAG_2HR_HAR_I_11th_b_% | Aggr 2hr Phase B 11st Current Magnitude Harmonics | float | 2 | R
0x5172 | 0x5173 | 20850 | 20851 | MAG_2HR_HAR_I_11th_c_% | Aggr 2hr Phase C 11st Current Magnitude Harmonics | float | 2 | R
0x5174 | 0x5175 | 20852 | 20853 | MAG_2HR_HAR_I_11th_n_% | Aggr 2hr Phase N 11st Current Magnitude Harmonics | float | 2 | R
0x5176 | 0x5177 | 20854 | 20855 | MAG_2HR_HAR_V_12th_a_% | Aggr 2hr Phase A 12nd Voltage Magnitude Harmonics | float | 2 | R
0x5178 | 0x5179 | 20856 | 20857 | MAG_2HR_HAR_V_12th_b_% | Aggr 2hr Phase B 12nd Voltage Magnitude Harmonics | float | 2 | R
0x517A | 0x517B | 20858 | 20859 | MAG_2HR_HAR_V_12th_c_% | Aggr 2hr Phase C 12nd Voltage Magnitude Harmonics | float | 2 | R
0x517C | 0x517D | 20860 | 20861 | MAG_2HR_HAR_I_12th_a_% | Aggr 2hr Phase A 12nd Current Magnitude Harmonics | float | 2 | R
0x517E | 0x517F | 20862 | 20863 | MAG_2HR_HAR_I_12th_b_% | Aggr 2hr Phase B 12nd Current Magnitude Harmonics | float | 2 | R
0x5180 | 0x5181 | 20864 | 20865 | MAG_2HR_HAR_I_12th_c_% | Aggr 2hr Phase C 12nd Current Magnitude Harmonics | float | 2 | R
0x5182 | 0x5183 | 20866 | 20867 | MAG_2HR_HAR_I_12th_n_% | Aggr 2hr Phase N 12nd Current Magnitude Harmonics | float | 2 | R
0x5184 | 0x5185 | 20868 | 20869 | MAG_2HR_HAR_V_13th_a_% | Aggr 2hr Phase A 13rd Voltage Magnitude Harmonics | float | 2 | R
0x5186 | 0x5187 | 20870 | 20871 | MAG_2HR_HAR_V_13th_b_% | Aggr 2hr Phase B 13rd Voltage Magnitude Harmonics | float | 2 | R
0x5188 | 0x5189 | 20872 | 20873 | MAG_2HR_HAR_V_13th_c_% | Aggr 2hr Phase C 13rd Voltage Magnitude Harmonics | float | 2 | R
0x518A | 0x518B | 20874 | 20875 | MAG_2HR_HAR_I_13th_a_% | Aggr 2hr Phase A 13rd Current Magnitude Harmonics | float | 2 | R
0x518C | 0x518D | 20876 | 20877 | MAG_2HR_HAR_I_13th_b_% | Aggr 2hr Phase B 13rd Current Magnitude Harmonics | float | 2 | R
0x518E | 0x518F | 20878 | 20879 | MAG_2HR_HAR_I_13th_c_% | Aggr 2hr Phase C 13rd Current Magnitude Harmonics | float | 2 | R
0x5190 | 0x5191 | 20880 | 20881 | MAG_2HR_HAR_I_13th_n_% | Aggr 2hr Phase N 13rd Current Magnitude Harmonics | float | 2 | R
0x5192 | 0x5193 | 20882 | 20883 | MAG_2HR_HAR_V_14th_a_% | Aggr 2hr Phase A 14th Voltage Magnitude Harmonics | float | 2 | R
0x5194 | 0x5195 | 20884 | 20885 | MAG_2HR_HAR_V_14th_b_% | Aggr 2hr Phase B 14th Voltage Magnitude Harmonics | float | 2 | R
0x5196 | 0x5197 | 20886 | 20887 | MAG_2HR_HAR_V_14th_c_% | Aggr 2hr Phase C 14th Voltage Magnitude Harmonics | float | 2 | R
0x5198 | 0x5199 | 20888 | 20889 | MAG_2HR_HAR_I_14th_a_% | Aggr 2hr Phase A 14th Current Magnitude Harmonics | float | 2 | R
0x519A | 0x519B | 20890 | 20891 | MAG_2HR_HAR_I_14th_b_% | Aggr 2hr Phase B 14th Current Magnitude Harmonics | float | 2 | R
0x519C | 0x519D | 20892 | 20893 | MAG_2HR_HAR_I_14th_c_% | Aggr 2hr Phase C 14th Current Magnitude Harmonics | float | 2 | R
0x519E | 0x519F | 20894 | 20895 | MAG_2HR_HAR_I_14th_n_% | Aggr 2hr Phase N 14th Current Magnitude Harmonics | float | 2 | R
0x51A0 | 0x51A1 | 20896 | 20897 | MAG_2HR_HAR_V_15th_a_% | Aggr 2hr Phase A 15th Voltage Magnitude Harmonics | float | 2 | R
0x51A2 | 0x51A3 | 20898 | 20899 | MAG_2HR_HAR_V_15th_b_% | Aggr 2hr Phase B 15th Voltage Magnitude Harmonics | float | 2 | R
0x51A4 | 0x51A5 | 20900 | 20901 | MAG_2HR_HAR_V_15th_c_% | Aggr 2hr Phase C 15th Voltage Magnitude Harmonics | float | 2 | R
0x51A6 | 0x51A7 | 20902 | 20903 | MAG_2HR_HAR_I_15th_a_% | Aggr 2hr Phase A 15th Current Magnitude Harmonics | float | 2 | R
0x51A8 | 0x51A9 | 20904 | 20905 | MAG_2HR_HAR_I_15th_b_% | Aggr 2hr Phase B 15th Current Magnitude Harmonics | float | 2 | R
0x51AA | 0x51AB | 20906 | 20907 | MAG_2HR_HAR_I_15th_c_% | Aggr 2hr Phase C 15th Current Magnitude Harmonics | float | 2 | R
0x51AC | 0x51AD | 20908 | 20909 | MAG_2HR_HAR_I_15th_n_% | Aggr 2hr Phase N 15th Current Magnitude Harmonics | float | 2 | R
0x51AE | 0x51AF | 20910 | 20911 | MAG_2HR_HAR_V_16th_a_% | Aggr 2hr Phase A 16th Voltage Magnitude Harmonics | float | 2 | R
0x51B0 | 0x51B1 | 20912 | 20913 | MAG_2HR_HAR_V_16th_b_% | Aggr 2hr Phase B 16th Voltage Magnitude Harmonics | float | 2 | R
0x51B2 | 0x51B3 | 20914 | 20915 | MAG_2HR_HAR_V_16th_c_% | Aggr 2hr Phase C 16th Voltage Magnitude Harmonics | float | 2 | R
0x51B4 | 0x51B5 | 20916 | 20917 | MAG_2HR_HAR_I_16th_a_% | Aggr 2hr Phase A 16th Current Magnitude Harmonics | float | 2 | R
0x51B6 | 0x51B7 | 20918 | 20919 | MAG_2HR_HAR_I_16th_b_% | Aggr 2hr Phase B 16th Current Magnitude Harmonics | float | 2 | R
0x51B8 | 0x51B9 | 20920 | 20921 | MAG_2HR_HAR_I_16th_c_% | Aggr 2hr Phase C 16th Current Magnitude Harmonics | float | 2 | R
0x51BA | 0x51BB | 20922 | 20923 | MAG_2HR_HAR_I_16th_n_% | Aggr 2hr Phase N 16th Current Magnitude Harmonics | float | 2 | R
0x51BC | 0x51BD | 20924 | 20925 | MAG_2HR_HAR_V_17th_a_% | Aggr 2hr Phase A 17th Voltage Magnitude Harmonics | float | 2 | R
0x51BE | 0x51BF | 20926 | 20927 | MAG_2HR_HAR_V_17th_b_% | Aggr 2hr Phase B 17th Voltage Magnitude Harmonics | float | 2 | R
0x51C0 | 0x51C1 | 20928 | 20929 | MAG_2HR_HAR_V_17th_c_% | Aggr 2hr Phase C 17th Voltage Magnitude Harmonics | float | 2 | R
0x51C2 | 0x51C3 | 20930 | 20931 | MAG_2HR_HAR_I_17th_a_% | Aggr 2hr Phase A 17th Current Magnitude Harmonics | float | 2 | R
0x51C4 | 0x51C5 | 20932 | 20933 | MAG_2HR_HAR_I_17th_b_% | Aggr 2hr Phase B 17th Current Magnitude Harmonics | float | 2 | R
0x51C6 | 0x51C7 | 20934 | 20935 | MAG_2HR_HAR_I_17th_c_% | Aggr 2hr Phase C 17th Current Magnitude Harmonics | float | 2 | R
0x51C8 | 0x51C9 | 20936 | 20937 | MAG_2HR_HAR_I_17th_n_% | Aggr 2hr Phase N 17th Current Magnitude Harmonics | float | 2 | R
0x51CA | 0x51CB | 20938 | 20939 | MAG_2HR_HAR_V_18th_a_% | Aggr 2hr Phase A 18th Voltage Magnitude Harmonics | float | 2 | R
0x51CC | 0x51CD | 20940 | 20941 | MAG_2HR_HAR_V_18th_b_% | Aggr 2hr Phase B 18th Voltage Magnitude Harmonics | float | 2 | R
0x51CE | 0x51CF | 20942 | 20943 | MAG_2HR_HAR_V_18th_c_% | Aggr 2hr Phase C 18th Voltage Magnitude Harmonics | float | 2 | R
0x51D0 | 0x51D1 | 20944 | 20945 | MAG_2HR_HAR_I_18th_a_% | Aggr 2hr Phase A 18th Current Magnitude Harmonics | float | 2 | R
0x51D2 | 0x51D3 | 20946 | 20947 | MAG_2HR_HAR_I_18th_b_% | Aggr 2hr Phase B 18th Current Magnitude Harmonics | float | 2 | R
0x51D4 | 0x51D5 | 20948 | 20949 | MAG_2HR_HAR_I_18th_c_% | Aggr 2hr Phase C 18th Current Magnitude Harmonics | float | 2 | R
0x51D6 | 0x51D7 | 20950 | 20951 | MAG_2HR_HAR_I_18th_n_% | Aggr 2hr Phase N 18th Current Magnitude Harmonics | float | 2 | R
0x51D8 | 0x51D9 | 20952 | 20953 | MAG_2HR_HAR_V_19th_a_% | Aggr 2hr Phase A 19th Voltage Magnitude Harmonics | float | 2 | R
0x51DA | 0x51DB | 20954 | 20955 | MAG_2HR_HAR_V_19th_b_% | Aggr 2hr Phase B 19th Voltage Magnitude Harmonics | float | 2 | R
0x51DC | 0x51DD | 20956 | 20957 | MAG_2HR_HAR_V_19th_c_% | Aggr 2hr Phase C 19th Voltage Magnitude Harmonics | float | 2 | R
0x51DE | 0x51DF | 20958 | 20959 | MAG_2HR_HAR_I_19th_a_% | Aggr 2hr Phase A 19th Current Magnitude Harmonics | float | 2 | R
0x51E0 | 0x51E1 | 20960 | 20961 | MAG_2HR_HAR_I_19th_b_% | Aggr 2hr Phase B 19th Current Magnitude Harmonics | float | 2 | R
0x51E2 | 0x51E3 | 20962 | 20963 | MAG_2HR_HAR_I_19th_c_% | Aggr 2hr Phase C 19th Current Magnitude Harmonics | float | 2 | R
0x51E4 | 0x51E5 | 20964 | 20965 | MAG_2HR_HAR_I_19th_n_% | Aggr 2hr Phase N 19th Current Magnitude Harmonics | float | 2 | R
0x51E6 | 0x51E7 | 20966 | 20967 | MAG_2HR_HAR_V_20th_a_% | Aggr 2hr Phase A 20th Voltage Magnitude Harmonics | float | 2 | R
0x51E8 | 0x51E9 | 20968 | 20969 | MAG_2HR_HAR_V_20th_b_% | Aggr 2hr Phase B 20th Voltage Magnitude Harmonics | float | 2 | R
0x51EA | 0x51EB | 20970 | 20971 | MAG_2HR_HAR_V_20th_c_% | Aggr 2hr Phase C 20th Voltage Magnitude Harmonics | float | 2 | R
0x51EC | 0x51ED | 20972 | 20973 | MAG_2HR_HAR_I_20th_a_% | Aggr 2hr Phase A 20th Current Magnitude Harmonics | float | 2 | R
0x51EE | 0x51EF | 20974 | 20975 | MAG_2HR_HAR_I_20th_b_% | Aggr 2hr Phase B 20th Current Magnitude Harmonics | float | 2 | R
0x51F0 | 0x51F1 | 20976 | 20977 | MAG_2HR_HAR_I_20th_c_% | Aggr 2hr Phase C 20th Current Magnitude Harmonics | float | 2 | R
0x51F2 | 0x51F3 | 20978 | 20979 | MAG_2HR_HAR_I_20th_n_% | Aggr 2hr Phase N 20th Current Magnitude Harmonics | float | 2 | R
0x51F4 | 0x51F5 | 20980 | 20981 | MAG_2HR_HAR_V_21th_a_% | Aggr 2hr Phase A 21st Voltage Magnitude Harmonics | float | 2 | R
0x51F6 | 0x51F7 | 20982 | 20983 | MAG_2HR_HAR_V_21th_b_% | Aggr 2hr Phase B 21st Voltage Magnitude Harmonics | float | 2 | R
0x51F8 | 0x51F9 | 20984 | 20985 | MAG_2HR_HAR_V_21th_c_% | Aggr 2hr Phase C 21st Voltage Magnitude Harmonics | float | 2 | R
0x51FA | 0x51FB | 20986 | 20987 | MAG_2HR_HAR_I_21th_a_% | Aggr 2hr Phase A 21st Current Magnitude Harmonics | float | 2 | R
0x51FC | 0x51FD | 20988 | 20989 | MAG_2HR_HAR_I_21th_b_% | Aggr 2hr Phase B 21st Current Magnitude Harmonics | float | 2 | R
0x51FE | 0x51FF | 20990 | 20991 | MAG_2HR_HAR_I_21th_c_% | Aggr 2hr Phase C 21st Current Magnitude Harmonics | float | 2 | R
0x5200 | 0x5201 | 20992 | 20993 | MAG_2HR_HAR_I_21th_n_% | Aggr 2hr Phase N 21st Current Magnitude Harmonics | float | 2 | R
0x5202 | 0x5203 | 20994 | 20995 | MAG_2HR_HAR_V_22th_a_% | Aggr 2hr Phase A 22nd Voltage Magnitude Harmonics | float | 2 | R
0x5204 | 0x5205 | 20996 | 20997 | MAG_2HR_HAR_V_22th_b_% | Aggr 2hr Phase B 22nd Voltage Magnitude Harmonics | float | 2 | R
0x5206 | 0x5207 | 20998 | 20999 | MAG_2HR_HAR_V_22th_c_% | Aggr 2hr Phase C 22nd Voltage Magnitude Harmonics | float | 2 | R
0x5208 | 0x5209 | 21000 | 21001 | MAG_2HR_HAR_I_22th_a_% | Aggr 2hr Phase A 22nd Current Magnitude Harmonics | float | 2 | R
0x520A | 0x520B | 21002 | 21003 | MAG_2HR_HAR_I_22th_b_% | Aggr 2hr Phase B 22nd Current Magnitude Harmonics | float | 2 | R
0x520C | 0x520D | 21004 | 21005 | MAG_2HR_HAR_I_22th_c_% | Aggr 2hr Phase C 22nd Current Magnitude Harmonics | float | 2 | R
0x520E | 0x520F | 21006 | 21007 | MAG_2HR_HAR_I_22th_n_% | Aggr 2hr Phase N 22nd Current Magnitude Harmonics | float | 2 | R
0x5210 | 0x5211 | 21008 | 21009 | MAG_2HR_HAR_V_23th_a_% | Aggr 2hr Phase A 23rd Voltage Magnitude Harmonics | float | 2 | R
0x5212 | 0x5213 | 21010 | 21011 | MAG_2HR_HAR_V_23th_b_% | Aggr 2hr Phase B 23rd Voltage Magnitude Harmonics | float | 2 | R
0x5214 | 0x5215 | 21012 | 21013 | MAG_2HR_HAR_V_23th_c_% | Aggr 2hr Phase C 23rd Voltage Magnitude Harmonics | float | 2 | R
0x5216 | 0x5217 | 21014 | 21015 | MAG_2HR_HAR_I_23th_a_% | Aggr 2hr Phase A 23rd Current Magnitude Harmonics | float | 2 | R
0x5218 | 0x5219 | 21016 | 21017 | MAG_2HR_HAR_I_23th_b_% | Aggr 2hr Phase B 23rd Current Magnitude Harmonics | float | 2 | R
0x521A | 0x521B | 21018 | 21019 | MAG_2HR_HAR_I_23th_c_% | Aggr 2hr Phase C 23rd Current Magnitude Harmonics | float | 2 | R
0x521C | 0x521D | 21020 | 21021 | MAG_2HR_HAR_I_23th_n_% | Aggr 2hr Phase N 23rd Current Magnitude Harmonics | float | 2 | R
0x521E | 0x521F | 21022 | 21023 | MAG_2HR_HAR_V_24th_a_% | Aggr 2hr Phase A 24th Voltage Magnitude Harmonics | float | 2 | R
0x5220 | 0x5221 | 21024 | 21025 | MAG_2HR_HAR_V_24th_b_% | Aggr 2hr Phase B 24th Voltage Magnitude Harmonics | float | 2 | R
0x5222 | 0x5223 | 21026 | 21027 | MAG_2HR_HAR_V_24th_c_% | Aggr 2hr Phase C 24th Voltage Magnitude Harmonics | float | 2 | R
0x5224 | 0x5225 | 21028 | 21029 | MAG_2HR_HAR_I_24th_a_% | Aggr 2hr Phase A 24th Current Magnitude Harmonics | float | 2 | R
0x5226 | 0x5227 | 21030 | 21031 | MAG_2HR_HAR_I_24th_b_% | Aggr 2hr Phase B 24th Current Magnitude Harmonics | float | 2 | R
0x5228 | 0x5229 | 21032 | 21033 | MAG_2HR_HAR_I_24th_c_% | Aggr 2hr Phase C 24th Current Magnitude Harmonics | float | 2 | R
0x522A | 0x522B | 21034 | 21035 | MAG_2HR_HAR_I_24th_n_% | Aggr 2hr Phase N 24th Current Magnitude Harmonics | float | 2 | R
0x522C | 0x522D | 21036 | 21037 | MAG_2HR_HAR_V_25th_a_% | Aggr 2hr Phase A 25th Voltage Magnitude Harmonics | float | 2 | R
0x522E | 0x522F | 21038 | 21039 | MAG_2HR_HAR_V_25th_b_% | Aggr 2hr Phase B 25th Voltage Magnitude Harmonics | float | 2 | R
0x5230 | 0x5231 | 21040 | 21041 | MAG_2HR_HAR_V_25th_c_% | Aggr 2hr Phase C 25th Voltage Magnitude Harmonics | float | 2 | R
0x5232 | 0x5233 | 21042 | 21043 | MAG_2HR_HAR_I_25th_a_% | Aggr 2hr Phase A 25th Current Magnitude Harmonics | float | 2 | R
0x5234 | 0x5235 | 21044 | 21045 | MAG_2HR_HAR_I_25th_b_% | Aggr 2hr Phase B 25th Current Magnitude Harmonics | float | 2 | R
0x5236 | 0x5237 | 21046 | 21047 | MAG_2HR_HAR_I_25th_c_% | Aggr 2hr Phase C 25th Current Magnitude Harmonics | float | 2 | R
0x5238 | 0x5239 | 21048 | 21049 | MAG_2HR_HAR_I_25th_n_% | Aggr 2hr Phase N 25th Current Magnitude Harmonics | float | 2 | R
0x523A | 0x523B | 21050 | 21051 | MAG_2HR_HAR_V_26th_a_% | Aggr 2hr Phase A 26th Voltage Magnitude Harmonics | float | 2 | R
0x523C | 0x523D | 21052 | 21053 | MAG_2HR_HAR_V_26th_b_% | Aggr 2hr Phase B 26th Voltage Magnitude Harmonics | float | 2 | R
0x523E | 0x523F | 21054 | 21055 | MAG_2HR_HAR_V_26th_c_% | Aggr 2hr Phase C 26th Voltage Magnitude Harmonics | float | 2 | R
0x5240 | 0x5241 | 21056 | 21057 | MAG_2HR_HAR_I_26th_a_% | Aggr 2hr Phase A 26th Current Magnitude Harmonics | float | 2 | R
0x5242 | 0x5243 | 21058 | 21059 | MAG_2HR_HAR_I_26th_b_% | Aggr 2hr Phase B 26th Current Magnitude Harmonics | float | 2 | R
0x5244 | 0x5245 | 21060 | 21061 | MAG_2HR_HAR_I_26th_c_% | Aggr 2hr Phase C 26th Current Magnitude Harmonics | float | 2 | R
0x5246 | 0x5247 | 21062 | 21063 | MAG_2HR_HAR_I_26th_n_% | Aggr 2hr Phase N 26th Current Magnitude Harmonics | float | 2 | R
0x5248 | 0x5249 | 21064 | 21065 | MAG_2HR_HAR_V_27th_a_% | Aggr 2hr Phase A 27th Voltage Magnitude Harmonics | float | 2 | R
0x524A | 0x524B | 21066 | 21067 | MAG_2HR_HAR_V_27th_b_% | Aggr 2hr Phase B 27th Voltage Magnitude Harmonics | float | 2 | R
0x524C | 0x524D | 21068 | 21069 | MAG_2HR_HAR_V_27th_c_% | Aggr 2hr Phase C 27th Voltage Magnitude Harmonics | float | 2 | R
0x524E | 0x524F | 21070 | 21071 | MAG_2HR_HAR_I_27th_a_% | Aggr 2hr Phase A 27th Current Magnitude Harmonics | float | 2 | R
0x5250 | 0x5251 | 21072 | 21073 | MAG_2HR_HAR_I_27th_b_% | Aggr 2hr Phase B 27th Current Magnitude Harmonics | float | 2 | R
0x5252 | 0x5253 | 21074 | 21075 | MAG_2HR_HAR_I_27th_c_% | Aggr 2hr Phase C 27th Current Magnitude Harmonics | float | 2 | R
0x5254 | 0x5255 | 21076 | 21077 | MAG_2HR_HAR_I_27th_n_% | Aggr 2hr Phase N 27th Current Magnitude Harmonics | float | 2 | R
0x5256 | 0x5257 | 21078 | 21079 | MAG_2HR_HAR_V_28th_a_% | Aggr 2hr Phase A 28th Voltage Magnitude Harmonics | float | 2 | R
0x5258 | 0x5259 | 21080 | 21081 | MAG_2HR_HAR_V_28th_b_% | Aggr 2hr Phase B 28th Voltage Magnitude Harmonics | float | 2 | R
0x525A | 0x525B | 21082 | 21083 | MAG_2HR_HAR_V_28th_c_% | Aggr 2hr Phase C 28th Voltage Magnitude Harmonics | float | 2 | R
0x525C | 0x525D | 21084 | 21085 | MAG_2HR_HAR_I_28th_a_% | Aggr 2hr Phase A 28th Current Magnitude Harmonics | float | 2 | R
0x525E | 0x525F | 21086 | 21087 | MAG_2HR_HAR_I_28th_b_% | Aggr 2hr Phase B 28th Current Magnitude Harmonics | float | 2 | R
0x5260 | 0x5261 | 21088 | 21089 | MAG_2HR_HAR_I_28th_c_% | Aggr 2hr Phase C 28th Current Magnitude Harmonics | float | 2 | R
0x5262 | 0x5263 | 21090 | 21091 | MAG_2HR_HAR_I_28th_n_% | Aggr 2hr Phase N 28th Current Magnitude Harmonics | float | 2 | R
0x5264 | 0x5265 | 21092 | 21093 | MAG_2HR_HAR_V_29th_a_% | Aggr 2hr Phase A 29th Voltage Magnitude Harmonics | float | 2 | R
0x5266 | 0x5267 | 21094 | 21095 | MAG_2HR_HAR_V_29th_b_% | Aggr 2hr Phase B 29th Voltage Magnitude Harmonics | float | 2 | R
0x5268 | 0x5269 | 21096 | 21097 | MAG_2HR_HAR_V_29th_c_% | Aggr 2hr Phase C 29th Voltage Magnitude Harmonics | float | 2 | R
0x526A | 0x526B | 21098 | 21099 | MAG_2HR_HAR_I_29th_a_% | Aggr 2hr Phase A 29th Current Magnitude Harmonics | float | 2 | R
0x526C | 0x526D | 21100 | 21101 | MAG_2HR_HAR_I_29th_b_% | Aggr 2hr Phase B 29th Current Magnitude Harmonics | float | 2 | R
0x526E | 0x526F | 21102 | 21103 | MAG_2HR_HAR_I_29th_c_% | Aggr 2hr Phase C 29th Current Magnitude Harmonics | float | 2 | R
0x5270 | 0x5271 | 21104 | 21105 | MAG_2HR_HAR_I_29th_n_% | Aggr 2hr Phase N 29th Current Magnitude Harmonics | float | 2 | R
0x5272 | 0x5273 | 21106 | 21107 | MAG_2HR_HAR_V_30th_a_% | Aggr 2hr Phase A 30th Voltage Magnitude Harmonics | float | 2 | R
0x5274 | 0x5275 | 21108 | 21109 | MAG_2HR_HAR_V_30th_b_% | Aggr 2hr Phase B 30th Voltage Magnitude Harmonics | float | 2 | R
0x5276 | 0x5277 | 21110 | 21111 | MAG_2HR_HAR_V_30th_c_% | Aggr 2hr Phase C 30th Voltage Magnitude Harmonics | float | 2 | R
0x5278 | 0x5279 | 21112 | 21113 | MAG_2HR_HAR_I_30th_a_% | Aggr 2hr Phase A 30th Current Magnitude Harmonics | float | 2 | R
0x527A | 0x527B | 21114 | 21115 | MAG_2HR_HAR_I_30th_b_% | Aggr 2hr Phase B 30th Current Magnitude Harmonics | float | 2 | R
0x527C | 0x527D | 21116 | 21117 | MAG_2HR_HAR_I_30th_c_% | Aggr 2hr Phase C 30th Current Magnitude Harmonics | float | 2 | R
0x527E | 0x527F | 21118 | 21119 | MAG_2HR_HAR_I_30th_n_% | Aggr 2hr Phase N 30th Current Magnitude Harmonics | float | 2 | R
0x5280 | 0x5281 | 21120 | 21121 | MAG_2HR_HAR_V_31th_a_% | Aggr 2hr Phase A 31st Voltage Magnitude Harmonics | float | 2 | R
0x5282 | 0x5283 | 21122 | 21123 | MAG_2HR_HAR_V_31th_b_% | Aggr 2hr Phase B 31st Voltage Magnitude Harmonics | float | 2 | R
0x5284 | 0x5285 | 21124 | 21125 | MAG_2HR_HAR_V_31th_c_% | Aggr 2hr Phase C 31st Voltage Magnitude Harmonics | float | 2 | R
0x5286 | 0x5287 | 21126 | 21127 | MAG_2HR_HAR_I_31th_a_% | Aggr 2hr Phase A 31st Current Magnitude Harmonics | float | 2 | R
0x5288 | 0x5289 | 21128 | 21129 | MAG_2HR_HAR_I_31th_b_% | Aggr 2hr Phase B 31st Current Magnitude Harmonics | float | 2 | R
0x528A | 0x528B | 21130 | 21131 | MAG_2HR_HAR_I_31th_c_% | Aggr 2hr Phase C 31st Current Magnitude Harmonics | float | 2 | R
0x528C | 0x528D | 21132 | 21133 | MAG_2HR_HAR_I_31th_n_% | Aggr 2hr Phase N 31st Current Magnitude Harmonics | float | 2 | R
0x528E | 0x528F | 21134 | 21135 | MAG_2HR_HAR_V_32th_a_% | Aggr 2hr Phase A 32nd Voltage Magnitude Harmonics | float | 2 | R
0x5290 | 0x5291 | 21136 | 21137 | MAG_2HR_HAR_V_32th_b_% | Aggr 2hr Phase B 32nd Voltage Magnitude Harmonics | float | 2 | R
0x5292 | 0x5293 | 21138 | 21139 | MAG_2HR_HAR_V_32th_c_% | Aggr 2hr Phase C 32nd Voltage Magnitude Harmonics | float | 2 | R
0x5294 | 0x5295 | 21140 | 21141 | MAG_2HR_HAR_I_32th_a_% | Aggr 2hr Phase A 32nd Current Magnitude Harmonics | float | 2 | R
0x5296 | 0x5297 | 21142 | 21143 | MAG_2HR_HAR_I_32th_b_% | Aggr 2hr Phase B 32nd Current Magnitude Harmonics | float | 2 | R
0x5298 | 0x5299 | 21144 | 21145 | MAG_2HR_HAR_I_32th_c_% | Aggr 2hr Phase C 32nd Current Magnitude Harmonics | float | 2 | R
0x529A | 0x529B | 21146 | 21147 | MAG_2HR_HAR_I_32th_n_% | Aggr 2hr Phase N 32nd Current Magnitude Harmonics | float | 2 | R
0x529C | 0x529D | 21148 | 21149 | MAG_2HR_HAR_V_33th_a_% | Aggr 2hr Phase A 33rd Voltage Magnitude Harmonics | float | 2 | R
0x529E | 0x529F | 21150 | 21151 | MAG_2HR_HAR_V_33th_b_% | Aggr 2hr Phase B 33rd Voltage Magnitude Harmonics | float | 2 | R
0x52A0 | 0x52A1 | 21152 | 21153 | MAG_2HR_HAR_V_33th_c_% | Aggr 2hr Phase C 33rd Voltage Magnitude Harmonics | float | 2 | R
0x52A2 | 0x52A3 | 21154 | 21155 | MAG_2HR_HAR_I_33th_a_% | Aggr 2hr Phase A 33rd Current Magnitude Harmonics | float | 2 | R
0x52A4 | 0x52A5 | 21156 | 21157 | MAG_2HR_HAR_I_33th_b_% | Aggr 2hr Phase B 33rd Current Magnitude Harmonics | float | 2 | R
0x52A6 | 0x52A7 | 21158 | 21159 | MAG_2HR_HAR_I_33th_c_% | Aggr 2hr Phase C 33rd Current Magnitude Harmonics | float | 2 | R
0x52A8 | 0x52A9 | 21160 | 21161 | MAG_2HR_HAR_I_33th_n_% | Aggr 2hr Phase N 33rd Current Magnitude Harmonics | float | 2 | R
0x52AA | 0x52AB | 21162 | 21163 | MAG_2HR_HAR_V_34th_a_% | Aggr 2hr Phase A 34th Voltage Magnitude Harmonics | float | 2 | R
0x52AC | 0x52AD | 21164 | 21165 | MAG_2HR_HAR_V_34th_b_% | Aggr 2hr Phase B 34th Voltage Magnitude Harmonics | float | 2 | R
0x52AE | 0x52AF | 21166 | 21167 | MAG_2HR_HAR_V_34th_c_% | Aggr 2hr Phase C 34th Voltage Magnitude Harmonics | float | 2 | R
0x52B0 | 0x52B1 | 21168 | 21169 | MAG_2HR_HAR_I_34th_a_% | Aggr 2hr Phase A 34th Current Magnitude Harmonics | float | 2 | R
0x52B2 | 0x52B3 | 21170 | 21171 | MAG_2HR_HAR_I_34th_b_% | Aggr 2hr Phase B 34th Current Magnitude Harmonics | float | 2 | R
0x52B4 | 0x52B5 | 21172 | 21173 | MAG_2HR_HAR_I_34th_c_% | Aggr 2hr Phase C 34th Current Magnitude Harmonics | float | 2 | R
0x52B6 | 0x52B7 | 21174 | 21175 | MAG_2HR_HAR_I_34th_n_% | Aggr 2hr Phase N 34th Current Magnitude Harmonics | float | 2 | R
0x52B8 | 0x52B9 | 21176 | 21177 | MAG_2HR_HAR_V_35th_a_% | Aggr 2hr Phase A 35th Voltage Magnitude Harmonics | float | 2 | R
0x52BA | 0x52BB | 21178 | 21179 | MAG_2HR_HAR_V_35th_b_% | Aggr 2hr Phase B 35th Voltage Magnitude Harmonics | float | 2 | R
0x52BC | 0x52BD | 21180 | 21181 | MAG_2HR_HAR_V_35th_c_% | Aggr 2hr Phase C 35th Voltage Magnitude Harmonics | float | 2 | R
0x52BE | 0x52BF | 21182 | 21183 | MAG_2HR_HAR_I_35th_a_% | Aggr 2hr Phase A 35th Current Magnitude Harmonics | float | 2 | R
0x52C0 | 0x52C1 | 21184 | 21185 | MAG_2HR_HAR_I_35th_b_% | Aggr 2hr Phase B 35th Current Magnitude Harmonics | float | 2 | R
0x52C2 | 0x52C3 | 21186 | 21187 | MAG_2HR_HAR_I_35th_c_% | Aggr 2hr Phase C 35th Current Magnitude Harmonics | float | 2 | R
0x52C4 | 0x52C5 | 21188 | 21189 | MAG_2HR_HAR_I_35th_n_% | Aggr 2hr Phase N 35th Current Magnitude Harmonics | float | 2 | R
0x52C6 | 0x52C7 | 21190 | 21191 | MAG_2HR_HAR_V_36th_a_% | Aggr 2hr Phase A 36th Voltage Magnitude Harmonics | float | 2 | R
0x52C8 | 0x52C9 | 21192 | 21193 | MAG_2HR_HAR_V_36th_b_% | Aggr 2hr Phase B 36th Voltage Magnitude Harmonics | float | 2 | R
0x52CA | 0x52CB | 21194 | 21195 | MAG_2HR_HAR_V_36th_c_% | Aggr 2hr Phase C 36th Voltage Magnitude Harmonics | float | 2 | R
0x52CC | 0x52CD | 21196 | 21197 | MAG_2HR_HAR_I_36th_a_% | Aggr 2hr Phase A 36th Current Magnitude Harmonics | float | 2 | R
0x52CE | 0x52CF | 21198 | 21199 | MAG_2HR_HAR_I_36th_b_% | Aggr 2hr Phase B 36th Current Magnitude Harmonics | float | 2 | R
0x52D0 | 0x52D1 | 21200 | 21201 | MAG_2HR_HAR_I_36th_c_% | Aggr 2hr Phase C 36th Current Magnitude Harmonics | float | 2 | R
0x52D2 | 0x52D3 | 21202 | 21203 | MAG_2HR_HAR_I_36th_n_% | Aggr 2hr Phase N 36th Current Magnitude Harmonics | float | 2 | R
0x52D4 | 0x52D5 | 21204 | 21205 | MAG_2HR_HAR_V_37th_a_% | Aggr 2hr Phase A 37th Voltage Magnitude Harmonics | float | 2 | R
0x52D6 | 0x52D7 | 21206 | 21207 | MAG_2HR_HAR_V_37th_b_% | Aggr 2hr Phase B 37th Voltage Magnitude Harmonics | float | 2 | R
0x52D8 | 0x52D9 | 21208 | 21209 | MAG_2HR_HAR_V_37th_c_% | Aggr 2hr Phase C 37th Voltage Magnitude Harmonics | float | 2 | R
0x52DA | 0x52DB | 21210 | 21211 | MAG_2HR_HAR_I_37th_a_% | Aggr 2hr Phase A 37th Current Magnitude Harmonics | float | 2 | R
0x52DC | 0x52DD | 21212 | 21213 | MAG_2HR_HAR_I_37th_b_% | Aggr 2hr Phase B 37th Current Magnitude Harmonics | float | 2 | R
0x52DE | 0x52DF | 21214 | 21215 | MAG_2HR_HAR_I_37th_c_% | Aggr 2hr Phase C 37th Current Magnitude Harmonics | float | 2 | R
0x52E0 | 0x52E1 | 21216 | 21217 | MAG_2HR_HAR_I_37th_n_% | Aggr 2hr Phase N 37th Current Magnitude Harmonics | float | 2 | R
0x52E2 | 0x52E3 | 21218 | 21219 | MAG_2HR_HAR_V_38th_a_% | Aggr 2hr Phase A 38th Voltage Magnitude Harmonics | float | 2 | R
0x52E4 | 0x52E5 | 21220 | 21221 | MAG_2HR_HAR_V_38th_b_% | Aggr 2hr Phase B 38th Voltage Magnitude Harmonics | float | 2 | R
0x52E6 | 0x52E7 | 21222 | 21223 | MAG_2HR_HAR_V_38th_c_% | Aggr 2hr Phase C 38th Voltage Magnitude Harmonics | float | 2 | R
0x52E8 | 0x52E9 | 21224 | 21225 | MAG_2HR_HAR_I_38th_a_% | Aggr 2hr Phase A 38th Current Magnitude Harmonics | float | 2 | R
0x52EA | 0x52EB | 21226 | 21227 | MAG_2HR_HAR_I_38th_b_% | Aggr 2hr Phase B 38th Current Magnitude Harmonics | float | 2 | R
0x52EC | 0x52ED | 21228 | 21229 | MAG_2HR_HAR_I_38th_c_% | Aggr 2hr Phase C 38th Current Magnitude Harmonics | float | 2 | R
0x52EE | 0x52EF | 21230 | 21231 | MAG_2HR_HAR_I_38th_n_% | Aggr 2hr Phase N 38th Current Magnitude Harmonics | float | 2 | R
0x52F0 | 0x52F1 | 21232 | 21233 | MAG_2HR_HAR_V_39th_a_% | Aggr 2hr Phase A 39th Voltage Magnitude Harmonics | float | 2 | R
0x52F2 | 0x52F3 | 21234 | 21235 | MAG_2HR_HAR_V_39th_b_% | Aggr 2hr Phase B 39th Voltage Magnitude Harmonics | float | 2 | R
0x52F4 | 0x52F5 | 21236 | 21237 | MAG_2HR_HAR_V_39th_c_% | Aggr 2hr Phase C 39th Voltage Magnitude Harmonics | float | 2 | R
0x52F6 | 0x52F7 | 21238 | 21239 | MAG_2HR_HAR_I_39th_a_% | Aggr 2hr Phase A 39th Current Magnitude Harmonics | float | 2 | R
0x52F8 | 0x52F9 | 21240 | 21241 | MAG_2HR_HAR_I_39th_b_% | Aggr 2hr Phase B 39th Current Magnitude Harmonics | float | 2 | R
0x52FA | 0x52FB | 21242 | 21243 | MAG_2HR_HAR_I_39th_c_% | Aggr 2hr Phase C 39th Current Magnitude Harmonics | float | 2 | R
0x52FC | 0x52FD | 21244 | 21245 | MAG_2HR_HAR_I_39th_n_% | Aggr 2hr Phase N 39th Current Magnitude Harmonics | float | 2 | R
0x52FE | 0x52FF | 21246 | 21247 | MAG_2HR_HAR_V_40th_a_% | Aggr 2hr Phase A 40th Voltage Magnitude Harmonics | float | 2 | R
0x5300 | 0x5301 | 21248 | 21249 | MAG_2HR_HAR_V_40th_b_% | Aggr 2hr Phase B 40th Voltage Magnitude Harmonics | float | 2 | R
0x5302 | 0x5303 | 21250 | 21251 | MAG_2HR_HAR_V_40th_c_% | Aggr 2hr Phase C 40th Voltage Magnitude Harmonics | float | 2 | R
0x5304 | 0x5305 | 21252 | 21253 | MAG_2HR_HAR_I_40th_a_% | Aggr 2hr Phase A 40th Current Magnitude Harmonics | float | 2 | R
0x5306 | 0x5307 | 21254 | 21255 | MAG_2HR_HAR_I_40th_b_% | Aggr 2hr Phase B 40th Current Magnitude Harmonics | float | 2 | R
0x5308 | 0x5309 | 21256 | 21257 | MAG_2HR_HAR_I_40th_c_% | Aggr 2hr Phase C 40th Current Magnitude Harmonics | float | 2 | R
0x530A | 0x530B | 21258 | 21259 | MAG_2HR_HAR_I_40th_n_% | Aggr 2hr Phase N 40th Current Magnitude Harmonics | float | 2 | R
0x530C | 0x530D | 21260 | 21261 | MAG_2HR_HAR_V_41th_a_% | Aggr 2hr Phase A 41st Voltage Magnitude Harmonics | float | 2 | R
0x530E | 0x530F | 21262 | 21263 | MAG_2HR_HAR_V_41th_b_% | Aggr 2hr Phase B 41st Voltage Magnitude Harmonics | float | 2 | R
0x5310 | 0x5311 | 21264 | 21265 | MAG_2HR_HAR_V_41th_c_% | Aggr 2hr Phase C 41st Voltage Magnitude Harmonics | float | 2 | R
0x5312 | 0x5313 | 21266 | 21267 | MAG_2HR_HAR_I_41th_a_% | Aggr 2hr Phase A 41st Current Magnitude Harmonics | float | 2 | R
0x5314 | 0x5315 | 21268 | 21269 | MAG_2HR_HAR_I_41th_b_% | Aggr 2hr Phase B 41st Current Magnitude Harmonics | float | 2 | R
0x5316 | 0x5317 | 21270 | 21271 | MAG_2HR_HAR_I_41th_c_% | Aggr 2hr Phase C 41st Current Magnitude Harmonics | float | 2 | R
0x5318 | 0x5319 | 21272 | 21273 | MAG_2HR_HAR_I_41th_n_% | Aggr 2hr Phase N 41st Current Magnitude Harmonics | float | 2 | R
0x531A | 0x531B | 21274 | 21275 | MAG_2HR_HAR_V_42th_a_% | Aggr 2hr Phase A 42nd Voltage Magnitude Harmonics | float | 2 | R
0x531C | 0x531D | 21276 | 21277 | MAG_2HR_HAR_V_42th_b_% | Aggr 2hr Phase B 42nd Voltage Magnitude Harmonics | float | 2 | R
0x531E | 0x531F | 21278 | 21279 | MAG_2HR_HAR_V_42th_c_% | Aggr 2hr Phase C 42nd Voltage Magnitude Harmonics | float | 2 | R
0x5320 | 0x5321 | 21280 | 21281 | MAG_2HR_HAR_I_42th_a_% | Aggr 2hr Phase A 42nd Current Magnitude Harmonics | float | 2 | R
0x5322 | 0x5323 | 21282 | 21283 | MAG_2HR_HAR_I_42th_b_% | Aggr 2hr Phase B 42nd Current Magnitude Harmonics | float | 2 | R
0x5324 | 0x5325 | 21284 | 21285 | MAG_2HR_HAR_I_42th_c_% | Aggr 2hr Phase C 42nd Current Magnitude Harmonics | float | 2 | R
0x5326 | 0x5327 | 21286 | 21287 | MAG_2HR_HAR_I_42th_n_% | Aggr 2hr Phase N 42nd Current Magnitude Harmonics | float | 2 | R
0x5328 | 0x5329 | 21288 | 21289 | MAG_2HR_HAR_V_43th_a_% | Aggr 2hr Phase A 43rd Voltage Magnitude Harmonics | float | 2 | R
0x532A | 0x532B | 21290 | 21291 | MAG_2HR_HAR_V_43th_b_% | Aggr 2hr Phase B 43rd Voltage Magnitude Harmonics | float | 2 | R
0x532C | 0x532D | 21292 | 21293 | MAG_2HR_HAR_V_43th_c_% | Aggr 2hr Phase C 43rd Voltage Magnitude Harmonics | float | 2 | R
0x532E | 0x532F | 21294 | 21295 | MAG_2HR_HAR_I_43th_a_% | Aggr 2hr Phase A 43rd Current Magnitude Harmonics | float | 2 | R
0x5330 | 0x5331 | 21296 | 21297 | MAG_2HR_HAR_I_43th_b_% | Aggr 2hr Phase B 43rd Current Magnitude Harmonics | float | 2 | R
0x5332 | 0x5333 | 21298 | 21299 | MAG_2HR_HAR_I_43th_c_% | Aggr 2hr Phase C 43rd Current Magnitude Harmonics | float | 2 | R
0x5334 | 0x5335 | 21300 | 21301 | MAG_2HR_HAR_I_43th_n_% | Aggr 2hr Phase N 43rd Current Magnitude Harmonics | float | 2 | R
0x5336 | 0x5337 | 21302 | 21303 | MAG_2HR_HAR_V_44th_a_% | Aggr 2hr Phase A 44th Voltage Magnitude Harmonics | float | 2 | R
0x5338 | 0x5339 | 21304 | 21305 | MAG_2HR_HAR_V_44th_b_% | Aggr 2hr Phase B 44th Voltage Magnitude Harmonics | float | 2 | R
0x533A | 0x533B | 21306 | 21307 | MAG_2HR_HAR_V_44th_c_% | Aggr 2hr Phase C 44th Voltage Magnitude Harmonics | float | 2 | R
0x533C | 0x533D | 21308 | 21309 | MAG_2HR_HAR_I_44th_a_% | Aggr 2hr Phase A 44th Current Magnitude Harmonics | float | 2 | R
0x533E | 0x533F | 21310 | 21311 | MAG_2HR_HAR_I_44th_b_% | Aggr 2hr Phase B 44th Current Magnitude Harmonics | float | 2 | R
0x5340 | 0x5341 | 21312 | 21313 | MAG_2HR_HAR_I_44th_c_% | Aggr 2hr Phase C 44th Current Magnitude Harmonics | float | 2 | R
0x5342 | 0x5343 | 21314 | 21315 | MAG_2HR_HAR_I_44th_n_% | Aggr 2hr Phase N 44th Current Magnitude Harmonics | float | 2 | R
0x5344 | 0x5345 | 21316 | 21317 | MAG_2HR_HAR_V_45th_a_% | Aggr 2hr Phase A 45th Voltage Magnitude Harmonics | float | 2 | R
0x5346 | 0x5347 | 21318 | 21319 | MAG_2HR_HAR_V_45th_b_% | Aggr 2hr Phase B 45th Voltage Magnitude Harmonics | float | 2 | R
0x5348 | 0x5349 | 21320 | 21321 | MAG_2HR_HAR_V_45th_c_% | Aggr 2hr Phase C 45th Voltage Magnitude Harmonics | float | 2 | R
0x534A | 0x534B | 21322 | 21323 | MAG_2HR_HAR_I_45th_a_% | Aggr 2hr Phase A 45th Current Magnitude Harmonics | float | 2 | R
0x534C | 0x534D | 21324 | 21325 | MAG_2HR_HAR_I_45th_b_% | Aggr 2hr Phase B 45th Current Magnitude Harmonics | float | 2 | R
0x534E | 0x534F | 21326 | 21327 | MAG_2HR_HAR_I_45th_c_% | Aggr 2hr Phase C 45th Current Magnitude Harmonics | float | 2 | R
0x5350 | 0x5351 | 21328 | 21329 | MAG_2HR_HAR_I_45th_n_% | Aggr 2hr Phase N 45th Current Magnitude Harmonics | float | 2 | R
0x5352 | 0x5353 | 21330 | 21331 | MAG_2HR_HAR_V_46th_a_% | Aggr 2hr Phase A 46th Voltage Magnitude Harmonics | float | 2 | R
0x5354 | 0x5355 | 21332 | 21333 | MAG_2HR_HAR_V_46th_b_% | Aggr 2hr Phase B 46th Voltage Magnitude Harmonics | float | 2 | R
0x5356 | 0x5357 | 21334 | 21335 | MAG_2HR_HAR_V_46th_c_% | Aggr 2hr Phase C 46th Voltage Magnitude Harmonics | float | 2 | R
0x5358 | 0x5359 | 21336 | 21337 | MAG_2HR_HAR_I_46th_a_% | Aggr 2hr Phase A 46th Current Magnitude Harmonics | float | 2 | R
0x535A | 0x535B | 21338 | 21339 | MAG_2HR_HAR_I_46th_b_% | Aggr 2hr Phase B 46th Current Magnitude Harmonics | float | 2 | R
0x535C | 0x535D | 21340 | 21341 | MAG_2HR_HAR_I_46th_c_% | Aggr 2hr Phase C 46th Current Magnitude Harmonics | float | 2 | R
0x535E | 0x535F | 21342 | 21343 | MAG_2HR_HAR_I_46th_n_% | Aggr 2hr Phase N 46th Current Magnitude Harmonics | float | 2 | R
0x5360 | 0x5361 | 21344 | 21345 | MAG_2HR_HAR_V_47th_a_% | Aggr 2hr Phase A 47th Voltage Magnitude Harmonics | float | 2 | R
0x5362 | 0x5363 | 21346 | 21347 | MAG_2HR_HAR_V_47th_b_% | Aggr 2hr Phase B 47th Voltage Magnitude Harmonics | float | 2 | R
0x5364 | 0x5365 | 21348 | 21349 | MAG_2HR_HAR_V_47th_c_% | Aggr 2hr Phase C 47th Voltage Magnitude Harmonics | float | 2 | R
0x5366 | 0x5367 | 21350 | 21351 | MAG_2HR_HAR_I_47th_a_% | Aggr 2hr Phase A 47th Current Magnitude Harmonics | float | 2 | R
0x5368 | 0x5369 | 21352 | 21353 | MAG_2HR_HAR_I_47th_b_% | Aggr 2hr Phase B 47th Current Magnitude Harmonics | float | 2 | R
0x536A | 0x536B | 21354 | 21355 | MAG_2HR_HAR_I_47th_c_% | Aggr 2hr Phase C 47th Current Magnitude Harmonics | float | 2 | R
0x536C | 0x536D | 21356 | 21357 | MAG_2HR_HAR_I_47th_n_% | Aggr 2hr Phase N 47th Current Magnitude Harmonics | float | 2 | R
0x536E | 0x536F | 21358 | 21359 | MAG_2HR_HAR_V_48th_a_% | Aggr 2hr Phase A 48th Voltage Magnitude Harmonics | float | 2 | R
0x5370 | 0x5371 | 21360 | 21361 | MAG_2HR_HAR_V_48th_b_% | Aggr 2hr Phase B 48th Voltage Magnitude Harmonics | float | 2 | R
0x5372 | 0x5373 | 21362 | 21363 | MAG_2HR_HAR_V_48th_c_% | Aggr 2hr Phase C 48th Voltage Magnitude Harmonics | float | 2 | R
0x5374 | 0x5375 | 21364 | 21365 | MAG_2HR_HAR_I_48th_a_% | Aggr 2hr Phase A 48th Current Magnitude Harmonics | float | 2 | R
0x5376 | 0x5377 | 21366 | 21367 | MAG_2HR_HAR_I_48th_b_% | Aggr 2hr Phase B 48th Current Magnitude Harmonics | float | 2 | R
0x5378 | 0x5379 | 21368 | 21369 | MAG_2HR_HAR_I_48th_c_% | Aggr 2hr Phase C 48th Current Magnitude Harmonics | float | 2 | R
0x537A | 0x537B | 21370 | 21371 | MAG_2HR_HAR_I_48th_n_% | Aggr 2hr Phase N 48th Current Magnitude Harmonics | float | 2 | R
0x537C | 0x537D | 21372 | 21373 | MAG_2HR_HAR_V_49th_a_% | Aggr 2hr Phase A 49th Voltage Magnitude Harmonics | float | 2 | R
0x537E | 0x537F | 21374 | 21375 | MAG_2HR_HAR_V_49th_b_% | Aggr 2hr Phase B 49th Voltage Magnitude Harmonics | float | 2 | R
0x5380 | 0x5381 | 21376 | 21377 | MAG_2HR_HAR_V_49th_c_% | Aggr 2hr Phase C 49th Voltage Magnitude Harmonics | float | 2 | R
0x5382 | 0x5383 | 21378 | 21379 | MAG_2HR_HAR_I_49th_a_% | Aggr 2hr Phase A 49th Current Magnitude Harmonics | float | 2 | R
0x5384 | 0x5385 | 21380 | 21381 | MAG_2HR_HAR_I_49th_b_% | Aggr 2hr Phase B 49th Current Magnitude Harmonics | float | 2 | R
0x5386 | 0x5387 | 21382 | 21383 | MAG_2HR_HAR_I_49th_c_% | Aggr 2hr Phase C 49th Current Magnitude Harmonics | float | 2 | R
0x5388 | 0x5389 | 21384 | 21385 | MAG_2HR_HAR_I_49th_n_% | Aggr 2hr Phase N 49th Current Magnitude Harmonics | float | 2 | R
0x538A | 0x538B | 21386 | 21387 | MAG_2HR_HAR_V_50th_a_% | Aggr 2hr Phase A 50th Voltage Magnitude Harmonics | float | 2 | R
0x538C | 0x538D | 21388 | 21389 | MAG_2HR_HAR_V_50th_b_% | Aggr 2hr Phase B 50th Voltage Magnitude Harmonics | float | 2 | R
0x538E | 0x538F | 21390 | 21391 | MAG_2HR_HAR_V_50th_c_% | Aggr 2hr Phase C 50th Voltage Magnitude Harmonics | float | 2 | R
0x5390 | 0x5391 | 21392 | 21393 | MAG_2HR_HAR_I_50th_a_% | Aggr 2hr Phase A 50th Current Magnitude Harmonics | float | 2 | R
0x5392 | 0x5393 | 21394 | 21395 | MAG_2HR_HAR_I_50th_b_% | Aggr 2hr Phase B 50th Current Magnitude Harmonics | float | 2 | R
0x5394 | 0x5395 | 21396 | 21397 | MAG_2HR_HAR_I_50th_c_% | Aggr 2hr Phase C 50th Current Magnitude Harmonics | float | 2 | R
0x5396 | 0x5397 | 21398 | 21399 | MAG_2HR_HAR_I_50th_n_% | Aggr 2hr Phase N 50th Current Magnitude Harmonics | float | 2 | R
0x5398 | 0x5399 | 21400 | 21401 | MAG_2HR_HAR_V_51th_a_% | Aggr 2hr Phase A 51st Voltage Magnitude Harmonics | float | 2 | R
0x539A | 0x539B | 21402 | 21403 | MAG_2HR_HAR_V_51th_b_% | Aggr 2hr Phase B 51st Voltage Magnitude Harmonics | float | 2 | R
0x539C | 0x539D | 21404 | 21405 | MAG_2HR_HAR_V_51th_c_% | Aggr 2hr Phase C 51st Voltage Magnitude Harmonics | float | 2 | R
0x539E | 0x539F | 21406 | 21407 | MAG_2HR_HAR_I_51th_a_% | Aggr 2hr Phase A 51st Current Magnitude Harmonics | float | 2 | R
0x53A0 | 0x53A1 | 21408 | 21409 | MAG_2HR_HAR_I_51th_b_% | Aggr 2hr Phase B 51st Current Magnitude Harmonics | float | 2 | R
0x53A2 | 0x53A3 | 21410 | 21411 | MAG_2HR_HAR_I_51th_c_% | Aggr 2hr Phase C 51st Current Magnitude Harmonics | float | 2 | R
0x53A4 | 0x53A5 | 21412 | 21413 | MAG_2HR_HAR_I_51th_n_% | Aggr 2hr Phase N 51st Current Magnitude Harmonics | float | 2 | R
0x53A6 | 0x53A7 | 21414 | 21415 | MAG_2HR_HAR_V_52th_a_% | Aggr 2hr Phase A 52nd Voltage Magnitude Harmonics | float | 2 | R
0x53A8 | 0x53A9 | 21416 | 21417 | MAG_2HR_HAR_V_52th_b_% | Aggr 2hr Phase B 52nd Voltage Magnitude Harmonics | float | 2 | R
0x53AA | 0x53AB | 21418 | 21419 | MAG_2HR_HAR_V_52th_c_% | Aggr 2hr Phase C 52nd Voltage Magnitude Harmonics | float | 2 | R
0x53AC | 0x53AD | 21420 | 21421 | MAG_2HR_HAR_I_52th_a_% | Aggr 2hr Phase A 52nd Current Magnitude Harmonics | float | 2 | R
0x53AE | 0x53AF | 21422 | 21423 | MAG_2HR_HAR_I_52th_b_% | Aggr 2hr Phase B 52nd Current Magnitude Harmonics | float | 2 | R
0x53B0 | 0x53B1 | 21424 | 21425 | MAG_2HR_HAR_I_52th_c_% | Aggr 2hr Phase C 52nd Current Magnitude Harmonics | float | 2 | R
0x53B2 | 0x53B3 | 21426 | 21427 | MAG_2HR_HAR_I_52th_n_% | Aggr 2hr Phase N 52nd Current Magnitude Harmonics | float | 2 | R
0x53B4 | 0x53B5 | 21428 | 21429 | MAG_2HR_HAR_V_53th_a_% | Aggr 2hr Phase A 53rd Voltage Magnitude Harmonics | float | 2 | R
0x53B6 | 0x53B7 | 21430 | 21431 | MAG_2HR_HAR_V_53th_b_% | Aggr 2hr Phase B 53rd Voltage Magnitude Harmonics | float | 2 | R
0x53B8 | 0x53B9 | 21432 | 21433 | MAG_2HR_HAR_V_53th_c_% | Aggr 2hr Phase C 53rd Voltage Magnitude Harmonics | float | 2 | R
0x53BA | 0x53BB | 21434 | 21435 | MAG_2HR_HAR_I_53th_a_% | Aggr 2hr Phase A 53rd Current Magnitude Harmonics | float | 2 | R
0x53BC | 0x53BD | 21436 | 21437 | MAG_2HR_HAR_I_53th_b_% | Aggr 2hr Phase B 53rd Current Magnitude Harmonics | float | 2 | R
0x53BE | 0x53BF | 21438 | 21439 | MAG_2HR_HAR_I_53th_c_% | Aggr 2hr Phase C 53rd Current Magnitude Harmonics | float | 2 | R
0x53C0 | 0x53C1 | 21440 | 21441 | MAG_2HR_HAR_I_53th_n_% | Aggr 2hr Phase N 53rd Current Magnitude Harmonics | float | 2 | R
0x53C2 | 0x53C3 | 21442 | 21443 | MAG_2HR_HAR_V_54th_a_% | Aggr 2hr Phase A 54th Voltage Magnitude Harmonics | float | 2 | R
0x53C4 | 0x53C5 | 21444 | 21445 | MAG_2HR_HAR_V_54th_b_% | Aggr 2hr Phase B 54th Voltage Magnitude Harmonics | float | 2 | R
0x53C6 | 0x53C7 | 21446 | 21447 | MAG_2HR_HAR_V_54th_c_% | Aggr 2hr Phase C 54th Voltage Magnitude Harmonics | float | 2 | R
0x53C8 | 0x53C9 | 21448 | 21449 | MAG_2HR_HAR_I_54th_a_% | Aggr 2hr Phase A 54th Current Magnitude Harmonics | float | 2 | R
0x53CA | 0x53CB | 21450 | 21451 | MAG_2HR_HAR_I_54th_b_% | Aggr 2hr Phase B 54th Current Magnitude Harmonics | float | 2 | R
0x53CC | 0x53CD | 21452 | 21453 | MAG_2HR_HAR_I_54th_c_% | Aggr 2hr Phase C 54th Current Magnitude Harmonics | float | 2 | R
0x53CE | 0x53CF | 21454 | 21455 | MAG_2HR_HAR_I_54th_n_% | Aggr 2hr Phase N 54th Current Magnitude Harmonics | float | 2 | R
0x53D0 | 0x53D1 | 21456 | 21457 | MAG_2HR_HAR_V_55th_a_% | Aggr 2hr Phase A 55th Voltage Magnitude Harmonics | float | 2 | R
0x53D2 | 0x53D3 | 21458 | 21459 | MAG_2HR_HAR_V_55th_b_% | Aggr 2hr Phase B 55th Voltage Magnitude Harmonics | float | 2 | R
0x53D4 | 0x53D5 | 21460 | 21461 | MAG_2HR_HAR_V_55th_c_% | Aggr 2hr Phase C 55th Voltage Magnitude Harmonics | float | 2 | R
0x53D6 | 0x53D7 | 21462 | 21463 | MAG_2HR_HAR_I_55th_a_% | Aggr 2hr Phase A 55th Current Magnitude Harmonics | float | 2 | R
0x53D8 | 0x53D9 | 21464 | 21465 | MAG_2HR_HAR_I_55th_b_% | Aggr 2hr Phase B 55th Current Magnitude Harmonics | float | 2 | R
0x53DA | 0x53DB | 21466 | 21467 | MAG_2HR_HAR_I_55th_c_% | Aggr 2hr Phase C 55th Current Magnitude Harmonics | float | 2 | R
0x53DC | 0x53DD | 21468 | 21469 | MAG_2HR_HAR_I_55th_n_% | Aggr 2hr Phase N 55th Current Magnitude Harmonics | float | 2 | R
0x53DE | 0x53DF | 21470 | 21471 | MAG_2HR_HAR_V_56th_a_% | Aggr 2hr Phase A 56th Voltage Magnitude Harmonics | float | 2 | R
0x53E0 | 0x53E1 | 21472 | 21473 | MAG_2HR_HAR_V_56th_b_% | Aggr 2hr Phase B 56th Voltage Magnitude Harmonics | float | 2 | R
0x53E2 | 0x53E3 | 21474 | 21475 | MAG_2HR_HAR_V_56th_c_% | Aggr 2hr Phase C 56th Voltage Magnitude Harmonics | float | 2 | R
0x53E4 | 0x53E5 | 21476 | 21477 | MAG_2HR_HAR_I_56th_a_% | Aggr 2hr Phase A 56th Current Magnitude Harmonics | float | 2 | R
0x53E6 | 0x53E7 | 21478 | 21479 | MAG_2HR_HAR_I_56th_b_% | Aggr 2hr Phase B 56th Current Magnitude Harmonics | float | 2 | R
0x53E8 | 0x53E9 | 21480 | 21481 | MAG_2HR_HAR_I_56th_c_% | Aggr 2hr Phase C 56th Current Magnitude Harmonics | float | 2 | R
0x53EA | 0x53EB | 21482 | 21483 | MAG_2HR_HAR_I_56th_n_% | Aggr 2hr Phase N 56th Current Magnitude Harmonics | float | 2 | R
0x53EC | 0x53ED | 21484 | 21485 | MAG_2HR_HAR_V_57th_a_% | Aggr 2hr Phase A 57th Voltage Magnitude Harmonics | float | 2 | R
0x53EE | 0x53EF | 21486 | 21487 | MAG_2HR_HAR_V_57th_b_% | Aggr 2hr Phase B 57th Voltage Magnitude Harmonics | float | 2 | R
0x53F0 | 0x53F1 | 21488 | 21489 | MAG_2HR_HAR_V_57th_c_% | Aggr 2hr Phase C 57th Voltage Magnitude Harmonics | float | 2 | R
0x53F2 | 0x53F3 | 21490 | 21491 | MAG_2HR_HAR_I_57th_a_% | Aggr 2hr Phase A 57th Current Magnitude Harmonics | float | 2 | R
0x53F4 | 0x53F5 | 21492 | 21493 | MAG_2HR_HAR_I_57th_b_% | Aggr 2hr Phase B 57th Current Magnitude Harmonics | float | 2 | R
0x53F6 | 0x53F7 | 21494 | 21495 | MAG_2HR_HAR_I_57th_c_% | Aggr 2hr Phase C 57th Current Magnitude Harmonics | float | 2 | R
0x53F8 | 0x53F9 | 21496 | 21497 | MAG_2HR_HAR_I_57th_n_% | Aggr 2hr Phase N 57th Current Magnitude Harmonics | float | 2 | R
0x53FA | 0x53FB | 21498 | 21499 | MAG_2HR_HAR_V_58th_a_% | Aggr 2hr Phase A 58th Voltage Magnitude Harmonics | float | 2 | R
0x53FC | 0x53FD | 21500 | 21501 | MAG_2HR_HAR_V_58th_b_% | Aggr 2hr Phase B 58th Voltage Magnitude Harmonics | float | 2 | R
0x53FE | 0x53FF | 21502 | 21503 | MAG_2HR_HAR_V_58th_c_% | Aggr 2hr Phase C 58th Voltage Magnitude Harmonics | float | 2 | R
0x5400 | 0x5401 | 21504 | 21505 | MAG_2HR_HAR_I_58th_a_% | Aggr 2hr Phase A 58th Current Magnitude Harmonics | float | 2 | R
0x5402 | 0x5403 | 21506 | 21507 | MAG_2HR_HAR_I_58th_b_% | Aggr 2hr Phase B 58th Current Magnitude Harmonics | float | 2 | R
0x5404 | 0x5405 | 21508 | 21509 | MAG_2HR_HAR_I_58th_c_% | Aggr 2hr Phase C 58th Current Magnitude Harmonics | float | 2 | R
0x5406 | 0x5407 | 21510 | 21511 | MAG_2HR_HAR_I_58th_n_% | Aggr 2hr Phase N 58th Current Magnitude Harmonics | float | 2 | R
0x5408 | 0x5409 | 21512 | 21513 | MAG_2HR_HAR_V_59th_a_% | Aggr 2hr Phase A 59th Voltage Magnitude Harmonics | float | 2 | R
0x540A | 0x540B | 21514 | 21515 | MAG_2HR_HAR_V_59th_b_% | Aggr 2hr Phase B 59th Voltage Magnitude Harmonics | float | 2 | R
0x540C | 0x540D | 21516 | 21517 | MAG_2HR_HAR_V_59th_c_% | Aggr 2hr Phase C 59th Voltage Magnitude Harmonics | float | 2 | R
0x540E | 0x540F | 21518 | 21519 | MAG_2HR_HAR_I_59th_a_% | Aggr 2hr Phase A 59th Current Magnitude Harmonics | float | 2 | R
0x5410 | 0x5411 | 21520 | 21521 | MAG_2HR_HAR_I_59th_b_% | Aggr 2hr Phase B 59th Current Magnitude Harmonics | float | 2 | R
0x5412 | 0x5413 | 21522 | 21523 | MAG_2HR_HAR_I_59th_c_% | Aggr 2hr Phase C 59th Current Magnitude Harmonics | float | 2 | R
0x5414 | 0x5415 | 21524 | 21525 | MAG_2HR_HAR_I_59th_n_% | Aggr 2hr Phase N 59th Current Magnitude Harmonics | float | 2 | R
0x5416 | 0x5417 | 21526 | 21527 | MAG_2HR_HAR_V_60th_a_% | Aggr 2hr Phase A 60th Voltage Magnitude Harmonics | float | 2 | R
0x5418 | 0x5419 | 21528 | 21529 | MAG_2HR_HAR_V_60th_b_% | Aggr 2hr Phase B 60th Voltage Magnitude Harmonics | float | 2 | R
0x541A | 0x541B | 21530 | 21531 | MAG_2HR_HAR_V_60th_c_% | Aggr 2hr Phase C 60th Voltage Magnitude Harmonics | float | 2 | R
0x541C | 0x541D | 21532 | 21533 | MAG_2HR_HAR_I_60th_a_% | Aggr 2hr Phase A 60th Current Magnitude Harmonics | float | 2 | R
0x541E | 0x541F | 21534 | 21535 | MAG_2HR_HAR_I_60th_b_% | Aggr 2hr Phase B 60th Current Magnitude Harmonics | float | 2 | R
0x5420 | 0x5421 | 21536 | 21537 | MAG_2HR_HAR_I_60th_c_% | Aggr 2hr Phase C 60th Current Magnitude Harmonics | float | 2 | R
0x5422 | 0x5423 | 21538 | 21539 | MAG_2HR_HAR_I_60th_n_% | Aggr 2hr Phase N 60th Current Magnitude Harmonics | float | 2 | R
0x5424 | 0x5425 | 21540 | 21541 | MAG_2HR_HAR_V_61th_a_% | Aggr 2hr Phase A 61st Voltage Magnitude Harmonics | float | 2 | R
0x5426 | 0x5427 | 21542 | 21543 | MAG_2HR_HAR_V_61th_b_% | Aggr 2hr Phase B 61st Voltage Magnitude Harmonics | float | 2 | R
0x5428 | 0x5429 | 21544 | 21545 | MAG_2HR_HAR_V_61th_c_% | Aggr 2hr Phase C 61st Voltage Magnitude Harmonics | float | 2 | R
0x542A | 0x542B | 21546 | 21547 | MAG_2HR_HAR_I_61th_a_% | Aggr 2hr Phase A 61st Current Magnitude Harmonics | float | 2 | R
0x542C | 0x542D | 21548 | 21549 | MAG_2HR_HAR_I_61th_b_% | Aggr 2hr Phase B 61st Current Magnitude Harmonics | float | 2 | R
0x542E | 0x542F | 21550 | 21551 | MAG_2HR_HAR_I_61th_c_% | Aggr 2hr Phase C 61st Current Magnitude Harmonics | float | 2 | R
0x5430 | 0x5431 | 21552 | 21553 | MAG_2HR_HAR_I_61th_n_% | Aggr 2hr Phase N 61st Current Magnitude Harmonics | float | 2 | R
0x5432 | 0x5433 | 21554 | 21555 | MAG_2HR_HAR_V_62th_a_% | Aggr 2hr Phase A 62nd Voltage Magnitude Harmonics | float | 2 | R
0x5434 | 0x5435 | 21556 | 21557 | MAG_2HR_HAR_V_62th_b_% | Aggr 2hr Phase B 62nd Voltage Magnitude Harmonics | float | 2 | R
0x5436 | 0x5437 | 21558 | 21559 | MAG_2HR_HAR_V_62th_c_% | Aggr 2hr Phase C 62nd Voltage Magnitude Harmonics | float | 2 | R
0x5438 | 0x5439 | 21560 | 21561 | MAG_2HR_HAR_I_62th_a_% | Aggr 2hr Phase A 62nd Current Magnitude Harmonics | float | 2 | R
0x543A | 0x543B | 21562 | 21563 | MAG_2HR_HAR_I_62th_b_% | Aggr 2hr Phase B 62nd Current Magnitude Harmonics | float | 2 | R
0x543C | 0x543D | 21564 | 21565 | MAG_2HR_HAR_I_62th_c_% | Aggr 2hr Phase C 62nd Current Magnitude Harmonics | float | 2 | R
0x543E | 0x543F | 21566 | 21567 | MAG_2HR_HAR_I_62th_n_% | Aggr 2hr Phase N 62nd Current Magnitude Harmonics | float | 2 | R
0x5440 | 0x5441 | 21568 | 21569 | MAG_2HR_HAR_V_63th_a_% | Aggr 2hr Phase A 63rd Voltage Magnitude Harmonics | float | 2 | R
0x5442 | 0x5443 | 21570 | 21571 | MAG_2HR_HAR_V_63th_b_% | Aggr 2hr Phase B 63rd Voltage Magnitude Harmonics | float | 2 | R
0x5444 | 0x5445 | 21572 | 21573 | MAG_2HR_HAR_V_63th_c_% | Aggr 2hr Phase C 63rd Voltage Magnitude Harmonics | float | 2 | R
0x5446 | 0x5447 | 21574 | 21575 | MAG_2HR_HAR_I_63th_a_% | Aggr 2hr Phase A 63rd Current Magnitude Harmonics | float | 2 | R
0x5448 | 0x5449 | 21576 | 21577 | MAG_2HR_HAR_I_63th_b_% | Aggr 2hr Phase B 63rd Current Magnitude Harmonics | float | 2 | R
0x544A | 0x544B | 21578 | 21579 | MAG_2HR_HAR_I_63th_c_% | Aggr 2hr Phase C 63rd Current Magnitude Harmonics | float | 2 | R
0x544C | 0x544D | 21580 | 21581 | MAG_2HR_HAR_I_63th_n_% | Aggr 2hr Phase N 63rd Current Magnitude Harmonics | float | 2 | R
0x544E | 0x544F | 21582 | 21583 | MAG_2HR_HAR_V_64th_a_% | Aggr 2hr Phase A 64th Voltage Magnitude Harmonics | float | 2 | R
0x5450 | 0x5451 | 21584 | 21585 | MAG_2HR_HAR_V_64th_b_% | Aggr 2hr Phase B 64th Voltage Magnitude Harmonics | float | 2 | R
0x5452 | 0x5453 | 21586 | 21587 | MAG_2HR_HAR_V_64th_c_% | Aggr 2hr Phase C 64th Voltage Magnitude Harmonics | float | 2 | R
0x5454 | 0x5455 | 21588 | 21589 | MAG_2HR_HAR_I_64th_a_% | Aggr 2hr Phase A 64th Current Magnitude Harmonics | float | 2 | R
0x5456 | 0x5457 | 21590 | 21591 | MAG_2HR_HAR_I_64th_b_% | Aggr 2hr Phase B 64th Current Magnitude Harmonics | float | 2 | R
0x5458 | 0x5459 | 21592 | 21593 | MAG_2HR_HAR_I_64th_c_% | Aggr 2hr Phase C 64th Current Magnitude Harmonics | float | 2 | R
0x545A | 0x545B | 21594 | 21595 | MAG_2HR_HAR_I_64th_n_% | Aggr 2hr Phase N 64th Current Magnitude Harmonics | float | 2 | R
0x545C | 0x545D | 21596 | 21597 | MAG_2HR_HAR_V_65th_a_% | Aggr 2hr Phase A 65th Voltage Magnitude Harmonics | float | 2 | R
0x545E | 0x545F | 21598 | 21599 | MAG_2HR_HAR_V_65th_b_% | Aggr 2hr Phase B 65th Voltage Magnitude Harmonics | float | 2 | R
0x5460 | 0x5461 | 21600 | 21601 | MAG_2HR_HAR_V_65th_c_% | Aggr 2hr Phase C 65th Voltage Magnitude Harmonics | float | 2 | R
0x5462 | 0x5463 | 21602 | 21603 | MAG_2HR_HAR_I_65th_a_% | Aggr 2hr Phase A 65th Current Magnitude Harmonics | float | 2 | R
0x5464 | 0x5465 | 21604 | 21605 | MAG_2HR_HAR_I_65th_b_% | Aggr 2hr Phase B 65th Current Magnitude Harmonics | float | 2 | R
0x5466 | 0x5467 | 21606 | 21607 | MAG_2HR_HAR_I_65th_c_% | Aggr 2hr Phase C 65th Current Magnitude Harmonics | float | 2 | R
0x5468 | 0x5469 | 21608 | 21609 | MAG_2HR_HAR_I_65th_n_% | Aggr 2hr Phase N 65th Current Magnitude Harmonics | float | 2 | R
0x546A | 0x546B | 21610 | 21611 | MAG_2HR_HAR_V_66th_a_% | Aggr 2hr Phase A 66th Voltage Magnitude Harmonics | float | 2 | R
0x546C | 0x546D | 21612 | 21613 | MAG_2HR_HAR_V_66th_b_% | Aggr 2hr Phase B 66th Voltage Magnitude Harmonics | float | 2 | R
0x546E | 0x546F | 21614 | 21615 | MAG_2HR_HAR_V_66th_c_% | Aggr 2hr Phase C 66th Voltage Magnitude Harmonics | float | 2 | R
0x5470 | 0x5471 | 21616 | 21617 | MAG_2HR_HAR_I_66th_a_% | Aggr 2hr Phase A 66th Current Magnitude Harmonics | float | 2 | R
0x5472 | 0x5473 | 21618 | 21619 | MAG_2HR_HAR_I_66th_b_% | Aggr 2hr Phase B 66th Current Magnitude Harmonics | float | 2 | R
0x5474 | 0x5475 | 21620 | 21621 | MAG_2HR_HAR_I_66th_c_% | Aggr 2hr Phase C 66th Current Magnitude Harmonics | float | 2 | R
0x5476 | 0x5477 | 21622 | 21623 | MAG_2HR_HAR_I_66th_n_% | Aggr 2hr Phase N 66th Current Magnitude Harmonics | float | 2 | R
0x5478 | 0x5479 | 21624 | 21625 | MAG_2HR_HAR_V_67th_a_% | Aggr 2hr Phase A 67th Voltage Magnitude Harmonics | float | 2 | R
0x547A | 0x547B | 21626 | 21627 | MAG_2HR_HAR_V_67th_b_% | Aggr 2hr Phase B 67th Voltage Magnitude Harmonics | float | 2 | R
0x547C | 0x547D | 21628 | 21629 | MAG_2HR_HAR_V_67th_c_% | Aggr 2hr Phase C 67th Voltage Magnitude Harmonics | float | 2 | R
0x547E | 0x547F | 21630 | 21631 | MAG_2HR_HAR_I_67th_a_% | Aggr 2hr Phase A 67th Current Magnitude Harmonics | float | 2 | R
0x5480 | 0x5481 | 21632 | 21633 | MAG_2HR_HAR_I_67th_b_% | Aggr 2hr Phase B 67th Current Magnitude Harmonics | float | 2 | R
0x5482 | 0x5483 | 21634 | 21635 | MAG_2HR_HAR_I_67th_c_% | Aggr 2hr Phase C 67th Current Magnitude Harmonics | float | 2 | R
0x5484 | 0x5485 | 21636 | 21637 | MAG_2HR_HAR_I_67th_n_% | Aggr 2hr Phase N 67th Current Magnitude Harmonics | float | 2 | R
0x5486 | 0x5487 | 21638 | 21639 | MAG_2HR_HAR_V_68th_a_% | Aggr 2hr Phase A 68th Voltage Magnitude Harmonics | float | 2 | R
0x5488 | 0x5489 | 21640 | 21641 | MAG_2HR_HAR_V_68th_b_% | Aggr 2hr Phase B 68th Voltage Magnitude Harmonics | float | 2 | R
0x548A | 0x548B | 21642 | 21643 | MAG_2HR_HAR_V_68th_c_% | Aggr 2hr Phase C 68th Voltage Magnitude Harmonics | float | 2 | R
0x548C | 0x548D | 21644 | 21645 | MAG_2HR_HAR_I_68th_a_% | Aggr 2hr Phase A 68th Current Magnitude Harmonics | float | 2 | R
0x548E | 0x548F | 21646 | 21647 | MAG_2HR_HAR_I_68th_b_% | Aggr 2hr Phase B 68th Current Magnitude Harmonics | float | 2 | R
0x5490 | 0x5491 | 21648 | 21649 | MAG_2HR_HAR_I_68th_c_% | Aggr 2hr Phase C 68th Current Magnitude Harmonics | float | 2 | R
0x5492 | 0x5493 | 21650 | 21651 | MAG_2HR_HAR_I_68th_n_% | Aggr 2hr Phase N 68th Current Magnitude Harmonics | float | 2 | R
0x5494 | 0x5495 | 21652 | 21653 | MAG_2HR_HAR_V_69th_a_% | Aggr 2hr Phase A 69th Voltage Magnitude Harmonics | float | 2 | R
0x5496 | 0x5497 | 21654 | 21655 | MAG_2HR_HAR_V_69th_b_% | Aggr 2hr Phase B 69th Voltage Magnitude Harmonics | float | 2 | R
0x5498 | 0x5499 | 21656 | 21657 | MAG_2HR_HAR_V_69th_c_% | Aggr 2hr Phase C 69th Voltage Magnitude Harmonics | float | 2 | R
0x549A | 0x549B | 21658 | 21659 | MAG_2HR_HAR_I_69th_a_% | Aggr 2hr Phase A 69th Current Magnitude Harmonics | float | 2 | R
0x549C | 0x549D | 21660 | 21661 | MAG_2HR_HAR_I_69th_b_% | Aggr 2hr Phase B 69th Current Magnitude Harmonics | float | 2 | R
0x549E | 0x549F | 21662 | 21663 | MAG_2HR_HAR_I_69th_c_% | Aggr 2hr Phase C 69th Current Magnitude Harmonics | float | 2 | R
0x54A0 | 0x54A1 | 21664 | 21665 | MAG_2HR_HAR_I_69th_n_% | Aggr 2hr Phase N 69th Current Magnitude Harmonics | float | 2 | R
0x54A2 | 0x54A3 | 21666 | 21667 | MAG_2HR_HAR_V_70th_a_% | Aggr 2hr Phase A 70th Voltage Magnitude Harmonics | float | 2 | R
0x54A4 | 0x54A5 | 21668 | 21669 | MAG_2HR_HAR_V_70th_b_% | Aggr 2hr Phase B 70th Voltage Magnitude Harmonics | float | 2 | R
0x54A6 | 0x54A7 | 21670 | 21671 | MAG_2HR_HAR_V_70th_c_% | Aggr 2hr Phase C 70th Voltage Magnitude Harmonics | float | 2 | R
0x54A8 | 0x54A9 | 21672 | 21673 | MAG_2HR_HAR_I_70th_a_% | Aggr 2hr Phase A 70th Current Magnitude Harmonics | float | 2 | R
0x54AA | 0x54AB | 21674 | 21675 | MAG_2HR_HAR_I_70th_b_% | Aggr 2hr Phase B 70th Current Magnitude Harmonics | float | 2 | R
0x54AC | 0x54AD | 21676 | 21677 | MAG_2HR_HAR_I_70th_c_% | Aggr 2hr Phase C 70th Current Magnitude Harmonics | float | 2 | R
0x54AE | 0x54AF | 21678 | 21679 | MAG_2HR_HAR_I_70th_n_% | Aggr 2hr Phase N 70th Current Magnitude Harmonics | float | 2 | R
0x54B0 | 0x54B1 | 21680 | 21681 | MAG_2HR_HAR_V_71th_a_% | Aggr 2hr Phase A 71st Voltage Magnitude Harmonics | float | 2 | R
0x54B2 | 0x54B3 | 21682 | 21683 | MAG_2HR_HAR_V_71th_b_% | Aggr 2hr Phase B 71st Voltage Magnitude Harmonics | float | 2 | R
0x54B4 | 0x54B5 | 21684 | 21685 | MAG_2HR_HAR_V_71th_c_% | Aggr 2hr Phase C 71st Voltage Magnitude Harmonics | float | 2 | R
0x54B6 | 0x54B7 | 21686 | 21687 | MAG_2HR_HAR_I_71th_a_% | Aggr 2hr Phase A 71st Current Magnitude Harmonics | float | 2 | R
0x54B8 | 0x54B9 | 21688 | 21689 | MAG_2HR_HAR_I_71th_b_% | Aggr 2hr Phase B 71st Current Magnitude Harmonics | float | 2 | R
0x54BA | 0x54BB | 21690 | 21691 | MAG_2HR_HAR_I_71th_c_% | Aggr 2hr Phase C 71st Current Magnitude Harmonics | float | 2 | R
0x54BC | 0x54BD | 21692 | 21693 | MAG_2HR_HAR_I_71th_n_% | Aggr 2hr Phase N 71st Current Magnitude Harmonics | float | 2 | R
0x54BE | 0x54BF | 21694 | 21695 | MAG_2HR_HAR_V_72th_a_% | Aggr 2hr Phase A 72nd Voltage Magnitude Harmonics | float | 2 | R
0x54C0 | 0x54C1 | 21696 | 21697 | MAG_2HR_HAR_V_72th_b_% | Aggr 2hr Phase B 72nd Voltage Magnitude Harmonics | float | 2 | R
0x54C2 | 0x54C3 | 21698 | 21699 | MAG_2HR_HAR_V_72th_c_% | Aggr 2hr Phase C 72nd Voltage Magnitude Harmonics | float | 2 | R
0x54C4 | 0x54C5 | 21700 | 21701 | MAG_2HR_HAR_I_72th_a_% | Aggr 2hr Phase A 72nd Current Magnitude Harmonics | float | 2 | R
0x54C6 | 0x54C7 | 21702 | 21703 | MAG_2HR_HAR_I_72th_b_% | Aggr 2hr Phase B 72nd Current Magnitude Harmonics | float | 2 | R
0x54C8 | 0x54C9 | 21704 | 21705 | MAG_2HR_HAR_I_72th_c_% | Aggr 2hr Phase C 72nd Current Magnitude Harmonics | float | 2 | R
0x54CA | 0x54CB | 21706 | 21707 | MAG_2HR_HAR_I_72th_n_% | Aggr 2hr Phase N 72nd Current Magnitude Harmonics | float | 2 | R
0x54CC | 0x54CD | 21708 | 21709 | MAG_2HR_HAR_V_73th_a_% | Aggr 2hr Phase A 73rd Voltage Magnitude Harmonics | float | 2 | R
0x54CE | 0x54CF | 21710 | 21711 | MAG_2HR_HAR_V_73th_b_% | Aggr 2hr Phase B 73rd Voltage Magnitude Harmonics | float | 2 | R
0x54D0 | 0x54D1 | 21712 | 21713 | MAG_2HR_HAR_V_73th_c_% | Aggr 2hr Phase C 73rd Voltage Magnitude Harmonics | float | 2 | R
0x54D2 | 0x54D3 | 21714 | 21715 | MAG_2HR_HAR_I_73th_a_% | Aggr 2hr Phase A 73rd Current Magnitude Harmonics | float | 2 | R
0x54D4 | 0x54D5 | 21716 | 21717 | MAG_2HR_HAR_I_73th_b_% | Aggr 2hr Phase B 73rd Current Magnitude Harmonics | float | 2 | R
0x54D6 | 0x54D7 | 21718 | 21719 | MAG_2HR_HAR_I_73th_c_% | Aggr 2hr Phase C 73rd Current Magnitude Harmonics | float | 2 | R
0x54D8 | 0x54D9 | 21720 | 21721 | MAG_2HR_HAR_I_73th_n_% | Aggr 2hr Phase N 73rd Current Magnitude Harmonics | float | 2 | R
0x54DA | 0x54DB | 21722 | 21723 | MAG_2HR_HAR_V_74th_a_% | Aggr 2hr Phase A 74th Voltage Magnitude Harmonics | float | 2 | R
0x54DC | 0x54DD | 21724 | 21725 | MAG_2HR_HAR_V_74th_b_% | Aggr 2hr Phase B 74th Voltage Magnitude Harmonics | float | 2 | R
0x54DE | 0x54DF | 21726 | 21727 | MAG_2HR_HAR_V_74th_c_% | Aggr 2hr Phase C 74th Voltage Magnitude Harmonics | float | 2 | R
0x54E0 | 0x54E1 | 21728 | 21729 | MAG_2HR_HAR_I_74th_a_% | Aggr 2hr Phase A 74th Current Magnitude Harmonics | float | 2 | R
0x54E2 | 0x54E3 | 21730 | 21731 | MAG_2HR_HAR_I_74th_b_% | Aggr 2hr Phase B 74th Current Magnitude Harmonics | float | 2 | R
0x54E4 | 0x54E5 | 21732 | 21733 | MAG_2HR_HAR_I_74th_c_% | Aggr 2hr Phase C 74th Current Magnitude Harmonics | float | 2 | R
0x54E6 | 0x54E7 | 21734 | 21735 | MAG_2HR_HAR_I_74th_n_% | Aggr 2hr Phase N 74th Current Magnitude Harmonics | float | 2 | R
0x54E8 | 0x54E9 | 21736 | 21737 | MAG_2HR_HAR_V_75th_a_% | Aggr 2hr Phase A 75th Voltage Magnitude Harmonics | float | 2 | R
0x54EA | 0x54EB | 21738 | 21739 | MAG_2HR_HAR_V_75th_b_% | Aggr 2hr Phase B 75th Voltage Magnitude Harmonics | float | 2 | R
0x54EC | 0x54ED | 21740 | 21741 | MAG_2HR_HAR_V_75th_c_% | Aggr 2hr Phase C 75th Voltage Magnitude Harmonics | float | 2 | R
0x54EE | 0x54EF | 21742 | 21743 | MAG_2HR_HAR_I_75th_a_% | Aggr 2hr Phase A 75th Current Magnitude Harmonics | float | 2 | R
0x54F0 | 0x54F1 | 21744 | 21745 | MAG_2HR_HAR_I_75th_b_% | Aggr 2hr Phase B 75th Current Magnitude Harmonics | float | 2 | R
0x54F2 | 0x54F3 | 21746 | 21747 | MAG_2HR_HAR_I_75th_c_% | Aggr 2hr Phase C 75th Current Magnitude Harmonics | float | 2 | R
0x54F4 | 0x54F5 | 21748 | 21749 | MAG_2HR_HAR_I_75th_n_% | Aggr 2hr Phase N 75th Current Magnitude Harmonics | float | 2 | R
0x54F6 | 0x54F7 | 21750 | 21751 | MAG_2HR_HAR_V_76th_a_% | Aggr 2hr Phase A 76th Voltage Magnitude Harmonics | float | 2 | R
0x54F8 | 0x54F9 | 21752 | 21753 | MAG_2HR_HAR_V_76th_b_% | Aggr 2hr Phase B 76th Voltage Magnitude Harmonics | float | 2 | R
0x54FA | 0x54FB | 21754 | 21755 | MAG_2HR_HAR_V_76th_c_% | Aggr 2hr Phase C 76th Voltage Magnitude Harmonics | float | 2 | R
0x54FC | 0x54FD | 21756 | 21757 | MAG_2HR_HAR_I_76th_a_% | Aggr 2hr Phase A 76th Current Magnitude Harmonics | float | 2 | R
0x54FE | 0x54FF | 21758 | 21759 | MAG_2HR_HAR_I_76th_b_% | Aggr 2hr Phase B 76th Current Magnitude Harmonics | float | 2 | R
0x5500 | 0x5501 | 21760 | 21761 | MAG_2HR_HAR_I_76th_c_% | Aggr 2hr Phase C 76th Current Magnitude Harmonics | float | 2 | R
0x5502 | 0x5503 | 21762 | 21763 | MAG_2HR_HAR_I_76th_n_% | Aggr 2hr Phase N 76th Current Magnitude Harmonics | float | 2 | R
0x5504 | 0x5505 | 21764 | 21765 | MAG_2HR_HAR_V_77th_a_% | Aggr 2hr Phase A 77th Voltage Magnitude Harmonics | float | 2 | R
0x5506 | 0x5507 | 21766 | 21767 | MAG_2HR_HAR_V_77th_b_% | Aggr 2hr Phase B 77th Voltage Magnitude Harmonics | float | 2 | R
0x5508 | 0x5509 | 21768 | 21769 | MAG_2HR_HAR_V_77th_c_% | Aggr 2hr Phase C 77th Voltage Magnitude Harmonics | float | 2 | R
0x550A | 0x550B | 21770 | 21771 | MAG_2HR_HAR_I_77th_a_% | Aggr 2hr Phase A 77th Current Magnitude Harmonics | float | 2 | R
0x550C | 0x550D | 21772 | 21773 | MAG_2HR_HAR_I_77th_b_% | Aggr 2hr Phase B 77th Current Magnitude Harmonics | float | 2 | R
0x550E | 0x550F | 21774 | 21775 | MAG_2HR_HAR_I_77th_c_% | Aggr 2hr Phase C 77th Current Magnitude Harmonics | float | 2 | R
0x5510 | 0x5511 | 21776 | 21777 | MAG_2HR_HAR_I_77th_n_% | Aggr 2hr Phase N 77th Current Magnitude Harmonics | float | 2 | R
0x5512 | 0x5513 | 21778 | 21779 | MAG_2HR_HAR_V_78th_a_% | Aggr 2hr Phase A 78th Voltage Magnitude Harmonics | float | 2 | R
0x5514 | 0x5515 | 21780 | 21781 | MAG_2HR_HAR_V_78th_b_% | Aggr 2hr Phase B 78th Voltage Magnitude Harmonics | float | 2 | R
0x5516 | 0x5517 | 21782 | 21783 | MAG_2HR_HAR_V_78th_c_% | Aggr 2hr Phase C 78th Voltage Magnitude Harmonics | float | 2 | R
0x5518 | 0x5519 | 21784 | 21785 | MAG_2HR_HAR_I_78th_a_% | Aggr 2hr Phase A 78th Current Magnitude Harmonics | float | 2 | R
0x551A | 0x551B | 21786 | 21787 | MAG_2HR_HAR_I_78th_b_% | Aggr 2hr Phase B 78th Current Magnitude Harmonics | float | 2 | R
0x551C | 0x551D | 21788 | 21789 | MAG_2HR_HAR_I_78th_c_% | Aggr 2hr Phase C 78th Current Magnitude Harmonics | float | 2 | R
0x551E | 0x551F | 21790 | 21791 | MAG_2HR_HAR_I_78th_n_% | Aggr 2hr Phase N 78th Current Magnitude Harmonics | float | 2 | R
0x5520 | 0x5521 | 21792 | 21793 | MAG_2HR_HAR_V_79th_a_% | Aggr 2hr Phase A 79th Voltage Magnitude Harmonics | float | 2 | R
0x5522 | 0x5523 | 21794 | 21795 | MAG_2HR_HAR_V_79th_b_% | Aggr 2hr Phase B 79th Voltage Magnitude Harmonics | float | 2 | R
0x5524 | 0x5525 | 21796 | 21797 | MAG_2HR_HAR_V_79th_c_% | Aggr 2hr Phase C 79th Voltage Magnitude Harmonics | float | 2 | R
0x5526 | 0x5527 | 21798 | 21799 | MAG_2HR_HAR_I_79th_a_% | Aggr 2hr Phase A 79th Current Magnitude Harmonics | float | 2 | R
0x5528 | 0x5529 | 21800 | 21801 | MAG_2HR_HAR_I_79th_b_% | Aggr 2hr Phase B 79th Current Magnitude Harmonics | float | 2 | R
0x552A | 0x552B | 21802 | 21803 | MAG_2HR_HAR_I_79th_c_% | Aggr 2hr Phase C 79th Current Magnitude Harmonics | float | 2 | R
0x552C | 0x552D | 21804 | 21805 | MAG_2HR_HAR_I_79th_n_% | Aggr 2hr Phase N 79th Current Magnitude Harmonics | float | 2 | R
0x552E | 0x552F | 21806 | 21807 | MAG_2HR_HAR_V_80th_a_% | Aggr 2hr Phase A 80th Voltage Magnitude Harmonics | float | 2 | R
0x5530 | 0x5531 | 21808 | 21809 | MAG_2HR_HAR_V_80th_b_% | Aggr 2hr Phase B 80th Voltage Magnitude Harmonics | float | 2 | R
0x5532 | 0x5533 | 21810 | 21811 | MAG_2HR_HAR_V_80th_c_% | Aggr 2hr Phase C 80th Voltage Magnitude Harmonics | float | 2 | R
0x5534 | 0x5535 | 21812 | 21813 | MAG_2HR_HAR_I_80th_a_% | Aggr 2hr Phase A 80th Current Magnitude Harmonics | float | 2 | R
0x5536 | 0x5537 | 21814 | 21815 | MAG_2HR_HAR_I_80th_b_% | Aggr 2hr Phase B 80th Current Magnitude Harmonics | float | 2 | R
0x5538 | 0x5539 | 21816 | 21817 | MAG_2HR_HAR_I_80th_c_% | Aggr 2hr Phase C 80th Current Magnitude Harmonics | float | 2 | R
0x553A | 0x553B | 21818 | 21819 | MAG_2HR_HAR_I_80th_n_% | Aggr 2hr Phase N 80th Current Magnitude Harmonics | float | 2 | R
0x553C | 0x553D | 21820 | 21821 | MAG_2HR_HAR_V_81th_a_% | Aggr 2hr Phase A 81st Voltage Magnitude Harmonics | float | 2 | R
0x553E | 0x553F | 21822 | 21823 | MAG_2HR_HAR_V_81th_b_% | Aggr 2hr Phase B 81st Voltage Magnitude Harmonics | float | 2 | R
0x5540 | 0x5541 | 21824 | 21825 | MAG_2HR_HAR_V_81th_c_% | Aggr 2hr Phase C 81st Voltage Magnitude Harmonics | float | 2 | R
0x5542 | 0x5543 | 21826 | 21827 | MAG_2HR_HAR_I_81th_a_% | Aggr 2hr Phase A 81st Current Magnitude Harmonics | float | 2 | R
0x5544 | 0x5545 | 21828 | 21829 | MAG_2HR_HAR_I_81th_b_% | Aggr 2hr Phase B 81st Current Magnitude Harmonics | float | 2 | R
0x5546 | 0x5547 | 21830 | 21831 | MAG_2HR_HAR_I_81th_c_% | Aggr 2hr Phase C 81st Current Magnitude Harmonics | float | 2 | R
0x5548 | 0x5549 | 21832 | 21833 | MAG_2HR_HAR_I_81th_n_% | Aggr 2hr Phase N 81st Current Magnitude Harmonics | float | 2 | R
0x554A | 0x554B | 21834 | 21835 | MAG_2HR_HAR_V_82th_a_% | Aggr 2hr Phase A 82nd Voltage Magnitude Harmonics | float | 2 | R
0x554C | 0x554D | 21836 | 21837 | MAG_2HR_HAR_V_82th_b_% | Aggr 2hr Phase B 82nd Voltage Magnitude Harmonics | float | 2 | R
0x554E | 0x554F | 21838 | 21839 | MAG_2HR_HAR_V_82th_c_% | Aggr 2hr Phase C 82nd Voltage Magnitude Harmonics | float | 2 | R
0x5550 | 0x5551 | 21840 | 21841 | MAG_2HR_HAR_I_82th_a_% | Aggr 2hr Phase A 82nd Current Magnitude Harmonics | float | 2 | R
0x5552 | 0x5553 | 21842 | 21843 | MAG_2HR_HAR_I_82th_b_% | Aggr 2hr Phase B 82nd Current Magnitude Harmonics | float | 2 | R
0x5554 | 0x5555 | 21844 | 21845 | MAG_2HR_HAR_I_82th_c_% | Aggr 2hr Phase C 82nd Current Magnitude Harmonics | float | 2 | R
0x5556 | 0x5557 | 21846 | 21847 | MAG_2HR_HAR_I_82th_n_% | Aggr 2hr Phase N 82nd Current Magnitude Harmonics | float | 2 | R
0x5558 | 0x5559 | 21848 | 21849 | MAG_2HR_HAR_V_83th_a_% | Aggr 2hr Phase A 83rd Voltage Magnitude Harmonics | float | 2 | R
0x555A | 0x555B | 21850 | 21851 | MAG_2HR_HAR_V_83th_b_% | Aggr 2hr Phase B 83rd Voltage Magnitude Harmonics | float | 2 | R
0x555C | 0x555D | 21852 | 21853 | MAG_2HR_HAR_V_83th_c_% | Aggr 2hr Phase C 83rd Voltage Magnitude Harmonics | float | 2 | R
0x555E | 0x555F | 21854 | 21855 | MAG_2HR_HAR_I_83th_a_% | Aggr 2hr Phase A 83rd Current Magnitude Harmonics | float | 2 | R
0x5560 | 0x5561 | 21856 | 21857 | MAG_2HR_HAR_I_83th_b_% | Aggr 2hr Phase B 83rd Current Magnitude Harmonics | float | 2 | R
0x5562 | 0x5563 | 21858 | 21859 | MAG_2HR_HAR_I_83th_c_% | Aggr 2hr Phase C 83rd Current Magnitude Harmonics | float | 2 | R
0x5564 | 0x5565 | 21860 | 21861 | MAG_2HR_HAR_I_83th_n_% | Aggr 2hr Phase N 83rd Current Magnitude Harmonics | float | 2 | R
0x5566 | 0x5567 | 21862 | 21863 | MAG_2HR_HAR_V_84th_a_% | Aggr 2hr Phase A 84th Voltage Magnitude Harmonics | float | 2 | R
0x5568 | 0x5569 | 21864 | 21865 | MAG_2HR_HAR_V_84th_b_% | Aggr 2hr Phase B 84th Voltage Magnitude Harmonics | float | 2 | R
0x556A | 0x556B | 21866 | 21867 | MAG_2HR_HAR_V_84th_c_% | Aggr 2hr Phase C 84th Voltage Magnitude Harmonics | float | 2 | R
0x556C | 0x556D | 21868 | 21869 | MAG_2HR_HAR_I_84th_a_% | Aggr 2hr Phase A 84th Current Magnitude Harmonics | float | 2 | R
0x556E | 0x556F | 21870 | 21871 | MAG_2HR_HAR_I_84th_b_% | Aggr 2hr Phase B 84th Current Magnitude Harmonics | float | 2 | R
0x5570 | 0x5571 | 21872 | 21873 | MAG_2HR_HAR_I_84th_c_% | Aggr 2hr Phase C 84th Current Magnitude Harmonics | float | 2 | R
0x5572 | 0x5573 | 21874 | 21875 | MAG_2HR_HAR_I_84th_n_% | Aggr 2hr Phase N 84th Current Magnitude Harmonics | float | 2 | R
0x5574 | 0x5575 | 21876 | 21877 | MAG_2HR_HAR_V_85th_a_% | Aggr 2hr Phase A 85th Voltage Magnitude Harmonics | float | 2 | R
0x5576 | 0x5577 | 21878 | 21879 | MAG_2HR_HAR_V_85th_b_% | Aggr 2hr Phase B 85th Voltage Magnitude Harmonics | float | 2 | R
0x5578 | 0x5579 | 21880 | 21881 | MAG_2HR_HAR_V_85th_c_% | Aggr 2hr Phase C 85th Voltage Magnitude Harmonics | float | 2 | R
0x557A | 0x557B | 21882 | 21883 | MAG_2HR_HAR_I_85th_a_% | Aggr 2hr Phase A 85th Current Magnitude Harmonics | float | 2 | R
0x557C | 0x557D | 21884 | 21885 | MAG_2HR_HAR_I_85th_b_% | Aggr 2hr Phase B 85th Current Magnitude Harmonics | float | 2 | R
0x557E | 0x557F | 21886 | 21887 | MAG_2HR_HAR_I_85th_c_% | Aggr 2hr Phase C 85th Current Magnitude Harmonics | float | 2 | R
0x5580 | 0x5581 | 21888 | 21889 | MAG_2HR_HAR_I_85th_n_% | Aggr 2hr Phase N 85th Current Magnitude Harmonics | float | 2 | R
0x5582 | 0x5583 | 21890 | 21891 | MAG_2HR_HAR_V_86th_a_% | Aggr 2hr Phase A 86th Voltage Magnitude Harmonics | float | 2 | R
0x5584 | 0x5585 | 21892 | 21893 | MAG_2HR_HAR_V_86th_b_% | Aggr 2hr Phase B 86th Voltage Magnitude Harmonics | float | 2 | R
0x5586 | 0x5587 | 21894 | 21895 | MAG_2HR_HAR_V_86th_c_% | Aggr 2hr Phase C 86th Voltage Magnitude Harmonics | float | 2 | R
0x5588 | 0x5589 | 21896 | 21897 | MAG_2HR_HAR_I_86th_a_% | Aggr 2hr Phase A 86th Current Magnitude Harmonics | float | 2 | R
0x558A | 0x558B | 21898 | 21899 | MAG_2HR_HAR_I_86th_b_% | Aggr 2hr Phase B 86th Current Magnitude Harmonics | float | 2 | R
0x558C | 0x558D | 21900 | 21901 | MAG_2HR_HAR_I_86th_c_% | Aggr 2hr Phase C 86th Current Magnitude Harmonics | float | 2 | R
0x558E | 0x558F | 21902 | 21903 | MAG_2HR_HAR_I_86th_n_% | Aggr 2hr Phase N 86th Current Magnitude Harmonics | float | 2 | R
0x5590 | 0x5591 | 21904 | 21905 | MAG_2HR_HAR_V_87th_a_% | Aggr 2hr Phase A 87th Voltage Magnitude Harmonics | float | 2 | R
0x5592 | 0x5593 | 21906 | 21907 | MAG_2HR_HAR_V_87th_b_% | Aggr 2hr Phase B 87th Voltage Magnitude Harmonics | float | 2 | R
0x5594 | 0x5595 | 21908 | 21909 | MAG_2HR_HAR_V_87th_c_% | Aggr 2hr Phase C 87th Voltage Magnitude Harmonics | float | 2 | R
0x5596 | 0x5597 | 21910 | 21911 | MAG_2HR_HAR_I_87th_a_% | Aggr 2hr Phase A 87th Current Magnitude Harmonics | float | 2 | R
0x5598 | 0x5599 | 21912 | 21913 | MAG_2HR_HAR_I_87th_b_% | Aggr 2hr Phase B 87th Current Magnitude Harmonics | float | 2 | R
0x559A | 0x559B | 21914 | 21915 | MAG_2HR_HAR_I_87th_c_% | Aggr 2hr Phase C 87th Current Magnitude Harmonics | float | 2 | R
0x559C | 0x559D | 21916 | 21917 | MAG_2HR_HAR_I_87th_n_% | Aggr 2hr Phase N 87th Current Magnitude Harmonics | float | 2 | R
0x559E | 0x559F | 21918 | 21919 | MAG_2HR_HAR_V_88th_a_% | Aggr 2hr Phase A 88th Voltage Magnitude Harmonics | float | 2 | R
0x55A0 | 0x55A1 | 21920 | 21921 | MAG_2HR_HAR_V_88th_b_% | Aggr 2hr Phase B 88th Voltage Magnitude Harmonics | float | 2 | R
0x55A2 | 0x55A3 | 21922 | 21923 | MAG_2HR_HAR_V_88th_c_% | Aggr 2hr Phase C 88th Voltage Magnitude Harmonics | float | 2 | R
0x55A4 | 0x55A5 | 21924 | 21925 | MAG_2HR_HAR_I_88th_a_% | Aggr 2hr Phase A 88th Current Magnitude Harmonics | float | 2 | R
0x55A6 | 0x55A7 | 21926 | 21927 | MAG_2HR_HAR_I_88th_b_% | Aggr 2hr Phase B 88th Current Magnitude Harmonics | float | 2 | R
0x55A8 | 0x55A9 | 21928 | 21929 | MAG_2HR_HAR_I_88th_c_% | Aggr 2hr Phase C 88th Current Magnitude Harmonics | float | 2 | R
0x55AA | 0x55AB | 21930 | 21931 | MAG_2HR_HAR_I_88th_n_% | Aggr 2hr Phase N 88th Current Magnitude Harmonics | float | 2 | R
0x55AC | 0x55AD | 21932 | 21933 | MAG_2HR_HAR_V_89th_a_% | Aggr 2hr Phase A 89th Voltage Magnitude Harmonics | float | 2 | R
0x55AE | 0x55AF | 21934 | 21935 | MAG_2HR_HAR_V_89th_b_% | Aggr 2hr Phase B 89th Voltage Magnitude Harmonics | float | 2 | R
0x55B0 | 0x55B1 | 21936 | 21937 | MAG_2HR_HAR_V_89th_c_% | Aggr 2hr Phase C 89th Voltage Magnitude Harmonics | float | 2 | R
0x55B2 | 0x55B3 | 21938 | 21939 | MAG_2HR_HAR_I_89th_a_% | Aggr 2hr Phase A 89th Current Magnitude Harmonics | float | 2 | R
0x55B4 | 0x55B5 | 21940 | 21941 | MAG_2HR_HAR_I_89th_b_% | Aggr 2hr Phase B 89th Current Magnitude Harmonics | float | 2 | R
0x55B6 | 0x55B7 | 21942 | 21943 | MAG_2HR_HAR_I_89th_c_% | Aggr 2hr Phase C 89th Current Magnitude Harmonics | float | 2 | R
0x55B8 | 0x55B9 | 21944 | 21945 | MAG_2HR_HAR_I_89th_n_% | Aggr 2hr Phase N 89th Current Magnitude Harmonics | float | 2 | R
0x55BA | 0x55BB | 21946 | 21947 | MAG_2HR_HAR_V_90th_a_% | Aggr 2hr Phase A 90th Voltage Magnitude Harmonics | float | 2 | R
0x55BC | 0x55BD | 21948 | 21949 | MAG_2HR_HAR_V_90th_b_% | Aggr 2hr Phase B 90th Voltage Magnitude Harmonics | float | 2 | R
0x55BE | 0x55BF | 21950 | 21951 | MAG_2HR_HAR_V_90th_c_% | Aggr 2hr Phase C 90th Voltage Magnitude Harmonics | float | 2 | R
0x55C0 | 0x55C1 | 21952 | 21953 | MAG_2HR_HAR_I_90th_a_% | Aggr 2hr Phase A 90th Current Magnitude Harmonics | float | 2 | R
0x55C2 | 0x55C3 | 21954 | 21955 | MAG_2HR_HAR_I_90th_b_% | Aggr 2hr Phase B 90th Current Magnitude Harmonics | float | 2 | R
0x55C4 | 0x55C5 | 21956 | 21957 | MAG_2HR_HAR_I_90th_c_% | Aggr 2hr Phase C 90th Current Magnitude Harmonics | float | 2 | R
0x55C6 | 0x55C7 | 21958 | 21959 | MAG_2HR_HAR_I_90th_n_% | Aggr 2hr Phase N 90th Current Magnitude Harmonics | float | 2 | R
0x55C8 | 0x55C9 | 21960 | 21961 | MAG_2HR_HAR_V_91th_a_% | Aggr 2hr Phase A 91st Voltage Magnitude Harmonics | float | 2 | R
0x55CA | 0x55CB | 21962 | 21963 | MAG_2HR_HAR_V_91th_b_% | Aggr 2hr Phase B 91st Voltage Magnitude Harmonics | float | 2 | R
0x55CC | 0x55CD | 21964 | 21965 | MAG_2HR_HAR_V_91th_c_% | Aggr 2hr Phase C 91st Voltage Magnitude Harmonics | float | 2 | R
0x55CE | 0x55CF | 21966 | 21967 | MAG_2HR_HAR_I_91th_a_% | Aggr 2hr Phase A 91st Current Magnitude Harmonics | float | 2 | R
0x55D0 | 0x55D1 | 21968 | 21969 | MAG_2HR_HAR_I_91th_b_% | Aggr 2hr Phase B 91st Current Magnitude Harmonics | float | 2 | R
0x55D2 | 0x55D3 | 21970 | 21971 | MAG_2HR_HAR_I_91th_c_% | Aggr 2hr Phase C 91st Current Magnitude Harmonics | float | 2 | R
0x55D4 | 0x55D5 | 21972 | 21973 | MAG_2HR_HAR_I_91th_n_% | Aggr 2hr Phase N 91st Current Magnitude Harmonics | float | 2 | R
0x55D6 | 0x55D7 | 21974 | 21975 | MAG_2HR_HAR_V_92th_a_% | Aggr 2hr Phase A 92nd Voltage Magnitude Harmonics | float | 2 | R
0x55D8 | 0x55D9 | 21976 | 21977 | MAG_2HR_HAR_V_92th_b_% | Aggr 2hr Phase B 92nd Voltage Magnitude Harmonics | float | 2 | R
0x55DA | 0x55DB | 21978 | 21979 | MAG_2HR_HAR_V_92th_c_% | Aggr 2hr Phase C 92nd Voltage Magnitude Harmonics | float | 2 | R
0x55DC | 0x55DD | 21980 | 21981 | MAG_2HR_HAR_I_92th_a_% | Aggr 2hr Phase A 92nd Current Magnitude Harmonics | float | 2 | R
0x55DE | 0x55DF | 21982 | 21983 | MAG_2HR_HAR_I_92th_b_% | Aggr 2hr Phase B 92nd Current Magnitude Harmonics | float | 2 | R
0x55E0 | 0x55E1 | 21984 | 21985 | MAG_2HR_HAR_I_92th_c_% | Aggr 2hr Phase C 92nd Current Magnitude Harmonics | float | 2 | R
0x55E2 | 0x55E3 | 21986 | 21987 | MAG_2HR_HAR_I_92th_n_% | Aggr 2hr Phase N 92nd Current Magnitude Harmonics | float | 2 | R
0x55E4 | 0x55E5 | 21988 | 21989 | MAG_2HR_HAR_V_93th_a_% | Aggr 2hr Phase A 93rd Voltage Magnitude Harmonics | float | 2 | R
0x55E6 | 0x55E7 | 21990 | 21991 | MAG_2HR_HAR_V_93th_b_% | Aggr 2hr Phase B 93rd Voltage Magnitude Harmonics | float | 2 | R
0x55E8 | 0x55E9 | 21992 | 21993 | MAG_2HR_HAR_V_93th_c_% | Aggr 2hr Phase C 93rd Voltage Magnitude Harmonics | float | 2 | R
0x55EA | 0x55EB | 21994 | 21995 | MAG_2HR_HAR_I_93th_a_% | Aggr 2hr Phase A 93rd Current Magnitude Harmonics | float | 2 | R
0x55EC | 0x55ED | 21996 | 21997 | MAG_2HR_HAR_I_93th_b_% | Aggr 2hr Phase B 93rd Current Magnitude Harmonics | float | 2 | R
0x55EE | 0x55EF | 21998 | 21999 | MAG_2HR_HAR_I_93th_c_% | Aggr 2hr Phase C 93rd Current Magnitude Harmonics | float | 2 | R
0x55F0 | 0x55F1 | 22000 | 22001 | MAG_2HR_HAR_I_93th_n_% | Aggr 2hr Phase N 93rd Current Magnitude Harmonics | float | 2 | R
0x55F2 | 0x55F3 | 22002 | 22003 | MAG_2HR_HAR_V_94th_a_% | Aggr 2hr Phase A 94th Voltage Magnitude Harmonics | float | 2 | R
0x55F4 | 0x55F5 | 22004 | 22005 | MAG_2HR_HAR_V_94th_b_% | Aggr 2hr Phase B 94th Voltage Magnitude Harmonics | float | 2 | R
0x55F6 | 0x55F7 | 22006 | 22007 | MAG_2HR_HAR_V_94th_c_% | Aggr 2hr Phase C 94th Voltage Magnitude Harmonics | float | 2 | R
0x55F8 | 0x55F9 | 22008 | 22009 | MAG_2HR_HAR_I_94th_a_% | Aggr 2hr Phase A 94th Current Magnitude Harmonics | float | 2 | R
0x55FA | 0x55FB | 22010 | 22011 | MAG_2HR_HAR_I_94th_b_% | Aggr 2hr Phase B 94th Current Magnitude Harmonics | float | 2 | R
0x55FC | 0x55FD | 22012 | 22013 | MAG_2HR_HAR_I_94th_c_% | Aggr 2hr Phase C 94th Current Magnitude Harmonics | float | 2 | R
0x55FE | 0x55FF | 22014 | 22015 | MAG_2HR_HAR_I_94th_n_% | Aggr 2hr Phase N 94th Current Magnitude Harmonics | float | 2 | R
0x5600 | 0x5601 | 22016 | 22017 | MAG_2HR_HAR_V_95th_a_% | Aggr 2hr Phase A 95th Voltage Magnitude Harmonics | float | 2 | R
0x5602 | 0x5603 | 22018 | 22019 | MAG_2HR_HAR_V_95th_b_% | Aggr 2hr Phase B 95th Voltage Magnitude Harmonics | float | 2 | R
0x5604 | 0x5605 | 22020 | 22021 | MAG_2HR_HAR_V_95th_c_% | Aggr 2hr Phase C 95th Voltage Magnitude Harmonics | float | 2 | R
0x5606 | 0x5607 | 22022 | 22023 | MAG_2HR_HAR_I_95th_a_% | Aggr 2hr Phase A 95th Current Magnitude Harmonics | float | 2 | R
0x5608 | 0x5609 | 22024 | 22025 | MAG_2HR_HAR_I_95th_b_% | Aggr 2hr Phase B 95th Current Magnitude Harmonics | float | 2 | R
0x560A | 0x560B | 22026 | 22027 | MAG_2HR_HAR_I_95th_c_% | Aggr 2hr Phase C 95th Current Magnitude Harmonics | float | 2 | R
0x560C | 0x560D | 22028 | 22029 | MAG_2HR_HAR_I_95th_n_% | Aggr 2hr Phase N 95th Current Magnitude Harmonics | float | 2 | R
0x560E | 0x560F | 22030 | 22031 | MAG_2HR_HAR_V_96th_a_% | Aggr 2hr Phase A 96th Voltage Magnitude Harmonics | float | 2 | R
0x5610 | 0x5611 | 22032 | 22033 | MAG_2HR_HAR_V_96th_b_% | Aggr 2hr Phase B 96th Voltage Magnitude Harmonics | float | 2 | R
0x5612 | 0x5613 | 22034 | 22035 | MAG_2HR_HAR_V_96th_c_% | Aggr 2hr Phase C 96th Voltage Magnitude Harmonics | float | 2 | R
0x5614 | 0x5615 | 22036 | 22037 | MAG_2HR_HAR_I_96th_a_% | Aggr 2hr Phase A 96th Current Magnitude Harmonics | float | 2 | R
0x5616 | 0x5617 | 22038 | 22039 | MAG_2HR_HAR_I_96th_b_% | Aggr 2hr Phase B 96th Current Magnitude Harmonics | float | 2 | R
0x5618 | 0x5619 | 22040 | 22041 | MAG_2HR_HAR_I_96th_c_% | Aggr 2hr Phase C 96th Current Magnitude Harmonics | float | 2 | R
0x561A | 0x561B | 22042 | 22043 | MAG_2HR_HAR_I_96th_n_% | Aggr 2hr Phase N 96th Current Magnitude Harmonics | float | 2 | R
0x561C | 0x561D | 22044 | 22045 | MAG_2HR_HAR_V_97th_a_% | Aggr 2hr Phase A 97th Voltage Magnitude Harmonics | float | 2 | R
0x561E | 0x561F | 22046 | 22047 | MAG_2HR_HAR_V_97th_b_% | Aggr 2hr Phase B 97th Voltage Magnitude Harmonics | float | 2 | R
0x5620 | 0x5621 | 22048 | 22049 | MAG_2HR_HAR_V_97th_c_% | Aggr 2hr Phase C 97th Voltage Magnitude Harmonics | float | 2 | R
0x5622 | 0x5623 | 22050 | 22051 | MAG_2HR_HAR_I_97th_a_% | Aggr 2hr Phase A 97th Current Magnitude Harmonics | float | 2 | R
0x5624 | 0x5625 | 22052 | 22053 | MAG_2HR_HAR_I_97th_b_% | Aggr 2hr Phase B 97th Current Magnitude Harmonics | float | 2 | R
0x5626 | 0x5627 | 22054 | 22055 | MAG_2HR_HAR_I_97th_c_% | Aggr 2hr Phase C 97th Current Magnitude Harmonics | float | 2 | R
0x5628 | 0x5629 | 22056 | 22057 | MAG_2HR_HAR_I_97th_n_% | Aggr 2hr Phase N 97th Current Magnitude Harmonics | float | 2 | R
0x562A | 0x562B | 22058 | 22059 | MAG_2HR_HAR_V_98th_a_% | Aggr 2hr Phase A 98th Voltage Magnitude Harmonics | float | 2 | R
0x562C | 0x562D | 22060 | 22061 | MAG_2HR_HAR_V_98th_b_% | Aggr 2hr Phase B 98th Voltage Magnitude Harmonics | float | 2 | R
0x562E | 0x562F | 22062 | 22063 | MAG_2HR_HAR_V_98th_c_% | Aggr 2hr Phase C 98th Voltage Magnitude Harmonics | float | 2 | R
0x5630 | 0x5631 | 22064 | 22065 | MAG_2HR_HAR_I_98th_a_% | Aggr 2hr Phase A 98th Current Magnitude Harmonics | float | 2 | R
0x5632 | 0x5633 | 22066 | 22067 | MAG_2HR_HAR_I_98th_b_% | Aggr 2hr Phase B 98th Current Magnitude Harmonics | float | 2 | R
0x5634 | 0x5635 | 22068 | 22069 | MAG_2HR_HAR_I_98th_c_% | Aggr 2hr Phase C 98th Current Magnitude Harmonics | float | 2 | R
0x5636 | 0x5637 | 22070 | 22071 | MAG_2HR_HAR_I_98th_n_% | Aggr 2hr Phase N 98th Current Magnitude Harmonics | float | 2 | R
0x5638 | 0x5639 | 22072 | 22073 | MAG_2HR_HAR_V_99th_a_% | Aggr 2hr Phase A 99th Voltage Magnitude Harmonics | float | 2 | R
0x563A | 0x563B | 22074 | 22075 | MAG_2HR_HAR_V_99th_b_% | Aggr 2hr Phase B 99th Voltage Magnitude Harmonics | float | 2 | R
0x563C | 0x563D | 22076 | 22077 | MAG_2HR_HAR_V_99th_c_% | Aggr 2hr Phase C 99th Voltage Magnitude Harmonics | float | 2 | R
0x563E | 0x563F | 22078 | 22079 | MAG_2HR_HAR_I_99th_a_% | Aggr 2hr Phase A 99th Current Magnitude Harmonics | float | 2 | R
0x5640 | 0x5641 | 22080 | 22081 | MAG_2HR_HAR_I_99th_b_% | Aggr 2hr Phase B 99th Current Magnitude Harmonics | float | 2 | R
0x5642 | 0x5643 | 22082 | 22083 | MAG_2HR_HAR_I_99th_c_% | Aggr 2hr Phase C 99th Current Magnitude Harmonics | float | 2 | R
0x5644 | 0x5645 | 22084 | 22085 | MAG_2HR_HAR_I_99th_n_% | Aggr 2hr Phase N 99th Current Magnitude Harmonics | float | 2 | R
0x5646 | 0x5647 | 22086 | 22087 | MAG_2HR_HAR_V_100th_a_% | Aggr 2hr Phase A 100th Voltage Magnitude Harmonics | float | 2 | R
0x5648 | 0x5649 | 22088 | 22089 | MAG_2HR_HAR_V_100th_b_% | Aggr 2hr Phase B 100th Voltage Magnitude Harmonics | float | 2 | R
0x564A | 0x564B | 22090 | 22091 | MAG_2HR_HAR_V_100th_c_% | Aggr 2hr Phase C 100th Voltage Magnitude Harmonics | float | 2 | R
0x564C | 0x564D | 22092 | 22093 | MAG_2HR_HAR_I_100th_a_% | Aggr 2hr Phase A 100th Current Magnitude Harmonics | float | 2 | R
0x564E | 0x564F | 22094 | 22095 | MAG_2HR_HAR_I_100th_b_% | Aggr 2hr Phase B 100th Current Magnitude Harmonics | float | 2 | R
0x5650 | 0x5651 | 22096 | 22097 | MAG_2HR_HAR_I_100th_c_% | Aggr 2hr Phase C 100th Current Magnitude Harmonics | float | 2 | R
0x5652 | 0x5653 | 22098 | 22099 | MAG_2HR_HAR_I_100th_n_% | Aggr 2hr Phase N 100th Current Magnitude Harmonics | float | 2 | R
0x5654 | 0x5655 | 22100 | 22101 | MAG_2HR_HAR_V_101th_a_% | Aggr 2hr Phase A 101st Voltage Magnitude Harmonics | float | 2 | R
0x5656 | 0x5657 | 22102 | 22103 | MAG_2HR_HAR_V_101th_b_% | Aggr 2hr Phase B 101st Voltage Magnitude Harmonics | float | 2 | R
0x5658 | 0x5659 | 22104 | 22105 | MAG_2HR_HAR_V_101th_c_% | Aggr 2hr Phase C 101st Voltage Magnitude Harmonics | float | 2 | R
0x565A | 0x565B | 22106 | 22107 | MAG_2HR_HAR_I_101th_a_% | Aggr 2hr Phase A 101st Current Magnitude Harmonics | float | 2 | R
0x565C | 0x565D | 22108 | 22109 | MAG_2HR_HAR_I_101th_b_% | Aggr 2hr Phase B 101st Current Magnitude Harmonics | float | 2 | R
0x565E | 0x565F | 22110 | 22111 | MAG_2HR_HAR_I_101th_c_% | Aggr 2hr Phase C 101st Current Magnitude Harmonics | float | 2 | R
0x5660 | 0x5661 | 22112 | 22113 | MAG_2HR_HAR_I_101th_n_% | Aggr 2hr Phase N 101st Current Magnitude Harmonics | float | 2 | R
0x5662 | 0x5663 | 22114 | 22115 | MAG_2HR_HAR_V_102th_a_% | Aggr 2hr Phase A 102nd Voltage Magnitude Harmonics | float | 2 | R
0x5664 | 0x5665 | 22116 | 22117 | MAG_2HR_HAR_V_102th_b_% | Aggr 2hr Phase B 102nd Voltage Magnitude Harmonics | float | 2 | R
0x5666 | 0x5667 | 22118 | 22119 | MAG_2HR_HAR_V_102th_c_% | Aggr 2hr Phase C 102nd Voltage Magnitude Harmonics | float | 2 | R
0x5668 | 0x5669 | 22120 | 22121 | MAG_2HR_HAR_I_102th_a_% | Aggr 2hr Phase A 102nd Current Magnitude Harmonics | float | 2 | R
0x566A | 0x566B | 22122 | 22123 | MAG_2HR_HAR_I_102th_b_% | Aggr 2hr Phase B 102nd Current Magnitude Harmonics | float | 2 | R
0x566C | 0x566D | 22124 | 22125 | MAG_2HR_HAR_I_102th_c_% | Aggr 2hr Phase C 102nd Current Magnitude Harmonics | float | 2 | R
0x566E | 0x566F | 22126 | 22127 | MAG_2HR_HAR_I_102th_n_% | Aggr 2hr Phase N 102nd Current Magnitude Harmonics | float | 2 | R
0x5670 | 0x5671 | 22128 | 22129 | MAG_2HR_HAR_V_103th_a_% | Aggr 2hr Phase A 103rd Voltage Magnitude Harmonics | float | 2 | R
0x5672 | 0x5673 | 22130 | 22131 | MAG_2HR_HAR_V_103th_b_% | Aggr 2hr Phase B 103rd Voltage Magnitude Harmonics | float | 2 | R
0x5674 | 0x5675 | 22132 | 22133 | MAG_2HR_HAR_V_103th_c_% | Aggr 2hr Phase C 103rd Voltage Magnitude Harmonics | float | 2 | R
0x5676 | 0x5677 | 22134 | 22135 | MAG_2HR_HAR_I_103th_a_% | Aggr 2hr Phase A 103rd Current Magnitude Harmonics | float | 2 | R
0x5678 | 0x5679 | 22136 | 22137 | MAG_2HR_HAR_I_103th_b_% | Aggr 2hr Phase B 103rd Current Magnitude Harmonics | float | 2 | R
0x567A | 0x567B | 22138 | 22139 | MAG_2HR_HAR_I_103th_c_% | Aggr 2hr Phase C 103rd Current Magnitude Harmonics | float | 2 | R
0x567C | 0x567D | 22140 | 22141 | MAG_2HR_HAR_I_103th_n_% | Aggr 2hr Phase N 103rd Current Magnitude Harmonics | float | 2 | R
0x567E | 0x567F | 22142 | 22143 | MAG_2HR_HAR_V_104th_a_% | Aggr 2hr Phase A 104th Voltage Magnitude Harmonics | float | 2 | R
0x5680 | 0x5681 | 22144 | 22145 | MAG_2HR_HAR_V_104th_b_% | Aggr 2hr Phase B 104th Voltage Magnitude Harmonics | float | 2 | R
0x5682 | 0x5683 | 22146 | 22147 | MAG_2HR_HAR_V_104th_c_% | Aggr 2hr Phase C 104th Voltage Magnitude Harmonics | float | 2 | R
0x5684 | 0x5685 | 22148 | 22149 | MAG_2HR_HAR_I_104th_a_% | Aggr 2hr Phase A 104th Current Magnitude Harmonics | float | 2 | R
0x5686 | 0x5687 | 22150 | 22151 | MAG_2HR_HAR_I_104th_b_% | Aggr 2hr Phase B 104th Current Magnitude Harmonics | float | 2 | R
0x5688 | 0x5689 | 22152 | 22153 | MAG_2HR_HAR_I_104th_c_% | Aggr 2hr Phase C 104th Current Magnitude Harmonics | float | 2 | R
0x568A | 0x568B | 22154 | 22155 | MAG_2HR_HAR_I_104th_n_% | Aggr 2hr Phase N 104th Current Magnitude Harmonics | float | 2 | R
0x568C | 0x568D | 22156 | 22157 | MAG_2HR_HAR_V_105th_a_% | Aggr 2hr Phase A 105th Voltage Magnitude Harmonics | float | 2 | R
0x568E | 0x568F | 22158 | 22159 | MAG_2HR_HAR_V_105th_b_% | Aggr 2hr Phase B 105th Voltage Magnitude Harmonics | float | 2 | R
0x5690 | 0x5691 | 22160 | 22161 | MAG_2HR_HAR_V_105th_c_% | Aggr 2hr Phase C 105th Voltage Magnitude Harmonics | float | 2 | R
0x5692 | 0x5693 | 22162 | 22163 | MAG_2HR_HAR_I_105th_a_% | Aggr 2hr Phase A 105th Current Magnitude Harmonics | float | 2 | R
0x5694 | 0x5695 | 22164 | 22165 | MAG_2HR_HAR_I_105th_b_% | Aggr 2hr Phase B 105th Current Magnitude Harmonics | float | 2 | R
0x5696 | 0x5697 | 22166 | 22167 | MAG_2HR_HAR_I_105th_c_% | Aggr 2hr Phase C 105th Current Magnitude Harmonics | float | 2 | R
0x5698 | 0x5699 | 22168 | 22169 | MAG_2HR_HAR_I_105th_n_% | Aggr 2hr Phase N 105th Current Magnitude Harmonics | float | 2 | R
0x569A | 0x569B | 22170 | 22171 | MAG_2HR_HAR_V_106th_a_% | Aggr 2hr Phase A 106th Voltage Magnitude Harmonics | float | 2 | R
0x569C | 0x569D | 22172 | 22173 | MAG_2HR_HAR_V_106th_b_% | Aggr 2hr Phase B 106th Voltage Magnitude Harmonics | float | 2 | R
0x569E | 0x569F | 22174 | 22175 | MAG_2HR_HAR_V_106th_c_% | Aggr 2hr Phase C 106th Voltage Magnitude Harmonics | float | 2 | R
0x56A0 | 0x56A1 | 22176 | 22177 | MAG_2HR_HAR_I_106th_a_% | Aggr 2hr Phase A 106th Current Magnitude Harmonics | float | 2 | R
0x56A2 | 0x56A3 | 22178 | 22179 | MAG_2HR_HAR_I_106th_b_% | Aggr 2hr Phase B 106th Current Magnitude Harmonics | float | 2 | R
0x56A4 | 0x56A5 | 22180 | 22181 | MAG_2HR_HAR_I_106th_c_% | Aggr 2hr Phase C 106th Current Magnitude Harmonics | float | 2 | R
0x56A6 | 0x56A7 | 22182 | 22183 | MAG_2HR_HAR_I_106th_n_% | Aggr 2hr Phase N 106th Current Magnitude Harmonics | float | 2 | R
0x56A8 | 0x56A9 | 22184 | 22185 | MAG_2HR_HAR_V_107th_a_% | Aggr 2hr Phase A 107th Voltage Magnitude Harmonics | float | 2 | R
0x56AA | 0x56AB | 22186 | 22187 | MAG_2HR_HAR_V_107th_b_% | Aggr 2hr Phase B 107th Voltage Magnitude Harmonics | float | 2 | R
0x56AC | 0x56AD | 22188 | 22189 | MAG_2HR_HAR_V_107th_c_% | Aggr 2hr Phase C 107th Voltage Magnitude Harmonics | float | 2 | R
0x56AE | 0x56AF | 22190 | 22191 | MAG_2HR_HAR_I_107th_a_% | Aggr 2hr Phase A 107th Current Magnitude Harmonics | float | 2 | R
0x56B0 | 0x56B1 | 22192 | 22193 | MAG_2HR_HAR_I_107th_b_% | Aggr 2hr Phase B 107th Current Magnitude Harmonics | float | 2 | R
0x56B2 | 0x56B3 | 22194 | 22195 | MAG_2HR_HAR_I_107th_c_% | Aggr 2hr Phase C 107th Current Magnitude Harmonics | float | 2 | R
0x56B4 | 0x56B5 | 22196 | 22197 | MAG_2HR_HAR_I_107th_n_% | Aggr 2hr Phase N 107th Current Magnitude Harmonics | float | 2 | R
0x56B6 | 0x56B7 | 22198 | 22199 | MAG_2HR_HAR_V_108th_a_% | Aggr 2hr Phase A 108th Voltage Magnitude Harmonics | float | 2 | R
0x56B8 | 0x56B9 | 22200 | 22201 | MAG_2HR_HAR_V_108th_b_% | Aggr 2hr Phase B 108th Voltage Magnitude Harmonics | float | 2 | R
0x56BA | 0x56BB | 22202 | 22203 | MAG_2HR_HAR_V_108th_c_% | Aggr 2hr Phase C 108th Voltage Magnitude Harmonics | float | 2 | R
0x56BC | 0x56BD | 22204 | 22205 | MAG_2HR_HAR_I_108th_a_% | Aggr 2hr Phase A 108th Current Magnitude Harmonics | float | 2 | R
0x56BE | 0x56BF | 22206 | 22207 | MAG_2HR_HAR_I_108th_b_% | Aggr 2hr Phase B 108th Current Magnitude Harmonics | float | 2 | R
0x56C0 | 0x56C1 | 22208 | 22209 | MAG_2HR_HAR_I_108th_c_% | Aggr 2hr Phase C 108th Current Magnitude Harmonics | float | 2 | R
0x56C2 | 0x56C3 | 22210 | 22211 | MAG_2HR_HAR_I_108th_n_% | Aggr 2hr Phase N 108th Current Magnitude Harmonics | float | 2 | R
0x56C4 | 0x56C5 | 22212 | 22213 | MAG_2HR_HAR_V_109th_a_% | Aggr 2hr Phase A 109th Voltage Magnitude Harmonics | float | 2 | R
0x56C6 | 0x56C7 | 22214 | 22215 | MAG_2HR_HAR_V_109th_b_% | Aggr 2hr Phase B 109th Voltage Magnitude Harmonics | float | 2 | R
0x56C8 | 0x56C9 | 22216 | 22217 | MAG_2HR_HAR_V_109th_c_% | Aggr 2hr Phase C 109th Voltage Magnitude Harmonics | float | 2 | R
0x56CA | 0x56CB | 22218 | 22219 | MAG_2HR_HAR_I_109th_a_% | Aggr 2hr Phase A 109th Current Magnitude Harmonics | float | 2 | R
0x56CC | 0x56CD | 22220 | 22221 | MAG_2HR_HAR_I_109th_b_% | Aggr 2hr Phase B 109th Current Magnitude Harmonics | float | 2 | R
0x56CE | 0x56CF | 22222 | 22223 | MAG_2HR_HAR_I_109th_c_% | Aggr 2hr Phase C 109th Current Magnitude Harmonics | float | 2 | R
0x56D0 | 0x56D1 | 22224 | 22225 | MAG_2HR_HAR_I_109th_n_% | Aggr 2hr Phase N 109th Current Magnitude Harmonics | float | 2 | R
0x56D2 | 0x56D3 | 22226 | 22227 | MAG_2HR_HAR_V_110th_a_% | Aggr 2hr Phase A 110th Voltage Magnitude Harmonics | float | 2 | R
0x56D4 | 0x56D5 | 22228 | 22229 | MAG_2HR_HAR_V_110th_b_% | Aggr 2hr Phase B 110th Voltage Magnitude Harmonics | float | 2 | R
0x56D6 | 0x56D7 | 22230 | 22231 | MAG_2HR_HAR_V_110th_c_% | Aggr 2hr Phase C 110th Voltage Magnitude Harmonics | float | 2 | R
0x56D8 | 0x56D9 | 22232 | 22233 | MAG_2HR_HAR_I_110th_a_% | Aggr 2hr Phase A 110th Current Magnitude Harmonics | float | 2 | R
0x56DA | 0x56DB | 22234 | 22235 | MAG_2HR_HAR_I_110th_b_% | Aggr 2hr Phase B 110th Current Magnitude Harmonics | float | 2 | R
0x56DC | 0x56DD | 22236 | 22237 | MAG_2HR_HAR_I_110th_c_% | Aggr 2hr Phase C 110th Current Magnitude Harmonics | float | 2 | R
0x56DE | 0x56DF | 22238 | 22239 | MAG_2HR_HAR_I_110th_n_% | Aggr 2hr Phase N 110th Current Magnitude Harmonics | float | 2 | R
0x56E0 | 0x56E1 | 22240 | 22241 | MAG_2HR_HAR_V_111th_a_% | Aggr 2hr Phase A 111st Voltage Magnitude Harmonics | float | 2 | R
0x56E2 | 0x56E3 | 22242 | 22243 | MAG_2HR_HAR_V_111th_b_% | Aggr 2hr Phase B 111st Voltage Magnitude Harmonics | float | 2 | R
0x56E4 | 0x56E5 | 22244 | 22245 | MAG_2HR_HAR_V_111th_c_% | Aggr 2hr Phase C 111st Voltage Magnitude Harmonics | float | 2 | R
0x56E6 | 0x56E7 | 22246 | 22247 | MAG_2HR_HAR_I_111th_a_% | Aggr 2hr Phase A 111st Current Magnitude Harmonics | float | 2 | R
0x56E8 | 0x56E9 | 22248 | 22249 | MAG_2HR_HAR_I_111th_b_% | Aggr 2hr Phase B 111st Current Magnitude Harmonics | float | 2 | R
0x56EA | 0x56EB | 22250 | 22251 | MAG_2HR_HAR_I_111th_c_% | Aggr 2hr Phase C 111st Current Magnitude Harmonics | float | 2 | R
0x56EC | 0x56ED | 22252 | 22253 | MAG_2HR_HAR_I_111th_n_% | Aggr 2hr Phase N 111st Current Magnitude Harmonics | float | 2 | R
0x56EE | 0x56EF | 22254 | 22255 | MAG_2HR_HAR_V_112th_a_% | Aggr 2hr Phase A 112nd Voltage Magnitude Harmonics | float | 2 | R
0x56F0 | 0x56F1 | 22256 | 22257 | MAG_2HR_HAR_V_112th_b_% | Aggr 2hr Phase B 112nd Voltage Magnitude Harmonics | float | 2 | R
0x56F2 | 0x56F3 | 22258 | 22259 | MAG_2HR_HAR_V_112th_c_% | Aggr 2hr Phase C 112nd Voltage Magnitude Harmonics | float | 2 | R
0x56F4 | 0x56F5 | 22260 | 22261 | MAG_2HR_HAR_I_112th_a_% | Aggr 2hr Phase A 112nd Current Magnitude Harmonics | float | 2 | R
0x56F6 | 0x56F7 | 22262 | 22263 | MAG_2HR_HAR_I_112th_b_% | Aggr 2hr Phase B 112nd Current Magnitude Harmonics | float | 2 | R
0x56F8 | 0x56F9 | 22264 | 22265 | MAG_2HR_HAR_I_112th_c_% | Aggr 2hr Phase C 112nd Current Magnitude Harmonics | float | 2 | R
0x56FA | 0x56FB | 22266 | 22267 | MAG_2HR_HAR_I_112th_n_% | Aggr 2hr Phase N 112nd Current Magnitude Harmonics | float | 2 | R
0x56FC | 0x56FD | 22268 | 22269 | MAG_2HR_HAR_V_113th_a_% | Aggr 2hr Phase A 113rd Voltage Magnitude Harmonics | float | 2 | R
0x56FE | 0x56FF | 22270 | 22271 | MAG_2HR_HAR_V_113th_b_% | Aggr 2hr Phase B 113rd Voltage Magnitude Harmonics | float | 2 | R
0x5700 | 0x5701 | 22272 | 22273 | MAG_2HR_HAR_V_113th_c_% | Aggr 2hr Phase C 113rd Voltage Magnitude Harmonics | float | 2 | R
0x5702 | 0x5703 | 22274 | 22275 | MAG_2HR_HAR_I_113th_a_% | Aggr 2hr Phase A 113rd Current Magnitude Harmonics | float | 2 | R
0x5704 | 0x5705 | 22276 | 22277 | MAG_2HR_HAR_I_113th_b_% | Aggr 2hr Phase B 113rd Current Magnitude Harmonics | float | 2 | R
0x5706 | 0x5707 | 22278 | 22279 | MAG_2HR_HAR_I_113th_c_% | Aggr 2hr Phase C 113rd Current Magnitude Harmonics | float | 2 | R
0x5708 | 0x5709 | 22280 | 22281 | MAG_2HR_HAR_I_113th_n_% | Aggr 2hr Phase N 113rd Current Magnitude Harmonics | float | 2 | R
0x570A | 0x570B | 22282 | 22283 | MAG_2HR_HAR_V_114th_a_% | Aggr 2hr Phase A 114th Voltage Magnitude Harmonics | float | 2 | R
0x570C | 0x570D | 22284 | 22285 | MAG_2HR_HAR_V_114th_b_% | Aggr 2hr Phase B 114th Voltage Magnitude Harmonics | float | 2 | R
0x570E | 0x570F | 22286 | 22287 | MAG_2HR_HAR_V_114th_c_% | Aggr 2hr Phase C 114th Voltage Magnitude Harmonics | float | 2 | R
0x5710 | 0x5711 | 22288 | 22289 | MAG_2HR_HAR_I_114th_a_% | Aggr 2hr Phase A 114th Current Magnitude Harmonics | float | 2 | R
0x5712 | 0x5713 | 22290 | 22291 | MAG_2HR_HAR_I_114th_b_% | Aggr 2hr Phase B 114th Current Magnitude Harmonics | float | 2 | R
0x5714 | 0x5715 | 22292 | 22293 | MAG_2HR_HAR_I_114th_c_% | Aggr 2hr Phase C 114th Current Magnitude Harmonics | float | 2 | R
0x5716 | 0x5717 | 22294 | 22295 | MAG_2HR_HAR_I_114th_n_% | Aggr 2hr Phase N 114th Current Magnitude Harmonics | float | 2 | R
0x5718 | 0x5719 | 22296 | 22297 | MAG_2HR_HAR_V_115th_a_% | Aggr 2hr Phase A 115th Voltage Magnitude Harmonics | float | 2 | R
0x571A | 0x571B | 22298 | 22299 | MAG_2HR_HAR_V_115th_b_% | Aggr 2hr Phase B 115th Voltage Magnitude Harmonics | float | 2 | R
0x571C | 0x571D | 22300 | 22301 | MAG_2HR_HAR_V_115th_c_% | Aggr 2hr Phase C 115th Voltage Magnitude Harmonics | float | 2 | R
0x571E | 0x571F | 22302 | 22303 | MAG_2HR_HAR_I_115th_a_% | Aggr 2hr Phase A 115th Current Magnitude Harmonics | float | 2 | R
0x5720 | 0x5721 | 22304 | 22305 | MAG_2HR_HAR_I_115th_b_% | Aggr 2hr Phase B 115th Current Magnitude Harmonics | float | 2 | R
0x5722 | 0x5723 | 22306 | 22307 | MAG_2HR_HAR_I_115th_c_% | Aggr 2hr Phase C 115th Current Magnitude Harmonics | float | 2 | R
0x5724 | 0x5725 | 22308 | 22309 | MAG_2HR_HAR_I_115th_n_% | Aggr 2hr Phase N 115th Current Magnitude Harmonics | float | 2 | R
0x5726 | 0x5727 | 22310 | 22311 | MAG_2HR_HAR_V_116th_a_% | Aggr 2hr Phase A 116th Voltage Magnitude Harmonics | float | 2 | R
0x5728 | 0x5729 | 22312 | 22313 | MAG_2HR_HAR_V_116th_b_% | Aggr 2hr Phase B 116th Voltage Magnitude Harmonics | float | 2 | R
0x572A | 0x572B | 22314 | 22315 | MAG_2HR_HAR_V_116th_c_% | Aggr 2hr Phase C 116th Voltage Magnitude Harmonics | float | 2 | R
0x572C | 0x572D | 22316 | 22317 | MAG_2HR_HAR_I_116th_a_% | Aggr 2hr Phase A 116th Current Magnitude Harmonics | float | 2 | R
0x572E | 0x572F | 22318 | 22319 | MAG_2HR_HAR_I_116th_b_% | Aggr 2hr Phase B 116th Current Magnitude Harmonics | float | 2 | R
0x5730 | 0x5731 | 22320 | 22321 | MAG_2HR_HAR_I_116th_c_% | Aggr 2hr Phase C 116th Current Magnitude Harmonics | float | 2 | R
0x5732 | 0x5733 | 22322 | 22323 | MAG_2HR_HAR_I_116th_n_% | Aggr 2hr Phase N 116th Current Magnitude Harmonics | float | 2 | R
0x5734 | 0x5735 | 22324 | 22325 | MAG_2HR_HAR_V_117th_a_% | Aggr 2hr Phase A 117th Voltage Magnitude Harmonics | float | 2 | R
0x5736 | 0x5737 | 22326 | 22327 | MAG_2HR_HAR_V_117th_b_% | Aggr 2hr Phase B 117th Voltage Magnitude Harmonics | float | 2 | R
0x5738 | 0x5739 | 22328 | 22329 | MAG_2HR_HAR_V_117th_c_% | Aggr 2hr Phase C 117th Voltage Magnitude Harmonics | float | 2 | R
0x573A | 0x573B | 22330 | 22331 | MAG_2HR_HAR_I_117th_a_% | Aggr 2hr Phase A 117th Current Magnitude Harmonics | float | 2 | R
0x573C | 0x573D | 22332 | 22333 | MAG_2HR_HAR_I_117th_b_% | Aggr 2hr Phase B 117th Current Magnitude Harmonics | float | 2 | R
0x573E | 0x573F | 22334 | 22335 | MAG_2HR_HAR_I_117th_c_% | Aggr 2hr Phase C 117th Current Magnitude Harmonics | float | 2 | R
0x5740 | 0x5741 | 22336 | 22337 | MAG_2HR_HAR_I_117th_n_% | Aggr 2hr Phase N 117th Current Magnitude Harmonics | float | 2 | R
0x5742 | 0x5743 | 22338 | 22339 | MAG_2HR_HAR_V_118th_a_% | Aggr 2hr Phase A 118th Voltage Magnitude Harmonics | float | 2 | R
0x5744 | 0x5745 | 22340 | 22341 | MAG_2HR_HAR_V_118th_b_% | Aggr 2hr Phase B 118th Voltage Magnitude Harmonics | float | 2 | R
0x5746 | 0x5747 | 22342 | 22343 | MAG_2HR_HAR_V_118th_c_% | Aggr 2hr Phase C 118th Voltage Magnitude Harmonics | float | 2 | R
0x5748 | 0x5749 | 22344 | 22345 | MAG_2HR_HAR_I_118th_a_% | Aggr 2hr Phase A 118th Current Magnitude Harmonics | float | 2 | R
0x574A | 0x574B | 22346 | 22347 | MAG_2HR_HAR_I_118th_b_% | Aggr 2hr Phase B 118th Current Magnitude Harmonics | float | 2 | R
0x574C | 0x574D | 22348 | 22349 | MAG_2HR_HAR_I_118th_c_% | Aggr 2hr Phase C 118th Current Magnitude Harmonics | float | 2 | R
0x574E | 0x574F | 22350 | 22351 | MAG_2HR_HAR_I_118th_n_% | Aggr 2hr Phase N 118th Current Magnitude Harmonics | float | 2 | R
0x5750 | 0x5751 | 22352 | 22353 | MAG_2HR_HAR_V_119th_a_% | Aggr 2hr Phase A 119th Voltage Magnitude Harmonics | float | 2 | R
0x5752 | 0x5753 | 22354 | 22355 | MAG_2HR_HAR_V_119th_b_% | Aggr 2hr Phase B 119th Voltage Magnitude Harmonics | float | 2 | R
0x5754 | 0x5755 | 22356 | 22357 | MAG_2HR_HAR_V_119th_c_% | Aggr 2hr Phase C 119th Voltage Magnitude Harmonics | float | 2 | R
0x5756 | 0x5757 | 22358 | 22359 | MAG_2HR_HAR_I_119th_a_% | Aggr 2hr Phase A 119th Current Magnitude Harmonics | float | 2 | R
0x5758 | 0x5759 | 22360 | 22361 | MAG_2HR_HAR_I_119th_b_% | Aggr 2hr Phase B 119th Current Magnitude Harmonics | float | 2 | R
0x575A | 0x575B | 22362 | 22363 | MAG_2HR_HAR_I_119th_c_% | Aggr 2hr Phase C 119th Current Magnitude Harmonics | float | 2 | R
0x575C | 0x575D | 22364 | 22365 | MAG_2HR_HAR_I_119th_n_% | Aggr 2hr Phase N 119th Current Magnitude Harmonics | float | 2 | R
0x575E | 0x575F | 22366 | 22367 | MAG_2HR_HAR_V_120th_a_% | Aggr 2hr Phase A 120th Voltage Magnitude Harmonics | float | 2 | R
0x5760 | 0x5761 | 22368 | 22369 | MAG_2HR_HAR_V_120th_b_% | Aggr 2hr Phase B 120th Voltage Magnitude Harmonics | float | 2 | R
0x5762 | 0x5763 | 22370 | 22371 | MAG_2HR_HAR_V_120th_c_% | Aggr 2hr Phase C 120th Voltage Magnitude Harmonics | float | 2 | R
0x5764 | 0x5765 | 22372 | 22373 | MAG_2HR_HAR_I_120th_a_% | Aggr 2hr Phase A 120th Current Magnitude Harmonics | float | 2 | R
0x5766 | 0x5767 | 22374 | 22375 | MAG_2HR_HAR_I_120th_b_% | Aggr 2hr Phase B 120th Current Magnitude Harmonics | float | 2 | R
0x5768 | 0x5769 | 22376 | 22377 | MAG_2HR_HAR_I_120th_c_% | Aggr 2hr Phase C 120th Current Magnitude Harmonics | float | 2 | R
0x576A | 0x576B | 22378 | 22379 | MAG_2HR_HAR_I_120th_n_% | Aggr 2hr Phase N 120th Current Magnitude Harmonics | float | 2 | R
0x576C | 0x576D | 22380 | 22381 | MAG_2HR_HAR_V_121th_a_% | Aggr 2hr Phase A 121st Voltage Magnitude Harmonics | float | 2 | R
0x576E | 0x576F | 22382 | 22383 | MAG_2HR_HAR_V_121th_b_% | Aggr 2hr Phase B 121st Voltage Magnitude Harmonics | float | 2 | R
0x5770 | 0x5771 | 22384 | 22385 | MAG_2HR_HAR_V_121th_c_% | Aggr 2hr Phase C 121st Voltage Magnitude Harmonics | float | 2 | R
0x5772 | 0x5773 | 22386 | 22387 | MAG_2HR_HAR_I_121th_a_% | Aggr 2hr Phase A 121st Current Magnitude Harmonics | float | 2 | R
0x5774 | 0x5775 | 22388 | 22389 | MAG_2HR_HAR_I_121th_b_% | Aggr 2hr Phase B 121st Current Magnitude Harmonics | float | 2 | R
0x5776 | 0x5777 | 22390 | 22391 | MAG_2HR_HAR_I_121th_c_% | Aggr 2hr Phase C 121st Current Magnitude Harmonics | float | 2 | R
0x5778 | 0x5779 | 22392 | 22393 | MAG_2HR_HAR_I_121th_n_% | Aggr 2hr Phase N 121st Current Magnitude Harmonics | float | 2 | R
0x577A | 0x577B | 22394 | 22395 | MAG_2HR_HAR_V_122th_a_% | Aggr 2hr Phase A 122nd Voltage Magnitude Harmonics | float | 2 | R
0x577C | 0x577D | 22396 | 22397 | MAG_2HR_HAR_V_122th_b_% | Aggr 2hr Phase B 122nd Voltage Magnitude Harmonics | float | 2 | R
0x577E | 0x577F | 22398 | 22399 | MAG_2HR_HAR_V_122th_c_% | Aggr 2hr Phase C 122nd Voltage Magnitude Harmonics | float | 2 | R
0x5780 | 0x5781 | 22400 | 22401 | MAG_2HR_HAR_I_122th_a_% | Aggr 2hr Phase A 122nd Current Magnitude Harmonics | float | 2 | R
0x5782 | 0x5783 | 22402 | 22403 | MAG_2HR_HAR_I_122th_b_% | Aggr 2hr Phase B 122nd Current Magnitude Harmonics | float | 2 | R
0x5784 | 0x5785 | 22404 | 22405 | MAG_2HR_HAR_I_122th_c_% | Aggr 2hr Phase C 122nd Current Magnitude Harmonics | float | 2 | R
0x5786 | 0x5787 | 22406 | 22407 | MAG_2HR_HAR_I_122th_n_% | Aggr 2hr Phase N 122nd Current Magnitude Harmonics | float | 2 | R
0x5788 | 0x5789 | 22408 | 22409 | MAG_2HR_HAR_V_123th_a_% | Aggr 2hr Phase A 123rd Voltage Magnitude Harmonics | float | 2 | R
0x578A | 0x578B | 22410 | 22411 | MAG_2HR_HAR_V_123th_b_% | Aggr 2hr Phase B 123rd Voltage Magnitude Harmonics | float | 2 | R
0x578C | 0x578D | 22412 | 22413 | MAG_2HR_HAR_V_123th_c_% | Aggr 2hr Phase C 123rd Voltage Magnitude Harmonics | float | 2 | R
0x578E | 0x578F | 22414 | 22415 | MAG_2HR_HAR_I_123th_a_% | Aggr 2hr Phase A 123rd Current Magnitude Harmonics | float | 2 | R
0x5790 | 0x5791 | 22416 | 22417 | MAG_2HR_HAR_I_123th_b_% | Aggr 2hr Phase B 123rd Current Magnitude Harmonics | float | 2 | R
0x5792 | 0x5793 | 22418 | 22419 | MAG_2HR_HAR_I_123th_c_% | Aggr 2hr Phase C 123rd Current Magnitude Harmonics | float | 2 | R
0x5794 | 0x5795 | 22420 | 22421 | MAG_2HR_HAR_I_123th_n_% | Aggr 2hr Phase N 123rd Current Magnitude Harmonics | float | 2 | R
0x5796 | 0x5797 | 22422 | 22423 | MAG_2HR_HAR_V_124th_a_% | Aggr 2hr Phase A 124th Voltage Magnitude Harmonics | float | 2 | R
0x5798 | 0x5799 | 22424 | 22425 | MAG_2HR_HAR_V_124th_b_% | Aggr 2hr Phase B 124th Voltage Magnitude Harmonics | float | 2 | R
0x579A | 0x579B | 22426 | 22427 | MAG_2HR_HAR_V_124th_c_% | Aggr 2hr Phase C 124th Voltage Magnitude Harmonics | float | 2 | R
0x579C | 0x579D | 22428 | 22429 | MAG_2HR_HAR_I_124th_a_% | Aggr 2hr Phase A 124th Current Magnitude Harmonics | float | 2 | R
0x579E | 0x579F | 22430 | 22431 | MAG_2HR_HAR_I_124th_b_% | Aggr 2hr Phase B 124th Current Magnitude Harmonics | float | 2 | R
0x57A0 | 0x57A1 | 22432 | 22433 | MAG_2HR_HAR_I_124th_c_% | Aggr 2hr Phase C 124th Current Magnitude Harmonics | float | 2 | R
0x57A2 | 0x57A3 | 22434 | 22435 | MAG_2HR_HAR_I_124th_n_% | Aggr 2hr Phase N 124th Current Magnitude Harmonics | float | 2 | R
0x57A4 | 0x57A5 | 22436 | 22437 | MAG_2HR_HAR_V_125th_a_% | Aggr 2hr Phase A 125th Voltage Magnitude Harmonics | float | 2 | R
0x57A6 | 0x57A7 | 22438 | 22439 | MAG_2HR_HAR_V_125th_b_% | Aggr 2hr Phase B 125th Voltage Magnitude Harmonics | float | 2 | R
0x57A8 | 0x57A9 | 22440 | 22441 | MAG_2HR_HAR_V_125th_c_% | Aggr 2hr Phase C 125th Voltage Magnitude Harmonics | float | 2 | R
0x57AA | 0x57AB | 22442 | 22443 | MAG_2HR_HAR_I_125th_a_% | Aggr 2hr Phase A 125th Current Magnitude Harmonics | float | 2 | R
0x57AC | 0x57AD | 22444 | 22445 | MAG_2HR_HAR_I_125th_b_% | Aggr 2hr Phase B 125th Current Magnitude Harmonics | float | 2 | R
0x57AE | 0x57AF | 22446 | 22447 | MAG_2HR_HAR_I_125th_c_% | Aggr 2hr Phase C 125th Current Magnitude Harmonics | float | 2 | R
0x57B0 | 0x57B1 | 22448 | 22449 | MAG_2HR_HAR_I_125th_n_% | Aggr 2hr Phase N 125th Current Magnitude Harmonics | float | 2 | R
0x57B2 | 0x57B3 | 22450 | 22451 | MAG_2HR_HAR_V_126th_a_% | Aggr 2hr Phase A 126th Voltage Magnitude Harmonics | float | 2 | R
0x57B4 | 0x57B5 | 22452 | 22453 | MAG_2HR_HAR_V_126th_b_% | Aggr 2hr Phase B 126th Voltage Magnitude Harmonics | float | 2 | R
0x57B6 | 0x57B7 | 22454 | 22455 | MAG_2HR_HAR_V_126th_c_% | Aggr 2hr Phase C 126th Voltage Magnitude Harmonics | float | 2 | R
0x57B8 | 0x57B9 | 22456 | 22457 | MAG_2HR_HAR_I_126th_a_% | Aggr 2hr Phase A 126th Current Magnitude Harmonics | float | 2 | R
0x57BA | 0x57BB | 22458 | 22459 | MAG_2HR_HAR_I_126th_b_% | Aggr 2hr Phase B 126th Current Magnitude Harmonics | float | 2 | R
0x57BC | 0x57BD | 22460 | 22461 | MAG_2HR_HAR_I_126th_c_% | Aggr 2hr Phase C 126th Current Magnitude Harmonics | float | 2 | R
0x57BE | 0x57BF | 22462 | 22463 | MAG_2HR_HAR_I_126th_n_% | Aggr 2hr Phase N 126th Current Magnitude Harmonics | float | 2 | R
0x57C0 | 0x57C1 | 22464 | 22465 | MAG_2HR_HAR_V_127th_a_% | Aggr 2hr Phase A 127th Voltage Magnitude Harmonics | float | 2 | R
0x57C2 | 0x57C3 | 22466 | 22467 | MAG_2HR_HAR_V_127th_b_% | Aggr 2hr Phase B 127th Voltage Magnitude Harmonics | float | 2 | R
0x57C4 | 0x57C5 | 22468 | 22469 | MAG_2HR_HAR_V_127th_c_% | Aggr 2hr Phase C 127th Voltage Magnitude Harmonics | float | 2 | R
0x57C6 | 0x57C7 | 22470 | 22471 | MAG_2HR_HAR_I_127th_a_% | Aggr 2hr Phase A 127th Current Magnitude Harmonics | float | 2 | R
0x57C8 | 0x57C9 | 22472 | 22473 | MAG_2HR_HAR_I_127th_b_% | Aggr 2hr Phase B 127th Current Magnitude Harmonics | float | 2 | R
0x57CA | 0x57CB | 22474 | 22475 | MAG_2HR_HAR_I_127th_c_% | Aggr 2hr Phase C 127th Current Magnitude Harmonics | float | 2 | R
0x57CC | 0x57CD | 22476 | 22477 | MAG_2HR_HAR_I_127th_n_% | Aggr 2hr Phase N 127th Current Magnitude Harmonics | float | 2 | R
0x57CE | 0x57CF | 22478 | 22479 | ANG_2HR_HAR_V_1th_a | Aggr 2hr Phase A 1st Voltage Angle Harmonics | float | 2 | R
0x57D0 | 0x57D1 | 22480 | 22481 | ANG_2HR_HAR_V_1th_b | Aggr 2hr Phase B 1st Voltage Angle Harmonics | float | 2 | R
0x57D2 | 0x57D3 | 22482 | 22483 | ANG_2HR_HAR_V_1th_c | Aggr 2hr Phase C 1st Voltage Angle Harmonics | float | 2 | R
0x57D4 | 0x57D5 | 22484 | 22485 | ANG_2HR_HAR_I_1th_a | Aggr 2hr Phase A 1st Current Angle Harmonics | float | 2 | R
0x57D6 | 0x57D7 | 22486 | 22487 | ANG_2HR_HAR_I_1th_b | Aggr 2hr Phase B 1st Current Angle Harmonics | float | 2 | R
0x57D8 | 0x57D9 | 22488 | 22489 | ANG_2HR_HAR_I_1th_c | Aggr 2hr Phase C 1st Current Angle Harmonics | float | 2 | R
0x57DA | 0x57DB | 22490 | 22491 | ANG_2HR_HAR_I_1th_n | Aggr 2hr Phase N 1st Current Angle Harmonics | float | 2 | R
0x57DC | 0x57DD | 22492 | 22493 | ANG_2HR_HAR_V_2th_a | Aggr 2hr Phase A 2nd Voltage Angle Harmonics | float | 2 | R
0x57DE | 0x57DF | 22494 | 22495 | ANG_2HR_HAR_V_2th_b | Aggr 2hr Phase B 2nd Voltage Angle Harmonics | float | 2 | R
0x57E0 | 0x57E1 | 22496 | 22497 | ANG_2HR_HAR_V_2th_c | Aggr 2hr Phase C 2nd Voltage Angle Harmonics | float | 2 | R
0x57E2 | 0x57E3 | 22498 | 22499 | ANG_2HR_HAR_I_2th_a | Aggr 2hr Phase A 2nd Current Angle Harmonics | float | 2 | R
0x57E4 | 0x57E5 | 22500 | 22501 | ANG_2HR_HAR_I_2th_b | Aggr 2hr Phase B 2nd Current Angle Harmonics | float | 2 | R
0x57E6 | 0x57E7 | 22502 | 22503 | ANG_2HR_HAR_I_2th_c | Aggr 2hr Phase C 2nd Current Angle Harmonics | float | 2 | R
0x57E8 | 0x57E9 | 22504 | 22505 | ANG_2HR_HAR_I_2th_n | Aggr 2hr Phase N 2nd Current Angle Harmonics | float | 2 | R
0x57EA | 0x57EB | 22506 | 22507 | ANG_2HR_HAR_V_3th_a | Aggr 2hr Phase A 3rd Voltage Angle Harmonics | float | 2 | R
0x57EC | 0x57ED | 22508 | 22509 | ANG_2HR_HAR_V_3th_b | Aggr 2hr Phase B 3rd Voltage Angle Harmonics | float | 2 | R
0x57EE | 0x57EF | 22510 | 22511 | ANG_2HR_HAR_V_3th_c | Aggr 2hr Phase C 3rd Voltage Angle Harmonics | float | 2 | R
0x57F0 | 0x57F1 | 22512 | 22513 | ANG_2HR_HAR_I_3th_a | Aggr 2hr Phase A 3rd Current Angle Harmonics | float | 2 | R
0x57F2 | 0x57F3 | 22514 | 22515 | ANG_2HR_HAR_I_3th_b | Aggr 2hr Phase B 3rd Current Angle Harmonics | float | 2 | R
0x57F4 | 0x57F5 | 22516 | 22517 | ANG_2HR_HAR_I_3th_c | Aggr 2hr Phase C 3rd Current Angle Harmonics | float | 2 | R
0x57F6 | 0x57F7 | 22518 | 22519 | ANG_2HR_HAR_I_3th_n | Aggr 2hr Phase N 3rd Current Angle Harmonics | float | 2 | R
0x57F8 | 0x57F9 | 22520 | 22521 | ANG_2HR_HAR_V_4th_a | Aggr 2hr Phase A 4th Voltage Angle Harmonics | float | 2 | R
0x57FA | 0x57FB | 22522 | 22523 | ANG_2HR_HAR_V_4th_b | Aggr 2hr Phase B 4th Voltage Angle Harmonics | float | 2 | R
0x57FC | 0x57FD | 22524 | 22525 | ANG_2HR_HAR_V_4th_c | Aggr 2hr Phase C 4th Voltage Angle Harmonics | float | 2 | R
0x57FE | 0x57FF | 22526 | 22527 | ANG_2HR_HAR_I_4th_a | Aggr 2hr Phase A 4th Current Angle Harmonics | float | 2 | R
0x5800 | 0x5801 | 22528 | 22529 | ANG_2HR_HAR_I_4th_b | Aggr 2hr Phase B 4th Current Angle Harmonics | float | 2 | R
0x5802 | 0x5803 | 22530 | 22531 | ANG_2HR_HAR_I_4th_c | Aggr 2hr Phase C 4th Current Angle Harmonics | float | 2 | R
0x5804 | 0x5805 | 22532 | 22533 | ANG_2HR_HAR_I_4th_n | Aggr 2hr Phase N 4th Current Angle Harmonics | float | 2 | R
0x5806 | 0x5807 | 22534 | 22535 | ANG_2HR_HAR_V_5th_a | Aggr 2hr Phase A 5th Voltage Angle Harmonics | float | 2 | R
0x5808 | 0x5809 | 22536 | 22537 | ANG_2HR_HAR_V_5th_b | Aggr 2hr Phase B 5th Voltage Angle Harmonics | float | 2 | R
0x580A | 0x580B | 22538 | 22539 | ANG_2HR_HAR_V_5th_c | Aggr 2hr Phase C 5th Voltage Angle Harmonics | float | 2 | R
0x580C | 0x580D | 22540 | 22541 | ANG_2HR_HAR_I_5th_a | Aggr 2hr Phase A 5th Current Angle Harmonics | float | 2 | R
0x580E | 0x580F | 22542 | 22543 | ANG_2HR_HAR_I_5th_b | Aggr 2hr Phase B 5th Current Angle Harmonics | float | 2 | R
0x5810 | 0x5811 | 22544 | 22545 | ANG_2HR_HAR_I_5th_c | Aggr 2hr Phase C 5th Current Angle Harmonics | float | 2 | R
0x5812 | 0x5813 | 22546 | 22547 | ANG_2HR_HAR_I_5th_n | Aggr 2hr Phase N 5th Current Angle Harmonics | float | 2 | R
0x5814 | 0x5815 | 22548 | 22549 | ANG_2HR_HAR_V_6th_a | Aggr 2hr Phase A 6th Voltage Angle Harmonics | float | 2 | R
0x5816 | 0x5817 | 22550 | 22551 | ANG_2HR_HAR_V_6th_b | Aggr 2hr Phase B 6th Voltage Angle Harmonics | float | 2 | R
0x5818 | 0x5819 | 22552 | 22553 | ANG_2HR_HAR_V_6th_c | Aggr 2hr Phase C 6th Voltage Angle Harmonics | float | 2 | R
0x581A | 0x581B | 22554 | 22555 | ANG_2HR_HAR_I_6th_a | Aggr 2hr Phase A 6th Current Angle Harmonics | float | 2 | R
0x581C | 0x581D | 22556 | 22557 | ANG_2HR_HAR_I_6th_b | Aggr 2hr Phase B 6th Current Angle Harmonics | float | 2 | R
0x581E | 0x581F | 22558 | 22559 | ANG_2HR_HAR_I_6th_c | Aggr 2hr Phase C 6th Current Angle Harmonics | float | 2 | R
0x5820 | 0x5821 | 22560 | 22561 | ANG_2HR_HAR_I_6th_n | Aggr 2hr Phase N 6th Current Angle Harmonics | float | 2 | R
0x5822 | 0x5823 | 22562 | 22563 | ANG_2HR_HAR_V_7th_a | Aggr 2hr Phase A 7th Voltage Angle Harmonics | float | 2 | R
0x5824 | 0x5825 | 22564 | 22565 | ANG_2HR_HAR_V_7th_b | Aggr 2hr Phase B 7th Voltage Angle Harmonics | float | 2 | R
0x5826 | 0x5827 | 22566 | 22567 | ANG_2HR_HAR_V_7th_c | Aggr 2hr Phase C 7th Voltage Angle Harmonics | float | 2 | R
0x5828 | 0x5829 | 22568 | 22569 | ANG_2HR_HAR_I_7th_a | Aggr 2hr Phase A 7th Current Angle Harmonics | float | 2 | R
0x582A | 0x582B | 22570 | 22571 | ANG_2HR_HAR_I_7th_b | Aggr 2hr Phase B 7th Current Angle Harmonics | float | 2 | R
0x582C | 0x582D | 22572 | 22573 | ANG_2HR_HAR_I_7th_c | Aggr 2hr Phase C 7th Current Angle Harmonics | float | 2 | R
0x582E | 0x582F | 22574 | 22575 | ANG_2HR_HAR_I_7th_n | Aggr 2hr Phase N 7th Current Angle Harmonics | float | 2 | R
0x5830 | 0x5831 | 22576 | 22577 | ANG_2HR_HAR_V_8th_a | Aggr 2hr Phase A 8th Voltage Angle Harmonics | float | 2 | R
0x5832 | 0x5833 | 22578 | 22579 | ANG_2HR_HAR_V_8th_b | Aggr 2hr Phase B 8th Voltage Angle Harmonics | float | 2 | R
0x5834 | 0x5835 | 22580 | 22581 | ANG_2HR_HAR_V_8th_c | Aggr 2hr Phase C 8th Voltage Angle Harmonics | float | 2 | R
0x5836 | 0x5837 | 22582 | 22583 | ANG_2HR_HAR_I_8th_a | Aggr 2hr Phase A 8th Current Angle Harmonics | float | 2 | R
0x5838 | 0x5839 | 22584 | 22585 | ANG_2HR_HAR_I_8th_b | Aggr 2hr Phase B 8th Current Angle Harmonics | float | 2 | R
0x583A | 0x583B | 22586 | 22587 | ANG_2HR_HAR_I_8th_c | Aggr 2hr Phase C 8th Current Angle Harmonics | float | 2 | R
0x583C | 0x583D | 22588 | 22589 | ANG_2HR_HAR_I_8th_n | Aggr 2hr Phase N 8th Current Angle Harmonics | float | 2 | R
0x583E | 0x583F | 22590 | 22591 | ANG_2HR_HAR_V_9th_a | Aggr 2hr Phase A 9th Voltage Angle Harmonics | float | 2 | R
0x5840 | 0x5841 | 22592 | 22593 | ANG_2HR_HAR_V_9th_b | Aggr 2hr Phase B 9th Voltage Angle Harmonics | float | 2 | R
0x5842 | 0x5843 | 22594 | 22595 | ANG_2HR_HAR_V_9th_c | Aggr 2hr Phase C 9th Voltage Angle Harmonics | float | 2 | R
0x5844 | 0x5845 | 22596 | 22597 | ANG_2HR_HAR_I_9th_a | Aggr 2hr Phase A 9th Current Angle Harmonics | float | 2 | R
0x5846 | 0x5847 | 22598 | 22599 | ANG_2HR_HAR_I_9th_b | Aggr 2hr Phase B 9th Current Angle Harmonics | float | 2 | R
0x5848 | 0x5849 | 22600 | 22601 | ANG_2HR_HAR_I_9th_c | Aggr 2hr Phase C 9th Current Angle Harmonics | float | 2 | R
0x584A | 0x584B | 22602 | 22603 | ANG_2HR_HAR_I_9th_n | Aggr 2hr Phase N 9th Current Angle Harmonics | float | 2 | R
0x584C | 0x584D | 22604 | 22605 | ANG_2HR_HAR_V_10th_a | Aggr 2hr Phase A 10th Voltage Angle Harmonics | float | 2 | R
0x584E | 0x584F | 22606 | 22607 | ANG_2HR_HAR_V_10th_b | Aggr 2hr Phase B 10th Voltage Angle Harmonics | float | 2 | R
0x5850 | 0x5851 | 22608 | 22609 | ANG_2HR_HAR_V_10th_c | Aggr 2hr Phase C 10th Voltage Angle Harmonics | float | 2 | R
0x5852 | 0x5853 | 22610 | 22611 | ANG_2HR_HAR_I_10th_a | Aggr 2hr Phase A 10th Current Angle Harmonics | float | 2 | R
0x5854 | 0x5855 | 22612 | 22613 | ANG_2HR_HAR_I_10th_b | Aggr 2hr Phase B 10th Current Angle Harmonics | float | 2 | R
0x5856 | 0x5857 | 22614 | 22615 | ANG_2HR_HAR_I_10th_c | Aggr 2hr Phase C 10th Current Angle Harmonics | float | 2 | R
0x5858 | 0x5859 | 22616 | 22617 | ANG_2HR_HAR_I_10th_n | Aggr 2hr Phase N 10th Current Angle Harmonics | float | 2 | R
0x585A | 0x585B | 22618 | 22619 | ANG_2HR_HAR_V_11th_a | Aggr 2hr Phase A 11st Voltage Angle Harmonics | float | 2 | R
0x585C | 0x585D | 22620 | 22621 | ANG_2HR_HAR_V_11th_b | Aggr 2hr Phase B 11st Voltage Angle Harmonics | float | 2 | R
0x585E | 0x585F | 22622 | 22623 | ANG_2HR_HAR_V_11th_c | Aggr 2hr Phase C 11st Voltage Angle Harmonics | float | 2 | R
0x5860 | 0x5861 | 22624 | 22625 | ANG_2HR_HAR_I_11th_a | Aggr 2hr Phase A 11st Current Angle Harmonics | float | 2 | R
0x5862 | 0x5863 | 22626 | 22627 | ANG_2HR_HAR_I_11th_b | Aggr 2hr Phase B 11st Current Angle Harmonics | float | 2 | R
0x5864 | 0x5865 | 22628 | 22629 | ANG_2HR_HAR_I_11th_c | Aggr 2hr Phase C 11st Current Angle Harmonics | float | 2 | R
0x5866 | 0x5867 | 22630 | 22631 | ANG_2HR_HAR_I_11th_n | Aggr 2hr Phase N 11st Current Angle Harmonics | float | 2 | R
0x5868 | 0x5869 | 22632 | 22633 | ANG_2HR_HAR_V_12th_a | Aggr 2hr Phase A 12nd Voltage Angle Harmonics | float | 2 | R
0x586A | 0x586B | 22634 | 22635 | ANG_2HR_HAR_V_12th_b | Aggr 2hr Phase B 12nd Voltage Angle Harmonics | float | 2 | R
0x586C | 0x586D | 22636 | 22637 | ANG_2HR_HAR_V_12th_c | Aggr 2hr Phase C 12nd Voltage Angle Harmonics | float | 2 | R
0x586E | 0x586F | 22638 | 22639 | ANG_2HR_HAR_I_12th_a | Aggr 2hr Phase A 12nd Current Angle Harmonics | float | 2 | R
0x5870 | 0x5871 | 22640 | 22641 | ANG_2HR_HAR_I_12th_b | Aggr 2hr Phase B 12nd Current Angle Harmonics | float | 2 | R
0x5872 | 0x5873 | 22642 | 22643 | ANG_2HR_HAR_I_12th_c | Aggr 2hr Phase C 12nd Current Angle Harmonics | float | 2 | R
0x5874 | 0x5875 | 22644 | 22645 | ANG_2HR_HAR_I_12th_n | Aggr 2hr Phase N 12nd Current Angle Harmonics | float | 2 | R
0x5876 | 0x5877 | 22646 | 22647 | ANG_2HR_HAR_V_13th_a | Aggr 2hr Phase A 13rd Voltage Angle Harmonics | float | 2 | R
0x5878 | 0x5879 | 22648 | 22649 | ANG_2HR_HAR_V_13th_b | Aggr 2hr Phase B 13rd Voltage Angle Harmonics | float | 2 | R
0x587A | 0x587B | 22650 | 22651 | ANG_2HR_HAR_V_13th_c | Aggr 2hr Phase C 13rd Voltage Angle Harmonics | float | 2 | R
0x587C | 0x587D | 22652 | 22653 | ANG_2HR_HAR_I_13th_a | Aggr 2hr Phase A 13rd Current Angle Harmonics | float | 2 | R
0x587E | 0x587F | 22654 | 22655 | ANG_2HR_HAR_I_13th_b | Aggr 2hr Phase B 13rd Current Angle Harmonics | float | 2 | R
0x5880 | 0x5881 | 22656 | 22657 | ANG_2HR_HAR_I_13th_c | Aggr 2hr Phase C 13rd Current Angle Harmonics | float | 2 | R
0x5882 | 0x5883 | 22658 | 22659 | ANG_2HR_HAR_I_13th_n | Aggr 2hr Phase N 13rd Current Angle Harmonics | float | 2 | R
0x5884 | 0x5885 | 22660 | 22661 | ANG_2HR_HAR_V_14th_a | Aggr 2hr Phase A 14th Voltage Angle Harmonics | float | 2 | R
0x5886 | 0x5887 | 22662 | 22663 | ANG_2HR_HAR_V_14th_b | Aggr 2hr Phase B 14th Voltage Angle Harmonics | float | 2 | R
0x5888 | 0x5889 | 22664 | 22665 | ANG_2HR_HAR_V_14th_c | Aggr 2hr Phase C 14th Voltage Angle Harmonics | float | 2 | R
0x588A | 0x588B | 22666 | 22667 | ANG_2HR_HAR_I_14th_a | Aggr 2hr Phase A 14th Current Angle Harmonics | float | 2 | R
0x588C | 0x588D | 22668 | 22669 | ANG_2HR_HAR_I_14th_b | Aggr 2hr Phase B 14th Current Angle Harmonics | float | 2 | R
0x588E | 0x588F | 22670 | 22671 | ANG_2HR_HAR_I_14th_c | Aggr 2hr Phase C 14th Current Angle Harmonics | float | 2 | R
0x5890 | 0x5891 | 22672 | 22673 | ANG_2HR_HAR_I_14th_n | Aggr 2hr Phase N 14th Current Angle Harmonics | float | 2 | R
0x5892 | 0x5893 | 22674 | 22675 | ANG_2HR_HAR_V_15th_a | Aggr 2hr Phase A 15th Voltage Angle Harmonics | float | 2 | R
0x5894 | 0x5895 | 22676 | 22677 | ANG_2HR_HAR_V_15th_b | Aggr 2hr Phase B 15th Voltage Angle Harmonics | float | 2 | R
0x5896 | 0x5897 | 22678 | 22679 | ANG_2HR_HAR_V_15th_c | Aggr 2hr Phase C 15th Voltage Angle Harmonics | float | 2 | R
0x5898 | 0x5899 | 22680 | 22681 | ANG_2HR_HAR_I_15th_a | Aggr 2hr Phase A 15th Current Angle Harmonics | float | 2 | R
0x589A | 0x589B | 22682 | 22683 | ANG_2HR_HAR_I_15th_b | Aggr 2hr Phase B 15th Current Angle Harmonics | float | 2 | R
0x589C | 0x589D | 22684 | 22685 | ANG_2HR_HAR_I_15th_c | Aggr 2hr Phase C 15th Current Angle Harmonics | float | 2 | R
0x589E | 0x589F | 22686 | 22687 | ANG_2HR_HAR_I_15th_n | Aggr 2hr Phase N 15th Current Angle Harmonics | float | 2 | R
0x58A0 | 0x58A1 | 22688 | 22689 | ANG_2HR_HAR_V_16th_a | Aggr 2hr Phase A 16th Voltage Angle Harmonics | float | 2 | R
0x58A2 | 0x58A3 | 22690 | 22691 | ANG_2HR_HAR_V_16th_b | Aggr 2hr Phase B 16th Voltage Angle Harmonics | float | 2 | R
0x58A4 | 0x58A5 | 22692 | 22693 | ANG_2HR_HAR_V_16th_c | Aggr 2hr Phase C 16th Voltage Angle Harmonics | float | 2 | R
0x58A6 | 0x58A7 | 22694 | 22695 | ANG_2HR_HAR_I_16th_a | Aggr 2hr Phase A 16th Current Angle Harmonics | float | 2 | R
0x58A8 | 0x58A9 | 22696 | 22697 | ANG_2HR_HAR_I_16th_b | Aggr 2hr Phase B 16th Current Angle Harmonics | float | 2 | R
0x58AA | 0x58AB | 22698 | 22699 | ANG_2HR_HAR_I_16th_c | Aggr 2hr Phase C 16th Current Angle Harmonics | float | 2 | R
0x58AC | 0x58AD | 22700 | 22701 | ANG_2HR_HAR_I_16th_n | Aggr 2hr Phase N 16th Current Angle Harmonics | float | 2 | R
0x58AE | 0x58AF | 22702 | 22703 | ANG_2HR_HAR_V_17th_a | Aggr 2hr Phase A 17th Voltage Angle Harmonics | float | 2 | R
0x58B0 | 0x58B1 | 22704 | 22705 | ANG_2HR_HAR_V_17th_b | Aggr 2hr Phase B 17th Voltage Angle Harmonics | float | 2 | R
0x58B2 | 0x58B3 | 22706 | 22707 | ANG_2HR_HAR_V_17th_c | Aggr 2hr Phase C 17th Voltage Angle Harmonics | float | 2 | R
0x58B4 | 0x58B5 | 22708 | 22709 | ANG_2HR_HAR_I_17th_a | Aggr 2hr Phase A 17th Current Angle Harmonics | float | 2 | R
0x58B6 | 0x58B7 | 22710 | 22711 | ANG_2HR_HAR_I_17th_b | Aggr 2hr Phase B 17th Current Angle Harmonics | float | 2 | R
0x58B8 | 0x58B9 | 22712 | 22713 | ANG_2HR_HAR_I_17th_c | Aggr 2hr Phase C 17th Current Angle Harmonics | float | 2 | R
0x58BA | 0x58BB | 22714 | 22715 | ANG_2HR_HAR_I_17th_n | Aggr 2hr Phase N 17th Current Angle Harmonics | float | 2 | R
0x58BC | 0x58BD | 22716 | 22717 | ANG_2HR_HAR_V_18th_a | Aggr 2hr Phase A 18th Voltage Angle Harmonics | float | 2 | R
0x58BE | 0x58BF | 22718 | 22719 | ANG_2HR_HAR_V_18th_b | Aggr 2hr Phase B 18th Voltage Angle Harmonics | float | 2 | R
0x58C0 | 0x58C1 | 22720 | 22721 | ANG_2HR_HAR_V_18th_c | Aggr 2hr Phase C 18th Voltage Angle Harmonics | float | 2 | R
0x58C2 | 0x58C3 | 22722 | 22723 | ANG_2HR_HAR_I_18th_a | Aggr 2hr Phase A 18th Current Angle Harmonics | float | 2 | R
0x58C4 | 0x58C5 | 22724 | 22725 | ANG_2HR_HAR_I_18th_b | Aggr 2hr Phase B 18th Current Angle Harmonics | float | 2 | R
0x58C6 | 0x58C7 | 22726 | 22727 | ANG_2HR_HAR_I_18th_c | Aggr 2hr Phase C 18th Current Angle Harmonics | float | 2 | R
0x58C8 | 0x58C9 | 22728 | 22729 | ANG_2HR_HAR_I_18th_n | Aggr 2hr Phase N 18th Current Angle Harmonics | float | 2 | R
0x58CA | 0x58CB | 22730 | 22731 | ANG_2HR_HAR_V_19th_a | Aggr 2hr Phase A 19th Voltage Angle Harmonics | float | 2 | R
0x58CC | 0x58CD | 22732 | 22733 | ANG_2HR_HAR_V_19th_b | Aggr 2hr Phase B 19th Voltage Angle Harmonics | float | 2 | R
0x58CE | 0x58CF | 22734 | 22735 | ANG_2HR_HAR_V_19th_c | Aggr 2hr Phase C 19th Voltage Angle Harmonics | float | 2 | R
0x58D0 | 0x58D1 | 22736 | 22737 | ANG_2HR_HAR_I_19th_a | Aggr 2hr Phase A 19th Current Angle Harmonics | float | 2 | R
0x58D2 | 0x58D3 | 22738 | 22739 | ANG_2HR_HAR_I_19th_b | Aggr 2hr Phase B 19th Current Angle Harmonics | float | 2 | R
0x58D4 | 0x58D5 | 22740 | 22741 | ANG_2HR_HAR_I_19th_c | Aggr 2hr Phase C 19th Current Angle Harmonics | float | 2 | R
0x58D6 | 0x58D7 | 22742 | 22743 | ANG_2HR_HAR_I_19th_n | Aggr 2hr Phase N 19th Current Angle Harmonics | float | 2 | R
0x58D8 | 0x58D9 | 22744 | 22745 | ANG_2HR_HAR_V_20th_a | Aggr 2hr Phase A 20th Voltage Angle Harmonics | float | 2 | R
0x58DA | 0x58DB | 22746 | 22747 | ANG_2HR_HAR_V_20th_b | Aggr 2hr Phase B 20th Voltage Angle Harmonics | float | 2 | R
0x58DC | 0x58DD | 22748 | 22749 | ANG_2HR_HAR_V_20th_c | Aggr 2hr Phase C 20th Voltage Angle Harmonics | float | 2 | R
0x58DE | 0x58DF | 22750 | 22751 | ANG_2HR_HAR_I_20th_a | Aggr 2hr Phase A 20th Current Angle Harmonics | float | 2 | R
0x58E0 | 0x58E1 | 22752 | 22753 | ANG_2HR_HAR_I_20th_b | Aggr 2hr Phase B 20th Current Angle Harmonics | float | 2 | R
0x58E2 | 0x58E3 | 22754 | 22755 | ANG_2HR_HAR_I_20th_c | Aggr 2hr Phase C 20th Current Angle Harmonics | float | 2 | R
0x58E4 | 0x58E5 | 22756 | 22757 | ANG_2HR_HAR_I_20th_n | Aggr 2hr Phase N 20th Current Angle Harmonics | float | 2 | R
0x58E6 | 0x58E7 | 22758 | 22759 | ANG_2HR_HAR_V_21th_a | Aggr 2hr Phase A 21st Voltage Angle Harmonics | float | 2 | R
0x58E8 | 0x58E9 | 22760 | 22761 | ANG_2HR_HAR_V_21th_b | Aggr 2hr Phase B 21st Voltage Angle Harmonics | float | 2 | R
0x58EA | 0x58EB | 22762 | 22763 | ANG_2HR_HAR_V_21th_c | Aggr 2hr Phase C 21st Voltage Angle Harmonics | float | 2 | R
0x58EC | 0x58ED | 22764 | 22765 | ANG_2HR_HAR_I_21th_a | Aggr 2hr Phase A 21st Current Angle Harmonics | float | 2 | R
0x58EE | 0x58EF | 22766 | 22767 | ANG_2HR_HAR_I_21th_b | Aggr 2hr Phase B 21st Current Angle Harmonics | float | 2 | R
0x58F0 | 0x58F1 | 22768 | 22769 | ANG_2HR_HAR_I_21th_c | Aggr 2hr Phase C 21st Current Angle Harmonics | float | 2 | R
0x58F2 | 0x58F3 | 22770 | 22771 | ANG_2HR_HAR_I_21th_n | Aggr 2hr Phase N 21st Current Angle Harmonics | float | 2 | R
0x58F4 | 0x58F5 | 22772 | 22773 | ANG_2HR_HAR_V_22th_a | Aggr 2hr Phase A 22nd Voltage Angle Harmonics | float | 2 | R
0x58F6 | 0x58F7 | 22774 | 22775 | ANG_2HR_HAR_V_22th_b | Aggr 2hr Phase B 22nd Voltage Angle Harmonics | float | 2 | R
0x58F8 | 0x58F9 | 22776 | 22777 | ANG_2HR_HAR_V_22th_c | Aggr 2hr Phase C 22nd Voltage Angle Harmonics | float | 2 | R
0x58FA | 0x58FB | 22778 | 22779 | ANG_2HR_HAR_I_22th_a | Aggr 2hr Phase A 22nd Current Angle Harmonics | float | 2 | R
0x58FC | 0x58FD | 22780 | 22781 | ANG_2HR_HAR_I_22th_b | Aggr 2hr Phase B 22nd Current Angle Harmonics | float | 2 | R
0x58FE | 0x58FF | 22782 | 22783 | ANG_2HR_HAR_I_22th_c | Aggr 2hr Phase C 22nd Current Angle Harmonics | float | 2 | R
0x5900 | 0x5901 | 22784 | 22785 | ANG_2HR_HAR_I_22th_n | Aggr 2hr Phase N 22nd Current Angle Harmonics | float | 2 | R
0x5902 | 0x5903 | 22786 | 22787 | ANG_2HR_HAR_V_23th_a | Aggr 2hr Phase A 23rd Voltage Angle Harmonics | float | 2 | R
0x5904 | 0x5905 | 22788 | 22789 | ANG_2HR_HAR_V_23th_b | Aggr 2hr Phase B 23rd Voltage Angle Harmonics | float | 2 | R
0x5906 | 0x5907 | 22790 | 22791 | ANG_2HR_HAR_V_23th_c | Aggr 2hr Phase C 23rd Voltage Angle Harmonics | float | 2 | R
0x5908 | 0x5909 | 22792 | 22793 | ANG_2HR_HAR_I_23th_a | Aggr 2hr Phase A 23rd Current Angle Harmonics | float | 2 | R
0x590A | 0x590B | 22794 | 22795 | ANG_2HR_HAR_I_23th_b | Aggr 2hr Phase B 23rd Current Angle Harmonics | float | 2 | R
0x590C | 0x590D | 22796 | 22797 | ANG_2HR_HAR_I_23th_c | Aggr 2hr Phase C 23rd Current Angle Harmonics | float | 2 | R
0x590E | 0x590F | 22798 | 22799 | ANG_2HR_HAR_I_23th_n | Aggr 2hr Phase N 23rd Current Angle Harmonics | float | 2 | R
0x5910 | 0x5911 | 22800 | 22801 | ANG_2HR_HAR_V_24th_a | Aggr 2hr Phase A 24th Voltage Angle Harmonics | float | 2 | R
0x5912 | 0x5913 | 22802 | 22803 | ANG_2HR_HAR_V_24th_b | Aggr 2hr Phase B 24th Voltage Angle Harmonics | float | 2 | R
0x5914 | 0x5915 | 22804 | 22805 | ANG_2HR_HAR_V_24th_c | Aggr 2hr Phase C 24th Voltage Angle Harmonics | float | 2 | R
0x5916 | 0x5917 | 22806 | 22807 | ANG_2HR_HAR_I_24th_a | Aggr 2hr Phase A 24th Current Angle Harmonics | float | 2 | R
0x5918 | 0x5919 | 22808 | 22809 | ANG_2HR_HAR_I_24th_b | Aggr 2hr Phase B 24th Current Angle Harmonics | float | 2 | R
0x591A | 0x591B | 22810 | 22811 | ANG_2HR_HAR_I_24th_c | Aggr 2hr Phase C 24th Current Angle Harmonics | float | 2 | R
0x591C | 0x591D | 22812 | 22813 | ANG_2HR_HAR_I_24th_n | Aggr 2hr Phase N 24th Current Angle Harmonics | float | 2 | R
0x591E | 0x591F | 22814 | 22815 | ANG_2HR_HAR_V_25th_a | Aggr 2hr Phase A 25th Voltage Angle Harmonics | float | 2 | R
0x5920 | 0x5921 | 22816 | 22817 | ANG_2HR_HAR_V_25th_b | Aggr 2hr Phase B 25th Voltage Angle Harmonics | float | 2 | R
0x5922 | 0x5923 | 22818 | 22819 | ANG_2HR_HAR_V_25th_c | Aggr 2hr Phase C 25th Voltage Angle Harmonics | float | 2 | R
0x5924 | 0x5925 | 22820 | 22821 | ANG_2HR_HAR_I_25th_a | Aggr 2hr Phase A 25th Current Angle Harmonics | float | 2 | R
0x5926 | 0x5927 | 22822 | 22823 | ANG_2HR_HAR_I_25th_b | Aggr 2hr Phase B 25th Current Angle Harmonics | float | 2 | R
0x5928 | 0x5929 | 22824 | 22825 | ANG_2HR_HAR_I_25th_c | Aggr 2hr Phase C 25th Current Angle Harmonics | float | 2 | R
0x592A | 0x592B | 22826 | 22827 | ANG_2HR_HAR_I_25th_n | Aggr 2hr Phase N 25th Current Angle Harmonics | float | 2 | R
0x592C | 0x592D | 22828 | 22829 | ANG_2HR_HAR_V_26th_a | Aggr 2hr Phase A 26th Voltage Angle Harmonics | float | 2 | R
0x592E | 0x592F | 22830 | 22831 | ANG_2HR_HAR_V_26th_b | Aggr 2hr Phase B 26th Voltage Angle Harmonics | float | 2 | R
0x5930 | 0x5931 | 22832 | 22833 | ANG_2HR_HAR_V_26th_c | Aggr 2hr Phase C 26th Voltage Angle Harmonics | float | 2 | R
0x5932 | 0x5933 | 22834 | 22835 | ANG_2HR_HAR_I_26th_a | Aggr 2hr Phase A 26th Current Angle Harmonics | float | 2 | R
0x5934 | 0x5935 | 22836 | 22837 | ANG_2HR_HAR_I_26th_b | Aggr 2hr Phase B 26th Current Angle Harmonics | float | 2 | R
0x5936 | 0x5937 | 22838 | 22839 | ANG_2HR_HAR_I_26th_c | Aggr 2hr Phase C 26th Current Angle Harmonics | float | 2 | R
0x5938 | 0x5939 | 22840 | 22841 | ANG_2HR_HAR_I_26th_n | Aggr 2hr Phase N 26th Current Angle Harmonics | float | 2 | R
0x593A | 0x593B | 22842 | 22843 | ANG_2HR_HAR_V_27th_a | Aggr 2hr Phase A 27th Voltage Angle Harmonics | float | 2 | R
0x593C | 0x593D | 22844 | 22845 | ANG_2HR_HAR_V_27th_b | Aggr 2hr Phase B 27th Voltage Angle Harmonics | float | 2 | R
0x593E | 0x593F | 22846 | 22847 | ANG_2HR_HAR_V_27th_c | Aggr 2hr Phase C 27th Voltage Angle Harmonics | float | 2 | R
0x5940 | 0x5941 | 22848 | 22849 | ANG_2HR_HAR_I_27th_a | Aggr 2hr Phase A 27th Current Angle Harmonics | float | 2 | R
0x5942 | 0x5943 | 22850 | 22851 | ANG_2HR_HAR_I_27th_b | Aggr 2hr Phase B 27th Current Angle Harmonics | float | 2 | R
0x5944 | 0x5945 | 22852 | 22853 | ANG_2HR_HAR_I_27th_c | Aggr 2hr Phase C 27th Current Angle Harmonics | float | 2 | R
0x5946 | 0x5947 | 22854 | 22855 | ANG_2HR_HAR_I_27th_n | Aggr 2hr Phase N 27th Current Angle Harmonics | float | 2 | R
0x5948 | 0x5949 | 22856 | 22857 | ANG_2HR_HAR_V_28th_a | Aggr 2hr Phase A 28th Voltage Angle Harmonics | float | 2 | R
0x594A | 0x594B | 22858 | 22859 | ANG_2HR_HAR_V_28th_b | Aggr 2hr Phase B 28th Voltage Angle Harmonics | float | 2 | R
0x594C | 0x594D | 22860 | 22861 | ANG_2HR_HAR_V_28th_c | Aggr 2hr Phase C 28th Voltage Angle Harmonics | float | 2 | R
0x594E | 0x594F | 22862 | 22863 | ANG_2HR_HAR_I_28th_a | Aggr 2hr Phase A 28th Current Angle Harmonics | float | 2 | R
0x5950 | 0x5951 | 22864 | 22865 | ANG_2HR_HAR_I_28th_b | Aggr 2hr Phase B 28th Current Angle Harmonics | float | 2 | R
0x5952 | 0x5953 | 22866 | 22867 | ANG_2HR_HAR_I_28th_c | Aggr 2hr Phase C 28th Current Angle Harmonics | float | 2 | R
0x5954 | 0x5955 | 22868 | 22869 | ANG_2HR_HAR_I_28th_n | Aggr 2hr Phase N 28th Current Angle Harmonics | float | 2 | R
0x5956 | 0x5957 | 22870 | 22871 | ANG_2HR_HAR_V_29th_a | Aggr 2hr Phase A 29th Voltage Angle Harmonics | float | 2 | R
0x5958 | 0x5959 | 22872 | 22873 | ANG_2HR_HAR_V_29th_b | Aggr 2hr Phase B 29th Voltage Angle Harmonics | float | 2 | R
0x595A | 0x595B | 22874 | 22875 | ANG_2HR_HAR_V_29th_c | Aggr 2hr Phase C 29th Voltage Angle Harmonics | float | 2 | R
0x595C | 0x595D | 22876 | 22877 | ANG_2HR_HAR_I_29th_a | Aggr 2hr Phase A 29th Current Angle Harmonics | float | 2 | R
0x595E | 0x595F | 22878 | 22879 | ANG_2HR_HAR_I_29th_b | Aggr 2hr Phase B 29th Current Angle Harmonics | float | 2 | R
0x5960 | 0x5961 | 22880 | 22881 | ANG_2HR_HAR_I_29th_c | Aggr 2hr Phase C 29th Current Angle Harmonics | float | 2 | R
0x5962 | 0x5963 | 22882 | 22883 | ANG_2HR_HAR_I_29th_n | Aggr 2hr Phase N 29th Current Angle Harmonics | float | 2 | R
0x5964 | 0x5965 | 22884 | 22885 | ANG_2HR_HAR_V_30th_a | Aggr 2hr Phase A 30th Voltage Angle Harmonics | float | 2 | R
0x5966 | 0x5967 | 22886 | 22887 | ANG_2HR_HAR_V_30th_b | Aggr 2hr Phase B 30th Voltage Angle Harmonics | float | 2 | R
0x5968 | 0x5969 | 22888 | 22889 | ANG_2HR_HAR_V_30th_c | Aggr 2hr Phase C 30th Voltage Angle Harmonics | float | 2 | R
0x596A | 0x596B | 22890 | 22891 | ANG_2HR_HAR_I_30th_a | Aggr 2hr Phase A 30th Current Angle Harmonics | float | 2 | R
0x596C | 0x596D | 22892 | 22893 | ANG_2HR_HAR_I_30th_b | Aggr 2hr Phase B 30th Current Angle Harmonics | float | 2 | R
0x596E | 0x596F | 22894 | 22895 | ANG_2HR_HAR_I_30th_c | Aggr 2hr Phase C 30th Current Angle Harmonics | float | 2 | R
0x5970 | 0x5971 | 22896 | 22897 | ANG_2HR_HAR_I_30th_n | Aggr 2hr Phase N 30th Current Angle Harmonics | float | 2 | R
0x5972 | 0x5973 | 22898 | 22899 | ANG_2HR_HAR_V_31th_a | Aggr 2hr Phase A 31st Voltage Angle Harmonics | float | 2 | R
0x5974 | 0x5975 | 22900 | 22901 | ANG_2HR_HAR_V_31th_b | Aggr 2hr Phase B 31st Voltage Angle Harmonics | float | 2 | R
0x5976 | 0x5977 | 22902 | 22903 | ANG_2HR_HAR_V_31th_c | Aggr 2hr Phase C 31st Voltage Angle Harmonics | float | 2 | R
0x5978 | 0x5979 | 22904 | 22905 | ANG_2HR_HAR_I_31th_a | Aggr 2hr Phase A 31st Current Angle Harmonics | float | 2 | R
0x597A | 0x597B | 22906 | 22907 | ANG_2HR_HAR_I_31th_b | Aggr 2hr Phase B 31st Current Angle Harmonics | float | 2 | R
0x597C | 0x597D | 22908 | 22909 | ANG_2HR_HAR_I_31th_c | Aggr 2hr Phase C 31st Current Angle Harmonics | float | 2 | R
0x597E | 0x597F | 22910 | 22911 | ANG_2HR_HAR_I_31th_n | Aggr 2hr Phase N 31st Current Angle Harmonics | float | 2 | R
0x5980 | 0x5981 | 22912 | 22913 | ANG_2HR_HAR_V_32th_a | Aggr 2hr Phase A 32nd Voltage Angle Harmonics | float | 2 | R
0x5982 | 0x5983 | 22914 | 22915 | ANG_2HR_HAR_V_32th_b | Aggr 2hr Phase B 32nd Voltage Angle Harmonics | float | 2 | R
0x5984 | 0x5985 | 22916 | 22917 | ANG_2HR_HAR_V_32th_c | Aggr 2hr Phase C 32nd Voltage Angle Harmonics | float | 2 | R
0x5986 | 0x5987 | 22918 | 22919 | ANG_2HR_HAR_I_32th_a | Aggr 2hr Phase A 32nd Current Angle Harmonics | float | 2 | R
0x5988 | 0x5989 | 22920 | 22921 | ANG_2HR_HAR_I_32th_b | Aggr 2hr Phase B 32nd Current Angle Harmonics | float | 2 | R
0x598A | 0x598B | 22922 | 22923 | ANG_2HR_HAR_I_32th_c | Aggr 2hr Phase C 32nd Current Angle Harmonics | float | 2 | R
0x598C | 0x598D | 22924 | 22925 | ANG_2HR_HAR_I_32th_n | Aggr 2hr Phase N 32nd Current Angle Harmonics | float | 2 | R
0x598E | 0x598F | 22926 | 22927 | ANG_2HR_HAR_V_33th_a | Aggr 2hr Phase A 33rd Voltage Angle Harmonics | float | 2 | R
0x5990 | 0x5991 | 22928 | 22929 | ANG_2HR_HAR_V_33th_b | Aggr 2hr Phase B 33rd Voltage Angle Harmonics | float | 2 | R
0x5992 | 0x5993 | 22930 | 22931 | ANG_2HR_HAR_V_33th_c | Aggr 2hr Phase C 33rd Voltage Angle Harmonics | float | 2 | R
0x5994 | 0x5995 | 22932 | 22933 | ANG_2HR_HAR_I_33th_a | Aggr 2hr Phase A 33rd Current Angle Harmonics | float | 2 | R
0x5996 | 0x5997 | 22934 | 22935 | ANG_2HR_HAR_I_33th_b | Aggr 2hr Phase B 33rd Current Angle Harmonics | float | 2 | R
0x5998 | 0x5999 | 22936 | 22937 | ANG_2HR_HAR_I_33th_c | Aggr 2hr Phase C 33rd Current Angle Harmonics | float | 2 | R
0x599A | 0x599B | 22938 | 22939 | ANG_2HR_HAR_I_33th_n | Aggr 2hr Phase N 33rd Current Angle Harmonics | float | 2 | R
0x599C | 0x599D | 22940 | 22941 | ANG_2HR_HAR_V_34th_a | Aggr 2hr Phase A 34th Voltage Angle Harmonics | float | 2 | R
0x599E | 0x599F | 22942 | 22943 | ANG_2HR_HAR_V_34th_b | Aggr 2hr Phase B 34th Voltage Angle Harmonics | float | 2 | R
0x59A0 | 0x59A1 | 22944 | 22945 | ANG_2HR_HAR_V_34th_c | Aggr 2hr Phase C 34th Voltage Angle Harmonics | float | 2 | R
0x59A2 | 0x59A3 | 22946 | 22947 | ANG_2HR_HAR_I_34th_a | Aggr 2hr Phase A 34th Current Angle Harmonics | float | 2 | R
0x59A4 | 0x59A5 | 22948 | 22949 | ANG_2HR_HAR_I_34th_b | Aggr 2hr Phase B 34th Current Angle Harmonics | float | 2 | R
0x59A6 | 0x59A7 | 22950 | 22951 | ANG_2HR_HAR_I_34th_c | Aggr 2hr Phase C 34th Current Angle Harmonics | float | 2 | R
0x59A8 | 0x59A9 | 22952 | 22953 | ANG_2HR_HAR_I_34th_n | Aggr 2hr Phase N 34th Current Angle Harmonics | float | 2 | R
0x59AA | 0x59AB | 22954 | 22955 | ANG_2HR_HAR_V_35th_a | Aggr 2hr Phase A 35th Voltage Angle Harmonics | float | 2 | R
0x59AC | 0x59AD | 22956 | 22957 | ANG_2HR_HAR_V_35th_b | Aggr 2hr Phase B 35th Voltage Angle Harmonics | float | 2 | R
0x59AE | 0x59AF | 22958 | 22959 | ANG_2HR_HAR_V_35th_c | Aggr 2hr Phase C 35th Voltage Angle Harmonics | float | 2 | R
0x59B0 | 0x59B1 | 22960 | 22961 | ANG_2HR_HAR_I_35th_a | Aggr 2hr Phase A 35th Current Angle Harmonics | float | 2 | R
0x59B2 | 0x59B3 | 22962 | 22963 | ANG_2HR_HAR_I_35th_b | Aggr 2hr Phase B 35th Current Angle Harmonics | float | 2 | R
0x59B4 | 0x59B5 | 22964 | 22965 | ANG_2HR_HAR_I_35th_c | Aggr 2hr Phase C 35th Current Angle Harmonics | float | 2 | R
0x59B6 | 0x59B7 | 22966 | 22967 | ANG_2HR_HAR_I_35th_n | Aggr 2hr Phase N 35th Current Angle Harmonics | float | 2 | R
0x59B8 | 0x59B9 | 22968 | 22969 | ANG_2HR_HAR_V_36th_a | Aggr 2hr Phase A 36th Voltage Angle Harmonics | float | 2 | R
0x59BA | 0x59BB | 22970 | 22971 | ANG_2HR_HAR_V_36th_b | Aggr 2hr Phase B 36th Voltage Angle Harmonics | float | 2 | R
0x59BC | 0x59BD | 22972 | 22973 | ANG_2HR_HAR_V_36th_c | Aggr 2hr Phase C 36th Voltage Angle Harmonics | float | 2 | R
0x59BE | 0x59BF | 22974 | 22975 | ANG_2HR_HAR_I_36th_a | Aggr 2hr Phase A 36th Current Angle Harmonics | float | 2 | R
0x59C0 | 0x59C1 | 22976 | 22977 | ANG_2HR_HAR_I_36th_b | Aggr 2hr Phase B 36th Current Angle Harmonics | float | 2 | R
0x59C2 | 0x59C3 | 22978 | 22979 | ANG_2HR_HAR_I_36th_c | Aggr 2hr Phase C 36th Current Angle Harmonics | float | 2 | R
0x59C4 | 0x59C5 | 22980 | 22981 | ANG_2HR_HAR_I_36th_n | Aggr 2hr Phase N 36th Current Angle Harmonics | float | 2 | R
0x59C6 | 0x59C7 | 22982 | 22983 | ANG_2HR_HAR_V_37th_a | Aggr 2hr Phase A 37th Voltage Angle Harmonics | float | 2 | R
0x59C8 | 0x59C9 | 22984 | 22985 | ANG_2HR_HAR_V_37th_b | Aggr 2hr Phase B 37th Voltage Angle Harmonics | float | 2 | R
0x59CA | 0x59CB | 22986 | 22987 | ANG_2HR_HAR_V_37th_c | Aggr 2hr Phase C 37th Voltage Angle Harmonics | float | 2 | R
0x59CC | 0x59CD | 22988 | 22989 | ANG_2HR_HAR_I_37th_a | Aggr 2hr Phase A 37th Current Angle Harmonics | float | 2 | R
0x59CE | 0x59CF | 22990 | 22991 | ANG_2HR_HAR_I_37th_b | Aggr 2hr Phase B 37th Current Angle Harmonics | float | 2 | R
0x59D0 | 0x59D1 | 22992 | 22993 | ANG_2HR_HAR_I_37th_c | Aggr 2hr Phase C 37th Current Angle Harmonics | float | 2 | R
0x59D2 | 0x59D3 | 22994 | 22995 | ANG_2HR_HAR_I_37th_n | Aggr 2hr Phase N 37th Current Angle Harmonics | float | 2 | R
0x59D4 | 0x59D5 | 22996 | 22997 | ANG_2HR_HAR_V_38th_a | Aggr 2hr Phase A 38th Voltage Angle Harmonics | float | 2 | R
0x59D6 | 0x59D7 | 22998 | 22999 | ANG_2HR_HAR_V_38th_b | Aggr 2hr Phase B 38th Voltage Angle Harmonics | float | 2 | R
0x59D8 | 0x59D9 | 23000 | 23001 | ANG_2HR_HAR_V_38th_c | Aggr 2hr Phase C 38th Voltage Angle Harmonics | float | 2 | R
0x59DA | 0x59DB | 23002 | 23003 | ANG_2HR_HAR_I_38th_a | Aggr 2hr Phase A 38th Current Angle Harmonics | float | 2 | R
0x59DC | 0x59DD | 23004 | 23005 | ANG_2HR_HAR_I_38th_b | Aggr 2hr Phase B 38th Current Angle Harmonics | float | 2 | R
0x59DE | 0x59DF | 23006 | 23007 | ANG_2HR_HAR_I_38th_c | Aggr 2hr Phase C 38th Current Angle Harmonics | float | 2 | R
0x59E0 | 0x59E1 | 23008 | 23009 | ANG_2HR_HAR_I_38th_n | Aggr 2hr Phase N 38th Current Angle Harmonics | float | 2 | R
0x59E2 | 0x59E3 | 23010 | 23011 | ANG_2HR_HAR_V_39th_a | Aggr 2hr Phase A 39th Voltage Angle Harmonics | float | 2 | R
0x59E4 | 0x59E5 | 23012 | 23013 | ANG_2HR_HAR_V_39th_b | Aggr 2hr Phase B 39th Voltage Angle Harmonics | float | 2 | R
0x59E6 | 0x59E7 | 23014 | 23015 | ANG_2HR_HAR_V_39th_c | Aggr 2hr Phase C 39th Voltage Angle Harmonics | float | 2 | R
0x59E8 | 0x59E9 | 23016 | 23017 | ANG_2HR_HAR_I_39th_a | Aggr 2hr Phase A 39th Current Angle Harmonics | float | 2 | R
0x59EA | 0x59EB | 23018 | 23019 | ANG_2HR_HAR_I_39th_b | Aggr 2hr Phase B 39th Current Angle Harmonics | float | 2 | R
0x59EC | 0x59ED | 23020 | 23021 | ANG_2HR_HAR_I_39th_c | Aggr 2hr Phase C 39th Current Angle Harmonics | float | 2 | R
0x59EE | 0x59EF | 23022 | 23023 | ANG_2HR_HAR_I_39th_n | Aggr 2hr Phase N 39th Current Angle Harmonics | float | 2 | R
0x59F0 | 0x59F1 | 23024 | 23025 | ANG_2HR_HAR_V_40th_a | Aggr 2hr Phase A 40th Voltage Angle Harmonics | float | 2 | R
0x59F2 | 0x59F3 | 23026 | 23027 | ANG_2HR_HAR_V_40th_b | Aggr 2hr Phase B 40th Voltage Angle Harmonics | float | 2 | R
0x59F4 | 0x59F5 | 23028 | 23029 | ANG_2HR_HAR_V_40th_c | Aggr 2hr Phase C 40th Voltage Angle Harmonics | float | 2 | R
0x59F6 | 0x59F7 | 23030 | 23031 | ANG_2HR_HAR_I_40th_a | Aggr 2hr Phase A 40th Current Angle Harmonics | float | 2 | R
0x59F8 | 0x59F9 | 23032 | 23033 | ANG_2HR_HAR_I_40th_b | Aggr 2hr Phase B 40th Current Angle Harmonics | float | 2 | R
0x59FA | 0x59FB | 23034 | 23035 | ANG_2HR_HAR_I_40th_c | Aggr 2hr Phase C 40th Current Angle Harmonics | float | 2 | R
0x59FC | 0x59FD | 23036 | 23037 | ANG_2HR_HAR_I_40th_n | Aggr 2hr Phase N 40th Current Angle Harmonics | float | 2 | R
0x59FE | 0x59FF | 23038 | 23039 | ANG_2HR_HAR_V_41th_a | Aggr 2hr Phase A 41st Voltage Angle Harmonics | float | 2 | R
0x5A00 | 0x5A01 | 23040 | 23041 | ANG_2HR_HAR_V_41th_b | Aggr 2hr Phase B 41st Voltage Angle Harmonics | float | 2 | R
0x5A02 | 0x5A03 | 23042 | 23043 | ANG_2HR_HAR_V_41th_c | Aggr 2hr Phase C 41st Voltage Angle Harmonics | float | 2 | R
0x5A04 | 0x5A05 | 23044 | 23045 | ANG_2HR_HAR_I_41th_a | Aggr 2hr Phase A 41st Current Angle Harmonics | float | 2 | R
0x5A06 | 0x5A07 | 23046 | 23047 | ANG_2HR_HAR_I_41th_b | Aggr 2hr Phase B 41st Current Angle Harmonics | float | 2 | R
0x5A08 | 0x5A09 | 23048 | 23049 | ANG_2HR_HAR_I_41th_c | Aggr 2hr Phase C 41st Current Angle Harmonics | float | 2 | R
0x5A0A | 0x5A0B | 23050 | 23051 | ANG_2HR_HAR_I_41th_n | Aggr 2hr Phase N 41st Current Angle Harmonics | float | 2 | R
0x5A0C | 0x5A0D | 23052 | 23053 | ANG_2HR_HAR_V_42th_a | Aggr 2hr Phase A 42nd Voltage Angle Harmonics | float | 2 | R
0x5A0E | 0x5A0F | 23054 | 23055 | ANG_2HR_HAR_V_42th_b | Aggr 2hr Phase B 42nd Voltage Angle Harmonics | float | 2 | R
0x5A10 | 0x5A11 | 23056 | 23057 | ANG_2HR_HAR_V_42th_c | Aggr 2hr Phase C 42nd Voltage Angle Harmonics | float | 2 | R
0x5A12 | 0x5A13 | 23058 | 23059 | ANG_2HR_HAR_I_42th_a | Aggr 2hr Phase A 42nd Current Angle Harmonics | float | 2 | R
0x5A14 | 0x5A15 | 23060 | 23061 | ANG_2HR_HAR_I_42th_b | Aggr 2hr Phase B 42nd Current Angle Harmonics | float | 2 | R
0x5A16 | 0x5A17 | 23062 | 23063 | ANG_2HR_HAR_I_42th_c | Aggr 2hr Phase C 42nd Current Angle Harmonics | float | 2 | R
0x5A18 | 0x5A19 | 23064 | 23065 | ANG_2HR_HAR_I_42th_n | Aggr 2hr Phase N 42nd Current Angle Harmonics | float | 2 | R
0x5A1A | 0x5A1B | 23066 | 23067 | ANG_2HR_HAR_V_43th_a | Aggr 2hr Phase A 43rd Voltage Angle Harmonics | float | 2 | R
0x5A1C | 0x5A1D | 23068 | 23069 | ANG_2HR_HAR_V_43th_b | Aggr 2hr Phase B 43rd Voltage Angle Harmonics | float | 2 | R
0x5A1E | 0x5A1F | 23070 | 23071 | ANG_2HR_HAR_V_43th_c | Aggr 2hr Phase C 43rd Voltage Angle Harmonics | float | 2 | R
0x5A20 | 0x5A21 | 23072 | 23073 | ANG_2HR_HAR_I_43th_a | Aggr 2hr Phase A 43rd Current Angle Harmonics | float | 2 | R
0x5A22 | 0x5A23 | 23074 | 23075 | ANG_2HR_HAR_I_43th_b | Aggr 2hr Phase B 43rd Current Angle Harmonics | float | 2 | R
0x5A24 | 0x5A25 | 23076 | 23077 | ANG_2HR_HAR_I_43th_c | Aggr 2hr Phase C 43rd Current Angle Harmonics | float | 2 | R
0x5A26 | 0x5A27 | 23078 | 23079 | ANG_2HR_HAR_I_43th_n | Aggr 2hr Phase N 43rd Current Angle Harmonics | float | 2 | R
0x5A28 | 0x5A29 | 23080 | 23081 | ANG_2HR_HAR_V_44th_a | Aggr 2hr Phase A 44th Voltage Angle Harmonics | float | 2 | R
0x5A2A | 0x5A2B | 23082 | 23083 | ANG_2HR_HAR_V_44th_b | Aggr 2hr Phase B 44th Voltage Angle Harmonics | float | 2 | R
0x5A2C | 0x5A2D | 23084 | 23085 | ANG_2HR_HAR_V_44th_c | Aggr 2hr Phase C 44th Voltage Angle Harmonics | float | 2 | R
0x5A2E | 0x5A2F | 23086 | 23087 | ANG_2HR_HAR_I_44th_a | Aggr 2hr Phase A 44th Current Angle Harmonics | float | 2 | R
0x5A30 | 0x5A31 | 23088 | 23089 | ANG_2HR_HAR_I_44th_b | Aggr 2hr Phase B 44th Current Angle Harmonics | float | 2 | R
0x5A32 | 0x5A33 | 23090 | 23091 | ANG_2HR_HAR_I_44th_c | Aggr 2hr Phase C 44th Current Angle Harmonics | float | 2 | R
0x5A34 | 0x5A35 | 23092 | 23093 | ANG_2HR_HAR_I_44th_n | Aggr 2hr Phase N 44th Current Angle Harmonics | float | 2 | R
0x5A36 | 0x5A37 | 23094 | 23095 | ANG_2HR_HAR_V_45th_a | Aggr 2hr Phase A 45th Voltage Angle Harmonics | float | 2 | R
0x5A38 | 0x5A39 | 23096 | 23097 | ANG_2HR_HAR_V_45th_b | Aggr 2hr Phase B 45th Voltage Angle Harmonics | float | 2 | R
0x5A3A | 0x5A3B | 23098 | 23099 | ANG_2HR_HAR_V_45th_c | Aggr 2hr Phase C 45th Voltage Angle Harmonics | float | 2 | R
0x5A3C | 0x5A3D | 23100 | 23101 | ANG_2HR_HAR_I_45th_a | Aggr 2hr Phase A 45th Current Angle Harmonics | float | 2 | R
0x5A3E | 0x5A3F | 23102 | 23103 | ANG_2HR_HAR_I_45th_b | Aggr 2hr Phase B 45th Current Angle Harmonics | float | 2 | R
0x5A40 | 0x5A41 | 23104 | 23105 | ANG_2HR_HAR_I_45th_c | Aggr 2hr Phase C 45th Current Angle Harmonics | float | 2 | R
0x5A42 | 0x5A43 | 23106 | 23107 | ANG_2HR_HAR_I_45th_n | Aggr 2hr Phase N 45th Current Angle Harmonics | float | 2 | R
0x5A44 | 0x5A45 | 23108 | 23109 | ANG_2HR_HAR_V_46th_a | Aggr 2hr Phase A 46th Voltage Angle Harmonics | float | 2 | R
0x5A46 | 0x5A47 | 23110 | 23111 | ANG_2HR_HAR_V_46th_b | Aggr 2hr Phase B 46th Voltage Angle Harmonics | float | 2 | R
0x5A48 | 0x5A49 | 23112 | 23113 | ANG_2HR_HAR_V_46th_c | Aggr 2hr Phase C 46th Voltage Angle Harmonics | float | 2 | R
0x5A4A | 0x5A4B | 23114 | 23115 | ANG_2HR_HAR_I_46th_a | Aggr 2hr Phase A 46th Current Angle Harmonics | float | 2 | R
0x5A4C | 0x5A4D | 23116 | 23117 | ANG_2HR_HAR_I_46th_b | Aggr 2hr Phase B 46th Current Angle Harmonics | float | 2 | R
0x5A4E | 0x5A4F | 23118 | 23119 | ANG_2HR_HAR_I_46th_c | Aggr 2hr Phase C 46th Current Angle Harmonics | float | 2 | R
0x5A50 | 0x5A51 | 23120 | 23121 | ANG_2HR_HAR_I_46th_n | Aggr 2hr Phase N 46th Current Angle Harmonics | float | 2 | R
0x5A52 | 0x5A53 | 23122 | 23123 | ANG_2HR_HAR_V_47th_a | Aggr 2hr Phase A 47th Voltage Angle Harmonics | float | 2 | R
0x5A54 | 0x5A55 | 23124 | 23125 | ANG_2HR_HAR_V_47th_b | Aggr 2hr Phase B 47th Voltage Angle Harmonics | float | 2 | R
0x5A56 | 0x5A57 | 23126 | 23127 | ANG_2HR_HAR_V_47th_c | Aggr 2hr Phase C 47th Voltage Angle Harmonics | float | 2 | R
0x5A58 | 0x5A59 | 23128 | 23129 | ANG_2HR_HAR_I_47th_a | Aggr 2hr Phase A 47th Current Angle Harmonics | float | 2 | R
0x5A5A | 0x5A5B | 23130 | 23131 | ANG_2HR_HAR_I_47th_b | Aggr 2hr Phase B 47th Current Angle Harmonics | float | 2 | R
0x5A5C | 0x5A5D | 23132 | 23133 | ANG_2HR_HAR_I_47th_c | Aggr 2hr Phase C 47th Current Angle Harmonics | float | 2 | R
0x5A5E | 0x5A5F | 23134 | 23135 | ANG_2HR_HAR_I_47th_n | Aggr 2hr Phase N 47th Current Angle Harmonics | float | 2 | R
0x5A60 | 0x5A61 | 23136 | 23137 | ANG_2HR_HAR_V_48th_a | Aggr 2hr Phase A 48th Voltage Angle Harmonics | float | 2 | R
0x5A62 | 0x5A63 | 23138 | 23139 | ANG_2HR_HAR_V_48th_b | Aggr 2hr Phase B 48th Voltage Angle Harmonics | float | 2 | R
0x5A64 | 0x5A65 | 23140 | 23141 | ANG_2HR_HAR_V_48th_c | Aggr 2hr Phase C 48th Voltage Angle Harmonics | float | 2 | R
0x5A66 | 0x5A67 | 23142 | 23143 | ANG_2HR_HAR_I_48th_a | Aggr 2hr Phase A 48th Current Angle Harmonics | float | 2 | R
0x5A68 | 0x5A69 | 23144 | 23145 | ANG_2HR_HAR_I_48th_b | Aggr 2hr Phase B 48th Current Angle Harmonics | float | 2 | R
0x5A6A | 0x5A6B | 23146 | 23147 | ANG_2HR_HAR_I_48th_c | Aggr 2hr Phase C 48th Current Angle Harmonics | float | 2 | R
0x5A6C | 0x5A6D | 23148 | 23149 | ANG_2HR_HAR_I_48th_n | Aggr 2hr Phase N 48th Current Angle Harmonics | float | 2 | R
0x5A6E | 0x5A6F | 23150 | 23151 | ANG_2HR_HAR_V_49th_a | Aggr 2hr Phase A 49th Voltage Angle Harmonics | float | 2 | R
0x5A70 | 0x5A71 | 23152 | 23153 | ANG_2HR_HAR_V_49th_b | Aggr 2hr Phase B 49th Voltage Angle Harmonics | float | 2 | R
0x5A72 | 0x5A73 | 23154 | 23155 | ANG_2HR_HAR_V_49th_c | Aggr 2hr Phase C 49th Voltage Angle Harmonics | float | 2 | R
0x5A74 | 0x5A75 | 23156 | 23157 | ANG_2HR_HAR_I_49th_a | Aggr 2hr Phase A 49th Current Angle Harmonics | float | 2 | R
0x5A76 | 0x5A77 | 23158 | 23159 | ANG_2HR_HAR_I_49th_b | Aggr 2hr Phase B 49th Current Angle Harmonics | float | 2 | R
0x5A78 | 0x5A79 | 23160 | 23161 | ANG_2HR_HAR_I_49th_c | Aggr 2hr Phase C 49th Current Angle Harmonics | float | 2 | R
0x5A7A | 0x5A7B | 23162 | 23163 | ANG_2HR_HAR_I_49th_n | Aggr 2hr Phase N 49th Current Angle Harmonics | float | 2 | R
0x5A7C | 0x5A7D | 23164 | 23165 | ANG_2HR_HAR_V_50th_a | Aggr 2hr Phase A 50th Voltage Angle Harmonics | float | 2 | R
0x5A7E | 0x5A7F | 23166 | 23167 | ANG_2HR_HAR_V_50th_b | Aggr 2hr Phase B 50th Voltage Angle Harmonics | float | 2 | R
0x5A80 | 0x5A81 | 23168 | 23169 | ANG_2HR_HAR_V_50th_c | Aggr 2hr Phase C 50th Voltage Angle Harmonics | float | 2 | R
0x5A82 | 0x5A83 | 23170 | 23171 | ANG_2HR_HAR_I_50th_a | Aggr 2hr Phase A 50th Current Angle Harmonics | float | 2 | R
0x5A84 | 0x5A85 | 23172 | 23173 | ANG_2HR_HAR_I_50th_b | Aggr 2hr Phase B 50th Current Angle Harmonics | float | 2 | R
0x5A86 | 0x5A87 | 23174 | 23175 | ANG_2HR_HAR_I_50th_c | Aggr 2hr Phase C 50th Current Angle Harmonics | float | 2 | R
0x5A88 | 0x5A89 | 23176 | 23177 | ANG_2HR_HAR_I_50th_n | Aggr 2hr Phase N 50th Current Angle Harmonics | float | 2 | R
0x5A8A | 0x5A8B | 23178 | 23179 | ANG_2HR_HAR_V_51th_a | Aggr 2hr Phase A 51st Voltage Angle Harmonics | float | 2 | R
0x5A8C | 0x5A8D | 23180 | 23181 | ANG_2HR_HAR_V_51th_b | Aggr 2hr Phase B 51st Voltage Angle Harmonics | float | 2 | R
0x5A8E | 0x5A8F | 23182 | 23183 | ANG_2HR_HAR_V_51th_c | Aggr 2hr Phase C 51st Voltage Angle Harmonics | float | 2 | R
0x5A90 | 0x5A91 | 23184 | 23185 | ANG_2HR_HAR_I_51th_a | Aggr 2hr Phase A 51st Current Angle Harmonics | float | 2 | R
0x5A92 | 0x5A93 | 23186 | 23187 | ANG_2HR_HAR_I_51th_b | Aggr 2hr Phase B 51st Current Angle Harmonics | float | 2 | R
0x5A94 | 0x5A95 | 23188 | 23189 | ANG_2HR_HAR_I_51th_c | Aggr 2hr Phase C 51st Current Angle Harmonics | float | 2 | R
0x5A96 | 0x5A97 | 23190 | 23191 | ANG_2HR_HAR_I_51th_n | Aggr 2hr Phase N 51st Current Angle Harmonics | float | 2 | R
0x5A98 | 0x5A99 | 23192 | 23193 | ANG_2HR_HAR_V_52th_a | Aggr 2hr Phase A 52nd Voltage Angle Harmonics | float | 2 | R
0x5A9A | 0x5A9B | 23194 | 23195 | ANG_2HR_HAR_V_52th_b | Aggr 2hr Phase B 52nd Voltage Angle Harmonics | float | 2 | R
0x5A9C | 0x5A9D | 23196 | 23197 | ANG_2HR_HAR_V_52th_c | Aggr 2hr Phase C 52nd Voltage Angle Harmonics | float | 2 | R
0x5A9E | 0x5A9F | 23198 | 23199 | ANG_2HR_HAR_I_52th_a | Aggr 2hr Phase A 52nd Current Angle Harmonics | float | 2 | R
0x5AA0 | 0x5AA1 | 23200 | 23201 | ANG_2HR_HAR_I_52th_b | Aggr 2hr Phase B 52nd Current Angle Harmonics | float | 2 | R
0x5AA2 | 0x5AA3 | 23202 | 23203 | ANG_2HR_HAR_I_52th_c | Aggr 2hr Phase C 52nd Current Angle Harmonics | float | 2 | R
0x5AA4 | 0x5AA5 | 23204 | 23205 | ANG_2HR_HAR_I_52th_n | Aggr 2hr Phase N 52nd Current Angle Harmonics | float | 2 | R
0x5AA6 | 0x5AA7 | 23206 | 23207 | ANG_2HR_HAR_V_53th_a | Aggr 2hr Phase A 53rd Voltage Angle Harmonics | float | 2 | R
0x5AA8 | 0x5AA9 | 23208 | 23209 | ANG_2HR_HAR_V_53th_b | Aggr 2hr Phase B 53rd Voltage Angle Harmonics | float | 2 | R
0x5AAA | 0x5AAB | 23210 | 23211 | ANG_2HR_HAR_V_53th_c | Aggr 2hr Phase C 53rd Voltage Angle Harmonics | float | 2 | R
0x5AAC | 0x5AAD | 23212 | 23213 | ANG_2HR_HAR_I_53th_a | Aggr 2hr Phase A 53rd Current Angle Harmonics | float | 2 | R
0x5AAE | 0x5AAF | 23214 | 23215 | ANG_2HR_HAR_I_53th_b | Aggr 2hr Phase B 53rd Current Angle Harmonics | float | 2 | R
0x5AB0 | 0x5AB1 | 23216 | 23217 | ANG_2HR_HAR_I_53th_c | Aggr 2hr Phase C 53rd Current Angle Harmonics | float | 2 | R
0x5AB2 | 0x5AB3 | 23218 | 23219 | ANG_2HR_HAR_I_53th_n | Aggr 2hr Phase N 53rd Current Angle Harmonics | float | 2 | R
0x5AB4 | 0x5AB5 | 23220 | 23221 | ANG_2HR_HAR_V_54th_a | Aggr 2hr Phase A 54th Voltage Angle Harmonics | float | 2 | R
0x5AB6 | 0x5AB7 | 23222 | 23223 | ANG_2HR_HAR_V_54th_b | Aggr 2hr Phase B 54th Voltage Angle Harmonics | float | 2 | R
0x5AB8 | 0x5AB9 | 23224 | 23225 | ANG_2HR_HAR_V_54th_c | Aggr 2hr Phase C 54th Voltage Angle Harmonics | float | 2 | R
0x5ABA | 0x5ABB | 23226 | 23227 | ANG_2HR_HAR_I_54th_a | Aggr 2hr Phase A 54th Current Angle Harmonics | float | 2 | R
0x5ABC | 0x5ABD | 23228 | 23229 | ANG_2HR_HAR_I_54th_b | Aggr 2hr Phase B 54th Current Angle Harmonics | float | 2 | R
0x5ABE | 0x5ABF | 23230 | 23231 | ANG_2HR_HAR_I_54th_c | Aggr 2hr Phase C 54th Current Angle Harmonics | float | 2 | R
0x5AC0 | 0x5AC1 | 23232 | 23233 | ANG_2HR_HAR_I_54th_n | Aggr 2hr Phase N 54th Current Angle Harmonics | float | 2 | R
0x5AC2 | 0x5AC3 | 23234 | 23235 | ANG_2HR_HAR_V_55th_a | Aggr 2hr Phase A 55th Voltage Angle Harmonics | float | 2 | R
0x5AC4 | 0x5AC5 | 23236 | 23237 | ANG_2HR_HAR_V_55th_b | Aggr 2hr Phase B 55th Voltage Angle Harmonics | float | 2 | R
0x5AC6 | 0x5AC7 | 23238 | 23239 | ANG_2HR_HAR_V_55th_c | Aggr 2hr Phase C 55th Voltage Angle Harmonics | float | 2 | R
0x5AC8 | 0x5AC9 | 23240 | 23241 | ANG_2HR_HAR_I_55th_a | Aggr 2hr Phase A 55th Current Angle Harmonics | float | 2 | R
0x5ACA | 0x5ACB | 23242 | 23243 | ANG_2HR_HAR_I_55th_b | Aggr 2hr Phase B 55th Current Angle Harmonics | float | 2 | R
0x5ACC | 0x5ACD | 23244 | 23245 | ANG_2HR_HAR_I_55th_c | Aggr 2hr Phase C 55th Current Angle Harmonics | float | 2 | R
0x5ACE | 0x5ACF | 23246 | 23247 | ANG_2HR_HAR_I_55th_n | Aggr 2hr Phase N 55th Current Angle Harmonics | float | 2 | R
0x5AD0 | 0x5AD1 | 23248 | 23249 | ANG_2HR_HAR_V_56th_a | Aggr 2hr Phase A 56th Voltage Angle Harmonics | float | 2 | R
0x5AD2 | 0x5AD3 | 23250 | 23251 | ANG_2HR_HAR_V_56th_b | Aggr 2hr Phase B 56th Voltage Angle Harmonics | float | 2 | R
0x5AD4 | 0x5AD5 | 23252 | 23253 | ANG_2HR_HAR_V_56th_c | Aggr 2hr Phase C 56th Voltage Angle Harmonics | float | 2 | R
0x5AD6 | 0x5AD7 | 23254 | 23255 | ANG_2HR_HAR_I_56th_a | Aggr 2hr Phase A 56th Current Angle Harmonics | float | 2 | R
0x5AD8 | 0x5AD9 | 23256 | 23257 | ANG_2HR_HAR_I_56th_b | Aggr 2hr Phase B 56th Current Angle Harmonics | float | 2 | R
0x5ADA | 0x5ADB | 23258 | 23259 | ANG_2HR_HAR_I_56th_c | Aggr 2hr Phase C 56th Current Angle Harmonics | float | 2 | R
0x5ADC | 0x5ADD | 23260 | 23261 | ANG_2HR_HAR_I_56th_n | Aggr 2hr Phase N 56th Current Angle Harmonics | float | 2 | R
0x5ADE | 0x5ADF | 23262 | 23263 | ANG_2HR_HAR_V_57th_a | Aggr 2hr Phase A 57th Voltage Angle Harmonics | float | 2 | R
0x5AE0 | 0x5AE1 | 23264 | 23265 | ANG_2HR_HAR_V_57th_b | Aggr 2hr Phase B 57th Voltage Angle Harmonics | float | 2 | R
0x5AE2 | 0x5AE3 | 23266 | 23267 | ANG_2HR_HAR_V_57th_c | Aggr 2hr Phase C 57th Voltage Angle Harmonics | float | 2 | R
0x5AE4 | 0x5AE5 | 23268 | 23269 | ANG_2HR_HAR_I_57th_a | Aggr 2hr Phase A 57th Current Angle Harmonics | float | 2 | R
0x5AE6 | 0x5AE7 | 23270 | 23271 | ANG_2HR_HAR_I_57th_b | Aggr 2hr Phase B 57th Current Angle Harmonics | float | 2 | R
0x5AE8 | 0x5AE9 | 23272 | 23273 | ANG_2HR_HAR_I_57th_c | Aggr 2hr Phase C 57th Current Angle Harmonics | float | 2 | R
0x5AEA | 0x5AEB | 23274 | 23275 | ANG_2HR_HAR_I_57th_n | Aggr 2hr Phase N 57th Current Angle Harmonics | float | 2 | R
0x5AEC | 0x5AED | 23276 | 23277 | ANG_2HR_HAR_V_58th_a | Aggr 2hr Phase A 58th Voltage Angle Harmonics | float | 2 | R
0x5AEE | 0x5AEF | 23278 | 23279 | ANG_2HR_HAR_V_58th_b | Aggr 2hr Phase B 58th Voltage Angle Harmonics | float | 2 | R
0x5AF0 | 0x5AF1 | 23280 | 23281 | ANG_2HR_HAR_V_58th_c | Aggr 2hr Phase C 58th Voltage Angle Harmonics | float | 2 | R
0x5AF2 | 0x5AF3 | 23282 | 23283 | ANG_2HR_HAR_I_58th_a | Aggr 2hr Phase A 58th Current Angle Harmonics | float | 2 | R
0x5AF4 | 0x5AF5 | 23284 | 23285 | ANG_2HR_HAR_I_58th_b | Aggr 2hr Phase B 58th Current Angle Harmonics | float | 2 | R
0x5AF6 | 0x5AF7 | 23286 | 23287 | ANG_2HR_HAR_I_58th_c | Aggr 2hr Phase C 58th Current Angle Harmonics | float | 2 | R
0x5AF8 | 0x5AF9 | 23288 | 23289 | ANG_2HR_HAR_I_58th_n | Aggr 2hr Phase N 58th Current Angle Harmonics | float | 2 | R
0x5AFA | 0x5AFB | 23290 | 23291 | ANG_2HR_HAR_V_59th_a | Aggr 2hr Phase A 59th Voltage Angle Harmonics | float | 2 | R
0x5AFC | 0x5AFD | 23292 | 23293 | ANG_2HR_HAR_V_59th_b | Aggr 2hr Phase B 59th Voltage Angle Harmonics | float | 2 | R
0x5AFE | 0x5AFF | 23294 | 23295 | ANG_2HR_HAR_V_59th_c | Aggr 2hr Phase C 59th Voltage Angle Harmonics | float | 2 | R
0x5B00 | 0x5B01 | 23296 | 23297 | ANG_2HR_HAR_I_59th_a | Aggr 2hr Phase A 59th Current Angle Harmonics | float | 2 | R
0x5B02 | 0x5B03 | 23298 | 23299 | ANG_2HR_HAR_I_59th_b | Aggr 2hr Phase B 59th Current Angle Harmonics | float | 2 | R
0x5B04 | 0x5B05 | 23300 | 23301 | ANG_2HR_HAR_I_59th_c | Aggr 2hr Phase C 59th Current Angle Harmonics | float | 2 | R
0x5B06 | 0x5B07 | 23302 | 23303 | ANG_2HR_HAR_I_59th_n | Aggr 2hr Phase N 59th Current Angle Harmonics | float | 2 | R
0x5B08 | 0x5B09 | 23304 | 23305 | ANG_2HR_HAR_V_60th_a | Aggr 2hr Phase A 60th Voltage Angle Harmonics | float | 2 | R
0x5B0A | 0x5B0B | 23306 | 23307 | ANG_2HR_HAR_V_60th_b | Aggr 2hr Phase B 60th Voltage Angle Harmonics | float | 2 | R
0x5B0C | 0x5B0D | 23308 | 23309 | ANG_2HR_HAR_V_60th_c | Aggr 2hr Phase C 60th Voltage Angle Harmonics | float | 2 | R
0x5B0E | 0x5B0F | 23310 | 23311 | ANG_2HR_HAR_I_60th_a | Aggr 2hr Phase A 60th Current Angle Harmonics | float | 2 | R
0x5B10 | 0x5B11 | 23312 | 23313 | ANG_2HR_HAR_I_60th_b | Aggr 2hr Phase B 60th Current Angle Harmonics | float | 2 | R
0x5B12 | 0x5B13 | 23314 | 23315 | ANG_2HR_HAR_I_60th_c | Aggr 2hr Phase C 60th Current Angle Harmonics | float | 2 | R
0x5B14 | 0x5B15 | 23316 | 23317 | ANG_2HR_HAR_I_60th_n | Aggr 2hr Phase N 60th Current Angle Harmonics | float | 2 | R
0x5B16 | 0x5B17 | 23318 | 23319 | ANG_2HR_HAR_V_61th_a | Aggr 2hr Phase A 61st Voltage Angle Harmonics | float | 2 | R
0x5B18 | 0x5B19 | 23320 | 23321 | ANG_2HR_HAR_V_61th_b | Aggr 2hr Phase B 61st Voltage Angle Harmonics | float | 2 | R
0x5B1A | 0x5B1B | 23322 | 23323 | ANG_2HR_HAR_V_61th_c | Aggr 2hr Phase C 61st Voltage Angle Harmonics | float | 2 | R
0x5B1C | 0x5B1D | 23324 | 23325 | ANG_2HR_HAR_I_61th_a | Aggr 2hr Phase A 61st Current Angle Harmonics | float | 2 | R
0x5B1E | 0x5B1F | 23326 | 23327 | ANG_2HR_HAR_I_61th_b | Aggr 2hr Phase B 61st Current Angle Harmonics | float | 2 | R
0x5B20 | 0x5B21 | 23328 | 23329 | ANG_2HR_HAR_I_61th_c | Aggr 2hr Phase C 61st Current Angle Harmonics | float | 2 | R
0x5B22 | 0x5B23 | 23330 | 23331 | ANG_2HR_HAR_I_61th_n | Aggr 2hr Phase N 61st Current Angle Harmonics | float | 2 | R
0x5B24 | 0x5B25 | 23332 | 23333 | ANG_2HR_HAR_V_62th_a | Aggr 2hr Phase A 62nd Voltage Angle Harmonics | float | 2 | R
0x5B26 | 0x5B27 | 23334 | 23335 | ANG_2HR_HAR_V_62th_b | Aggr 2hr Phase B 62nd Voltage Angle Harmonics | float | 2 | R
0x5B28 | 0x5B29 | 23336 | 23337 | ANG_2HR_HAR_V_62th_c | Aggr 2hr Phase C 62nd Voltage Angle Harmonics | float | 2 | R
0x5B2A | 0x5B2B | 23338 | 23339 | ANG_2HR_HAR_I_62th_a | Aggr 2hr Phase A 62nd Current Angle Harmonics | float | 2 | R
0x5B2C | 0x5B2D | 23340 | 23341 | ANG_2HR_HAR_I_62th_b | Aggr 2hr Phase B 62nd Current Angle Harmonics | float | 2 | R
0x5B2E | 0x5B2F | 23342 | 23343 | ANG_2HR_HAR_I_62th_c | Aggr 2hr Phase C 62nd Current Angle Harmonics | float | 2 | R
0x5B30 | 0x5B31 | 23344 | 23345 | ANG_2HR_HAR_I_62th_n | Aggr 2hr Phase N 62nd Current Angle Harmonics | float | 2 | R
0x5B32 | 0x5B33 | 23346 | 23347 | ANG_2HR_HAR_V_63th_a | Aggr 2hr Phase A 63rd Voltage Angle Harmonics | float | 2 | R
0x5B34 | 0x5B35 | 23348 | 23349 | ANG_2HR_HAR_V_63th_b | Aggr 2hr Phase B 63rd Voltage Angle Harmonics | float | 2 | R
0x5B36 | 0x5B37 | 23350 | 23351 | ANG_2HR_HAR_V_63th_c | Aggr 2hr Phase C 63rd Voltage Angle Harmonics | float | 2 | R
0x5B38 | 0x5B39 | 23352 | 23353 | ANG_2HR_HAR_I_63th_a | Aggr 2hr Phase A 63rd Current Angle Harmonics | float | 2 | R
0x5B3A | 0x5B3B | 23354 | 23355 | ANG_2HR_HAR_I_63th_b | Aggr 2hr Phase B 63rd Current Angle Harmonics | float | 2 | R
0x5B3C | 0x5B3D | 23356 | 23357 | ANG_2HR_HAR_I_63th_c | Aggr 2hr Phase C 63rd Current Angle Harmonics | float | 2 | R
0x5B3E | 0x5B3F | 23358 | 23359 | ANG_2HR_HAR_I_63th_n | Aggr 2hr Phase N 63rd Current Angle Harmonics | float | 2 | R
0x5B40 | 0x5B41 | 23360 | 23361 | ANG_2HR_HAR_V_64th_a | Aggr 2hr Phase A 64th Voltage Angle Harmonics | float | 2 | R
0x5B42 | 0x5B43 | 23362 | 23363 | ANG_2HR_HAR_V_64th_b | Aggr 2hr Phase B 64th Voltage Angle Harmonics | float | 2 | R
0x5B44 | 0x5B45 | 23364 | 23365 | ANG_2HR_HAR_V_64th_c | Aggr 2hr Phase C 64th Voltage Angle Harmonics | float | 2 | R
0x5B46 | 0x5B47 | 23366 | 23367 | ANG_2HR_HAR_I_64th_a | Aggr 2hr Phase A 64th Current Angle Harmonics | float | 2 | R
0x5B48 | 0x5B49 | 23368 | 23369 | ANG_2HR_HAR_I_64th_b | Aggr 2hr Phase B 64th Current Angle Harmonics | float | 2 | R
0x5B4A | 0x5B4B | 23370 | 23371 | ANG_2HR_HAR_I_64th_c | Aggr 2hr Phase C 64th Current Angle Harmonics | float | 2 | R
0x5B4C | 0x5B4D | 23372 | 23373 | ANG_2HR_HAR_I_64th_n | Aggr 2hr Phase N 64th Current Angle Harmonics | float | 2 | R
0x5B4E | 0x5B4F | 23374 | 23375 | ANG_2HR_HAR_V_65th_a | Aggr 2hr Phase A 65th Voltage Angle Harmonics | float | 2 | R
0x5B50 | 0x5B51 | 23376 | 23377 | ANG_2HR_HAR_V_65th_b | Aggr 2hr Phase B 65th Voltage Angle Harmonics | float | 2 | R
0x5B52 | 0x5B53 | 23378 | 23379 | ANG_2HR_HAR_V_65th_c | Aggr 2hr Phase C 65th Voltage Angle Harmonics | float | 2 | R
0x5B54 | 0x5B55 | 23380 | 23381 | ANG_2HR_HAR_I_65th_a | Aggr 2hr Phase A 65th Current Angle Harmonics | float | 2 | R
0x5B56 | 0x5B57 | 23382 | 23383 | ANG_2HR_HAR_I_65th_b | Aggr 2hr Phase B 65th Current Angle Harmonics | float | 2 | R
0x5B58 | 0x5B59 | 23384 | 23385 | ANG_2HR_HAR_I_65th_c | Aggr 2hr Phase C 65th Current Angle Harmonics | float | 2 | R
0x5B5A | 0x5B5B | 23386 | 23387 | ANG_2HR_HAR_I_65th_n | Aggr 2hr Phase N 65th Current Angle Harmonics | float | 2 | R
0x5B5C | 0x5B5D | 23388 | 23389 | ANG_2HR_HAR_V_66th_a | Aggr 2hr Phase A 66th Voltage Angle Harmonics | float | 2 | R
0x5B5E | 0x5B5F | 23390 | 23391 | ANG_2HR_HAR_V_66th_b | Aggr 2hr Phase B 66th Voltage Angle Harmonics | float | 2 | R
0x5B60 | 0x5B61 | 23392 | 23393 | ANG_2HR_HAR_V_66th_c | Aggr 2hr Phase C 66th Voltage Angle Harmonics | float | 2 | R
0x5B62 | 0x5B63 | 23394 | 23395 | ANG_2HR_HAR_I_66th_a | Aggr 2hr Phase A 66th Current Angle Harmonics | float | 2 | R
0x5B64 | 0x5B65 | 23396 | 23397 | ANG_2HR_HAR_I_66th_b | Aggr 2hr Phase B 66th Current Angle Harmonics | float | 2 | R
0x5B66 | 0x5B67 | 23398 | 23399 | ANG_2HR_HAR_I_66th_c | Aggr 2hr Phase C 66th Current Angle Harmonics | float | 2 | R
0x5B68 | 0x5B69 | 23400 | 23401 | ANG_2HR_HAR_I_66th_n | Aggr 2hr Phase N 66th Current Angle Harmonics | float | 2 | R
0x5B6A | 0x5B6B | 23402 | 23403 | ANG_2HR_HAR_V_67th_a | Aggr 2hr Phase A 67th Voltage Angle Harmonics | float | 2 | R
0x5B6C | 0x5B6D | 23404 | 23405 | ANG_2HR_HAR_V_67th_b | Aggr 2hr Phase B 67th Voltage Angle Harmonics | float | 2 | R
0x5B6E | 0x5B6F | 23406 | 23407 | ANG_2HR_HAR_V_67th_c | Aggr 2hr Phase C 67th Voltage Angle Harmonics | float | 2 | R
0x5B70 | 0x5B71 | 23408 | 23409 | ANG_2HR_HAR_I_67th_a | Aggr 2hr Phase A 67th Current Angle Harmonics | float | 2 | R
0x5B72 | 0x5B73 | 23410 | 23411 | ANG_2HR_HAR_I_67th_b | Aggr 2hr Phase B 67th Current Angle Harmonics | float | 2 | R
0x5B74 | 0x5B75 | 23412 | 23413 | ANG_2HR_HAR_I_67th_c | Aggr 2hr Phase C 67th Current Angle Harmonics | float | 2 | R
0x5B76 | 0x5B77 | 23414 | 23415 | ANG_2HR_HAR_I_67th_n | Aggr 2hr Phase N 67th Current Angle Harmonics | float | 2 | R
0x5B78 | 0x5B79 | 23416 | 23417 | ANG_2HR_HAR_V_68th_a | Aggr 2hr Phase A 68th Voltage Angle Harmonics | float | 2 | R
0x5B7A | 0x5B7B | 23418 | 23419 | ANG_2HR_HAR_V_68th_b | Aggr 2hr Phase B 68th Voltage Angle Harmonics | float | 2 | R
0x5B7C | 0x5B7D | 23420 | 23421 | ANG_2HR_HAR_V_68th_c | Aggr 2hr Phase C 68th Voltage Angle Harmonics | float | 2 | R
0x5B7E | 0x5B7F | 23422 | 23423 | ANG_2HR_HAR_I_68th_a | Aggr 2hr Phase A 68th Current Angle Harmonics | float | 2 | R
0x5B80 | 0x5B81 | 23424 | 23425 | ANG_2HR_HAR_I_68th_b | Aggr 2hr Phase B 68th Current Angle Harmonics | float | 2 | R
0x5B82 | 0x5B83 | 23426 | 23427 | ANG_2HR_HAR_I_68th_c | Aggr 2hr Phase C 68th Current Angle Harmonics | float | 2 | R
0x5B84 | 0x5B85 | 23428 | 23429 | ANG_2HR_HAR_I_68th_n | Aggr 2hr Phase N 68th Current Angle Harmonics | float | 2 | R
0x5B86 | 0x5B87 | 23430 | 23431 | ANG_2HR_HAR_V_69th_a | Aggr 2hr Phase A 69th Voltage Angle Harmonics | float | 2 | R
0x5B88 | 0x5B89 | 23432 | 23433 | ANG_2HR_HAR_V_69th_b | Aggr 2hr Phase B 69th Voltage Angle Harmonics | float | 2 | R
0x5B8A | 0x5B8B | 23434 | 23435 | ANG_2HR_HAR_V_69th_c | Aggr 2hr Phase C 69th Voltage Angle Harmonics | float | 2 | R
0x5B8C | 0x5B8D | 23436 | 23437 | ANG_2HR_HAR_I_69th_a | Aggr 2hr Phase A 69th Current Angle Harmonics | float | 2 | R
0x5B8E | 0x5B8F | 23438 | 23439 | ANG_2HR_HAR_I_69th_b | Aggr 2hr Phase B 69th Current Angle Harmonics | float | 2 | R
0x5B90 | 0x5B91 | 23440 | 23441 | ANG_2HR_HAR_I_69th_c | Aggr 2hr Phase C 69th Current Angle Harmonics | float | 2 | R
0x5B92 | 0x5B93 | 23442 | 23443 | ANG_2HR_HAR_I_69th_n | Aggr 2hr Phase N 69th Current Angle Harmonics | float | 2 | R
0x5B94 | 0x5B95 | 23444 | 23445 | ANG_2HR_HAR_V_70th_a | Aggr 2hr Phase A 70th Voltage Angle Harmonics | float | 2 | R
0x5B96 | 0x5B97 | 23446 | 23447 | ANG_2HR_HAR_V_70th_b | Aggr 2hr Phase B 70th Voltage Angle Harmonics | float | 2 | R
0x5B98 | 0x5B99 | 23448 | 23449 | ANG_2HR_HAR_V_70th_c | Aggr 2hr Phase C 70th Voltage Angle Harmonics | float | 2 | R
0x5B9A | 0x5B9B | 23450 | 23451 | ANG_2HR_HAR_I_70th_a | Aggr 2hr Phase A 70th Current Angle Harmonics | float | 2 | R
0x5B9C | 0x5B9D | 23452 | 23453 | ANG_2HR_HAR_I_70th_b | Aggr 2hr Phase B 70th Current Angle Harmonics | float | 2 | R
0x5B9E | 0x5B9F | 23454 | 23455 | ANG_2HR_HAR_I_70th_c | Aggr 2hr Phase C 70th Current Angle Harmonics | float | 2 | R
0x5BA0 | 0x5BA1 | 23456 | 23457 | ANG_2HR_HAR_I_70th_n | Aggr 2hr Phase N 70th Current Angle Harmonics | float | 2 | R
0x5BA2 | 0x5BA3 | 23458 | 23459 | ANG_2HR_HAR_V_71th_a | Aggr 2hr Phase A 71st Voltage Angle Harmonics | float | 2 | R
0x5BA4 | 0x5BA5 | 23460 | 23461 | ANG_2HR_HAR_V_71th_b | Aggr 2hr Phase B 71st Voltage Angle Harmonics | float | 2 | R
0x5BA6 | 0x5BA7 | 23462 | 23463 | ANG_2HR_HAR_V_71th_c | Aggr 2hr Phase C 71st Voltage Angle Harmonics | float | 2 | R
0x5BA8 | 0x5BA9 | 23464 | 23465 | ANG_2HR_HAR_I_71th_a | Aggr 2hr Phase A 71st Current Angle Harmonics | float | 2 | R
0x5BAA | 0x5BAB | 23466 | 23467 | ANG_2HR_HAR_I_71th_b | Aggr 2hr Phase B 71st Current Angle Harmonics | float | 2 | R
0x5BAC | 0x5BAD | 23468 | 23469 | ANG_2HR_HAR_I_71th_c | Aggr 2hr Phase C 71st Current Angle Harmonics | float | 2 | R
0x5BAE | 0x5BAF | 23470 | 23471 | ANG_2HR_HAR_I_71th_n | Aggr 2hr Phase N 71st Current Angle Harmonics | float | 2 | R
0x5BB0 | 0x5BB1 | 23472 | 23473 | ANG_2HR_HAR_V_72th_a | Aggr 2hr Phase A 72nd Voltage Angle Harmonics | float | 2 | R
0x5BB2 | 0x5BB3 | 23474 | 23475 | ANG_2HR_HAR_V_72th_b | Aggr 2hr Phase B 72nd Voltage Angle Harmonics | float | 2 | R
0x5BB4 | 0x5BB5 | 23476 | 23477 | ANG_2HR_HAR_V_72th_c | Aggr 2hr Phase C 72nd Voltage Angle Harmonics | float | 2 | R
0x5BB6 | 0x5BB7 | 23478 | 23479 | ANG_2HR_HAR_I_72th_a | Aggr 2hr Phase A 72nd Current Angle Harmonics | float | 2 | R
0x5BB8 | 0x5BB9 | 23480 | 23481 | ANG_2HR_HAR_I_72th_b | Aggr 2hr Phase B 72nd Current Angle Harmonics | float | 2 | R
0x5BBA | 0x5BBB | 23482 | 23483 | ANG_2HR_HAR_I_72th_c | Aggr 2hr Phase C 72nd Current Angle Harmonics | float | 2 | R
0x5BBC | 0x5BBD | 23484 | 23485 | ANG_2HR_HAR_I_72th_n | Aggr 2hr Phase N 72nd Current Angle Harmonics | float | 2 | R
0x5BBE | 0x5BBF | 23486 | 23487 | ANG_2HR_HAR_V_73th_a | Aggr 2hr Phase A 73rd Voltage Angle Harmonics | float | 2 | R
0x5BC0 | 0x5BC1 | 23488 | 23489 | ANG_2HR_HAR_V_73th_b | Aggr 2hr Phase B 73rd Voltage Angle Harmonics | float | 2 | R
0x5BC2 | 0x5BC3 | 23490 | 23491 | ANG_2HR_HAR_V_73th_c | Aggr 2hr Phase C 73rd Voltage Angle Harmonics | float | 2 | R
0x5BC4 | 0x5BC5 | 23492 | 23493 | ANG_2HR_HAR_I_73th_a | Aggr 2hr Phase A 73rd Current Angle Harmonics | float | 2 | R
0x5BC6 | 0x5BC7 | 23494 | 23495 | ANG_2HR_HAR_I_73th_b | Aggr 2hr Phase B 73rd Current Angle Harmonics | float | 2 | R
0x5BC8 | 0x5BC9 | 23496 | 23497 | ANG_2HR_HAR_I_73th_c | Aggr 2hr Phase C 73rd Current Angle Harmonics | float | 2 | R
0x5BCA | 0x5BCB | 23498 | 23499 | ANG_2HR_HAR_I_73th_n | Aggr 2hr Phase N 73rd Current Angle Harmonics | float | 2 | R
0x5BCC | 0x5BCD | 23500 | 23501 | ANG_2HR_HAR_V_74th_a | Aggr 2hr Phase A 74th Voltage Angle Harmonics | float | 2 | R
0x5BCE | 0x5BCF | 23502 | 23503 | ANG_2HR_HAR_V_74th_b | Aggr 2hr Phase B 74th Voltage Angle Harmonics | float | 2 | R
0x5BD0 | 0x5BD1 | 23504 | 23505 | ANG_2HR_HAR_V_74th_c | Aggr 2hr Phase C 74th Voltage Angle Harmonics | float | 2 | R
0x5BD2 | 0x5BD3 | 23506 | 23507 | ANG_2HR_HAR_I_74th_a | Aggr 2hr Phase A 74th Current Angle Harmonics | float | 2 | R
0x5BD4 | 0x5BD5 | 23508 | 23509 | ANG_2HR_HAR_I_74th_b | Aggr 2hr Phase B 74th Current Angle Harmonics | float | 2 | R
0x5BD6 | 0x5BD7 | 23510 | 23511 | ANG_2HR_HAR_I_74th_c | Aggr 2hr Phase C 74th Current Angle Harmonics | float | 2 | R
0x5BD8 | 0x5BD9 | 23512 | 23513 | ANG_2HR_HAR_I_74th_n | Aggr 2hr Phase N 74th Current Angle Harmonics | float | 2 | R
0x5BDA | 0x5BDB | 23514 | 23515 | ANG_2HR_HAR_V_75th_a | Aggr 2hr Phase A 75th Voltage Angle Harmonics | float | 2 | R
0x5BDC | 0x5BDD | 23516 | 23517 | ANG_2HR_HAR_V_75th_b | Aggr 2hr Phase B 75th Voltage Angle Harmonics | float | 2 | R
0x5BDE | 0x5BDF | 23518 | 23519 | ANG_2HR_HAR_V_75th_c | Aggr 2hr Phase C 75th Voltage Angle Harmonics | float | 2 | R
0x5BE0 | 0x5BE1 | 23520 | 23521 | ANG_2HR_HAR_I_75th_a | Aggr 2hr Phase A 75th Current Angle Harmonics | float | 2 | R
0x5BE2 | 0x5BE3 | 23522 | 23523 | ANG_2HR_HAR_I_75th_b | Aggr 2hr Phase B 75th Current Angle Harmonics | float | 2 | R
0x5BE4 | 0x5BE5 | 23524 | 23525 | ANG_2HR_HAR_I_75th_c | Aggr 2hr Phase C 75th Current Angle Harmonics | float | 2 | R
0x5BE6 | 0x5BE7 | 23526 | 23527 | ANG_2HR_HAR_I_75th_n | Aggr 2hr Phase N 75th Current Angle Harmonics | float | 2 | R
0x5BE8 | 0x5BE9 | 23528 | 23529 | ANG_2HR_HAR_V_76th_a | Aggr 2hr Phase A 76th Voltage Angle Harmonics | float | 2 | R
0x5BEA | 0x5BEB | 23530 | 23531 | ANG_2HR_HAR_V_76th_b | Aggr 2hr Phase B 76th Voltage Angle Harmonics | float | 2 | R
0x5BEC | 0x5BED | 23532 | 23533 | ANG_2HR_HAR_V_76th_c | Aggr 2hr Phase C 76th Voltage Angle Harmonics | float | 2 | R
0x5BEE | 0x5BEF | 23534 | 23535 | ANG_2HR_HAR_I_76th_a | Aggr 2hr Phase A 76th Current Angle Harmonics | float | 2 | R
0x5BF0 | 0x5BF1 | 23536 | 23537 | ANG_2HR_HAR_I_76th_b | Aggr 2hr Phase B 76th Current Angle Harmonics | float | 2 | R
0x5BF2 | 0x5BF3 | 23538 | 23539 | ANG_2HR_HAR_I_76th_c | Aggr 2hr Phase C 76th Current Angle Harmonics | float | 2 | R
0x5BF4 | 0x5BF5 | 23540 | 23541 | ANG_2HR_HAR_I_76th_n | Aggr 2hr Phase N 76th Current Angle Harmonics | float | 2 | R
0x5BF6 | 0x5BF7 | 23542 | 23543 | ANG_2HR_HAR_V_77th_a | Aggr 2hr Phase A 77th Voltage Angle Harmonics | float | 2 | R
0x5BF8 | 0x5BF9 | 23544 | 23545 | ANG_2HR_HAR_V_77th_b | Aggr 2hr Phase B 77th Voltage Angle Harmonics | float | 2 | R
0x5BFA | 0x5BFB | 23546 | 23547 | ANG_2HR_HAR_V_77th_c | Aggr 2hr Phase C 77th Voltage Angle Harmonics | float | 2 | R
0x5BFC | 0x5BFD | 23548 | 23549 | ANG_2HR_HAR_I_77th_a | Aggr 2hr Phase A 77th Current Angle Harmonics | float | 2 | R
0x5BFE | 0x5BFF | 23550 | 23551 | ANG_2HR_HAR_I_77th_b | Aggr 2hr Phase B 77th Current Angle Harmonics | float | 2 | R
0x5C00 | 0x5C01 | 23552 | 23553 | ANG_2HR_HAR_I_77th_c | Aggr 2hr Phase C 77th Current Angle Harmonics | float | 2 | R
0x5C02 | 0x5C03 | 23554 | 23555 | ANG_2HR_HAR_I_77th_n | Aggr 2hr Phase N 77th Current Angle Harmonics | float | 2 | R
0x5C04 | 0x5C05 | 23556 | 23557 | ANG_2HR_HAR_V_78th_a | Aggr 2hr Phase A 78th Voltage Angle Harmonics | float | 2 | R
0x5C06 | 0x5C07 | 23558 | 23559 | ANG_2HR_HAR_V_78th_b | Aggr 2hr Phase B 78th Voltage Angle Harmonics | float | 2 | R
0x5C08 | 0x5C09 | 23560 | 23561 | ANG_2HR_HAR_V_78th_c | Aggr 2hr Phase C 78th Voltage Angle Harmonics | float | 2 | R
0x5C0A | 0x5C0B | 23562 | 23563 | ANG_2HR_HAR_I_78th_a | Aggr 2hr Phase A 78th Current Angle Harmonics | float | 2 | R
0x5C0C | 0x5C0D | 23564 | 23565 | ANG_2HR_HAR_I_78th_b | Aggr 2hr Phase B 78th Current Angle Harmonics | float | 2 | R
0x5C0E | 0x5C0F | 23566 | 23567 | ANG_2HR_HAR_I_78th_c | Aggr 2hr Phase C 78th Current Angle Harmonics | float | 2 | R
0x5C10 | 0x5C11 | 23568 | 23569 | ANG_2HR_HAR_I_78th_n | Aggr 2hr Phase N 78th Current Angle Harmonics | float | 2 | R
0x5C12 | 0x5C13 | 23570 | 23571 | ANG_2HR_HAR_V_79th_a | Aggr 2hr Phase A 79th Voltage Angle Harmonics | float | 2 | R
0x5C14 | 0x5C15 | 23572 | 23573 | ANG_2HR_HAR_V_79th_b | Aggr 2hr Phase B 79th Voltage Angle Harmonics | float | 2 | R
0x5C16 | 0x5C17 | 23574 | 23575 | ANG_2HR_HAR_V_79th_c | Aggr 2hr Phase C 79th Voltage Angle Harmonics | float | 2 | R
0x5C18 | 0x5C19 | 23576 | 23577 | ANG_2HR_HAR_I_79th_a | Aggr 2hr Phase A 79th Current Angle Harmonics | float | 2 | R
0x5C1A | 0x5C1B | 23578 | 23579 | ANG_2HR_HAR_I_79th_b | Aggr 2hr Phase B 79th Current Angle Harmonics | float | 2 | R
0x5C1C | 0x5C1D | 23580 | 23581 | ANG_2HR_HAR_I_79th_c | Aggr 2hr Phase C 79th Current Angle Harmonics | float | 2 | R
0x5C1E | 0x5C1F | 23582 | 23583 | ANG_2HR_HAR_I_79th_n | Aggr 2hr Phase N 79th Current Angle Harmonics | float | 2 | R
0x5C20 | 0x5C21 | 23584 | 23585 | ANG_2HR_HAR_V_80th_a | Aggr 2hr Phase A 80th Voltage Angle Harmonics | float | 2 | R
0x5C22 | 0x5C23 | 23586 | 23587 | ANG_2HR_HAR_V_80th_b | Aggr 2hr Phase B 80th Voltage Angle Harmonics | float | 2 | R
0x5C24 | 0x5C25 | 23588 | 23589 | ANG_2HR_HAR_V_80th_c | Aggr 2hr Phase C 80th Voltage Angle Harmonics | float | 2 | R
0x5C26 | 0x5C27 | 23590 | 23591 | ANG_2HR_HAR_I_80th_a | Aggr 2hr Phase A 80th Current Angle Harmonics | float | 2 | R
0x5C28 | 0x5C29 | 23592 | 23593 | ANG_2HR_HAR_I_80th_b | Aggr 2hr Phase B 80th Current Angle Harmonics | float | 2 | R
0x5C2A | 0x5C2B | 23594 | 23595 | ANG_2HR_HAR_I_80th_c | Aggr 2hr Phase C 80th Current Angle Harmonics | float | 2 | R
0x5C2C | 0x5C2D | 23596 | 23597 | ANG_2HR_HAR_I_80th_n | Aggr 2hr Phase N 80th Current Angle Harmonics | float | 2 | R
0x5C2E | 0x5C2F | 23598 | 23599 | ANG_2HR_HAR_V_81th_a | Aggr 2hr Phase A 81st Voltage Angle Harmonics | float | 2 | R
0x5C30 | 0x5C31 | 23600 | 23601 | ANG_2HR_HAR_V_81th_b | Aggr 2hr Phase B 81st Voltage Angle Harmonics | float | 2 | R
0x5C32 | 0x5C33 | 23602 | 23603 | ANG_2HR_HAR_V_81th_c | Aggr 2hr Phase C 81st Voltage Angle Harmonics | float | 2 | R
0x5C34 | 0x5C35 | 23604 | 23605 | ANG_2HR_HAR_I_81th_a | Aggr 2hr Phase A 81st Current Angle Harmonics | float | 2 | R
0x5C36 | 0x5C37 | 23606 | 23607 | ANG_2HR_HAR_I_81th_b | Aggr 2hr Phase B 81st Current Angle Harmonics | float | 2 | R
0x5C38 | 0x5C39 | 23608 | 23609 | ANG_2HR_HAR_I_81th_c | Aggr 2hr Phase C 81st Current Angle Harmonics | float | 2 | R
0x5C3A | 0x5C3B | 23610 | 23611 | ANG_2HR_HAR_I_81th_n | Aggr 2hr Phase N 81st Current Angle Harmonics | float | 2 | R
0x5C3C | 0x5C3D | 23612 | 23613 | ANG_2HR_HAR_V_82th_a | Aggr 2hr Phase A 82nd Voltage Angle Harmonics | float | 2 | R
0x5C3E | 0x5C3F | 23614 | 23615 | ANG_2HR_HAR_V_82th_b | Aggr 2hr Phase B 82nd Voltage Angle Harmonics | float | 2 | R
0x5C40 | 0x5C41 | 23616 | 23617 | ANG_2HR_HAR_V_82th_c | Aggr 2hr Phase C 82nd Voltage Angle Harmonics | float | 2 | R
0x5C42 | 0x5C43 | 23618 | 23619 | ANG_2HR_HAR_I_82th_a | Aggr 2hr Phase A 82nd Current Angle Harmonics | float | 2 | R
0x5C44 | 0x5C45 | 23620 | 23621 | ANG_2HR_HAR_I_82th_b | Aggr 2hr Phase B 82nd Current Angle Harmonics | float | 2 | R
0x5C46 | 0x5C47 | 23622 | 23623 | ANG_2HR_HAR_I_82th_c | Aggr 2hr Phase C 82nd Current Angle Harmonics | float | 2 | R
0x5C48 | 0x5C49 | 23624 | 23625 | ANG_2HR_HAR_I_82th_n | Aggr 2hr Phase N 82nd Current Angle Harmonics | float | 2 | R
0x5C4A | 0x5C4B | 23626 | 23627 | ANG_2HR_HAR_V_83th_a | Aggr 2hr Phase A 83rd Voltage Angle Harmonics | float | 2 | R
0x5C4C | 0x5C4D | 23628 | 23629 | ANG_2HR_HAR_V_83th_b | Aggr 2hr Phase B 83rd Voltage Angle Harmonics | float | 2 | R
0x5C4E | 0x5C4F | 23630 | 23631 | ANG_2HR_HAR_V_83th_c | Aggr 2hr Phase C 83rd Voltage Angle Harmonics | float | 2 | R
0x5C50 | 0x5C51 | 23632 | 23633 | ANG_2HR_HAR_I_83th_a | Aggr 2hr Phase A 83rd Current Angle Harmonics | float | 2 | R
0x5C52 | 0x5C53 | 23634 | 23635 | ANG_2HR_HAR_I_83th_b | Aggr 2hr Phase B 83rd Current Angle Harmonics | float | 2 | R
0x5C54 | 0x5C55 | 23636 | 23637 | ANG_2HR_HAR_I_83th_c | Aggr 2hr Phase C 83rd Current Angle Harmonics | float | 2 | R
0x5C56 | 0x5C57 | 23638 | 23639 | ANG_2HR_HAR_I_83th_n | Aggr 2hr Phase N 83rd Current Angle Harmonics | float | 2 | R
0x5C58 | 0x5C59 | 23640 | 23641 | ANG_2HR_HAR_V_84th_a | Aggr 2hr Phase A 84th Voltage Angle Harmonics | float | 2 | R
0x5C5A | 0x5C5B | 23642 | 23643 | ANG_2HR_HAR_V_84th_b | Aggr 2hr Phase B 84th Voltage Angle Harmonics | float | 2 | R
0x5C5C | 0x5C5D | 23644 | 23645 | ANG_2HR_HAR_V_84th_c | Aggr 2hr Phase C 84th Voltage Angle Harmonics | float | 2 | R
0x5C5E | 0x5C5F | 23646 | 23647 | ANG_2HR_HAR_I_84th_a | Aggr 2hr Phase A 84th Current Angle Harmonics | float | 2 | R
0x5C60 | 0x5C61 | 23648 | 23649 | ANG_2HR_HAR_I_84th_b | Aggr 2hr Phase B 84th Current Angle Harmonics | float | 2 | R
0x5C62 | 0x5C63 | 23650 | 23651 | ANG_2HR_HAR_I_84th_c | Aggr 2hr Phase C 84th Current Angle Harmonics | float | 2 | R
0x5C64 | 0x5C65 | 23652 | 23653 | ANG_2HR_HAR_I_84th_n | Aggr 2hr Phase N 84th Current Angle Harmonics | float | 2 | R
0x5C66 | 0x5C67 | 23654 | 23655 | ANG_2HR_HAR_V_85th_a | Aggr 2hr Phase A 85th Voltage Angle Harmonics | float | 2 | R
0x5C68 | 0x5C69 | 23656 | 23657 | ANG_2HR_HAR_V_85th_b | Aggr 2hr Phase B 85th Voltage Angle Harmonics | float | 2 | R
0x5C6A | 0x5C6B | 23658 | 23659 | ANG_2HR_HAR_V_85th_c | Aggr 2hr Phase C 85th Voltage Angle Harmonics | float | 2 | R
0x5C6C | 0x5C6D | 23660 | 23661 | ANG_2HR_HAR_I_85th_a | Aggr 2hr Phase A 85th Current Angle Harmonics | float | 2 | R
0x5C6E | 0x5C6F | 23662 | 23663 | ANG_2HR_HAR_I_85th_b | Aggr 2hr Phase B 85th Current Angle Harmonics | float | 2 | R
0x5C70 | 0x5C71 | 23664 | 23665 | ANG_2HR_HAR_I_85th_c | Aggr 2hr Phase C 85th Current Angle Harmonics | float | 2 | R
0x5C72 | 0x5C73 | 23666 | 23667 | ANG_2HR_HAR_I_85th_n | Aggr 2hr Phase N 85th Current Angle Harmonics | float | 2 | R
0x5C74 | 0x5C75 | 23668 | 23669 | ANG_2HR_HAR_V_86th_a | Aggr 2hr Phase A 86th Voltage Angle Harmonics | float | 2 | R
0x5C76 | 0x5C77 | 23670 | 23671 | ANG_2HR_HAR_V_86th_b | Aggr 2hr Phase B 86th Voltage Angle Harmonics | float | 2 | R
0x5C78 | 0x5C79 | 23672 | 23673 | ANG_2HR_HAR_V_86th_c | Aggr 2hr Phase C 86th Voltage Angle Harmonics | float | 2 | R
0x5C7A | 0x5C7B | 23674 | 23675 | ANG_2HR_HAR_I_86th_a | Aggr 2hr Phase A 86th Current Angle Harmonics | float | 2 | R
0x5C7C | 0x5C7D | 23676 | 23677 | ANG_2HR_HAR_I_86th_b | Aggr 2hr Phase B 86th Current Angle Harmonics | float | 2 | R
0x5C7E | 0x5C7F | 23678 | 23679 | ANG_2HR_HAR_I_86th_c | Aggr 2hr Phase C 86th Current Angle Harmonics | float | 2 | R
0x5C80 | 0x5C81 | 23680 | 23681 | ANG_2HR_HAR_I_86th_n | Aggr 2hr Phase N 86th Current Angle Harmonics | float | 2 | R
0x5C82 | 0x5C83 | 23682 | 23683 | ANG_2HR_HAR_V_87th_a | Aggr 2hr Phase A 87th Voltage Angle Harmonics | float | 2 | R
0x5C84 | 0x5C85 | 23684 | 23685 | ANG_2HR_HAR_V_87th_b | Aggr 2hr Phase B 87th Voltage Angle Harmonics | float | 2 | R
0x5C86 | 0x5C87 | 23686 | 23687 | ANG_2HR_HAR_V_87th_c | Aggr 2hr Phase C 87th Voltage Angle Harmonics | float | 2 | R
0x5C88 | 0x5C89 | 23688 | 23689 | ANG_2HR_HAR_I_87th_a | Aggr 2hr Phase A 87th Current Angle Harmonics | float | 2 | R
0x5C8A | 0x5C8B | 23690 | 23691 | ANG_2HR_HAR_I_87th_b | Aggr 2hr Phase B 87th Current Angle Harmonics | float | 2 | R
0x5C8C | 0x5C8D | 23692 | 23693 | ANG_2HR_HAR_I_87th_c | Aggr 2hr Phase C 87th Current Angle Harmonics | float | 2 | R
0x5C8E | 0x5C8F | 23694 | 23695 | ANG_2HR_HAR_I_87th_n | Aggr 2hr Phase N 87th Current Angle Harmonics | float | 2 | R
0x5C90 | 0x5C91 | 23696 | 23697 | ANG_2HR_HAR_V_88th_a | Aggr 2hr Phase A 88th Voltage Angle Harmonics | float | 2 | R
0x5C92 | 0x5C93 | 23698 | 23699 | ANG_2HR_HAR_V_88th_b | Aggr 2hr Phase B 88th Voltage Angle Harmonics | float | 2 | R
0x5C94 | 0x5C95 | 23700 | 23701 | ANG_2HR_HAR_V_88th_c | Aggr 2hr Phase C 88th Voltage Angle Harmonics | float | 2 | R
0x5C96 | 0x5C97 | 23702 | 23703 | ANG_2HR_HAR_I_88th_a | Aggr 2hr Phase A 88th Current Angle Harmonics | float | 2 | R
0x5C98 | 0x5C99 | 23704 | 23705 | ANG_2HR_HAR_I_88th_b | Aggr 2hr Phase B 88th Current Angle Harmonics | float | 2 | R
0x5C9A | 0x5C9B | 23706 | 23707 | ANG_2HR_HAR_I_88th_c | Aggr 2hr Phase C 88th Current Angle Harmonics | float | 2 | R
0x5C9C | 0x5C9D | 23708 | 23709 | ANG_2HR_HAR_I_88th_n | Aggr 2hr Phase N 88th Current Angle Harmonics | float | 2 | R
0x5C9E | 0x5C9F | 23710 | 23711 | ANG_2HR_HAR_V_89th_a | Aggr 2hr Phase A 89th Voltage Angle Harmonics | float | 2 | R
0x5CA0 | 0x5CA1 | 23712 | 23713 | ANG_2HR_HAR_V_89th_b | Aggr 2hr Phase B 89th Voltage Angle Harmonics | float | 2 | R
0x5CA2 | 0x5CA3 | 23714 | 23715 | ANG_2HR_HAR_V_89th_c | Aggr 2hr Phase C 89th Voltage Angle Harmonics | float | 2 | R
0x5CA4 | 0x5CA5 | 23716 | 23717 | ANG_2HR_HAR_I_89th_a | Aggr 2hr Phase A 89th Current Angle Harmonics | float | 2 | R
0x5CA6 | 0x5CA7 | 23718 | 23719 | ANG_2HR_HAR_I_89th_b | Aggr 2hr Phase B 89th Current Angle Harmonics | float | 2 | R
0x5CA8 | 0x5CA9 | 23720 | 23721 | ANG_2HR_HAR_I_89th_c | Aggr 2hr Phase C 89th Current Angle Harmonics | float | 2 | R
0x5CAA | 0x5CAB | 23722 | 23723 | ANG_2HR_HAR_I_89th_n | Aggr 2hr Phase N 89th Current Angle Harmonics | float | 2 | R
0x5CAC | 0x5CAD | 23724 | 23725 | ANG_2HR_HAR_V_90th_a | Aggr 2hr Phase A 90th Voltage Angle Harmonics | float | 2 | R
0x5CAE | 0x5CAF | 23726 | 23727 | ANG_2HR_HAR_V_90th_b | Aggr 2hr Phase B 90th Voltage Angle Harmonics | float | 2 | R
0x5CB0 | 0x5CB1 | 23728 | 23729 | ANG_2HR_HAR_V_90th_c | Aggr 2hr Phase C 90th Voltage Angle Harmonics | float | 2 | R
0x5CB2 | 0x5CB3 | 23730 | 23731 | ANG_2HR_HAR_I_90th_a | Aggr 2hr Phase A 90th Current Angle Harmonics | float | 2 | R
0x5CB4 | 0x5CB5 | 23732 | 23733 | ANG_2HR_HAR_I_90th_b | Aggr 2hr Phase B 90th Current Angle Harmonics | float | 2 | R
0x5CB6 | 0x5CB7 | 23734 | 23735 | ANG_2HR_HAR_I_90th_c | Aggr 2hr Phase C 90th Current Angle Harmonics | float | 2 | R
0x5CB8 | 0x5CB9 | 23736 | 23737 | ANG_2HR_HAR_I_90th_n | Aggr 2hr Phase N 90th Current Angle Harmonics | float | 2 | R
0x5CBA | 0x5CBB | 23738 | 23739 | ANG_2HR_HAR_V_91th_a | Aggr 2hr Phase A 91st Voltage Angle Harmonics | float | 2 | R
0x5CBC | 0x5CBD | 23740 | 23741 | ANG_2HR_HAR_V_91th_b | Aggr 2hr Phase B 91st Voltage Angle Harmonics | float | 2 | R
0x5CBE | 0x5CBF | 23742 | 23743 | ANG_2HR_HAR_V_91th_c | Aggr 2hr Phase C 91st Voltage Angle Harmonics | float | 2 | R
0x5CC0 | 0x5CC1 | 23744 | 23745 | ANG_2HR_HAR_I_91th_a | Aggr 2hr Phase A 91st Current Angle Harmonics | float | 2 | R
0x5CC2 | 0x5CC3 | 23746 | 23747 | ANG_2HR_HAR_I_91th_b | Aggr 2hr Phase B 91st Current Angle Harmonics | float | 2 | R
0x5CC4 | 0x5CC5 | 23748 | 23749 | ANG_2HR_HAR_I_91th_c | Aggr 2hr Phase C 91st Current Angle Harmonics | float | 2 | R
0x5CC6 | 0x5CC7 | 23750 | 23751 | ANG_2HR_HAR_I_91th_n | Aggr 2hr Phase N 91st Current Angle Harmonics | float | 2 | R
0x5CC8 | 0x5CC9 | 23752 | 23753 | ANG_2HR_HAR_V_92th_a | Aggr 2hr Phase A 92nd Voltage Angle Harmonics | float | 2 | R
0x5CCA | 0x5CCB | 23754 | 23755 | ANG_2HR_HAR_V_92th_b | Aggr 2hr Phase B 92nd Voltage Angle Harmonics | float | 2 | R
0x5CCC | 0x5CCD | 23756 | 23757 | ANG_2HR_HAR_V_92th_c | Aggr 2hr Phase C 92nd Voltage Angle Harmonics | float | 2 | R
0x5CCE | 0x5CCF | 23758 | 23759 | ANG_2HR_HAR_I_92th_a | Aggr 2hr Phase A 92nd Current Angle Harmonics | float | 2 | R
0x5CD0 | 0x5CD1 | 23760 | 23761 | ANG_2HR_HAR_I_92th_b | Aggr 2hr Phase B 92nd Current Angle Harmonics | float | 2 | R
0x5CD2 | 0x5CD3 | 23762 | 23763 | ANG_2HR_HAR_I_92th_c | Aggr 2hr Phase C 92nd Current Angle Harmonics | float | 2 | R
0x5CD4 | 0x5CD5 | 23764 | 23765 | ANG_2HR_HAR_I_92th_n | Aggr 2hr Phase N 92nd Current Angle Harmonics | float | 2 | R
0x5CD6 | 0x5CD7 | 23766 | 23767 | ANG_2HR_HAR_V_93th_a | Aggr 2hr Phase A 93rd Voltage Angle Harmonics | float | 2 | R
0x5CD8 | 0x5CD9 | 23768 | 23769 | ANG_2HR_HAR_V_93th_b | Aggr 2hr Phase B 93rd Voltage Angle Harmonics | float | 2 | R
0x5CDA | 0x5CDB | 23770 | 23771 | ANG_2HR_HAR_V_93th_c | Aggr 2hr Phase C 93rd Voltage Angle Harmonics | float | 2 | R
0x5CDC | 0x5CDD | 23772 | 23773 | ANG_2HR_HAR_I_93th_a | Aggr 2hr Phase A 93rd Current Angle Harmonics | float | 2 | R
0x5CDE | 0x5CDF | 23774 | 23775 | ANG_2HR_HAR_I_93th_b | Aggr 2hr Phase B 93rd Current Angle Harmonics | float | 2 | R
0x5CE0 | 0x5CE1 | 23776 | 23777 | ANG_2HR_HAR_I_93th_c | Aggr 2hr Phase C 93rd Current Angle Harmonics | float | 2 | R
0x5CE2 | 0x5CE3 | 23778 | 23779 | ANG_2HR_HAR_I_93th_n | Aggr 2hr Phase N 93rd Current Angle Harmonics | float | 2 | R
0x5CE4 | 0x5CE5 | 23780 | 23781 | ANG_2HR_HAR_V_94th_a | Aggr 2hr Phase A 94th Voltage Angle Harmonics | float | 2 | R
0x5CE6 | 0x5CE7 | 23782 | 23783 | ANG_2HR_HAR_V_94th_b | Aggr 2hr Phase B 94th Voltage Angle Harmonics | float | 2 | R
0x5CE8 | 0x5CE9 | 23784 | 23785 | ANG_2HR_HAR_V_94th_c | Aggr 2hr Phase C 94th Voltage Angle Harmonics | float | 2 | R
0x5CEA | 0x5CEB | 23786 | 23787 | ANG_2HR_HAR_I_94th_a | Aggr 2hr Phase A 94th Current Angle Harmonics | float | 2 | R
0x5CEC | 0x5CED | 23788 | 23789 | ANG_2HR_HAR_I_94th_b | Aggr 2hr Phase B 94th Current Angle Harmonics | float | 2 | R
0x5CEE | 0x5CEF | 23790 | 23791 | ANG_2HR_HAR_I_94th_c | Aggr 2hr Phase C 94th Current Angle Harmonics | float | 2 | R
0x5CF0 | 0x5CF1 | 23792 | 23793 | ANG_2HR_HAR_I_94th_n | Aggr 2hr Phase N 94th Current Angle Harmonics | float | 2 | R
0x5CF2 | 0x5CF3 | 23794 | 23795 | ANG_2HR_HAR_V_95th_a | Aggr 2hr Phase A 95th Voltage Angle Harmonics | float | 2 | R
0x5CF4 | 0x5CF5 | 23796 | 23797 | ANG_2HR_HAR_V_95th_b | Aggr 2hr Phase B 95th Voltage Angle Harmonics | float | 2 | R
0x5CF6 | 0x5CF7 | 23798 | 23799 | ANG_2HR_HAR_V_95th_c | Aggr 2hr Phase C 95th Voltage Angle Harmonics | float | 2 | R
0x5CF8 | 0x5CF9 | 23800 | 23801 | ANG_2HR_HAR_I_95th_a | Aggr 2hr Phase A 95th Current Angle Harmonics | float | 2 | R
0x5CFA | 0x5CFB | 23802 | 23803 | ANG_2HR_HAR_I_95th_b | Aggr 2hr Phase B 95th Current Angle Harmonics | float | 2 | R
0x5CFC | 0x5CFD | 23804 | 23805 | ANG_2HR_HAR_I_95th_c | Aggr 2hr Phase C 95th Current Angle Harmonics | float | 2 | R
0x5CFE | 0x5CFF | 23806 | 23807 | ANG_2HR_HAR_I_95th_n | Aggr 2hr Phase N 95th Current Angle Harmonics | float | 2 | R
0x5D00 | 0x5D01 | 23808 | 23809 | ANG_2HR_HAR_V_96th_a | Aggr 2hr Phase A 96th Voltage Angle Harmonics | float | 2 | R
0x5D02 | 0x5D03 | 23810 | 23811 | ANG_2HR_HAR_V_96th_b | Aggr 2hr Phase B 96th Voltage Angle Harmonics | float | 2 | R
0x5D04 | 0x5D05 | 23812 | 23813 | ANG_2HR_HAR_V_96th_c | Aggr 2hr Phase C 96th Voltage Angle Harmonics | float | 2 | R
0x5D06 | 0x5D07 | 23814 | 23815 | ANG_2HR_HAR_I_96th_a | Aggr 2hr Phase A 96th Current Angle Harmonics | float | 2 | R
0x5D08 | 0x5D09 | 23816 | 23817 | ANG_2HR_HAR_I_96th_b | Aggr 2hr Phase B 96th Current Angle Harmonics | float | 2 | R
0x5D0A | 0x5D0B | 23818 | 23819 | ANG_2HR_HAR_I_96th_c | Aggr 2hr Phase C 96th Current Angle Harmonics | float | 2 | R
0x5D0C | 0x5D0D | 23820 | 23821 | ANG_2HR_HAR_I_96th_n | Aggr 2hr Phase N 96th Current Angle Harmonics | float | 2 | R
0x5D0E | 0x5D0F | 23822 | 23823 | ANG_2HR_HAR_V_97th_a | Aggr 2hr Phase A 97th Voltage Angle Harmonics | float | 2 | R
0x5D10 | 0x5D11 | 23824 | 23825 | ANG_2HR_HAR_V_97th_b | Aggr 2hr Phase B 97th Voltage Angle Harmonics | float | 2 | R
0x5D12 | 0x5D13 | 23826 | 23827 | ANG_2HR_HAR_V_97th_c | Aggr 2hr Phase C 97th Voltage Angle Harmonics | float | 2 | R
0x5D14 | 0x5D15 | 23828 | 23829 | ANG_2HR_HAR_I_97th_a | Aggr 2hr Phase A 97th Current Angle Harmonics | float | 2 | R
0x5D16 | 0x5D17 | 23830 | 23831 | ANG_2HR_HAR_I_97th_b | Aggr 2hr Phase B 97th Current Angle Harmonics | float | 2 | R
0x5D18 | 0x5D19 | 23832 | 23833 | ANG_2HR_HAR_I_97th_c | Aggr 2hr Phase C 97th Current Angle Harmonics | float | 2 | R
0x5D1A | 0x5D1B | 23834 | 23835 | ANG_2HR_HAR_I_97th_n | Aggr 2hr Phase N 97th Current Angle Harmonics | float | 2 | R
0x5D1C | 0x5D1D | 23836 | 23837 | ANG_2HR_HAR_V_98th_a | Aggr 2hr Phase A 98th Voltage Angle Harmonics | float | 2 | R
0x5D1E | 0x5D1F | 23838 | 23839 | ANG_2HR_HAR_V_98th_b | Aggr 2hr Phase B 98th Voltage Angle Harmonics | float | 2 | R
0x5D20 | 0x5D21 | 23840 | 23841 | ANG_2HR_HAR_V_98th_c | Aggr 2hr Phase C 98th Voltage Angle Harmonics | float | 2 | R
0x5D22 | 0x5D23 | 23842 | 23843 | ANG_2HR_HAR_I_98th_a | Aggr 2hr Phase A 98th Current Angle Harmonics | float | 2 | R
0x5D24 | 0x5D25 | 23844 | 23845 | ANG_2HR_HAR_I_98th_b | Aggr 2hr Phase B 98th Current Angle Harmonics | float | 2 | R
0x5D26 | 0x5D27 | 23846 | 23847 | ANG_2HR_HAR_I_98th_c | Aggr 2hr Phase C 98th Current Angle Harmonics | float | 2 | R
0x5D28 | 0x5D29 | 23848 | 23849 | ANG_2HR_HAR_I_98th_n | Aggr 2hr Phase N 98th Current Angle Harmonics | float | 2 | R
0x5D2A | 0x5D2B | 23850 | 23851 | ANG_2HR_HAR_V_99th_a | Aggr 2hr Phase A 99th Voltage Angle Harmonics | float | 2 | R
0x5D2C | 0x5D2D | 23852 | 23853 | ANG_2HR_HAR_V_99th_b | Aggr 2hr Phase B 99th Voltage Angle Harmonics | float | 2 | R
0x5D2E | 0x5D2F | 23854 | 23855 | ANG_2HR_HAR_V_99th_c | Aggr 2hr Phase C 99th Voltage Angle Harmonics | float | 2 | R
0x5D30 | 0x5D31 | 23856 | 23857 | ANG_2HR_HAR_I_99th_a | Aggr 2hr Phase A 99th Current Angle Harmonics | float | 2 | R
0x5D32 | 0x5D33 | 23858 | 23859 | ANG_2HR_HAR_I_99th_b | Aggr 2hr Phase B 99th Current Angle Harmonics | float | 2 | R
0x5D34 | 0x5D35 | 23860 | 23861 | ANG_2HR_HAR_I_99th_c | Aggr 2hr Phase C 99th Current Angle Harmonics | float | 2 | R
0x5D36 | 0x5D37 | 23862 | 23863 | ANG_2HR_HAR_I_99th_n | Aggr 2hr Phase N 99th Current Angle Harmonics | float | 2 | R
0x5D38 | 0x5D39 | 23864 | 23865 | ANG_2HR_HAR_V_100th_a | Aggr 2hr Phase A 100th Voltage Angle Harmonics | float | 2 | R
0x5D3A | 0x5D3B | 23866 | 23867 | ANG_2HR_HAR_V_100th_b | Aggr 2hr Phase B 100th Voltage Angle Harmonics | float | 2 | R
0x5D3C | 0x5D3D | 23868 | 23869 | ANG_2HR_HAR_V_100th_c | Aggr 2hr Phase C 100th Voltage Angle Harmonics | float | 2 | R
0x5D3E | 0x5D3F | 23870 | 23871 | ANG_2HR_HAR_I_100th_a | Aggr 2hr Phase A 100th Current Angle Harmonics | float | 2 | R
0x5D40 | 0x5D41 | 23872 | 23873 | ANG_2HR_HAR_I_100th_b | Aggr 2hr Phase B 100th Current Angle Harmonics | float | 2 | R
0x5D42 | 0x5D43 | 23874 | 23875 | ANG_2HR_HAR_I_100th_c | Aggr 2hr Phase C 100th Current Angle Harmonics | float | 2 | R
0x5D44 | 0x5D45 | 23876 | 23877 | ANG_2HR_HAR_I_100th_n | Aggr 2hr Phase N 100th Current Angle Harmonics | float | 2 | R
0x5D46 | 0x5D47 | 23878 | 23879 | ANG_2HR_HAR_V_101th_a | Aggr 2hr Phase A 101st Voltage Angle Harmonics | float | 2 | R
0x5D48 | 0x5D49 | 23880 | 23881 | ANG_2HR_HAR_V_101th_b | Aggr 2hr Phase B 101st Voltage Angle Harmonics | float | 2 | R
0x5D4A | 0x5D4B | 23882 | 23883 | ANG_2HR_HAR_V_101th_c | Aggr 2hr Phase C 101st Voltage Angle Harmonics | float | 2 | R
0x5D4C | 0x5D4D | 23884 | 23885 | ANG_2HR_HAR_I_101th_a | Aggr 2hr Phase A 101st Current Angle Harmonics | float | 2 | R
0x5D4E | 0x5D4F | 23886 | 23887 | ANG_2HR_HAR_I_101th_b | Aggr 2hr Phase B 101st Current Angle Harmonics | float | 2 | R
0x5D50 | 0x5D51 | 23888 | 23889 | ANG_2HR_HAR_I_101th_c | Aggr 2hr Phase C 101st Current Angle Harmonics | float | 2 | R
0x5D52 | 0x5D53 | 23890 | 23891 | ANG_2HR_HAR_I_101th_n | Aggr 2hr Phase N 101st Current Angle Harmonics | float | 2 | R
0x5D54 | 0x5D55 | 23892 | 23893 | ANG_2HR_HAR_V_102th_a | Aggr 2hr Phase A 102nd Voltage Angle Harmonics | float | 2 | R
0x5D56 | 0x5D57 | 23894 | 23895 | ANG_2HR_HAR_V_102th_b | Aggr 2hr Phase B 102nd Voltage Angle Harmonics | float | 2 | R
0x5D58 | 0x5D59 | 23896 | 23897 | ANG_2HR_HAR_V_102th_c | Aggr 2hr Phase C 102nd Voltage Angle Harmonics | float | 2 | R
0x5D5A | 0x5D5B | 23898 | 23899 | ANG_2HR_HAR_I_102th_a | Aggr 2hr Phase A 102nd Current Angle Harmonics | float | 2 | R
0x5D5C | 0x5D5D | 23900 | 23901 | ANG_2HR_HAR_I_102th_b | Aggr 2hr Phase B 102nd Current Angle Harmonics | float | 2 | R
0x5D5E | 0x5D5F | 23902 | 23903 | ANG_2HR_HAR_I_102th_c | Aggr 2hr Phase C 102nd Current Angle Harmonics | float | 2 | R
0x5D60 | 0x5D61 | 23904 | 23905 | ANG_2HR_HAR_I_102th_n | Aggr 2hr Phase N 102nd Current Angle Harmonics | float | 2 | R
0x5D62 | 0x5D63 | 23906 | 23907 | ANG_2HR_HAR_V_103th_a | Aggr 2hr Phase A 103rd Voltage Angle Harmonics | float | 2 | R
0x5D64 | 0x5D65 | 23908 | 23909 | ANG_2HR_HAR_V_103th_b | Aggr 2hr Phase B 103rd Voltage Angle Harmonics | float | 2 | R
0x5D66 | 0x5D67 | 23910 | 23911 | ANG_2HR_HAR_V_103th_c | Aggr 2hr Phase C 103rd Voltage Angle Harmonics | float | 2 | R
0x5D68 | 0x5D69 | 23912 | 23913 | ANG_2HR_HAR_I_103th_a | Aggr 2hr Phase A 103rd Current Angle Harmonics | float | 2 | R
0x5D6A | 0x5D6B | 23914 | 23915 | ANG_2HR_HAR_I_103th_b | Aggr 2hr Phase B 103rd Current Angle Harmonics | float | 2 | R
0x5D6C | 0x5D6D | 23916 | 23917 | ANG_2HR_HAR_I_103th_c | Aggr 2hr Phase C 103rd Current Angle Harmonics | float | 2 | R
0x5D6E | 0x5D6F | 23918 | 23919 | ANG_2HR_HAR_I_103th_n | Aggr 2hr Phase N 103rd Current Angle Harmonics | float | 2 | R
0x5D70 | 0x5D71 | 23920 | 23921 | ANG_2HR_HAR_V_104th_a | Aggr 2hr Phase A 104th Voltage Angle Harmonics | float | 2 | R
0x5D72 | 0x5D73 | 23922 | 23923 | ANG_2HR_HAR_V_104th_b | Aggr 2hr Phase B 104th Voltage Angle Harmonics | float | 2 | R
0x5D74 | 0x5D75 | 23924 | 23925 | ANG_2HR_HAR_V_104th_c | Aggr 2hr Phase C 104th Voltage Angle Harmonics | float | 2 | R
0x5D76 | 0x5D77 | 23926 | 23927 | ANG_2HR_HAR_I_104th_a | Aggr 2hr Phase A 104th Current Angle Harmonics | float | 2 | R
0x5D78 | 0x5D79 | 23928 | 23929 | ANG_2HR_HAR_I_104th_b | Aggr 2hr Phase B 104th Current Angle Harmonics | float | 2 | R
0x5D7A | 0x5D7B | 23930 | 23931 | ANG_2HR_HAR_I_104th_c | Aggr 2hr Phase C 104th Current Angle Harmonics | float | 2 | R
0x5D7C | 0x5D7D | 23932 | 23933 | ANG_2HR_HAR_I_104th_n | Aggr 2hr Phase N 104th Current Angle Harmonics | float | 2 | R
0x5D7E | 0x5D7F | 23934 | 23935 | ANG_2HR_HAR_V_105th_a | Aggr 2hr Phase A 105th Voltage Angle Harmonics | float | 2 | R
0x5D80 | 0x5D81 | 23936 | 23937 | ANG_2HR_HAR_V_105th_b | Aggr 2hr Phase B 105th Voltage Angle Harmonics | float | 2 | R
0x5D82 | 0x5D83 | 23938 | 23939 | ANG_2HR_HAR_V_105th_c | Aggr 2hr Phase C 105th Voltage Angle Harmonics | float | 2 | R
0x5D84 | 0x5D85 | 23940 | 23941 | ANG_2HR_HAR_I_105th_a | Aggr 2hr Phase A 105th Current Angle Harmonics | float | 2 | R
0x5D86 | 0x5D87 | 23942 | 23943 | ANG_2HR_HAR_I_105th_b | Aggr 2hr Phase B 105th Current Angle Harmonics | float | 2 | R
0x5D88 | 0x5D89 | 23944 | 23945 | ANG_2HR_HAR_I_105th_c | Aggr 2hr Phase C 105th Current Angle Harmonics | float | 2 | R
0x5D8A | 0x5D8B | 23946 | 23947 | ANG_2HR_HAR_I_105th_n | Aggr 2hr Phase N 105th Current Angle Harmonics | float | 2 | R
0x5D8C | 0x5D8D | 23948 | 23949 | ANG_2HR_HAR_V_106th_a | Aggr 2hr Phase A 106th Voltage Angle Harmonics | float | 2 | R
0x5D8E | 0x5D8F | 23950 | 23951 | ANG_2HR_HAR_V_106th_b | Aggr 2hr Phase B 106th Voltage Angle Harmonics | float | 2 | R
0x5D90 | 0x5D91 | 23952 | 23953 | ANG_2HR_HAR_V_106th_c | Aggr 2hr Phase C 106th Voltage Angle Harmonics | float | 2 | R
0x5D92 | 0x5D93 | 23954 | 23955 | ANG_2HR_HAR_I_106th_a | Aggr 2hr Phase A 106th Current Angle Harmonics | float | 2 | R
0x5D94 | 0x5D95 | 23956 | 23957 | ANG_2HR_HAR_I_106th_b | Aggr 2hr Phase B 106th Current Angle Harmonics | float | 2 | R
0x5D96 | 0x5D97 | 23958 | 23959 | ANG_2HR_HAR_I_106th_c | Aggr 2hr Phase C 106th Current Angle Harmonics | float | 2 | R
0x5D98 | 0x5D99 | 23960 | 23961 | ANG_2HR_HAR_I_106th_n | Aggr 2hr Phase N 106th Current Angle Harmonics | float | 2 | R
0x5D9A | 0x5D9B | 23962 | 23963 | ANG_2HR_HAR_V_107th_a | Aggr 2hr Phase A 107th Voltage Angle Harmonics | float | 2 | R
0x5D9C | 0x5D9D | 23964 | 23965 | ANG_2HR_HAR_V_107th_b | Aggr 2hr Phase B 107th Voltage Angle Harmonics | float | 2 | R
0x5D9E | 0x5D9F | 23966 | 23967 | ANG_2HR_HAR_V_107th_c | Aggr 2hr Phase C 107th Voltage Angle Harmonics | float | 2 | R
0x5DA0 | 0x5DA1 | 23968 | 23969 | ANG_2HR_HAR_I_107th_a | Aggr 2hr Phase A 107th Current Angle Harmonics | float | 2 | R
0x5DA2 | 0x5DA3 | 23970 | 23971 | ANG_2HR_HAR_I_107th_b | Aggr 2hr Phase B 107th Current Angle Harmonics | float | 2 | R
0x5DA4 | 0x5DA5 | 23972 | 23973 | ANG_2HR_HAR_I_107th_c | Aggr 2hr Phase C 107th Current Angle Harmonics | float | 2 | R
0x5DA6 | 0x5DA7 | 23974 | 23975 | ANG_2HR_HAR_I_107th_n | Aggr 2hr Phase N 107th Current Angle Harmonics | float | 2 | R
0x5DA8 | 0x5DA9 | 23976 | 23977 | ANG_2HR_HAR_V_108th_a | Aggr 2hr Phase A 108th Voltage Angle Harmonics | float | 2 | R
0x5DAA | 0x5DAB | 23978 | 23979 | ANG_2HR_HAR_V_108th_b | Aggr 2hr Phase B 108th Voltage Angle Harmonics | float | 2 | R
0x5DAC | 0x5DAD | 23980 | 23981 | ANG_2HR_HAR_V_108th_c | Aggr 2hr Phase C 108th Voltage Angle Harmonics | float | 2 | R
0x5DAE | 0x5DAF | 23982 | 23983 | ANG_2HR_HAR_I_108th_a | Aggr 2hr Phase A 108th Current Angle Harmonics | float | 2 | R
0x5DB0 | 0x5DB1 | 23984 | 23985 | ANG_2HR_HAR_I_108th_b | Aggr 2hr Phase B 108th Current Angle Harmonics | float | 2 | R
0x5DB2 | 0x5DB3 | 23986 | 23987 | ANG_2HR_HAR_I_108th_c | Aggr 2hr Phase C 108th Current Angle Harmonics | float | 2 | R
0x5DB4 | 0x5DB5 | 23988 | 23989 | ANG_2HR_HAR_I_108th_n | Aggr 2hr Phase N 108th Current Angle Harmonics | float | 2 | R
0x5DB6 | 0x5DB7 | 23990 | 23991 | ANG_2HR_HAR_V_109th_a | Aggr 2hr Phase A 109th Voltage Angle Harmonics | float | 2 | R
0x5DB8 | 0x5DB9 | 23992 | 23993 | ANG_2HR_HAR_V_109th_b | Aggr 2hr Phase B 109th Voltage Angle Harmonics | float | 2 | R
0x5DBA | 0x5DBB | 23994 | 23995 | ANG_2HR_HAR_V_109th_c | Aggr 2hr Phase C 109th Voltage Angle Harmonics | float | 2 | R
0x5DBC | 0x5DBD | 23996 | 23997 | ANG_2HR_HAR_I_109th_a | Aggr 2hr Phase A 109th Current Angle Harmonics | float | 2 | R
0x5DBE | 0x5DBF | 23998 | 23999 | ANG_2HR_HAR_I_109th_b | Aggr 2hr Phase B 109th Current Angle Harmonics | float | 2 | R
0x5DC0 | 0x5DC1 | 24000 | 24001 | ANG_2HR_HAR_I_109th_c | Aggr 2hr Phase C 109th Current Angle Harmonics | float | 2 | R
0x5DC2 | 0x5DC3 | 24002 | 24003 | ANG_2HR_HAR_I_109th_n | Aggr 2hr Phase N 109th Current Angle Harmonics | float | 2 | R
0x5DC4 | 0x5DC5 | 24004 | 24005 | ANG_2HR_HAR_V_110th_a | Aggr 2hr Phase A 110th Voltage Angle Harmonics | float | 2 | R
0x5DC6 | 0x5DC7 | 24006 | 24007 | ANG_2HR_HAR_V_110th_b | Aggr 2hr Phase B 110th Voltage Angle Harmonics | float | 2 | R
0x5DC8 | 0x5DC9 | 24008 | 24009 | ANG_2HR_HAR_V_110th_c | Aggr 2hr Phase C 110th Voltage Angle Harmonics | float | 2 | R
0x5DCA | 0x5DCB | 24010 | 24011 | ANG_2HR_HAR_I_110th_a | Aggr 2hr Phase A 110th Current Angle Harmonics | float | 2 | R
0x5DCC | 0x5DCD | 24012 | 24013 | ANG_2HR_HAR_I_110th_b | Aggr 2hr Phase B 110th Current Angle Harmonics | float | 2 | R
0x5DCE | 0x5DCF | 24014 | 24015 | ANG_2HR_HAR_I_110th_c | Aggr 2hr Phase C 110th Current Angle Harmonics | float | 2 | R
0x5DD0 | 0x5DD1 | 24016 | 24017 | ANG_2HR_HAR_I_110th_n | Aggr 2hr Phase N 110th Current Angle Harmonics | float | 2 | R
0x5DD2 | 0x5DD3 | 24018 | 24019 | ANG_2HR_HAR_V_111th_a | Aggr 2hr Phase A 111st Voltage Angle Harmonics | float | 2 | R
0x5DD4 | 0x5DD5 | 24020 | 24021 | ANG_2HR_HAR_V_111th_b | Aggr 2hr Phase B 111st Voltage Angle Harmonics | float | 2 | R
0x5DD6 | 0x5DD7 | 24022 | 24023 | ANG_2HR_HAR_V_111th_c | Aggr 2hr Phase C 111st Voltage Angle Harmonics | float | 2 | R
0x5DD8 | 0x5DD9 | 24024 | 24025 | ANG_2HR_HAR_I_111th_a | Aggr 2hr Phase A 111st Current Angle Harmonics | float | 2 | R
0x5DDA | 0x5DDB | 24026 | 24027 | ANG_2HR_HAR_I_111th_b | Aggr 2hr Phase B 111st Current Angle Harmonics | float | 2 | R
0x5DDC | 0x5DDD | 24028 | 24029 | ANG_2HR_HAR_I_111th_c | Aggr 2hr Phase C 111st Current Angle Harmonics | float | 2 | R
0x5DDE | 0x5DDF | 24030 | 24031 | ANG_2HR_HAR_I_111th_n | Aggr 2hr Phase N 111st Current Angle Harmonics | float | 2 | R
0x5DE0 | 0x5DE1 | 24032 | 24033 | ANG_2HR_HAR_V_112th_a | Aggr 2hr Phase A 112nd Voltage Angle Harmonics | float | 2 | R
0x5DE2 | 0x5DE3 | 24034 | 24035 | ANG_2HR_HAR_V_112th_b | Aggr 2hr Phase B 112nd Voltage Angle Harmonics | float | 2 | R
0x5DE4 | 0x5DE5 | 24036 | 24037 | ANG_2HR_HAR_V_112th_c | Aggr 2hr Phase C 112nd Voltage Angle Harmonics | float | 2 | R
0x5DE6 | 0x5DE7 | 24038 | 24039 | ANG_2HR_HAR_I_112th_a | Aggr 2hr Phase A 112nd Current Angle Harmonics | float | 2 | R
0x5DE8 | 0x5DE9 | 24040 | 24041 | ANG_2HR_HAR_I_112th_b | Aggr 2hr Phase B 112nd Current Angle Harmonics | float | 2 | R
0x5DEA | 0x5DEB | 24042 | 24043 | ANG_2HR_HAR_I_112th_c | Aggr 2hr Phase C 112nd Current Angle Harmonics | float | 2 | R
0x5DEC | 0x5DED | 24044 | 24045 | ANG_2HR_HAR_I_112th_n | Aggr 2hr Phase N 112nd Current Angle Harmonics | float | 2 | R
0x5DEE | 0x5DEF | 24046 | 24047 | ANG_2HR_HAR_V_113th_a | Aggr 2hr Phase A 113rd Voltage Angle Harmonics | float | 2 | R
0x5DF0 | 0x5DF1 | 24048 | 24049 | ANG_2HR_HAR_V_113th_b | Aggr 2hr Phase B 113rd Voltage Angle Harmonics | float | 2 | R
0x5DF2 | 0x5DF3 | 24050 | 24051 | ANG_2HR_HAR_V_113th_c | Aggr 2hr Phase C 113rd Voltage Angle Harmonics | float | 2 | R
0x5DF4 | 0x5DF5 | 24052 | 24053 | ANG_2HR_HAR_I_113th_a | Aggr 2hr Phase A 113rd Current Angle Harmonics | float | 2 | R
0x5DF6 | 0x5DF7 | 24054 | 24055 | ANG_2HR_HAR_I_113th_b | Aggr 2hr Phase B 113rd Current Angle Harmonics | float | 2 | R
0x5DF8 | 0x5DF9 | 24056 | 24057 | ANG_2HR_HAR_I_113th_c | Aggr 2hr Phase C 113rd Current Angle Harmonics | float | 2 | R
0x5DFA | 0x5DFB | 24058 | 24059 | ANG_2HR_HAR_I_113th_n | Aggr 2hr Phase N 113rd Current Angle Harmonics | float | 2 | R
0x5DFC | 0x5DFD | 24060 | 24061 | ANG_2HR_HAR_V_114th_a | Aggr 2hr Phase A 114th Voltage Angle Harmonics | float | 2 | R
0x5DFE | 0x5DFF | 24062 | 24063 | ANG_2HR_HAR_V_114th_b | Aggr 2hr Phase B 114th Voltage Angle Harmonics | float | 2 | R
0x5E00 | 0x5E01 | 24064 | 24065 | ANG_2HR_HAR_V_114th_c | Aggr 2hr Phase C 114th Voltage Angle Harmonics | float | 2 | R
0x5E02 | 0x5E03 | 24066 | 24067 | ANG_2HR_HAR_I_114th_a | Aggr 2hr Phase A 114th Current Angle Harmonics | float | 2 | R
0x5E04 | 0x5E05 | 24068 | 24069 | ANG_2HR_HAR_I_114th_b | Aggr 2hr Phase B 114th Current Angle Harmonics | float | 2 | R
0x5E06 | 0x5E07 | 24070 | 24071 | ANG_2HR_HAR_I_114th_c | Aggr 2hr Phase C 114th Current Angle Harmonics | float | 2 | R
0x5E08 | 0x5E09 | 24072 | 24073 | ANG_2HR_HAR_I_114th_n | Aggr 2hr Phase N 114th Current Angle Harmonics | float | 2 | R
0x5E0A | 0x5E0B | 24074 | 24075 | ANG_2HR_HAR_V_115th_a | Aggr 2hr Phase A 115th Voltage Angle Harmonics | float | 2 | R
0x5E0C | 0x5E0D | 24076 | 24077 | ANG_2HR_HAR_V_115th_b | Aggr 2hr Phase B 115th Voltage Angle Harmonics | float | 2 | R
0x5E0E | 0x5E0F | 24078 | 24079 | ANG_2HR_HAR_V_115th_c | Aggr 2hr Phase C 115th Voltage Angle Harmonics | float | 2 | R
0x5E10 | 0x5E11 | 24080 | 24081 | ANG_2HR_HAR_I_115th_a | Aggr 2hr Phase A 115th Current Angle Harmonics | float | 2 | R
0x5E12 | 0x5E13 | 24082 | 24083 | ANG_2HR_HAR_I_115th_b | Aggr 2hr Phase B 115th Current Angle Harmonics | float | 2 | R
0x5E14 | 0x5E15 | 24084 | 24085 | ANG_2HR_HAR_I_115th_c | Aggr 2hr Phase C 115th Current Angle Harmonics | float | 2 | R
0x5E16 | 0x5E17 | 24086 | 24087 | ANG_2HR_HAR_I_115th_n | Aggr 2hr Phase N 115th Current Angle Harmonics | float | 2 | R
0x5E18 | 0x5E19 | 24088 | 24089 | ANG_2HR_HAR_V_116th_a | Aggr 2hr Phase A 116th Voltage Angle Harmonics | float | 2 | R
0x5E1A | 0x5E1B | 24090 | 24091 | ANG_2HR_HAR_V_116th_b | Aggr 2hr Phase B 116th Voltage Angle Harmonics | float | 2 | R
0x5E1C | 0x5E1D | 24092 | 24093 | ANG_2HR_HAR_V_116th_c | Aggr 2hr Phase C 116th Voltage Angle Harmonics | float | 2 | R
0x5E1E | 0x5E1F | 24094 | 24095 | ANG_2HR_HAR_I_116th_a | Aggr 2hr Phase A 116th Current Angle Harmonics | float | 2 | R
0x5E20 | 0x5E21 | 24096 | 24097 | ANG_2HR_HAR_I_116th_b | Aggr 2hr Phase B 116th Current Angle Harmonics | float | 2 | R
0x5E22 | 0x5E23 | 24098 | 24099 | ANG_2HR_HAR_I_116th_c | Aggr 2hr Phase C 116th Current Angle Harmonics | float | 2 | R
0x5E24 | 0x5E25 | 24100 | 24101 | ANG_2HR_HAR_I_116th_n | Aggr 2hr Phase N 116th Current Angle Harmonics | float | 2 | R
0x5E26 | 0x5E27 | 24102 | 24103 | ANG_2HR_HAR_V_117th_a | Aggr 2hr Phase A 117th Voltage Angle Harmonics | float | 2 | R
0x5E28 | 0x5E29 | 24104 | 24105 | ANG_2HR_HAR_V_117th_b | Aggr 2hr Phase B 117th Voltage Angle Harmonics | float | 2 | R
0x5E2A | 0x5E2B | 24106 | 24107 | ANG_2HR_HAR_V_117th_c | Aggr 2hr Phase C 117th Voltage Angle Harmonics | float | 2 | R
0x5E2C | 0x5E2D | 24108 | 24109 | ANG_2HR_HAR_I_117th_a | Aggr 2hr Phase A 117th Current Angle Harmonics | float | 2 | R
0x5E2E | 0x5E2F | 24110 | 24111 | ANG_2HR_HAR_I_117th_b | Aggr 2hr Phase B 117th Current Angle Harmonics | float | 2 | R
0x5E30 | 0x5E31 | 24112 | 24113 | ANG_2HR_HAR_I_117th_c | Aggr 2hr Phase C 117th Current Angle Harmonics | float | 2 | R
0x5E32 | 0x5E33 | 24114 | 24115 | ANG_2HR_HAR_I_117th_n | Aggr 2hr Phase N 117th Current Angle Harmonics | float | 2 | R
0x5E34 | 0x5E35 | 24116 | 24117 | ANG_2HR_HAR_V_118th_a | Aggr 2hr Phase A 118th Voltage Angle Harmonics | float | 2 | R
0x5E36 | 0x5E37 | 24118 | 24119 | ANG_2HR_HAR_V_118th_b | Aggr 2hr Phase B 118th Voltage Angle Harmonics | float | 2 | R
0x5E38 | 0x5E39 | 24120 | 24121 | ANG_2HR_HAR_V_118th_c | Aggr 2hr Phase C 118th Voltage Angle Harmonics | float | 2 | R
0x5E3A | 0x5E3B | 24122 | 24123 | ANG_2HR_HAR_I_118th_a | Aggr 2hr Phase A 118th Current Angle Harmonics | float | 2 | R
0x5E3C | 0x5E3D | 24124 | 24125 | ANG_2HR_HAR_I_118th_b | Aggr 2hr Phase B 118th Current Angle Harmonics | float | 2 | R
0x5E3E | 0x5E3F | 24126 | 24127 | ANG_2HR_HAR_I_118th_c | Aggr 2hr Phase C 118th Current Angle Harmonics | float | 2 | R
0x5E40 | 0x5E41 | 24128 | 24129 | ANG_2HR_HAR_I_118th_n | Aggr 2hr Phase N 118th Current Angle Harmonics | float | 2 | R
0x5E42 | 0x5E43 | 24130 | 24131 | ANG_2HR_HAR_V_119th_a | Aggr 2hr Phase A 119th Voltage Angle Harmonics | float | 2 | R
0x5E44 | 0x5E45 | 24132 | 24133 | ANG_2HR_HAR_V_119th_b | Aggr 2hr Phase B 119th Voltage Angle Harmonics | float | 2 | R
0x5E46 | 0x5E47 | 24134 | 24135 | ANG_2HR_HAR_V_119th_c | Aggr 2hr Phase C 119th Voltage Angle Harmonics | float | 2 | R
0x5E48 | 0x5E49 | 24136 | 24137 | ANG_2HR_HAR_I_119th_a | Aggr 2hr Phase A 119th Current Angle Harmonics | float | 2 | R
0x5E4A | 0x5E4B | 24138 | 24139 | ANG_2HR_HAR_I_119th_b | Aggr 2hr Phase B 119th Current Angle Harmonics | float | 2 | R
0x5E4C | 0x5E4D | 24140 | 24141 | ANG_2HR_HAR_I_119th_c | Aggr 2hr Phase C 119th Current Angle Harmonics | float | 2 | R
0x5E4E | 0x5E4F | 24142 | 24143 | ANG_2HR_HAR_I_119th_n | Aggr 2hr Phase N 119th Current Angle Harmonics | float | 2 | R
0x5E50 | 0x5E51 | 24144 | 24145 | ANG_2HR_HAR_V_120th_a | Aggr 2hr Phase A 120th Voltage Angle Harmonics | float | 2 | R
0x5E52 | 0x5E53 | 24146 | 24147 | ANG_2HR_HAR_V_120th_b | Aggr 2hr Phase B 120th Voltage Angle Harmonics | float | 2 | R
0x5E54 | 0x5E55 | 24148 | 24149 | ANG_2HR_HAR_V_120th_c | Aggr 2hr Phase C 120th Voltage Angle Harmonics | float | 2 | R
0x5E56 | 0x5E57 | 24150 | 24151 | ANG_2HR_HAR_I_120th_a | Aggr 2hr Phase A 120th Current Angle Harmonics | float | 2 | R
0x5E58 | 0x5E59 | 24152 | 24153 | ANG_2HR_HAR_I_120th_b | Aggr 2hr Phase B 120th Current Angle Harmonics | float | 2 | R
0x5E5A | 0x5E5B | 24154 | 24155 | ANG_2HR_HAR_I_120th_c | Aggr 2hr Phase C 120th Current Angle Harmonics | float | 2 | R
0x5E5C | 0x5E5D | 24156 | 24157 | ANG_2HR_HAR_I_120th_n | Aggr 2hr Phase N 120th Current Angle Harmonics | float | 2 | R
0x5E5E | 0x5E5F | 24158 | 24159 | ANG_2HR_HAR_V_121th_a | Aggr 2hr Phase A 121st Voltage Angle Harmonics | float | 2 | R
0x5E60 | 0x5E61 | 24160 | 24161 | ANG_2HR_HAR_V_121th_b | Aggr 2hr Phase B 121st Voltage Angle Harmonics | float | 2 | R
0x5E62 | 0x5E63 | 24162 | 24163 | ANG_2HR_HAR_V_121th_c | Aggr 2hr Phase C 121st Voltage Angle Harmonics | float | 2 | R
0x5E64 | 0x5E65 | 24164 | 24165 | ANG_2HR_HAR_I_121th_a | Aggr 2hr Phase A 121st Current Angle Harmonics | float | 2 | R
0x5E66 | 0x5E67 | 24166 | 24167 | ANG_2HR_HAR_I_121th_b | Aggr 2hr Phase B 121st Current Angle Harmonics | float | 2 | R
0x5E68 | 0x5E69 | 24168 | 24169 | ANG_2HR_HAR_I_121th_c | Aggr 2hr Phase C 121st Current Angle Harmonics | float | 2 | R
0x5E6A | 0x5E6B | 24170 | 24171 | ANG_2HR_HAR_I_121th_n | Aggr 2hr Phase N 121st Current Angle Harmonics | float | 2 | R
0x5E6C | 0x5E6D | 24172 | 24173 | ANG_2HR_HAR_V_122th_a | Aggr 2hr Phase A 122nd Voltage Angle Harmonics | float | 2 | R
0x5E6E | 0x5E6F | 24174 | 24175 | ANG_2HR_HAR_V_122th_b | Aggr 2hr Phase B 122nd Voltage Angle Harmonics | float | 2 | R
0x5E70 | 0x5E71 | 24176 | 24177 | ANG_2HR_HAR_V_122th_c | Aggr 2hr Phase C 122nd Voltage Angle Harmonics | float | 2 | R
0x5E72 | 0x5E73 | 24178 | 24179 | ANG_2HR_HAR_I_122th_a | Aggr 2hr Phase A 122nd Current Angle Harmonics | float | 2 | R
0x5E74 | 0x5E75 | 24180 | 24181 | ANG_2HR_HAR_I_122th_b | Aggr 2hr Phase B 122nd Current Angle Harmonics | float | 2 | R
0x5E76 | 0x5E77 | 24182 | 24183 | ANG_2HR_HAR_I_122th_c | Aggr 2hr Phase C 122nd Current Angle Harmonics | float | 2 | R
0x5E78 | 0x5E79 | 24184 | 24185 | ANG_2HR_HAR_I_122th_n | Aggr 2hr Phase N 122nd Current Angle Harmonics | float | 2 | R
0x5E7A | 0x5E7B | 24186 | 24187 | ANG_2HR_HAR_V_123th_a | Aggr 2hr Phase A 123rd Voltage Angle Harmonics | float | 2 | R
0x5E7C | 0x5E7D | 24188 | 24189 | ANG_2HR_HAR_V_123th_b | Aggr 2hr Phase B 123rd Voltage Angle Harmonics | float | 2 | R
0x5E7E | 0x5E7F | 24190 | 24191 | ANG_2HR_HAR_V_123th_c | Aggr 2hr Phase C 123rd Voltage Angle Harmonics | float | 2 | R
0x5E80 | 0x5E81 | 24192 | 24193 | ANG_2HR_HAR_I_123th_a | Aggr 2hr Phase A 123rd Current Angle Harmonics | float | 2 | R
0x5E82 | 0x5E83 | 24194 | 24195 | ANG_2HR_HAR_I_123th_b | Aggr 2hr Phase B 123rd Current Angle Harmonics | float | 2 | R
0x5E84 | 0x5E85 | 24196 | 24197 | ANG_2HR_HAR_I_123th_c | Aggr 2hr Phase C 123rd Current Angle Harmonics | float | 2 | R
0x5E86 | 0x5E87 | 24198 | 24199 | ANG_2HR_HAR_I_123th_n | Aggr 2hr Phase N 123rd Current Angle Harmonics | float | 2 | R
0x5E88 | 0x5E89 | 24200 | 24201 | ANG_2HR_HAR_V_124th_a | Aggr 2hr Phase A 124th Voltage Angle Harmonics | float | 2 | R
0x5E8A | 0x5E8B | 24202 | 24203 | ANG_2HR_HAR_V_124th_b | Aggr 2hr Phase B 124th Voltage Angle Harmonics | float | 2 | R
0x5E8C | 0x5E8D | 24204 | 24205 | ANG_2HR_HAR_V_124th_c | Aggr 2hr Phase C 124th Voltage Angle Harmonics | float | 2 | R
0x5E8E | 0x5E8F | 24206 | 24207 | ANG_2HR_HAR_I_124th_a | Aggr 2hr Phase A 124th Current Angle Harmonics | float | 2 | R
0x5E90 | 0x5E91 | 24208 | 24209 | ANG_2HR_HAR_I_124th_b | Aggr 2hr Phase B 124th Current Angle Harmonics | float | 2 | R
0x5E92 | 0x5E93 | 24210 | 24211 | ANG_2HR_HAR_I_124th_c | Aggr 2hr Phase C 124th Current Angle Harmonics | float | 2 | R
0x5E94 | 0x5E95 | 24212 | 24213 | ANG_2HR_HAR_I_124th_n | Aggr 2hr Phase N 124th Current Angle Harmonics | float | 2 | R
0x5E96 | 0x5E97 | 24214 | 24215 | ANG_2HR_HAR_V_125th_a | Aggr 2hr Phase A 125th Voltage Angle Harmonics | float | 2 | R
0x5E98 | 0x5E99 | 24216 | 24217 | ANG_2HR_HAR_V_125th_b | Aggr 2hr Phase B 125th Voltage Angle Harmonics | float | 2 | R
0x5E9A | 0x5E9B | 24218 | 24219 | ANG_2HR_HAR_V_125th_c | Aggr 2hr Phase C 125th Voltage Angle Harmonics | float | 2 | R
0x5E9C | 0x5E9D | 24220 | 24221 | ANG_2HR_HAR_I_125th_a | Aggr 2hr Phase A 125th Current Angle Harmonics | float | 2 | R
0x5E9E | 0x5E9F | 24222 | 24223 | ANG_2HR_HAR_I_125th_b | Aggr 2hr Phase B 125th Current Angle Harmonics | float | 2 | R
0x5EA0 | 0x5EA1 | 24224 | 24225 | ANG_2HR_HAR_I_125th_c | Aggr 2hr Phase C 125th Current Angle Harmonics | float | 2 | R
0x5EA2 | 0x5EA3 | 24226 | 24227 | ANG_2HR_HAR_I_125th_n | Aggr 2hr Phase N 125th Current Angle Harmonics | float | 2 | R
0x5EA4 | 0x5EA5 | 24228 | 24229 | ANG_2HR_HAR_V_126th_a | Aggr 2hr Phase A 126th Voltage Angle Harmonics | float | 2 | R
0x5EA6 | 0x5EA7 | 24230 | 24231 | ANG_2HR_HAR_V_126th_b | Aggr 2hr Phase B 126th Voltage Angle Harmonics | float | 2 | R
0x5EA8 | 0x5EA9 | 24232 | 24233 | ANG_2HR_HAR_V_126th_c | Aggr 2hr Phase C 126th Voltage Angle Harmonics | float | 2 | R
0x5EAA | 0x5EAB | 24234 | 24235 | ANG_2HR_HAR_I_126th_a | Aggr 2hr Phase A 126th Current Angle Harmonics | float | 2 | R
0x5EAC | 0x5EAD | 24236 | 24237 | ANG_2HR_HAR_I_126th_b | Aggr 2hr Phase B 126th Current Angle Harmonics | float | 2 | R
0x5EAE | 0x5EAF | 24238 | 24239 | ANG_2HR_HAR_I_126th_c | Aggr 2hr Phase C 126th Current Angle Harmonics | float | 2 | R
0x5EB0 | 0x5EB1 | 24240 | 24241 | ANG_2HR_HAR_I_126th_n | Aggr 2hr Phase N 126th Current Angle Harmonics | float | 2 | R
0x5EB2 | 0x5EB3 | 24242 | 24243 | ANG_2HR_HAR_V_127th_a | Aggr 2hr Phase A 127th Voltage Angle Harmonics | float | 2 | R
0x5EB4 | 0x5EB5 | 24244 | 24245 | ANG_2HR_HAR_V_127th_b | Aggr 2hr Phase B 127th Voltage Angle Harmonics | float | 2 | R
0x5EB6 | 0x5EB7 | 24246 | 24247 | ANG_2HR_HAR_V_127th_c | Aggr 2hr Phase C 127th Voltage Angle Harmonics | float | 2 | R
0x5EB8 | 0x5EB9 | 24248 | 24249 | ANG_2HR_HAR_I_127th_a | Aggr 2hr Phase A 127th Current Angle Harmonics | float | 2 | R
0x5EBA | 0x5EBB | 24250 | 24251 | ANG_2HR_HAR_I_127th_b | Aggr 2hr Phase B 127th Current Angle Harmonics | float | 2 | R
0x5EBC | 0x5EBD | 24252 | 24253 | ANG_2HR_HAR_I_127th_c | Aggr 2hr Phase C 127th Current Angle Harmonics | float | 2 | R
0x5EBE | 0x5EBF | 24254 | 24255 | ANG_2HR_HAR_I_127th_n | Aggr 2hr Phase N 127th Current Angle Harmonics | float | 2 | R
0x5EC0 | 0x5EC1 | 24256 | 24257 | FUND_HAR_Va_V | Aggr 2hr Phase A Fundamental Voltage | float | 2 | R
0x5EC2 | 0x5EC3 | 24258 | 24259 | FUND_HAR_Vb_V | Aggr 2hr Phase B Fundamental Voltage | float | 2 | R
0x5EC4 | 0x5EC5 | 24260 | 24261 | FUND_HAR_Vc_V | Aggr 2hr Phase C Fundamental Voltage | float | 2 | R
0x5EC6 | 0x5EC7 | 24262 | 24263 | FUND_HAR_Ia_A | Aggr 2hr Phase A Fundamental Current | float | 2 | R
0x5EC8 | 0x5EC9 | 24264 | 24265 | FUND_HAR_Ib_A | Aggr 2hr Phase B Fundamental Current | float | 2 | R
0x5ECA | 0x5ECB | 24266 | 24267 | FUND_HAR_Ic_A | Aggr 2hr Phase C Fundamental Current | float | 2 | R
0x5ECC | 0x5ECD | 24268 | 24269 | FUND_HAR_In_A | Aggr 2hr Phase N Fundamental Current | float | 2 | R

## Fundamental
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x6000 | 0x6001 | 24576 | 24577 | 200MS_FUND_VLN_a_V | Phase A Fundamental Line-to-Neutral Voltage | float | 2 | R
0x6002 | 0x6003 | 24578 | 24579 | 200MS_FUND_VLN_b_V | Phase B Fundamental Line-to-Neutral Voltage | float | 2 | R
0x6004 | 0x6005 | 24580 | 24581 | 200MS_FUND_VLN_c_V | Phase C Fundamental Line-to-Neutral Voltage | float | 2 | R
0x6006 | 0x6007 | 24582 | 24583 | 200MS_FUND_VLN_avg_V | Average Fundamental Line-to-Neutral Voltage | float | 2 | R
0x6008 | 0x6009 | 24584 | 24585 | 200MS_FUND_VLL_ab_V | Phase AB Fundamental Line-to-Line Voltage | float | 2 | R
0x600A | 0x600B | 24586 | 24587 | 200MS_FUND_VLL_bc_V | Phase BC Fundamental Line-to-Line Voltage | float | 2 | R
0x600C | 0x600D | 24588 | 24589 | 200MS_FUND_VLL_ca_V | Phase CA Fundamental Line-to-Line Voltage | float | 2 | R
0x600E | 0x600F | 24590 | 24591 | 200MS_FUND_VLL_avg_V | Average Fundamental Line-to-Line Voltage | float | 2 | R
0x6010 | 0x6011 | 24592 | 24593 | 200MS_FUND_I_a_A | Phase A Fundamental Line Current | float | 2 | R
0x6012 | 0x6013 | 24594 | 24595 | 200MS_FUND_I_b_A | Phase B Fundamental Line Current | float | 2 | R
0x6014 | 0x6015 | 24596 | 24597 | 200MS_FUND_I_c_A | Phase C Fundamental Line Current | float | 2 | R
0x6016 | 0x6017 | 24598 | 24599 | 200MS_FUND_I_n_A | Phase N Fundamental Line Current | float | 2 | R
0x6018 | 0x6019 | 24600 | 24601 | 200MS_FUND_I_avg_A | Average Fundamental Line Current | float | 2 | R
0x601A | 0x601B | 24602 | 24603 | 200MS_FUND_P_a_kW | Phase A Fundamental Active Power | float | 2 | R
0x601C | 0x601D | 24604 | 24605 | 200MS_FUND_P_b_kW | Phase B Fundamental Active Power | float | 2 | R
0x601E | 0x601F | 24606 | 24607 | 200MS_FUND_P_c_kW | Phase C Fundamental Active Power | float | 2 | R
0x6020 | 0x6021 | 24608 | 24609 | 200MS_FUND_P_kW | System Fundamental Active Power | float | 2 | R
0x6022 | 0x6023 | 24610 | 24611 | 200MS_FUND_Q_a_kvar | Phase A Fundamental Reactive Power | float | 2 | R
0x6024 | 0x6025 | 24612 | 24613 | 200MS_FUND_Q_b_kvar | Phase B Fundamental Reactive Power | float | 2 | R
0x6026 | 0x6027 | 24614 | 24615 | 200MS_FUND_Q_c_kvar | Phase C Fundamental Reactive Power | float | 2 | R
0x6028 | 0x6029 | 24616 | 24617 | 200MS_FUND_Q_kvar | System Fundamental Reactive Power | float | 2 | R
0x602A | 0x602B | 24618 | 24619 | 200MS_FUND_S_a_kVA | Phase A Fundamental Apparent Power | float | 2 | R
0x602C | 0x602D | 24620 | 24621 | 200MS_FUND_S_b_kVA | Phase B Fundamental Apparent Power | float | 2 | R
0x602E | 0x602F | 24622 | 24623 | 200MS_FUND_S_c_kVA | Phase C Fundamental Apparent Power | float | 2 | R
0x6030 | 0x6031 | 24624 | 24625 | 200MS_FUND_S_kVA | System Fundamental Apparent Power | float | 2 | R
0x6032 | 0x6033 | 24626 | 24627 | 200MS_DIS_PF_a | Phase A Displacement Power Factor | float | 2 | R
0x6034 | 0x6035 | 24628 | 24629 | 200MS_DIS_PF_b | Phase B Displacement Power Factor | float | 2 | R
0x6036 | 0x6037 | 24630 | 24631 | 200MS_DIS_PF_c | Phase C Displacement Power Factor | float | 2 | R
0x6038 | 0x6039 | 24632 | 24633 | 200MS_DIS_PF | System Displacement Power Factor | float | 2 | R

## Min Max
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x6B00 | 0x6B01 | 27392 | 27393 | MAX_Freq_Hz | Max System Frequency | float | 2 | R
0x6B02 | 0x6B03 | 27394 | 27395 | MAX_VLN_a_V | Max Phase A Line-to-Neutral Voltage | float | 2 | R
0x6B04 | 0x6B05 | 27396 | 27397 | MAX_VLN_b_V | Max Phase B Line-to-Neutral Voltage | float | 2 | R
0x6B06 | 0x6B07 | 27398 | 27399 | MAX_VLN_c_V | Max Phase C Line-to-Neutral Voltage | float | 2 | R
0x6B08 | 0x6B09 | 27400 | 27401 | MAX_VLN_avg_V | Max Average Line-to-Neutral Voltage | float | 2 | R
0x6B0A | 0x6B0B | 27402 | 27403 | MAX_VLL_ab_V | Max Phase AB Line-to-Line Voltage | float | 2 | R
0x6B0C | 0x6B0D | 27404 | 27405 | MAX_VLL_bc_V | Max Phase BC Line-to-Line Voltage | float | 2 | R
0x6B0E | 0x6B0F | 27406 | 27407 | MAX_VLL_ca_V | Max Phase CA Line-to-Line Voltage | float | 2 | R
0x6B10 | 0x6B11 | 27408 | 27409 | MAX_VLL_avg_V | Max Average Line-to-Line Voltage | float | 2 | R
0x6B12 | 0x6B13 | 27410 | 27411 | MAX_I_a_A | Max Phase A Current | float | 2 | R
0x6B14 | 0x6B15 | 27412 | 27413 | MAX_I_b_A | Max Phase B Current | float | 2 | R
0x6B16 | 0x6B17 | 27414 | 27415 | MAX_I_c_A | Max Phase C Current | float | 2 | R
0x6B18 | 0x6B19 | 27416 | 27417 | MAX_I_n_A | Max Phase N Current | float | 2 | R
0x6B1A | 0x6B1B | 27418 | 27419 | MAX_I_avg_A | Max Average Current | float | 2 | R
0x6B1C | 0x6B1D | 27420 | 27421 | MAX_P_a_kW | Max Phase A Active Power | float | 2 | R
0x6B1E | 0x6B1F | 27422 | 27423 | MAX_P_b_kW | Max Phase B Active Power | float | 2 | R
0x6B20 | 0x6B21 | 27424 | 27425 | MAX_P_c_kW | Max Phase C Active Power | float | 2 | R
0x6B22 | 0x6B23 | 27426 | 27427 | MAX_P_kW | Max System Active Power | float | 2 | R
0x6B24 | 0x6B25 | 27428 | 27429 | MAX_Q_a_kvar | Max Phase A Reactive Power | float | 2 | R
0x6B26 | 0x6B27 | 27430 | 27431 | MAX_Q_b_kvar | Max Phase B Reactive Power | float | 2 | R
0x6B28 | 0x6B29 | 27432 | 27433 | MAX_Q_c_kvar | Max Phase C Reactive Power | float | 2 | R
0x6B2A | 0x6B2B | 27434 | 27435 | MAX_Q_kvar | Max System Reactive Power | float | 2 | R
0x6B2C | 0x6B2D | 27436 | 27437 | MAX_S_a_kVA | Max Phase A Apparent Power | float | 2 | R
0x6B2E | 0x6B2F | 27438 | 27439 | MAX_S_b_kVA | Max Phase B Apparent Power | float | 2 | R
0x6B30 | 0x6B31 | 27440 | 27441 | MAX_S_c_kVA | Max Phase C Apparent Power | float | 2 | R
0x6B32 | 0x6B33 | 27442 | 27443 | MAX_S_kVA | Max System Apparent Power | float | 2 | R
0x6B34 | 0x6B35 | 27444 | 27445 | MAX_LEAD_PF_a | Max Phase A Leading Power Factor | float | 2 | R
0x6B36 | 0x6B37 | 27446 | 27447 | MAX_LEAD_PF_b | Max Phase B Leading Power Factor | float | 2 | R
0x6B38 | 0x6B39 | 27448 | 27449 | MAX_LEAD_PF_c | Max Phase C Leading Power Factor | float | 2 | R
0x6B3A | 0x6B3B | 27450 | 27451 | MAX_LEAD_PF | Max System Leading Power Factor | float | 2 | R
0x6B3C | 0x6B3D | 27452 | 27453 | MAX_LAG_PF_a | Max Phase A Lagging Power Factor | float | 2 | R
0x6B3E | 0x6B3F | 27454 | 27455 | MAX_LAG_PF_b | Max Phase B Lagging Power Factor | float | 2 | R
0x6B40 | 0x6B41 | 27456 | 27457 | MAX_LAG_PF_c | Max Phase C Lagging Power Factor | float | 2 | R
0x6B42 | 0x6B43 | 27458 | 27459 | MAX_LAG_PF | Max System Lagging Power Factor | float | 2 | R
0x6B44 | 0x6B45 | 27460 | 27461 | MAX_UNBL_V_% | Max System Voltage Unbalance Factor | float | 2 | R
0x6B46 | 0x6B47 | 27462 | 27463 | MAX_UNBL_I_% | Max System Current Unbalance Factor | float | 2 | R
0x6B48 | 0x6B4B | 27464 | 27467 | MAX_TIME_FREQ | Max System Frequency Time | time_t | 4 | R
0x6B4C | 0x6B4F | 27468 | 27471 | MAX_TIME_VLN_a | Max Phase A VLN Time | time_t | 4 | R
0x6B50 | 0x6B53 | 27472 | 27475 | MAX_TIME_VLN_b | Max Phase B VLN Time | time_t | 4 | R
0x6B54 | 0x6B57 | 27476 | 27479 | MAX_TIME_VLN_c | Max Phase C VLN Time | time_t | 4 | R
0x6B58 | 0x6B5B | 27480 | 27483 | MAX_TIME_VLN_avg | Max Average VLN Time | time_t | 4 | R
0x6B5C | 0x6B5F | 27484 | 27487 | MAX_TIME_VLL_ab | Max Phase AB VLL Time | time_t | 4 | R
0x6B60 | 0x6B63 | 27488 | 27491 | MAX_TIME_VLL_bc | Max Phase BC VLL Time | time_t | 4 | R
0x6B64 | 0x6B67 | 27492 | 27495 | MAX_TIME_VLL_ca | Max Phase CA VLL Time | time_t | 4 | R
0x6B68 | 0x6B6B | 27496 | 27499 | MAX_TIME_VLL_avg | Max Average VLL Time | time_t | 4 | R
0x6B6C | 0x6B6F | 27500 | 27503 | MAX_TIME_I_a | Max Phase A Current Time | time_t | 4 | R
0x6B70 | 0x6B73 | 27504 | 27507 | MAX_TIME_I_b | Max Phase B Current Time | time_t | 4 | R
0x6B74 | 0x6B77 | 27508 | 27511 | MAX_TIME_I_c | Max Phase C Current Time | time_t | 4 | R
0x6B78 | 0x6B7B | 27512 | 27515 | MAX_TIME_I_n | Max Phase N Current Time | time_t | 4 | R
0x6B7C | 0x6B7F | 27516 | 27519 | MAX_TIME_I_avg | Max Average Current Time | time_t | 4 | R
0x6B80 | 0x6B83 | 27520 | 27523 | MAX_TIME_P_a | Max Phase A Active Power Time | time_t | 4 | R
0x6B84 | 0x6B87 | 27524 | 27527 | MAX_TIME_P_b | Max Phase B Active Power Time | time_t | 4 | R
0x6B88 | 0x6B8B | 27528 | 27531 | MAX_TIME_P_c | Max Phase C Active Power Time | time_t | 4 | R
0x6B8C | 0x6B8F | 27532 | 27535 | MAX_TIME_P | Max System Active Power Time | time_t | 4 | R
0x6B90 | 0x6B93 | 27536 | 27539 | MAX_TIME_Q_a | Max Phase A Reactive Power Time | time_t | 4 | R
0x6B94 | 0x6B97 | 27540 | 27543 | MAX_TIME_Q_b | Max Phase B Reactive Power Time | time_t | 4 | R
0x6B98 | 0x6B9B | 27544 | 27547 | MAX_TIME_Q_c | Max Phase C Reactive Power Time | time_t | 4 | R
0x6B9C | 0x6B9F | 27548 | 27551 | MAX_TIME_Q | Max System Reactive Power Time | time_t | 4 | R
0x6BA0 | 0x6BA3 | 27552 | 27555 | MAX_TIME_S_a | Max Phase A Apparent Power Time | time_t | 4 | R
0x6BA4 | 0x6BA7 | 27556 | 27559 | MAX_TIME_S_b | Max Phase B Apparent Power Time | time_t | 4 | R
0x6BA8 | 0x6BAB | 27560 | 27563 | MAX_TIME_S_c | Max Phase C Apparent Power Time | time_t | 4 | R
0x6BAC | 0x6BAF | 27564 | 27567 | MAX_TIME_S | Max System Apparent Power Time | time_t | 4 | R
0x6BB0 | 0x6BB3 | 27568 | 27571 | MAX_TIME_LEAD_PF_a | Max Phase A Leading Power Factor Time | time_t | 4 | R
0x6BB4 | 0x6BB7 | 27572 | 27575 | MAX_TIME_LEAD_PF_b | Max Phase B Leading Power Factor Time | time_t | 4 | R
0x6BB8 | 0x6BBB | 27576 | 27579 | MAX_TIME_LEAD_PF_c | Max Phase C Leading Power Factor Time | time_t | 4 | R
0x6BBC | 0x6BBF | 27580 | 27583 | MAX_TIME_LEAD_PF | Max System Leading Power Factor Time | time_t | 4 | R
0x6BC0 | 0x6BC3 | 27584 | 27587 | MAX_TIME_LAG_PF_a | Max Phase A Lagging Power Factor Time | time_t | 4 | R
0x6BC4 | 0x6BC7 | 27588 | 27591 | MAX_TIME_LAG_PF_b | Max Phase B Lagging Power Factor Time | time_t | 4 | R
0x6BC8 | 0x6BCB | 27592 | 27595 | MAX_TIME_LAG_PF_c | Max Phase C Lagging Power Factor Time | time_t | 4 | R
0x6BCC | 0x6BCF | 27596 | 27599 | MAX_TIME_LAG_PF | Max System Lagging Power Factor Time | time_t | 4 | R
0x6BD0 | 0x6BD3 | 27600 | 27603 | MAX_TIME_UNBL_V | Max System Unbalance Voltage Time | time_t | 4 | R
0x6BD4 | 0x6BD7 | 27604 | 27607 | MAX_TIME_UNBL_I | Max System Unbalance Current Time | time_t | 4 | R
0x6C00 | 0x6C01 | 27648 | 27649 | MIN_Freq_Hz | Min System Frequency | float | 2 | R
0x6C02 | 0x6C03 | 27650 | 27651 | MIN_VLN_a_V | Min Phase A Line-to-Neutral Voltage | float | 2 | R
0x6C04 | 0x6C05 | 27652 | 27653 | MIN_VLN_b_V | Min Phase B Line-to-Neutral Voltage | float | 2 | R
0x6C06 | 0x6C07 | 27654 | 27655 | MIN_VLN_c_V | Min Phase C Line-to-Neutral Voltage | float | 2 | R
0x6C08 | 0x6C09 | 27656 | 27657 | MIN_VLN_avg_V | Min Average Line-to-Neutral Voltage | float | 2 | R
0x6C0A | 0x6C0B | 27658 | 27659 | MIN_VLL_ab_V | Min Phase AB Line-to-Line Voltage | float | 2 | R
0x6C0C | 0x6C0D | 27660 | 27661 | MIN_VLL_bc_V | Min Phase BC Line-to-Line Voltage | float | 2 | R
0x6C0E | 0x6C0F | 27662 | 27663 | MIN_VLL_ca_V | Min Phase CA Line-to-Line Voltage | float | 2 | R
0x6C10 | 0x6C11 | 27664 | 27665 | MIN_VLL_avg_V | Min Average Line-to-Line Voltage | float | 2 | R
0x6C12 | 0x6C13 | 27666 | 27667 | MIN_I_a_A | Min Phase A Current | float | 2 | R
0x6C14 | 0x6C15 | 27668 | 27669 | MIN_I_b_A | Min Phase B Current | float | 2 | R
0x6C16 | 0x6C17 | 27670 | 27671 | MIN_I_c_A | Min Phase C Current | float | 2 | R
0x6C18 | 0x6C19 | 27672 | 27673 | MIN_I_n_A | Min Phase N Current | float | 2 | R
0x6C1A | 0x6C1B | 27674 | 27675 | MIN_I_avg_A | Min Average Current | float | 2 | R
0x6C1C | 0x6C1D | 27676 | 27677 | MIN_P_a_kW | Min Phase A Active Power | float | 2 | R
0x6C1E | 0x6C1F | 27678 | 27679 | MIN_P_b_kW | Min Phase B Active Power | float | 2 | R
0x6C20 | 0x6C21 | 27680 | 27681 | MIN_P_c_kW | Min Phase C Active Power | float | 2 | R
0x6C22 | 0x6C23 | 27682 | 27683 | MIN_P_kW | Min System Active Power | float | 2 | R
0x6C24 | 0x6C25 | 27684 | 27685 | MIN_Q_a_kvar | Min Phase A Reactive Power | float | 2 | R
0x6C26 | 0x6C27 | 27686 | 27687 | MIN_Q_b_kvar | Min Phase B Reactive Power | float | 2 | R
0x6C28 | 0x6C29 | 27688 | 27689 | MIN_Q_c_kvar | Min Phase C Reactive Power | float | 2 | R
0x6C2A | 0x6C2B | 27690 | 27691 | MIN_Q_kvar | Min System Reactive Power | float | 2 | R
0x6C2C | 0x6C2D | 27692 | 27693 | MIN_S_a_kVA | Min Phase A Apparent Power | float | 2 | R
0x6C2E | 0x6C2F | 27694 | 27695 | MIN_S_b_kVA | Min Phase B Apparent Power | float | 2 | R
0x6C30 | 0x6C31 | 27696 | 27697 | MIN_S_c_kVA | Min Phase C Apparent Power | float | 2 | R
0x6C32 | 0x6C33 | 27698 | 27699 | MIN_S_kVA | Min System Apparent Power | float | 2 | R
0x6C34 | 0x6C35 | 27700 | 27701 | MIN_LEAD_PF_a | Min Phase A Leading Power Factor | float | 2 | R
0x6C36 | 0x6C37 | 27702 | 27703 | MIN_LEAD_PF_b | Min Phase B Leading Power Factor | float | 2 | R
0x6C38 | 0x6C39 | 27704 | 27705 | MIN_LEAD_PF_c | Min Phase C Leading Power Factor | float | 2 | R
0x6C3A | 0x6C3B | 27706 | 27707 | MIN_LEAD_PF | Min System Leading Power Factor | float | 2 | R
0x6C3C | 0x6C3D | 27708 | 27709 | MIN_LAG_PF_a | Min Phase A Lagging Power Factor | float | 2 | R
0x6C3E | 0x6C3F | 27710 | 27711 | MIN_LAG_PF_b | Min Phase B Lagging Power Factor | float | 2 | R
0x6C40 | 0x6C41 | 27712 | 27713 | MIN_LAG_PF_c | Min Phase C Lagging Power Factor | float | 2 | R
0x6C42 | 0x6C43 | 27714 | 27715 | MIN_LAG_PF | Min System Lagging Power Factor | float | 2 | R
0x6C44 | 0x6C45 | 27716 | 27717 | MIN_UNBL_V_% | Min System Voltage Unbalance Factor | float | 2 | R
0x6C46 | 0x6C47 | 27718 | 27719 | MIN_UNBL_I_% | Min System Current Unbalance Factor | float | 2 | R
0x6C48 | 0x6C4B | 27720 | 27723 | MIN_TIME_FREQ | Min System Frequency Time | time_t | 4 | R
0x6C4C | 0x6C4F | 27724 | 27727 | MIN_TIME_VLN_a | Min Phase A VLN Time | time_t | 4 | R
0x6C50 | 0x6C53 | 27728 | 27731 | MIN_TIME_VLN_b | Min Phase B VLN Time | time_t | 4 | R
0x6C54 | 0x6C57 | 27732 | 27735 | MIN_TIME_VLN_c | Min Phase C VLN Time | time_t | 4 | R
0x6C58 | 0x6C5B | 27736 | 27739 | MIN_TIME_VLN_avg | Min Average VLN Time | time_t | 4 | R
0x6C5C | 0x6C5F | 27740 | 27743 | MIN_TIME_VLL_ab | Min Phase AB VLL Time | time_t | 4 | R
0x6C60 | 0x6C63 | 27744 | 27747 | MIN_TIME_VLL_bc | Min Phase BC VLL Time | time_t | 4 | R
0x6C64 | 0x6C67 | 27748 | 27751 | MIN_TIME_VLL_ca | Min Phase CA VLL Time | time_t | 4 | R
0x6C68 | 0x6C6B | 27752 | 27755 | MIN_TIME_VLL_avg | Min Average VLL Time | time_t | 4 | R
0x6C6C | 0x6C6F | 27756 | 27759 | MIN_TIME_I_a | Min Phase A Current Time | time_t | 4 | R
0x6C70 | 0x6C73 | 27760 | 27763 | MIN_TIME_I_b | Min Phase B Current Time | time_t | 4 | R
0x6C74 | 0x6C77 | 27764 | 27767 | MIN_TIME_I_c | Min Phase C Current Time | time_t | 4 | R
0x6C78 | 0x6C7B | 27768 | 27771 | MIN_TIME_I_n | Min Phase N Current Time | time_t | 4 | R
0x6C7C | 0x6C7F | 27772 | 27775 | MIN_TIME_I_avg | Min Average Current Time | time_t | 4 | R
0x6C80 | 0x6C83 | 27776 | 27779 | MIN_TIME_P_a | Min Phase A Active Power Time | time_t | 4 | R
0x6C84 | 0x6C87 | 27780 | 27783 | MIN_TIME_P_b | Min Phase B Active Power Time | time_t | 4 | R
0x6C88 | 0x6C8B | 27784 | 27787 | MIN_TIME_P_c | Min Phase C Active Power Time | time_t | 4 | R
0x6C8C | 0x6C8F | 27788 | 27791 | MIN_TIME_P | Min System Active Power Time | time_t | 4 | R
0x6C90 | 0x6C93 | 27792 | 27795 | MIN_TIME_Q_a | Min Phase A Reactive Power Time | time_t | 4 | R
0x6C94 | 0x6C97 | 27796 | 27799 | MIN_TIME_Q_b | Min Phase B Reactive Power Time | time_t | 4 | R
0x6C98 | 0x6C9B | 27800 | 27803 | MIN_TIME_Q_c | Min Phase C Reactive Power Time | time_t | 4 | R
0x6C9C | 0x6C9F | 27804 | 27807 | MIN_TIME_Q | Min System Reactive Power Time | time_t | 4 | R
0x6CA0 | 0x6CA3 | 27808 | 27811 | MIN_TIME_S_a | Min Phase A Apparent Power Time | time_t | 4 | R
0x6CA4 | 0x6CA7 | 27812 | 27815 | MIN_TIME_S_b | Min Phase B Apparent Power Time | time_t | 4 | R
0x6CA8 | 0x6CAB | 27816 | 27819 | MIN_TIME_S_c | Min Phase C Apparent Power Time | time_t | 4 | R
0x6CAC | 0x6CAF | 27820 | 27823 | MIN_TIME_S | Min System Apparent Power Time | time_t | 4 | R
0x6CB0 | 0x6CB3 | 27824 | 27827 | MIN_TIME_LEAD_PF_a | Min Phase A Leading Power Factor Time | time_t | 4 | R
0x6CB4 | 0x6CB7 | 27828 | 27831 | MIN_TIME_LEAD_PF_b | Min Phase B Leading Power Factor Time | time_t | 4 | R
0x6CB8 | 0x6CBB | 27832 | 27835 | MIN_TIME_LEAD_PF_c | Min Phase C Leading Power Factor Time | time_t | 4 | R
0x6CBC | 0x6CBF | 27836 | 27839 | MIN_TIME_LEAD_PF | Min System Leading Power Factor Time | time_t | 4 | R
0x6CC0 | 0x6CC3 | 27840 | 27843 | MIN_TIME_LAG_PF_a | Min Phase A Lagging Power Factor Time | time_t | 4 | R
0x6CC4 | 0x6CC7 | 27844 | 27847 | MIN_TIME_LAG_PF_b | Min Phase B Lagging Power Factor Time | time_t | 4 | R
0x6CC8 | 0x6CCB | 27848 | 27851 | MIN_TIME_LAG_PF_c | Min Phase C Lagging Power Factor Time | time_t | 4 | R
0x6CCC | 0x6CCF | 27852 | 27855 | MIN_TIME_LAG_PF | Min System Lagging Power Factor Time | time_t | 4 | R
0x6CD0 | 0x6CD3 | 27856 | 27859 | MIN_TIME_UNBL_V | Min System Unbalance Voltage Time | time_t | 4 | R
0x6CD4 | 0x6CD7 | 27860 | 27863 | MIN_TIME_UNBL_I | Min System Unbalance Current Time | time_t | 4 | R

## Mains Signaling Status
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x6E54 | 0x6E54 | 28244 | 28244 | MAINS_SIGNAL_STATUS_a | Phase A Mains Signaling Status | bool | 1 | R |  | 0
0x6E55 | 0x6E55 | 28245 | 28245 | MAINS_SIGNAL_STATUS_b | Phase B Mains Signaling Status | bool | 1 | R |  | 0
0x6E56 | 0x6E56 | 28246 | 28246 | MAINS_SIGNAL_STATUS_c | Phase C Mains Signaling Status | bool | 1 | R |  | 0

## Demand
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x6100 | 0x6101 | 24832 | 24833 | DMD_I_a_A | Phase A Current Demand | float | 2 | R
0x6102 | 0x6103 | 24834 | 24835 | DMD_I_b_A | Phase B Current Demand | float | 2 | R
0x6104 | 0x6105 | 24836 | 24837 | DMD_I_c_A | Phase C Current Demand | float | 2 | R
0x6106 | 0x6107 | 24838 | 24839 | DMD_I_avg_A | Average Current Demand | float | 2 | R
0x6108 | 0x6109 | 24840 | 24841 | DMD_Q1_P_a_kW | Phase A Active Power Demand-Quad 1 | float | 2 | R
0x610A | 0x610B | 24842 | 24843 | DMD_Q1_P_b_kW | Phase B Active Power Demand-Quad 1 | float | 2 | R
0x610C | 0x610D | 24844 | 24845 | DMD_Q1_P_c_kW | Phase C Active Power Demand-Quad 1 | float | 2 | R
0x610E | 0x610F | 24846 | 24847 | DMD_Q1_P_kW | System Active Power Demand-Quad 1 | float | 2 | R
0x6110 | 0x6111 | 24848 | 24849 | DMD_Q1_Q_a_kvar | Phase A Reactive Power Demand-Quad 1 | float | 2 | R
0x6112 | 0x6113 | 24850 | 24851 | DMD_Q1_Q_b_kvar | Phase B Reactive Power Demand-Quad 1 | float | 2 | R
0x6114 | 0x6115 | 24852 | 24853 | DMD_Q1_Q_c_kvar | Phase C Reactive Power Demand-Quad 1 | float | 2 | R
0x6116 | 0x6117 | 24854 | 24855 | DMD_Q1_Q_kvar | System Reactive Power Demand-Quad 1 | float | 2 | R
0x6118 | 0x6119 | 24856 | 24857 | DMD_Q1_S_a_kVA | Phase A Apparent Power Demand-Quad 1 | float | 2 | R
0x611A | 0x611B | 24858 | 24859 | DMD_Q1_S_b_kVA | Phase B Apparent Power Demand-Quad 1 | float | 2 | R
0x611C | 0x611D | 24860 | 24861 | DMD_Q1_S_c_kVA | Phase C Apparent Power Demand-Quad 1 | float | 2 | R
0x611E | 0x611F | 24862 | 24863 | DMD_Q1_S_kVA | System Apparent Power Demand-Quad 1 | float | 2 | R
0x6120 | 0x6121 | 24864 | 24865 | DMD_Q2_P_a_kW | Phase A Active Power Demand-Quad 2 | float | 2 | R
0x6122 | 0x6123 | 24866 | 24867 | DMD_Q2_P_b_kW | Phase B Active Power Demand-Quad 2 | float | 2 | R
0x6124 | 0x6125 | 24868 | 24869 | DMD_Q2_P_c_kW | Phase C Active Power Demand-Quad 2 | float | 2 | R
0x6126 | 0x6127 | 24870 | 24871 | DMD_Q2_P_kW | System Active Power Demand-Quad 2 | float | 2 | R
0x6128 | 0x6129 | 24872 | 24873 | DMD_Q2_Q_a_kvar | Phase A Reactive Power Demand-Quad 2 | float | 2 | R
0x612A | 0x612B | 24874 | 24875 | DMD_Q2_Q_b_kvar | Phase B Reactive Power Demand-Quad 2 | float | 2 | R
0x612C | 0x612D | 24876 | 24877 | DMD_Q2_Q_c_kvar | Phase C Reactive Power Demand-Quad 2 | float | 2 | R
0x612E | 0x612F | 24878 | 24879 | DMD_Q2_Q_kvar | System Reactive Power Demand-Quad 2 | float | 2 | R
0x6130 | 0x6131 | 24880 | 24881 | DMD_Q2_S_a_kVA | Phase A Apparent Power Demand-Quad 2 | float | 2 | R
0x6132 | 0x6133 | 24882 | 24883 | DMD_Q2_S_b_kVA | Phase B Apparent Power Demand-Quad 2 | float | 2 | R
0x6134 | 0x6135 | 24884 | 24885 | DMD_Q2_S_c_kVA | Phase C Apparent Power Demand-Quad 2 | float | 2 | R
0x6136 | 0x6137 | 24886 | 24887 | DMD_Q2_S_kVA | System Apparent Power Demand-Quad 2 | float | 2 | R
0x6138 | 0x6139 | 24888 | 24889 | DMD_Q3_P_a_kW | Phase A Active Power Demand-Quad 3 | float | 2 | R
0x613A | 0x613B | 24890 | 24891 | DMD_Q3_P_b_kW | Phase B Active Power Demand-Quad 3 | float | 2 | R
0x613C | 0x613D | 24892 | 24893 | DMD_Q3_P_c_kW | Phase C Active Power Demand-Quad 3 | float | 2 | R
0x613E | 0x613F | 24894 | 24895 | DMD_Q3_P_kW | System Active Power Demand-Quad 3 | float | 2 | R
0x6140 | 0x6141 | 24896 | 24897 | DMD_Q3_Q_a_kvar | Phase A Reactive Power Demand-Quad 3 | float | 2 | R
0x6142 | 0x6143 | 24898 | 24899 | DMD_Q3_Q_b_kvar | Phase B Reactive Power Demand-Quad 3 | float | 2 | R
0x6144 | 0x6145 | 24900 | 24901 | DMD_Q3_Q_c_kvar | Phase C Reactive Power Demand-Quad 3 | float | 2 | R
0x6146 | 0x6147 | 24902 | 24903 | DMD_Q3_Q_kvar | System Reactive Power Demand-Quad 3 | float | 2 | R
0x6148 | 0x6149 | 24904 | 24905 | DMD_Q3_S_a_kVA | Phase A Apparent Power Demand-Quad 3 | float | 2 | R
0x614A | 0x614B | 24906 | 24907 | DMD_Q3_S_b_kVA | Phase B Apparent Power Demand-Quad 3 | float | 2 | R
0x614C | 0x614D | 24908 | 24909 | DMD_Q3_S_c_kVA | Phase C Apparent Power Demand-Quad 3 | float | 2 | R
0x614E | 0x614F | 24910 | 24911 | DMD_Q3_S_kVA | System Apparent Power Demand-Quad 3 | float | 2 | R
0x6150 | 0x6151 | 24912 | 24913 | DMD_Q4_P_a_kW | Phase A Active Power Demand-Quad 4 | float | 2 | R
0x6152 | 0x6153 | 24914 | 24915 | DMD_Q4_P_b_kW | Phase B Active Power Demand-Quad 4 | float | 2 | R
0x6154 | 0x6155 | 24916 | 24917 | DMD_Q4_P_c_kW | Phase C Active Power Demand-Quad 4 | float | 2 | R
0x6156 | 0x6157 | 24918 | 24919 | DMD_Q4_P_kW | System Active Power Demand-Quad 4 | float | 2 | R
0x6158 | 0x6159 | 24920 | 24921 | DMD_Q4_Q_a_kvar | Phase A Reactive Power Demand-Quad 4 | float | 2 | R
0x615A | 0x615B | 24922 | 24923 | DMD_Q4_Q_b_kvar | Phase B Reactive Power Demand-Quad 4 | float | 2 | R
0x615C | 0x615D | 24924 | 24925 | DMD_Q4_Q_c_kvar | Phase C Reactive Power Demand-Quad 4 | float | 2 | R
0x615E | 0x615F | 24926 | 24927 | DMD_Q4_Q_kvar | System Reactive Power Demand-Quad 4 | float | 2 | R
0x6160 | 0x6161 | 24928 | 24929 | DMD_Q4_S_a_kVA | Phase A Apparent Power Demand-Quad 4 | float | 2 | R
0x6162 | 0x6163 | 24930 | 24931 | DMD_Q4_S_b_kVA | Phase B Apparent Power Demand-Quad 4 | float | 2 | R
0x6164 | 0x6165 | 24932 | 24933 | DMD_Q4_S_c_kVA | Phase C Apparent Power Demand-Quad 4 | float | 2 | R
0x6166 | 0x6167 | 24934 | 24935 | DMD_Q4_S_kVA | System Apparent Power Demand-Quad 4 | float | 2 | R
0x6168 | 0x6169 | 24936 | 24937 | DMD_IMP_P_a_kW | Phase A Active Power Demand-Import | float | 2 | R
0x616A | 0x616B | 24938 | 24939 | DMD_IMP_P_b_kW | Phase B Active Power Demand-Import | float | 2 | R
0x616C | 0x616D | 24940 | 24941 | DMD_IMP_P_c_kW | Phase C Active Power Demand-Import | float | 2 | R
0x616E | 0x616F | 24942 | 24943 | DMD_IMP_P_kW | System Active Power Demand-Import | float | 2 | R
0x6170 | 0x6171 | 24944 | 24945 | DMD_IMP_Q_a_kvar | Phase A Reactive Power Demand-Import | float | 2 | R
0x6172 | 0x6173 | 24946 | 24947 | DMD_IMP_Q_b_kvar | Phase B Reactive Power Demand-Import | float | 2 | R
0x6174 | 0x6175 | 24948 | 24949 | DMD_IMP_Q_c_kvar | Phase C Reactive Power Demand-Import | float | 2 | R
0x6176 | 0x6177 | 24950 | 24951 | DMD_IMP_Q_kvar | System Reactive Power Demand-Import | float | 2 | R
0x6178 | 0x6179 | 24952 | 24953 | DMD_EXP_P_a_kW | Phase A Active Power Demand-Export | float | 2 | R
0x617A | 0x617B | 24954 | 24955 | DMD_EXP_P_b_kW | Phase B Active Power Demand-Export | float | 2 | R
0x617C | 0x617D | 24956 | 24957 | DMD_EXP_P_c_kW | Phase C Active Power Demand-Export | float | 2 | R
0x617E | 0x617F | 24958 | 24959 | DMD_EXP_P_kW | System Active Power Demand-Export | float | 2 | R
0x6180 | 0x6181 | 24960 | 24961 | DMD_EXP_Q_a_kvar | Phase A Reactive Power Demand-Export | float | 2 | R
0x6182 | 0x6183 | 24962 | 24963 | DMD_EXP_Q_b_kvar | Phase B Reactive Power Demand-Export | float | 2 | R
0x6184 | 0x6185 | 24964 | 24965 | DMD_EXP_Q_c_kvar | Phase C Reactive Power Demand-Export | float | 2 | R
0x6186 | 0x6187 | 24966 | 24967 | DMD_EXP_Q_kvar | System Reactive Power Demand-Export | float | 2 | R
0x6188 | 0x6189 | 24968 | 24969 | DMD_NET_P_a_kW | Phase A Active Power Demand-Net | float | 2 | R
0x618A | 0x618B | 24970 | 24971 | DMD_NET_P_b_kW | Phase B Active Power Demand-Net | float | 2 | R
0x618C | 0x618D | 24972 | 24973 | DMD_NET_P_c_kW | Phase C Active Power Demand-Net | float | 2 | R
0x618E | 0x618F | 24974 | 24975 | DMD_NET_P_kW | System Active Power Demand-Net | float | 2 | R
0x6190 | 0x6191 | 24976 | 24977 | DMD_NET_Q_a_kvar | Phase A Reactive Power Demand-Net | float | 2 | R
0x6192 | 0x6193 | 24978 | 24979 | DMD_NET_Q_b_kvar | Phase B Reactive Power Demand-Net | float | 2 | R
0x6194 | 0x6195 | 24980 | 24981 | DMD_NET_Q_c_kvar | Phase C Reactive Power Demand-Net | float | 2 | R
0x6196 | 0x6197 | 24982 | 24983 | DMD_NET_Q_kvar | System Reactive Power Demand-Net | float | 2 | R
0x6198 | 0x6199 | 24984 | 24985 | DMD_TOTAL_P_a_kW | Phase A Active Power Demand-Total | float | 2 | R
0x619A | 0x619B | 24986 | 24987 | DMD_TOTAL_P_b_kW | Phase B Active Power Demand-Total | float | 2 | R
0x619C | 0x619D | 24988 | 24989 | DMD_TOTAL_P_c_kW | Phase C Active Power Demand-Total | float | 2 | R
0x619E | 0x619F | 24990 | 24991 | DMD_TOTAL_P_kW | System Active Power Demand-Total | float | 2 | R
0x61A0 | 0x61A1 | 24992 | 24993 | DMD_TOTAL_Q_a_kvar | Phase A Reactive Power Demand-Total | float | 2 | R
0x61A2 | 0x61A3 | 24994 | 24995 | DMD_TOTAL_Q_b_kvar | Phase B Reactive Power Demand-Total | float | 2 | R
0x61A4 | 0x61A5 | 24996 | 24997 | DMD_TOTAL_Q_c_kvar | Phase C Reactive Power Demand-Total | float | 2 | R
0x61A6 | 0x61A7 | 24998 | 24999 | DMD_TOTAL_Q_kvar | System Reactive Power Demand-Total | float | 2 | R
0x61A8 | 0x61A9 | 25000 | 25001 | DMD_S_a_kVA | Phase A Apparent Power Demand | float | 2 | R
0x61AA | 0x61AB | 25002 | 25003 | DMD_S_b_kVA | Phase B Apparent Power Demand | float | 2 | R
0x61AC | 0x61AD | 25004 | 25005 | DMD_S_c_kVA | Phase C Apparent Power Demand | float | 2 | R
0x61AE | 0x61AF | 25006 | 25007 | DMD_S_kVA | System Apparent Power Demand | float | 2 | R
0x6200 | 0x6201 | 25088 | 25089 | MAX_DMD_I_a_A | Max Phase A Current Demand | float | 2 | R
0x6202 | 0x6203 | 25090 | 25091 | MAX_DMD_I_b_A | Max Phase B Current Demand | float | 2 | R
0x6204 | 0x6205 | 25092 | 25093 | MAX_DMD_I_c_A | Max Phase C Current Demand | float | 2 | R
0x6206 | 0x6207 | 25094 | 25095 | MAX_DMD_I_avg_A | Max Average Current Demand | float | 2 | R
0x6208 | 0x6209 | 25096 | 25097 | MAX_DMD_Q1_P_a_kW | Max Phase A Active Power Demand-Quad 1 | float | 2 | R
0x620A | 0x620B | 25098 | 25099 | MAX_DMD_Q1_P_b_kW | Max Phase B Active Power Demand-Quad 1 | float | 2 | R
0x620C | 0x620D | 25100 | 25101 | MAX_DMD_Q1_P_c_kW | Max Phase C Active Power Demand-Quad 1 | float | 2 | R
0x620E | 0x620F | 25102 | 25103 | MAX_DMD_Q1_P_kW | Max System Active Power Demand-Quad 1 | float | 2 | R
0x6210 | 0x6211 | 25104 | 25105 | MAX_DMD_Q1_Q_a_kvar | Max Phase A Reactive Power Demand-Quad 1 | float | 2 | R
0x6212 | 0x6213 | 25106 | 25107 | MAX_DMD_Q1_Q_b_kvar | Max Phase B Reactive Power Demand-Quad 1 | float | 2 | R
0x6214 | 0x6215 | 25108 | 25109 | MAX_DMD_Q1_Q_c_kvar | Max Phase C Reactive Power Demand-Quad 1 | float | 2 | R
0x6216 | 0x6217 | 25110 | 25111 | MAX_DMD_Q1_Q_kvar | Max System Reactive Power Demand-Quad 1 | float | 2 | R
0x6218 | 0x6219 | 25112 | 25113 | MAX_DMD_Q1_S_a_kVA | Max Phase A Apparent Power Demand-Quad 1 | float | 2 | R
0x621A | 0x621B | 25114 | 25115 | MAX_DMD_Q1_S_b_kVA | Max Phase B Apparent Power Demand-Quad 1 | float | 2 | R
0x621C | 0x621D | 25116 | 25117 | MAX_DMD_Q1_S_c_kVA | Max Phase C Apparent Power Demand-Quad 1 | float | 2 | R
0x621E | 0x621F | 25118 | 25119 | MAX_DMD_Q1_S_kVA | Max System Apparent Power Demand-Quad 1 | float | 2 | R
0x6220 | 0x6221 | 25120 | 25121 | MAX_DMD_Q2_P_a_kW | Max Phase A Active Power Demand-Quad 2 | float | 2 | R
0x6222 | 0x6223 | 25122 | 25123 | MAX_DMD_Q2_P_b_kW | Max Phase B Active Power Demand-Quad 2 | float | 2 | R
0x6224 | 0x6225 | 25124 | 25125 | MAX_DMD_Q2_P_c_kW | Max Phase C Active Power Demand-Quad 2 | float | 2 | R
0x6226 | 0x6227 | 25126 | 25127 | MAX_DMD_Q2_P_kW | Max System Active Power Demand-Quad 2 | float | 2 | R
0x6228 | 0x6229 | 25128 | 25129 | MAX_DMD_Q2_Q_a_kvar | Max Phase A Reactive Power Demand-Quad 2 | float | 2 | R
0x622A | 0x622B | 25130 | 25131 | MAX_DMD_Q2_Q_b_kvar | Max Phase B Reactive Power Demand-Quad 2 | float | 2 | R
0x622C | 0x622D | 25132 | 25133 | MAX_DMD_Q2_Q_c_kvar | Max Phase C Reactive Power Demand-Quad 2 | float | 2 | R
0x622E | 0x622F | 25134 | 25135 | MAX_DMD_Q2_Q_kvar | Max System Reactive Power Demand-Quad 2 | float | 2 | R
0x6230 | 0x6231 | 25136 | 25137 | MAX_DMD_Q2_S_a_kVA | Max Phase A Apparent Power Demand-Quad 2 | float | 2 | R
0x6232 | 0x6233 | 25138 | 25139 | MAX_DMD_Q2_S_b_kVA | Max Phase B Apparent Power Demand-Quad 2 | float | 2 | R
0x6234 | 0x6235 | 25140 | 25141 | MAX_DMD_Q2_S_c_kVA | Max Phase C Apparent Power Demand-Quad 2 | float | 2 | R
0x6236 | 0x6237 | 25142 | 25143 | MAX_DMD_Q2_S_kVA | Max System Apparent Power Demand-Quad 2 | float | 2 | R
0x6238 | 0x6239 | 25144 | 25145 | MAX_DMD_Q3_P_a_kW | Max Phase A Active Power Demand-Quad 3 | float | 2 | R
0x623A | 0x623B | 25146 | 25147 | MAX_DMD_Q3_P_b_kW | Max Phase B Active Power Demand-Quad 3 | float | 2 | R
0x623C | 0x623D | 25148 | 25149 | MAX_DMD_Q3_P_c_kW | Max Phase C Active Power Demand-Quad 3 | float | 2 | R
0x623E | 0x623F | 25150 | 25151 | MAX_DMD_Q3_P_kW | Max System Active Power Demand-Quad 3 | float | 2 | R
0x6240 | 0x6241 | 25152 | 25153 | MAX_DMD_Q3_Q_a_kvar | Max Phase A Reactive Power Demand-Quad 3 | float | 2 | R
0x6242 | 0x6243 | 25154 | 25155 | MAX_DMD_Q3_Q_b_kvar | Max Phase B Reactive Power Demand-Quad 3 | float | 2 | R
0x6244 | 0x6245 | 25156 | 25157 | MAX_DMD_Q3_Q_c_kvar | Max Phase C Reactive Power Demand-Quad 3 | float | 2 | R
0x6246 | 0x6247 | 25158 | 25159 | MAX_DMD_Q3_Q_kvar | Max System Reactive Power Demand-Quad 3 | float | 2 | R
0x6248 | 0x6249 | 25160 | 25161 | MAX_DMD_Q3_S_a_kVA | Max Phase A Apparent Power Demand-Quad 3 | float | 2 | R
0x624A | 0x624B | 25162 | 25163 | MAX_DMD_Q3_S_b_kVA | Max Phase B Apparent Power Demand-Quad 3 | float | 2 | R
0x624C | 0x624D | 25164 | 25165 | MAX_DMD_Q3_S_c_kVA | Max Phase C Apparent Power Demand-Quad 3 | float | 2 | R
0x624E | 0x624F | 25166 | 25167 | MAX_DMD_Q3_S_kVA | Max System Apparent Power Demand-Quad 3 | float | 2 | R
0x6250 | 0x6251 | 25168 | 25169 | MAX_DMD_Q4_P_a_kW | Max Phase A Active Power Demand-Quad 4 | float | 2 | R
0x6252 | 0x6253 | 25170 | 25171 | MAX_DMD_Q4_P_b_kW | Max Phase B Active Power Demand-Quad 4 | float | 2 | R
0x6254 | 0x6255 | 25172 | 25173 | MAX_DMD_Q4_P_c_kW | Max Phase C Active Power Demand-Quad 4 | float | 2 | R
0x6256 | 0x6257 | 25174 | 25175 | MAX_DMD_Q4_P_kW | Max System Active Power Demand-Quad 4 | float | 2 | R
0x6258 | 0x6259 | 25176 | 25177 | MAX_DMD_Q4_Q_a_kvar | Max Phase A Reactive Power Demand-Quad 4 | float | 2 | R
0x625A | 0x625B | 25178 | 25179 | MAX_DMD_Q4_Q_b_kvar | Max Phase B Reactive Power Demand-Quad 4 | float | 2 | R
0x625C | 0x625D | 25180 | 25181 | MAX_DMD_Q4_Q_c_kvar | Max Phase C Reactive Power Demand-Quad 4 | float | 2 | R
0x625E | 0x625F | 25182 | 25183 | MAX_DMD_Q4_Q_kvar | Max System Reactive Power Demand-Quad 4 | float | 2 | R
0x6260 | 0x6261 | 25184 | 25185 | MAX_DMD_Q4_S_a_kVA | Max Phase A Apparent Power Demand-Quad 4 | float | 2 | R
0x6262 | 0x6263 | 25186 | 25187 | MAX_DMD_Q4_S_b_kVA | Max Phase B Apparent Power Demand-Quad 4 | float | 2 | R
0x6264 | 0x6265 | 25188 | 25189 | MAX_DMD_Q4_S_c_kVA | Max Phase C Apparent Power Demand-Quad 4 | float | 2 | R
0x6266 | 0x6267 | 25190 | 25191 | MAX_DMD_Q4_S_kVA | Max System Apparent Power Demand-Quad 4 | float | 2 | R
0x6268 | 0x6269 | 25192 | 25193 | MAX_DMD_IMP_P_a_kW | Max Phase A Active Power Demand-Import | float | 2 | R
0x626A | 0x626B | 25194 | 25195 | MAX_DMD_IMP_P_b_kW | Max Phase B Active Power Demand-Import | float | 2 | R
0x626C | 0x626D | 25196 | 25197 | MAX_DMD_IMP_P_c_kW | Max Phase C Active Power Demand-Import | float | 2 | R
0x626E | 0x626F | 25198 | 25199 | MAX_DMD_IMP_P_kW | Max System Active Power Demand-Import | float | 2 | R
0x6270 | 0x6271 | 25200 | 25201 | MAX_DMD_IMP_Q_a_kvar | Max Phase A Reactive Power Demand-Import | float | 2 | R
0x6272 | 0x6273 | 25202 | 25203 | MAX_DMD_IMP_Q_b_kvar | Max Phase B Reactive Power Demand-Import | float | 2 | R
0x6274 | 0x6275 | 25204 | 25205 | MAX_DMD_IMP_Q_c_kvar | Max Phase C Reactive Power Demand-Import | float | 2 | R
0x6276 | 0x6277 | 25206 | 25207 | MAX_DMD_IMP_Q_kvar | Max System Reactive Power Demand-Import | float | 2 | R
0x6278 | 0x6279 | 25208 | 25209 | MAX_DMD_EXP_P_a_kW | Max Phase A Active Power Demand-Export | float | 2 | R
0x627A | 0x627B | 25210 | 25211 | MAX_DMD_EXP_P_b_kW | Max Phase B Active Power Demand-Export | float | 2 | R
0x627C | 0x627D | 25212 | 25213 | MAX_DMD_EXP_P_c_kW | Max Phase C Active Power Demand-Export | float | 2 | R
0x627E | 0x627F | 25214 | 25215 | MAX_DMD_EXP_P_kW | Max System Active Power Demand-Export | float | 2 | R
0x6280 | 0x6281 | 25216 | 25217 | MAX_DMD_EXP_Q_a_kvar | Max Phase A Reactive Power Demand-Export | float | 2 | R
0x6282 | 0x6283 | 25218 | 25219 | MAX_DMD_EXP_Q_b_kvar | Max Phase B Reactive Power Demand-Export | float | 2 | R
0x6284 | 0x6285 | 25220 | 25221 | MAX_DMD_EXP_Q_c_kvar | Max Phase C Reactive Power Demand-Export | float | 2 | R
0x6286 | 0x6287 | 25222 | 25223 | MAX_DMD_EXP_Q_kvar | Max System Reactive Power Demand-Export | float | 2 | R
0x6288 | 0x6289 | 25224 | 25225 | MAX_DMD_NET_P_a_kW | Max Phase A Active Power Demand-Net | float | 2 | R
0x628A | 0x628B | 25226 | 25227 | MAX_DMD_NET_P_b_kW | Max Phase B Active Power Demand-Net | float | 2 | R
0x628C | 0x628D | 25228 | 25229 | MAX_DMD_NET_P_c_kW | Max Phase C Active Power Demand-Net | float | 2 | R
0x628E | 0x628F | 25230 | 25231 | MAX_DMD_NET_P_kW | Max System Active Power Demand-Net | float | 2 | R
0x6290 | 0x6291 | 25232 | 25233 | MAX_DMD_NET_Q_a_kvar | Max Phase A Reactive Power Demand-Net | float | 2 | R
0x6292 | 0x6293 | 25234 | 25235 | MAX_DMD_NET_Q_b_kvar | Max Phase B Reactive Power Demand-Net | float | 2 | R
0x6294 | 0x6295 | 25236 | 25237 | MAX_DMD_NET_Q_c_kvar | Max Phase C Reactive Power Demand-Net | float | 2 | R
0x6296 | 0x6297 | 25238 | 25239 | MAX_DMD_NET_Q_kvar | Max System Reactive Power Demand-Net | float | 2 | R
0x6298 | 0x6299 | 25240 | 25241 | MAX_DMD_TOTAL_P_a_kW | Max Phase A Active Power Demand-Total | float | 2 | R
0x629A | 0x629B | 25242 | 25243 | MAX_DMD_TOTAL_P_b_kW | Max Phase B Active Power Demand-Total | float | 2 | R
0x629C | 0x629D | 25244 | 25245 | MAX_DMD_TOTAL_P_c_kW | Max Phase C Active Power Demand-Total | float | 2 | R
0x629E | 0x629F | 25246 | 25247 | MAX_DMD_TOTAL_P_kW | Max System Active Power Demand-Total | float | 2 | R
0x62A0 | 0x62A1 | 25248 | 25249 | MAX_DMD_TOTAL_Q_a_kvar | Max Phase A Reactive Power Demand-Total | float | 2 | R
0x62A2 | 0x62A3 | 25250 | 25251 | MAX_DMD_TOTAL_Q_b_kvar | Max Phase B Reactive Power Demand-Total | float | 2 | R
0x62A4 | 0x62A5 | 25252 | 25253 | MAX_DMD_TOTAL_Q_c_kvar | Max Phase C Reactive Power Demand-Total | float | 2 | R
0x62A6 | 0x62A7 | 25254 | 25255 | MAX_DMD_TOTAL_Q_kvar | Max System Reactive Power Demand-Total | float | 2 | R
0x62A8 | 0x62A9 | 25256 | 25257 | MAX_DMD_S_a_kVA | Max Phase A Apparent Power Demand | float | 2 | R
0x62AA | 0x62AB | 25258 | 25259 | MAX_DMD_S_b_kVA | Max Phase B Apparent Power Demand | float | 2 | R
0x62AC | 0x62AD | 25260 | 25261 | MAX_DMD_S_c_kVA | Max Phase C Apparent Power Demand | float | 2 | R
0x62AE | 0x62AF | 25262 | 25263 | MAX_DMD_S_kVA | Max System Apparent Power Demand | float | 2 | R
0x62B0 | 0x62B3 | 25264 | 25267 | MAX_DMD_TIME_I_a | Max Phase A Current Demand Time | time_t | 4 | R
0x62B4 | 0x62B7 | 25268 | 25271 | MAX_DMD_TIME_I_b | Max Phase B Current Demand Time | time_t | 4 | R
0x62B8 | 0x62BB | 25272 | 25275 | MAX_DMD_TIME_I_c | Max Phase C Current Demand Time | time_t | 4 | R
0x62BC | 0x62BF | 25276 | 25279 | MAX_DMD_TIME_I_avg | Max Average Current Demand Time | time_t | 4 | R
0x62C0 | 0x62C3 | 25280 | 25283 | MAX_DMD_TIME_Q1_P_a | Max Phase A Active Power Demand-Quad 1 Time | time_t | 4 | R
0x62C4 | 0x62C7 | 25284 | 25287 | MAX_DMD_TIME_Q1_P_b | Max Phase B Active Power Demand-Quad 1 Time | time_t | 4 | R
0x62C8 | 0x62CB | 25288 | 25291 | MAX_DMD_TIME_Q1_P_c | Max Phase C Active Power Demand-Quad 1 Time | time_t | 4 | R
0x62CC | 0x62CF | 25292 | 25295 | MAX_DMD_TIME_Q1_P | Max System Active Power Demand-Quad 1 Time | time_t | 4 | R
0x62D0 | 0x62D3 | 25296 | 25299 | MAX_DMD_TIME_Q1_Q_a | Max Phase A Reactive Power Demand-Quad 1 Time | time_t | 4 | R
0x62D4 | 0x62D7 | 25300 | 25303 | MAX_DMD_TIME_Q1_Q_b | Max Phase B Reactive Power Demand-Quad 1 Time | time_t | 4 | R
0x62D8 | 0x62DB | 25304 | 25307 | MAX_DMD_TIME_Q1_Q_c | Max Phase C Reactive Power Demand-Quad 1 Time | time_t | 4 | R
0x62DC | 0x62DF | 25308 | 25311 | MAX_DMD_TIME_Q1_Q | Max System Reactive Power Demand-Quad 1 Time | time_t | 4 | R
0x62E0 | 0x62E3 | 25312 | 25315 | MAX_DMD_TIME_Q1_S_a | Max Phase A Apparent Power Demand-Quad 1 Time | time_t | 4 | R
0x62E4 | 0x62E7 | 25316 | 25319 | MAX_DMD_TIME_Q1_S_b | Max Phase B Apparent Power Demand-Quad 1 Time | time_t | 4 | R
0x62E8 | 0x62EB | 25320 | 25323 | MAX_DMD_TIME_Q1_S_c | Max Phase C Apparent Power Demand-Quad 1 Time | time_t | 4 | R
0x62EC | 0x62EF | 25324 | 25327 | MAX_DMD_TIME_Q1_S | Max System Apparent Power Demand-Quad 1 Time | time_t | 4 | R
0x62F0 | 0x62F3 | 25328 | 25331 | MAX_DMD_TIME_Q2_P_a | Max Phase A Active Power Demand-Quad 2 Time | time_t | 4 | R
0x62F4 | 0x62F7 | 25332 | 25335 | MAX_DMD_TIME_Q2_P_b | Max Phase B Active Power Demand-Quad 2 Time | time_t | 4 | R
0x62F8 | 0x62FB | 25336 | 25339 | MAX_DMD_TIME_Q2_P_c | Max Phase C Active Power Demand-Quad 2 Time | time_t | 4 | R
0x62FC | 0x62FF | 25340 | 25343 | MAX_DMD_TIME_Q2_P | Max System Active Power Demand-Quad 2 Time | time_t | 4 | R
0x6300 | 0x6303 | 25344 | 25347 | MAX_DMD_TIME_Q2_Q_a | Max Phase A Reactive Power Demand-Quad 2 Time | time_t | 4 | R
0x6304 | 0x6307 | 25348 | 25351 | MAX_DMD_TIME_Q2_Q_b | Max Phase B Reactive Power Demand-Quad 2 Time | time_t | 4 | R
0x6308 | 0x630B | 25352 | 25355 | MAX_DMD_TIME_Q2_Q_c | Max Phase C Reactive Power Demand-Quad 2 Time | time_t | 4 | R
0x630C | 0x630F | 25356 | 25359 | MAX_DMD_TIME_Q2_Q | Max System Reactive Power Demand-Quad 2 Time | time_t | 4 | R
0x6310 | 0x6313 | 25360 | 25363 | MAX_DMD_TIME_Q2_S_a | Max Phase A Apparent Power Demand-Quad 2 Time | time_t | 4 | R
0x6314 | 0x6317 | 25364 | 25367 | MAX_DMD_TIME_Q2_S_b | Max Phase B Apparent Power Demand-Quad 2 Time | time_t | 4 | R
0x6318 | 0x631B | 25368 | 25371 | MAX_DMD_TIME_Q2_S_c | Max Phase C Apparent Power Demand-Quad 2 Time | time_t | 4 | R
0x631C | 0x631F | 25372 | 25375 | MAX_DMD_TIME_Q2_S | Max System Apparent Power Demand-Quad 2 Time | time_t | 4 | R
0x6320 | 0x6323 | 25376 | 25379 | MAX_DMD_TIME_Q3_P_a | Max Phase A Active Power Demand-Quad 3 Time | time_t | 4 | R
0x6324 | 0x6327 | 25380 | 25383 | MAX_DMD_TIME_Q3_P_b | Max Phase B Active Power Demand-Quad 3 Time | time_t | 4 | R
0x6328 | 0x632B | 25384 | 25387 | MAX_DMD_TIME_Q3_P_c | Max Phase C Active Power Demand-Quad 3 Time | time_t | 4 | R
0x632C | 0x632F | 25388 | 25391 | MAX_DMD_TIME_Q3_P | Max System Active Power Demand-Quad 3 Time | time_t | 4 | R
0x6330 | 0x6333 | 25392 | 25395 | MAX_DMD_TIME_Q3_Q_a | Max Phase A Reactive Power Demand-Quad 3 Time | time_t | 4 | R
0x6334 | 0x6337 | 25396 | 25399 | MAX_DMD_TIME_Q3_Q_b | Max Phase B Reactive Power Demand-Quad 3 Time | time_t | 4 | R
0x6338 | 0x633B | 25400 | 25403 | MAX_DMD_TIME_Q3_Q_c | Max Phase C Reactive Power Demand-Quad 3 Time | time_t | 4 | R
0x633C | 0x633F | 25404 | 25407 | MAX_DMD_TIME_Q3_Q | Max System Reactive Power Demand-Quad 3 Time | time_t | 4 | R
0x6340 | 0x6343 | 25408 | 25411 | MAX_DMD_TIME_Q3_S_a | Max Phase A Apparent Power Demand-Quad 3 Time | time_t | 4 | R
0x6344 | 0x6347 | 25412 | 25415 | MAX_DMD_TIME_Q3_S_b | Max Phase B Apparent Power Demand-Quad 3 Time | time_t | 4 | R
0x6348 | 0x634B | 25416 | 25419 | MAX_DMD_TIME_Q3_S_c | Max Phase C Apparent Power Demand-Quad 3 Time | time_t | 4 | R
0x634C | 0x634F | 25420 | 25423 | MAX_DMD_TIME_Q3_S | Max System Apparent Power Demand-Quad 3 Time | time_t | 4 | R
0x6350 | 0x6353 | 25424 | 25427 | MAX_DMD_TIME_Q4_P_a | Max Phase A Active Power Demand-Quad 4 Time | time_t | 4 | R
0x6354 | 0x6357 | 25428 | 25431 | MAX_DMD_TIME_Q4_P_b | Max Phase B Active Power Demand-Quad 4 Time | time_t | 4 | R
0x6358 | 0x635B | 25432 | 25435 | MAX_DMD_TIME_Q4_P_c | Max Phase C Active Power Demand-Quad 4 Time | time_t | 4 | R
0x635C | 0x635F | 25436 | 25439 | MAX_DMD_TIME_Q4_P | Max System Active Power Demand-Quad 4 Time | time_t | 4 | R
0x6360 | 0x6363 | 25440 | 25443 | MAX_DMD_TIME_Q4_Q_a | Max Phase A Reactive Power Demand-Quad 4 Time | time_t | 4 | R
0x6364 | 0x6367 | 25444 | 25447 | MAX_DMD_TIME_Q4_Q_b | Max Phase B Reactive Power Demand-Quad 4 Time | time_t | 4 | R
0x6368 | 0x636B | 25448 | 25451 | MAX_DMD_TIME_Q4_Q_c | Max Phase C Reactive Power Demand-Quad 4 Time | time_t | 4 | R
0x636C | 0x636F | 25452 | 25455 | MAX_DMD_TIME_Q4_Q | Max System Reactive Power Demand-Quad 4 Time | time_t | 4 | R
0x6370 | 0x6373 | 25456 | 25459 | MAX_DMD_TIME_Q4_S_a | Max Phase A Apparent Power Demand-Quad 4 Time | time_t | 4 | R
0x6374 | 0x6377 | 25460 | 25463 | MAX_DMD_TIME_Q4_S_b | Max Phase B Apparent Power Demand-Quad 4 Time | time_t | 4 | R
0x6378 | 0x637B | 25464 | 25467 | MAX_DMD_TIME_Q4_S_c | Max Phase C Apparent Power Demand-Quad 4 Time | time_t | 4 | R
0x637C | 0x637F | 25468 | 25471 | MAX_DMD_TIME_Q4_S | Max System Apparent Power Demand-Quad 4 Time | time_t | 4 | R
0x6500 | 0x6383 | 25472 | 25475 | MAX_DMD_TIME_IMP_P_a | Max Phase A Active Power Demand-Import Time | time_t | 4 | R
0x6384 | 0x6387 | 25476 | 25479 | MAX_DMD_TIME_IMP_P_b | Max Phase B Active Power Demand-Import Time | time_t | 4 | R
0x6388 | 0x638B | 25480 | 25483 | MAX_DMD_TIME_IMP_P_c | Max Phase C Active Power Demand-Import Time | time_t | 4 | R
0x638C | 0x638F | 25484 | 25487 | MAX_DMD_TIME_IMP_P | Max System Active Power Demand-Import Time | time_t | 4 | R
0x6390 | 0x6393 | 25488 | 25491 | MAX_DMD_TIME_IMP_Q_a | Max Phase A Reactive Power Demand-Import Time | time_t | 4 | R
0x6394 | 0x6397 | 25492 | 25495 | MAX_DMD_TIME_IMP_Q_b | Max Phase B Reactive Power Demand-Import Time | time_t | 4 | R
0x6398 | 0x639B | 25496 | 25499 | MAX_DMD_TIME_IMP_Q_c | Max Phase C Reactive Power Demand-Import Time | time_t | 4 | R
0x639C | 0x639F | 25500 | 25503 | MAX_DMD_TIME_IMP_Q | Max System Reactive Power Demand-Import Time | time_t | 4 | R
0x63A0 | 0x63A3 | 25504 | 25507 | MAX_DMD_TIME_EXP_P_a | Max Phase A Active Power Demand-Export Time | time_t | 4 | R
0x63A4 | 0x63A7 | 25508 | 25511 | MAX_DMD_TIME_EXP_P_b | Max Phase B Active Power Demand-Export Time | time_t | 4 | R
0x63A8 | 0x63AB | 25512 | 25515 | MAX_DMD_TIME_EXP_P_c | Max Phase C Active Power Demand-Export Time | time_t | 4 | R
0x63AC | 0x63AF | 25516 | 25519 | MAX_DMD_TIME_EXP_P | Max System Active Power Demand-Export Time | time_t | 4 | R
0x63B0 | 0x63B3 | 25520 | 25523 | MAX_DMD_TIME_EXP_Q_a | Max Phase A Reactive Power Demand-Export Time | time_t | 4 | R
0x63B4 | 0x63B7 | 25524 | 25527 | MAX_DMD_TIME_EXP_Q_b | Max Phase B Reactive Power Demand-Export Time | time_t | 4 | R
0x63B8 | 0x63BB | 25528 | 25531 | MAX_DMD_TIME_EXP_Q_c | Max Phase C Reactive Power Demand-Export Time | time_t | 4 | R
0x63BC | 0x63BF | 25532 | 25535 | MAX_DMD_TIME_EXP_Q | Max System Reactive Power Demand-Export Time | time_t | 4 | R
0x63C0 | 0x63C3 | 25536 | 25539 | MAX_DMD_TIME_NET_P_a | Max Phase A Active Power Demand-Net Time | time_t | 4 | R
0x63C4 | 0x63C7 | 25540 | 25543 | MAX_DMD_TIME_NET_P_b | Max Phase B Active Power Demand-Net Time | time_t | 4 | R
0x63C8 | 0x63CB | 25544 | 25547 | MAX_DMD_TIME_NET_P_c | Max Phase C Active Power Demand-Net Time | time_t | 4 | R
0x63CC | 0x63CF | 25548 | 25551 | MAX_DMD_TIME_NET_P | Max System Active Power Demand-Net Time | time_t | 4 | R
0x63D0 | 0x63D3 | 25552 | 25555 | MAX_DMD_TIME_NET_Q_a | Max Phase A Reactive Power Demand-Net Time | time_t | 4 | R
0x63D4 | 0x63D7 | 25556 | 25559 | MAX_DMD_TIME_NET_Q_b | Max Phase B Reactive Power Demand-Net Time | time_t | 4 | R
0x63D8 | 0x63DB | 25560 | 25563 | MAX_DMD_TIME_NET_Q_c | Max Phase C Reactive Power Demand-Net Time | time_t | 4 | R
0x63DC | 0x63DF | 25564 | 25567 | MAX_DMD_TIME_NET_Q | Max System Reactive Power Demand-Net Time | time_t | 4 | R
0x63E0 | 0x63E3 | 25568 | 25571 | MAX_DMD_TIME_TOTAL_P_a | Max Phase A Active Power Demand-Total Time | time_t | 4 | R
0x63E4 | 0x63E7 | 25572 | 25575 | MAX_DMD_TIME_TOTAL_P_b | Max Phase B Active Power Demand-Total Time | time_t | 4 | R
0x63E8 | 0x63EB | 25576 | 25579 | MAX_DMD_TIME_TOTAL_P_c | Max Phase C Active Power Demand-Total Time | time_t | 4 | R
0x63EC | 0x63EF | 25580 | 25583 | MAX_DMD_TIME_TOTAL_P | Max System Active Power Demand-Total Time | time_t | 4 | R
0x63F0 | 0x63F3 | 25584 | 25587 | MAX_DMD_TIME_TOTAL_Q_a | Max Phase A Reactive Power Demand-Total Time | time_t | 4 | R
0x63F4 | 0x63F7 | 25588 | 25591 | MAX_DMD_TIME_TOTAL_Q_b | Max Phase B Reactive Power Demand-Total Time | time_t | 4 | R
0x63F8 | 0x63FB | 25592 | 25595 | MAX_DMD_TIME_TOTAL_Q_c | Max Phase C Reactive Power Demand-Total Time | time_t | 4 | R
0x63FC | 0x63FF | 25596 | 25599 | MAX_DMD_TIME_TOTAL_Q | Max System Reactive Power Demand-Total Time | time_t | 4 | R
0x6400 | 0x6403 | 25600 | 25603 | MAX_DMD_TIME_S_a | Max Phase A Apparent Power Demand Time | time_t | 4 | R
0x6404 | 0x6407 | 25604 | 25607 | MAX_DMD_TIME_S_b | Max Phase B Apparent Power Demand Time | time_t | 4 | R
0x6408 | 0x640B | 25608 | 25611 | MAX_DMD_TIME_S_c | Max Phase C Apparent Power Demand Time | time_t | 4 | R
0x640C | 0x640F | 25612 | 25615 | MAX_DMD_TIME_S | Max System Apparent Power Demand Time | time_t | 4 | R

## Energy
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x6500 | 0x6503 | 25856 | 25859 | ACCUM_EP_Q1_a_kWh | Accumulative Phase A Active Energy-Quad 1 | Double | 4 | R
0x6504 | 0x6507 | 25860 | 25863 | ACCUM_EP_Q1_b_kWh | Accumulative Phase B Active Energy-Quad 1 | Double | 4 | R
0x6508 | 0x650B | 25864 | 25867 | ACCUM_EP_Q1_c_kWh | Accumulative Phase C Active Energy-Quad 1 | Double | 4 | R
0x650C | 0x650F | 25868 | 25871 | ACCUM_EP_Q1_kWh | Accumulative System Active Energy-Quad 1 | Double | 4 | R
0x6510 | 0x6513 | 25872 | 25875 | ACCUM_EQ_Q1_a_kvarh | Accumulative Phase A Reactive Energy-Quad 1 | Double | 4 | R
0x6514 | 0x6517 | 25876 | 25879 | ACCUM_EQ_Q1_b_kvarh | Accumulative Phase B Reactive Energy-Quad 1 | Double | 4 | R
0x6518 | 0x651B | 25880 | 25883 | ACCUM_EQ_Q1_c_kvarh | Accumulative Phase C Reactive Energy-Quad 1 | Double | 4 | R
0x651C | 0x651F | 25884 | 25887 | ACCUM_EQ_Q1_kvarh | Accumulative System Reactive Energy-Quad 1 | Double | 4 | R
0x6520 | 0x6523 | 25888 | 25891 | ACCUM_ES_Q1_a_kVAh | Accumulative Phase A Apparent Energy-Quad 1 | Double | 4 | R
0x6524 | 0x6527 | 25892 | 25895 | ACCUM_ES_Q1_b_kVAh | Accumulative Phase B Apparent Energy-Quad 1 | Double | 4 | R
0x6528 | 0x652B | 25896 | 25899 | ACCUM_ES_Q1_c_kVAh | Accumulative Phase C Apparent Energy-Quad 1 | Double | 4 | R
0x652C | 0x652F | 25900 | 25903 | ACCUM_ES_Q1_kVAh | Accumulative System Apparent Energy-Quad 1 | Double | 4 | R
0x6530 | 0x6533 | 25904 | 25907 | ACCUM_EP_Q2_a_kWh | Accumulative Phase A Active Energy-Quad 2 | Double | 4 | R
0x6534 | 0x6537 | 25908 | 25911 | ACCUM_EP_Q2_b_kWh | Accumulative Phase B Active Energy-Quad 2 | Double | 4 | R
0x6538 | 0x653B | 25912 | 25915 | ACCUM_EP_Q2_c_kWh | Accumulative Phase C Active Energy-Quad 2 | Double | 4 | R
0x653C | 0x653F | 25916 | 25919 | ACCUM_EP_Q2_kWh | Accumulative System Active Energy-Quad 2 | Double | 4 | R
0x6540 | 0x6543 | 25920 | 25923 | ACCUM_EQ_Q2_a_kvarh | Accumulative Phase A Reactive Energy-Quad 2 | Double | 4 | R
0x6544 | 0x6547 | 25924 | 25927 | ACCUM_EQ_Q2_b_kvarh | Accumulative Phase B Reactive Energy-Quad 2 | Double | 4 | R
0x6548 | 0x654B | 25928 | 25931 | ACCUM_EQ_Q2_c_kvarh | Accumulative Phase C Reactive Energy-Quad 2 | Double | 4 | R
0x654C | 0x654F | 25932 | 25935 | ACCUM_EQ_Q2_kvarh | Accumulative System Reactive Energy-Quad 2 | Double | 4 | R
0x6550 | 0x6553 | 25936 | 25939 | ACCUM_ES_Q2_a_kVAh | Accumulative Phase A Apparent Energy-Quad 2 | Double | 4 | R
0x6554 | 0x6557 | 25940 | 25943 | ACCUM_ES_Q2_b_kVAh | Accumulative Phase B Apparent Energy-Quad 2 | Double | 4 | R
0x6558 | 0x655B | 25944 | 25947 | ACCUM_ES_Q2_c_kVAh | Accumulative Phase C Apparent Energy-Quad 2 | Double | 4 | R
0x655C | 0x655F | 25948 | 25951 | ACCUM_ES_Q2_kVAh | Accumulative System Apparent Energy-Quad 2 | Double | 4 | R
0x6560 | 0x6563 | 25952 | 25955 | ACCUM_EP_Q3_a_kWh | Accumulative Phase A Active Energy-Quad 3 | Double | 4 | R
0x6564 | 0x6567 | 25956 | 25959 | ACCUM_EP_Q3_b_kWh | Accumulative Phase B Active Energy-Quad 3 | Double | 4 | R
0x6568 | 0x656B | 25960 | 25963 | ACCUM_EP_Q3_c_kWh | Accumulative Phase C Active Energy-Quad 3 | Double | 4 | R
0x656C | 0x656F | 25964 | 25967 | ACCUM_EP_Q3_kWh | Accumulative System Active Energy-Quad 3 | Double | 4 | R
0x6570 | 0x6573 | 25968 | 25971 | ACCUM_EQ_Q3_a_kvarh | Accumulative Phase A Reactive Energy-Quad 3 | Double | 4 | R
0x6574 | 0x6577 | 25972 | 25975 | ACCUM_EQ_Q3_b_kvarh | Accumulative Phase B Reactive Energy-Quad 3 | Double | 4 | R
0x6578 | 0x657B | 25976 | 25979 | ACCUM_EQ_Q3_c_kvarh | Accumulative Phase C Reactive Energy-Quad 3 | Double | 4 | R
0x657C | 0x657F | 25980 | 25983 | ACCUM_EQ_Q3_kvarh | Accumulative System Reactive Energy-Quad 3 | Double | 4 | R
0x6580 | 0x6583 | 25984 | 25987 | ACCUM_ES_Q3_a_kVAh | Accumulative Phase A Apparent Energy-Quad 3 | Double | 4 | R
0x6584 | 0x6587 | 25988 | 25991 | ACCUM_ES_Q3_b_kVAh | Accumulative Phase B Apparent Energy-Quad 3 | Double | 4 | R
0x6588 | 0x658B | 25992 | 25995 | ACCUM_ES_Q3_c_kVAh | Accumulative Phase C Apparent Energy-Quad 3 | Double | 4 | R
0x658C | 0x658F | 25996 | 25999 | ACCUM_ES_Q3_kVAh | Accumulative System Apparent Energy-Quad 3 | Double | 4 | R
0x6590 | 0x6593 | 26000 | 26003 | ACCUM_EP_Q4_a_kWh | Accumulative Phase A Active Energy-Quad 4 | Double | 4 | R
0x6594 | 0x6597 | 26004 | 26007 | ACCUM_EP_Q4_b_kWh | Accumulative Phase B Active Energy-Quad 4 | Double | 4 | R
0x6598 | 0x659B | 26008 | 26011 | ACCUM_EP_Q4_c_kWh | Accumulative Phase C Active Energy-Quad 4 | Double | 4 | R
0x659C | 0x659F | 26012 | 26015 | ACCUM_EP_Q4_kWh | Accumulative System Active Energy-Quad 4 | Double | 4 | R
0x65A0 | 0x65A3 | 26016 | 26019 | ACCUM_EQ_Q4_a_kvarh | Accumulative Phase A Reactive Energy-Quad 4 | Double | 4 | R
0x65A4 | 0x65A7 | 26020 | 26023 | ACCUM_EQ_Q4_b_kvarh | Accumulative Phase B Reactive Energy-Quad 4 | Double | 4 | R
0x65A8 | 0x65AB | 26024 | 26027 | ACCUM_EQ_Q4_c_kvarh | Accumulative Phase C Reactive Energy-Quad 4 | Double | 4 | R
0x65AC | 0x65AF | 26028 | 26031 | ACCUM_EQ_Q4_kvarh | Accumulative System Reactive Energy-Quad 4 | Double | 4 | R
0x65B0 | 0x65B3 | 26032 | 26035 | ACCUM_ES_Q4_a_kVAh | Accumulative Phase A Apparent Energy-Quad 4 | Double | 4 | R
0x65B4 | 0x65B7 | 26036 | 26039 | ACCUM_ES_Q4_b_kVAh | Accumulative Phase B Apparent Energy-Quad 4 | Double | 4 | R
0x65B8 | 0x65BB | 26040 | 26043 | ACCUM_ES_Q4_c_kVAh | Accumulative Phase C Apparent Energy-Quad 4 | Double | 4 | R
0x65BC | 0x65BF | 26044 | 26047 | ACCUM_ES_Q4_kVAh | Accumulative System Apparent Energy-Quad 4 | Double | 4 | R
0x65C0 | 0x65C3 | 26048 | 26051 | ACCUM_EP_IMP_a_kWh | Accumulative Phase A Active Energy-Import | Double | 4 | R
0x65C4 | 0x65C7 | 26052 | 26055 | ACCUM_EP_IMP_b_kWh | Accumulative Phase B Active Energy-Import | Double | 4 | R
0x65C8 | 0x65CB | 26056 | 26059 | ACCUM_EP_IMP_c_kWh | Accumulative Phase C Active Energy-Import | Double | 4 | R
0x65CC | 0x65CF | 26060 | 26063 | ACCUM_EP_IMP_kWh | Accumulative System Active Energy-Import | Double | 4 | R
0x65D0 | 0x65D3 | 26064 | 26067 | ACCUM_EQ_IMP_a_kvarh | Accumulative Phase A Reactive Energy-Import | Double | 4 | R
0x65D4 | 0x65D7 | 26068 | 26071 | ACCUM_EQ_IMP_b_kvarh | Accumulative Phase B Reactive Energy-Import | Double | 4 | R
0x65D8 | 0x65DB | 26072 | 26075 | ACCUM_EQ_IMP_c_kvarh | Accumulative Phase C Reactive Energy-Import | Double | 4 | R
0x65DC | 0x65DF | 26076 | 26079 | ACCUM_EQ_IMP_kvarh | Accumulative System Reactive Energy-Import | Double | 4 | R
0x65E0 | 0x65E3 | 26080 | 26083 | ACCUM_EP_EXP_a_kWh | Accumulative Phase A Active Energy-Export | Double | 4 | R
0x65E4 | 0x65E7 | 26084 | 26087 | ACCUM_EP_EXP_b_kWh | Accumulative Phase B Active Energy-Export | Double | 4 | R
0x65E8 | 0x65EB | 26088 | 26091 | ACCUM_EP_EXP_c_kWh | Accumulative Phase C Active Energy-Export | Double | 4 | R
0x65EC | 0x65EF | 26092 | 26095 | ACCUM_EP_EXP_kWh | Accumulative System Active Energy-Export | Double | 4 | R
0x65F0 | 0x65F3 | 26096 | 26099 | ACCUM_EQ_EXP_a_kvarh | Accumulative Phase A Reactive Energy-Export | Double | 4 | R
0x65F4 | 0x65F7 | 26100 | 26103 | ACCUM_EQ_EXP_b_kvarh | Accumulative Phase B Reactive Energy-Export | Double | 4 | R
0x65F8 | 0x65FB | 26104 | 26107 | ACCUM_EQ_EXP_c_kvarh | Accumulative Phase C Reactive Energy-Export | Double | 4 | R
0x65FC | 0x65FF | 26108 | 26111 | ACCUM_EQ_EXP_kvarh | Accumulative System Reactive Energy-Export | Double | 4 | R
0x6600 | 0x6603 | 26112 | 26115 | ACCUM_EP_NET_a_kWh | Accumulative Phase A Active Energy-Net | Double | 4 | R
0x6604 | 0x6607 | 26116 | 26119 | ACCUM_EP_NET_b_kWh | Accumulative Phase B Active Energy-Net | Double | 4 | R
0x6608 | 0x660B | 26120 | 26123 | ACCUM_EP_NET_c_kWh | Accumulative Phase C Active Energy-Net | Double | 4 | R
0x660C | 0x660F | 26124 | 26127 | ACCUM_EP_NET_kWh | Accumulative System Active Energy-Net | Double | 4 | R
0x6610 | 0x6613 | 26128 | 26131 | ACCUM_EQ_NET_a_kvarh | Accumulative Phase A Reactive Energy-Net | Double | 4 | R
0x6614 | 0x6617 | 26132 | 26135 | ACCUM_EQ_NET_b_kvarh | Accumulative Phase B Reactive Energy-Net | Double | 4 | R
0x6618 | 0x661B | 26136 | 26139 | ACCUM_EQ_NET_c_kvarh | Accumulative Phase C Reactive Energy-Net | Double | 4 | R
0x661C | 0x661F | 26140 | 26143 | ACCUM_EQ_NET_kvarh | Accumulative System Reactive Energy-Net | Double | 4 | R
0x6620 | 0x6623 | 26144 | 26147 | ACCUM_EP_TOTAL_a_kWh | Accumulative Phase A Active Energy-Total | Double | 4 | R
0x6624 | 0x6627 | 26148 | 26151 | ACCUM_EP_TOTAL_b_kWh | Accumulative Phase B Active Energy-Total | Double | 4 | R
0x6628 | 0x662B | 26152 | 26155 | ACCUM_EP_TOTAL_c_kWh | Accumulative Phase C Active Energy-Total | Double | 4 | R
0x662C | 0x662F | 26156 | 26159 | ACCUM_EP_TOTAL_kWh | Accumulative System Active Energy-Total | Double | 4 | R
0x6630 | 0x6633 | 26160 | 26163 | ACCUM_EQ_TOTAL_a_kvarh | Accumulative Phase A Reactive Energy-Total | Double | 4 | R
0x6634 | 0x6637 | 26164 | 26167 | ACCUM_EQ_TOTAL_b_kvarh | Accumulative Phase B Reactive Energy-Total | Double | 4 | R
0x6638 | 0x663B | 26168 | 26171 | ACCUM_EQ_TOTAL_c_kvarh | Accumulative Phase C Reactive Energy-Total | Double | 4 | R
0x663C | 0x663F | 26172 | 26175 | ACCUM_EQ_TOTAL_kvarh | Accumulative System Reactive Energy-Total | Double | 4 | R
0x6640 | 0x6643 | 26176 | 26179 | ACCUM_ES_a_kVAh | Accumulative Phase A Apparent Energy | Double | 4 | R
0x6644 | 0x6647 | 26180 | 26183 | ACCUM_ES_b_kVAh | Accumulative Phase B Apparent Energy | Double | 4 | R
0x6648 | 0x664B | 26184 | 26187 | ACCUM_ES_c_kVAh | Accumulative Phase C Apparent Energy | Double | 4 | R
0x664C | 0x664F | 26188 | 26191 | ACCUM_ES_kVAh | Accumulative System Apparent Energy | Double | 4 | R
0x6680 | 0x6683 | 26240 | 26243 | MB_ACCUM_EP_MB_Q1_a_kWh | Modbus Accumulative Phase A Active MB Energy-Quad 1 | Int64 | 4 | R
0x6684 | 0x6687 | 26244 | 26247 | MB_ACCUM_EP_MB_Q1_b_kWh | Modbus Accumulative Phase B Active MB Energy-Quad 1 | Int64 | 4 | R
0x6688 | 0x668B | 26248 | 26251 | MB_ACCUM_EP_MB_Q1_c_kWh | Modbus Accumulative Phase C Active MB Energy-Quad 1 | Int64 | 4 | R
0x668C | 0x668F | 26252 | 26255 | MB_ACCUM_EP_MB_Q1_kWh | Modbus Accumulative System Active MB Energy-Quad 1 | Int64 | 4 | R
0x6690 | 0x6693 | 26256 | 26259 | MB_ACCUM_EQ_MB_Q1_a_kvarh | Modbus Accumulative Phase A Reactive MB Energy-Quad 1 | Int64 | 4 | R
0x6694 | 0x6697 | 26260 | 26263 | MB_ACCUM_EQ_MB_Q1_b_kvarh | Modbus Accumulative Phase B Reactive MB Energy-Quad 1 | Int64 | 4 | R
0x6698 | 0x669B | 26264 | 26267 | MB_ACCUM_EQ_MB_Q1_c_kvarh | Modbus Accumulative Phase C Reactive MB Energy-Quad 1 | Int64 | 4 | R
0x669C | 0x669F | 26268 | 26271 | MB_ACCUM_EQ_MB_Q1_kvarh | Modbus Accumulative System Reactive MB Energy-Quad 1 | Int64 | 4 | R
0x66A0 | 0x66A3 | 26272 | 26275 | MB_ACCUM_ES_MB_Q1_a_kVAh | Modbus Accumulative Phase A Apparent MB Energy-Quad 1 | Int64 | 4 | R
0x66A4 | 0x66A7 | 26276 | 26279 | MB_ACCUM_ES_MB_Q1_b_kVAh | Modbus Accumulative Phase B Apparent MB Energy-Quad 1 | Int64 | 4 | R
0x66A8 | 0x66AB | 26280 | 26283 | MB_ACCUM_ES_MB_Q1_c_kVAh | Modbus Accumulative Phase C Apparent MB Energy-Quad 1 | Int64 | 4 | R
0x66AC | 0x66AF | 26284 | 26287 | MB_ACCUM_ES_MB_Q1_kVAh | Modbus Accumulative System Apparent MB Energy-Quad 1 | Int64 | 4 | R
0x66B0 | 0x66B3 | 26288 | 26291 | MB_ACCUM_EP_MB_Q2_a_kWh | Modbus Accumulative Phase A Active MB Energy-Quad 2 | Int64 | 4 | R
0x66B4 | 0x66B7 | 26292 | 26295 | MB_ACCUM_EP_MB_Q2_b_kWh | Modbus Accumulative Phase B Active MB Energy-Quad 2 | Int64 | 4 | R
0x66B8 | 0x66BB | 26296 | 26299 | MB_ACCUM_EP_MB_Q2_c_kWh | Modbus Accumulative Phase C Active MB Energy-Quad 2 | Int64 | 4 | R
0x66BC | 0x66BF | 26300 | 26303 | MB_ACCUM_EP_MB_Q2_kWh | Modbus Accumulative System Active MB Energy-Quad 2 | Int64 | 4 | R
0x66C0 | 0x66C3 | 26304 | 26307 | MB_ACCUM_EQ_MB_Q2_a_kvarh | Modbus Accumulative Phase A Reactive MB Energy-Quad 2 | Int64 | 4 | R
0x66C4 | 0x66C7 | 26308 | 26311 | MB_ACCUM_EQ_MB_Q2_b_kvarh | Modbus Accumulative Phase B Reactive MB Energy-Quad 2 | Int64 | 4 | R
0x66C8 | 0x66CB | 26312 | 26315 | MB_ACCUM_EQ_MB_Q2_c_kvarh | Modbus Accumulative Phase C Reactive MB Energy-Quad 2 | Int64 | 4 | R
0x66CC | 0x66CF | 26316 | 26319 | MB_ACCUM_EQ_MB_Q2_kvarh | Modbus Accumulative System Reactive MB Energy-Quad 2 | Int64 | 4 | R
0x66D0 | 0x66D3 | 26320 | 26323 | MB_ACCUM_ES_MB_Q2_a_kVAh | Modbus Accumulative Phase A Apparent MB Energy-Quad 2 | Int64 | 4 | R
0x66D4 | 0x66D7 | 26324 | 26327 | MB_ACCUM_ES_MB_Q2_b_kVAh | Modbus Accumulative Phase B Apparent MB Energy-Quad 2 | Int64 | 4 | R
0x66D8 | 0x66DB | 26328 | 26331 | MB_ACCUM_ES_MB_Q2_c_kVAh | Modbus Accumulative Phase C Apparent MB Energy-Quad 2 | Int64 | 4 | R
0x66DC | 0x66DF | 26332 | 26335 | MB_ACCUM_ES_MB_Q2_kVAh | Modbus Accumulative System Apparent MB Energy-Quad 2 | Int64 | 4 | R
0x66E0 | 0x66E3 | 26336 | 26339 | MB_ACCUM_EP_MB_Q3_a_kWh | Modbus Accumulative Phase A Active MB Energy-Quad 3 | Int64 | 4 | R
0x66E4 | 0x66E7 | 26340 | 26343 | MB_ACCUM_EP_MB_Q3_b_kWh | Modbus Accumulative Phase B Active MB Energy-Quad 3 | Int64 | 4 | R
0x66E8 | 0x66EB | 26344 | 26347 | MB_ACCUM_EP_MB_Q3_c_kWh | Modbus Accumulative Phase C Active MB Energy-Quad 3 | Int64 | 4 | R
0x66EC | 0x66EF | 26348 | 26351 | MB_ACCUM_EP_MB_Q3_kWh | Modbus Accumulative System Active MB Energy-Quad 3 | Int64 | 4 | R
0x66F0 | 0x66F3 | 26352 | 26355 | MB_ACCUM_EQ_MB_Q3_a_kvarh | Modbus Accumulative Phase A Reactive MB Energy-Quad 3 | Int64 | 4 | R
0x66F4 | 0x66F7 | 26356 | 26359 | MB_ACCUM_EQ_MB_Q3_b_kvarh | Modbus Accumulative Phase B Reactive MB Energy-Quad 3 | Int64 | 4 | R
0x66F8 | 0x66FB | 26360 | 26363 | MB_ACCUM_EQ_MB_Q3_c_kvarh | Modbus Accumulative Phase C Reactive MB Energy-Quad 3 | Int64 | 4 | R
0x66FC | 0x66FF | 26364 | 26367 | MB_ACCUM_EQ_MB_Q3_kvarh | Modbus Accumulative System Reactive MB Energy-Quad 3 | Int64 | 4 | R
0x6700 | 0x6703 | 26368 | 26371 | MB_ACCUM_ES_MB_Q3_a_kVAh | Modbus Accumulative Phase A Apparent MB Energy-Quad 3 | Int64 | 4 | R
0x6704 | 0x6707 | 26372 | 26375 | MB_ACCUM_ES_MB_Q3_b_kVAh | Modbus Accumulative Phase B Apparent MB Energy-Quad 3 | Int64 | 4 | R
0x6708 | 0x670B | 26376 | 26379 | MB_ACCUM_ES_MB_Q3_c_kVAh | Modbus Accumulative Phase C Apparent MB Energy-Quad 3 | Int64 | 4 | R
0x670C | 0x670F | 26380 | 26383 | MB_ACCUM_ES_MB_Q3_kVAh | Modbus Accumulative System Apparent MB Energy-Quad 3 | Int64 | 4 | R
0x6710 | 0x6713 | 26384 | 26387 | MB_ACCUM_EP_MB_Q4_a_kWh | Modbus Accumulative Phase A Active MB Energy-Quad 4 | Int64 | 4 | R
0x6714 | 0x6717 | 26388 | 26391 | MB_ACCUM_EP_MB_Q4_b_kWh | Modbus Accumulative Phase B Active MB Energy-Quad 4 | Int64 | 4 | R
0x6718 | 0x671B | 26392 | 26395 | MB_ACCUM_EP_MB_Q4_c_kWh | Modbus Accumulative Phase C Active MB Energy-Quad 4 | Int64 | 4 | R
0x671C | 0x671F | 26396 | 26399 | MB_ACCUM_EP_MB_Q4_kWh | Modbus Accumulative System Active MB Energy-Quad 4 | Int64 | 4 | R
0x6720 | 0x6723 | 26400 | 26403 | MB_ACCUM_EQ_MB_Q4_a_kvarh | Modbus Accumulative Phase A Reactive MB Energy-Quad 4 | Int64 | 4 | R
0x6724 | 0x6727 | 26404 | 26407 | MB_ACCUM_EQ_MB_Q4_b_kvarh | Modbus Accumulative Phase B Reactive MB Energy-Quad 4 | Int64 | 4 | R
0x6728 | 0x672B | 26408 | 26411 | MB_ACCUM_EQ_MB_Q4_c_kvarh | Modbus Accumulative Phase C Reactive MB Energy-Quad 4 | Int64 | 4 | R
0x672C | 0x672F | 26412 | 26415 | MB_ACCUM_EQ_MB_Q4_kvarh | Modbus Accumulative System Reactive MB Energy-Quad 4 | Int64 | 4 | R
0x6730 | 0x6733 | 26416 | 26419 | MB_ACCUM_ES_MB_Q4_a_kVAh | Modbus Accumulative Phase A Apparent MB Energy-Quad 4 | Int64 | 4 | R
0x6734 | 0x6737 | 26420 | 26423 | MB_ACCUM_ES_MB_Q4_b_kVAh | Modbus Accumulative Phase B Apparent MB Energy-Quad 4 | Int64 | 4 | R
0x6738 | 0x673B | 26424 | 26427 | MB_ACCUM_ES_MB_Q4_c_kVAh | Modbus Accumulative Phase C Apparent MB Energy-Quad 4 | Int64 | 4 | R
0x673C | 0x673F | 26428 | 26431 | MB_ACCUM_ES_MB_Q4_kVAh | Modbus Accumulative System Apparent MB Energy-Quad 4 | Int64 | 4 | R
0x6740 | 0x6743 | 26432 | 26435 | MB_ACCUM_EP_MB_IMP_a_kWh | Modbus Accumulative Phase A Active MB Energy-Import | Int64 | 4 | R
0x6744 | 0x6747 | 26436 | 26439 | MB_ACCUM_EP_MB_IMP_b_kWh | Modbus Accumulative Phase B Active MB Energy-Import | Int64 | 4 | R
0x6748 | 0x674B | 26440 | 26443 | MB_ACCUM_EP_MB_IMP_c_kWh | Modbus Accumulative Phase C Active MB Energy-Import | Int64 | 4 | R
0x674C | 0x674F | 26444 | 26447 | MB_ACCUM_EP_MB_IMP_kWh | Modbus Accumulative System Active MB Energy-Import | Int64 | 4 | R
0x6750 | 0x6753 | 26448 | 26451 | MB_ACCUM_EQ_MB_IMP_a_kvarh | Modbus Accumulative Phase A Reactive MB Energy-Import | Int64 | 4 | R
0x6754 | 0x6757 | 26452 | 26455 | MB_ACCUM_EQ_MB_IMP_b_kvarh | Modbus Accumulative Phase B Reactive MB Energy-Import | Int64 | 4 | R
0x6758 | 0x675B | 26456 | 26459 | MB_ACCUM_EQ_MB_IMP_c_kvarh | Modbus Accumulative Phase C Reactive MB Energy-Import | Int64 | 4 | R
0x675C | 0x675F | 26460 | 26463 | MB_ACCUM_EQ_MB_IMP_kvarh | Modbus Accumulative System Reactive MB Energy-Import | Int64 | 4 | R
0x6760 | 0x6763 | 26464 | 26467 | MB_ACCUM_EP_MB_EXP_a_kWh | Modbus Accumulative Phase A Active MB Energy-Export | Int64 | 4 | R
0x6764 | 0x6767 | 26468 | 26471 | MB_ACCUM_EP_MB_EXP_b_kWh | Modbus Accumulative Phase B Active MB Energy-Export | Int64 | 4 | R
0x6768 | 0x676B | 26472 | 26475 | MB_ACCUM_EP_MB_EXP_c_kWh | Modbus Accumulative Phase C Active MB Energy-Export | Int64 | 4 | R
0x676C | 0x676F | 26476 | 26479 | MB_ACCUM_EP_MB_EXP_kWh | Modbus Accumulative System Active MB Energy-Export | Int64 | 4 | R
0x6770 | 0x6773 | 26480 | 26483 | MB_ACCUM_EQ_MB_EXP_a_kvarh | Modbus Accumulative Phase A Reactive MB Energy-Export | Int64 | 4 | R
0x6774 | 0x6777 | 26484 | 26487 | MB_ACCUM_EQ_MB_EXP_b_kvarh | Modbus Accumulative Phase B Reactive MB Energy-Export | Int64 | 4 | R
0x6778 | 0x677B | 26488 | 26491 | MB_ACCUM_EQ_MB_EXP_c_kvarh | Modbus Accumulative Phase C Reactive MB Energy-Export | Int64 | 4 | R
0x677C | 0x677F | 26492 | 26495 | MB_ACCUM_EQ_MB_EXP_kvarh | Modbus Accumulative System Reactive MB Energy-Export | Int64 | 4 | R
0x6780 | 0x6783 | 26496 | 26499 | MB_ACCUM_EP_MB_NET_a_kWh | Modbus Accumulative Phase A Active MB Energy-Net | Int64 | 4 | R
0x6784 | 0x6787 | 26500 | 26503 | MB_ACCUM_EP_MB_NET_b_kWh | Modbus Accumulative Phase B Active MB Energy-Net | Int64 | 4 | R
0x6788 | 0x678B | 26504 | 26507 | MB_ACCUM_EP_MB_NET_c_kWh | Modbus Accumulative Phase C Active MB Energy-Net | Int64 | 4 | R
0x678C | 0x678F | 26508 | 26511 | MB_ACCUM_EP_MB_NET_kWh | Modbus Accumulative System Active MB Energy-Net | Int64 | 4 | R
0x6790 | 0x6793 | 26512 | 26515 | MB_ACCUM_EQ_MB_NET_a_kvarh | Modbus Accumulative Phase A Reactive MB Energy-Net | Int64 | 4 | R
0x6794 | 0x6797 | 26516 | 26519 | MB_ACCUM_EQ_MB_NET_b_kvarh | Modbus Accumulative Phase B Reactive MB Energy-Net | Int64 | 4 | R
0x6798 | 0x679B | 26520 | 26523 | MB_ACCUM_EQ_MB_NET_c_kvarh | Modbus Accumulative Phase C Reactive MB Energy-Net | Int64 | 4 | R
0x679C | 0x679F | 26524 | 26527 | MB_ACCUM_EQ_MB_NET_kvarh | Modbus Accumulative System Reactive MB Energy-Net | Int64 | 4 | R
0x67A0 | 0x67A3 | 26528 | 26531 | MB_ACCUM_EP_MB_TOTAL_a_kWh | Modbus Accumulative Phase A Active MB Energy-Total | Int64 | 4 | R
0x67A4 | 0x67A7 | 26532 | 26535 | MB_ACCUM_EP_MB_TOTAL_b_kWh | Modbus Accumulative Phase B Active MB Energy-Total | Int64 | 4 | R
0x67A8 | 0x67AB | 26536 | 26539 | MB_ACCUM_EP_MB_TOTAL_c_kWh | Modbus Accumulative Phase C Active MB Energy-Total | Int64 | 4 | R
0x67AC | 0x67AF | 26540 | 26543 | MB_ACCUM_EP_MB_TOTAL_kWh | Modbus Accumulative System Active MB Energy-Total | Int64 | 4 | R
0x67B0 | 0x67B3 | 26544 | 26547 | MB_ACCUM_EQ_MB_TOTAL_a_kvarh | Modbus Accumulative Phase A Reactive MB Energy-Total | Int64 | 4 | R
0x67B4 | 0x67B7 | 26548 | 26551 | MB_ACCUM_EQ_MB_TOTAL_b_kvarh | Modbus Accumulative Phase B Reactive MB Energy-Total | Int64 | 4 | R
0x67B8 | 0x67BB | 26552 | 26555 | MB_ACCUM_EQ_MB_TOTAL_c_kvarh | Modbus Accumulative Phase C Reactive MB Energy-Total | Int64 | 4 | R
0x67BC | 0x67BF | 26556 | 26559 | MB_ACCUM_EQ_MB_TOTAL_kvarh | Modbus Accumulative System Reactive MB Energy-Total | Int64 | 4 | R
0x67C0 | 0x67C3 | 26560 | 26563 | MB_ACCUM_ES_MB_a_kVAh | Modbus Accumulative Phase A Apparent MB Energy | Int64 | 4 | R
0x67C4 | 0x67C7 | 26564 | 26567 | MB_ACCUM_ES_MB_b_kVAh | Modbus Accumulative Phase B Apparent MB Energy | Int64 | 4 | R
0x67C8 | 0x67CB | 26568 | 26571 | MB_ACCUM_ES_MB_c_kVAh | Modbus Accumulative Phase C Apparent MB Energy | Int64 | 4 | R
0x67CC | 0x67CF | 26572 | 26575 | MB_ACCUM_ES_MB_kVAh | Modbus Accumulative System Apparent MB Energy | Int64 | 4 | R

## TOU
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x6D00 | 0x6D03 | 27904 | 27907 | TOU_IMP_P_TAR_TOTAL_kWh | Total TOU Import Active Energy | double | 4 | R
0x6D04 | 0x6D07 | 27908 | 27911 | TOU_IMP_P_TAR_1_kWh | Rate 1 TOU Import Active Energy | double | 4 | R
0x6D08 | 0x6D0B | 27912 | 27915 | TOU_IMP_P_TAR_2_kWh | Rate 2 TOU Import Active Energy | double | 4 | R
0x6D0C | 0x6D0F | 27916 | 27919 | TOU_IMP_P_TAR_3_kWh | Rate 3 TOU Import Active Energy | double | 4 | R
0x6D10 | 0x6D13 | 27920 | 27923 | TOU_IMP_P_TAR_4_kWh | Rate 4 TOU Import Active Energy | double | 4 | R
0x6D14 | 0x6D17 | 27924 | 27927 | TOU_IMP_P_TAR_5_kWh | Rate 5 TOU Import Active Energy | double | 4 | R
0x6D18 | 0x6D1B | 27928 | 27931 | TOU_IMP_P_TAR_6_kWh | Rate 6 TOU Import Active Energy | double | 4 | R
0x6D1C | 0x6D1F | 27932 | 27935 | TOU_IMP_P_TAR_7_kWh | Rate 7 TOU Import Active Energy | double | 4 | R
0x6D20 | 0x6D23 | 27936 | 27939 | TOU_IMP_P_TAR_8_kWh | Rate 8 TOU Import Active Energy | double | 4 | R
0x6D24 | 0x6D27 | 27940 | 27943 | TOU_IMP_Q_TAR_TOTAL_kvarh | Total TOU Import Reactive Energy | double | 4 | R
0x6D28 | 0x6D2B | 27944 | 27947 | TOU_IMP_Q_TAR_1_kvarh | Rate 1 TOU Import Reactive Energy | double | 4 | R
0x6D2C | 0x6D2F | 27948 | 27951 | TOU_IMP_Q_TAR_2_kvarh | Rate 2 TOU Import Reactive Energy | double | 4 | R
0x6D30 | 0x6D33 | 27952 | 27955 | TOU_IMP_Q_TAR_3_kvarh | Rate 3 TOU Import Reactive Energy | double | 4 | R
0x6D34 | 0x6D37 | 27956 | 27959 | TOU_IMP_Q_TAR_4_kvarh | Rate 4 TOU Import Reactive Energy | double | 4 | R
0x6D38 | 0x6D3B | 27960 | 27963 | TOU_IMP_Q_TAR_5_kvarh | Rate 5 TOU Import Reactive Energy | double | 4 | R
0x6D3C | 0x6D3F | 27964 | 27967 | TOU_IMP_Q_TAR_6_kvarh | Rate 6 TOU Import Reactive Energy | double | 4 | R
0x6D40 | 0x6D43 | 27968 | 27971 | TOU_IMP_Q_TAR_7_kvarh | Rate 7 TOU Import Reactive Energy | double | 4 | R
0x6D44 | 0x6D47 | 27972 | 27975 | TOU_IMP_Q_TAR_8_kvarh | Rate 8 TOU Import Reactive Energy | double | 4 | R
0x6D48 | 0x6D4B | 27976 | 27979 | TOU_S_TAR_TOTAL_kVAh | Total TOU Apparent Energy | double | 4 | R
0x6D4C | 0x6D4F | 27980 | 27983 | TOU_S_TAR_1_kVAh | Rate 1 TOU Apparent Energy | double | 4 | R
0x6D50 | 0x6D53 | 27984 | 27987 | TOU_S_TAR_2_kVAh | Rate 2 TOU Apparent Energy | double | 4 | R
0x6D54 | 0x6D57 | 27988 | 27991 | TOU_S_TAR_3_kVAh | Rate 3 TOU Apparent Energy | double | 4 | R
0x6D58 | 0x6D5B | 27992 | 27995 | TOU_S_TAR_4_kVAh | Rate 4 TOU Apparent Energy | double | 4 | R
0x6D5C | 0x6D5F | 27996 | 27999 | TOU_S_TAR_5_kVAh | Rate 5 TOU Apparent Energy | double | 4 | R
0x6D60 | 0x6D63 | 28000 | 28003 | TOU_S_TAR_6_kVAh | Rate 6 TOU Apparent Energy | double | 4 | R
0x6D64 | 0x6D67 | 28004 | 28007 | TOU_S_TAR_7_kVAh | Rate 7 TOU Apparent Energy | double | 4 | R
0x6D68 | 0x6D6B | 28008 | 28011 | TOU_S_TAR_8_kVAh | Rate 8 TOU Apparent Energy | double | 4 | R
0x6D6C | 0x6D6F | 28012 | 28015 | TOU_IMP_MB_P_TAR_TOTAL_kWh | Total TOU Import Active ModBus Energy | int64 | 4 | R
0x6D70 | 0x6D73 | 28016 | 28019 | TOU_IMP_MB_Q_TAR_TOTAL_kvarh | Total TOU Import Reactive ModBus Energy | int64 | 4 | R
0x6D74 | 0x6D77 | 28020 | 28023 | TOU_MB_S_TAR_TOTAL_kVAh | Total TOU Apparent ModBus Energy | int64 | 4 | R
0x6D6C | 0x6D6F | 28012 | 28015 | TOU_IMP_MB_P_TAR_TOTAL_kWh | Total TOU Import Active ModBus Energy | int64 | 4 | R
0x6D70 | 0x6D73 | 28016 | 28019 | TOU_IMP_MB_P_TAR_1_kWh | Rate 1 TOU Import Active ModBus Energy | int64 | 4 | R
0x6D74 | 0x6D77 | 28020 | 28023 | TOU_IMP_MB_P_TAR_2_kWh | Rate 2 TOU Import Active ModBus Energy | int64 | 4 | R
0x6D78 | 0x6D7B | 28024 | 28027 | TOU_IMP_MB_P_TAR_3_kWh | Rate 3 TOU Import Active ModBus Energy | int64 | 4 | R
0x6D7C | 0x6D7F | 28028 | 28031 | TOU_IMP_MB_P_TAR_4_kWh | Rate 4 TOU Import Active ModBus Energy | int64 | 4 | R
0x6D80 | 0x6D83 | 28032 | 28035 | TOU_IMP_MB_P_TAR_5_kWh | Rate 5 TOU Import Active ModBus Energy | int64 | 4 | R
0x6D84 | 0x6D87 | 28036 | 28039 | TOU_IMP_MB_P_TAR_6_kWh | Rate 6 TOU Import Active ModBus Energy | int64 | 4 | R
0x6D88 | 0x6D8B | 28040 | 28043 | TOU_IMP_MB_P_TAR_7_kWh | Rate 7 TOU Import Active ModBus Energy | int64 | 4 | R
0x6D8C | 0x6D8F | 28044 | 28047 | TOU_IMP_MB_P_TAR_8_kWh | Rate 8 TOU Import Active ModBus Energy | int64 | 4 | R
0x6D90 | 0x6D93 | 28048 | 28051 | TOU_IMP_MB_Q_TAR_TOTAL_kvarh | Total TOU Import Reactive ModBus Energy | int64 | 4 | R
0x6D94 | 0x6D97 | 28052 | 28055 | TOU_IMP_MB_Q_TAR_1_kvarh | Rate 1 TOU Import Reactive ModBus Energy | int64 | 4 | R
0x6D98 | 0x6D9B | 28056 | 28059 | TOU_IMP_MB_Q_TAR_2_kvarh | Rate 2 TOU Import Reactive ModBus Energy | int64 | 4 | R
0x6D9C | 0x6D9F | 28060 | 28063 | TOU_IMP_MB_Q_TAR_3_kvarh | Rate 3 TOU Import Reactive ModBus Energy | int64 | 4 | R
0x6DA0 | 0x6DA3 | 28064 | 28067 | TOU_IMP_MB_Q_TAR_4_kvarh | Rate 4 TOU Import Reactive ModBus Energy | int64 | 4 | R
0x6DA4 | 0x6DA7 | 28068 | 28071 | TOU_IMP_MB_Q_TAR_5_kvarh | Rate 5 TOU Import Reactive ModBus Energy | int64 | 4 | R
0x6DA8 | 0x6DAB | 28072 | 28075 | TOU_IMP_MB_Q_TAR_6_kvarh | Rate 6 TOU Import Reactive ModBus Energy | int64 | 4 | R
0x6DAC | 0x6DAF | 28076 | 28079 | TOU_IMP_MB_Q_TAR_7_kvarh | Rate 7 TOU Import Reactive ModBus Energy | int64 | 4 | R
0x6DB0 | 0x6DB3 | 28080 | 28083 | TOU_IMP_MB_Q_TAR_8_kvarh | Rate 8 TOU Import Reactive ModBus Energy | int64 | 4 | R
0x6DB4 | 0x6DB7 | 28084 | 28087 | TOU_MB_S_TAR_TOTAL_kVAh | Total TOU Apparent ModBus Energy | int64 | 4 | R
0x6DB8 | 0x6DBB | 28088 | 28091 | TOU_MB_S_TAR_1_kVAh | Rate 1 TOU Apparent ModBus Energy | int64 | 4 | R
0x6DBC | 0x6DBF | 28092 | 28095 | TOU_MB_S_TAR_2_kVAh | Rate 2 TOU Apparent ModBus Energy | int64 | 4 | R
0x6DC0 | 0x6DC3 | 28096 | 28099 | TOU_MB_S_TAR_3_kVAh | Rate 3 TOU Apparent ModBus Energy | int64 | 4 | R
0x6DC4 | 0x6DC7 | 28100 | 28103 | TOU_MB_S_TAR_4_kVAh | Rate 4 TOU Apparent ModBus Energy | int64 | 4 | R
0x6DC8 | 0x6DCB | 28104 | 28107 | TOU_MB_S_TAR_5_kVAh | Rate 5 TOU Apparent ModBus Energy | int64 | 4 | R
0x6DCC | 0x6DCF | 28108 | 28111 | TOU_MB_S_TAR_6_kVAh | Rate 6 TOU Apparent ModBus Energy | int64 | 4 | R
0x6DD0 | 0x6DD3 | 28112 | 28115 | TOU_MB_S_TAR_7_kVAh | Rate 7 TOU Apparent ModBus Energy | int64 | 4 | R
0x6DD4 | 0x6DD7 | 28116 | 28119 | TOU_MB_S_TAR_8_kVAh | Rate 8 TOU Apparent ModBus Energy | int64 | 4 | R
0x6DD8 | 0x6DD9 | 28120 | 28121 | TOU_DMD_IMP_P_TAR_TOTAL_kW | Total TOU Max Import Active Power Demand | float | 2 | R
0x6DDA | 0x6DDD | 28122 | 28125 | TOU_DMD_TIME_IMP_P_TAR_TOTAL | Total TOU Max Import Active Power Demand Time | time_t | 4 | R
0x6DDE | 0x6DDF | 28126 | 28127 | TOU_DMD_IMP_Q_TAR_TOTAL_kvar | Total TOU Max Import Reactive Power Demand | float | 2 | R
0x6DE0 | 0x6DE3 | 28128 | 28131 | TOU_DMD_TIME_IMP_Q_TAR_TOTAL | Total TOU Max Import Reactive Power Demand Time | time_t | 4 | R
0x6DE4 | 0x6DE5 | 28132 | 28133 | TOU_DMD_S_TAR_TOTAL_kVA | Total TOU Max Apparent Power Demand | float | 2 | R
0x6DE6 | 0x6DE9 | 28134 | 28137 | TOU_DMD_TIME_S_TAR_TOTAL | Total TOU Max Apparent Power Demand Time | time_t | 4 | R

## PQ Event
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x6E00 | 0x6E00 | 28160 | 28160 | PQE_V_SAG_a | Phase A PQ Event Status-Voltage Sag | bool | 1 | R
0x6E01 | 0x6E01 | 28161 | 28161 | PQE_V_SAG_b | Phase B PQ Event Status-Voltage Sag | bool | 1 | R
0x6E02 | 0x6E02 | 28162 | 28162 | PQE_V_SAG_c | Phase C PQ Event Status-Voltage Sag | bool | 1 | R
0x6E03 | 0x6E03 | 28163 | 28163 | PQE_V_SWELL_a | Phase A PQ Event Status-Voltage Swell | bool | 1 | R
0x6E04 | 0x6E04 | 28164 | 28164 | PQE_V_SWELL_b | Phase B PQ Event Status-Voltage Swell | bool | 1 | R
0x6E05 | 0x6E05 | 28165 | 28165 | PQE_V_SWELL_c | Phase C PQ Event Status-Voltage Swell | bool | 1 | R
0x6E06 | 0x6E06 | 28166 | 28166 | PQE_V_INTRP_a | Phase A PQ Event Status-Voltage Interruption | bool | 1 | R
0x6E07 | 0x6E07 | 28167 | 28167 | PQE_V_INTRP_b | Phase B PQ Event Status-Voltage Interruption | bool | 1 | R
0x6E08 | 0x6E08 | 28168 | 28168 | PQE_V_INTRP_c | Phase C PQ Event Status-Voltage Interruption | bool | 1 | R
0x6E09 | 0x6E09 | 28169 | 28169 | PQE_V_UNBL | System PQ Event Status-Voltage Unbalance | bool | 1 | R
0x6E0A | 0x6E0A | 28170 | 28170 | PQE_V_TRANS_a | Phase A PQ Event Status-Voltage Transient | bool | 1 | R
0x6E0B | 0x6E0B | 28171 | 28171 | PQE_V_TRANS_b | Phase B PQ Event Status-Voltage Transient | bool | 1 | R
0x6E0C | 0x6E0C | 28172 | 28172 | PQE_V_TRANS_c | Phase C PQ Event Status-Voltage Transient | bool | 1 | R
0x6E0D | 0x6E0D | 28173 | 28173 | PQE_I_SAG_a | Phase A PQ Event Status-Current Sag | bool | 1 | R
0x6E0E | 0x6E0E | 28174 | 28174 | PQE_I_SAG_b | Phase B PQ Event Status-Current Sag | bool | 1 | R
0x6E0F | 0x6E0F | 28175 | 28175 | PQE_I_SAG_c | Phase C PQ Event Status-Current Sag | bool | 1 | R
0x6E10 | 0x6E10 | 28176 | 28176 | PQE_I_SWELL_a | Phase A PQ Event Status-Current Swell | bool | 1 | R
0x6E11 | 0x6E11 | 28177 | 28177 | PQE_I_SWELL_b | Phase B PQ Event Status-Current Swell | bool | 1 | R
0x6E12 | 0x6E12 | 28178 | 28178 | PQE_I_SWELL_c | Phase C PQ Event Status-Current Swell | bool | 1 | R
0x6E13 | 0x6E13 | 28179 | 28179 | PQE_I_UNBL | System PQ Event Status-Current Unbalance | bool | 1 | R

## Alarm
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
0x6E14 | 0x6E14 | 28180 | 28180 | ALARM_MONITOR_01 | Alarm 1 | uint16 | 1 | R
0x6E15 | 0x6E15 | 28181 | 28181 | ALARM_MONITOR_02 | Alarm 2 | uint16 | 1 | R
0x6E16 | 0x6E16 | 28182 | 28182 | ALARM_MONITOR_03 | Alarm 3 | uint16 | 1 | R
0x6E17 | 0x6E17 | 28183 | 28183 | ALARM_MONITOR_04 | Alarm 4 | uint16 | 1 | R
0x6E18 | 0x6E18 | 28184 | 28184 | ALARM_MONITOR_05 | Alarm 5 | uint16 | 1 | R
0x6E19 | 0x6E19 | 28185 | 28185 | ALARM_MONITOR_06 | Alarm 6 | uint16 | 1 | R
0x6E1A | 0x6E1A | 28186 | 28186 | ALARM_MONITOR_07 | Alarm 7 | uint16 | 1 | R
0x6E1B | 0x6E1B | 28187 | 28187 | ALARM_MONITOR_08 | Alarm 8 | uint16 | 1 | R
0x6E1C | 0x6E1C | 28188 | 28188 | ALARM_MONITOR_09 | Alarm 9 | uint16 | 1 | R
0x6E1D | 0x6E1D | 28189 | 28189 | ALARM_MONITOR_10 | Alarm 10 | uint16 | 1 | R
0x6E1E | 0x6E1E | 28190 | 28190 | ALARM_MONITOR_11 | Alarm 11 | uint16 | 1 | R
0x6E1F | 0x6E1F | 28191 | 28191 | ALARM_MONITOR_12 | Alarm 12 | uint16 | 1 | R
0x6E20 | 0x6E20 | 28192 | 28192 | ALARM_MONITOR_13 | Alarm 13 | uint16 | 1 | R
0x6E21 | 0x6E21 | 28193 | 28193 | ALARM_MONITOR_14 | Alarm 14 | uint16 | 1 | R
0x6E22 | 0x6E22 | 28194 | 28194 | ALARM_MONITOR_15 | Alarm 15 | uint16 | 1 | R
0x6E23 | 0x6E23 | 28195 | 28195 | ALARM_MONITOR_16 | Alarm 16 | uint16 | 1 | R
0x6E24 | 0x6E24 | 28196 | 28196 | ALARM_MONITOR_17 | Alarm 17 | uint16 | 1 | R
0x6E25 | 0x6E25 | 28197 | 28197 | ALARM_MONITOR_18 | Alarm 18 | uint16 | 1 | R
0x6E26 | 0x6E26 | 28198 | 28198 | ALARM_MONITOR_19 | Alarm 19 | uint16 | 1 | R
0x6E27 | 0x6E27 | 28199 | 28199 | ALARM_MONITOR_20 | Alarm 20 | uint16 | 1 | R
0x6E28 | 0x6E28 | 28200 | 28200 | ALARM_MONITOR_21 | Alarm 21 | uint16 | 1 | R
0x6E29 | 0x6E29 | 28201 | 28201 | ALARM_MONITOR_22 | Alarm 22 | uint16 | 1 | R
0x6E2A | 0x6E2A | 28202 | 28202 | ALARM_MONITOR_23 | Alarm 23 | uint16 | 1 | R
0x6E2B | 0x6E2B | 28203 | 28203 | ALARM_MONITOR_24 | Alarm 24 | uint16 | 1 | R
0x6E2C | 0x6E2C | 28204 | 28204 | ALARM_MONITOR_25 | Alarm 25 | uint16 | 1 | R
0x6E2D | 0x6E2D | 28205 | 28205 | ALARM_MONITOR_26 | Alarm 26 | uint16 | 1 | R
0x6E2E | 0x6E2E | 28206 | 28206 | ALARM_MONITOR_27 | Alarm 27 | uint16 | 1 | R
0x6E2F | 0x6E2F | 28207 | 28207 | ALARM_MONITOR_28 | Alarm 28 | uint16 | 1 | R
0x6E30 | 0x6E30 | 28208 | 28208 | ALARM_MONITOR_29 | Alarm 29 | uint16 | 1 | R
0x6E31 | 0x6E31 | 28209 | 28209 | ALARM_MONITOR_30 | Alarm 30 | uint16 | 1 | R
0x6E32 | 0x6E32 | 28210 | 28210 | ALARM_MONITOR_31 | Alarm 31 | uint16 | 1 | R
0x6E33 | 0x6E33 | 28211 | 28211 | ALARM_MONITOR_32 | Alarm 32 | uint16 | 1 | R
0x6E34 | 0x6E34 | 28212 | 28212 | ALARM_MONITOR_33 | Alarm 33 | uint16 | 1 | R
0x6E35 | 0x6E35 | 28213 | 28213 | ALARM_MONITOR_34 | Alarm 34 | uint16 | 1 | R
0x6E36 | 0x6E36 | 28214 | 28214 | ALARM_MONITOR_35 | Alarm 35 | uint16 | 1 | R
0x6E37 | 0x6E37 | 28215 | 28215 | ALARM_MONITOR_36 | Alarm 36 | uint16 | 1 | R
0x6E38 | 0x6E38 | 28216 | 28216 | ALARM_MONITOR_37 | Alarm 37 | uint16 | 1 | R
0x6E39 | 0x6E39 | 28217 | 28217 | ALARM_MONITOR_38 | Alarm 38 | uint16 | 1 | R
0x6E3A | 0x6E3A | 28218 | 28218 | ALARM_MONITOR_39 | Alarm 39 | uint16 | 1 | R
0x6E3B | 0x6E3B | 28219 | 28219 | ALARM_MONITOR_40 | Alarm 40 | uint16 | 1 | R
0x6E3C | 0x6E3C | 28220 | 28220 | ALARM_MONITOR_41 | Alarm 41 | uint16 | 1 | R
0x6E3D | 0x6E3D | 28221 | 28221 | ALARM_MONITOR_42 | Alarm 42 | uint16 | 1 | R
0x6E3E | 0x6E3E | 28222 | 28222 | ALARM_MONITOR_43 | Alarm 43 | uint16 | 1 | R
0x6E3F | 0x6E3F | 28223 | 28223 | ALARM_MONITOR_44 | Alarm 44 | uint16 | 1 | R
0x6E40 | 0x6E40 | 28224 | 28224 | ALARM_MONITOR_45 | Alarm 45 | uint16 | 1 | R
0x6E41 | 0x6E41 | 28225 | 28225 | ALARM_MONITOR_46 | Alarm 46 | uint16 | 1 | R
0x6E42 | 0x6E42 | 28226 | 28226 | ALARM_MONITOR_47 | Alarm 47 | uint16 | 1 | R
0x6E43 | 0x6E43 | 28227 | 28227 | ALARM_MONITOR_48 | Alarm 48 | uint16 | 1 | R
0x6E44 | 0x6E44 | 28228 | 28228 | ALARM_MONITOR_49 | Alarm 49 | uint16 | 1 | R
0x6E45 | 0x6E45 | 28229 | 28229 | ALARM_MONITOR_50 | Alarm 50 | uint16 | 1 | R
0x6E46 | 0x6E46 | 28230 | 28230 | ALARM_MONITOR_51 | Alarm 51 | uint16 | 1 | R
0x6E47 | 0x6E47 | 28231 | 28231 | ALARM_MONITOR_52 | Alarm 52 | uint16 | 1 | R
0x6E48 | 0x6E48 | 28232 | 28232 | ALARM_MONITOR_53 | Alarm 53 | uint16 | 1 | R
0x6E49 | 0x6E49 | 28233 | 28233 | ALARM_MONITOR_54 | Alarm 54 | uint16 | 1 | R
0x6E4A | 0x6E4A | 28234 | 28234 | ALARM_MONITOR_55 | Alarm 55 | uint16 | 1 | R
0x6E4B | 0x6E4B | 28235 | 28235 | ALARM_MONITOR_56 | Alarm 56 | uint16 | 1 | R
0x6E4C | 0x6E4C | 28236 | 28236 | ALARM_MONITOR_57 | Alarm 57 | uint16 | 1 | R
0x6E4D | 0x6E4D | 28237 | 28237 | ALARM_MONITOR_58 | Alarm 58 | uint16 | 1 | R
0x6E4E | 0x6E4E | 28238 | 28238 | ALARM_MONITOR_59 | Alarm 59 | uint16 | 1 | R
0x6E4F | 0x6E4F | 28239 | 28239 | ALARM_MONITOR_60 | Alarm 60 | uint16 | 1 | R
0x6E50 | 0x6E50 | 28240 | 28240 | ALARM_MONITOR_61 | Alarm 61 | uint16 | 1 | R
0x6E51 | 0x6E51 | 28241 | 28241 | ALARM_MONITOR_62 | Alarm 62 | uint16 | 1 | R
0x6E52 | 0x6E52 | 28242 | 28242 | ALARM_MONITOR_63 | Alarm 63 | uint16 | 1 | R
0x6E53 | 0x6E53 | 28243 | 28243 | ALARM_MONITOR_64 | Alarm 64 | uint16 | 1 | R

## Open Short Circuit
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default
0xA74F | 0xA74F | 42831 | 42831 | Short Circuit Phase A Voltage Status |  | bool | 1 | R | 0: off 1: ON
0xA750 | 0xA750 | 42832 | 42832 | Short Circuit Phase A Current Status |  | bool | 1 | R
0xA751 | 0xA751 | 42833 | 42833 | Short Circuit Phase B Voltage Status |  | bool | 1 | R
0xA752 | 0xA752 | 42834 | 42834 | Short Circuit Phase B Current Status |  | bool | 1 | R
0xA753 | 0xA753 | 42835 | 42835 | Short Circuit Phase C Voltage Status |  | bool | 1 | R
0xA754 | 0xA754 | 42836 | 42836 | Short Circuit Phase C Current Status |  | bool | 1 | R
0xA755 | 0xA755 | 42837 | 42837 | Open Circuit Phase A Voltage Status |  | bool | 1 | R
0xA756 | 0xA756 | 42838 | 42838 | Open Circuit Phase A Current Status |  | bool | 1 | R
0xA757 | 0xA757 | 42839 | 42839 | Open Circuit Phase B Voltage Status |  | bool | 1 | R
0xA758 | 0xA758 | 42840 | 42840 | Open Circuit Phase B Current Status |  | bool | 1 | R
0xA759 | 0xA759 | 42841 | 42841 | Open Circuit Phase C Voltage Status |  | bool | 1 | R
0xA75A | 0xA75A | 42842 | 42842 | Open Circuit Phase C Current Status |  | bool | 1 | R

## IO
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
DI COUNTER
0x6E57 | 0x6E58 | 28247 | 28248 | DI_COUNTER_01_1 | IO01 DI COUNTER 1 | uint32 | 2 | R
0x6E59 | 0x6E5A | 28249 | 28250 | DI_COUNTER_01_2 | IO01 DI COUNTER 2 | uint32 | 2 | R
0x6E5B | 0x6E5C | 28251 | 28252 | DI_COUNTER_01_3 | IO01 DI COUNTER 3 | uint32 | 2 | R
0x6E5D | 0x6E5E | 28253 | 28254 | DI_COUNTER_01_4 | IO01 DI COUNTER 4 | uint32 | 2 | R
0x6E5F | 0x6E60 | 28255 | 28256 | DI_COUNTER_11_1 | IO11 DI COUNTER 1 | uint32 | 2 | R
0x6E61 | 0x6E62 | 28257 | 28258 | DI_COUNTER_11_2 | IO11 DI COUNTER 2 | uint32 | 2 | R
0x6E63 | 0x6E64 | 28259 | 28260 | DI_COUNTER_11_3 | IO11 DI COUNTER 3 | uint32 | 2 | R
0x6E65 | 0x6E66 | 28261 | 28262 | DI_COUNTER_11_4 | IO11 DI COUNTER 4 | uint32 | 2 | R
0x6E67 | 0x6E68 | 28263 | 28264 | DI_COUNTER_11_5 | IO11 DI COUNTER 5 | uint32 | 2 | R
0x6E69 | 0x6E6A | 28265 | 28266 | DI_COUNTER_11_6 | IO11 DI COUNTER 6 | uint32 | 2 | R
0x6E6B | 0x6E6C | 28267 | 28268 | DI_COUNTER_12_1 | IO12 DI COUNTER 1 | uint32 | 2 | R
0x6E6D | 0x6E6E | 28269 | 28270 | DI_COUNTER_12_2 | IO12 DI COUNTER 2 | uint32 | 2 | R
0x6E6F | 0x6E70 | 28271 | 28272 | DI_COUNTER_12_3 | IO12 DI COUNTER 3 | uint32 | 2 | R
0x6E71 | 0x6E72 | 28273 | 28274 | DI_COUNTER_12_4 | IO12 DI COUNTER 4 | uint32 | 2 | R
0x6E73 | 0x6E74 | 28275 | 28276 | DI_COUNTER_12_5 | IO12 DI COUNTER 5 | uint32 | 2 | R
0x6E75 | 0x6E76 | 28277 | 28278 | DI_COUNTER_12_6 | IO12 DI COUNTER 6 | uint32 | 2 | R
0x6E77 | 0x6E78 | 28279 | 28280 | DI_COUNTER_13_1 | IO13 DI COUNTER 1 | uint32 | 2 | R
0x6E79 | 0x6E7A | 28281 | 28282 | DI_COUNTER_13_2 | IO13 DI COUNTER 2 | uint32 | 2 | R
0x6E7B | 0x6E7C | 28283 | 28284 | DI_COUNTER_13_3 | IO13 DI COUNTER 3 | uint32 | 2 | R
0x6E7D | 0x6E7E | 28285 | 28286 | DI_COUNTER_13_4 | IO13 DI COUNTER 4 | uint32 | 2 | R
0x6E7F | 0x6E80 | 28287 | 28288 | DI_COUNTER_13_5 | IO13 DI COUNTER 5 | uint32 | 2 | R
0x6E81 | 0x6E82 | 28289 | 28290 | DI_COUNTER_13_6 | IO13 DI COUNTER 6 | uint32 | 2 | R
0x6E83 | 0x6E84 | 28291 | 28292 | DI_COUNTER_14_1 | IO14 DI COUNTER 1 | uint32 | 2 | R
0x6E85 | 0x6E86 | 28293 | 28294 | DI_COUNTER_14_2 | IO14 DI COUNTER 2 | uint32 | 2 | R
0x6E87 | 0x6E88 | 28295 | 28296 | DI_COUNTER_14_3 | IO14 DI COUNTER 3 | uint32 | 2 | R
0x6E89 | 0x6E8A | 28297 | 28298 | DI_COUNTER_14_4 | IO14 DI COUNTER 4 | uint32 | 2 | R
0x6E8B | 0x6E8C | 28299 | 28300 | DI_COUNTER_14_5 | IO14 DI COUNTER 5 | uint32 | 2 | R
0x6E8D | 0x6E8E | 28301 | 28302 | DI_COUNTER_14_6 | IO14 DI COUNTER 6 | uint32 | 2 | R
0x6E8F | 0x6E90 | 28303 | 28304 | DI_COUNTER_21_1 | IO21 DI COUNTER 1 | uint32 | 2 | R
0x6E91 | 0x6E92 | 28305 | 28306 | DI_COUNTER_21_2 | IO21 DI COUNTER 2 | uint32 | 2 | R
0x6E93 | 0x6E94 | 28307 | 28308 | DI_COUNTER_21_3 | IO21 DI COUNTER 3 | uint32 | 2 | R
0x6E95 | 0x6E96 | 28309 | 28310 | DI_COUNTER_21_4 | IO21 DI COUNTER 4 | uint32 | 2 | R
0x6E97 | 0x6E98 | 28311 | 28312 | DI_COUNTER_22_1 | IO22 DI COUNTER 1 | uint32 | 2 | R
0x6E99 | 0x6E9A | 28313 | 28314 | DI_COUNTER_22_2 | IO22 DI COUNTER 2 | uint32 | 2 | R
0x6E9B | 0x6E9C | 28315 | 28316 | DI_COUNTER_22_3 | IO22 DI COUNTER 3 | uint32 | 2 | R
0x6E9D | 0x6E9E | 28317 | 28318 | DI_COUNTER_22_4 | IO22 DI COUNTER 4 | uint32 | 2 | R
0x6E9F | 0x6EA0 | 28319 | 28320 | DI_COUNTER_23_1 | IO23 DI COUNTER 1 | uint32 | 2 | R
0x6EA1 | 0x6EA2 | 28321 | 28322 | DI_COUNTER_23_2 | IO23 DI COUNTER 2 | uint32 | 2 | R
0x6EA3 | 0x6EA4 | 28323 | 28324 | DI_COUNTER_23_3 | IO23 DI COUNTER 3 | uint32 | 2 | R
0x6EA5 | 0x6EA6 | 28325 | 28326 | DI_COUNTER_23_4 | IO23 DI COUNTER 4 | uint32 | 2 | R
0x6EA7 | 0x6EA8 | 28327 | 28328 | DI_COUNTER_24_1 | IO24 DI COUNTER 1 | uint32 | 2 | R
0x6EA9 | 0x6EAA | 28329 | 28330 | DI_COUNTER_24_2 | IO24 DI COUNTER 2 | uint32 | 2 | R
0x6EAB | 0x6EAC | 28331 | 28332 | DI_COUNTER_24_3 | IO24 DI COUNTER 3 | uint32 | 2 | R
0x6EAD | 0x6EAE | 28333 | 28334 | DI_COUNTER_24_4 | IO24 DI COUNTER 4 | uint32 | 2 | R
0x6EAF | 0x6EB0 | 28335 | 28336 | DI_COUNTER_31_1 | IO31 DI COUNTER 1 | uint32 | 2 | R
0x6EB1 | 0x6EB2 | 28337 | 28338 | DI_COUNTER_31_2 | IO31 DI COUNTER 2 | uint32 | 2 | R
0x6EB3 | 0x6EB4 | 28339 | 28340 | DI_COUNTER_31_3 | IO31 DI COUNTER 3 | uint32 | 2 | R
0x6EB5 | 0x6EB6 | 28341 | 28342 | DI_COUNTER_31_4 | IO31 DI COUNTER 4 | uint32 | 2 | R
0x6EB7 | 0x6EB8 | 28343 | 28344 | DI_COUNTER_32_1 | IO32 DI COUNTER 1 | uint32 | 2 | R
0x6EB9 | 0x6EBA | 28345 | 28346 | DI_COUNTER_32_2 | IO32 DI COUNTER 2 | uint32 | 2 | R
0x6EBB | 0x6EBC | 28347 | 28348 | DI_COUNTER_32_3 | IO32 DI COUNTER 3 | uint32 | 2 | R
0x6EBD | 0x6EBE | 28349 | 28350 | DI_COUNTER_32_4 | IO32 DI COUNTER 4 | uint32 | 2 | R
0x6EBF | 0x6EC0 | 28351 | 28352 | DI_COUNTER_33_1 | IO33 DI COUNTER 1 | uint32 | 2 | R
0x6EC1 | 0x6EC2 | 28353 | 28354 | DI_COUNTER_33_2 | IO33 DI COUNTER 2 | uint32 | 2 | R
0x6EC3 | 0x6EC4 | 28355 | 28356 | DI_COUNTER_33_3 | IO33 DI COUNTER 3 | uint32 | 2 | R
0x6EC5 | 0x6EC6 | 28357 | 28358 | DI_COUNTER_33_4 | IO33 DI COUNTER 4 | uint32 | 2 | R
0x6EC7 | 0x6EC8 | 28359 | 28360 | DI_COUNTER_34_1 | IO34 DI COUNTER 1 | uint32 | 2 | R
0x6EC9 | 0x6ECA | 28361 | 28362 | DI_COUNTER_34_2 | IO34 DI COUNTER 2 | uint32 | 2 | R
0x6ECB | 0x6ECC | 28363 | 28364 | DI_COUNTER_34_3 | IO34 DI COUNTER 3 | uint32 | 2 | R
0x6ECD | 0x6ECE | 28365 | 28366 | DI_COUNTER_34_4 | IO34 DI COUNTER 4 | uint32 | 2 | R
DI STATUS |  | Read: 0x02 Read Discrete Inputs
0x0 | 0x0 | 0 | 0 | DI_STATUS_01_1 | IO01 DI STATUS 1 | bool | 1 | R
0x1 | 0x1 | 1 | 1 | DI_STATUS_01_2 | IO01 DI STATUS 2 | bool | 1 | R
0x2 | 0x2 | 2 | 2 | DI_STATUS_01_3 | IO01 DI STATUS 3 | bool | 1 | R
0x3 | 0x3 | 3 | 3 | DI_STATUS_01_4 | IO01 DI STATUS 4 | bool | 1 | R
0x4 | 0x4 | 4 | 4 | DI_STATUS_11_1 | IO11 DI STATUS 1 | bool | 1 | R
0x5 | 0x5 | 5 | 5 | DI_STATUS_11_2 | IO11 DI STATUS 2 | bool | 1 | R
0x6 | 0x6 | 6 | 6 | DI_STATUS_11_3 | IO11 DI STATUS 3 | bool | 1 | R
0x7 | 0x7 | 7 | 7 | DI_STATUS_11_4 | IO11 DI STATUS 4 | bool | 1 | R
0x8 | 0x8 | 8 | 8 | DI_STATUS_11_5 | IO11 DI STATUS 5 | bool | 1 | R
0x9 | 0x9 | 9 | 9 | DI_STATUS_11_6 | IO11 DI STATUS 6 | bool | 1 | R
0xA | 0xA | 10 | 10 | DI_STATUS_12_1 | IO12 DI STATUS 1 | bool | 1 | R
0xB | 0xB | 11 | 11 | DI_STATUS_12_2 | IO12 DI STATUS 2 | bool | 1 | R
0xC | 0xC | 12 | 12 | DI_STATUS_12_3 | IO12 DI STATUS 3 | bool | 1 | R
0xD | 0xD | 13 | 13 | DI_STATUS_12_4 | IO12 DI STATUS 4 | bool | 1 | R
0xE | 0xE | 14 | 14 | DI_STATUS_12_5 | IO12 DI STATUS 5 | bool | 1 | R
0xF | 0xF | 15 | 15 | DI_STATUS_12_6 | IO12 DI STATUS 6 | bool | 1 | R
0x10 | 0x10 | 16 | 16 | DI_STATUS_13_1 | IO13 DI STATUS 1 | bool | 1 | R
0x11 | 0x11 | 17 | 17 | DI_STATUS_13_2 | IO13 DI STATUS 2 | bool | 1 | R
0x12 | 0x12 | 18 | 18 | DI_STATUS_13_3 | IO13 DI STATUS 3 | bool | 1 | R
0x13 | 0x13 | 19 | 19 | DI_STATUS_13_4 | IO13 DI STATUS 4 | bool | 1 | R
0x14 | 0x14 | 20 | 20 | DI_STATUS_13_5 | IO13 DI STATUS 5 | bool | 1 | R
0x15 | 0x15 | 21 | 21 | DI_STATUS_13_6 | IO13 DI STATUS 6 | bool | 1 | R
0x16 | 0x16 | 22 | 22 | DI_STATUS_14_1 | IO14 DI STATUS 1 | bool | 1 | R
0x17 | 0x17 | 23 | 23 | DI_STATUS_14_2 | IO14 DI STATUS 2 | bool | 1 | R
0x18 | 0x18 | 24 | 24 | DI_STATUS_14_3 | IO14 DI STATUS 3 | bool | 1 | R
0x19 | 0x19 | 25 | 25 | DI_STATUS_14_4 | IO14 DI STATUS 4 | bool | 1 | R
0x1A | 0x1A | 26 | 26 | DI_STATUS_14_5 | IO14 DI STATUS 5 | bool | 1 | R
0x1B | 0x1B | 27 | 27 | DI_STATUS_14_6 | IO14 DI STATUS 6 | bool | 1 | R
0x1C | 0x1C | 28 | 28 | DI_STATUS_21_1 | IO21 DI STATUS 1 | bool | 1 | R
0x1D | 0x1D | 29 | 29 | DI_STATUS_21_2 | IO21 DI STATUS 2 | bool | 1 | R
0x1E | 0x1E | 30 | 30 | DI_STATUS_21_3 | IO21 DI STATUS 3 | bool | 1 | R
0x1F | 0x1F | 31 | 31 | DI_STATUS_21_4 | IO21 DI STATUS 4 | bool | 1 | R
0x20 | 0x20 | 32 | 32 | DI_STATUS_22_1 | IO22 DI STATUS 1 | bool | 1 | R
0x21 | 0x21 | 33 | 33 | DI_STATUS_22_2 | IO22 DI STATUS 2 | bool | 1 | R
0x22 | 0x22 | 34 | 34 | DI_STATUS_22_3 | IO22 DI STATUS 3 | bool | 1 | R
0x23 | 0x23 | 35 | 35 | DI_STATUS_22_4 | IO22 DI STATUS 4 | bool | 1 | R
0x24 | 0x24 | 36 | 36 | DI_STATUS_23_1 | IO23 DI STATUS 1 | bool | 1 | R
0x25 | 0x25 | 37 | 37 | DI_STATUS_23_2 | IO23 DI STATUS 2 | bool | 1 | R
0x26 | 0x26 | 38 | 38 | DI_STATUS_23_3 | IO23 DI STATUS 3 | bool | 1 | R
0x27 | 0x27 | 39 | 39 | DI_STATUS_23_4 | IO23 DI STATUS 4 | bool | 1 | R
0x28 | 0x28 | 40 | 40 | DI_STATUS_24_1 | IO24 DI STATUS 1 | bool | 1 | R
0x29 | 0x29 | 41 | 41 | DI_STATUS_24_2 | IO24 DI STATUS 2 | bool | 1 | R
0x2A | 0x2A | 42 | 42 | DI_STATUS_24_3 | IO24 DI STATUS 3 | bool | 1 | R
0x2B | 0x2B | 43 | 43 | DI_STATUS_24_4 | IO24 DI STATUS 4 | bool | 1 | R
0x2C | 0x2C | 44 | 44 | DI_STATUS_31_1 | IO31 DI STATUS 1 | bool | 1 | R
0x2D | 0x2D | 45 | 45 | DI_STATUS_31_2 | IO31 DI STATUS 2 | bool | 1 | R
0x2E | 0x2E | 46 | 46 | DI_STATUS_31_3 | IO31 DI STATUS 3 | bool | 1 | R
0x2F | 0x2F | 47 | 47 | DI_STATUS_31_4 | IO31 DI STATUS 4 | bool | 1 | R
0x30 | 0x30 | 48 | 48 | DI_STATUS_32_1 | IO32 DI STATUS 1 | bool | 1 | R
0x31 | 0x31 | 49 | 49 | DI_STATUS_32_2 | IO32 DI STATUS 2 | bool | 1 | R
0x32 | 0x32 | 50 | 50 | DI_STATUS_32_3 | IO32 DI STATUS 3 | bool | 1 | R
0x33 | 0x33 | 51 | 51 | DI_STATUS_32_4 | IO32 DI STATUS 4 | bool | 1 | R
0x34 | 0x34 | 52 | 52 | DI_STATUS_33_1 | IO33 DI STATUS 1 | bool | 1 | R
0x35 | 0x35 | 53 | 53 | DI_STATUS_33_2 | IO33 DI STATUS 2 | bool | 1 | R
0x36 | 0x36 | 54 | 54 | DI_STATUS_33_3 | IO33 DI STATUS 3 | bool | 1 | R
0x37 | 0x37 | 55 | 55 | DI_STATUS_33_4 | IO33 DI STATUS 4 | bool | 1 | R
0x38 | 0x38 | 56 | 56 | DI_STATUS_34_1 | IO34 DI STATUS 1 | bool | 1 | R
0x39 | 0x39 | 57 | 57 | DI_STATUS_34_2 | IO34 DI STATUS 2 | bool | 1 | R
0x3A | 0x3A | 58 | 58 | DI_STATUS_34_3 | IO34 DI STATUS 3 | bool | 1 | R
0x3B | 0x3B | 59 | 59 | DI_STATUS_34_4 | IO34 DI STATUS 4 | bool | 1 | R
RO |  | Read: 0x01 Read Coils
0x0 | 0x0 | 0 | 0 | RO_11_1 | IO11 RO 1 | bool | 1 | R
0x1 | 0x1 | 1 | 1 | RO_11_2 | IO11 RO 2 | bool | 1 | R
0x2 | 0x2 | 2 | 2 | RO_12_1 | IO12 RO 1 | bool | 1 | R
0x3 | 0x3 | 3 | 3 | RO_12_2 | IO12 RO 2 | bool | 1 | R
0x4 | 0x4 | 4 | 4 | RO_13_1 | IO13 RO 1 | bool | 1 | R
0x5 | 0x5 | 5 | 5 | RO_13_2 | IO13 RO 2 | bool | 1 | R
0x6 | 0x6 | 6 | 6 | RO_14_1 | IO14 RO 1 | bool | 1 | R
0x7 | 0x7 | 7 | 7 | RO_14_2 | IO14 RO 2 | bool | 1 | R
0x8 | 0x8 | 8 | 8 | RO_31_1 | IO31 RO 1 | bool | 1 | R
0x9 | 0x9 | 9 | 9 | RO_31_2 | IO31 RO 2 | bool | 1 | R
0xA | 0xA | 10 | 10 | RO_32_1 | IO32 RO 1 | bool | 1 | R
0xB | 0xB | 11 | 11 | RO_32_2 | IO32 RO 2 | bool | 1 | R
0xC | 0xC | 12 | 12 | RO_33_1 | IO33 RO 1 | bool | 1 | R
0xD | 0xD | 13 | 13 | RO_33_2 | IO33 RO 2 | bool | 1 | R
0xE | 0xE | 14 | 14 | RO_34_1 | IO34 RO 1 | bool | 1 | R
0xF | 0xF | 15 | 15 | RO_34_2 | IO34 RO 2 | bool | 1 | R
AI
Input
0x6ECF | 0x6ED0 | 28367 | 28368 | AI_31_1 | IO31 AI 1 | float | 2 | R
0x6ED1 | 0x6ED2 | 28369 | 28370 | AI_31_2 | IO31 AI 2 | float | 2 | R
0x6ED3 | 0x6ED4 | 28371 | 28372 | AI_32_1 | IO32 AI 1 | float | 2 | R
0x6ED5 | 0x6ED6 | 28373 | 28374 | AI_32_2 | IO32 AI 2 | float | 2 | R
0x6ED7 | 0x6ED8 | 28375 | 28376 | AI_33_1 | IO33 AI 1 | float | 2 | R
0x6ED9 | 0x6EDA | 28377 | 28378 | AI_33_2 | IO33 AI 2 | float | 2 | R
0x6EDB | 0x6EDC | 28379 | 28380 | AI_34_1 | IO34 AI 1 | float | 2 | R
0x6EDD | 0x6EDE | 28381 | 28382 | AI_34_2 | IO34 AI 2 | float | 2 | R
Reading
0x6EEF | 0x6EF0 | 28399 | 28400 | AI_31_1 | IO31 AI 1 | float | 2 | R
0x6EF1 | 0x6EF2 | 28401 | 28402 | AI_31_2 | IO31 AI 2 | float | 2 | R
0x6EF3 | 0x6EF4 | 28403 | 28404 | AI_32_1 | IO32 AI 1 | float | 2 | R
0x6EF5 | 0x6EF6 | 28405 | 28406 | AI_32_2 | IO32 AI 2 | float | 2 | R
0x6EF7 | 0x6EF8 | 28407 | 28408 | AI_33_1 | IO33 AI 1 | float | 2 | R
0x6EF9 | 0x6EFA | 28409 | 28410 | AI_33_2 | IO33 AI 2 | float | 2 | R
0x6EFB | 0x6EFC | 28411 | 28412 | AI_34_1 | IO34 AI 1 | float | 2 | R
0x6EFD | 0x6EFE | 28413 | 28414 | AI_34_2 | IO34 AI 2 | float | 2 | R
AO
0x6EDF | 0x6EE0 | 28383 | 28384 | AO_21_1 | IO21 AO 1 | float | 2 | R
0x6EE1 | 0x6EE2 | 28385 | 28386 | AO_21_2 | IO21 AO 2 | float | 2 | R
0x6EE3 | 0x6EE4 | 28387 | 28388 | AO_22_1 | IO22 AO 1 | float | 2 | R
0x6EE5 | 0x6EE6 | 28389 | 28390 | AO_22_2 | IO22 AO 2 | float | 2 | R
0x6EE7 | 0x6EE8 | 28391 | 28392 | AO_23_1 | IO23 AO 1 | float | 2 | R
0x6EE9 | 0x6EEA | 28393 | 28394 | AO_23_2 | IO23 AO 2 | float | 2 | R
0x6EEB | 0x6EEC | 28395 | 28396 | AO_24_1 | IO24 AO 1 | float | 2 | R
0x6EED | 0x6EEE | 28397 | 28398 | AO_24_2 | IO24 AO 2 | float | 2 | R

## PQ Report 50160
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
PQ Report 50160 Current
0x7000 | 0x7000 | 28672 | 28672 | 10S_N_VALID | 10sec Voltage Valid Counter | uint16 | 1 | R
0x7001 | 0x7001 | 28673 | 28673 | 10S_N_INVALID | 10sec Voltage Invalid Counter | uint16 | 1 | R
0x7002 | 0x7002 | 28674 | 28674 | 10S_N_FREQ1 | 10sec 1st Frequency Bin Counter | uint16 | 1 | R
0x7003 | 0x7003 | 28675 | 28675 | 10S_N_FREQ2 | 10sec 2nd Frequency Bin Counter | uint16 | 1 | R
0x7004 | 0x7004 | 28676 | 28676 | 10S_N_FREQ3 | 10sec 3rd Frequency Bin Counter | uint16 | 1 | R
0x7005 | 0x7005 | 28677 | 28677 | 10S_N_FREQ4 | 10sec 4th Frequency Bin Counter | uint16 | 1 | R
0x7006 | 0x7006 | 28678 | 28678 | 10S_N_FREQ5 | 10sec 5th Frequency Bin Counter | uint16 | 1 | R
0x7007 | 0x7008 | 28679 | 28680 | 10S_FREQ_PASS1 | 10sec 1st Frequency Zone Trigger Pass Rate | float | 2 | R
0x7009 | 0x700A | 28681 | 28682 | 10S_FREQ_PASS2 | 10sec 2nd Frequency Zone Trigger Pass Rate | float | 2 | R
0x700B | 0x700C | 28683 | 28684 | 10S_FREQ_MAX | 10sec Frequency Maximum Value | float | 2 | R
0x700D | 0x700E | 28685 | 28686 | 10S_FREQ_MIN | 10sec Frequency Minimum Value | float | 2 | R
0x700F | 0x7010 | 28687 | 28688 | 10S_FREQ_AVG | 10sec Frequency Average Value | float | 2 | R
0x7011 | 0x7011 | 28689 | 28689 | 10S_N_INTRPT1 | 10sec 1st PQ Event Interrupt Counter | uint16 | 1 | R
0x7012 | 0x7012 | 28690 | 28690 | 10S_N_INTRPT2 | 10sec 2nd PQ Event Interrupt Counter | uint16 | 1 | R
0x7013 | 0x7013 | 28691 | 28691 | 10S_N_INTRPT3 | 10sec 3rd PQ Event Interrupt Counter | uint16 | 1 | R
0x7014 | 0x7014 | 28692 | 28692 | 10S_N_DIP_A1 | 10sec 1st PQ Event Voltage Dips Cell-A Counter | uint16 | 1 | R
0x7015 | 0x7015 | 28693 | 28693 | 10S_N_DIP_A2 | 10sec 2nd PQ Event Voltage Dips Cell-A Counter | uint16 | 1 | R
0x7016 | 0x7016 | 28694 | 28694 | 10S_N_DIP_A3 | 10sec 3rd PQ Event Voltage Dips Cell-A Counter | uint16 | 1 | R
0x7017 | 0x7017 | 28695 | 28695 | 10S_N_DIP_A4 | 10sec 4th PQ Event Voltage Dips Cell-A Counter | uint16 | 1 | R
0x7018 | 0x7018 | 28696 | 28696 | 10S_N_DIP_A5 | 10sec 5th PQ Event Voltage Dips Cell-A Counter | uint16 | 1 | R
0x7019 | 0x7019 | 28697 | 28697 | 10S_N_DIP_B1 | 10sec 1st PQ Event Voltage Dips Cell-B Counter | uint16 | 1 | R
0x701A | 0x701A | 28698 | 28698 | 10S_N_DIP_B2 | 10sec 2nd PQ Event Voltage Dips Cell-B Counter | uint16 | 1 | R
0x701B | 0x701B | 28699 | 28699 | 10S_N_DIP_B3 | 10sec 3rd PQ Event Voltage Dips Cell-B Counter | uint16 | 1 | R
0x701C | 0x701C | 28700 | 28700 | 10S_N_DIP_B4 | 10sec 4th PQ Event Voltage Dips Cell-B Counter | uint16 | 1 | R
0x701D | 0x701D | 28701 | 28701 | 10S_N_DIP_B5 | 10sec 5th PQ Event Voltage Dips Cell-B Counter | uint16 | 1 | R
0x701E | 0x701E | 28702 | 28702 | 10S_N_DIP_C1 | 10sec 1st PQ Event Voltage Dips Cell-C Counter | uint16 | 1 | R
0x701F | 0x701F | 28703 | 28703 | 10S_N_DIP_C2 | 10sec 2nd PQ Event Voltage Dips Cell-C Counter | uint16 | 1 | R
0x7020 | 0x7020 | 28704 | 28704 | 10S_N_DIP_C3 | 10sec 3rd PQ Event Voltage Dips Cell-C Counter | uint16 | 1 | R
0x7021 | 0x7021 | 28705 | 28705 | 10S_N_DIP_C4 | 10sec 4th PQ Event Voltage Dips Cell-C Counter | uint16 | 1 | R
0x7022 | 0x7022 | 28706 | 28706 | 10S_N_DIP_C5 | 10sec 5th PQ Event Voltage Dips Cell-C Counter | uint16 | 1 | R
0x7023 | 0x7023 | 28707 | 28707 | 10S_N_DIP_D1 | 10sec 1st PQ Event Voltage Dips Cell-D Counter | uint16 | 1 | R
0x7024 | 0x7024 | 28708 | 28708 | 10S_N_DIP_D2 | 10sec 2nd PQ Event Voltage Dips Cell-D Counter | uint16 | 1 | R
0x7025 | 0x7025 | 28709 | 28709 | 10S_N_DIP_D3 | 10sec 3rd PQ Event Voltage Dips Cell-D Counter | uint16 | 1 | R
0x7026 | 0x7026 | 28710 | 28710 | 10S_N_DIP_D4 | 10sec 4th PQ Event Voltage Dips Cell-D Counter | uint16 | 1 | R
0x7027 | 0x7027 | 28711 | 28711 | 10S_N_DIP_D5 | 10sec 5th PQ Event Voltage Dips Cell-D Counter | uint16 | 1 | R
0x7028 | 0x7028 | 28712 | 28712 | 10S_N_DIP_X1 | 10sec 1st PQ Event Voltage Dips Cell-X Counter | uint16 | 1 | R
0x7029 | 0x7029 | 28713 | 28713 | 10S_N_DIP_X2 | 10sec 2nd PQ Event Voltage Dips Cell-X Counter | uint16 | 1 | R
0x702A | 0x702A | 28714 | 28714 | 10S_N_DIP_X3 | 10sec 3rd PQ Event Voltage Dips Cell-X Counter | uint16 | 1 | R
0x702B | 0x702B | 28715 | 28715 | 10S_N_DIP_X4 | 10sec 4th PQ Event Voltage Dips Cell-X Counter | uint16 | 1 | R
0x702C | 0x702C | 28716 | 28716 | 10S_N_DIP_X5 | 10sec 5th PQ Event Voltage Dips Cell-X Counter | uint16 | 1 | R
0x702D | 0x702D | 28717 | 28717 | 10S_N_SWELL_S1 | 10sec 1st PQ Event Voltage Swells Cell-S Counter | uint16 | 1 | R
0x702E | 0x702E | 28718 | 28718 | 10S_N_SWELL_S2 | 10sec 2nd PQ Event Voltage Swells Cell-S Counter | uint16 | 1 | R
0x702F | 0x702F | 28719 | 28719 | 10S_N_SWELL_S3 | 10sec 3rd PQ Event Voltage Swells Cell-S Counter | uint16 | 1 | R
0x7030 | 0x7030 | 28720 | 28720 | 10S_N_SWELL_T1 | 10sec 1st PQ Event Voltage Swells Cell-T Counter | uint16 | 1 | R
0x7031 | 0x7031 | 28721 | 28721 | 10S_N_SWELL_T2 | 10sec 2nd PQ Event Voltage Swells Cell-T Counter | uint16 | 1 | R
0x7032 | 0x7032 | 28722 | 28722 | 10S_N_SWELL_T3 | 10sec 3rd PQ Event Voltage Swells Cell-T Counter | uint16 | 1 | R
0x7033 | 0x7033 | 28723 | 28723 | 10M_N_VALID | 10min Voltage Valid Counter | uint16 | 1 | R
0x7034 | 0x7034 | 28724 | 28724 | 10M_N_INVALID | 10min Voltage Invalid Counter | uint16 | 1 | R
0x7035 | 0x7035 | 28725 | 28725 | 10M_N_RMSa1 | 10min 1st Phase A RMS Voltage Bin Counter | uint16 | 1 | R
0x7036 | 0x7036 | 28726 | 28726 | 10M_N_RMSa2 | 10min 2nd Phase A RMS Voltage Bin Counter | uint16 | 1 | R
0x7037 | 0x7037 | 28727 | 28727 | 10M_N_RMSa3 | 10min 3rd Phase A RMS Voltage Bin Counter | uint16 | 1 | R
0x7038 | 0x7038 | 28728 | 28728 | 10M_N_RMSa4 | 10min 4th Phase A RMS Voltage Bin Counter | uint16 | 1 | R
0x7039 | 0x7039 | 28729 | 28729 | 10M_N_RMSa5 | 10min 5th Phase A RMS Voltage Bin Counter | uint16 | 1 | R
0x703A | 0x703A | 28730 | 28730 | 10M_N_RMSb1 | 10min 1st Phase B RMS Voltage Bin Counter | uint16 | 1 | R
0x703B | 0x703B | 28731 | 28731 | 10M_N_RMSb2 | 10min 2nd Phase B RMS Voltage Bin Counter | uint16 | 1 | R
0x703C | 0x703C | 28732 | 28732 | 10M_N_RMSb3 | 10min 3rd Phase B RMS Voltage Bin Counter | uint16 | 1 | R
0x703D | 0x703D | 28733 | 28733 | 10M_N_RMSb4 | 10min 4th Phase B RMS Voltage Bin Counter | uint16 | 1 | R
0x703E | 0x703E | 28734 | 28734 | 10M_N_RMSb5 | 10min 5th Phase B RMS Voltage Bin Counter | uint16 | 1 | R
0x703F | 0x703F | 28735 | 28735 | 10M_N_RMSc1 | 10min 1st Phase C RMS Voltage Bin Counter | uint16 | 1 | R
0x7040 | 0x7040 | 28736 | 28736 | 10M_N_RMSc2 | 10min 2nd Phase C RMS Voltage Bin Counter | uint16 | 1 | R
0x7041 | 0x7041 | 28737 | 28737 | 10M_N_RMSc3 | 10min 3rd Phase C RMS Voltage Bin Counter | uint16 | 1 | R
0x7042 | 0x7042 | 28738 | 28738 | 10M_N_RMSc4 | 10min 4th Phase C RMS Voltage Bin Counter | uint16 | 1 | R
0x7043 | 0x7043 | 28739 | 28739 | 10M_N_RMSc5 | 10min 5th Phase C RMS Voltage Bin Counter | uint16 | 1 | R
0x7044 | 0x7045 | 28740 | 28741 | 10M_RMS_PASSa1 | 10min 1st Phase A RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x7046 | 0x7047 | 28742 | 28743 | 10M_RMS_PASSa2 | 10min 2nd Phase A RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x7048 | 0x7049 | 28744 | 28745 | 10M_RMS_PASSb1 | 10min 1st Phase B RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x704A | 0x704B | 28746 | 28747 | 10M_RMS_PASSb2 | 10min 2nd Phase B RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x704C | 0x704D | 28748 | 28749 | 10M_RMS_PASSc1 | 10min 1st Phase C RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x704E | 0x704F | 28750 | 28751 | 10M_RMS_PASSc2 | 10min 2nd Phase C RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x7050 | 0x7051 | 28752 | 28753 | 10M_RMS_MAXa | 10min Phase A RMS Voltage Maximum Value | float | 2 | R
0x7052 | 0x7053 | 28754 | 28755 | 10M_RMS_MAXb | 10min Phase B RMS Voltage Maximum Value | float | 2 | R
0x7054 | 0x7055 | 28756 | 28757 | 10M_RMS_MAXc | 10min Phase C RMS Voltage Maximum Value | float | 2 | R
0x7056 | 0x7057 | 28758 | 28759 | 10M_RMS_MINa | 10min Phase A RMS Voltage Minimum Value | float | 2 | R
0x7058 | 0x7059 | 28760 | 28761 | 10M_RMS_MINb | 10min Phase B RMS Voltage Minimum Value | float | 2 | R
0x705A | 0x705B | 28762 | 28763 | 10M_RMS_MINc | 10min Phase C RMS Voltage Minimum Value | float | 2 | R
0x705C | 0x705D | 28764 | 28765 | 10M_RMS_AVGa | 10min Phase A RMS Voltage Average Value | float | 2 | R
0x705E | 0x705F | 28766 | 28767 | 10M_RMS_AVGb | 10min Phase B RMS Voltage Average Value | float | 2 | R
0x7060 | 0x7061 | 28768 | 28769 | 10M_RMS_AVGc | 10min Phase C RMS Voltage Average Value | float | 2 | R
0x7062 | 0x7062 | 28770 | 28770 | 10M_N_PSTa1 | 10min 1st Phase A Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7063 | 0x7063 | 28771 | 28771 | 10M_N_PSTa2 | 10min 2nd Phase A Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7064 | 0x7064 | 28772 | 28772 | 10M_N_PSTb1 | 10min 1st Phase B Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7065 | 0x7065 | 28773 | 28773 | 10M_N_PSTb2 | 10min 2nd Phase B Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7066 | 0x7066 | 28774 | 28774 | 10M_N_PSTc1 | 10min 1st Phase C Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7067 | 0x7067 | 28775 | 28775 | 10M_N_PSTc2 | 10min 2nd Phase C Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7068 | 0x7069 | 28776 | 28777 | 10M_PST_PASSa | 10min Phase A Flicker Severity Short-term Zone Trigger Pass Rate | float | 2 | R
0x706A | 0x706B | 28778 | 28779 | 10M_PST_PASSb | 10min Phase B Flicker Severity Short-term Zone Trigger Pass Rate | float | 2 | R
0x706C | 0x706D | 28780 | 28781 | 10M_PST_PASSc | 10min Phase C Flicker Severity Short-term Zone Trigger Pass Rate | float | 2 | R
0x706E | 0x706F | 28782 | 28783 | 10M_PST_MAXa | 10min Phase A Flicker Severity Short-term Maximum Value | float | 2 | R
0x7070 | 0x7071 | 28784 | 28785 | 10M_PST_MAXb | 10min Phase B Flicker Severity Short-term Maximum Value | float | 2 | R
0x7072 | 0x7073 | 28786 | 28787 | 10M_PST_MAXc | 10min Phase C Flicker Severity Short-term Maximum Value | float | 2 | R
0x7074 | 0x7075 | 28788 | 28789 | 10M_PST_MINa | 10min Phase A Flicker Severity Short-term Minimum Value | float | 2 | R
0x7076 | 0x7077 | 28790 | 28791 | 10M_PST_MINb | 10min Phase B Flicker Severity Short-term Minimum Value | float | 2 | R
0x7078 | 0x7079 | 28792 | 28793 | 10M_PST_MINc | 10min Phase C Flicker Severity Short-term Minimum Value | float | 2 | R
0x707A | 0x707B | 28794 | 28795 | 10M_PST_AVGa | 10min Phase A Flicker Severity Short-term Average Value | float | 2 | R
0x707C | 0x707D | 28796 | 28797 | 10M_PST_AVGb | 10min Phase B Flicker Severity Short-term Average Value | float | 2 | R
0x707E | 0x707F | 28798 | 28799 | 10M_PST_AVGc | 10min Phase C Flicker Severity Short-term Average Value | float | 2 | R
0x7080 | 0x7080 | 28800 | 28800 | 10M_N_UNBL1 | 10min 1st Voltage Unbalance Bin Counter | uint16 | 1 | R
0x7081 | 0x7081 | 28801 | 28801 | 10M_N_UNBL2 | 10min 2nd Voltage Unbalance Bin Counter | uint16 | 1 | R
0x7082 | 0x7083 | 28802 | 28803 | 10M_UNBL_PASS | 10min Voltage Unbalance Zone Trigger Pass Rate | float | 2 | R
0x7084 | 0x7085 | 28804 | 28805 | 10M_UNBL_MAX | 10min Voltage Unbalance Maximum Value | float | 2 | R
0x7086 | 0x7087 | 28806 | 28807 | 10M_UNBL_MIN | 10min Voltage Unbalance Minimum Value | float | 2 | R
0x7088 | 0x7089 | 28808 | 28809 | 10M_UNBL_AVG | 10min Voltage Unbalance Average Value | float | 2 | R
0x708A | 0x708A | 28810 | 28810 | 10M_N_HRMa2 | 10min 2nd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x708B | 0x708B | 28811 | 28811 | 10M_N_HRMa3 | 10min 3rd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x708C | 0x708C | 28812 | 28812 | 10M_N_HRMa4 | 10min 4th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x708D | 0x708D | 28813 | 28813 | 10M_N_HRMa5 | 10min 5th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x708E | 0x708E | 28814 | 28814 | 10M_N_HRMa6 | 10min 6th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x708F | 0x708F | 28815 | 28815 | 10M_N_HRMa7 | 10min 7th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7090 | 0x7090 | 28816 | 28816 | 10M_N_HRMa8 | 10min 8th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7091 | 0x7091 | 28817 | 28817 | 10M_N_HRMa9 | 10min 9th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7092 | 0x7092 | 28818 | 28818 | 10M_N_HRMa10 | 10min 10th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7093 | 0x7093 | 28819 | 28819 | 10M_N_HRMa11 | 10min 11st Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7094 | 0x7094 | 28820 | 28820 | 10M_N_HRMa12 | 10min 12nd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7095 | 0x7095 | 28821 | 28821 | 10M_N_HRMa13 | 10min 13rd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7096 | 0x7096 | 28822 | 28822 | 10M_N_HRMa14 | 10min 14th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7097 | 0x7097 | 28823 | 28823 | 10M_N_HRMa15 | 10min 15th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7098 | 0x7098 | 28824 | 28824 | 10M_N_HRMa16 | 10min 16th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7099 | 0x7099 | 28825 | 28825 | 10M_N_HRMa17 | 10min 17th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x709A | 0x709A | 28826 | 28826 | 10M_N_HRMa18 | 10min 18th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x709B | 0x709B | 28827 | 28827 | 10M_N_HRMa19 | 10min 19th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x709C | 0x709C | 28828 | 28828 | 10M_N_HRMa20 | 10min 20th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x709D | 0x709D | 28829 | 28829 | 10M_N_HRMa21 | 10min 21st Phase A Harmonics Bin Counter | uint16 | 1 | R
0x709E | 0x709E | 28830 | 28830 | 10M_N_HRMa22 | 10min 22nd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x709F | 0x709F | 28831 | 28831 | 10M_N_HRMa23 | 10min 23rd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x70A0 | 0x70A0 | 28832 | 28832 | 10M_N_HRMa24 | 10min 24th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x70A1 | 0x70A1 | 28833 | 28833 | 10M_N_HRMa25 | 10min 25th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x70A2 | 0x70A2 | 28834 | 28834 | 10M_N_HRMb2 | 10min 2nd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70A3 | 0x70A3 | 28835 | 28835 | 10M_N_HRMb3 | 10min 3rd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70A4 | 0x70A4 | 28836 | 28836 | 10M_N_HRMb4 | 10min 4th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70A5 | 0x70A5 | 28837 | 28837 | 10M_N_HRMb5 | 10min 5th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70A6 | 0x70A6 | 28838 | 28838 | 10M_N_HRMb6 | 10min 6th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70A7 | 0x70A7 | 28839 | 28839 | 10M_N_HRMb7 | 10min 7th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70A8 | 0x70A8 | 28840 | 28840 | 10M_N_HRMb8 | 10min 8th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70A9 | 0x70A9 | 28841 | 28841 | 10M_N_HRMb9 | 10min 9th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70AA | 0x70AA | 28842 | 28842 | 10M_N_HRMb10 | 10min 10th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70AB | 0x70AB | 28843 | 28843 | 10M_N_HRMb11 | 10min 11st Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70AC | 0x70AC | 28844 | 28844 | 10M_N_HRMb12 | 10min 12nd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70AD | 0x70AD | 28845 | 28845 | 10M_N_HRMb13 | 10min 13rd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70AE | 0x70AE | 28846 | 28846 | 10M_N_HRMb14 | 10min 14th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70AF | 0x70AF | 28847 | 28847 | 10M_N_HRMb15 | 10min 15th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70B0 | 0x70B0 | 28848 | 28848 | 10M_N_HRMb16 | 10min 16th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70B1 | 0x70B1 | 28849 | 28849 | 10M_N_HRMb17 | 10min 17th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70B2 | 0x70B2 | 28850 | 28850 | 10M_N_HRMb18 | 10min 18th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70B3 | 0x70B3 | 28851 | 28851 | 10M_N_HRMb19 | 10min 19th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70B4 | 0x70B4 | 28852 | 28852 | 10M_N_HRMb20 | 10min 20th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70B5 | 0x70B5 | 28853 | 28853 | 10M_N_HRMb21 | 10min 21st Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70B6 | 0x70B6 | 28854 | 28854 | 10M_N_HRMb22 | 10min 22nd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70B7 | 0x70B7 | 28855 | 28855 | 10M_N_HRMb23 | 10min 23rd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70B8 | 0x70B8 | 28856 | 28856 | 10M_N_HRMb24 | 10min 24th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70B9 | 0x70B9 | 28857 | 28857 | 10M_N_HRMb25 | 10min 25th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x70BA | 0x70BA | 28858 | 28858 | 10M_N_HRMc2 | 10min 2nd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70BB | 0x70BB | 28859 | 28859 | 10M_N_HRMc3 | 10min 3rd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70BC | 0x70BC | 28860 | 28860 | 10M_N_HRMc4 | 10min 4th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70BD | 0x70BD | 28861 | 28861 | 10M_N_HRMc5 | 10min 5th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70BE | 0x70BE | 28862 | 28862 | 10M_N_HRMc6 | 10min 6th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70BF | 0x70BF | 28863 | 28863 | 10M_N_HRMc7 | 10min 7th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70C0 | 0x70C0 | 28864 | 28864 | 10M_N_HRMc8 | 10min 8th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70C1 | 0x70C1 | 28865 | 28865 | 10M_N_HRMc9 | 10min 9th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70C2 | 0x70C2 | 28866 | 28866 | 10M_N_HRMc10 | 10min 10th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70C3 | 0x70C3 | 28867 | 28867 | 10M_N_HRMc11 | 10min 11st Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70C4 | 0x70C4 | 28868 | 28868 | 10M_N_HRMc12 | 10min 12nd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70C5 | 0x70C5 | 28869 | 28869 | 10M_N_HRMc13 | 10min 13rd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70C6 | 0x70C6 | 28870 | 28870 | 10M_N_HRMc14 | 10min 14th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70C7 | 0x70C7 | 28871 | 28871 | 10M_N_HRMc15 | 10min 15th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70C8 | 0x70C8 | 28872 | 28872 | 10M_N_HRMc16 | 10min 16th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70C9 | 0x70C9 | 28873 | 28873 | 10M_N_HRMc17 | 10min 17th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70CA | 0x70CA | 28874 | 28874 | 10M_N_HRMc18 | 10min 18th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70CB | 0x70CB | 28875 | 28875 | 10M_N_HRMc19 | 10min 19th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70CC | 0x70CC | 28876 | 28876 | 10M_N_HRMc20 | 10min 20th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70CD | 0x70CD | 28877 | 28877 | 10M_N_HRMc21 | 10min 21st Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70CE | 0x70CE | 28878 | 28878 | 10M_N_HRMc22 | 10min 22nd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70CF | 0x70CF | 28879 | 28879 | 10M_N_HRMc23 | 10min 23rd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70D0 | 0x70D0 | 28880 | 28880 | 10M_N_HRMc24 | 10min 24th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70D1 | 0x70D1 | 28881 | 28881 | 10M_N_HRMc25 | 10min 25th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x70D2 | 0x70D3 | 28882 | 28883 | 10M_HRM_PASSa2 | 10min 2nd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70D4 | 0x70D5 | 28884 | 28885 | 10M_HRM_PASSa3 | 10min 3rd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70D6 | 0x70D7 | 28886 | 28887 | 10M_HRM_PASSa4 | 10min 4th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70D8 | 0x70D9 | 28888 | 28889 | 10M_HRM_PASSa5 | 10min 5th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70DA | 0x70DB | 28890 | 28891 | 10M_HRM_PASSa6 | 10min 6th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70DC | 0x70DD | 28892 | 28893 | 10M_HRM_PASSa7 | 10min 7th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70DE | 0x70DF | 28894 | 28895 | 10M_HRM_PASSa8 | 10min 8th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70E0 | 0x70E1 | 28896 | 28897 | 10M_HRM_PASSa9 | 10min 9th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70E2 | 0x70E3 | 28898 | 28899 | 10M_HRM_PASSa10 | 10min 10th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70E4 | 0x70E5 | 28900 | 28901 | 10M_HRM_PASSa11 | 10min 11st Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70E6 | 0x70E7 | 28902 | 28903 | 10M_HRM_PASSa12 | 10min 12nd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70E8 | 0x70E9 | 28904 | 28905 | 10M_HRM_PASSa13 | 10min 13rd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70EA | 0x70EB | 28906 | 28907 | 10M_HRM_PASSa14 | 10min 14th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70EC | 0x70ED | 28908 | 28909 | 10M_HRM_PASSa15 | 10min 15th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70EE | 0x70EF | 28910 | 28911 | 10M_HRM_PASSa16 | 10min 16th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70F0 | 0x70F1 | 28912 | 28913 | 10M_HRM_PASSa17 | 10min 17th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70F2 | 0x70F3 | 28914 | 28915 | 10M_HRM_PASSa18 | 10min 18th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70F4 | 0x70F5 | 28916 | 28917 | 10M_HRM_PASSa19 | 10min 19th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70F6 | 0x70F7 | 28918 | 28919 | 10M_HRM_PASSa20 | 10min 20th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70F8 | 0x70F9 | 28920 | 28921 | 10M_HRM_PASSa21 | 10min 21st Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70FA | 0x70FB | 28922 | 28923 | 10M_HRM_PASSa22 | 10min 22nd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70FC | 0x70FD | 28924 | 28925 | 10M_HRM_PASSa23 | 10min 23rd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x70FE | 0x70FF | 28926 | 28927 | 10M_HRM_PASSa24 | 10min 24th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7100 | 0x7101 | 28928 | 28929 | 10M_HRM_PASSa25 | 10min 25th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7102 | 0x7103 | 28930 | 28931 | 10M_HRM_PASSb2 | 10min 2nd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7104 | 0x7105 | 28932 | 28933 | 10M_HRM_PASSb3 | 10min 3rd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7106 | 0x7107 | 28934 | 28935 | 10M_HRM_PASSb4 | 10min 4th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7108 | 0x7109 | 28936 | 28937 | 10M_HRM_PASSb5 | 10min 5th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x710A | 0x710B | 28938 | 28939 | 10M_HRM_PASSb6 | 10min 6th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x710C | 0x710D | 28940 | 28941 | 10M_HRM_PASSb7 | 10min 7th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x710E | 0x710F | 28942 | 28943 | 10M_HRM_PASSb8 | 10min 8th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7110 | 0x7111 | 28944 | 28945 | 10M_HRM_PASSb9 | 10min 9th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7112 | 0x7113 | 28946 | 28947 | 10M_HRM_PASSb10 | 10min 10th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7114 | 0x7115 | 28948 | 28949 | 10M_HRM_PASSb11 | 10min 11st Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7116 | 0x7117 | 28950 | 28951 | 10M_HRM_PASSb12 | 10min 12nd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7118 | 0x7119 | 28952 | 28953 | 10M_HRM_PASSb13 | 10min 13rd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x711A | 0x711B | 28954 | 28955 | 10M_HRM_PASSb14 | 10min 14th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x711C | 0x711D | 28956 | 28957 | 10M_HRM_PASSb15 | 10min 15th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x711E | 0x711F | 28958 | 28959 | 10M_HRM_PASSb16 | 10min 16th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7120 | 0x7121 | 28960 | 28961 | 10M_HRM_PASSb17 | 10min 17th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7122 | 0x7123 | 28962 | 28963 | 10M_HRM_PASSb18 | 10min 18th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7124 | 0x7125 | 28964 | 28965 | 10M_HRM_PASSb19 | 10min 19th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7126 | 0x7127 | 28966 | 28967 | 10M_HRM_PASSb20 | 10min 20th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7128 | 0x7129 | 28968 | 28969 | 10M_HRM_PASSb21 | 10min 21st Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x712A | 0x712B | 28970 | 28971 | 10M_HRM_PASSb22 | 10min 22nd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x712C | 0x712D | 28972 | 28973 | 10M_HRM_PASSb23 | 10min 23rd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x712E | 0x712F | 28974 | 28975 | 10M_HRM_PASSb24 | 10min 24th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7130 | 0x7131 | 28976 | 28977 | 10M_HRM_PASSb25 | 10min 25th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7132 | 0x7133 | 28978 | 28979 | 10M_HRM_PASSc2 | 10min 2nd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7134 | 0x7135 | 28980 | 28981 | 10M_HRM_PASSc3 | 10min 3rd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7136 | 0x7137 | 28982 | 28983 | 10M_HRM_PASSc4 | 10min 4th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7138 | 0x7139 | 28984 | 28985 | 10M_HRM_PASSc5 | 10min 5th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x713A | 0x713B | 28986 | 28987 | 10M_HRM_PASSc6 | 10min 6th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x713C | 0x713D | 28988 | 28989 | 10M_HRM_PASSc7 | 10min 7th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x713E | 0x713F | 28990 | 28991 | 10M_HRM_PASSc8 | 10min 8th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7140 | 0x7141 | 28992 | 28993 | 10M_HRM_PASSc9 | 10min 9th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7142 | 0x7143 | 28994 | 28995 | 10M_HRM_PASSc10 | 10min 10th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7144 | 0x7145 | 28996 | 28997 | 10M_HRM_PASSc11 | 10min 11st Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7146 | 0x7147 | 28998 | 28999 | 10M_HRM_PASSc12 | 10min 12nd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7148 | 0x7149 | 29000 | 29001 | 10M_HRM_PASSc13 | 10min 13rd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x714A | 0x714B | 29002 | 29003 | 10M_HRM_PASSc14 | 10min 14th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x714C | 0x714D | 29004 | 29005 | 10M_HRM_PASSc15 | 10min 15th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x714E | 0x714F | 29006 | 29007 | 10M_HRM_PASSc16 | 10min 16th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7150 | 0x7151 | 29008 | 29009 | 10M_HRM_PASSc17 | 10min 17th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7152 | 0x7153 | 29010 | 29011 | 10M_HRM_PASSc18 | 10min 18th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7154 | 0x7155 | 29012 | 29013 | 10M_HRM_PASSc19 | 10min 19th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7156 | 0x7157 | 29014 | 29015 | 10M_HRM_PASSc20 | 10min 20th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7158 | 0x7159 | 29016 | 29017 | 10M_HRM_PASSc21 | 10min 21st Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x715A | 0x715B | 29018 | 29019 | 10M_HRM_PASSc22 | 10min 22nd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x715C | 0x715D | 29020 | 29021 | 10M_HRM_PASSc23 | 10min 23rd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x715E | 0x715F | 29022 | 29023 | 10M_HRM_PASSc24 | 10min 24th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7160 | 0x7161 | 29024 | 29025 | 10M_HRM_PASSc25 | 10min 25th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7162 | 0x7163 | 29026 | 29027 | 10M_HRM_MAXa2 | 10min 2nd Phase A Harmonics Max Value | float | 2 | R
0x7164 | 0x7165 | 29028 | 29029 | 10M_HRM_MAXa3 | 10min 3rd Phase A Harmonics Max Value | float | 2 | R
0x7166 | 0x7167 | 29030 | 29031 | 10M_HRM_MAXa4 | 10min 4th Phase A Harmonics Max Value | float | 2 | R
0x7168 | 0x7169 | 29032 | 29033 | 10M_HRM_MAXa5 | 10min 5th Phase A Harmonics Max Value | float | 2 | R
0x716A | 0x716B | 29034 | 29035 | 10M_HRM_MAXa6 | 10min 6th Phase A Harmonics Max Value | float | 2 | R
0x716C | 0x716D | 29036 | 29037 | 10M_HRM_MAXa7 | 10min 7th Phase A Harmonics Max Value | float | 2 | R
0x716E | 0x716F | 29038 | 29039 | 10M_HRM_MAXa8 | 10min 8th Phase A Harmonics Max Value | float | 2 | R
0x7170 | 0x7171 | 29040 | 29041 | 10M_HRM_MAXa9 | 10min 9th Phase A Harmonics Max Value | float | 2 | R
0x7172 | 0x7173 | 29042 | 29043 | 10M_HRM_MAXa10 | 10min 10th Phase A Harmonics Max Value | float | 2 | R
0x7174 | 0x7175 | 29044 | 29045 | 10M_HRM_MAXa11 | 10min 11st Phase A Harmonics Max Value | float | 2 | R
0x7176 | 0x7177 | 29046 | 29047 | 10M_HRM_MAXa12 | 10min 12nd Phase A Harmonics Max Value | float | 2 | R
0x7178 | 0x7179 | 29048 | 29049 | 10M_HRM_MAXa13 | 10min 13rd Phase A Harmonics Max Value | float | 2 | R
0x717A | 0x717B | 29050 | 29051 | 10M_HRM_MAXa14 | 10min 14th Phase A Harmonics Max Value | float | 2 | R
0x717C | 0x717D | 29052 | 29053 | 10M_HRM_MAXa15 | 10min 15th Phase A Harmonics Max Value | float | 2 | R
0x717E | 0x717F | 29054 | 29055 | 10M_HRM_MAXa16 | 10min 16th Phase A Harmonics Max Value | float | 2 | R
0x7180 | 0x7181 | 29056 | 29057 | 10M_HRM_MAXa17 | 10min 17th Phase A Harmonics Max Value | float | 2 | R
0x7182 | 0x7183 | 29058 | 29059 | 10M_HRM_MAXa18 | 10min 18th Phase A Harmonics Max Value | float | 2 | R
0x7184 | 0x7185 | 29060 | 29061 | 10M_HRM_MAXa19 | 10min 19th Phase A Harmonics Max Value | float | 2 | R
0x7186 | 0x7187 | 29062 | 29063 | 10M_HRM_MAXa20 | 10min 20th Phase A Harmonics Max Value | float | 2 | R
0x7188 | 0x7189 | 29064 | 29065 | 10M_HRM_MAXa21 | 10min 21st Phase A Harmonics Max Value | float | 2 | R
0x718A | 0x718B | 29066 | 29067 | 10M_HRM_MAXa22 | 10min 22nd Phase A Harmonics Max Value | float | 2 | R
0x718C | 0x718D | 29068 | 29069 | 10M_HRM_MAXa23 | 10min 23rd Phase A Harmonics Max Value | float | 2 | R
0x718E | 0x718F | 29070 | 29071 | 10M_HRM_MAXa24 | 10min 24th Phase A Harmonics Max Value | float | 2 | R
0x7190 | 0x7191 | 29072 | 29073 | 10M_HRM_MAXa25 | 10min 25th Phase A Harmonics Max Value | float | 2 | R
0x7192 | 0x7193 | 29074 | 29075 | 10M_HRM_MAXb2 | 10min 2nd Phase B Harmonics Max Value | float | 2 | R
0x7194 | 0x7195 | 29076 | 29077 | 10M_HRM_MAXb3 | 10min 3rd Phase B Harmonics Max Value | float | 2 | R
0x7196 | 0x7197 | 29078 | 29079 | 10M_HRM_MAXb4 | 10min 4th Phase B Harmonics Max Value | float | 2 | R
0x7198 | 0x7199 | 29080 | 29081 | 10M_HRM_MAXb5 | 10min 5th Phase B Harmonics Max Value | float | 2 | R
0x719A | 0x719B | 29082 | 29083 | 10M_HRM_MAXb6 | 10min 6th Phase B Harmonics Max Value | float | 2 | R
0x719C | 0x719D | 29084 | 29085 | 10M_HRM_MAXb7 | 10min 7th Phase B Harmonics Max Value | float | 2 | R
0x719E | 0x719F | 29086 | 29087 | 10M_HRM_MAXb8 | 10min 8th Phase B Harmonics Max Value | float | 2 | R
0x71A0 | 0x71A1 | 29088 | 29089 | 10M_HRM_MAXb9 | 10min 9th Phase B Harmonics Max Value | float | 2 | R
0x71A2 | 0x71A3 | 29090 | 29091 | 10M_HRM_MAXb10 | 10min 10th Phase B Harmonics Max Value | float | 2 | R
0x71A4 | 0x71A5 | 29092 | 29093 | 10M_HRM_MAXb11 | 10min 11st Phase B Harmonics Max Value | float | 2 | R
0x71A6 | 0x71A7 | 29094 | 29095 | 10M_HRM_MAXb12 | 10min 12nd Phase B Harmonics Max Value | float | 2 | R
0x71A8 | 0x71A9 | 29096 | 29097 | 10M_HRM_MAXb13 | 10min 13rd Phase B Harmonics Max Value | float | 2 | R
0x71AA | 0x71AB | 29098 | 29099 | 10M_HRM_MAXb14 | 10min 14th Phase B Harmonics Max Value | float | 2 | R
0x71AC | 0x71AD | 29100 | 29101 | 10M_HRM_MAXb15 | 10min 15th Phase B Harmonics Max Value | float | 2 | R
0x71AE | 0x71AF | 29102 | 29103 | 10M_HRM_MAXb16 | 10min 16th Phase B Harmonics Max Value | float | 2 | R
0x71B0 | 0x71B1 | 29104 | 29105 | 10M_HRM_MAXb17 | 10min 17th Phase B Harmonics Max Value | float | 2 | R
0x71B2 | 0x71B3 | 29106 | 29107 | 10M_HRM_MAXb18 | 10min 18th Phase B Harmonics Max Value | float | 2 | R
0x71B4 | 0x71B5 | 29108 | 29109 | 10M_HRM_MAXb19 | 10min 19th Phase B Harmonics Max Value | float | 2 | R
0x71B6 | 0x71B7 | 29110 | 29111 | 10M_HRM_MAXb20 | 10min 20th Phase B Harmonics Max Value | float | 2 | R
0x71B8 | 0x71B9 | 29112 | 29113 | 10M_HRM_MAXb21 | 10min 21st Phase B Harmonics Max Value | float | 2 | R
0x71BA | 0x71BB | 29114 | 29115 | 10M_HRM_MAXb22 | 10min 22nd Phase B Harmonics Max Value | float | 2 | R
0x71BC | 0x71BD | 29116 | 29117 | 10M_HRM_MAXb23 | 10min 23rd Phase B Harmonics Max Value | float | 2 | R
0x71BE | 0x71BF | 29118 | 29119 | 10M_HRM_MAXb24 | 10min 24th Phase B Harmonics Max Value | float | 2 | R
0x71C0 | 0x71C1 | 29120 | 29121 | 10M_HRM_MAXb25 | 10min 25th Phase B Harmonics Max Value | float | 2 | R
0x71C2 | 0x71C3 | 29122 | 29123 | 10M_HRM_MAXc2 | 10min 2nd Phase C Harmonics Max Value | float | 2 | R
0x71C4 | 0x71C5 | 29124 | 29125 | 10M_HRM_MAXc3 | 10min 3rd Phase C Harmonics Max Value | float | 2 | R
0x71C6 | 0x71C7 | 29126 | 29127 | 10M_HRM_MAXc4 | 10min 4th Phase C Harmonics Max Value | float | 2 | R
0x71C8 | 0x71C9 | 29128 | 29129 | 10M_HRM_MAXc5 | 10min 5th Phase C Harmonics Max Value | float | 2 | R
0x71CA | 0x71CB | 29130 | 29131 | 10M_HRM_MAXc6 | 10min 6th Phase C Harmonics Max Value | float | 2 | R
0x71CC | 0x71CD | 29132 | 29133 | 10M_HRM_MAXc7 | 10min 7th Phase C Harmonics Max Value | float | 2 | R
0x71CE | 0x71CF | 29134 | 29135 | 10M_HRM_MAXc8 | 10min 8th Phase C Harmonics Max Value | float | 2 | R
0x71D0 | 0x71D1 | 29136 | 29137 | 10M_HRM_MAXc9 | 10min 9th Phase C Harmonics Max Value | float | 2 | R
0x71D2 | 0x71D3 | 29138 | 29139 | 10M_HRM_MAXc10 | 10min 10th Phase C Harmonics Max Value | float | 2 | R
0x71D4 | 0x71D5 | 29140 | 29141 | 10M_HRM_MAXc11 | 10min 11st Phase C Harmonics Max Value | float | 2 | R
0x71D6 | 0x71D7 | 29142 | 29143 | 10M_HRM_MAXc12 | 10min 12nd Phase C Harmonics Max Value | float | 2 | R
0x71D8 | 0x71D9 | 29144 | 29145 | 10M_HRM_MAXc13 | 10min 13rd Phase C Harmonics Max Value | float | 2 | R
0x71DA | 0x71DB | 29146 | 29147 | 10M_HRM_MAXc14 | 10min 14th Phase C Harmonics Max Value | float | 2 | R
0x71DC | 0x71DD | 29148 | 29149 | 10M_HRM_MAXc15 | 10min 15th Phase C Harmonics Max Value | float | 2 | R
0x71DE | 0x71DF | 29150 | 29151 | 10M_HRM_MAXc16 | 10min 16th Phase C Harmonics Max Value | float | 2 | R
0x71E0 | 0x71E1 | 29152 | 29153 | 10M_HRM_MAXc17 | 10min 17th Phase C Harmonics Max Value | float | 2 | R
0x71E2 | 0x71E3 | 29154 | 29155 | 10M_HRM_MAXc18 | 10min 18th Phase C Harmonics Max Value | float | 2 | R
0x71E4 | 0x71E5 | 29156 | 29157 | 10M_HRM_MAXc19 | 10min 19th Phase C Harmonics Max Value | float | 2 | R
0x71E6 | 0x71E7 | 29158 | 29159 | 10M_HRM_MAXc20 | 10min 20th Phase C Harmonics Max Value | float | 2 | R
0x71E8 | 0x71E9 | 29160 | 29161 | 10M_HRM_MAXc21 | 10min 21st Phase C Harmonics Max Value | float | 2 | R
0x71EA | 0x71EB | 29162 | 29163 | 10M_HRM_MAXc22 | 10min 22nd Phase C Harmonics Max Value | float | 2 | R
0x71EC | 0x71ED | 29164 | 29165 | 10M_HRM_MAXc23 | 10min 23rd Phase C Harmonics Max Value | float | 2 | R
0x71EE | 0x71EF | 29166 | 29167 | 10M_HRM_MAXc24 | 10min 24th Phase C Harmonics Max Value | float | 2 | R
0x71F0 | 0x71F1 | 29168 | 29169 | 10M_HRM_MAXc25 | 10min 25th Phase C Harmonics Max Value | float | 2 | R
0x71F2 | 0x71F3 | 29170 | 29171 | 10M_HRM_MINa2 | 10min 2nd Phase A Harmonics Min Value | float | 2 | R
0x71F4 | 0x71F5 | 29172 | 29173 | 10M_HRM_MINa3 | 10min 3rd Phase A Harmonics Min Value | float | 2 | R
0x71F6 | 0x71F7 | 29174 | 29175 | 10M_HRM_MINa4 | 10min 4th Phase A Harmonics Min Value | float | 2 | R
0x71F8 | 0x71F9 | 29176 | 29177 | 10M_HRM_MINa5 | 10min 5th Phase A Harmonics Min Value | float | 2 | R
0x71FA | 0x71FB | 29178 | 29179 | 10M_HRM_MINa6 | 10min 6th Phase A Harmonics Min Value | float | 2 | R
0x71FC | 0x71FD | 29180 | 29181 | 10M_HRM_MINa7 | 10min 7th Phase A Harmonics Min Value | float | 2 | R
0x71FE | 0x71FF | 29182 | 29183 | 10M_HRM_MINa8 | 10min 8th Phase A Harmonics Min Value | float | 2 | R
0x7200 | 0x7201 | 29184 | 29185 | 10M_HRM_MINa9 | 10min 9th Phase A Harmonics Min Value | float | 2 | R
0x7202 | 0x7203 | 29186 | 29187 | 10M_HRM_MINa10 | 10min 10th Phase A Harmonics Min Value | float | 2 | R
0x7204 | 0x7205 | 29188 | 29189 | 10M_HRM_MINa11 | 10min 11st Phase A Harmonics Min Value | float | 2 | R
0x7206 | 0x7207 | 29190 | 29191 | 10M_HRM_MINa12 | 10min 12nd Phase A Harmonics Min Value | float | 2 | R
0x7208 | 0x7209 | 29192 | 29193 | 10M_HRM_MINa13 | 10min 13rd Phase A Harmonics Min Value | float | 2 | R
0x720A | 0x720B | 29194 | 29195 | 10M_HRM_MINa14 | 10min 14th Phase A Harmonics Min Value | float | 2 | R
0x720C | 0x720D | 29196 | 29197 | 10M_HRM_MINa15 | 10min 15th Phase A Harmonics Min Value | float | 2 | R
0x720E | 0x720F | 29198 | 29199 | 10M_HRM_MINa16 | 10min 16th Phase A Harmonics Min Value | float | 2 | R
0x7210 | 0x7211 | 29200 | 29201 | 10M_HRM_MINa17 | 10min 17th Phase A Harmonics Min Value | float | 2 | R
0x7212 | 0x7213 | 29202 | 29203 | 10M_HRM_MINa18 | 10min 18th Phase A Harmonics Min Value | float | 2 | R
0x7214 | 0x7215 | 29204 | 29205 | 10M_HRM_MINa19 | 10min 19th Phase A Harmonics Min Value | float | 2 | R
0x7216 | 0x7217 | 29206 | 29207 | 10M_HRM_MINa20 | 10min 20th Phase A Harmonics Min Value | float | 2 | R
0x7218 | 0x7219 | 29208 | 29209 | 10M_HRM_MINa21 | 10min 21st Phase A Harmonics Min Value | float | 2 | R
0x721A | 0x721B | 29210 | 29211 | 10M_HRM_MINa22 | 10min 22nd Phase A Harmonics Min Value | float | 2 | R
0x721C | 0x721D | 29212 | 29213 | 10M_HRM_MINa23 | 10min 23rd Phase A Harmonics Min Value | float | 2 | R
0x721E | 0x721F | 29214 | 29215 | 10M_HRM_MINa24 | 10min 24th Phase A Harmonics Min Value | float | 2 | R
0x7220 | 0x7221 | 29216 | 29217 | 10M_HRM_MINa25 | 10min 25th Phase A Harmonics Min Value | float | 2 | R
0x7222 | 0x7223 | 29218 | 29219 | 10M_HRM_MINb2 | 10min 2nd Phase B Harmonics Min Value | float | 2 | R
0x7224 | 0x7225 | 29220 | 29221 | 10M_HRM_MINb3 | 10min 3rd Phase B Harmonics Min Value | float | 2 | R
0x7226 | 0x7227 | 29222 | 29223 | 10M_HRM_MINb4 | 10min 4th Phase B Harmonics Min Value | float | 2 | R
0x7228 | 0x7229 | 29224 | 29225 | 10M_HRM_MINb5 | 10min 5th Phase B Harmonics Min Value | float | 2 | R
0x722A | 0x722B | 29226 | 29227 | 10M_HRM_MINb6 | 10min 6th Phase B Harmonics Min Value | float | 2 | R
0x722C | 0x722D | 29228 | 29229 | 10M_HRM_MINb7 | 10min 7th Phase B Harmonics Min Value | float | 2 | R
0x722E | 0x722F | 29230 | 29231 | 10M_HRM_MINb8 | 10min 8th Phase B Harmonics Min Value | float | 2 | R
0x7230 | 0x7231 | 29232 | 29233 | 10M_HRM_MINb9 | 10min 9th Phase B Harmonics Min Value | float | 2 | R
0x7232 | 0x7233 | 29234 | 29235 | 10M_HRM_MINb10 | 10min 10th Phase B Harmonics Min Value | float | 2 | R
0x7234 | 0x7235 | 29236 | 29237 | 10M_HRM_MINb11 | 10min 11st Phase B Harmonics Min Value | float | 2 | R
0x7236 | 0x7237 | 29238 | 29239 | 10M_HRM_MINb12 | 10min 12nd Phase B Harmonics Min Value | float | 2 | R
0x7238 | 0x7239 | 29240 | 29241 | 10M_HRM_MINb13 | 10min 13rd Phase B Harmonics Min Value | float | 2 | R
0x723A | 0x723B | 29242 | 29243 | 10M_HRM_MINb14 | 10min 14th Phase B Harmonics Min Value | float | 2 | R
0x723C | 0x723D | 29244 | 29245 | 10M_HRM_MINb15 | 10min 15th Phase B Harmonics Min Value | float | 2 | R
0x723E | 0x723F | 29246 | 29247 | 10M_HRM_MINb16 | 10min 16th Phase B Harmonics Min Value | float | 2 | R
0x7240 | 0x7241 | 29248 | 29249 | 10M_HRM_MINb17 | 10min 17th Phase B Harmonics Min Value | float | 2 | R
0x7242 | 0x7243 | 29250 | 29251 | 10M_HRM_MINb18 | 10min 18th Phase B Harmonics Min Value | float | 2 | R
0x7244 | 0x7245 | 29252 | 29253 | 10M_HRM_MINb19 | 10min 19th Phase B Harmonics Min Value | float | 2 | R
0x7246 | 0x7247 | 29254 | 29255 | 10M_HRM_MINb20 | 10min 20th Phase B Harmonics Min Value | float | 2 | R
0x7248 | 0x7249 | 29256 | 29257 | 10M_HRM_MINb21 | 10min 21st Phase B Harmonics Min Value | float | 2 | R
0x724A | 0x724B | 29258 | 29259 | 10M_HRM_MINb22 | 10min 22nd Phase B Harmonics Min Value | float | 2 | R
0x724C | 0x724D | 29260 | 29261 | 10M_HRM_MINb23 | 10min 23rd Phase B Harmonics Min Value | float | 2 | R
0x724E | 0x724F | 29262 | 29263 | 10M_HRM_MINb24 | 10min 24th Phase B Harmonics Min Value | float | 2 | R
0x7250 | 0x7251 | 29264 | 29265 | 10M_HRM_MINb25 | 10min 25th Phase B Harmonics Min Value | float | 2 | R
0x7252 | 0x7253 | 29266 | 29267 | 10M_HRM_MINc2 | 10min 2nd Phase C Harmonics Min Value | float | 2 | R
0x7254 | 0x7255 | 29268 | 29269 | 10M_HRM_MINc3 | 10min 3rd Phase C Harmonics Min Value | float | 2 | R
0x7256 | 0x7257 | 29270 | 29271 | 10M_HRM_MINc4 | 10min 4th Phase C Harmonics Min Value | float | 2 | R
0x7258 | 0x7259 | 29272 | 29273 | 10M_HRM_MINc5 | 10min 5th Phase C Harmonics Min Value | float | 2 | R
0x725A | 0x725B | 29274 | 29275 | 10M_HRM_MINc6 | 10min 6th Phase C Harmonics Min Value | float | 2 | R
0x725C | 0x725D | 29276 | 29277 | 10M_HRM_MINc7 | 10min 7th Phase C Harmonics Min Value | float | 2 | R
0x725E | 0x725F | 29278 | 29279 | 10M_HRM_MINc8 | 10min 8th Phase C Harmonics Min Value | float | 2 | R
0x7260 | 0x7261 | 29280 | 29281 | 10M_HRM_MINc9 | 10min 9th Phase C Harmonics Min Value | float | 2 | R
0x7262 | 0x7263 | 29282 | 29283 | 10M_HRM_MINc10 | 10min 10th Phase C Harmonics Min Value | float | 2 | R
0x7264 | 0x7265 | 29284 | 29285 | 10M_HRM_MINc11 | 10min 11st Phase C Harmonics Min Value | float | 2 | R
0x7266 | 0x7267 | 29286 | 29287 | 10M_HRM_MINc12 | 10min 12nd Phase C Harmonics Min Value | float | 2 | R
0x7268 | 0x7269 | 29288 | 29289 | 10M_HRM_MINc13 | 10min 13rd Phase C Harmonics Min Value | float | 2 | R
0x726A | 0x726B | 29290 | 29291 | 10M_HRM_MINc14 | 10min 14th Phase C Harmonics Min Value | float | 2 | R
0x726C | 0x726D | 29292 | 29293 | 10M_HRM_MINc15 | 10min 15th Phase C Harmonics Min Value | float | 2 | R
0x726E | 0x726F | 29294 | 29295 | 10M_HRM_MINc16 | 10min 16th Phase C Harmonics Min Value | float | 2 | R
0x7270 | 0x7271 | 29296 | 29297 | 10M_HRM_MINc17 | 10min 17th Phase C Harmonics Min Value | float | 2 | R
0x7272 | 0x7273 | 29298 | 29299 | 10M_HRM_MINc18 | 10min 18th Phase C Harmonics Min Value | float | 2 | R
0x7274 | 0x7275 | 29300 | 29301 | 10M_HRM_MINc19 | 10min 19th Phase C Harmonics Min Value | float | 2 | R
0x7276 | 0x7277 | 29302 | 29303 | 10M_HRM_MINc20 | 10min 20th Phase C Harmonics Min Value | float | 2 | R
0x7278 | 0x7279 | 29304 | 29305 | 10M_HRM_MINc21 | 10min 21st Phase C Harmonics Min Value | float | 2 | R
0x727A | 0x727B | 29306 | 29307 | 10M_HRM_MINc22 | 10min 22nd Phase C Harmonics Min Value | float | 2 | R
0x727C | 0x727D | 29308 | 29309 | 10M_HRM_MINc23 | 10min 23rd Phase C Harmonics Min Value | float | 2 | R
0x727E | 0x727F | 29310 | 29311 | 10M_HRM_MINc24 | 10min 24th Phase C Harmonics Min Value | float | 2 | R
0x7280 | 0x7281 | 29312 | 29313 | 10M_HRM_MINc25 | 10min 25th Phase C Harmonics Min Value | float | 2 | R
0x7282 | 0x7283 | 29314 | 29315 | 10M_HRM_AVGa2 | 10min 2nd Phase A Harmonics Avg Value | float | 2 | R
0x7284 | 0x7285 | 29316 | 29317 | 10M_HRM_AVGa3 | 10min 3rd Phase A Harmonics Avg Value | float | 2 | R
0x7286 | 0x7287 | 29318 | 29319 | 10M_HRM_AVGa4 | 10min 4th Phase A Harmonics Avg Value | float | 2 | R
0x7288 | 0x7289 | 29320 | 29321 | 10M_HRM_AVGa5 | 10min 5th Phase A Harmonics Avg Value | float | 2 | R
0x728A | 0x728B | 29322 | 29323 | 10M_HRM_AVGa6 | 10min 6th Phase A Harmonics Avg Value | float | 2 | R
0x728C | 0x728D | 29324 | 29325 | 10M_HRM_AVGa7 | 10min 7th Phase A Harmonics Avg Value | float | 2 | R
0x728E | 0x728F | 29326 | 29327 | 10M_HRM_AVGa8 | 10min 8th Phase A Harmonics Avg Value | float | 2 | R
0x7290 | 0x7291 | 29328 | 29329 | 10M_HRM_AVGa9 | 10min 9th Phase A Harmonics Avg Value | float | 2 | R
0x7292 | 0x7293 | 29330 | 29331 | 10M_HRM_AVGa10 | 10min 10th Phase A Harmonics Avg Value | float | 2 | R
0x7294 | 0x7295 | 29332 | 29333 | 10M_HRM_AVGa11 | 10min 11st Phase A Harmonics Avg Value | float | 2 | R
0x7296 | 0x7297 | 29334 | 29335 | 10M_HRM_AVGa12 | 10min 12nd Phase A Harmonics Avg Value | float | 2 | R
0x7298 | 0x7299 | 29336 | 29337 | 10M_HRM_AVGa13 | 10min 13rd Phase A Harmonics Avg Value | float | 2 | R
0x729A | 0x729B | 29338 | 29339 | 10M_HRM_AVGa14 | 10min 14th Phase A Harmonics Avg Value | float | 2 | R
0x729C | 0x729D | 29340 | 29341 | 10M_HRM_AVGa15 | 10min 15th Phase A Harmonics Avg Value | float | 2 | R
0x729E | 0x729F | 29342 | 29343 | 10M_HRM_AVGa16 | 10min 16th Phase A Harmonics Avg Value | float | 2 | R
0x72A0 | 0x72A1 | 29344 | 29345 | 10M_HRM_AVGa17 | 10min 17th Phase A Harmonics Avg Value | float | 2 | R
0x72A2 | 0x72A3 | 29346 | 29347 | 10M_HRM_AVGa18 | 10min 18th Phase A Harmonics Avg Value | float | 2 | R
0x72A4 | 0x72A5 | 29348 | 29349 | 10M_HRM_AVGa19 | 10min 19th Phase A Harmonics Avg Value | float | 2 | R
0x72A6 | 0x72A7 | 29350 | 29351 | 10M_HRM_AVGa20 | 10min 20th Phase A Harmonics Avg Value | float | 2 | R
0x72A8 | 0x72A9 | 29352 | 29353 | 10M_HRM_AVGa21 | 10min 21st Phase A Harmonics Avg Value | float | 2 | R
0x72AA | 0x72AB | 29354 | 29355 | 10M_HRM_AVGa22 | 10min 22nd Phase A Harmonics Avg Value | float | 2 | R
0x72AC | 0x72AD | 29356 | 29357 | 10M_HRM_AVGa23 | 10min 23rd Phase A Harmonics Avg Value | float | 2 | R
0x72AE | 0x72AF | 29358 | 29359 | 10M_HRM_AVGa24 | 10min 24th Phase A Harmonics Avg Value | float | 2 | R
0x72B0 | 0x72B1 | 29360 | 29361 | 10M_HRM_AVGa25 | 10min 25th Phase A Harmonics Avg Value | float | 2 | R
0x72B2 | 0x72B3 | 29362 | 29363 | 10M_HRM_AVGb2 | 10min 2nd Phase B Harmonics Avg Value | float | 2 | R
0x72B4 | 0x72B5 | 29364 | 29365 | 10M_HRM_AVGb3 | 10min 3rd Phase B Harmonics Avg Value | float | 2 | R
0x72B6 | 0x72B7 | 29366 | 29367 | 10M_HRM_AVGb4 | 10min 4th Phase B Harmonics Avg Value | float | 2 | R
0x72B8 | 0x72B9 | 29368 | 29369 | 10M_HRM_AVGb5 | 10min 5th Phase B Harmonics Avg Value | float | 2 | R
0x72BA | 0x72BB | 29370 | 29371 | 10M_HRM_AVGb6 | 10min 6th Phase B Harmonics Avg Value | float | 2 | R
0x72BC | 0x72BD | 29372 | 29373 | 10M_HRM_AVGb7 | 10min 7th Phase B Harmonics Avg Value | float | 2 | R
0x72BE | 0x72BF | 29374 | 29375 | 10M_HRM_AVGb8 | 10min 8th Phase B Harmonics Avg Value | float | 2 | R
0x72C0 | 0x72C1 | 29376 | 29377 | 10M_HRM_AVGb9 | 10min 9th Phase B Harmonics Avg Value | float | 2 | R
0x72C2 | 0x72C3 | 29378 | 29379 | 10M_HRM_AVGb10 | 10min 10th Phase B Harmonics Avg Value | float | 2 | R
0x72C4 | 0x72C5 | 29380 | 29381 | 10M_HRM_AVGb11 | 10min 11st Phase B Harmonics Avg Value | float | 2 | R
0x72C6 | 0x72C7 | 29382 | 29383 | 10M_HRM_AVGb12 | 10min 12nd Phase B Harmonics Avg Value | float | 2 | R
0x72C8 | 0x72C9 | 29384 | 29385 | 10M_HRM_AVGb13 | 10min 13rd Phase B Harmonics Avg Value | float | 2 | R
0x72CA | 0x72CB | 29386 | 29387 | 10M_HRM_AVGb14 | 10min 14th Phase B Harmonics Avg Value | float | 2 | R
0x72CC | 0x72CD | 29388 | 29389 | 10M_HRM_AVGb15 | 10min 15th Phase B Harmonics Avg Value | float | 2 | R
0x72CE | 0x72CF | 29390 | 29391 | 10M_HRM_AVGb16 | 10min 16th Phase B Harmonics Avg Value | float | 2 | R
0x72D0 | 0x72D1 | 29392 | 29393 | 10M_HRM_AVGb17 | 10min 17th Phase B Harmonics Avg Value | float | 2 | R
0x72D2 | 0x72D3 | 29394 | 29395 | 10M_HRM_AVGb18 | 10min 18th Phase B Harmonics Avg Value | float | 2 | R
0x72D4 | 0x72D5 | 29396 | 29397 | 10M_HRM_AVGb19 | 10min 19th Phase B Harmonics Avg Value | float | 2 | R
0x72D6 | 0x72D7 | 29398 | 29399 | 10M_HRM_AVGb20 | 10min 20th Phase B Harmonics Avg Value | float | 2 | R
0x72D8 | 0x72D9 | 29400 | 29401 | 10M_HRM_AVGb21 | 10min 21st Phase B Harmonics Avg Value | float | 2 | R
0x72DA | 0x72DB | 29402 | 29403 | 10M_HRM_AVGb22 | 10min 22nd Phase B Harmonics Avg Value | float | 2 | R
0x72DC | 0x72DD | 29404 | 29405 | 10M_HRM_AVGb23 | 10min 23rd Phase B Harmonics Avg Value | float | 2 | R
0x72DE | 0x72DF | 29406 | 29407 | 10M_HRM_AVGb24 | 10min 24th Phase B Harmonics Avg Value | float | 2 | R
0x72E0 | 0x72E1 | 29408 | 29409 | 10M_HRM_AVGb25 | 10min 25th Phase B Harmonics Avg Value | float | 2 | R
0x72E2 | 0x72E3 | 29410 | 29411 | 10M_HRM_AVGc2 | 10min 2nd Phase C Harmonics Avg Value | float | 2 | R
0x72E4 | 0x72E5 | 29412 | 29413 | 10M_HRM_AVGc3 | 10min 3rd Phase C Harmonics Avg Value | float | 2 | R
0x72E6 | 0x72E7 | 29414 | 29415 | 10M_HRM_AVGc4 | 10min 4th Phase C Harmonics Avg Value | float | 2 | R
0x72E8 | 0x72E9 | 29416 | 29417 | 10M_HRM_AVGc5 | 10min 5th Phase C Harmonics Avg Value | float | 2 | R
0x72EA | 0x72EB | 29418 | 29419 | 10M_HRM_AVGc6 | 10min 6th Phase C Harmonics Avg Value | float | 2 | R
0x72EC | 0x72ED | 29420 | 29421 | 10M_HRM_AVGc7 | 10min 7th Phase C Harmonics Avg Value | float | 2 | R
0x72EE | 0x72EF | 29422 | 29423 | 10M_HRM_AVGc8 | 10min 8th Phase C Harmonics Avg Value | float | 2 | R
0x72F0 | 0x72F1 | 29424 | 29425 | 10M_HRM_AVGc9 | 10min 9th Phase C Harmonics Avg Value | float | 2 | R
0x72F2 | 0x72F3 | 29426 | 29427 | 10M_HRM_AVGc10 | 10min 10th Phase C Harmonics Avg Value | float | 2 | R
0x72F4 | 0x72F5 | 29428 | 29429 | 10M_HRM_AVGc11 | 10min 11st Phase C Harmonics Avg Value | float | 2 | R
0x72F6 | 0x72F7 | 29430 | 29431 | 10M_HRM_AVGc12 | 10min 12nd Phase C Harmonics Avg Value | float | 2 | R
0x72F8 | 0x72F9 | 29432 | 29433 | 10M_HRM_AVGc13 | 10min 13rd Phase C Harmonics Avg Value | float | 2 | R
0x72FA | 0x72FB | 29434 | 29435 | 10M_HRM_AVGc14 | 10min 14th Phase C Harmonics Avg Value | float | 2 | R
0x72FC | 0x72FD | 29436 | 29437 | 10M_HRM_AVGc15 | 10min 15th Phase C Harmonics Avg Value | float | 2 | R
0x72FE | 0x72FF | 29438 | 29439 | 10M_HRM_AVGc16 | 10min 16th Phase C Harmonics Avg Value | float | 2 | R
0x7300 | 0x7301 | 29440 | 29441 | 10M_HRM_AVGc17 | 10min 17th Phase C Harmonics Avg Value | float | 2 | R
0x7302 | 0x7303 | 29442 | 29443 | 10M_HRM_AVGc18 | 10min 18th Phase C Harmonics Avg Value | float | 2 | R
0x7304 | 0x7305 | 29444 | 29445 | 10M_HRM_AVGc19 | 10min 19th Phase C Harmonics Avg Value | float | 2 | R
0x7306 | 0x7307 | 29446 | 29447 | 10M_HRM_AVGc20 | 10min 20th Phase C Harmonics Avg Value | float | 2 | R
0x7308 | 0x7309 | 29448 | 29449 | 10M_HRM_AVGc21 | 10min 21st Phase C Harmonics Avg Value | float | 2 | R
0x730A | 0x730B | 29450 | 29451 | 10M_HRM_AVGc22 | 10min 22nd Phase C Harmonics Avg Value | float | 2 | R
0x730C | 0x730D | 29452 | 29453 | 10M_HRM_AVGc23 | 10min 23rd Phase C Harmonics Avg Value | float | 2 | R
0x730E | 0x730F | 29454 | 29455 | 10M_HRM_AVGc24 | 10min 24th Phase C Harmonics Avg Value | float | 2 | R
0x7310 | 0x7311 | 29456 | 29457 | 10M_HRM_AVGc25 | 10min 25th Phase C Harmonics Avg Value | float | 2 | R
0x7312 | 0x7312 | 29458 | 29458 | 10M_N_THDa | 10min Phase A THD Bin Counter | uint16 | 1 | R
0x7313 | 0x7313 | 29459 | 29459 | 10M_N_THDb | 10min Phase B THD Bin Counter | uint16 | 1 | R
0x7314 | 0x7314 | 29460 | 29460 | 10M_N_THDc | 10min Phase C THD Bin Counter | uint16 | 1 | R
0x7315 | 0x7316 | 29461 | 29462 | 10M_THD_PASSa | 10min Phase A THD Bin Zone Trigger Pass Rate | float | 2 | R
0x7317 | 0x7318 | 29463 | 29464 | 10M_THD_PASSb | 10min Phase B THD Bin Zone Trigger Pass Rate | float | 2 | R
0x7319 | 0x731A | 29465 | 29466 | 10M_THD_PASSc | 10min Phase C THD Bin Zone Trigger Pass Rate | float | 2 | R
0x731B | 0x731C | 29467 | 29468 | 10M_THD_MAXa | 10min Phase A THD Maximum Value | float | 2 | R
0x731D | 0x731E | 29469 | 29470 | 10M_THD_MAXb | 10min Phase B THD Maximum Value | float | 2 | R
0x731F | 0x7320 | 29471 | 29472 | 10M_THD_MAXc | 10min Phase C THD Maximum Value | float | 2 | R
0x7321 | 0x7322 | 29473 | 29474 | 10M_THD_MINa | 10min Phase A THD Minimum Value | float | 2 | R
0x7323 | 0x7324 | 29475 | 29476 | 10M_THD_MINb | 10min Phase B THD Minimum Value | float | 2 | R
0x7325 | 0x7326 | 29477 | 29478 | 10M_THD_MINc | 10min Phase C THD Minimum Value | float | 2 | R
0x7327 | 0x7328 | 29479 | 29480 | 10M_THD_AVGa | 10min Phase A THD Average Value | float | 2 | R
0x7329 | 0x732A | 29481 | 29482 | 10M_THD_AVGb | 10min Phase B THD Average Value | float | 2 | R
0x732B | 0x732C | 29483 | 29484 | 10M_THD_AVGc | 10min Phase C THD Average Value | float | 2 | R
0x732D | 0x732E | 29485 | 29486 | 10M_TOHD_MAXa | 10min Phase A TOHD Maximum Value | float | 2 | R
0x732F | 0x7330 | 29487 | 29488 | 10M_TOHD_MAXb | 10min Phase B TOHD Maximum Value | float | 2 | R
0x7331 | 0x7332 | 29489 | 29490 | 10M_TOHD_MAXc | 10min Phase C TOHD Maximum Value | float | 2 | R
0x7333 | 0x7334 | 29491 | 29492 | 10M_TOHD_MINa | 10min Phase A TOHD Minimum Value | float | 2 | R
0x7335 | 0x7336 | 29493 | 29494 | 10M_TOHD_MINb | 10min Phase B TOHD Minimum Value | float | 2 | R
0x7337 | 0x7338 | 29495 | 29496 | 10M_TOHD_MINc | 10min Phase C TOHD Minimum Value | float | 2 | R
0x7339 | 0x733A | 29497 | 29498 | 10M_TOHD_AVGa | 10min Phase A TOHD Average Value | float | 2 | R
0x733B | 0x733C | 29499 | 29500 | 10M_TOHD_AVGb | 10min Phase B TOHD Average Value | float | 2 | R
0x733D | 0x733E | 29501 | 29502 | 10M_TOHD_AVGc | 10min Phase C TOHD Average Value | float | 2 | R
0x733F | 0x7340 | 29503 | 29504 | 10M_TEHD_MAXa | 10min Phase A TEHD Maximum Value | float | 2 | R
0x7341 | 0x7342 | 29505 | 29506 | 10M_TEHD_MAXb | 10min Phase B TEHD Maximum Value | float | 2 | R
0x7343 | 0x7344 | 29507 | 29508 | 10M_TEHD_MAXc | 10min Phase C TEHD Maximum Value | float | 2 | R
0x7345 | 0x7346 | 29509 | 29510 | 10M_TEHD_MINa | 10min Phase A TEHD Minimum Value | float | 2 | R
0x7347 | 0x7348 | 29511 | 29512 | 10M_TEHD_MINb | 10min Phase B TEHD Minimum Value | float | 2 | R
0x7349 | 0x734A | 29513 | 29514 | 10M_TEHD_MINc | 10min Phase C TEHD Minimum Value | float | 2 | R
0x734B | 0x734C | 29515 | 29516 | 10M_TEHD_AVGa | 10min Phase A TEHD Average Value | float | 2 | R
0x734D | 0x734E | 29517 | 29518 | 10M_TEHD_AVGb | 10min Phase B TEHD Average Value | float | 2 | R
0x734F | 0x7350 | 29519 | 29520 | 10M_TEHD_AVGc | 10min Phase C TEHD Average Value | float | 2 | R
0x7351 | 0x7351 | 29521 | 29521 | 2HR_N_VALID | 2hr Voltage Valid Counter | uint16 | 1 | R
0x7352 | 0x7352 | 29522 | 29522 | 2HR_N_INVALID | 2hr Voltage Invalid Counter | uint16 | 1 | R
0x7353 | 0x7353 | 29523 | 29523 | 2HR_N_PLTa1 | 2hr 1st Phase A Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7354 | 0x7354 | 29524 | 29524 | 2HR_N_PLTa2 | 2hr 2nd Phase A Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7355 | 0x7355 | 29525 | 29525 | 2HR_N_PLTb1 | 2hr 1st Phase B Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7356 | 0x7356 | 29526 | 29526 | 2HR_N_PLTb2 | 2hr 2nd Phase B Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7357 | 0x7357 | 29527 | 29527 | 2HR_N_PLTc1 | 2hr 1st Phase C Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7358 | 0x7358 | 29528 | 29528 | 2HR_N_PLTc2 | 2hr 2nd Phase C Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7359 | 0x735A | 29529 | 29530 | 2HR_PLT_PASSa | 2hr Phase A Flicker Severity Long-term Trigger Pass Rate | float | 2 | R
0x735B | 0x735C | 29531 | 29532 | 2HR_PLT_PASSb | 2hr Phase B Flicker Severity Long-term Trigger Pass Rate | float | 2 | R
0x735D | 0x735E | 29533 | 29534 | 2HR_PLT_PASSc | 2hr Phase C Flicker Severity Long-term Trigger Pass Rate | float | 2 | R
0x735F | 0x7360 | 29535 | 29536 | 2HR_PLT_MAXa | 2hr Phase A Flicker Severity Long-term Maximum Value | float | 2 | R
0x7361 | 0x7362 | 29537 | 29538 | 2HR_PLT_MAXb | 2hr Phase B Flicker Severity Long-term Maximum Value | float | 2 | R
0x7363 | 0x7364 | 29539 | 29540 | 2HR_PLT_MAXc | 2hr Phase C Flicker Severity Long-term Maximum Value | float | 2 | R
0x7365 | 0x7366 | 29541 | 29542 | 2HR_PLT_MINa | 2hr Phase A Flicker Severity Long-term Minimum Value | float | 2 | R
0x7367 | 0x7368 | 29543 | 29544 | 2HR_PLT_MINb | 2hr Phase B Flicker Severity Long-term Minimum Value | float | 2 | R
0x7369 | 0x736A | 29545 | 29546 | 2HR_PLT_MINc | 2hr Phase C Flicker Severity Long-term Minimum Value | float | 2 | R
0x736B | 0x736C | 29547 | 29548 | 2HR_PLT_AVGa | 2hr Phase A Flicker Severity Long-term Average Value | float | 2 | R
0x736D | 0x736E | 29549 | 29550 | 2HR_PLT_AVGb | 2hr Phase B Flicker Severity Long-term Average Value | float | 2 | R
0x736F | 0x7370 | 29551 | 29552 | 2HR_PLT_AVGc | 2hr Phase C Flicker Severity Long-term Average Value | float | 2 | R
PQ Report 50160 Last | [5 empty] | FALSE
0x7400 | 0x7400 | 29696 | 29696 | LAST_10S_N_VALID | Last Period 10sec Voltage Valid Counter | uint16 | 1 | R
0x7401 | 0x7401 | 29697 | 29697 | LAST_10S_N_INVALID | Last Period 10sec Voltage Invalid Counter | uint16 | 1 | R
0x7402 | 0x7402 | 29698 | 29698 | LAST_10S_N_FREQ1 | Last Period 10sec 1st Frequency Bin Counter | uint16 | 1 | R
0x7403 | 0x7403 | 29699 | 29699 | LAST_10S_N_FREQ2 | Last Period 10sec 2nd Frequency Bin Counter | uint16 | 1 | R
0x7404 | 0x7404 | 29700 | 29700 | LAST_10S_N_FREQ3 | Last Period 10sec 3rd Frequency Bin Counter | uint16 | 1 | R
0x7405 | 0x7405 | 29701 | 29701 | LAST_10S_N_FREQ4 | Last Period 10sec 4th Frequency Bin Counter | uint16 | 1 | R
0x7406 | 0x7406 | 29702 | 29702 | LAST_10S_N_FREQ5 | Last Period 10sec 5th Frequency Bin Counter | uint16 | 1 | R
0x7407 | 0x7408 | 29703 | 29704 | LAST_10S_FREQ_PASS1 | Last Period 10sec 1st Frequency Zone Trigger Pass Rate | float | 2 | R
0x7409 | 0x740A | 29705 | 29706 | LAST_10S_FREQ_PASS2 | Last Period 10sec 2nd Frequency Zone Trigger Pass Rate | float | 2 | R
0x740B | 0x740C | 29707 | 29708 | LAST_10S_FREQ_MAX | Last Period 10sec Frequency Maximum Value | float | 2 | R
0x740D | 0x740E | 29709 | 29710 | LAST_10S_FREQ_MIN | Last Period 10sec Frequency Minimum Value | float | 2 | R
0x740F | 0x7410 | 29711 | 29712 | LAST_10S_FREQ_AVG | Last Period 10sec Frequency Average Value | float | 2 | R
0x7411 | 0x7411 | 29713 | 29713 | LAST_10S_N_INTRPT1 | Last Period 10sec 1st PQ Event Interrupt Counter | uint16 | 1 | R
0x7412 | 0x7412 | 29714 | 29714 | LAST_10S_N_INTRPT2 | Last Period 10sec 2nd PQ Event Interrupt Counter | uint16 | 1 | R
0x7413 | 0x7413 | 29715 | 29715 | LAST_10S_N_INTRPT3 | Last Period 10sec 3rd PQ Event Interrupt Counter | uint16 | 1 | R
0x7414 | 0x7414 | 29716 | 29716 | LAST_10S_N_DIP_A1 | Last Period 10sec 1st PQ Event Voltage Dips Cell-A Counter | uint16 | 1 | R
0x7415 | 0x7415 | 29717 | 29717 | LAST_10S_N_DIP_A2 | Last Period 10sec 2nd PQ Event Voltage Dips Cell-A Counter | uint16 | 1 | R
0x7416 | 0x7416 | 29718 | 29718 | LAST_10S_N_DIP_A3 | Last Period 10sec 3rd PQ Event Voltage Dips Cell-A Counter | uint16 | 1 | R
0x7417 | 0x7417 | 29719 | 29719 | LAST_10S_N_DIP_A4 | Last Period 10sec 4th PQ Event Voltage Dips Cell-A Counter | uint16 | 1 | R
0x7418 | 0x7418 | 29720 | 29720 | LAST_10S_N_DIP_A5 | Last Period 10sec 5th PQ Event Voltage Dips Cell-A Counter | uint16 | 1 | R
0x7419 | 0x7419 | 29721 | 29721 | LAST_10S_N_DIP_B1 | Last Period 10sec 1st PQ Event Voltage Dips Cell-B Counter | uint16 | 1 | R
0x741A | 0x741A | 29722 | 29722 | LAST_10S_N_DIP_B2 | Last Period 10sec 2nd PQ Event Voltage Dips Cell-B Counter | uint16 | 1 | R
0x741B | 0x741B | 29723 | 29723 | LAST_10S_N_DIP_B3 | Last Period 10sec 3rd PQ Event Voltage Dips Cell-B Counter | uint16 | 1 | R
0x741C | 0x741C | 29724 | 29724 | LAST_10S_N_DIP_B4 | Last Period 10sec 4th PQ Event Voltage Dips Cell-B Counter | uint16 | 1 | R
0x741D | 0x741D | 29725 | 29725 | LAST_10S_N_DIP_B5 | Last Period 10sec 5th PQ Event Voltage Dips Cell-B Counter | uint16 | 1 | R
0x741E | 0x741E | 29726 | 29726 | LAST_10S_N_DIP_C1 | Last Period 10sec 1st PQ Event Voltage Dips Cell-C Counter | uint16 | 1 | R
0x741F | 0x741F | 29727 | 29727 | LAST_10S_N_DIP_C2 | Last Period 10sec 2nd PQ Event Voltage Dips Cell-C Counter | uint16 | 1 | R
0x7420 | 0x7420 | 29728 | 29728 | LAST_10S_N_DIP_C3 | Last Period 10sec 3rd PQ Event Voltage Dips Cell-C Counter | uint16 | 1 | R
0x7421 | 0x7421 | 29729 | 29729 | LAST_10S_N_DIP_C4 | Last Period 10sec 4th PQ Event Voltage Dips Cell-C Counter | uint16 | 1 | R
0x7422 | 0x7422 | 29730 | 29730 | LAST_10S_N_DIP_C5 | Last Period 10sec 5th PQ Event Voltage Dips Cell-C Counter | uint16 | 1 | R
0x7423 | 0x7423 | 29731 | 29731 | LAST_10S_N_DIP_D1 | Last Period 10sec 1st PQ Event Voltage Dips Cell-D Counter | uint16 | 1 | R
0x7424 | 0x7424 | 29732 | 29732 | LAST_10S_N_DIP_D2 | Last Period 10sec 2nd PQ Event Voltage Dips Cell-D Counter | uint16 | 1 | R
0x7425 | 0x7425 | 29733 | 29733 | LAST_10S_N_DIP_D3 | Last Period 10sec 3rd PQ Event Voltage Dips Cell-D Counter | uint16 | 1 | R
0x7426 | 0x7426 | 29734 | 29734 | LAST_10S_N_DIP_D4 | Last Period 10sec 4th PQ Event Voltage Dips Cell-D Counter | uint16 | 1 | R
0x7427 | 0x7427 | 29735 | 29735 | LAST_10S_N_DIP_D5 | Last Period 10sec 5th PQ Event Voltage Dips Cell-D Counter | uint16 | 1 | R
0x7428 | 0x7428 | 29736 | 29736 | LAST_10S_N_DIP_X1 | Last Period 10sec 1st PQ Event Voltage Dips Cell-X Counter | uint16 | 1 | R
0x7429 | 0x7429 | 29737 | 29737 | LAST_10S_N_DIP_X2 | Last Period 10sec 2nd PQ Event Voltage Dips Cell-X Counter | uint16 | 1 | R
0x742A | 0x742A | 29738 | 29738 | LAST_10S_N_DIP_X3 | Last Period 10sec 3rd PQ Event Voltage Dips Cell-X Counter | uint16 | 1 | R
0x742B | 0x742B | 29739 | 29739 | LAST_10S_N_DIP_X4 | Last Period 10sec 4th PQ Event Voltage Dips Cell-X Counter | uint16 | 1 | R
0x742C | 0x742C | 29740 | 29740 | LAST_10S_N_DIP_X5 | Last Period 10sec 5th PQ Event Voltage Dips Cell-X Counter | uint16 | 1 | R
0x742D | 0x742D | 29741 | 29741 | LAST_10S_N_SWELL_S1 | Last Period 10sec 1st PQ Event Voltage Swells Cell-S Counter | uint16 | 1 | R
0x742E | 0x742E | 29742 | 29742 | LAST_10S_N_SWELL_S2 | Last Period 10sec 2nd PQ Event Voltage Swells Cell-S Counter | uint16 | 1 | R
0x742F | 0x742F | 29743 | 29743 | LAST_10S_N_SWELL_S3 | Last Period 10sec 3rd PQ Event Voltage Swells Cell-S Counter | uint16 | 1 | R
0x7430 | 0x7430 | 29744 | 29744 | LAST_10S_N_SWELL_T1 | Last Period 10sec 1st PQ Event Voltage Swells Cell-T Counter | uint16 | 1 | R
0x7431 | 0x7431 | 29745 | 29745 | LAST_10S_N_SWELL_T2 | Last Period 10sec 2nd PQ Event Voltage Swells Cell-T Counter | uint16 | 1 | R
0x7432 | 0x7432 | 29746 | 29746 | LAST_10S_N_SWELL_T3 | Last Period 10sec 3rd PQ Event Voltage Swells Cell-T Counter | uint16 | 1 | R
0x7433 | 0x7433 | 29747 | 29747 | LAST_10M_N_VALID | Last Period 10min Voltage Valid Counter | uint16 | 1 | R
0x7434 | 0x7434 | 29748 | 29748 | LAST_10M_N_INVALID | Last Period 10min Voltage Invalid Counter | uint16 | 1 | R
0x7435 | 0x7435 | 29749 | 29749 | LAST_10M_N_RMSa1 | Last Period 10min 1st Phase A RMS Voltage Bin Counter | uint16 | 1 | R
0x7436 | 0x7436 | 29750 | 29750 | LAST_10M_N_RMSa2 | Last Period 10min 2nd Phase A RMS Voltage Bin Counter | uint16 | 1 | R
0x7437 | 0x7437 | 29751 | 29751 | LAST_10M_N_RMSa3 | Last Period 10min 3rd Phase A RMS Voltage Bin Counter | uint16 | 1 | R
0x7438 | 0x7438 | 29752 | 29752 | LAST_10M_N_RMSa4 | Last Period 10min 4th Phase A RMS Voltage Bin Counter | uint16 | 1 | R
0x7439 | 0x7439 | 29753 | 29753 | LAST_10M_N_RMSa5 | Last Period 10min 5th Phase A RMS Voltage Bin Counter | uint16 | 1 | R
0x743A | 0x743A | 29754 | 29754 | LAST_10M_N_RMSb1 | Last Period 10min 1st Phase B RMS Voltage Bin Counter | uint16 | 1 | R
0x743B | 0x743B | 29755 | 29755 | LAST_10M_N_RMSb2 | Last Period 10min 2nd Phase B RMS Voltage Bin Counter | uint16 | 1 | R
0x743C | 0x743C | 29756 | 29756 | LAST_10M_N_RMSb3 | Last Period 10min 3rd Phase B RMS Voltage Bin Counter | uint16 | 1 | R
0x743D | 0x743D | 29757 | 29757 | LAST_10M_N_RMSb4 | Last Period 10min 4th Phase B RMS Voltage Bin Counter | uint16 | 1 | R
0x743E | 0x743E | 29758 | 29758 | LAST_10M_N_RMSb5 | Last Period 10min 5th Phase B RMS Voltage Bin Counter | uint16 | 1 | R
0x743F | 0x743F | 29759 | 29759 | LAST_10M_N_RMSc1 | Last Period 10min 1st Phase C RMS Voltage Bin Counter | uint16 | 1 | R
0x7440 | 0x7440 | 29760 | 29760 | LAST_10M_N_RMSc2 | Last Period 10min 2nd Phase C RMS Voltage Bin Counter | uint16 | 1 | R
0x7441 | 0x7441 | 29761 | 29761 | LAST_10M_N_RMSc3 | Last Period 10min 3rd Phase C RMS Voltage Bin Counter | uint16 | 1 | R
0x7442 | 0x7442 | 29762 | 29762 | LAST_10M_N_RMSc4 | Last Period 10min 4th Phase C RMS Voltage Bin Counter | uint16 | 1 | R
0x7443 | 0x7443 | 29763 | 29763 | LAST_10M_N_RMSc5 | Last Period 10min 5th Phase C RMS Voltage Bin Counter | uint16 | 1 | R
0x7444 | 0x7445 | 29764 | 29765 | LAST_10M_RMS_PASSa1 | Last Period 10min 1st Phase A RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x7446 | 0x7447 | 29766 | 29767 | LAST_10M_RMS_PASSa2 | Last Period 10min 2nd Phase A RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x7448 | 0x7449 | 29768 | 29769 | LAST_10M_RMS_PASSb1 | Last Period 10min 1st Phase B RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x744A | 0x744B | 29770 | 29771 | LAST_10M_RMS_PASSb2 | Last Period 10min 2nd Phase B RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x744C | 0x744D | 29772 | 29773 | LAST_10M_RMS_PASSc1 | Last Period 10min 1st Phase C RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x744E | 0x744F | 29774 | 29775 | LAST_10M_RMS_PASSc2 | Last Period 10min 2nd Phase C RMS Voltage Zone Trigger Pass Rate | float | 2 | R
0x7450 | 0x7451 | 29776 | 29777 | LAST_10M_RMS_MAXa | Last Period 10min Phase A RMS Voltage Maximum Value | float | 2 | R
0x7452 | 0x7453 | 29778 | 29779 | LAST_10M_RMS_MAXb | Last Period 10min Phase B RMS Voltage Maximum Value | float | 2 | R
0x7454 | 0x7455 | 29780 | 29781 | LAST_10M_RMS_MAXc | Last Period 10min Phase C RMS Voltage Maximum Value | float | 2 | R
0x7456 | 0x7457 | 29782 | 29783 | LAST_10M_RMS_MINa | Last Period 10min Phase A RMS Voltage Minimum Value | float | 2 | R
0x7458 | 0x7459 | 29784 | 29785 | LAST_10M_RMS_MINb | Last Period 10min Phase B RMS Voltage Minimum Value | float | 2 | R
0x745A | 0x745B | 29786 | 29787 | LAST_10M_RMS_MINc | Last Period 10min Phase C RMS Voltage Minimum Value | float | 2 | R
0x745C | 0x745D | 29788 | 29789 | LAST_10M_RMS_AVGa | Last Period 10min Phase A RMS Voltage Average Value | float | 2 | R
0x745E | 0x745F | 29790 | 29791 | LAST_10M_RMS_AVGb | Last Period 10min Phase B RMS Voltage Average Value | float | 2 | R
0x7460 | 0x7461 | 29792 | 29793 | LAST_10M_RMS_AVGc | Last Period 10min Phase C RMS Voltage Average Value | float | 2 | R
0x7462 | 0x7462 | 29794 | 29794 | LAST_10M_N_PSTa1 | Last Period 10min 1st Phase A Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7463 | 0x7463 | 29795 | 29795 | LAST_10M_N_PSTa2 | Last Period 10min 2nd Phase A Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7464 | 0x7464 | 29796 | 29796 | LAST_10M_N_PSTb1 | Last Period 10min 1st Phase B Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7465 | 0x7465 | 29797 | 29797 | LAST_10M_N_PSTb2 | Last Period 10min 2nd Phase B Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7466 | 0x7466 | 29798 | 29798 | LAST_10M_N_PSTc1 | Last Period 10min 1st Phase C Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7467 | 0x7467 | 29799 | 29799 | LAST_10M_N_PSTc2 | Last Period 10min 2nd Phase C Flicker Severity Short-term Bin Counter | uint16 | 1 | R
0x7468 | 0x7469 | 29800 | 29801 | LAST_10M_PST_PASSa | Last Period 10min Phase A Flicker Severity Short-term Zone Trigger Pass Rate | float | 2 | R
0x746A | 0x746B | 29802 | 29803 | LAST_10M_PST_PASSb | Last Period 10min Phase B Flicker Severity Short-term Zone Trigger Pass Rate | float | 2 | R
0x746C | 0x746D | 29804 | 29805 | LAST_10M_PST_PASSc | Last Period 10min Phase C Flicker Severity Short-term Zone Trigger Pass Rate | float | 2 | R
0x746E | 0x746F | 29806 | 29807 | LAST_10M_PST_MAXa | Last Period 10min Phase A Flicker Severity Short-term Maximum Value | float | 2 | R
0x7470 | 0x7471 | 29808 | 29809 | LAST_10M_PST_MAXb | Last Period 10min Phase B Flicker Severity Short-term Maximum Value | float | 2 | R
0x7472 | 0x7473 | 29810 | 29811 | LAST_10M_PST_MAXc | Last Period 10min Phase C Flicker Severity Short-term Maximum Value | float | 2 | R
0x7474 | 0x7475 | 29812 | 29813 | LAST_10M_PST_MINa | Last Period 10min Phase A Flicker Severity Short-term Minimum Value | float | 2 | R
0x7476 | 0x7477 | 29814 | 29815 | LAST_10M_PST_MINb | Last Period 10min Phase B Flicker Severity Short-term Minimum Value | float | 2 | R
0x7478 | 0x7479 | 29816 | 29817 | LAST_10M_PST_MINc | Last Period 10min Phase C Flicker Severity Short-term Minimum Value | float | 2 | R
0x747A | 0x747B | 29818 | 29819 | LAST_10M_PST_AVGa | Last Period 10min Phase A Flicker Severity Short-term Average Value | float | 2 | R
0x747C | 0x747D | 29820 | 29821 | LAST_10M_PST_AVGb | Last Period 10min Phase B Flicker Severity Short-term Average Value | float | 2 | R
0x747E | 0x747F | 29822 | 29823 | LAST_10M_PST_AVGc | Last Period 10min Phase C Flicker Severity Short-term Average Value | float | 2 | R
0x7480 | 0x7480 | 29824 | 29824 | LAST_10M_N_UNBL1 | Last Period 10min 1st Voltage Unbalance Bin Counter | uint16 | 1 | R
0x7481 | 0x7481 | 29825 | 29825 | LAST_10M_N_UNBL2 | Last Period 10min 2nd Voltage Unbalance Bin Counter | uint16 | 1 | R
0x7482 | 0x7483 | 29826 | 29827 | LAST_10M_UNBL_PASS | Last Period 10min Voltage Unbalance Zone Trigger Pass Rate | float | 2 | R
0x7484 | 0x7485 | 29828 | 29829 | LAST_10M_UNBL_MAX | Last Period 10min Voltage Unbalance Maximum Value | float | 2 | R
0x7486 | 0x7487 | 29830 | 29831 | LAST_10M_UNBL_MIN | Last Period 10min Voltage Unbalance Minimum Value | float | 2 | R
0x7488 | 0x7489 | 29832 | 29833 | LAST_10M_UNBL_AVG | Last Period 10min Voltage Unbalance Average Value | float | 2 | R
0x748A | 0x748A | 29834 | 29834 | LAST_10M_N_HRMa2 | Last Period 10min 2nd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x748B | 0x748B | 29835 | 29835 | LAST_10M_N_HRMa3 | Last Period 10min 3rd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x748C | 0x748C | 29836 | 29836 | LAST_10M_N_HRMa4 | Last Period 10min 4th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x748D | 0x748D | 29837 | 29837 | LAST_10M_N_HRMa5 | Last Period 10min 5th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x748E | 0x748E | 29838 | 29838 | LAST_10M_N_HRMa6 | Last Period 10min 6th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x748F | 0x748F | 29839 | 29839 | LAST_10M_N_HRMa7 | Last Period 10min 7th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7490 | 0x7490 | 29840 | 29840 | LAST_10M_N_HRMa8 | Last Period 10min 8th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7491 | 0x7491 | 29841 | 29841 | LAST_10M_N_HRMa9 | Last Period 10min 9th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7492 | 0x7492 | 29842 | 29842 | LAST_10M_N_HRMa10 | Last Period 10min 10th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7493 | 0x7493 | 29843 | 29843 | LAST_10M_N_HRMa11 | Last Period 10min 11st Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7494 | 0x7494 | 29844 | 29844 | LAST_10M_N_HRMa12 | Last Period 10min 12nd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7495 | 0x7495 | 29845 | 29845 | LAST_10M_N_HRMa13 | Last Period 10min 13rd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7496 | 0x7496 | 29846 | 29846 | LAST_10M_N_HRMa14 | Last Period 10min 14th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7497 | 0x7497 | 29847 | 29847 | LAST_10M_N_HRMa15 | Last Period 10min 15th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7498 | 0x7498 | 29848 | 29848 | LAST_10M_N_HRMa16 | Last Period 10min 16th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x7499 | 0x7499 | 29849 | 29849 | LAST_10M_N_HRMa17 | Last Period 10min 17th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x749A | 0x749A | 29850 | 29850 | LAST_10M_N_HRMa18 | Last Period 10min 18th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x749B | 0x749B | 29851 | 29851 | LAST_10M_N_HRMa19 | Last Period 10min 19th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x749C | 0x749C | 29852 | 29852 | LAST_10M_N_HRMa20 | Last Period 10min 20th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x749D | 0x749D | 29853 | 29853 | LAST_10M_N_HRMa21 | Last Period 10min 21st Phase A Harmonics Bin Counter | uint16 | 1 | R
0x749E | 0x749E | 29854 | 29854 | LAST_10M_N_HRMa22 | Last Period 10min 22nd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x749F | 0x749F | 29855 | 29855 | LAST_10M_N_HRMa23 | Last Period 10min 23rd Phase A Harmonics Bin Counter | uint16 | 1 | R
0x74A0 | 0x74A0 | 29856 | 29856 | LAST_10M_N_HRMa24 | Last Period 10min 24th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x74A1 | 0x74A1 | 29857 | 29857 | LAST_10M_N_HRMa25 | Last Period 10min 25th Phase A Harmonics Bin Counter | uint16 | 1 | R
0x74A2 | 0x74A2 | 29858 | 29858 | LAST_10M_N_HRMb2 | Last Period 10min 2nd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74A3 | 0x74A3 | 29859 | 29859 | LAST_10M_N_HRMb3 | Last Period 10min 3rd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74A4 | 0x74A4 | 29860 | 29860 | LAST_10M_N_HRMb4 | Last Period 10min 4th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74A5 | 0x74A5 | 29861 | 29861 | LAST_10M_N_HRMb5 | Last Period 10min 5th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74A6 | 0x74A6 | 29862 | 29862 | LAST_10M_N_HRMb6 | Last Period 10min 6th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74A7 | 0x74A7 | 29863 | 29863 | LAST_10M_N_HRMb7 | Last Period 10min 7th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74A8 | 0x74A8 | 29864 | 29864 | LAST_10M_N_HRMb8 | Last Period 10min 8th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74A9 | 0x74A9 | 29865 | 29865 | LAST_10M_N_HRMb9 | Last Period 10min 9th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74AA | 0x74AA | 29866 | 29866 | LAST_10M_N_HRMb10 | Last Period 10min 10th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74AB | 0x74AB | 29867 | 29867 | LAST_10M_N_HRMb11 | Last Period 10min 11st Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74AC | 0x74AC | 29868 | 29868 | LAST_10M_N_HRMb12 | Last Period 10min 12nd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74AD | 0x74AD | 29869 | 29869 | LAST_10M_N_HRMb13 | Last Period 10min 13rd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74AE | 0x74AE | 29870 | 29870 | LAST_10M_N_HRMb14 | Last Period 10min 14th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74AF | 0x74AF | 29871 | 29871 | LAST_10M_N_HRMb15 | Last Period 10min 15th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74B0 | 0x74B0 | 29872 | 29872 | LAST_10M_N_HRMb16 | Last Period 10min 16th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74B1 | 0x74B1 | 29873 | 29873 | LAST_10M_N_HRMb17 | Last Period 10min 17th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74B2 | 0x74B2 | 29874 | 29874 | LAST_10M_N_HRMb18 | Last Period 10min 18th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74B3 | 0x74B3 | 29875 | 29875 | LAST_10M_N_HRMb19 | Last Period 10min 19th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74B4 | 0x74B4 | 29876 | 29876 | LAST_10M_N_HRMb20 | Last Period 10min 20th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74B5 | 0x74B5 | 29877 | 29877 | LAST_10M_N_HRMb21 | Last Period 10min 21st Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74B6 | 0x74B6 | 29878 | 29878 | LAST_10M_N_HRMb22 | Last Period 10min 22nd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74B7 | 0x74B7 | 29879 | 29879 | LAST_10M_N_HRMb23 | Last Period 10min 23rd Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74B8 | 0x74B8 | 29880 | 29880 | LAST_10M_N_HRMb24 | Last Period 10min 24th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74B9 | 0x74B9 | 29881 | 29881 | LAST_10M_N_HRMb25 | Last Period 10min 25th Phase B Harmonics Bin Counter | uint16 | 1 | R
0x74BA | 0x74BA | 29882 | 29882 | LAST_10M_N_HRMc2 | Last Period 10min 2nd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74BB | 0x74BB | 29883 | 29883 | LAST_10M_N_HRMc3 | Last Period 10min 3rd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74BC | 0x74BC | 29884 | 29884 | LAST_10M_N_HRMc4 | Last Period 10min 4th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74BD | 0x74BD | 29885 | 29885 | LAST_10M_N_HRMc5 | Last Period 10min 5th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74BE | 0x74BE | 29886 | 29886 | LAST_10M_N_HRMc6 | Last Period 10min 6th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74BF | 0x74BF | 29887 | 29887 | LAST_10M_N_HRMc7 | Last Period 10min 7th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74C0 | 0x74C0 | 29888 | 29888 | LAST_10M_N_HRMc8 | Last Period 10min 8th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74C1 | 0x74C1 | 29889 | 29889 | LAST_10M_N_HRMc9 | Last Period 10min 9th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74C2 | 0x74C2 | 29890 | 29890 | LAST_10M_N_HRMc10 | Last Period 10min 10th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74C3 | 0x74C3 | 29891 | 29891 | LAST_10M_N_HRMc11 | Last Period 10min 11st Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74C4 | 0x74C4 | 29892 | 29892 | LAST_10M_N_HRMc12 | Last Period 10min 12nd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74C5 | 0x74C5 | 29893 | 29893 | LAST_10M_N_HRMc13 | Last Period 10min 13rd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74C6 | 0x74C6 | 29894 | 29894 | LAST_10M_N_HRMc14 | Last Period 10min 14th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74C7 | 0x74C7 | 29895 | 29895 | LAST_10M_N_HRMc15 | Last Period 10min 15th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74C8 | 0x74C8 | 29896 | 29896 | LAST_10M_N_HRMc16 | Last Period 10min 16th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74C9 | 0x74C9 | 29897 | 29897 | LAST_10M_N_HRMc17 | Last Period 10min 17th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74CA | 0x74CA | 29898 | 29898 | LAST_10M_N_HRMc18 | Last Period 10min 18th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74CB | 0x74CB | 29899 | 29899 | LAST_10M_N_HRMc19 | Last Period 10min 19th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74CC | 0x74CC | 29900 | 29900 | LAST_10M_N_HRMc20 | Last Period 10min 20th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74CD | 0x74CD | 29901 | 29901 | LAST_10M_N_HRMc21 | Last Period 10min 21st Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74CE | 0x74CE | 29902 | 29902 | LAST_10M_N_HRMc22 | Last Period 10min 22nd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74CF | 0x74CF | 29903 | 29903 | LAST_10M_N_HRMc23 | Last Period 10min 23rd Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74D0 | 0x74D0 | 29904 | 29904 | LAST_10M_N_HRMc24 | Last Period 10min 24th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74D1 | 0x74D1 | 29905 | 29905 | LAST_10M_N_HRMc25 | Last Period 10min 25th Phase C Harmonics Bin Counter | uint16 | 1 | R
0x74D2 | 0x74D3 | 29906 | 29907 | LAST_10M_HRM_PASSa2 | Last Period 10min 2nd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74D4 | 0x74D5 | 29908 | 29909 | LAST_10M_HRM_PASSa3 | Last Period 10min 3rd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74D6 | 0x74D7 | 29910 | 29911 | LAST_10M_HRM_PASSa4 | Last Period 10min 4th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74D8 | 0x74D9 | 29912 | 29913 | LAST_10M_HRM_PASSa5 | Last Period 10min 5th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74DA | 0x74DB | 29914 | 29915 | LAST_10M_HRM_PASSa6 | Last Period 10min 6th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74DC | 0x74DD | 29916 | 29917 | LAST_10M_HRM_PASSa7 | Last Period 10min 7th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74DE | 0x74DF | 29918 | 29919 | LAST_10M_HRM_PASSa8 | Last Period 10min 8th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74E0 | 0x74E1 | 29920 | 29921 | LAST_10M_HRM_PASSa9 | Last Period 10min 9th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74E2 | 0x74E3 | 29922 | 29923 | LAST_10M_HRM_PASSa10 | Last Period 10min 10th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74E4 | 0x74E5 | 29924 | 29925 | LAST_10M_HRM_PASSa11 | Last Period 10min 11st Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74E6 | 0x74E7 | 29926 | 29927 | LAST_10M_HRM_PASSa12 | Last Period 10min 12nd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74E8 | 0x74E9 | 29928 | 29929 | LAST_10M_HRM_PASSa13 | Last Period 10min 13rd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74EA | 0x74EB | 29930 | 29931 | LAST_10M_HRM_PASSa14 | Last Period 10min 14th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74EC | 0x74ED | 29932 | 29933 | LAST_10M_HRM_PASSa15 | Last Period 10min 15th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74EE | 0x74EF | 29934 | 29935 | LAST_10M_HRM_PASSa16 | Last Period 10min 16th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74F0 | 0x74F1 | 29936 | 29937 | LAST_10M_HRM_PASSa17 | Last Period 10min 17th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74F2 | 0x74F3 | 29938 | 29939 | LAST_10M_HRM_PASSa18 | Last Period 10min 18th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74F4 | 0x74F5 | 29940 | 29941 | LAST_10M_HRM_PASSa19 | Last Period 10min 19th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74F6 | 0x74F7 | 29942 | 29943 | LAST_10M_HRM_PASSa20 | Last Period 10min 20th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74F8 | 0x74F9 | 29944 | 29945 | LAST_10M_HRM_PASSa21 | Last Period 10min 21st Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74FA | 0x74FB | 29946 | 29947 | LAST_10M_HRM_PASSa22 | Last Period 10min 22nd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74FC | 0x74FD | 29948 | 29949 | LAST_10M_HRM_PASSa23 | Last Period 10min 23rd Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x74FE | 0x74FF | 29950 | 29951 | LAST_10M_HRM_PASSa24 | Last Period 10min 24th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7500 | 0x7501 | 29952 | 29953 | LAST_10M_HRM_PASSa25 | Last Period 10min 25th Phase A Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7502 | 0x7503 | 29954 | 29955 | LAST_10M_HRM_PASSb2 | Last Period 10min 2nd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7504 | 0x7505 | 29956 | 29957 | LAST_10M_HRM_PASSb3 | Last Period 10min 3rd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7506 | 0x7507 | 29958 | 29959 | LAST_10M_HRM_PASSb4 | Last Period 10min 4th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7508 | 0x7509 | 29960 | 29961 | LAST_10M_HRM_PASSb5 | Last Period 10min 5th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x750A | 0x750B | 29962 | 29963 | LAST_10M_HRM_PASSb6 | Last Period 10min 6th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x750C | 0x750D | 29964 | 29965 | LAST_10M_HRM_PASSb7 | Last Period 10min 7th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x750E | 0x750F | 29966 | 29967 | LAST_10M_HRM_PASSb8 | Last Period 10min 8th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7510 | 0x7511 | 29968 | 29969 | LAST_10M_HRM_PASSb9 | Last Period 10min 9th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7512 | 0x7513 | 29970 | 29971 | LAST_10M_HRM_PASSb10 | Last Period 10min 10th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7514 | 0x7515 | 29972 | 29973 | LAST_10M_HRM_PASSb11 | Last Period 10min 11st Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7516 | 0x7517 | 29974 | 29975 | LAST_10M_HRM_PASSb12 | Last Period 10min 12nd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7518 | 0x7519 | 29976 | 29977 | LAST_10M_HRM_PASSb13 | Last Period 10min 13rd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x751A | 0x751B | 29978 | 29979 | LAST_10M_HRM_PASSb14 | Last Period 10min 14th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x751C | 0x751D | 29980 | 29981 | LAST_10M_HRM_PASSb15 | Last Period 10min 15th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x751E | 0x751F | 29982 | 29983 | LAST_10M_HRM_PASSb16 | Last Period 10min 16th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7520 | 0x7521 | 29984 | 29985 | LAST_10M_HRM_PASSb17 | Last Period 10min 17th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7522 | 0x7523 | 29986 | 29987 | LAST_10M_HRM_PASSb18 | Last Period 10min 18th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7524 | 0x7525 | 29988 | 29989 | LAST_10M_HRM_PASSb19 | Last Period 10min 19th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7526 | 0x7527 | 29990 | 29991 | LAST_10M_HRM_PASSb20 | Last Period 10min 20th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7528 | 0x7529 | 29992 | 29993 | LAST_10M_HRM_PASSb21 | Last Period 10min 21st Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x752A | 0x752B | 29994 | 29995 | LAST_10M_HRM_PASSb22 | Last Period 10min 22nd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x752C | 0x752D | 29996 | 29997 | LAST_10M_HRM_PASSb23 | Last Period 10min 23rd Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x752E | 0x752F | 29998 | 29999 | LAST_10M_HRM_PASSb24 | Last Period 10min 24th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7530 | 0x7531 | 30000 | 30001 | LAST_10M_HRM_PASSb25 | Last Period 10min 25th Phase B Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7532 | 0x7533 | 30002 | 30003 | LAST_10M_HRM_PASSc2 | Last Period 10min 2nd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7534 | 0x7535 | 30004 | 30005 | LAST_10M_HRM_PASSc3 | Last Period 10min 3rd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7536 | 0x7537 | 30006 | 30007 | LAST_10M_HRM_PASSc4 | Last Period 10min 4th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7538 | 0x7539 | 30008 | 30009 | LAST_10M_HRM_PASSc5 | Last Period 10min 5th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x753A | 0x753B | 30010 | 30011 | LAST_10M_HRM_PASSc6 | Last Period 10min 6th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x753C | 0x753D | 30012 | 30013 | LAST_10M_HRM_PASSc7 | Last Period 10min 7th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x753E | 0x753F | 30014 | 30015 | LAST_10M_HRM_PASSc8 | Last Period 10min 8th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7540 | 0x7541 | 30016 | 30017 | LAST_10M_HRM_PASSc9 | Last Period 10min 9th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7542 | 0x7543 | 30018 | 30019 | LAST_10M_HRM_PASSc10 | Last Period 10min 10th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7544 | 0x7545 | 30020 | 30021 | LAST_10M_HRM_PASSc11 | Last Period 10min 11st Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7546 | 0x7547 | 30022 | 30023 | LAST_10M_HRM_PASSc12 | Last Period 10min 12nd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7548 | 0x7549 | 30024 | 30025 | LAST_10M_HRM_PASSc13 | Last Period 10min 13rd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x754A | 0x754B | 30026 | 30027 | LAST_10M_HRM_PASSc14 | Last Period 10min 14th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x754C | 0x754D | 30028 | 30029 | LAST_10M_HRM_PASSc15 | Last Period 10min 15th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x754E | 0x754F | 30030 | 30031 | LAST_10M_HRM_PASSc16 | Last Period 10min 16th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7550 | 0x7551 | 30032 | 30033 | LAST_10M_HRM_PASSc17 | Last Period 10min 17th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7552 | 0x7553 | 30034 | 30035 | LAST_10M_HRM_PASSc18 | Last Period 10min 18th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7554 | 0x7555 | 30036 | 30037 | LAST_10M_HRM_PASSc19 | Last Period 10min 19th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7556 | 0x7557 | 30038 | 30039 | LAST_10M_HRM_PASSc20 | Last Period 10min 20th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7558 | 0x7559 | 30040 | 30041 | LAST_10M_HRM_PASSc21 | Last Period 10min 21st Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x755A | 0x755B | 30042 | 30043 | LAST_10M_HRM_PASSc22 | Last Period 10min 22nd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x755C | 0x755D | 30044 | 30045 | LAST_10M_HRM_PASSc23 | Last Period 10min 23rd Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x755E | 0x755F | 30046 | 30047 | LAST_10M_HRM_PASSc24 | Last Period 10min 24th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7560 | 0x7561 | 30048 | 30049 | LAST_10M_HRM_PASSc25 | Last Period 10min 25th Phase C Harmonics Zone Trigger Pass Rate | float | 2 | R
0x7562 | 0x7563 | 30050 | 30051 | LAST_10M_HRM_MAXa2 | Last Period 10min 2nd Phase A Harmonics Max Value | float | 2 | R
0x7564 | 0x7565 | 30052 | 30053 | LAST_10M_HRM_MAXa3 | Last Period 10min 3rd Phase A Harmonics Max Value | float | 2 | R
0x7566 | 0x7567 | 30054 | 30055 | LAST_10M_HRM_MAXa4 | Last Period 10min 4th Phase A Harmonics Max Value | float | 2 | R
0x7568 | 0x7569 | 30056 | 30057 | LAST_10M_HRM_MAXa5 | Last Period 10min 5th Phase A Harmonics Max Value | float | 2 | R
0x756A | 0x756B | 30058 | 30059 | LAST_10M_HRM_MAXa6 | Last Period 10min 6th Phase A Harmonics Max Value | float | 2 | R
0x756C | 0x756D | 30060 | 30061 | LAST_10M_HRM_MAXa7 | Last Period 10min 7th Phase A Harmonics Max Value | float | 2 | R
0x756E | 0x756F | 30062 | 30063 | LAST_10M_HRM_MAXa8 | Last Period 10min 8th Phase A Harmonics Max Value | float | 2 | R
0x7570 | 0x7571 | 30064 | 30065 | LAST_10M_HRM_MAXa9 | Last Period 10min 9th Phase A Harmonics Max Value | float | 2 | R
0x7572 | 0x7573 | 30066 | 30067 | LAST_10M_HRM_MAXa10 | Last Period 10min 10th Phase A Harmonics Max Value | float | 2 | R
0x7574 | 0x7575 | 30068 | 30069 | LAST_10M_HRM_MAXa11 | Last Period 10min 11st Phase A Harmonics Max Value | float | 2 | R
0x7576 | 0x7577 | 30070 | 30071 | LAST_10M_HRM_MAXa12 | Last Period 10min 12nd Phase A Harmonics Max Value | float | 2 | R
0x7578 | 0x7579 | 30072 | 30073 | LAST_10M_HRM_MAXa13 | Last Period 10min 13rd Phase A Harmonics Max Value | float | 2 | R
0x757A | 0x757B | 30074 | 30075 | LAST_10M_HRM_MAXa14 | Last Period 10min 14th Phase A Harmonics Max Value | float | 2 | R
0x757C | 0x757D | 30076 | 30077 | LAST_10M_HRM_MAXa15 | Last Period 10min 15th Phase A Harmonics Max Value | float | 2 | R
0x757E | 0x757F | 30078 | 30079 | LAST_10M_HRM_MAXa16 | Last Period 10min 16th Phase A Harmonics Max Value | float | 2 | R
0x7580 | 0x7581 | 30080 | 30081 | LAST_10M_HRM_MAXa17 | Last Period 10min 17th Phase A Harmonics Max Value | float | 2 | R
0x7582 | 0x7583 | 30082 | 30083 | LAST_10M_HRM_MAXa18 | Last Period 10min 18th Phase A Harmonics Max Value | float | 2 | R
0x7584 | 0x7585 | 30084 | 30085 | LAST_10M_HRM_MAXa19 | Last Period 10min 19th Phase A Harmonics Max Value | float | 2 | R
0x7586 | 0x7587 | 30086 | 30087 | LAST_10M_HRM_MAXa20 | Last Period 10min 20th Phase A Harmonics Max Value | float | 2 | R
0x7588 | 0x7589 | 30088 | 30089 | LAST_10M_HRM_MAXa21 | Last Period 10min 21st Phase A Harmonics Max Value | float | 2 | R
0x758A | 0x758B | 30090 | 30091 | LAST_10M_HRM_MAXa22 | Last Period 10min 22nd Phase A Harmonics Max Value | float | 2 | R
0x758C | 0x758D | 30092 | 30093 | LAST_10M_HRM_MAXa23 | Last Period 10min 23rd Phase A Harmonics Max Value | float | 2 | R
0x758E | 0x758F | 30094 | 30095 | LAST_10M_HRM_MAXa24 | Last Period 10min 24th Phase A Harmonics Max Value | float | 2 | R
0x7590 | 0x7591 | 30096 | 30097 | LAST_10M_HRM_MAXa25 | Last Period 10min 25th Phase A Harmonics Max Value | float | 2 | R
0x7592 | 0x7593 | 30098 | 30099 | LAST_10M_HRM_MAXb2 | Last Period 10min 2nd Phase B Harmonics Max Value | float | 2 | R
0x7594 | 0x7595 | 30100 | 30101 | LAST_10M_HRM_MAXb3 | Last Period 10min 3rd Phase B Harmonics Max Value | float | 2 | R
0x7596 | 0x7597 | 30102 | 30103 | LAST_10M_HRM_MAXb4 | Last Period 10min 4th Phase B Harmonics Max Value | float | 2 | R
0x7598 | 0x7599 | 30104 | 30105 | LAST_10M_HRM_MAXb5 | Last Period 10min 5th Phase B Harmonics Max Value | float | 2 | R
0x759A | 0x759B | 30106 | 30107 | LAST_10M_HRM_MAXb6 | Last Period 10min 6th Phase B Harmonics Max Value | float | 2 | R
0x759C | 0x759D | 30108 | 30109 | LAST_10M_HRM_MAXb7 | Last Period 10min 7th Phase B Harmonics Max Value | float | 2 | R
0x759E | 0x759F | 30110 | 30111 | LAST_10M_HRM_MAXb8 | Last Period 10min 8th Phase B Harmonics Max Value | float | 2 | R
0x75A0 | 0x75A1 | 30112 | 30113 | LAST_10M_HRM_MAXb9 | Last Period 10min 9th Phase B Harmonics Max Value | float | 2 | R
0x75A2 | 0x75A3 | 30114 | 30115 | LAST_10M_HRM_MAXb10 | Last Period 10min 10th Phase B Harmonics Max Value | float | 2 | R
0x75A4 | 0x75A5 | 30116 | 30117 | LAST_10M_HRM_MAXb11 | Last Period 10min 11st Phase B Harmonics Max Value | float | 2 | R
0x75A6 | 0x75A7 | 30118 | 30119 | LAST_10M_HRM_MAXb12 | Last Period 10min 12nd Phase B Harmonics Max Value | float | 2 | R
0x75A8 | 0x75A9 | 30120 | 30121 | LAST_10M_HRM_MAXb13 | Last Period 10min 13rd Phase B Harmonics Max Value | float | 2 | R
0x75AA | 0x75AB | 30122 | 30123 | LAST_10M_HRM_MAXb14 | Last Period 10min 14th Phase B Harmonics Max Value | float | 2 | R
0x75AC | 0x75AD | 30124 | 30125 | LAST_10M_HRM_MAXb15 | Last Period 10min 15th Phase B Harmonics Max Value | float | 2 | R
0x75AE | 0x75AF | 30126 | 30127 | LAST_10M_HRM_MAXb16 | Last Period 10min 16th Phase B Harmonics Max Value | float | 2 | R
0x75B0 | 0x75B1 | 30128 | 30129 | LAST_10M_HRM_MAXb17 | Last Period 10min 17th Phase B Harmonics Max Value | float | 2 | R
0x75B2 | 0x75B3 | 30130 | 30131 | LAST_10M_HRM_MAXb18 | Last Period 10min 18th Phase B Harmonics Max Value | float | 2 | R
0x75B4 | 0x75B5 | 30132 | 30133 | LAST_10M_HRM_MAXb19 | Last Period 10min 19th Phase B Harmonics Max Value | float | 2 | R
0x75B6 | 0x75B7 | 30134 | 30135 | LAST_10M_HRM_MAXb20 | Last Period 10min 20th Phase B Harmonics Max Value | float | 2 | R
0x75B8 | 0x75B9 | 30136 | 30137 | LAST_10M_HRM_MAXb21 | Last Period 10min 21st Phase B Harmonics Max Value | float | 2 | R
0x75BA | 0x75BB | 30138 | 30139 | LAST_10M_HRM_MAXb22 | Last Period 10min 22nd Phase B Harmonics Max Value | float | 2 | R
0x75BC | 0x75BD | 30140 | 30141 | LAST_10M_HRM_MAXb23 | Last Period 10min 23rd Phase B Harmonics Max Value | float | 2 | R
0x75BE | 0x75BF | 30142 | 30143 | LAST_10M_HRM_MAXb24 | Last Period 10min 24th Phase B Harmonics Max Value | float | 2 | R
0x75C0 | 0x75C1 | 30144 | 30145 | LAST_10M_HRM_MAXb25 | Last Period 10min 25th Phase B Harmonics Max Value | float | 2 | R
0x75C2 | 0x75C3 | 30146 | 30147 | LAST_10M_HRM_MAXc2 | Last Period 10min 2nd Phase C Harmonics Max Value | float | 2 | R
0x75C4 | 0x75C5 | 30148 | 30149 | LAST_10M_HRM_MAXc3 | Last Period 10min 3rd Phase C Harmonics Max Value | float | 2 | R
0x75C6 | 0x75C7 | 30150 | 30151 | LAST_10M_HRM_MAXc4 | Last Period 10min 4th Phase C Harmonics Max Value | float | 2 | R
0x75C8 | 0x75C9 | 30152 | 30153 | LAST_10M_HRM_MAXc5 | Last Period 10min 5th Phase C Harmonics Max Value | float | 2 | R
0x75CA | 0x75CB | 30154 | 30155 | LAST_10M_HRM_MAXc6 | Last Period 10min 6th Phase C Harmonics Max Value | float | 2 | R
0x75CC | 0x75CD | 30156 | 30157 | LAST_10M_HRM_MAXc7 | Last Period 10min 7th Phase C Harmonics Max Value | float | 2 | R
0x75CE | 0x75CF | 30158 | 30159 | LAST_10M_HRM_MAXc8 | Last Period 10min 8th Phase C Harmonics Max Value | float | 2 | R
0x75D0 | 0x75D1 | 30160 | 30161 | LAST_10M_HRM_MAXc9 | Last Period 10min 9th Phase C Harmonics Max Value | float | 2 | R
0x75D2 | 0x75D3 | 30162 | 30163 | LAST_10M_HRM_MAXc10 | Last Period 10min 10th Phase C Harmonics Max Value | float | 2 | R
0x75D4 | 0x75D5 | 30164 | 30165 | LAST_10M_HRM_MAXc11 | Last Period 10min 11st Phase C Harmonics Max Value | float | 2 | R
0x75D6 | 0x75D7 | 30166 | 30167 | LAST_10M_HRM_MAXc12 | Last Period 10min 12nd Phase C Harmonics Max Value | float | 2 | R
0x75D8 | 0x75D9 | 30168 | 30169 | LAST_10M_HRM_MAXc13 | Last Period 10min 13rd Phase C Harmonics Max Value | float | 2 | R
0x75DA | 0x75DB | 30170 | 30171 | LAST_10M_HRM_MAXc14 | Last Period 10min 14th Phase C Harmonics Max Value | float | 2 | R
0x75DC | 0x75DD | 30172 | 30173 | LAST_10M_HRM_MAXc15 | Last Period 10min 15th Phase C Harmonics Max Value | float | 2 | R
0x75DE | 0x75DF | 30174 | 30175 | LAST_10M_HRM_MAXc16 | Last Period 10min 16th Phase C Harmonics Max Value | float | 2 | R
0x75E0 | 0x75E1 | 30176 | 30177 | LAST_10M_HRM_MAXc17 | Last Period 10min 17th Phase C Harmonics Max Value | float | 2 | R
0x75E2 | 0x75E3 | 30178 | 30179 | LAST_10M_HRM_MAXc18 | Last Period 10min 18th Phase C Harmonics Max Value | float | 2 | R
0x75E4 | 0x75E5 | 30180 | 30181 | LAST_10M_HRM_MAXc19 | Last Period 10min 19th Phase C Harmonics Max Value | float | 2 | R
0x75E6 | 0x75E7 | 30182 | 30183 | LAST_10M_HRM_MAXc20 | Last Period 10min 20th Phase C Harmonics Max Value | float | 2 | R
0x75E8 | 0x75E9 | 30184 | 30185 | LAST_10M_HRM_MAXc21 | Last Period 10min 21st Phase C Harmonics Max Value | float | 2 | R
0x75EA | 0x75EB | 30186 | 30187 | LAST_10M_HRM_MAXc22 | Last Period 10min 22nd Phase C Harmonics Max Value | float | 2 | R
0x75EC | 0x75ED | 30188 | 30189 | LAST_10M_HRM_MAXc23 | Last Period 10min 23rd Phase C Harmonics Max Value | float | 2 | R
0x75EE | 0x75EF | 30190 | 30191 | LAST_10M_HRM_MAXc24 | Last Period 10min 24th Phase C Harmonics Max Value | float | 2 | R
0x75F0 | 0x75F1 | 30192 | 30193 | LAST_10M_HRM_MAXc25 | Last Period 10min 25th Phase C Harmonics Max Value | float | 2 | R
0x75F2 | 0x75F3 | 30194 | 30195 | LAST_10M_HRM_MINa2 | Last Period 10min 2nd Phase A Harmonics Min Value | float | 2 | R
0x75F4 | 0x75F5 | 30196 | 30197 | LAST_10M_HRM_MINa3 | Last Period 10min 3rd Phase A Harmonics Min Value | float | 2 | R
0x75F6 | 0x75F7 | 30198 | 30199 | LAST_10M_HRM_MINa4 | Last Period 10min 4th Phase A Harmonics Min Value | float | 2 | R
0x75F8 | 0x75F9 | 30200 | 30201 | LAST_10M_HRM_MINa5 | Last Period 10min 5th Phase A Harmonics Min Value | float | 2 | R
0x75FA | 0x75FB | 30202 | 30203 | LAST_10M_HRM_MINa6 | Last Period 10min 6th Phase A Harmonics Min Value | float | 2 | R
0x75FC | 0x75FD | 30204 | 30205 | LAST_10M_HRM_MINa7 | Last Period 10min 7th Phase A Harmonics Min Value | float | 2 | R
0x75FE | 0x75FF | 30206 | 30207 | LAST_10M_HRM_MINa8 | Last Period 10min 8th Phase A Harmonics Min Value | float | 2 | R
0x7600 | 0x7601 | 30208 | 30209 | LAST_10M_HRM_MINa9 | Last Period 10min 9th Phase A Harmonics Min Value | float | 2 | R
0x7602 | 0x7603 | 30210 | 30211 | LAST_10M_HRM_MINa10 | Last Period 10min 10th Phase A Harmonics Min Value | float | 2 | R
0x7604 | 0x7605 | 30212 | 30213 | LAST_10M_HRM_MINa11 | Last Period 10min 11st Phase A Harmonics Min Value | float | 2 | R
0x7606 | 0x7607 | 30214 | 30215 | LAST_10M_HRM_MINa12 | Last Period 10min 12nd Phase A Harmonics Min Value | float | 2 | R
0x7608 | 0x7609 | 30216 | 30217 | LAST_10M_HRM_MINa13 | Last Period 10min 13rd Phase A Harmonics Min Value | float | 2 | R
0x760A | 0x760B | 30218 | 30219 | LAST_10M_HRM_MINa14 | Last Period 10min 14th Phase A Harmonics Min Value | float | 2 | R
0x760C | 0x760D | 30220 | 30221 | LAST_10M_HRM_MINa15 | Last Period 10min 15th Phase A Harmonics Min Value | float | 2 | R
0x760E | 0x760F | 30222 | 30223 | LAST_10M_HRM_MINa16 | Last Period 10min 16th Phase A Harmonics Min Value | float | 2 | R
0x7610 | 0x7611 | 30224 | 30225 | LAST_10M_HRM_MINa17 | Last Period 10min 17th Phase A Harmonics Min Value | float | 2 | R
0x7612 | 0x7613 | 30226 | 30227 | LAST_10M_HRM_MINa18 | Last Period 10min 18th Phase A Harmonics Min Value | float | 2 | R
0x7614 | 0x7615 | 30228 | 30229 | LAST_10M_HRM_MINa19 | Last Period 10min 19th Phase A Harmonics Min Value | float | 2 | R
0x7616 | 0x7617 | 30230 | 30231 | LAST_10M_HRM_MINa20 | Last Period 10min 20th Phase A Harmonics Min Value | float | 2 | R
0x7618 | 0x7619 | 30232 | 30233 | LAST_10M_HRM_MINa21 | Last Period 10min 21st Phase A Harmonics Min Value | float | 2 | R
0x761A | 0x761B | 30234 | 30235 | LAST_10M_HRM_MINa22 | Last Period 10min 22nd Phase A Harmonics Min Value | float | 2 | R
0x761C | 0x761D | 30236 | 30237 | LAST_10M_HRM_MINa23 | Last Period 10min 23rd Phase A Harmonics Min Value | float | 2 | R
0x761E | 0x761F | 30238 | 30239 | LAST_10M_HRM_MINa24 | Last Period 10min 24th Phase A Harmonics Min Value | float | 2 | R
0x7620 | 0x7621 | 30240 | 30241 | LAST_10M_HRM_MINa25 | Last Period 10min 25th Phase A Harmonics Min Value | float | 2 | R
0x7622 | 0x7623 | 30242 | 30243 | LAST_10M_HRM_MINb2 | Last Period 10min 2nd Phase B Harmonics Min Value | float | 2 | R
0x7624 | 0x7625 | 30244 | 30245 | LAST_10M_HRM_MINb3 | Last Period 10min 3rd Phase B Harmonics Min Value | float | 2 | R
0x7626 | 0x7627 | 30246 | 30247 | LAST_10M_HRM_MINb4 | Last Period 10min 4th Phase B Harmonics Min Value | float | 2 | R
0x7628 | 0x7629 | 30248 | 30249 | LAST_10M_HRM_MINb5 | Last Period 10min 5th Phase B Harmonics Min Value | float | 2 | R
0x762A | 0x762B | 30250 | 30251 | LAST_10M_HRM_MINb6 | Last Period 10min 6th Phase B Harmonics Min Value | float | 2 | R
0x762C | 0x762D | 30252 | 30253 | LAST_10M_HRM_MINb7 | Last Period 10min 7th Phase B Harmonics Min Value | float | 2 | R
0x762E | 0x762F | 30254 | 30255 | LAST_10M_HRM_MINb8 | Last Period 10min 8th Phase B Harmonics Min Value | float | 2 | R
0x7630 | 0x7631 | 30256 | 30257 | LAST_10M_HRM_MINb9 | Last Period 10min 9th Phase B Harmonics Min Value | float | 2 | R
0x7632 | 0x7633 | 30258 | 30259 | LAST_10M_HRM_MINb10 | Last Period 10min 10th Phase B Harmonics Min Value | float | 2 | R
0x7634 | 0x7635 | 30260 | 30261 | LAST_10M_HRM_MINb11 | Last Period 10min 11st Phase B Harmonics Min Value | float | 2 | R
0x7636 | 0x7637 | 30262 | 30263 | LAST_10M_HRM_MINb12 | Last Period 10min 12nd Phase B Harmonics Min Value | float | 2 | R
0x7638 | 0x7639 | 30264 | 30265 | LAST_10M_HRM_MINb13 | Last Period 10min 13rd Phase B Harmonics Min Value | float | 2 | R
0x763A | 0x763B | 30266 | 30267 | LAST_10M_HRM_MINb14 | Last Period 10min 14th Phase B Harmonics Min Value | float | 2 | R
0x763C | 0x763D | 30268 | 30269 | LAST_10M_HRM_MINb15 | Last Period 10min 15th Phase B Harmonics Min Value | float | 2 | R
0x763E | 0x763F | 30270 | 30271 | LAST_10M_HRM_MINb16 | Last Period 10min 16th Phase B Harmonics Min Value | float | 2 | R
0x7640 | 0x7641 | 30272 | 30273 | LAST_10M_HRM_MINb17 | Last Period 10min 17th Phase B Harmonics Min Value | float | 2 | R
0x7642 | 0x7643 | 30274 | 30275 | LAST_10M_HRM_MINb18 | Last Period 10min 18th Phase B Harmonics Min Value | float | 2 | R
0x7644 | 0x7645 | 30276 | 30277 | LAST_10M_HRM_MINb19 | Last Period 10min 19th Phase B Harmonics Min Value | float | 2 | R
0x7646 | 0x7647 | 30278 | 30279 | LAST_10M_HRM_MINb20 | Last Period 10min 20th Phase B Harmonics Min Value | float | 2 | R
0x7648 | 0x7649 | 30280 | 30281 | LAST_10M_HRM_MINb21 | Last Period 10min 21st Phase B Harmonics Min Value | float | 2 | R
0x764A | 0x764B | 30282 | 30283 | LAST_10M_HRM_MINb22 | Last Period 10min 22nd Phase B Harmonics Min Value | float | 2 | R
0x764C | 0x764D | 30284 | 30285 | LAST_10M_HRM_MINb23 | Last Period 10min 23rd Phase B Harmonics Min Value | float | 2 | R
0x764E | 0x764F | 30286 | 30287 | LAST_10M_HRM_MINb24 | Last Period 10min 24th Phase B Harmonics Min Value | float | 2 | R
0x7650 | 0x7651 | 30288 | 30289 | LAST_10M_HRM_MINb25 | Last Period 10min 25th Phase B Harmonics Min Value | float | 2 | R
0x7652 | 0x7653 | 30290 | 30291 | LAST_10M_HRM_MINc2 | Last Period 10min 2nd Phase C Harmonics Min Value | float | 2 | R
0x7654 | 0x7655 | 30292 | 30293 | LAST_10M_HRM_MINc3 | Last Period 10min 3rd Phase C Harmonics Min Value | float | 2 | R
0x7656 | 0x7657 | 30294 | 30295 | LAST_10M_HRM_MINc4 | Last Period 10min 4th Phase C Harmonics Min Value | float | 2 | R
0x7658 | 0x7659 | 30296 | 30297 | LAST_10M_HRM_MINc5 | Last Period 10min 5th Phase C Harmonics Min Value | float | 2 | R
0x765A | 0x765B | 30298 | 30299 | LAST_10M_HRM_MINc6 | Last Period 10min 6th Phase C Harmonics Min Value | float | 2 | R
0x765C | 0x765D | 30300 | 30301 | LAST_10M_HRM_MINc7 | Last Period 10min 7th Phase C Harmonics Min Value | float | 2 | R
0x765E | 0x765F | 30302 | 30303 | LAST_10M_HRM_MINc8 | Last Period 10min 8th Phase C Harmonics Min Value | float | 2 | R
0x7660 | 0x7661 | 30304 | 30305 | LAST_10M_HRM_MINc9 | Last Period 10min 9th Phase C Harmonics Min Value | float | 2 | R
0x7662 | 0x7663 | 30306 | 30307 | LAST_10M_HRM_MINc10 | Last Period 10min 10th Phase C Harmonics Min Value | float | 2 | R
0x7664 | 0x7665 | 30308 | 30309 | LAST_10M_HRM_MINc11 | Last Period 10min 11st Phase C Harmonics Min Value | float | 2 | R
0x7666 | 0x7667 | 30310 | 30311 | LAST_10M_HRM_MINc12 | Last Period 10min 12nd Phase C Harmonics Min Value | float | 2 | R
0x7668 | 0x7669 | 30312 | 30313 | LAST_10M_HRM_MINc13 | Last Period 10min 13rd Phase C Harmonics Min Value | float | 2 | R
0x766A | 0x766B | 30314 | 30315 | LAST_10M_HRM_MINc14 | Last Period 10min 14th Phase C Harmonics Min Value | float | 2 | R
0x766C | 0x766D | 30316 | 30317 | LAST_10M_HRM_MINc15 | Last Period 10min 15th Phase C Harmonics Min Value | float | 2 | R
0x766E | 0x766F | 30318 | 30319 | LAST_10M_HRM_MINc16 | Last Period 10min 16th Phase C Harmonics Min Value | float | 2 | R
0x7670 | 0x7671 | 30320 | 30321 | LAST_10M_HRM_MINc17 | Last Period 10min 17th Phase C Harmonics Min Value | float | 2 | R
0x7672 | 0x7673 | 30322 | 30323 | LAST_10M_HRM_MINc18 | Last Period 10min 18th Phase C Harmonics Min Value | float | 2 | R
0x7674 | 0x7675 | 30324 | 30325 | LAST_10M_HRM_MINc19 | Last Period 10min 19th Phase C Harmonics Min Value | float | 2 | R
0x7676 | 0x7677 | 30326 | 30327 | LAST_10M_HRM_MINc20 | Last Period 10min 20th Phase C Harmonics Min Value | float | 2 | R
0x7678 | 0x7679 | 30328 | 30329 | LAST_10M_HRM_MINc21 | Last Period 10min 21st Phase C Harmonics Min Value | float | 2 | R
0x767A | 0x767B | 30330 | 30331 | LAST_10M_HRM_MINc22 | Last Period 10min 22nd Phase C Harmonics Min Value | float | 2 | R
0x767C | 0x767D | 30332 | 30333 | LAST_10M_HRM_MINc23 | Last Period 10min 23rd Phase C Harmonics Min Value | float | 2 | R
0x767E | 0x767F | 30334 | 30335 | LAST_10M_HRM_MINc24 | Last Period 10min 24th Phase C Harmonics Min Value | float | 2 | R
0x7680 | 0x7681 | 30336 | 30337 | LAST_10M_HRM_MINc25 | Last Period 10min 25th Phase C Harmonics Min Value | float | 2 | R
0x7682 | 0x7683 | 30338 | 30339 | LAST_10M_HRM_AVGa2 | Last Period 10min 2nd Phase A Harmonics Avg Value | float | 2 | R
0x7684 | 0x7685 | 30340 | 30341 | LAST_10M_HRM_AVGa3 | Last Period 10min 3rd Phase A Harmonics Avg Value | float | 2 | R
0x7686 | 0x7687 | 30342 | 30343 | LAST_10M_HRM_AVGa4 | Last Period 10min 4th Phase A Harmonics Avg Value | float | 2 | R
0x7688 | 0x7689 | 30344 | 30345 | LAST_10M_HRM_AVGa5 | Last Period 10min 5th Phase A Harmonics Avg Value | float | 2 | R
0x768A | 0x768B | 30346 | 30347 | LAST_10M_HRM_AVGa6 | Last Period 10min 6th Phase A Harmonics Avg Value | float | 2 | R
0x768C | 0x768D | 30348 | 30349 | LAST_10M_HRM_AVGa7 | Last Period 10min 7th Phase A Harmonics Avg Value | float | 2 | R
0x768E | 0x768F | 30350 | 30351 | LAST_10M_HRM_AVGa8 | Last Period 10min 8th Phase A Harmonics Avg Value | float | 2 | R
0x7690 | 0x7691 | 30352 | 30353 | LAST_10M_HRM_AVGa9 | Last Period 10min 9th Phase A Harmonics Avg Value | float | 2 | R
0x7692 | 0x7693 | 30354 | 30355 | LAST_10M_HRM_AVGa10 | Last Period 10min 10th Phase A Harmonics Avg Value | float | 2 | R
0x7694 | 0x7695 | 30356 | 30357 | LAST_10M_HRM_AVGa11 | Last Period 10min 11st Phase A Harmonics Avg Value | float | 2 | R
0x7696 | 0x7697 | 30358 | 30359 | LAST_10M_HRM_AVGa12 | Last Period 10min 12nd Phase A Harmonics Avg Value | float | 2 | R
0x7698 | 0x7699 | 30360 | 30361 | LAST_10M_HRM_AVGa13 | Last Period 10min 13rd Phase A Harmonics Avg Value | float | 2 | R
0x769A | 0x769B | 30362 | 30363 | LAST_10M_HRM_AVGa14 | Last Period 10min 14th Phase A Harmonics Avg Value | float | 2 | R
0x769C | 0x769D | 30364 | 30365 | LAST_10M_HRM_AVGa15 | Last Period 10min 15th Phase A Harmonics Avg Value | float | 2 | R
0x769E | 0x769F | 30366 | 30367 | LAST_10M_HRM_AVGa16 | Last Period 10min 16th Phase A Harmonics Avg Value | float | 2 | R
0x76A0 | 0x76A1 | 30368 | 30369 | LAST_10M_HRM_AVGa17 | Last Period 10min 17th Phase A Harmonics Avg Value | float | 2 | R
0x76A2 | 0x76A3 | 30370 | 30371 | LAST_10M_HRM_AVGa18 | Last Period 10min 18th Phase A Harmonics Avg Value | float | 2 | R
0x76A4 | 0x76A5 | 30372 | 30373 | LAST_10M_HRM_AVGa19 | Last Period 10min 19th Phase A Harmonics Avg Value | float | 2 | R
0x76A6 | 0x76A7 | 30374 | 30375 | LAST_10M_HRM_AVGa20 | Last Period 10min 20th Phase A Harmonics Avg Value | float | 2 | R
0x76A8 | 0x76A9 | 30376 | 30377 | LAST_10M_HRM_AVGa21 | Last Period 10min 21st Phase A Harmonics Avg Value | float | 2 | R
0x76AA | 0x76AB | 30378 | 30379 | LAST_10M_HRM_AVGa22 | Last Period 10min 22nd Phase A Harmonics Avg Value | float | 2 | R
0x76AC | 0x76AD | 30380 | 30381 | LAST_10M_HRM_AVGa23 | Last Period 10min 23rd Phase A Harmonics Avg Value | float | 2 | R
0x76AE | 0x76AF | 30382 | 30383 | LAST_10M_HRM_AVGa24 | Last Period 10min 24th Phase A Harmonics Avg Value | float | 2 | R
0x76B0 | 0x76B1 | 30384 | 30385 | LAST_10M_HRM_AVGa25 | Last Period 10min 25th Phase A Harmonics Avg Value | float | 2 | R
0x76B2 | 0x76B3 | 30386 | 30387 | LAST_10M_HRM_AVGb2 | Last Period 10min 2nd Phase B Harmonics Avg Value | float | 2 | R
0x76B4 | 0x76B5 | 30388 | 30389 | LAST_10M_HRM_AVGb3 | Last Period 10min 3rd Phase B Harmonics Avg Value | float | 2 | R
0x76B6 | 0x76B7 | 30390 | 30391 | LAST_10M_HRM_AVGb4 | Last Period 10min 4th Phase B Harmonics Avg Value | float | 2 | R
0x76B8 | 0x76B9 | 30392 | 30393 | LAST_10M_HRM_AVGb5 | Last Period 10min 5th Phase B Harmonics Avg Value | float | 2 | R
0x76BA | 0x76BB | 30394 | 30395 | LAST_10M_HRM_AVGb6 | Last Period 10min 6th Phase B Harmonics Avg Value | float | 2 | R
0x76BC | 0x76BD | 30396 | 30397 | LAST_10M_HRM_AVGb7 | Last Period 10min 7th Phase B Harmonics Avg Value | float | 2 | R
0x76BE | 0x76BF | 30398 | 30399 | LAST_10M_HRM_AVGb8 | Last Period 10min 8th Phase B Harmonics Avg Value | float | 2 | R
0x76C0 | 0x76C1 | 30400 | 30401 | LAST_10M_HRM_AVGb9 | Last Period 10min 9th Phase B Harmonics Avg Value | float | 2 | R
0x76C2 | 0x76C3 | 30402 | 30403 | LAST_10M_HRM_AVGb10 | Last Period 10min 10th Phase B Harmonics Avg Value | float | 2 | R
0x76C4 | 0x76C5 | 30404 | 30405 | LAST_10M_HRM_AVGb11 | Last Period 10min 11st Phase B Harmonics Avg Value | float | 2 | R
0x76C6 | 0x76C7 | 30406 | 30407 | LAST_10M_HRM_AVGb12 | Last Period 10min 12nd Phase B Harmonics Avg Value | float | 2 | R
0x76C8 | 0x76C9 | 30408 | 30409 | LAST_10M_HRM_AVGb13 | Last Period 10min 13rd Phase B Harmonics Avg Value | float | 2 | R
0x76CA | 0x76CB | 30410 | 30411 | LAST_10M_HRM_AVGb14 | Last Period 10min 14th Phase B Harmonics Avg Value | float | 2 | R
0x76CC | 0x76CD | 30412 | 30413 | LAST_10M_HRM_AVGb15 | Last Period 10min 15th Phase B Harmonics Avg Value | float | 2 | R
0x76CE | 0x76CF | 30414 | 30415 | LAST_10M_HRM_AVGb16 | Last Period 10min 16th Phase B Harmonics Avg Value | float | 2 | R
0x76D0 | 0x76D1 | 30416 | 30417 | LAST_10M_HRM_AVGb17 | Last Period 10min 17th Phase B Harmonics Avg Value | float | 2 | R
0x76D2 | 0x76D3 | 30418 | 30419 | LAST_10M_HRM_AVGb18 | Last Period 10min 18th Phase B Harmonics Avg Value | float | 2 | R
0x76D4 | 0x76D5 | 30420 | 30421 | LAST_10M_HRM_AVGb19 | Last Period 10min 19th Phase B Harmonics Avg Value | float | 2 | R
0x76D6 | 0x76D7 | 30422 | 30423 | LAST_10M_HRM_AVGb20 | Last Period 10min 20th Phase B Harmonics Avg Value | float | 2 | R
0x76D8 | 0x76D9 | 30424 | 30425 | LAST_10M_HRM_AVGb21 | Last Period 10min 21st Phase B Harmonics Avg Value | float | 2 | R
0x76DA | 0x76DB | 30426 | 30427 | LAST_10M_HRM_AVGb22 | Last Period 10min 22nd Phase B Harmonics Avg Value | float | 2 | R
0x76DC | 0x76DD | 30428 | 30429 | LAST_10M_HRM_AVGb23 | Last Period 10min 23rd Phase B Harmonics Avg Value | float | 2 | R
0x76DE | 0x76DF | 30430 | 30431 | LAST_10M_HRM_AVGb24 | Last Period 10min 24th Phase B Harmonics Avg Value | float | 2 | R
0x76E0 | 0x76E1 | 30432 | 30433 | LAST_10M_HRM_AVGb25 | Last Period 10min 25th Phase B Harmonics Avg Value | float | 2 | R
0x76E2 | 0x76E3 | 30434 | 30435 | LAST_10M_HRM_AVGc2 | Last Period 10min 2nd Phase C Harmonics Avg Value | float | 2 | R
0x76E4 | 0x76E5 | 30436 | 30437 | LAST_10M_HRM_AVGc3 | Last Period 10min 3rd Phase C Harmonics Avg Value | float | 2 | R
0x76E6 | 0x76E7 | 30438 | 30439 | LAST_10M_HRM_AVGc4 | Last Period 10min 4th Phase C Harmonics Avg Value | float | 2 | R
0x76E8 | 0x76E9 | 30440 | 30441 | LAST_10M_HRM_AVGc5 | Last Period 10min 5th Phase C Harmonics Avg Value | float | 2 | R
0x76EA | 0x76EB | 30442 | 30443 | LAST_10M_HRM_AVGc6 | Last Period 10min 6th Phase C Harmonics Avg Value | float | 2 | R
0x76EC | 0x76ED | 30444 | 30445 | LAST_10M_HRM_AVGc7 | Last Period 10min 7th Phase C Harmonics Avg Value | float | 2 | R
0x76EE | 0x76EF | 30446 | 30447 | LAST_10M_HRM_AVGc8 | Last Period 10min 8th Phase C Harmonics Avg Value | float | 2 | R
0x76F0 | 0x76F1 | 30448 | 30449 | LAST_10M_HRM_AVGc9 | Last Period 10min 9th Phase C Harmonics Avg Value | float | 2 | R
0x76F2 | 0x76F3 | 30450 | 30451 | LAST_10M_HRM_AVGc10 | Last Period 10min 10th Phase C Harmonics Avg Value | float | 2 | R
0x76F4 | 0x76F5 | 30452 | 30453 | LAST_10M_HRM_AVGc11 | Last Period 10min 11st Phase C Harmonics Avg Value | float | 2 | R
0x76F6 | 0x76F7 | 30454 | 30455 | LAST_10M_HRM_AVGc12 | Last Period 10min 12nd Phase C Harmonics Avg Value | float | 2 | R
0x76F8 | 0x76F9 | 30456 | 30457 | LAST_10M_HRM_AVGc13 | Last Period 10min 13rd Phase C Harmonics Avg Value | float | 2 | R
0x76FA | 0x76FB | 30458 | 30459 | LAST_10M_HRM_AVGc14 | Last Period 10min 14th Phase C Harmonics Avg Value | float | 2 | R
0x76FC | 0x76FD | 30460 | 30461 | LAST_10M_HRM_AVGc15 | Last Period 10min 15th Phase C Harmonics Avg Value | float | 2 | R
0x76FE | 0x76FF | 30462 | 30463 | LAST_10M_HRM_AVGc16 | Last Period 10min 16th Phase C Harmonics Avg Value | float | 2 | R
0x7700 | 0x7701 | 30464 | 30465 | LAST_10M_HRM_AVGc17 | Last Period 10min 17th Phase C Harmonics Avg Value | float | 2 | R
0x7702 | 0x7703 | 30466 | 30467 | LAST_10M_HRM_AVGc18 | Last Period 10min 18th Phase C Harmonics Avg Value | float | 2 | R
0x7704 | 0x7705 | 30468 | 30469 | LAST_10M_HRM_AVGc19 | Last Period 10min 19th Phase C Harmonics Avg Value | float | 2 | R
0x7706 | 0x7707 | 30470 | 30471 | LAST_10M_HRM_AVGc20 | Last Period 10min 20th Phase C Harmonics Avg Value | float | 2 | R
0x7708 | 0x7709 | 30472 | 30473 | LAST_10M_HRM_AVGc21 | Last Period 10min 21st Phase C Harmonics Avg Value | float | 2 | R
0x770A | 0x770B | 30474 | 30475 | LAST_10M_HRM_AVGc22 | Last Period 10min 22nd Phase C Harmonics Avg Value | float | 2 | R
0x770C | 0x770D | 30476 | 30477 | LAST_10M_HRM_AVGc23 | Last Period 10min 23rd Phase C Harmonics Avg Value | float | 2 | R
0x770E | 0x770F | 30478 | 30479 | LAST_10M_HRM_AVGc24 | Last Period 10min 24th Phase C Harmonics Avg Value | float | 2 | R
0x7710 | 0x7711 | 30480 | 30481 | LAST_10M_HRM_AVGc25 | Last Period 10min 25th Phase C Harmonics Avg Value | float | 2 | R
0x7712 | 0x7712 | 30482 | 30482 | LAST_10M_N_THDa | Last Period 10min Phase A THD Bin Counter | uint16 | 1 | R
0x7713 | 0x7713 | 30483 | 30483 | LAST_10M_N_THDb | Last Period 10min Phase B THD Bin Counter | uint16 | 1 | R
0x7714 | 0x7714 | 30484 | 30484 | LAST_10M_N_THDc | Last Period 10min Phase C THD Bin Counter | uint16 | 1 | R
0x7715 | 0x7716 | 30485 | 30486 | LAST_10M_THD_PASSa | Last Period 10min Phase A THD Bin Zone Trigger Pass Rate | float | 2 | R
0x7717 | 0x7718 | 30487 | 30488 | LAST_10M_THD_PASSb | Last Period 10min Phase B THD Bin Zone Trigger Pass Rate | float | 2 | R
0x7719 | 0x771A | 30489 | 30490 | LAST_10M_THD_PASSc | Last Period 10min Phase C THD Bin Zone Trigger Pass Rate | float | 2 | R
0x771B | 0x771C | 30491 | 30492 | LAST_10M_THD_MAXa | Last Period 10min Phase A THD Maximum Value | float | 2 | R
0x771D | 0x771E | 30493 | 30494 | LAST_10M_THD_MAXb | Last Period 10min Phase B THD Maximum Value | float | 2 | R
0x771F | 0x7720 | 30495 | 30496 | LAST_10M_THD_MAXc | Last Period 10min Phase C THD Maximum Value | float | 2 | R
0x7721 | 0x7722 | 30497 | 30498 | LAST_10M_THD_MINa | Last Period 10min Phase A THD Minimum Value | float | 2 | R
0x7723 | 0x7724 | 30499 | 30500 | LAST_10M_THD_MINb | Last Period 10min Phase B THD Minimum Value | float | 2 | R
0x7725 | 0x7726 | 30501 | 30502 | LAST_10M_THD_MINc | Last Period 10min Phase C THD Minimum Value | float | 2 | R
0x7727 | 0x7728 | 30503 | 30504 | LAST_10M_THD_AVGa | Last Period 10min Phase A THD Average Value | float | 2 | R
0x7729 | 0x772A | 30505 | 30506 | LAST_10M_THD_AVGb | Last Period 10min Phase B THD Average Value | float | 2 | R
0x772B | 0x772C | 30507 | 30508 | LAST_10M_THD_AVGc | Last Period 10min Phase C THD Average Value | float | 2 | R
0x772D | 0x772E | 30509 | 30510 | LAST_10M_TOHD_MAXa | Last Period 10min Phase A TOHD Maximum Value | float | 2 | R
0x772F | 0x7730 | 30511 | 30512 | LAST_10M_TOHD_MAXb | Last Period 10min Phase B TOHD Maximum Value | float | 2 | R
0x7731 | 0x7732 | 30513 | 30514 | LAST_10M_TOHD_MAXc | Last Period 10min Phase C TOHD Maximum Value | float | 2 | R
0x7733 | 0x7734 | 30515 | 30516 | LAST_10M_TOHD_MINa | Last Period 10min Phase A TOHD Minimum Value | float | 2 | R
0x7735 | 0x7736 | 30517 | 30518 | LAST_10M_TOHD_MINb | Last Period 10min Phase B TOHD Minimum Value | float | 2 | R
0x7737 | 0x7738 | 30519 | 30520 | LAST_10M_TOHD_MINc | Last Period 10min Phase C TOHD Minimum Value | float | 2 | R
0x7739 | 0x773A | 30521 | 30522 | LAST_10M_TOHD_AVGa | Last Period 10min Phase A TOHD Average Value | float | 2 | R
0x773B | 0x773C | 30523 | 30524 | LAST_10M_TOHD_AVGb | Last Period 10min Phase B TOHD Average Value | float | 2 | R
0x773D | 0x773E | 30525 | 30526 | LAST_10M_TOHD_AVGc | Last Period 10min Phase C TOHD Average Value | float | 2 | R
0x773F | 0x7740 | 30527 | 30528 | LAST_10M_TEHD_MAXa | Last Period 10min Phase A TEHD Maximum Value | float | 2 | R
0x7741 | 0x7742 | 30529 | 30530 | LAST_10M_TEHD_MAXb | Last Period 10min Phase B TEHD Maximum Value | float | 2 | R
0x7743 | 0x7744 | 30531 | 30532 | LAST_10M_TEHD_MAXc | Last Period 10min Phase C TEHD Maximum Value | float | 2 | R
0x7745 | 0x7746 | 30533 | 30534 | LAST_10M_TEHD_MINa | Last Period 10min Phase A TEHD Minimum Value | float | 2 | R
0x7747 | 0x7748 | 30535 | 30536 | LAST_10M_TEHD_MINb | Last Period 10min Phase B TEHD Minimum Value | float | 2 | R
0x7749 | 0x774A | 30537 | 30538 | LAST_10M_TEHD_MINc | Last Period 10min Phase C TEHD Minimum Value | float | 2 | R
0x774B | 0x774C | 30539 | 30540 | LAST_10M_TEHD_AVGa | Last Period 10min Phase A TEHD Average Value | float | 2 | R
0x774D | 0x774E | 30541 | 30542 | LAST_10M_TEHD_AVGb | Last Period 10min Phase B TEHD Average Value | float | 2 | R
0x774F | 0x7750 | 30543 | 30544 | LAST_10M_TEHD_AVGc | Last Period 10min Phase C TEHD Average Value | float | 2 | R
0x7751 | 0x7751 | 30545 | 30545 | LAST_2HR_N_VALID | Last Period 2hr Voltage Valid Counter | uint16 | 1 | R
0x7752 | 0x7752 | 30546 | 30546 | LAST_2HR_N_INVALID | Last Period 2hr Voltage Invalid Counter | uint16 | 1 | R
0x7753 | 0x7753 | 30547 | 30547 | LAST_2HR_N_PLTa1 | Last Period 2hr 1st Phase A Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7754 | 0x7754 | 30548 | 30548 | LAST_2HR_N_PLTa2 | Last Period 2hr 2nd Phase A Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7755 | 0x7755 | 30549 | 30549 | LAST_2HR_N_PLTb1 | Last Period 2hr 1st Phase B Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7756 | 0x7756 | 30550 | 30550 | LAST_2HR_N_PLTb2 | Last Period 2hr 2nd Phase B Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7757 | 0x7757 | 30551 | 30551 | LAST_2HR_N_PLTc1 | Last Period 2hr 1st Phase C Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7758 | 0x7758 | 30552 | 30552 | LAST_2HR_N_PLTc2 | Last Period 2hr 2nd Phase C Flicker Severity Long-term Bin Counter | uint16 | 1 | R
0x7759 | 0x775A | 30553 | 30554 | LAST_2HR_PLT_PASSa | Last Period 2hr Phase A Flicker Severity Long-term Trigger Pass Rate | float | 2 | R
0x775B | 0x775C | 30555 | 30556 | LAST_2HR_PLT_PASSb | Last Period 2hr Phase B Flicker Severity Long-term Trigger Pass Rate | float | 2 | R
0x775D | 0x775E | 30557 | 30558 | LAST_2HR_PLT_PASSc | Last Period 2hr Phase C Flicker Severity Long-term Trigger Pass Rate | float | 2 | R
0x775F | 0x7760 | 30559 | 30560 | LAST_2HR_PLT_MAXa | Last Period 2hr Phase A Flicker Severity Long-term Maximum Value | float | 2 | R
0x7761 | 0x7762 | 30561 | 30562 | LAST_2HR_PLT_MAXb | Last Period 2hr Phase B Flicker Severity Long-term Maximum Value | float | 2 | R
0x7763 | 0x7764 | 30563 | 30564 | LAST_2HR_PLT_MAXc | Last Period 2hr Phase C Flicker Severity Long-term Maximum Value | float | 2 | R
0x7765 | 0x7766 | 30565 | 30566 | LAST_2HR_PLT_MINa | Last Period 2hr Phase A Flicker Severity Long-term Minimum Value | float | 2 | R
0x7767 | 0x7768 | 30567 | 30568 | LAST_2HR_PLT_MINb | Last Period 2hr Phase B Flicker Severity Long-term Minimum Value | float | 2 | R
0x7769 | 0x776A | 30569 | 30570 | LAST_2HR_PLT_MINc | Last Period 2hr Phase C Flicker Severity Long-term Minimum Value | float | 2 | R
0x776B | 0x776C | 30571 | 30572 | LAST_2HR_PLT_AVGa | Last Period 2hr Phase A Flicker Severity Long-term Average Value | float | 2 | R
0x776D | 0x776E | 30573 | 30574 | LAST_2HR_PLT_AVGb | Last Period 2hr Phase B Flicker Severity Long-term Average Value | float | 2 | R
0x776F | 0x7770 | 30575 | 30576 | LAST_2HR_PLT_AVGc | Last Period 2hr Phase C Flicker Severity Long-term Average Value | float | 2 | R

## PQ Report 519 Daily
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
PQ Report 519 Daily Current
0x7800 | 0x7800 | 30720 | 30720 | N_VALID | 3sec 519 Report Valid Circle Counter | uint16 | 1 | R
0x7801 | 0x7801 | 30721 | 30721 | N_THDa | 3sec Phase A THD Counter | uint16 | 1 | R
0x7802 | 0x7802 | 30722 | 30722 | N_THDb | 3sec Phase B THD Counter | uint16 | 1 | R
0x7803 | 0x7803 | 30723 | 30723 | N_THDc | 3sec Phase C THD Counter | uint16 | 1 | R
0x7804 | 0x7805 | 30724 | 30725 | THD_PASSa | 3sec Phase A THD Trigger Pass Rate | float | 2 | R
0x7806 | 0x7807 | 30726 | 30727 | THD_PASSb | 3sec Phase B THD Trigger Pass Rate | float | 2 | R
0x7808 | 0x7809 | 30728 | 30729 | THD_PASSc | 3sec Phase C THD Trigger Pass Rate | float | 2 | R
0x780A | 0x780B | 30730 | 30731 | THD_MAXa | 3sec Phase A THD Maximum Value | float | 2 | R
0x780C | 0x780D | 30732 | 30733 | THD_MAXb | 3sec Phase B THD Maximum Value | float | 2 | R
0x780E | 0x780F | 30734 | 30735 | THD_MAXc | 3sec Phase C THD Maximum Value | float | 2 | R
0x7810 | 0x7811 | 30736 | 30737 | THD_MINa | 3sec Phase A THD Minimum Value | float | 2 | R
0x7812 | 0x7813 | 30738 | 30739 | THD_MINb | 3sec Phase B THD Minimum Value | float | 2 | R
0x7814 | 0x7815 | 30740 | 30741 | THD_MINc | 3sec Phase C THD Minimum Value | float | 2 | R
0x7816 | 0x7817 | 30742 | 30743 | THD_AVGa | 3sec Phase A THD Average Value | float | 2 | R
0x7818 | 0x7819 | 30744 | 30745 | THD_AVGb | 3sec Phase B THD Average Value | float | 2 | R
0x781A | 0x781B | 30746 | 30747 | THD_AVGc | 3sec Phase C THD Average Value | float | 2 | R
0x781C | 0x781C | 30748 | 30748 | N_VOL_HARMa2 | 3sec 2nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x781D | 0x781D | 30749 | 30749 | N_VOL_HARMa3 | 3sec 3rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x781E | 0x781E | 30750 | 30750 | N_VOL_HARMa4 | 3sec 4th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x781F | 0x781F | 30751 | 30751 | N_VOL_HARMa5 | 3sec 5th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7820 | 0x7820 | 30752 | 30752 | N_VOL_HARMa6 | 3sec 6th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7821 | 0x7821 | 30753 | 30753 | N_VOL_HARMa7 | 3sec 7th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7822 | 0x7822 | 30754 | 30754 | N_VOL_HARMa8 | 3sec 8th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7823 | 0x7823 | 30755 | 30755 | N_VOL_HARMa9 | 3sec 9th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7824 | 0x7824 | 30756 | 30756 | N_VOL_HARMa10 | 3sec 10th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7825 | 0x7825 | 30757 | 30757 | N_VOL_HARMa11 | 3sec 11st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7826 | 0x7826 | 30758 | 30758 | N_VOL_HARMa12 | 3sec 12nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7827 | 0x7827 | 30759 | 30759 | N_VOL_HARMa13 | 3sec 13rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7828 | 0x7828 | 30760 | 30760 | N_VOL_HARMa14 | 3sec 14th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7829 | 0x7829 | 30761 | 30761 | N_VOL_HARMa15 | 3sec 15th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x782A | 0x782A | 30762 | 30762 | N_VOL_HARMa16 | 3sec 16th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x782B | 0x782B | 30763 | 30763 | N_VOL_HARMa17 | 3sec 17th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x782C | 0x782C | 30764 | 30764 | N_VOL_HARMa18 | 3sec 18th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x782D | 0x782D | 30765 | 30765 | N_VOL_HARMa19 | 3sec 19th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x782E | 0x782E | 30766 | 30766 | N_VOL_HARMa20 | 3sec 20th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x782F | 0x782F | 30767 | 30767 | N_VOL_HARMa21 | 3sec 21st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7830 | 0x7830 | 30768 | 30768 | N_VOL_HARMa22 | 3sec 22nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7831 | 0x7831 | 30769 | 30769 | N_VOL_HARMa23 | 3sec 23rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7832 | 0x7832 | 30770 | 30770 | N_VOL_HARMa24 | 3sec 24th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7833 | 0x7833 | 30771 | 30771 | N_VOL_HARMa25 | 3sec 25th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7834 | 0x7834 | 30772 | 30772 | N_VOL_HARMa26 | 3sec 26th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7835 | 0x7835 | 30773 | 30773 | N_VOL_HARMa27 | 3sec 27th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7836 | 0x7836 | 30774 | 30774 | N_VOL_HARMa28 | 3sec 28th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7837 | 0x7837 | 30775 | 30775 | N_VOL_HARMa29 | 3sec 29th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7838 | 0x7838 | 30776 | 30776 | N_VOL_HARMa30 | 3sec 30th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7839 | 0x7839 | 30777 | 30777 | N_VOL_HARMa31 | 3sec 31st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x783A | 0x783A | 30778 | 30778 | N_VOL_HARMa32 | 3sec 32nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x783B | 0x783B | 30779 | 30779 | N_VOL_HARMa33 | 3sec 33rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x783C | 0x783C | 30780 | 30780 | N_VOL_HARMa34 | 3sec 34th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x783D | 0x783D | 30781 | 30781 | N_VOL_HARMa35 | 3sec 35th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x783E | 0x783E | 30782 | 30782 | N_VOL_HARMa36 | 3sec 36th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x783F | 0x783F | 30783 | 30783 | N_VOL_HARMa37 | 3sec 37th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7840 | 0x7840 | 30784 | 30784 | N_VOL_HARMa38 | 3sec 38th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7841 | 0x7841 | 30785 | 30785 | N_VOL_HARMa39 | 3sec 39th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7842 | 0x7842 | 30786 | 30786 | N_VOL_HARMa40 | 3sec 40th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7843 | 0x7843 | 30787 | 30787 | N_VOL_HARMa41 | 3sec 41st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7844 | 0x7844 | 30788 | 30788 | N_VOL_HARMa42 | 3sec 42nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7845 | 0x7845 | 30789 | 30789 | N_VOL_HARMa43 | 3sec 43rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7846 | 0x7846 | 30790 | 30790 | N_VOL_HARMa44 | 3sec 44th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7847 | 0x7847 | 30791 | 30791 | N_VOL_HARMa45 | 3sec 45th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7848 | 0x7848 | 30792 | 30792 | N_VOL_HARMa46 | 3sec 46th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x7849 | 0x7849 | 30793 | 30793 | N_VOL_HARMa47 | 3sec 47th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x784A | 0x784A | 30794 | 30794 | N_VOL_HARMa48 | 3sec 48th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x784B | 0x784B | 30795 | 30795 | N_VOL_HARMa49 | 3sec 49th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x784C | 0x784C | 30796 | 30796 | N_VOL_HARMa50 | 3sec 50th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x784D | 0x784D | 30797 | 30797 | N_VOL_HARMb2 | 3sec 2nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x784E | 0x784E | 30798 | 30798 | N_VOL_HARMb3 | 3sec 3rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x784F | 0x784F | 30799 | 30799 | N_VOL_HARMb4 | 3sec 4th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7850 | 0x7850 | 30800 | 30800 | N_VOL_HARMb5 | 3sec 5th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7851 | 0x7851 | 30801 | 30801 | N_VOL_HARMb6 | 3sec 6th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7852 | 0x7852 | 30802 | 30802 | N_VOL_HARMb7 | 3sec 7th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7853 | 0x7853 | 30803 | 30803 | N_VOL_HARMb8 | 3sec 8th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7854 | 0x7854 | 30804 | 30804 | N_VOL_HARMb9 | 3sec 9th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7855 | 0x7855 | 30805 | 30805 | N_VOL_HARMb10 | 3sec 10th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7856 | 0x7856 | 30806 | 30806 | N_VOL_HARMb11 | 3sec 11st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7857 | 0x7857 | 30807 | 30807 | N_VOL_HARMb12 | 3sec 12nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7858 | 0x7858 | 30808 | 30808 | N_VOL_HARMb13 | 3sec 13rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7859 | 0x7859 | 30809 | 30809 | N_VOL_HARMb14 | 3sec 14th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x785A | 0x785A | 30810 | 30810 | N_VOL_HARMb15 | 3sec 15th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x785B | 0x785B | 30811 | 30811 | N_VOL_HARMb16 | 3sec 16th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x785C | 0x785C | 30812 | 30812 | N_VOL_HARMb17 | 3sec 17th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x785D | 0x785D | 30813 | 30813 | N_VOL_HARMb18 | 3sec 18th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x785E | 0x785E | 30814 | 30814 | N_VOL_HARMb19 | 3sec 19th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x785F | 0x785F | 30815 | 30815 | N_VOL_HARMb20 | 3sec 20th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7860 | 0x7860 | 30816 | 30816 | N_VOL_HARMb21 | 3sec 21st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7861 | 0x7861 | 30817 | 30817 | N_VOL_HARMb22 | 3sec 22nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7862 | 0x7862 | 30818 | 30818 | N_VOL_HARMb23 | 3sec 23rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7863 | 0x7863 | 30819 | 30819 | N_VOL_HARMb24 | 3sec 24th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7864 | 0x7864 | 30820 | 30820 | N_VOL_HARMb25 | 3sec 25th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7865 | 0x7865 | 30821 | 30821 | N_VOL_HARMb26 | 3sec 26th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7866 | 0x7866 | 30822 | 30822 | N_VOL_HARMb27 | 3sec 27th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7867 | 0x7867 | 30823 | 30823 | N_VOL_HARMb28 | 3sec 28th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7868 | 0x7868 | 30824 | 30824 | N_VOL_HARMb29 | 3sec 29th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7869 | 0x7869 | 30825 | 30825 | N_VOL_HARMb30 | 3sec 30th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x786A | 0x786A | 30826 | 30826 | N_VOL_HARMb31 | 3sec 31st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x786B | 0x786B | 30827 | 30827 | N_VOL_HARMb32 | 3sec 32nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x786C | 0x786C | 30828 | 30828 | N_VOL_HARMb33 | 3sec 33rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x786D | 0x786D | 30829 | 30829 | N_VOL_HARMb34 | 3sec 34th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x786E | 0x786E | 30830 | 30830 | N_VOL_HARMb35 | 3sec 35th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x786F | 0x786F | 30831 | 30831 | N_VOL_HARMb36 | 3sec 36th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7870 | 0x7870 | 30832 | 30832 | N_VOL_HARMb37 | 3sec 37th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7871 | 0x7871 | 30833 | 30833 | N_VOL_HARMb38 | 3sec 38th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7872 | 0x7872 | 30834 | 30834 | N_VOL_HARMb39 | 3sec 39th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7873 | 0x7873 | 30835 | 30835 | N_VOL_HARMb40 | 3sec 40th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7874 | 0x7874 | 30836 | 30836 | N_VOL_HARMb41 | 3sec 41st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7875 | 0x7875 | 30837 | 30837 | N_VOL_HARMb42 | 3sec 42nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7876 | 0x7876 | 30838 | 30838 | N_VOL_HARMb43 | 3sec 43rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7877 | 0x7877 | 30839 | 30839 | N_VOL_HARMb44 | 3sec 44th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7878 | 0x7878 | 30840 | 30840 | N_VOL_HARMb45 | 3sec 45th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x7879 | 0x7879 | 30841 | 30841 | N_VOL_HARMb46 | 3sec 46th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x787A | 0x787A | 30842 | 30842 | N_VOL_HARMb47 | 3sec 47th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x787B | 0x787B | 30843 | 30843 | N_VOL_HARMb48 | 3sec 48th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x787C | 0x787C | 30844 | 30844 | N_VOL_HARMb49 | 3sec 49th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x787D | 0x787D | 30845 | 30845 | N_VOL_HARMb50 | 3sec 50th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x787E | 0x787E | 30846 | 30846 | N_VOL_HARMc2 | 3sec 2nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x787F | 0x787F | 30847 | 30847 | N_VOL_HARMc3 | 3sec 3rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7880 | 0x7880 | 30848 | 30848 | N_VOL_HARMc4 | 3sec 4th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7881 | 0x7881 | 30849 | 30849 | N_VOL_HARMc5 | 3sec 5th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7882 | 0x7882 | 30850 | 30850 | N_VOL_HARMc6 | 3sec 6th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7883 | 0x7883 | 30851 | 30851 | N_VOL_HARMc7 | 3sec 7th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7884 | 0x7884 | 30852 | 30852 | N_VOL_HARMc8 | 3sec 8th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7885 | 0x7885 | 30853 | 30853 | N_VOL_HARMc9 | 3sec 9th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7886 | 0x7886 | 30854 | 30854 | N_VOL_HARMc10 | 3sec 10th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7887 | 0x7887 | 30855 | 30855 | N_VOL_HARMc11 | 3sec 11st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7888 | 0x7888 | 30856 | 30856 | N_VOL_HARMc12 | 3sec 12nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7889 | 0x7889 | 30857 | 30857 | N_VOL_HARMc13 | 3sec 13rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x788A | 0x788A | 30858 | 30858 | N_VOL_HARMc14 | 3sec 14th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x788B | 0x788B | 30859 | 30859 | N_VOL_HARMc15 | 3sec 15th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x788C | 0x788C | 30860 | 30860 | N_VOL_HARMc16 | 3sec 16th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x788D | 0x788D | 30861 | 30861 | N_VOL_HARMc17 | 3sec 17th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x788E | 0x788E | 30862 | 30862 | N_VOL_HARMc18 | 3sec 18th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x788F | 0x788F | 30863 | 30863 | N_VOL_HARMc19 | 3sec 19th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7890 | 0x7890 | 30864 | 30864 | N_VOL_HARMc20 | 3sec 20th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7891 | 0x7891 | 30865 | 30865 | N_VOL_HARMc21 | 3sec 21st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7892 | 0x7892 | 30866 | 30866 | N_VOL_HARMc22 | 3sec 22nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7893 | 0x7893 | 30867 | 30867 | N_VOL_HARMc23 | 3sec 23rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7894 | 0x7894 | 30868 | 30868 | N_VOL_HARMc24 | 3sec 24th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7895 | 0x7895 | 30869 | 30869 | N_VOL_HARMc25 | 3sec 25th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7896 | 0x7896 | 30870 | 30870 | N_VOL_HARMc26 | 3sec 26th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7897 | 0x7897 | 30871 | 30871 | N_VOL_HARMc27 | 3sec 27th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7898 | 0x7898 | 30872 | 30872 | N_VOL_HARMc28 | 3sec 28th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x7899 | 0x7899 | 30873 | 30873 | N_VOL_HARMc29 | 3sec 29th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x789A | 0x789A | 30874 | 30874 | N_VOL_HARMc30 | 3sec 30th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x789B | 0x789B | 30875 | 30875 | N_VOL_HARMc31 | 3sec 31st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x789C | 0x789C | 30876 | 30876 | N_VOL_HARMc32 | 3sec 32nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x789D | 0x789D | 30877 | 30877 | N_VOL_HARMc33 | 3sec 33rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x789E | 0x789E | 30878 | 30878 | N_VOL_HARMc34 | 3sec 34th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x789F | 0x789F | 30879 | 30879 | N_VOL_HARMc35 | 3sec 35th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78A0 | 0x78A0 | 30880 | 30880 | N_VOL_HARMc36 | 3sec 36th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78A1 | 0x78A1 | 30881 | 30881 | N_VOL_HARMc37 | 3sec 37th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78A2 | 0x78A2 | 30882 | 30882 | N_VOL_HARMc38 | 3sec 38th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78A3 | 0x78A3 | 30883 | 30883 | N_VOL_HARMc39 | 3sec 39th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78A4 | 0x78A4 | 30884 | 30884 | N_VOL_HARMc40 | 3sec 40th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78A5 | 0x78A5 | 30885 | 30885 | N_VOL_HARMc41 | 3sec 41st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78A6 | 0x78A6 | 30886 | 30886 | N_VOL_HARMc42 | 3sec 42nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78A7 | 0x78A7 | 30887 | 30887 | N_VOL_HARMc43 | 3sec 43rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78A8 | 0x78A8 | 30888 | 30888 | N_VOL_HARMc44 | 3sec 44th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78A9 | 0x78A9 | 30889 | 30889 | N_VOL_HARMc45 | 3sec 45th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78AA | 0x78AA | 30890 | 30890 | N_VOL_HARMc46 | 3sec 46th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78AB | 0x78AB | 30891 | 30891 | N_VOL_HARMc47 | 3sec 47th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78AC | 0x78AC | 30892 | 30892 | N_VOL_HARMc48 | 3sec 48th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78AD | 0x78AD | 30893 | 30893 | N_VOL_HARMc49 | 3sec 49th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78AE | 0x78AE | 30894 | 30894 | N_VOL_HARMc50 | 3sec 50th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x78AF | 0x78B0 | 30895 | 30896 | VOL_HARM_PASSa2 | 3sec 2nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78B1 | 0x78B2 | 30897 | 30898 | VOL_HARM_PASSa3 | 3sec 3rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78B3 | 0x78B4 | 30899 | 30900 | VOL_HARM_PASSa4 | 3sec 4th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78B5 | 0x78B6 | 30901 | 30902 | VOL_HARM_PASSa5 | 3sec 5th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78B7 | 0x78B8 | 30903 | 30904 | VOL_HARM_PASSa6 | 3sec 6th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78B9 | 0x78BA | 30905 | 30906 | VOL_HARM_PASSa7 | 3sec 7th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78BB | 0x78BC | 30907 | 30908 | VOL_HARM_PASSa8 | 3sec 8th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78BD | 0x78BE | 30909 | 30910 | VOL_HARM_PASSa9 | 3sec 9th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78BF | 0x78C0 | 30911 | 30912 | VOL_HARM_PASSa10 | 3sec 10th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78C1 | 0x78C2 | 30913 | 30914 | VOL_HARM_PASSa11 | 3sec 11st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78C3 | 0x78C4 | 30915 | 30916 | VOL_HARM_PASSa12 | 3sec 12nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78C5 | 0x78C6 | 30917 | 30918 | VOL_HARM_PASSa13 | 3sec 13rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78C7 | 0x78C8 | 30919 | 30920 | VOL_HARM_PASSa14 | 3sec 14th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78C9 | 0x78CA | 30921 | 30922 | VOL_HARM_PASSa15 | 3sec 15th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78CB | 0x78CC | 30923 | 30924 | VOL_HARM_PASSa16 | 3sec 16th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78CD | 0x78CE | 30925 | 30926 | VOL_HARM_PASSa17 | 3sec 17th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78CF | 0x78D0 | 30927 | 30928 | VOL_HARM_PASSa18 | 3sec 18th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78D1 | 0x78D2 | 30929 | 30930 | VOL_HARM_PASSa19 | 3sec 19th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78D3 | 0x78D4 | 30931 | 30932 | VOL_HARM_PASSa20 | 3sec 20th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78D5 | 0x78D6 | 30933 | 30934 | VOL_HARM_PASSa21 | 3sec 21st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78D7 | 0x78D8 | 30935 | 30936 | VOL_HARM_PASSa22 | 3sec 22nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78D9 | 0x78DA | 30937 | 30938 | VOL_HARM_PASSa23 | 3sec 23rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78DB | 0x78DC | 30939 | 30940 | VOL_HARM_PASSa24 | 3sec 24th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78DD | 0x78DE | 30941 | 30942 | VOL_HARM_PASSa25 | 3sec 25th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78DF | 0x78E0 | 30943 | 30944 | VOL_HARM_PASSa26 | 3sec 26th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78E1 | 0x78E2 | 30945 | 30946 | VOL_HARM_PASSa27 | 3sec 27th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78E3 | 0x78E4 | 30947 | 30948 | VOL_HARM_PASSa28 | 3sec 28th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78E5 | 0x78E6 | 30949 | 30950 | VOL_HARM_PASSa29 | 3sec 29th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78E7 | 0x78E8 | 30951 | 30952 | VOL_HARM_PASSa30 | 3sec 30th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78E9 | 0x78EA | 30953 | 30954 | VOL_HARM_PASSa31 | 3sec 31st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78EB | 0x78EC | 30955 | 30956 | VOL_HARM_PASSa32 | 3sec 32nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78ED | 0x78EE | 30957 | 30958 | VOL_HARM_PASSa33 | 3sec 33rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78EF | 0x78F0 | 30959 | 30960 | VOL_HARM_PASSa34 | 3sec 34th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78F1 | 0x78F2 | 30961 | 30962 | VOL_HARM_PASSa35 | 3sec 35th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78F3 | 0x78F4 | 30963 | 30964 | VOL_HARM_PASSa36 | 3sec 36th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78F5 | 0x78F6 | 30965 | 30966 | VOL_HARM_PASSa37 | 3sec 37th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78F7 | 0x78F8 | 30967 | 30968 | VOL_HARM_PASSa38 | 3sec 38th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78F9 | 0x78FA | 30969 | 30970 | VOL_HARM_PASSa39 | 3sec 39th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78FB | 0x78FC | 30971 | 30972 | VOL_HARM_PASSa40 | 3sec 40th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78FD | 0x78FE | 30973 | 30974 | VOL_HARM_PASSa41 | 3sec 41st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x78FF | 0x7900 | 30975 | 30976 | VOL_HARM_PASSa42 | 3sec 42nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x7901 | 0x7902 | 30977 | 30978 | VOL_HARM_PASSa43 | 3sec 43rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x7903 | 0x7904 | 30979 | 30980 | VOL_HARM_PASSa44 | 3sec 44th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x7905 | 0x7906 | 30981 | 30982 | VOL_HARM_PASSa45 | 3sec 45th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x7907 | 0x7908 | 30983 | 30984 | VOL_HARM_PASSa46 | 3sec 46th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x7909 | 0x790A | 30985 | 30986 | VOL_HARM_PASSa47 | 3sec 47th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x790B | 0x790C | 30987 | 30988 | VOL_HARM_PASSa48 | 3sec 48th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x790D | 0x790E | 30989 | 30990 | VOL_HARM_PASSa49 | 3sec 49th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x790F | 0x7910 | 30991 | 30992 | VOL_HARM_PASSa50 | 3sec 50th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x7911 | 0x7912 | 30993 | 30994 | VOL_HARM_PASSb2 | 3sec 2nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7913 | 0x7914 | 30995 | 30996 | VOL_HARM_PASSb3 | 3sec 3rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7915 | 0x7916 | 30997 | 30998 | VOL_HARM_PASSb4 | 3sec 4th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7917 | 0x7918 | 30999 | 31000 | VOL_HARM_PASSb5 | 3sec 5th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7919 | 0x791A | 31001 | 31002 | VOL_HARM_PASSb6 | 3sec 6th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x791B | 0x791C | 31003 | 31004 | VOL_HARM_PASSb7 | 3sec 7th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x791D | 0x791E | 31005 | 31006 | VOL_HARM_PASSb8 | 3sec 8th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x791F | 0x7920 | 31007 | 31008 | VOL_HARM_PASSb9 | 3sec 9th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7921 | 0x7922 | 31009 | 31010 | VOL_HARM_PASSb10 | 3sec 10th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7923 | 0x7924 | 31011 | 31012 | VOL_HARM_PASSb11 | 3sec 11st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7925 | 0x7926 | 31013 | 31014 | VOL_HARM_PASSb12 | 3sec 12nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7927 | 0x7928 | 31015 | 31016 | VOL_HARM_PASSb13 | 3sec 13rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7929 | 0x792A | 31017 | 31018 | VOL_HARM_PASSb14 | 3sec 14th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x792B | 0x792C | 31019 | 31020 | VOL_HARM_PASSb15 | 3sec 15th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x792D | 0x792E | 31021 | 31022 | VOL_HARM_PASSb16 | 3sec 16th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x792F | 0x7930 | 31023 | 31024 | VOL_HARM_PASSb17 | 3sec 17th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7931 | 0x7932 | 31025 | 31026 | VOL_HARM_PASSb18 | 3sec 18th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7933 | 0x7934 | 31027 | 31028 | VOL_HARM_PASSb19 | 3sec 19th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7935 | 0x7936 | 31029 | 31030 | VOL_HARM_PASSb20 | 3sec 20th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7937 | 0x7938 | 31031 | 31032 | VOL_HARM_PASSb21 | 3sec 21st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7939 | 0x793A | 31033 | 31034 | VOL_HARM_PASSb22 | 3sec 22nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x793B | 0x793C | 31035 | 31036 | VOL_HARM_PASSb23 | 3sec 23rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x793D | 0x793E | 31037 | 31038 | VOL_HARM_PASSb24 | 3sec 24th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x793F | 0x7940 | 31039 | 31040 | VOL_HARM_PASSb25 | 3sec 25th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7941 | 0x7942 | 31041 | 31042 | VOL_HARM_PASSb26 | 3sec 26th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7943 | 0x7944 | 31043 | 31044 | VOL_HARM_PASSb27 | 3sec 27th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7945 | 0x7946 | 31045 | 31046 | VOL_HARM_PASSb28 | 3sec 28th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7947 | 0x7948 | 31047 | 31048 | VOL_HARM_PASSb29 | 3sec 29th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7949 | 0x794A | 31049 | 31050 | VOL_HARM_PASSb30 | 3sec 30th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x794B | 0x794C | 31051 | 31052 | VOL_HARM_PASSb31 | 3sec 31st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x794D | 0x794E | 31053 | 31054 | VOL_HARM_PASSb32 | 3sec 32nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x794F | 0x7950 | 31055 | 31056 | VOL_HARM_PASSb33 | 3sec 33rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7951 | 0x7952 | 31057 | 31058 | VOL_HARM_PASSb34 | 3sec 34th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7953 | 0x7954 | 31059 | 31060 | VOL_HARM_PASSb35 | 3sec 35th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7955 | 0x7956 | 31061 | 31062 | VOL_HARM_PASSb36 | 3sec 36th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7957 | 0x7958 | 31063 | 31064 | VOL_HARM_PASSb37 | 3sec 37th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7959 | 0x795A | 31065 | 31066 | VOL_HARM_PASSb38 | 3sec 38th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x795B | 0x795C | 31067 | 31068 | VOL_HARM_PASSb39 | 3sec 39th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x795D | 0x795E | 31069 | 31070 | VOL_HARM_PASSb40 | 3sec 40th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x795F | 0x7960 | 31071 | 31072 | VOL_HARM_PASSb41 | 3sec 41st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7961 | 0x7962 | 31073 | 31074 | VOL_HARM_PASSb42 | 3sec 42nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7963 | 0x7964 | 31075 | 31076 | VOL_HARM_PASSb43 | 3sec 43rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7965 | 0x7966 | 31077 | 31078 | VOL_HARM_PASSb44 | 3sec 44th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7967 | 0x7968 | 31079 | 31080 | VOL_HARM_PASSb45 | 3sec 45th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7969 | 0x796A | 31081 | 31082 | VOL_HARM_PASSb46 | 3sec 46th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x796B | 0x796C | 31083 | 31084 | VOL_HARM_PASSb47 | 3sec 47th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x796D | 0x796E | 31085 | 31086 | VOL_HARM_PASSb48 | 3sec 48th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x796F | 0x7970 | 31087 | 31088 | VOL_HARM_PASSb49 | 3sec 49th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7971 | 0x7972 | 31089 | 31090 | VOL_HARM_PASSb50 | 3sec 50th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x7973 | 0x7974 | 31091 | 31092 | VOL_HARM_PASSc2 | 3sec 2nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7975 | 0x7976 | 31093 | 31094 | VOL_HARM_PASSc3 | 3sec 3rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7977 | 0x7978 | 31095 | 31096 | VOL_HARM_PASSc4 | 3sec 4th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7979 | 0x797A | 31097 | 31098 | VOL_HARM_PASSc5 | 3sec 5th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x797B | 0x797C | 31099 | 31100 | VOL_HARM_PASSc6 | 3sec 6th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x797D | 0x797E | 31101 | 31102 | VOL_HARM_PASSc7 | 3sec 7th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x797F | 0x7980 | 31103 | 31104 | VOL_HARM_PASSc8 | 3sec 8th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7981 | 0x7982 | 31105 | 31106 | VOL_HARM_PASSc9 | 3sec 9th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7983 | 0x7984 | 31107 | 31108 | VOL_HARM_PASSc10 | 3sec 10th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7985 | 0x7986 | 31109 | 31110 | VOL_HARM_PASSc11 | 3sec 11st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7987 | 0x7988 | 31111 | 31112 | VOL_HARM_PASSc12 | 3sec 12nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7989 | 0x798A | 31113 | 31114 | VOL_HARM_PASSc13 | 3sec 13rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x798B | 0x798C | 31115 | 31116 | VOL_HARM_PASSc14 | 3sec 14th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x798D | 0x798E | 31117 | 31118 | VOL_HARM_PASSc15 | 3sec 15th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x798F | 0x7990 | 31119 | 31120 | VOL_HARM_PASSc16 | 3sec 16th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7991 | 0x7992 | 31121 | 31122 | VOL_HARM_PASSc17 | 3sec 17th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7993 | 0x7994 | 31123 | 31124 | VOL_HARM_PASSc18 | 3sec 18th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7995 | 0x7996 | 31125 | 31126 | VOL_HARM_PASSc19 | 3sec 19th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7997 | 0x7998 | 31127 | 31128 | VOL_HARM_PASSc20 | 3sec 20th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x7999 | 0x799A | 31129 | 31130 | VOL_HARM_PASSc21 | 3sec 21st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x799B | 0x799C | 31131 | 31132 | VOL_HARM_PASSc22 | 3sec 22nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x799D | 0x799E | 31133 | 31134 | VOL_HARM_PASSc23 | 3sec 23rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x799F | 0x79A0 | 31135 | 31136 | VOL_HARM_PASSc24 | 3sec 24th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79A1 | 0x79A2 | 31137 | 31138 | VOL_HARM_PASSc25 | 3sec 25th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79A3 | 0x79A4 | 31139 | 31140 | VOL_HARM_PASSc26 | 3sec 26th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79A5 | 0x79A6 | 31141 | 31142 | VOL_HARM_PASSc27 | 3sec 27th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79A7 | 0x79A8 | 31143 | 31144 | VOL_HARM_PASSc28 | 3sec 28th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79A9 | 0x79AA | 31145 | 31146 | VOL_HARM_PASSc29 | 3sec 29th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79AB | 0x79AC | 31147 | 31148 | VOL_HARM_PASSc30 | 3sec 30th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79AD | 0x79AE | 31149 | 31150 | VOL_HARM_PASSc31 | 3sec 31st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79AF | 0x79B0 | 31151 | 31152 | VOL_HARM_PASSc32 | 3sec 32nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79B1 | 0x79B2 | 31153 | 31154 | VOL_HARM_PASSc33 | 3sec 33rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79B3 | 0x79B4 | 31155 | 31156 | VOL_HARM_PASSc34 | 3sec 34th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79B5 | 0x79B6 | 31157 | 31158 | VOL_HARM_PASSc35 | 3sec 35th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79B7 | 0x79B8 | 31159 | 31160 | VOL_HARM_PASSc36 | 3sec 36th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79B9 | 0x79BA | 31161 | 31162 | VOL_HARM_PASSc37 | 3sec 37th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79BB | 0x79BC | 31163 | 31164 | VOL_HARM_PASSc38 | 3sec 38th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79BD | 0x79BE | 31165 | 31166 | VOL_HARM_PASSc39 | 3sec 39th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79BF | 0x79C0 | 31167 | 31168 | VOL_HARM_PASSc40 | 3sec 40th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79C1 | 0x79C2 | 31169 | 31170 | VOL_HARM_PASSc41 | 3sec 41st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79C3 | 0x79C4 | 31171 | 31172 | VOL_HARM_PASSc42 | 3sec 42nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79C5 | 0x79C6 | 31173 | 31174 | VOL_HARM_PASSc43 | 3sec 43rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79C7 | 0x79C8 | 31175 | 31176 | VOL_HARM_PASSc44 | 3sec 44th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79C9 | 0x79CA | 31177 | 31178 | VOL_HARM_PASSc45 | 3sec 45th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79CB | 0x79CC | 31179 | 31180 | VOL_HARM_PASSc46 | 3sec 46th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79CD | 0x79CE | 31181 | 31182 | VOL_HARM_PASSc47 | 3sec 47th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79CF | 0x79D0 | 31183 | 31184 | VOL_HARM_PASSc48 | 3sec 48th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79D1 | 0x79D2 | 31185 | 31186 | VOL_HARM_PASSc49 | 3sec 49th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79D3 | 0x79D4 | 31187 | 31188 | VOL_HARM_PASSc50 | 3sec 50th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x79D5 | 0x79D6 | 31189 | 31190 | VOL_HARM_MAXa2 | 3sec 2nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79D7 | 0x79D8 | 31191 | 31192 | VOL_HARM_MAXa3 | 3sec 3rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79D9 | 0x79DA | 31193 | 31194 | VOL_HARM_MAXa4 | 3sec 4th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79DB | 0x79DC | 31195 | 31196 | VOL_HARM_MAXa5 | 3sec 5th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79DD | 0x79DE | 31197 | 31198 | VOL_HARM_MAXa6 | 3sec 6th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79DF | 0x79E0 | 31199 | 31200 | VOL_HARM_MAXa7 | 3sec 7th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79E1 | 0x79E2 | 31201 | 31202 | VOL_HARM_MAXa8 | 3sec 8th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79E3 | 0x79E4 | 31203 | 31204 | VOL_HARM_MAXa9 | 3sec 9th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79E5 | 0x79E6 | 31205 | 31206 | VOL_HARM_MAXa10 | 3sec 10th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79E7 | 0x79E8 | 31207 | 31208 | VOL_HARM_MAXa11 | 3sec 11st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79E9 | 0x79EA | 31209 | 31210 | VOL_HARM_MAXa12 | 3sec 12nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79EB | 0x79EC | 31211 | 31212 | VOL_HARM_MAXa13 | 3sec 13rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79ED | 0x79EE | 31213 | 31214 | VOL_HARM_MAXa14 | 3sec 14th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79EF | 0x79F0 | 31215 | 31216 | VOL_HARM_MAXa15 | 3sec 15th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79F1 | 0x79F2 | 31217 | 31218 | VOL_HARM_MAXa16 | 3sec 16th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79F3 | 0x79F4 | 31219 | 31220 | VOL_HARM_MAXa17 | 3sec 17th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79F5 | 0x79F6 | 31221 | 31222 | VOL_HARM_MAXa18 | 3sec 18th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79F7 | 0x79F8 | 31223 | 31224 | VOL_HARM_MAXa19 | 3sec 19th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79F9 | 0x79FA | 31225 | 31226 | VOL_HARM_MAXa20 | 3sec 20th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79FB | 0x79FC | 31227 | 31228 | VOL_HARM_MAXa21 | 3sec 21st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79FD | 0x79FE | 31229 | 31230 | VOL_HARM_MAXa22 | 3sec 22nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x79FF | 0x7A00 | 31231 | 31232 | VOL_HARM_MAXa23 | 3sec 23rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A01 | 0x7A02 | 31233 | 31234 | VOL_HARM_MAXa24 | 3sec 24th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A03 | 0x7A04 | 31235 | 31236 | VOL_HARM_MAXa25 | 3sec 25th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A05 | 0x7A06 | 31237 | 31238 | VOL_HARM_MAXa26 | 3sec 26th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A07 | 0x7A08 | 31239 | 31240 | VOL_HARM_MAXa27 | 3sec 27th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A09 | 0x7A0A | 31241 | 31242 | VOL_HARM_MAXa28 | 3sec 28th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A0B | 0x7A0C | 31243 | 31244 | VOL_HARM_MAXa29 | 3sec 29th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A0D | 0x7A0E | 31245 | 31246 | VOL_HARM_MAXa30 | 3sec 30th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A0F | 0x7A10 | 31247 | 31248 | VOL_HARM_MAXa31 | 3sec 31st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A11 | 0x7A12 | 31249 | 31250 | VOL_HARM_MAXa32 | 3sec 32nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A13 | 0x7A14 | 31251 | 31252 | VOL_HARM_MAXa33 | 3sec 33rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A15 | 0x7A16 | 31253 | 31254 | VOL_HARM_MAXa34 | 3sec 34th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A17 | 0x7A18 | 31255 | 31256 | VOL_HARM_MAXa35 | 3sec 35th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A19 | 0x7A1A | 31257 | 31258 | VOL_HARM_MAXa36 | 3sec 36th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A1B | 0x7A1C | 31259 | 31260 | VOL_HARM_MAXa37 | 3sec 37th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A1D | 0x7A1E | 31261 | 31262 | VOL_HARM_MAXa38 | 3sec 38th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A1F | 0x7A20 | 31263 | 31264 | VOL_HARM_MAXa39 | 3sec 39th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A21 | 0x7A22 | 31265 | 31266 | VOL_HARM_MAXa40 | 3sec 40th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A23 | 0x7A24 | 31267 | 31268 | VOL_HARM_MAXa41 | 3sec 41st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A25 | 0x7A26 | 31269 | 31270 | VOL_HARM_MAXa42 | 3sec 42nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A27 | 0x7A28 | 31271 | 31272 | VOL_HARM_MAXa43 | 3sec 43rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A29 | 0x7A2A | 31273 | 31274 | VOL_HARM_MAXa44 | 3sec 44th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A2B | 0x7A2C | 31275 | 31276 | VOL_HARM_MAXa45 | 3sec 45th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A2D | 0x7A2E | 31277 | 31278 | VOL_HARM_MAXa46 | 3sec 46th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A2F | 0x7A30 | 31279 | 31280 | VOL_HARM_MAXa47 | 3sec 47th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A31 | 0x7A32 | 31281 | 31282 | VOL_HARM_MAXa48 | 3sec 48th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A33 | 0x7A34 | 31283 | 31284 | VOL_HARM_MAXa49 | 3sec 49th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A35 | 0x7A36 | 31285 | 31286 | VOL_HARM_MAXa50 | 3sec 50th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x7A37 | 0x7A38 | 31287 | 31288 | VOL_HARM_MAXb2 | 3sec 2nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A39 | 0x7A3A | 31289 | 31290 | VOL_HARM_MAXb3 | 3sec 3rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A3B | 0x7A3C | 31291 | 31292 | VOL_HARM_MAXb4 | 3sec 4th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A3D | 0x7A3E | 31293 | 31294 | VOL_HARM_MAXb5 | 3sec 5th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A3F | 0x7A40 | 31295 | 31296 | VOL_HARM_MAXb6 | 3sec 6th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A41 | 0x7A42 | 31297 | 31298 | VOL_HARM_MAXb7 | 3sec 7th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A43 | 0x7A44 | 31299 | 31300 | VOL_HARM_MAXb8 | 3sec 8th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A45 | 0x7A46 | 31301 | 31302 | VOL_HARM_MAXb9 | 3sec 9th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A47 | 0x7A48 | 31303 | 31304 | VOL_HARM_MAXb10 | 3sec 10th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A49 | 0x7A4A | 31305 | 31306 | VOL_HARM_MAXb11 | 3sec 11st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A4B | 0x7A4C | 31307 | 31308 | VOL_HARM_MAXb12 | 3sec 12nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A4D | 0x7A4E | 31309 | 31310 | VOL_HARM_MAXb13 | 3sec 13rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A4F | 0x7A50 | 31311 | 31312 | VOL_HARM_MAXb14 | 3sec 14th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A51 | 0x7A52 | 31313 | 31314 | VOL_HARM_MAXb15 | 3sec 15th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A53 | 0x7A54 | 31315 | 31316 | VOL_HARM_MAXb16 | 3sec 16th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A55 | 0x7A56 | 31317 | 31318 | VOL_HARM_MAXb17 | 3sec 17th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A57 | 0x7A58 | 31319 | 31320 | VOL_HARM_MAXb18 | 3sec 18th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A59 | 0x7A5A | 31321 | 31322 | VOL_HARM_MAXb19 | 3sec 19th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A5B | 0x7A5C | 31323 | 31324 | VOL_HARM_MAXb20 | 3sec 20th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A5D | 0x7A5E | 31325 | 31326 | VOL_HARM_MAXb21 | 3sec 21st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A5F | 0x7A60 | 31327 | 31328 | VOL_HARM_MAXb22 | 3sec 22nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A61 | 0x7A62 | 31329 | 31330 | VOL_HARM_MAXb23 | 3sec 23rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A63 | 0x7A64 | 31331 | 31332 | VOL_HARM_MAXb24 | 3sec 24th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A65 | 0x7A66 | 31333 | 31334 | VOL_HARM_MAXb25 | 3sec 25th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A67 | 0x7A68 | 31335 | 31336 | VOL_HARM_MAXb26 | 3sec 26th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A69 | 0x7A6A | 31337 | 31338 | VOL_HARM_MAXb27 | 3sec 27th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A6B | 0x7A6C | 31339 | 31340 | VOL_HARM_MAXb28 | 3sec 28th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A6D | 0x7A6E | 31341 | 31342 | VOL_HARM_MAXb29 | 3sec 29th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A6F | 0x7A70 | 31343 | 31344 | VOL_HARM_MAXb30 | 3sec 30th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A71 | 0x7A72 | 31345 | 31346 | VOL_HARM_MAXb31 | 3sec 31st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A73 | 0x7A74 | 31347 | 31348 | VOL_HARM_MAXb32 | 3sec 32nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A75 | 0x7A76 | 31349 | 31350 | VOL_HARM_MAXb33 | 3sec 33rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A77 | 0x7A78 | 31351 | 31352 | VOL_HARM_MAXb34 | 3sec 34th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A79 | 0x7A7A | 31353 | 31354 | VOL_HARM_MAXb35 | 3sec 35th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A7B | 0x7A7C | 31355 | 31356 | VOL_HARM_MAXb36 | 3sec 36th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A7D | 0x7A7E | 31357 | 31358 | VOL_HARM_MAXb37 | 3sec 37th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A7F | 0x7A80 | 31359 | 31360 | VOL_HARM_MAXb38 | 3sec 38th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A81 | 0x7A82 | 31361 | 31362 | VOL_HARM_MAXb39 | 3sec 39th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A83 | 0x7A84 | 31363 | 31364 | VOL_HARM_MAXb40 | 3sec 40th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A85 | 0x7A86 | 31365 | 31366 | VOL_HARM_MAXb41 | 3sec 41st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A87 | 0x7A88 | 31367 | 31368 | VOL_HARM_MAXb42 | 3sec 42nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A89 | 0x7A8A | 31369 | 31370 | VOL_HARM_MAXb43 | 3sec 43rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A8B | 0x7A8C | 31371 | 31372 | VOL_HARM_MAXb44 | 3sec 44th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A8D | 0x7A8E | 31373 | 31374 | VOL_HARM_MAXb45 | 3sec 45th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A8F | 0x7A90 | 31375 | 31376 | VOL_HARM_MAXb46 | 3sec 46th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A91 | 0x7A92 | 31377 | 31378 | VOL_HARM_MAXb47 | 3sec 47th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A93 | 0x7A94 | 31379 | 31380 | VOL_HARM_MAXb48 | 3sec 48th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A95 | 0x7A96 | 31381 | 31382 | VOL_HARM_MAXb49 | 3sec 49th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A97 | 0x7A98 | 31383 | 31384 | VOL_HARM_MAXb50 | 3sec 50th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x7A99 | 0x7A9A | 31385 | 31386 | VOL_HARM_MAXc2 | 3sec 2nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7A9B | 0x7A9C | 31387 | 31388 | VOL_HARM_MAXc3 | 3sec 3rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7A9D | 0x7A9E | 31389 | 31390 | VOL_HARM_MAXc4 | 3sec 4th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7A9F | 0x7AA0 | 31391 | 31392 | VOL_HARM_MAXc5 | 3sec 5th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AA1 | 0x7AA2 | 31393 | 31394 | VOL_HARM_MAXc6 | 3sec 6th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AA3 | 0x7AA4 | 31395 | 31396 | VOL_HARM_MAXc7 | 3sec 7th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AA5 | 0x7AA6 | 31397 | 31398 | VOL_HARM_MAXc8 | 3sec 8th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AA7 | 0x7AA8 | 31399 | 31400 | VOL_HARM_MAXc9 | 3sec 9th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AA9 | 0x7AAA | 31401 | 31402 | VOL_HARM_MAXc10 | 3sec 10th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AAB | 0x7AAC | 31403 | 31404 | VOL_HARM_MAXc11 | 3sec 11st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AAD | 0x7AAE | 31405 | 31406 | VOL_HARM_MAXc12 | 3sec 12nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AAF | 0x7AB0 | 31407 | 31408 | VOL_HARM_MAXc13 | 3sec 13rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AB1 | 0x7AB2 | 31409 | 31410 | VOL_HARM_MAXc14 | 3sec 14th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AB3 | 0x7AB4 | 31411 | 31412 | VOL_HARM_MAXc15 | 3sec 15th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AB5 | 0x7AB6 | 31413 | 31414 | VOL_HARM_MAXc16 | 3sec 16th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AB7 | 0x7AB8 | 31415 | 31416 | VOL_HARM_MAXc17 | 3sec 17th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AB9 | 0x7ABA | 31417 | 31418 | VOL_HARM_MAXc18 | 3sec 18th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7ABB | 0x7ABC | 31419 | 31420 | VOL_HARM_MAXc19 | 3sec 19th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7ABD | 0x7ABE | 31421 | 31422 | VOL_HARM_MAXc20 | 3sec 20th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7ABF | 0x7AC0 | 31423 | 31424 | VOL_HARM_MAXc21 | 3sec 21st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AC1 | 0x7AC2 | 31425 | 31426 | VOL_HARM_MAXc22 | 3sec 22nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AC3 | 0x7AC4 | 31427 | 31428 | VOL_HARM_MAXc23 | 3sec 23rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AC5 | 0x7AC6 | 31429 | 31430 | VOL_HARM_MAXc24 | 3sec 24th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AC7 | 0x7AC8 | 31431 | 31432 | VOL_HARM_MAXc25 | 3sec 25th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AC9 | 0x7ACA | 31433 | 31434 | VOL_HARM_MAXc26 | 3sec 26th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7ACB | 0x7ACC | 31435 | 31436 | VOL_HARM_MAXc27 | 3sec 27th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7ACD | 0x7ACE | 31437 | 31438 | VOL_HARM_MAXc28 | 3sec 28th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7ACF | 0x7AD0 | 31439 | 31440 | VOL_HARM_MAXc29 | 3sec 29th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AD1 | 0x7AD2 | 31441 | 31442 | VOL_HARM_MAXc30 | 3sec 30th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AD3 | 0x7AD4 | 31443 | 31444 | VOL_HARM_MAXc31 | 3sec 31st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AD5 | 0x7AD6 | 31445 | 31446 | VOL_HARM_MAXc32 | 3sec 32nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AD7 | 0x7AD8 | 31447 | 31448 | VOL_HARM_MAXc33 | 3sec 33rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AD9 | 0x7ADA | 31449 | 31450 | VOL_HARM_MAXc34 | 3sec 34th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7ADB | 0x7ADC | 31451 | 31452 | VOL_HARM_MAXc35 | 3sec 35th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7ADD | 0x7ADE | 31453 | 31454 | VOL_HARM_MAXc36 | 3sec 36th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7ADF | 0x7AE0 | 31455 | 31456 | VOL_HARM_MAXc37 | 3sec 37th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AE1 | 0x7AE2 | 31457 | 31458 | VOL_HARM_MAXc38 | 3sec 38th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AE3 | 0x7AE4 | 31459 | 31460 | VOL_HARM_MAXc39 | 3sec 39th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AE5 | 0x7AE6 | 31461 | 31462 | VOL_HARM_MAXc40 | 3sec 40th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AE7 | 0x7AE8 | 31463 | 31464 | VOL_HARM_MAXc41 | 3sec 41st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AE9 | 0x7AEA | 31465 | 31466 | VOL_HARM_MAXc42 | 3sec 42nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AEB | 0x7AEC | 31467 | 31468 | VOL_HARM_MAXc43 | 3sec 43rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AED | 0x7AEE | 31469 | 31470 | VOL_HARM_MAXc44 | 3sec 44th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AEF | 0x7AF0 | 31471 | 31472 | VOL_HARM_MAXc45 | 3sec 45th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AF1 | 0x7AF2 | 31473 | 31474 | VOL_HARM_MAXc46 | 3sec 46th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AF3 | 0x7AF4 | 31475 | 31476 | VOL_HARM_MAXc47 | 3sec 47th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AF5 | 0x7AF6 | 31477 | 31478 | VOL_HARM_MAXc48 | 3sec 48th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AF7 | 0x7AF8 | 31479 | 31480 | VOL_HARM_MAXc49 | 3sec 49th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AF9 | 0x7AFA | 31481 | 31482 | VOL_HARM_MAXc50 | 3sec 50th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x7AFB | 0x7AFC | 31483 | 31484 | VOL_HARM_MINa2 | 3sec 2nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7AFD | 0x7AFE | 31485 | 31486 | VOL_HARM_MINa3 | 3sec 3rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7AFF | 0x7B00 | 31487 | 31488 | VOL_HARM_MINa4 | 3sec 4th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B01 | 0x7B02 | 31489 | 31490 | VOL_HARM_MINa5 | 3sec 5th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B03 | 0x7B04 | 31491 | 31492 | VOL_HARM_MINa6 | 3sec 6th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B05 | 0x7B06 | 31493 | 31494 | VOL_HARM_MINa7 | 3sec 7th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B07 | 0x7B08 | 31495 | 31496 | VOL_HARM_MINa8 | 3sec 8th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B09 | 0x7B0A | 31497 | 31498 | VOL_HARM_MINa9 | 3sec 9th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B0B | 0x7B0C | 31499 | 31500 | VOL_HARM_MINa10 | 3sec 10th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B0D | 0x7B0E | 31501 | 31502 | VOL_HARM_MINa11 | 3sec 11st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B0F | 0x7B10 | 31503 | 31504 | VOL_HARM_MINa12 | 3sec 12nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B11 | 0x7B12 | 31505 | 31506 | VOL_HARM_MINa13 | 3sec 13rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B13 | 0x7B14 | 31507 | 31508 | VOL_HARM_MINa14 | 3sec 14th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B15 | 0x7B16 | 31509 | 31510 | VOL_HARM_MINa15 | 3sec 15th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B17 | 0x7B18 | 31511 | 31512 | VOL_HARM_MINa16 | 3sec 16th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B19 | 0x7B1A | 31513 | 31514 | VOL_HARM_MINa17 | 3sec 17th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B1B | 0x7B1C | 31515 | 31516 | VOL_HARM_MINa18 | 3sec 18th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B1D | 0x7B1E | 31517 | 31518 | VOL_HARM_MINa19 | 3sec 19th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B1F | 0x7B20 | 31519 | 31520 | VOL_HARM_MINa20 | 3sec 20th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B21 | 0x7B22 | 31521 | 31522 | VOL_HARM_MINa21 | 3sec 21st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B23 | 0x7B24 | 31523 | 31524 | VOL_HARM_MINa22 | 3sec 22nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B25 | 0x7B26 | 31525 | 31526 | VOL_HARM_MINa23 | 3sec 23rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B27 | 0x7B28 | 31527 | 31528 | VOL_HARM_MINa24 | 3sec 24th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B29 | 0x7B2A | 31529 | 31530 | VOL_HARM_MINa25 | 3sec 25th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B2B | 0x7B2C | 31531 | 31532 | VOL_HARM_MINa26 | 3sec 26th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B2D | 0x7B2E | 31533 | 31534 | VOL_HARM_MINa27 | 3sec 27th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B2F | 0x7B30 | 31535 | 31536 | VOL_HARM_MINa28 | 3sec 28th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B31 | 0x7B32 | 31537 | 31538 | VOL_HARM_MINa29 | 3sec 29th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B33 | 0x7B34 | 31539 | 31540 | VOL_HARM_MINa30 | 3sec 30th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B35 | 0x7B36 | 31541 | 31542 | VOL_HARM_MINa31 | 3sec 31st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B37 | 0x7B38 | 31543 | 31544 | VOL_HARM_MINa32 | 3sec 32nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B39 | 0x7B3A | 31545 | 31546 | VOL_HARM_MINa33 | 3sec 33rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B3B | 0x7B3C | 31547 | 31548 | VOL_HARM_MINa34 | 3sec 34th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B3D | 0x7B3E | 31549 | 31550 | VOL_HARM_MINa35 | 3sec 35th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B3F | 0x7B40 | 31551 | 31552 | VOL_HARM_MINa36 | 3sec 36th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B41 | 0x7B42 | 31553 | 31554 | VOL_HARM_MINa37 | 3sec 37th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B43 | 0x7B44 | 31555 | 31556 | VOL_HARM_MINa38 | 3sec 38th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B45 | 0x7B46 | 31557 | 31558 | VOL_HARM_MINa39 | 3sec 39th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B47 | 0x7B48 | 31559 | 31560 | VOL_HARM_MINa40 | 3sec 40th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B49 | 0x7B4A | 31561 | 31562 | VOL_HARM_MINa41 | 3sec 41st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B4B | 0x7B4C | 31563 | 31564 | VOL_HARM_MINa42 | 3sec 42nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B4D | 0x7B4E | 31565 | 31566 | VOL_HARM_MINa43 | 3sec 43rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B4F | 0x7B50 | 31567 | 31568 | VOL_HARM_MINa44 | 3sec 44th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B51 | 0x7B52 | 31569 | 31570 | VOL_HARM_MINa45 | 3sec 45th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B53 | 0x7B54 | 31571 | 31572 | VOL_HARM_MINa46 | 3sec 46th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B55 | 0x7B56 | 31573 | 31574 | VOL_HARM_MINa47 | 3sec 47th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B57 | 0x7B58 | 31575 | 31576 | VOL_HARM_MINa48 | 3sec 48th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B59 | 0x7B5A | 31577 | 31578 | VOL_HARM_MINa49 | 3sec 49th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B5B | 0x7B5C | 31579 | 31580 | VOL_HARM_MINa50 | 3sec 50th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x7B5D | 0x7B5E | 31581 | 31582 | VOL_HARM_MINb2 | 3sec 2nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B5F | 0x7B60 | 31583 | 31584 | VOL_HARM_MINb3 | 3sec 3rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B61 | 0x7B62 | 31585 | 31586 | VOL_HARM_MINb4 | 3sec 4th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B63 | 0x7B64 | 31587 | 31588 | VOL_HARM_MINb5 | 3sec 5th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B65 | 0x7B66 | 31589 | 31590 | VOL_HARM_MINb6 | 3sec 6th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B67 | 0x7B68 | 31591 | 31592 | VOL_HARM_MINb7 | 3sec 7th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B69 | 0x7B6A | 31593 | 31594 | VOL_HARM_MINb8 | 3sec 8th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B6B | 0x7B6C | 31595 | 31596 | VOL_HARM_MINb9 | 3sec 9th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B6D | 0x7B6E | 31597 | 31598 | VOL_HARM_MINb10 | 3sec 10th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B6F | 0x7B70 | 31599 | 31600 | VOL_HARM_MINb11 | 3sec 11st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B71 | 0x7B72 | 31601 | 31602 | VOL_HARM_MINb12 | 3sec 12nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B73 | 0x7B74 | 31603 | 31604 | VOL_HARM_MINb13 | 3sec 13rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B75 | 0x7B76 | 31605 | 31606 | VOL_HARM_MINb14 | 3sec 14th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B77 | 0x7B78 | 31607 | 31608 | VOL_HARM_MINb15 | 3sec 15th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B79 | 0x7B7A | 31609 | 31610 | VOL_HARM_MINb16 | 3sec 16th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B7B | 0x7B7C | 31611 | 31612 | VOL_HARM_MINb17 | 3sec 17th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B7D | 0x7B7E | 31613 | 31614 | VOL_HARM_MINb18 | 3sec 18th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B7F | 0x7B80 | 31615 | 31616 | VOL_HARM_MINb19 | 3sec 19th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B81 | 0x7B82 | 31617 | 31618 | VOL_HARM_MINb20 | 3sec 20th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B83 | 0x7B84 | 31619 | 31620 | VOL_HARM_MINb21 | 3sec 21st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B85 | 0x7B86 | 31621 | 31622 | VOL_HARM_MINb22 | 3sec 22nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B87 | 0x7B88 | 31623 | 31624 | VOL_HARM_MINb23 | 3sec 23rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B89 | 0x7B8A | 31625 | 31626 | VOL_HARM_MINb24 | 3sec 24th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B8B | 0x7B8C | 31627 | 31628 | VOL_HARM_MINb25 | 3sec 25th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B8D | 0x7B8E | 31629 | 31630 | VOL_HARM_MINb26 | 3sec 26th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B8F | 0x7B90 | 31631 | 31632 | VOL_HARM_MINb27 | 3sec 27th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B91 | 0x7B92 | 31633 | 31634 | VOL_HARM_MINb28 | 3sec 28th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B93 | 0x7B94 | 31635 | 31636 | VOL_HARM_MINb29 | 3sec 29th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B95 | 0x7B96 | 31637 | 31638 | VOL_HARM_MINb30 | 3sec 30th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B97 | 0x7B98 | 31639 | 31640 | VOL_HARM_MINb31 | 3sec 31st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B99 | 0x7B9A | 31641 | 31642 | VOL_HARM_MINb32 | 3sec 32nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B9B | 0x7B9C | 31643 | 31644 | VOL_HARM_MINb33 | 3sec 33rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B9D | 0x7B9E | 31645 | 31646 | VOL_HARM_MINb34 | 3sec 34th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7B9F | 0x7BA0 | 31647 | 31648 | VOL_HARM_MINb35 | 3sec 35th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BA1 | 0x7BA2 | 31649 | 31650 | VOL_HARM_MINb36 | 3sec 36th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BA3 | 0x7BA4 | 31651 | 31652 | VOL_HARM_MINb37 | 3sec 37th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BA5 | 0x7BA6 | 31653 | 31654 | VOL_HARM_MINb38 | 3sec 38th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BA7 | 0x7BA8 | 31655 | 31656 | VOL_HARM_MINb39 | 3sec 39th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BA9 | 0x7BAA | 31657 | 31658 | VOL_HARM_MINb40 | 3sec 40th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BAB | 0x7BAC | 31659 | 31660 | VOL_HARM_MINb41 | 3sec 41st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BAD | 0x7BAE | 31661 | 31662 | VOL_HARM_MINb42 | 3sec 42nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BAF | 0x7BB0 | 31663 | 31664 | VOL_HARM_MINb43 | 3sec 43rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BB1 | 0x7BB2 | 31665 | 31666 | VOL_HARM_MINb44 | 3sec 44th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BB3 | 0x7BB4 | 31667 | 31668 | VOL_HARM_MINb45 | 3sec 45th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BB5 | 0x7BB6 | 31669 | 31670 | VOL_HARM_MINb46 | 3sec 46th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BB7 | 0x7BB8 | 31671 | 31672 | VOL_HARM_MINb47 | 3sec 47th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BB9 | 0x7BBA | 31673 | 31674 | VOL_HARM_MINb48 | 3sec 48th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BBB | 0x7BBC | 31675 | 31676 | VOL_HARM_MINb49 | 3sec 49th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BBD | 0x7BBE | 31677 | 31678 | VOL_HARM_MINb50 | 3sec 50th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x7BBF | 0x7BC0 | 31679 | 31680 | VOL_HARM_MINc2 | 3sec 2nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BC1 | 0x7BC2 | 31681 | 31682 | VOL_HARM_MINc3 | 3sec 3rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BC3 | 0x7BC4 | 31683 | 31684 | VOL_HARM_MINc4 | 3sec 4th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BC5 | 0x7BC6 | 31685 | 31686 | VOL_HARM_MINc5 | 3sec 5th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BC7 | 0x7BC8 | 31687 | 31688 | VOL_HARM_MINc6 | 3sec 6th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BC9 | 0x7BCA | 31689 | 31690 | VOL_HARM_MINc7 | 3sec 7th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BCB | 0x7BCC | 31691 | 31692 | VOL_HARM_MINc8 | 3sec 8th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BCD | 0x7BCE | 31693 | 31694 | VOL_HARM_MINc9 | 3sec 9th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BCF | 0x7BD0 | 31695 | 31696 | VOL_HARM_MINc10 | 3sec 10th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BD1 | 0x7BD2 | 31697 | 31698 | VOL_HARM_MINc11 | 3sec 11st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BD3 | 0x7BD4 | 31699 | 31700 | VOL_HARM_MINc12 | 3sec 12nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BD5 | 0x7BD6 | 31701 | 31702 | VOL_HARM_MINc13 | 3sec 13rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BD7 | 0x7BD8 | 31703 | 31704 | VOL_HARM_MINc14 | 3sec 14th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BD9 | 0x7BDA | 31705 | 31706 | VOL_HARM_MINc15 | 3sec 15th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BDB | 0x7BDC | 31707 | 31708 | VOL_HARM_MINc16 | 3sec 16th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BDD | 0x7BDE | 31709 | 31710 | VOL_HARM_MINc17 | 3sec 17th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BDF | 0x7BE0 | 31711 | 31712 | VOL_HARM_MINc18 | 3sec 18th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BE1 | 0x7BE2 | 31713 | 31714 | VOL_HARM_MINc19 | 3sec 19th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BE3 | 0x7BE4 | 31715 | 31716 | VOL_HARM_MINc20 | 3sec 20th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BE5 | 0x7BE6 | 31717 | 31718 | VOL_HARM_MINc21 | 3sec 21st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BE7 | 0x7BE8 | 31719 | 31720 | VOL_HARM_MINc22 | 3sec 22nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BE9 | 0x7BEA | 31721 | 31722 | VOL_HARM_MINc23 | 3sec 23rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BEB | 0x7BEC | 31723 | 31724 | VOL_HARM_MINc24 | 3sec 24th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BED | 0x7BEE | 31725 | 31726 | VOL_HARM_MINc25 | 3sec 25th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BEF | 0x7BF0 | 31727 | 31728 | VOL_HARM_MINc26 | 3sec 26th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BF1 | 0x7BF2 | 31729 | 31730 | VOL_HARM_MINc27 | 3sec 27th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BF3 | 0x7BF4 | 31731 | 31732 | VOL_HARM_MINc28 | 3sec 28th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BF5 | 0x7BF6 | 31733 | 31734 | VOL_HARM_MINc29 | 3sec 29th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BF7 | 0x7BF8 | 31735 | 31736 | VOL_HARM_MINc30 | 3sec 30th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BF9 | 0x7BFA | 31737 | 31738 | VOL_HARM_MINc31 | 3sec 31st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BFB | 0x7BFC | 31739 | 31740 | VOL_HARM_MINc32 | 3sec 32nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BFD | 0x7BFE | 31741 | 31742 | VOL_HARM_MINc33 | 3sec 33rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7BFF | 0x7C00 | 31743 | 31744 | VOL_HARM_MINc34 | 3sec 34th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C01 | 0x7C02 | 31745 | 31746 | VOL_HARM_MINc35 | 3sec 35th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C03 | 0x7C04 | 31747 | 31748 | VOL_HARM_MINc36 | 3sec 36th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C05 | 0x7C06 | 31749 | 31750 | VOL_HARM_MINc37 | 3sec 37th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C07 | 0x7C08 | 31751 | 31752 | VOL_HARM_MINc38 | 3sec 38th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C09 | 0x7C0A | 31753 | 31754 | VOL_HARM_MINc39 | 3sec 39th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C0B | 0x7C0C | 31755 | 31756 | VOL_HARM_MINc40 | 3sec 40th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C0D | 0x7C0E | 31757 | 31758 | VOL_HARM_MINc41 | 3sec 41st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C0F | 0x7C10 | 31759 | 31760 | VOL_HARM_MINc42 | 3sec 42nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C11 | 0x7C12 | 31761 | 31762 | VOL_HARM_MINc43 | 3sec 43rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C13 | 0x7C14 | 31763 | 31764 | VOL_HARM_MINc44 | 3sec 44th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C15 | 0x7C16 | 31765 | 31766 | VOL_HARM_MINc45 | 3sec 45th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C17 | 0x7C18 | 31767 | 31768 | VOL_HARM_MINc46 | 3sec 46th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C19 | 0x7C1A | 31769 | 31770 | VOL_HARM_MINc47 | 3sec 47th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C1B | 0x7C1C | 31771 | 31772 | VOL_HARM_MINc48 | 3sec 48th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C1D | 0x7C1E | 31773 | 31774 | VOL_HARM_MINc49 | 3sec 49th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C1F | 0x7C20 | 31775 | 31776 | VOL_HARM_MINc50 | 3sec 50th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x7C21 | 0x7C22 | 31777 | 31778 | VOL_HARM_AVGa2 | 3sec 2nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C23 | 0x7C24 | 31779 | 31780 | VOL_HARM_AVGa3 | 3sec 3rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C25 | 0x7C26 | 31781 | 31782 | VOL_HARM_AVGa4 | 3sec 4th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C27 | 0x7C28 | 31783 | 31784 | VOL_HARM_AVGa5 | 3sec 5th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C29 | 0x7C2A | 31785 | 31786 | VOL_HARM_AVGa6 | 3sec 6th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C2B | 0x7C2C | 31787 | 31788 | VOL_HARM_AVGa7 | 3sec 7th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C2D | 0x7C2E | 31789 | 31790 | VOL_HARM_AVGa8 | 3sec 8th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C2F | 0x7C30 | 31791 | 31792 | VOL_HARM_AVGa9 | 3sec 9th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C31 | 0x7C32 | 31793 | 31794 | VOL_HARM_AVGa10 | 3sec 10th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C33 | 0x7C34 | 31795 | 31796 | VOL_HARM_AVGa11 | 3sec 11st Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C35 | 0x7C36 | 31797 | 31798 | VOL_HARM_AVGa12 | 3sec 12nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C37 | 0x7C38 | 31799 | 31800 | VOL_HARM_AVGa13 | 3sec 13rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C39 | 0x7C3A | 31801 | 31802 | VOL_HARM_AVGa14 | 3sec 14th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C3B | 0x7C3C | 31803 | 31804 | VOL_HARM_AVGa15 | 3sec 15th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C3D | 0x7C3E | 31805 | 31806 | VOL_HARM_AVGa16 | 3sec 16th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C3F | 0x7C40 | 31807 | 31808 | VOL_HARM_AVGa17 | 3sec 17th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C41 | 0x7C42 | 31809 | 31810 | VOL_HARM_AVGa18 | 3sec 18th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C43 | 0x7C44 | 31811 | 31812 | VOL_HARM_AVGa19 | 3sec 19th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C45 | 0x7C46 | 31813 | 31814 | VOL_HARM_AVGa20 | 3sec 20th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C47 | 0x7C48 | 31815 | 31816 | VOL_HARM_AVGa21 | 3sec 21st Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C49 | 0x7C4A | 31817 | 31818 | VOL_HARM_AVGa22 | 3sec 22nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C4B | 0x7C4C | 31819 | 31820 | VOL_HARM_AVGa23 | 3sec 23rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C4D | 0x7C4E | 31821 | 31822 | VOL_HARM_AVGa24 | 3sec 24th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C4F | 0x7C50 | 31823 | 31824 | VOL_HARM_AVGa25 | 3sec 25th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C51 | 0x7C52 | 31825 | 31826 | VOL_HARM_AVGa26 | 3sec 26th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C53 | 0x7C54 | 31827 | 31828 | VOL_HARM_AVGa27 | 3sec 27th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C55 | 0x7C56 | 31829 | 31830 | VOL_HARM_AVGa28 | 3sec 28th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C57 | 0x7C58 | 31831 | 31832 | VOL_HARM_AVGa29 | 3sec 29th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C59 | 0x7C5A | 31833 | 31834 | VOL_HARM_AVGa30 | 3sec 30th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C5B | 0x7C5C | 31835 | 31836 | VOL_HARM_AVGa31 | 3sec 31st Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C5D | 0x7C5E | 31837 | 31838 | VOL_HARM_AVGa32 | 3sec 32nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C5F | 0x7C60 | 31839 | 31840 | VOL_HARM_AVGa33 | 3sec 33rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C61 | 0x7C62 | 31841 | 31842 | VOL_HARM_AVGa34 | 3sec 34th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C63 | 0x7C64 | 31843 | 31844 | VOL_HARM_AVGa35 | 3sec 35th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C65 | 0x7C66 | 31845 | 31846 | VOL_HARM_AVGa36 | 3sec 36th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C67 | 0x7C68 | 31847 | 31848 | VOL_HARM_AVGa37 | 3sec 37th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C69 | 0x7C6A | 31849 | 31850 | VOL_HARM_AVGa38 | 3sec 38th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C6B | 0x7C6C | 31851 | 31852 | VOL_HARM_AVGa39 | 3sec 39th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C6D | 0x7C6E | 31853 | 31854 | VOL_HARM_AVGa40 | 3sec 40th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C6F | 0x7C70 | 31855 | 31856 | VOL_HARM_AVGa41 | 3sec 41st Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C71 | 0x7C72 | 31857 | 31858 | VOL_HARM_AVGa42 | 3sec 42nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C73 | 0x7C74 | 31859 | 31860 | VOL_HARM_AVGa43 | 3sec 43rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C75 | 0x7C76 | 31861 | 31862 | VOL_HARM_AVGa44 | 3sec 44th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C77 | 0x7C78 | 31863 | 31864 | VOL_HARM_AVGa45 | 3sec 45th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C79 | 0x7C7A | 31865 | 31866 | VOL_HARM_AVGa46 | 3sec 46th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C7B | 0x7C7C | 31867 | 31868 | VOL_HARM_AVGa47 | 3sec 47th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C7D | 0x7C7E | 31869 | 31870 | VOL_HARM_AVGa48 | 3sec 48th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C7F | 0x7C80 | 31871 | 31872 | VOL_HARM_AVGa49 | 3sec 49th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C81 | 0x7C82 | 31873 | 31874 | VOL_HARM_AVGa50 | 3sec 50th Phase A Voltage Harmonics Average Value | float | 2 | R
0x7C83 | 0x7C84 | 31875 | 31876 | VOL_HARM_AVGb2 | 3sec 2nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C85 | 0x7C86 | 31877 | 31878 | VOL_HARM_AVGb3 | 3sec 3rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C87 | 0x7C88 | 31879 | 31880 | VOL_HARM_AVGb4 | 3sec 4th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C89 | 0x7C8A | 31881 | 31882 | VOL_HARM_AVGb5 | 3sec 5th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C8B | 0x7C8C | 31883 | 31884 | VOL_HARM_AVGb6 | 3sec 6th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C8D | 0x7C8E | 31885 | 31886 | VOL_HARM_AVGb7 | 3sec 7th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C8F | 0x7C90 | 31887 | 31888 | VOL_HARM_AVGb8 | 3sec 8th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C91 | 0x7C92 | 31889 | 31890 | VOL_HARM_AVGb9 | 3sec 9th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C93 | 0x7C94 | 31891 | 31892 | VOL_HARM_AVGb10 | 3sec 10th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C95 | 0x7C96 | 31893 | 31894 | VOL_HARM_AVGb11 | 3sec 11st Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C97 | 0x7C98 | 31895 | 31896 | VOL_HARM_AVGb12 | 3sec 12nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C99 | 0x7C9A | 31897 | 31898 | VOL_HARM_AVGb13 | 3sec 13rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C9B | 0x7C9C | 31899 | 31900 | VOL_HARM_AVGb14 | 3sec 14th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C9D | 0x7C9E | 31901 | 31902 | VOL_HARM_AVGb15 | 3sec 15th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7C9F | 0x7CA0 | 31903 | 31904 | VOL_HARM_AVGb16 | 3sec 16th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CA1 | 0x7CA2 | 31905 | 31906 | VOL_HARM_AVGb17 | 3sec 17th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CA3 | 0x7CA4 | 31907 | 31908 | VOL_HARM_AVGb18 | 3sec 18th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CA5 | 0x7CA6 | 31909 | 31910 | VOL_HARM_AVGb19 | 3sec 19th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CA7 | 0x7CA8 | 31911 | 31912 | VOL_HARM_AVGb20 | 3sec 20th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CA9 | 0x7CAA | 31913 | 31914 | VOL_HARM_AVGb21 | 3sec 21st Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CAB | 0x7CAC | 31915 | 31916 | VOL_HARM_AVGb22 | 3sec 22nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CAD | 0x7CAE | 31917 | 31918 | VOL_HARM_AVGb23 | 3sec 23rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CAF | 0x7CB0 | 31919 | 31920 | VOL_HARM_AVGb24 | 3sec 24th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CB1 | 0x7CB2 | 31921 | 31922 | VOL_HARM_AVGb25 | 3sec 25th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CB3 | 0x7CB4 | 31923 | 31924 | VOL_HARM_AVGb26 | 3sec 26th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CB5 | 0x7CB6 | 31925 | 31926 | VOL_HARM_AVGb27 | 3sec 27th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CB7 | 0x7CB8 | 31927 | 31928 | VOL_HARM_AVGb28 | 3sec 28th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CB9 | 0x7CBA | 31929 | 31930 | VOL_HARM_AVGb29 | 3sec 29th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CBB | 0x7CBC | 31931 | 31932 | VOL_HARM_AVGb30 | 3sec 30th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CBD | 0x7CBE | 31933 | 31934 | VOL_HARM_AVGb31 | 3sec 31st Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CBF | 0x7CC0 | 31935 | 31936 | VOL_HARM_AVGb32 | 3sec 32nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CC1 | 0x7CC2 | 31937 | 31938 | VOL_HARM_AVGb33 | 3sec 33rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CC3 | 0x7CC4 | 31939 | 31940 | VOL_HARM_AVGb34 | 3sec 34th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CC5 | 0x7CC6 | 31941 | 31942 | VOL_HARM_AVGb35 | 3sec 35th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CC7 | 0x7CC8 | 31943 | 31944 | VOL_HARM_AVGb36 | 3sec 36th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CC9 | 0x7CCA | 31945 | 31946 | VOL_HARM_AVGb37 | 3sec 37th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CCB | 0x7CCC | 31947 | 31948 | VOL_HARM_AVGb38 | 3sec 38th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CCD | 0x7CCE | 31949 | 31950 | VOL_HARM_AVGb39 | 3sec 39th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CCF | 0x7CD0 | 31951 | 31952 | VOL_HARM_AVGb40 | 3sec 40th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CD1 | 0x7CD2 | 31953 | 31954 | VOL_HARM_AVGb41 | 3sec 41st Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CD3 | 0x7CD4 | 31955 | 31956 | VOL_HARM_AVGb42 | 3sec 42nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CD5 | 0x7CD6 | 31957 | 31958 | VOL_HARM_AVGb43 | 3sec 43rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CD7 | 0x7CD8 | 31959 | 31960 | VOL_HARM_AVGb44 | 3sec 44th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CD9 | 0x7CDA | 31961 | 31962 | VOL_HARM_AVGb45 | 3sec 45th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CDB | 0x7CDC | 31963 | 31964 | VOL_HARM_AVGb46 | 3sec 46th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CDD | 0x7CDE | 31965 | 31966 | VOL_HARM_AVGb47 | 3sec 47th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CDF | 0x7CE0 | 31967 | 31968 | VOL_HARM_AVGb48 | 3sec 48th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CE1 | 0x7CE2 | 31969 | 31970 | VOL_HARM_AVGb49 | 3sec 49th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CE3 | 0x7CE4 | 31971 | 31972 | VOL_HARM_AVGb50 | 3sec 50th Phase B Voltage Harmonics Average Value | float | 2 | R
0x7CE5 | 0x7CE6 | 31973 | 31974 | VOL_HARM_AVGc2 | 3sec 2nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CE7 | 0x7CE8 | 31975 | 31976 | VOL_HARM_AVGc3 | 3sec 3rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CE9 | 0x7CEA | 31977 | 31978 | VOL_HARM_AVGc4 | 3sec 4th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CEB | 0x7CEC | 31979 | 31980 | VOL_HARM_AVGc5 | 3sec 5th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CED | 0x7CEE | 31981 | 31982 | VOL_HARM_AVGc6 | 3sec 6th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CEF | 0x7CF0 | 31983 | 31984 | VOL_HARM_AVGc7 | 3sec 7th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CF1 | 0x7CF2 | 31985 | 31986 | VOL_HARM_AVGc8 | 3sec 8th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CF3 | 0x7CF4 | 31987 | 31988 | VOL_HARM_AVGc9 | 3sec 9th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CF5 | 0x7CF6 | 31989 | 31990 | VOL_HARM_AVGc10 | 3sec 10th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CF7 | 0x7CF8 | 31991 | 31992 | VOL_HARM_AVGc11 | 3sec 11st Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CF9 | 0x7CFA | 31993 | 31994 | VOL_HARM_AVGc12 | 3sec 12nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CFB | 0x7CFC | 31995 | 31996 | VOL_HARM_AVGc13 | 3sec 13rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CFD | 0x7CFE | 31997 | 31998 | VOL_HARM_AVGc14 | 3sec 14th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7CFF | 0x7D00 | 31999 | 32000 | VOL_HARM_AVGc15 | 3sec 15th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D01 | 0x7D02 | 32001 | 32002 | VOL_HARM_AVGc16 | 3sec 16th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D03 | 0x7D04 | 32003 | 32004 | VOL_HARM_AVGc17 | 3sec 17th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D05 | 0x7D06 | 32005 | 32006 | VOL_HARM_AVGc18 | 3sec 18th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D07 | 0x7D08 | 32007 | 32008 | VOL_HARM_AVGc19 | 3sec 19th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D09 | 0x7D0A | 32009 | 32010 | VOL_HARM_AVGc20 | 3sec 20th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D0B | 0x7D0C | 32011 | 32012 | VOL_HARM_AVGc21 | 3sec 21st Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D0D | 0x7D0E | 32013 | 32014 | VOL_HARM_AVGc22 | 3sec 22nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D0F | 0x7D10 | 32015 | 32016 | VOL_HARM_AVGc23 | 3sec 23rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D11 | 0x7D12 | 32017 | 32018 | VOL_HARM_AVGc24 | 3sec 24th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D13 | 0x7D14 | 32019 | 32020 | VOL_HARM_AVGc25 | 3sec 25th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D15 | 0x7D16 | 32021 | 32022 | VOL_HARM_AVGc26 | 3sec 26th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D17 | 0x7D18 | 32023 | 32024 | VOL_HARM_AVGc27 | 3sec 27th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D19 | 0x7D1A | 32025 | 32026 | VOL_HARM_AVGc28 | 3sec 28th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D1B | 0x7D1C | 32027 | 32028 | VOL_HARM_AVGc29 | 3sec 29th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D1D | 0x7D1E | 32029 | 32030 | VOL_HARM_AVGc30 | 3sec 30th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D1F | 0x7D20 | 32031 | 32032 | VOL_HARM_AVGc31 | 3sec 31st Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D21 | 0x7D22 | 32033 | 32034 | VOL_HARM_AVGc32 | 3sec 32nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D23 | 0x7D24 | 32035 | 32036 | VOL_HARM_AVGc33 | 3sec 33rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D25 | 0x7D26 | 32037 | 32038 | VOL_HARM_AVGc34 | 3sec 34th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D27 | 0x7D28 | 32039 | 32040 | VOL_HARM_AVGc35 | 3sec 35th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D29 | 0x7D2A | 32041 | 32042 | VOL_HARM_AVGc36 | 3sec 36th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D2B | 0x7D2C | 32043 | 32044 | VOL_HARM_AVGc37 | 3sec 37th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D2D | 0x7D2E | 32045 | 32046 | VOL_HARM_AVGc38 | 3sec 38th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D2F | 0x7D30 | 32047 | 32048 | VOL_HARM_AVGc39 | 3sec 39th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D31 | 0x7D32 | 32049 | 32050 | VOL_HARM_AVGc40 | 3sec 40th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D33 | 0x7D34 | 32051 | 32052 | VOL_HARM_AVGc41 | 3sec 41st Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D35 | 0x7D36 | 32053 | 32054 | VOL_HARM_AVGc42 | 3sec 42nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D37 | 0x7D38 | 32055 | 32056 | VOL_HARM_AVGc43 | 3sec 43rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D39 | 0x7D3A | 32057 | 32058 | VOL_HARM_AVGc44 | 3sec 44th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D3B | 0x7D3C | 32059 | 32060 | VOL_HARM_AVGc45 | 3sec 45th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D3D | 0x7D3E | 32061 | 32062 | VOL_HARM_AVGc46 | 3sec 46th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D3F | 0x7D40 | 32063 | 32064 | VOL_HARM_AVGc47 | 3sec 47th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D41 | 0x7D42 | 32065 | 32066 | VOL_HARM_AVGc48 | 3sec 48th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D43 | 0x7D44 | 32067 | 32068 | VOL_HARM_AVGc49 | 3sec 49th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D45 | 0x7D46 | 32069 | 32070 | VOL_HARM_AVGc50 | 3sec 50th Phase C Voltage Harmonics Average Value | float | 2 | R
0x7D47 | 0x7D48 | 32071 | 32072 | TDD_MAXa | 3sec Phase A TDD Maximum Value | float | 2 | R
0x7D49 | 0x7D4A | 32073 | 32074 | TDD_MAXb | 3sec Phase B TDD Maximum Value | float | 2 | R
0x7D4B | 0x7D4C | 32075 | 32076 | TDD_MAXc | 3sec Phase C TDD Maximum Value | float | 2 | R
0x7D4D | 0x7D4E | 32077 | 32078 | TDD_MINa | 3sec Phase A TDD Minimum Value | float | 2 | R
0x7D4F | 0x7D50 | 32079 | 32080 | TDD_MINb | 3sec Phase B TDD Minimum Value | float | 2 | R
0x7D51 | 0x7D52 | 32081 | 32082 | TDD_MINc | 3sec Phase C TDD Minimum Value | float | 2 | R
0x7D53 | 0x7D54 | 32083 | 32084 | TDD_AVGa | 3sec Phase A TDD Average Value | float | 2 | R
0x7D55 | 0x7D56 | 32085 | 32086 | TDD_AVGb | 3sec Phase B TDD Average Value | float | 2 | R
0x7D57 | 0x7D58 | 32087 | 32088 | TDD_AVGc | 3sec Phase C TDD Average Value | float | 2 | R
0x7D59 | 0x7D5A | 32089 | 32090 | CUR_HARM_MAXa2 | 3sec 2nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D5B | 0x7D5C | 32091 | 32092 | CUR_HARM_MAXa3 | 3sec 3rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D5D | 0x7D5E | 32093 | 32094 | CUR_HARM_MAXa4 | 3sec 4th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D5F | 0x7D60 | 32095 | 32096 | CUR_HARM_MAXa5 | 3sec 5th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D61 | 0x7D62 | 32097 | 32098 | CUR_HARM_MAXa6 | 3sec 6th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D63 | 0x7D64 | 32099 | 32100 | CUR_HARM_MAXa7 | 3sec 7th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D65 | 0x7D66 | 32101 | 32102 | CUR_HARM_MAXa8 | 3sec 8th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D67 | 0x7D68 | 32103 | 32104 | CUR_HARM_MAXa9 | 3sec 9th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D69 | 0x7D6A | 32105 | 32106 | CUR_HARM_MAXa10 | 3sec 10th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D6B | 0x7D6C | 32107 | 32108 | CUR_HARM_MAXa11 | 3sec 11st Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D6D | 0x7D6E | 32109 | 32110 | CUR_HARM_MAXa12 | 3sec 12nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D6F | 0x7D70 | 32111 | 32112 | CUR_HARM_MAXa13 | 3sec 13rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D71 | 0x7D72 | 32113 | 32114 | CUR_HARM_MAXa14 | 3sec 14th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D73 | 0x7D74 | 32115 | 32116 | CUR_HARM_MAXa15 | 3sec 15th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D75 | 0x7D76 | 32117 | 32118 | CUR_HARM_MAXa16 | 3sec 16th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D77 | 0x7D78 | 32119 | 32120 | CUR_HARM_MAXa17 | 3sec 17th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D79 | 0x7D7A | 32121 | 32122 | CUR_HARM_MAXa18 | 3sec 18th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D7B | 0x7D7C | 32123 | 32124 | CUR_HARM_MAXa19 | 3sec 19th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D7D | 0x7D7E | 32125 | 32126 | CUR_HARM_MAXa20 | 3sec 20th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D7F | 0x7D80 | 32127 | 32128 | CUR_HARM_MAXa21 | 3sec 21st Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D81 | 0x7D82 | 32129 | 32130 | CUR_HARM_MAXa22 | 3sec 22nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D83 | 0x7D84 | 32131 | 32132 | CUR_HARM_MAXa23 | 3sec 23rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D85 | 0x7D86 | 32133 | 32134 | CUR_HARM_MAXa24 | 3sec 24th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D87 | 0x7D88 | 32135 | 32136 | CUR_HARM_MAXa25 | 3sec 25th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D89 | 0x7D8A | 32137 | 32138 | CUR_HARM_MAXa26 | 3sec 26th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D8B | 0x7D8C | 32139 | 32140 | CUR_HARM_MAXa27 | 3sec 27th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D8D | 0x7D8E | 32141 | 32142 | CUR_HARM_MAXa28 | 3sec 28th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D8F | 0x7D90 | 32143 | 32144 | CUR_HARM_MAXa29 | 3sec 29th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D91 | 0x7D92 | 32145 | 32146 | CUR_HARM_MAXa30 | 3sec 30th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D93 | 0x7D94 | 32147 | 32148 | CUR_HARM_MAXa31 | 3sec 31st Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D95 | 0x7D96 | 32149 | 32150 | CUR_HARM_MAXa32 | 3sec 32nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D97 | 0x7D98 | 32151 | 32152 | CUR_HARM_MAXa33 | 3sec 33rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D99 | 0x7D9A | 32153 | 32154 | CUR_HARM_MAXa34 | 3sec 34th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D9B | 0x7D9C | 32155 | 32156 | CUR_HARM_MAXa35 | 3sec 35th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D9D | 0x7D9E | 32157 | 32158 | CUR_HARM_MAXa36 | 3sec 36th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7D9F | 0x7DA0 | 32159 | 32160 | CUR_HARM_MAXa37 | 3sec 37th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DA1 | 0x7DA2 | 32161 | 32162 | CUR_HARM_MAXa38 | 3sec 38th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DA3 | 0x7DA4 | 32163 | 32164 | CUR_HARM_MAXa39 | 3sec 39th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DA5 | 0x7DA6 | 32165 | 32166 | CUR_HARM_MAXa40 | 3sec 40th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DA7 | 0x7DA8 | 32167 | 32168 | CUR_HARM_MAXa41 | 3sec 41st Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DA9 | 0x7DAA | 32169 | 32170 | CUR_HARM_MAXa42 | 3sec 42nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DAB | 0x7DAC | 32171 | 32172 | CUR_HARM_MAXa43 | 3sec 43rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DAD | 0x7DAE | 32173 | 32174 | CUR_HARM_MAXa44 | 3sec 44th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DAF | 0x7DB0 | 32175 | 32176 | CUR_HARM_MAXa45 | 3sec 45th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DB1 | 0x7DB2 | 32177 | 32178 | CUR_HARM_MAXa46 | 3sec 46th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DB3 | 0x7DB4 | 32179 | 32180 | CUR_HARM_MAXa47 | 3sec 47th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DB5 | 0x7DB6 | 32181 | 32182 | CUR_HARM_MAXa48 | 3sec 48th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DB7 | 0x7DB8 | 32183 | 32184 | CUR_HARM_MAXa49 | 3sec 49th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DB9 | 0x7DBA | 32185 | 32186 | CUR_HARM_MAXa50 | 3sec 50th Phase A Current Harmonics Maximum Value | float | 2 | R
0x7DBB | 0x7DBC | 32187 | 32188 | CUR_HARM_MAXb2 | 3sec 2nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DBD | 0x7DBE | 32189 | 32190 | CUR_HARM_MAXb3 | 3sec 3rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DBF | 0x7DC0 | 32191 | 32192 | CUR_HARM_MAXb4 | 3sec 4th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DC1 | 0x7DC2 | 32193 | 32194 | CUR_HARM_MAXb5 | 3sec 5th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DC3 | 0x7DC4 | 32195 | 32196 | CUR_HARM_MAXb6 | 3sec 6th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DC5 | 0x7DC6 | 32197 | 32198 | CUR_HARM_MAXb7 | 3sec 7th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DC7 | 0x7DC8 | 32199 | 32200 | CUR_HARM_MAXb8 | 3sec 8th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DC9 | 0x7DCA | 32201 | 32202 | CUR_HARM_MAXb9 | 3sec 9th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DCB | 0x7DCC | 32203 | 32204 | CUR_HARM_MAXb10 | 3sec 10th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DCD | 0x7DCE | 32205 | 32206 | CUR_HARM_MAXb11 | 3sec 11st Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DCF | 0x7DD0 | 32207 | 32208 | CUR_HARM_MAXb12 | 3sec 12nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DD1 | 0x7DD2 | 32209 | 32210 | CUR_HARM_MAXb13 | 3sec 13rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DD3 | 0x7DD4 | 32211 | 32212 | CUR_HARM_MAXb14 | 3sec 14th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DD5 | 0x7DD6 | 32213 | 32214 | CUR_HARM_MAXb15 | 3sec 15th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DD7 | 0x7DD8 | 32215 | 32216 | CUR_HARM_MAXb16 | 3sec 16th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DD9 | 0x7DDA | 32217 | 32218 | CUR_HARM_MAXb17 | 3sec 17th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DDB | 0x7DDC | 32219 | 32220 | CUR_HARM_MAXb18 | 3sec 18th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DDD | 0x7DDE | 32221 | 32222 | CUR_HARM_MAXb19 | 3sec 19th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DDF | 0x7DE0 | 32223 | 32224 | CUR_HARM_MAXb20 | 3sec 20th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DE1 | 0x7DE2 | 32225 | 32226 | CUR_HARM_MAXb21 | 3sec 21st Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DE3 | 0x7DE4 | 32227 | 32228 | CUR_HARM_MAXb22 | 3sec 22nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DE5 | 0x7DE6 | 32229 | 32230 | CUR_HARM_MAXb23 | 3sec 23rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DE7 | 0x7DE8 | 32231 | 32232 | CUR_HARM_MAXb24 | 3sec 24th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DE9 | 0x7DEA | 32233 | 32234 | CUR_HARM_MAXb25 | 3sec 25th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DEB | 0x7DEC | 32235 | 32236 | CUR_HARM_MAXb26 | 3sec 26th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DED | 0x7DEE | 32237 | 32238 | CUR_HARM_MAXb27 | 3sec 27th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DEF | 0x7DF0 | 32239 | 32240 | CUR_HARM_MAXb28 | 3sec 28th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DF1 | 0x7DF2 | 32241 | 32242 | CUR_HARM_MAXb29 | 3sec 29th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DF3 | 0x7DF4 | 32243 | 32244 | CUR_HARM_MAXb30 | 3sec 30th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DF5 | 0x7DF6 | 32245 | 32246 | CUR_HARM_MAXb31 | 3sec 31st Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DF7 | 0x7DF8 | 32247 | 32248 | CUR_HARM_MAXb32 | 3sec 32nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DF9 | 0x7DFA | 32249 | 32250 | CUR_HARM_MAXb33 | 3sec 33rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DFB | 0x7DFC | 32251 | 32252 | CUR_HARM_MAXb34 | 3sec 34th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DFD | 0x7DFE | 32253 | 32254 | CUR_HARM_MAXb35 | 3sec 35th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7DFF | 0x7E00 | 32255 | 32256 | CUR_HARM_MAXb36 | 3sec 36th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E01 | 0x7E02 | 32257 | 32258 | CUR_HARM_MAXb37 | 3sec 37th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E03 | 0x7E04 | 32259 | 32260 | CUR_HARM_MAXb38 | 3sec 38th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E05 | 0x7E06 | 32261 | 32262 | CUR_HARM_MAXb39 | 3sec 39th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E07 | 0x7E08 | 32263 | 32264 | CUR_HARM_MAXb40 | 3sec 40th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E09 | 0x7E0A | 32265 | 32266 | CUR_HARM_MAXb41 | 3sec 41st Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E0B | 0x7E0C | 32267 | 32268 | CUR_HARM_MAXb42 | 3sec 42nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E0D | 0x7E0E | 32269 | 32270 | CUR_HARM_MAXb43 | 3sec 43rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E0F | 0x7E10 | 32271 | 32272 | CUR_HARM_MAXb44 | 3sec 44th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E11 | 0x7E12 | 32273 | 32274 | CUR_HARM_MAXb45 | 3sec 45th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E13 | 0x7E14 | 32275 | 32276 | CUR_HARM_MAXb46 | 3sec 46th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E15 | 0x7E16 | 32277 | 32278 | CUR_HARM_MAXb47 | 3sec 47th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E17 | 0x7E18 | 32279 | 32280 | CUR_HARM_MAXb48 | 3sec 48th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E19 | 0x7E1A | 32281 | 32282 | CUR_HARM_MAXb49 | 3sec 49th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E1B | 0x7E1C | 32283 | 32284 | CUR_HARM_MAXb50 | 3sec 50th Phase B Current Harmonics Maximum Value | float | 2 | R
0x7E1D | 0x7E1E | 32285 | 32286 | CUR_HARM_MAXc2 | 3sec 2nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E1F | 0x7E20 | 32287 | 32288 | CUR_HARM_MAXc3 | 3sec 3rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E21 | 0x7E22 | 32289 | 32290 | CUR_HARM_MAXc4 | 3sec 4th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E23 | 0x7E24 | 32291 | 32292 | CUR_HARM_MAXc5 | 3sec 5th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E25 | 0x7E26 | 32293 | 32294 | CUR_HARM_MAXc6 | 3sec 6th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E27 | 0x7E28 | 32295 | 32296 | CUR_HARM_MAXc7 | 3sec 7th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E29 | 0x7E2A | 32297 | 32298 | CUR_HARM_MAXc8 | 3sec 8th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E2B | 0x7E2C | 32299 | 32300 | CUR_HARM_MAXc9 | 3sec 9th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E2D | 0x7E2E | 32301 | 32302 | CUR_HARM_MAXc10 | 3sec 10th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E2F | 0x7E30 | 32303 | 32304 | CUR_HARM_MAXc11 | 3sec 11st Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E31 | 0x7E32 | 32305 | 32306 | CUR_HARM_MAXc12 | 3sec 12nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E33 | 0x7E34 | 32307 | 32308 | CUR_HARM_MAXc13 | 3sec 13rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E35 | 0x7E36 | 32309 | 32310 | CUR_HARM_MAXc14 | 3sec 14th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E37 | 0x7E38 | 32311 | 32312 | CUR_HARM_MAXc15 | 3sec 15th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E39 | 0x7E3A | 32313 | 32314 | CUR_HARM_MAXc16 | 3sec 16th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E3B | 0x7E3C | 32315 | 32316 | CUR_HARM_MAXc17 | 3sec 17th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E3D | 0x7E3E | 32317 | 32318 | CUR_HARM_MAXc18 | 3sec 18th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E3F | 0x7E40 | 32319 | 32320 | CUR_HARM_MAXc19 | 3sec 19th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E41 | 0x7E42 | 32321 | 32322 | CUR_HARM_MAXc20 | 3sec 20th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E43 | 0x7E44 | 32323 | 32324 | CUR_HARM_MAXc21 | 3sec 21st Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E45 | 0x7E46 | 32325 | 32326 | CUR_HARM_MAXc22 | 3sec 22nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E47 | 0x7E48 | 32327 | 32328 | CUR_HARM_MAXc23 | 3sec 23rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E49 | 0x7E4A | 32329 | 32330 | CUR_HARM_MAXc24 | 3sec 24th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E4B | 0x7E4C | 32331 | 32332 | CUR_HARM_MAXc25 | 3sec 25th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E4D | 0x7E4E | 32333 | 32334 | CUR_HARM_MAXc26 | 3sec 26th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E4F | 0x7E50 | 32335 | 32336 | CUR_HARM_MAXc27 | 3sec 27th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E51 | 0x7E52 | 32337 | 32338 | CUR_HARM_MAXc28 | 3sec 28th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E53 | 0x7E54 | 32339 | 32340 | CUR_HARM_MAXc29 | 3sec 29th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E55 | 0x7E56 | 32341 | 32342 | CUR_HARM_MAXc30 | 3sec 30th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E57 | 0x7E58 | 32343 | 32344 | CUR_HARM_MAXc31 | 3sec 31st Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E59 | 0x7E5A | 32345 | 32346 | CUR_HARM_MAXc32 | 3sec 32nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E5B | 0x7E5C | 32347 | 32348 | CUR_HARM_MAXc33 | 3sec 33rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E5D | 0x7E5E | 32349 | 32350 | CUR_HARM_MAXc34 | 3sec 34th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E5F | 0x7E60 | 32351 | 32352 | CUR_HARM_MAXc35 | 3sec 35th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E61 | 0x7E62 | 32353 | 32354 | CUR_HARM_MAXc36 | 3sec 36th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E63 | 0x7E64 | 32355 | 32356 | CUR_HARM_MAXc37 | 3sec 37th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E65 | 0x7E66 | 32357 | 32358 | CUR_HARM_MAXc38 | 3sec 38th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E67 | 0x7E68 | 32359 | 32360 | CUR_HARM_MAXc39 | 3sec 39th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E69 | 0x7E6A | 32361 | 32362 | CUR_HARM_MAXc40 | 3sec 40th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E6B | 0x7E6C | 32363 | 32364 | CUR_HARM_MAXc41 | 3sec 41st Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E6D | 0x7E6E | 32365 | 32366 | CUR_HARM_MAXc42 | 3sec 42nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E6F | 0x7E70 | 32367 | 32368 | CUR_HARM_MAXc43 | 3sec 43rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E71 | 0x7E72 | 32369 | 32370 | CUR_HARM_MAXc44 | 3sec 44th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E73 | 0x7E74 | 32371 | 32372 | CUR_HARM_MAXc45 | 3sec 45th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E75 | 0x7E76 | 32373 | 32374 | CUR_HARM_MAXc46 | 3sec 46th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E77 | 0x7E78 | 32375 | 32376 | CUR_HARM_MAXc47 | 3sec 47th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E79 | 0x7E7A | 32377 | 32378 | CUR_HARM_MAXc48 | 3sec 48th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E7B | 0x7E7C | 32379 | 32380 | CUR_HARM_MAXc49 | 3sec 49th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E7D | 0x7E7E | 32381 | 32382 | CUR_HARM_MAXc50 | 3sec 50th Phase C Current Harmonics Maximum Value | float | 2 | R
0x7E7F | 0x7E80 | 32383 | 32384 | CUR_HARM_MINa2 | 3sec 2nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E81 | 0x7E82 | 32385 | 32386 | CUR_HARM_MINa3 | 3sec 3rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E83 | 0x7E84 | 32387 | 32388 | CUR_HARM_MINa4 | 3sec 4th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E85 | 0x7E86 | 32389 | 32390 | CUR_HARM_MINa5 | 3sec 5th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E87 | 0x7E88 | 32391 | 32392 | CUR_HARM_MINa6 | 3sec 6th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E89 | 0x7E8A | 32393 | 32394 | CUR_HARM_MINa7 | 3sec 7th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E8B | 0x7E8C | 32395 | 32396 | CUR_HARM_MINa8 | 3sec 8th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E8D | 0x7E8E | 32397 | 32398 | CUR_HARM_MINa9 | 3sec 9th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E8F | 0x7E90 | 32399 | 32400 | CUR_HARM_MINa10 | 3sec 10th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E91 | 0x7E92 | 32401 | 32402 | CUR_HARM_MINa11 | 3sec 11st Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E93 | 0x7E94 | 32403 | 32404 | CUR_HARM_MINa12 | 3sec 12nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E95 | 0x7E96 | 32405 | 32406 | CUR_HARM_MINa13 | 3sec 13rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E97 | 0x7E98 | 32407 | 32408 | CUR_HARM_MINa14 | 3sec 14th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E99 | 0x7E9A | 32409 | 32410 | CUR_HARM_MINa15 | 3sec 15th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E9B | 0x7E9C | 32411 | 32412 | CUR_HARM_MINa16 | 3sec 16th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E9D | 0x7E9E | 32413 | 32414 | CUR_HARM_MINa17 | 3sec 17th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7E9F | 0x7EA0 | 32415 | 32416 | CUR_HARM_MINa18 | 3sec 18th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EA1 | 0x7EA2 | 32417 | 32418 | CUR_HARM_MINa19 | 3sec 19th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EA3 | 0x7EA4 | 32419 | 32420 | CUR_HARM_MINa20 | 3sec 20th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EA5 | 0x7EA6 | 32421 | 32422 | CUR_HARM_MINa21 | 3sec 21st Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EA7 | 0x7EA8 | 32423 | 32424 | CUR_HARM_MINa22 | 3sec 22nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EA9 | 0x7EAA | 32425 | 32426 | CUR_HARM_MINa23 | 3sec 23rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EAB | 0x7EAC | 32427 | 32428 | CUR_HARM_MINa24 | 3sec 24th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EAD | 0x7EAE | 32429 | 32430 | CUR_HARM_MINa25 | 3sec 25th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EAF | 0x7EB0 | 32431 | 32432 | CUR_HARM_MINa26 | 3sec 26th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EB1 | 0x7EB2 | 32433 | 32434 | CUR_HARM_MINa27 | 3sec 27th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EB3 | 0x7EB4 | 32435 | 32436 | CUR_HARM_MINa28 | 3sec 28th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EB5 | 0x7EB6 | 32437 | 32438 | CUR_HARM_MINa29 | 3sec 29th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EB7 | 0x7EB8 | 32439 | 32440 | CUR_HARM_MINa30 | 3sec 30th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EB9 | 0x7EBA | 32441 | 32442 | CUR_HARM_MINa31 | 3sec 31st Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EBB | 0x7EBC | 32443 | 32444 | CUR_HARM_MINa32 | 3sec 32nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EBD | 0x7EBE | 32445 | 32446 | CUR_HARM_MINa33 | 3sec 33rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EBF | 0x7EC0 | 32447 | 32448 | CUR_HARM_MINa34 | 3sec 34th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EC1 | 0x7EC2 | 32449 | 32450 | CUR_HARM_MINa35 | 3sec 35th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EC3 | 0x7EC4 | 32451 | 32452 | CUR_HARM_MINa36 | 3sec 36th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EC5 | 0x7EC6 | 32453 | 32454 | CUR_HARM_MINa37 | 3sec 37th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EC7 | 0x7EC8 | 32455 | 32456 | CUR_HARM_MINa38 | 3sec 38th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EC9 | 0x7ECA | 32457 | 32458 | CUR_HARM_MINa39 | 3sec 39th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7ECB | 0x7ECC | 32459 | 32460 | CUR_HARM_MINa40 | 3sec 40th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7ECD | 0x7ECE | 32461 | 32462 | CUR_HARM_MINa41 | 3sec 41st Phase A Current Harmonics Minimum Value | float | 2 | R
0x7ECF | 0x7ED0 | 32463 | 32464 | CUR_HARM_MINa42 | 3sec 42nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x7ED1 | 0x7ED2 | 32465 | 32466 | CUR_HARM_MINa43 | 3sec 43rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x7ED3 | 0x7ED4 | 32467 | 32468 | CUR_HARM_MINa44 | 3sec 44th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7ED5 | 0x7ED6 | 32469 | 32470 | CUR_HARM_MINa45 | 3sec 45th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7ED7 | 0x7ED8 | 32471 | 32472 | CUR_HARM_MINa46 | 3sec 46th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7ED9 | 0x7EDA | 32473 | 32474 | CUR_HARM_MINa47 | 3sec 47th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EDB | 0x7EDC | 32475 | 32476 | CUR_HARM_MINa48 | 3sec 48th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EDD | 0x7EDE | 32477 | 32478 | CUR_HARM_MINa49 | 3sec 49th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EDF | 0x7EE0 | 32479 | 32480 | CUR_HARM_MINa50 | 3sec 50th Phase A Current Harmonics Minimum Value | float | 2 | R
0x7EE1 | 0x7EE2 | 32481 | 32482 | CUR_HARM_MINb2 | 3sec 2nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EE3 | 0x7EE4 | 32483 | 32484 | CUR_HARM_MINb3 | 3sec 3rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EE5 | 0x7EE6 | 32485 | 32486 | CUR_HARM_MINb4 | 3sec 4th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EE7 | 0x7EE8 | 32487 | 32488 | CUR_HARM_MINb5 | 3sec 5th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EE9 | 0x7EEA | 32489 | 32490 | CUR_HARM_MINb6 | 3sec 6th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EEB | 0x7EEC | 32491 | 32492 | CUR_HARM_MINb7 | 3sec 7th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EED | 0x7EEE | 32493 | 32494 | CUR_HARM_MINb8 | 3sec 8th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EEF | 0x7EF0 | 32495 | 32496 | CUR_HARM_MINb9 | 3sec 9th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EF1 | 0x7EF2 | 32497 | 32498 | CUR_HARM_MINb10 | 3sec 10th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EF3 | 0x7EF4 | 32499 | 32500 | CUR_HARM_MINb11 | 3sec 11st Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EF5 | 0x7EF6 | 32501 | 32502 | CUR_HARM_MINb12 | 3sec 12nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EF7 | 0x7EF8 | 32503 | 32504 | CUR_HARM_MINb13 | 3sec 13rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EF9 | 0x7EFA | 32505 | 32506 | CUR_HARM_MINb14 | 3sec 14th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EFB | 0x7EFC | 32507 | 32508 | CUR_HARM_MINb15 | 3sec 15th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EFD | 0x7EFE | 32509 | 32510 | CUR_HARM_MINb16 | 3sec 16th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7EFF | 0x7F00 | 32511 | 32512 | CUR_HARM_MINb17 | 3sec 17th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F01 | 0x7F02 | 32513 | 32514 | CUR_HARM_MINb18 | 3sec 18th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F03 | 0x7F04 | 32515 | 32516 | CUR_HARM_MINb19 | 3sec 19th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F05 | 0x7F06 | 32517 | 32518 | CUR_HARM_MINb20 | 3sec 20th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F07 | 0x7F08 | 32519 | 32520 | CUR_HARM_MINb21 | 3sec 21st Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F09 | 0x7F0A | 32521 | 32522 | CUR_HARM_MINb22 | 3sec 22nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F0B | 0x7F0C | 32523 | 32524 | CUR_HARM_MINb23 | 3sec 23rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F0D | 0x7F0E | 32525 | 32526 | CUR_HARM_MINb24 | 3sec 24th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F0F | 0x7F10 | 32527 | 32528 | CUR_HARM_MINb25 | 3sec 25th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F11 | 0x7F12 | 32529 | 32530 | CUR_HARM_MINb26 | 3sec 26th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F13 | 0x7F14 | 32531 | 32532 | CUR_HARM_MINb27 | 3sec 27th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F15 | 0x7F16 | 32533 | 32534 | CUR_HARM_MINb28 | 3sec 28th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F17 | 0x7F18 | 32535 | 32536 | CUR_HARM_MINb29 | 3sec 29th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F19 | 0x7F1A | 32537 | 32538 | CUR_HARM_MINb30 | 3sec 30th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F1B | 0x7F1C | 32539 | 32540 | CUR_HARM_MINb31 | 3sec 31st Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F1D | 0x7F1E | 32541 | 32542 | CUR_HARM_MINb32 | 3sec 32nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F1F | 0x7F20 | 32543 | 32544 | CUR_HARM_MINb33 | 3sec 33rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F21 | 0x7F22 | 32545 | 32546 | CUR_HARM_MINb34 | 3sec 34th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F23 | 0x7F24 | 32547 | 32548 | CUR_HARM_MINb35 | 3sec 35th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F25 | 0x7F26 | 32549 | 32550 | CUR_HARM_MINb36 | 3sec 36th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F27 | 0x7F28 | 32551 | 32552 | CUR_HARM_MINb37 | 3sec 37th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F29 | 0x7F2A | 32553 | 32554 | CUR_HARM_MINb38 | 3sec 38th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F2B | 0x7F2C | 32555 | 32556 | CUR_HARM_MINb39 | 3sec 39th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F2D | 0x7F2E | 32557 | 32558 | CUR_HARM_MINb40 | 3sec 40th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F2F | 0x7F30 | 32559 | 32560 | CUR_HARM_MINb41 | 3sec 41st Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F31 | 0x7F32 | 32561 | 32562 | CUR_HARM_MINb42 | 3sec 42nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F33 | 0x7F34 | 32563 | 32564 | CUR_HARM_MINb43 | 3sec 43rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F35 | 0x7F36 | 32565 | 32566 | CUR_HARM_MINb44 | 3sec 44th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F37 | 0x7F38 | 32567 | 32568 | CUR_HARM_MINb45 | 3sec 45th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F39 | 0x7F3A | 32569 | 32570 | CUR_HARM_MINb46 | 3sec 46th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F3B | 0x7F3C | 32571 | 32572 | CUR_HARM_MINb47 | 3sec 47th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F3D | 0x7F3E | 32573 | 32574 | CUR_HARM_MINb48 | 3sec 48th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F3F | 0x7F40 | 32575 | 32576 | CUR_HARM_MINb49 | 3sec 49th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F41 | 0x7F42 | 32577 | 32578 | CUR_HARM_MINb50 | 3sec 50th Phase B Current Harmonics Minimum Value | float | 2 | R
0x7F43 | 0x7F44 | 32579 | 32580 | CUR_HARM_MINc2 | 3sec 2nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F45 | 0x7F46 | 32581 | 32582 | CUR_HARM_MINc3 | 3sec 3rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F47 | 0x7F48 | 32583 | 32584 | CUR_HARM_MINc4 | 3sec 4th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F49 | 0x7F4A | 32585 | 32586 | CUR_HARM_MINc5 | 3sec 5th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F4B | 0x7F4C | 32587 | 32588 | CUR_HARM_MINc6 | 3sec 6th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F4D | 0x7F4E | 32589 | 32590 | CUR_HARM_MINc7 | 3sec 7th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F4F | 0x7F50 | 32591 | 32592 | CUR_HARM_MINc8 | 3sec 8th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F51 | 0x7F52 | 32593 | 32594 | CUR_HARM_MINc9 | 3sec 9th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F53 | 0x7F54 | 32595 | 32596 | CUR_HARM_MINc10 | 3sec 10th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F55 | 0x7F56 | 32597 | 32598 | CUR_HARM_MINc11 | 3sec 11st Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F57 | 0x7F58 | 32599 | 32600 | CUR_HARM_MINc12 | 3sec 12nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F59 | 0x7F5A | 32601 | 32602 | CUR_HARM_MINc13 | 3sec 13rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F5B | 0x7F5C | 32603 | 32604 | CUR_HARM_MINc14 | 3sec 14th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F5D | 0x7F5E | 32605 | 32606 | CUR_HARM_MINc15 | 3sec 15th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F5F | 0x7F60 | 32607 | 32608 | CUR_HARM_MINc16 | 3sec 16th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F61 | 0x7F62 | 32609 | 32610 | CUR_HARM_MINc17 | 3sec 17th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F63 | 0x7F64 | 32611 | 32612 | CUR_HARM_MINc18 | 3sec 18th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F65 | 0x7F66 | 32613 | 32614 | CUR_HARM_MINc19 | 3sec 19th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F67 | 0x7F68 | 32615 | 32616 | CUR_HARM_MINc20 | 3sec 20th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F69 | 0x7F6A | 32617 | 32618 | CUR_HARM_MINc21 | 3sec 21st Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F6B | 0x7F6C | 32619 | 32620 | CUR_HARM_MINc22 | 3sec 22nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F6D | 0x7F6E | 32621 | 32622 | CUR_HARM_MINc23 | 3sec 23rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F6F | 0x7F70 | 32623 | 32624 | CUR_HARM_MINc24 | 3sec 24th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F71 | 0x7F72 | 32625 | 32626 | CUR_HARM_MINc25 | 3sec 25th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F73 | 0x7F74 | 32627 | 32628 | CUR_HARM_MINc26 | 3sec 26th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F75 | 0x7F76 | 32629 | 32630 | CUR_HARM_MINc27 | 3sec 27th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F77 | 0x7F78 | 32631 | 32632 | CUR_HARM_MINc28 | 3sec 28th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F79 | 0x7F7A | 32633 | 32634 | CUR_HARM_MINc29 | 3sec 29th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F7B | 0x7F7C | 32635 | 32636 | CUR_HARM_MINc30 | 3sec 30th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F7D | 0x7F7E | 32637 | 32638 | CUR_HARM_MINc31 | 3sec 31st Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F7F | 0x7F80 | 32639 | 32640 | CUR_HARM_MINc32 | 3sec 32nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F81 | 0x7F82 | 32641 | 32642 | CUR_HARM_MINc33 | 3sec 33rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F83 | 0x7F84 | 32643 | 32644 | CUR_HARM_MINc34 | 3sec 34th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F85 | 0x7F86 | 32645 | 32646 | CUR_HARM_MINc35 | 3sec 35th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F87 | 0x7F88 | 32647 | 32648 | CUR_HARM_MINc36 | 3sec 36th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F89 | 0x7F8A | 32649 | 32650 | CUR_HARM_MINc37 | 3sec 37th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F8B | 0x7F8C | 32651 | 32652 | CUR_HARM_MINc38 | 3sec 38th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F8D | 0x7F8E | 32653 | 32654 | CUR_HARM_MINc39 | 3sec 39th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F8F | 0x7F90 | 32655 | 32656 | CUR_HARM_MINc40 | 3sec 40th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F91 | 0x7F92 | 32657 | 32658 | CUR_HARM_MINc41 | 3sec 41st Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F93 | 0x7F94 | 32659 | 32660 | CUR_HARM_MINc42 | 3sec 42nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F95 | 0x7F96 | 32661 | 32662 | CUR_HARM_MINc43 | 3sec 43rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F97 | 0x7F98 | 32663 | 32664 | CUR_HARM_MINc44 | 3sec 44th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F99 | 0x7F9A | 32665 | 32666 | CUR_HARM_MINc45 | 3sec 45th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F9B | 0x7F9C | 32667 | 32668 | CUR_HARM_MINc46 | 3sec 46th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F9D | 0x7F9E | 32669 | 32670 | CUR_HARM_MINc47 | 3sec 47th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7F9F | 0x7FA0 | 32671 | 32672 | CUR_HARM_MINc48 | 3sec 48th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7FA1 | 0x7FA2 | 32673 | 32674 | CUR_HARM_MINc49 | 3sec 49th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7FA3 | 0x7FA4 | 32675 | 32676 | CUR_HARM_MINc50 | 3sec 50th Phase C Current Harmonics Minimum Value | float | 2 | R
0x7FA5 | 0x7FA6 | 32677 | 32678 | CUR_HARM_AVGa2 | 3sec 2nd Phase A Current Harmonics Average Value | float | 2 | R
0x7FA7 | 0x7FA8 | 32679 | 32680 | CUR_HARM_AVGa3 | 3sec 3rd Phase A Current Harmonics Average Value | float | 2 | R
0x7FA9 | 0x7FAA | 32681 | 32682 | CUR_HARM_AVGa4 | 3sec 4th Phase A Current Harmonics Average Value | float | 2 | R
0x7FAB | 0x7FAC | 32683 | 32684 | CUR_HARM_AVGa5 | 3sec 5th Phase A Current Harmonics Average Value | float | 2 | R
0x7FAD | 0x7FAE | 32685 | 32686 | CUR_HARM_AVGa6 | 3sec 6th Phase A Current Harmonics Average Value | float | 2 | R
0x7FAF | 0x7FB0 | 32687 | 32688 | CUR_HARM_AVGa7 | 3sec 7th Phase A Current Harmonics Average Value | float | 2 | R
0x7FB1 | 0x7FB2 | 32689 | 32690 | CUR_HARM_AVGa8 | 3sec 8th Phase A Current Harmonics Average Value | float | 2 | R
0x7FB3 | 0x7FB4 | 32691 | 32692 | CUR_HARM_AVGa9 | 3sec 9th Phase A Current Harmonics Average Value | float | 2 | R
0x7FB5 | 0x7FB6 | 32693 | 32694 | CUR_HARM_AVGa10 | 3sec 10th Phase A Current Harmonics Average Value | float | 2 | R
0x7FB7 | 0x7FB8 | 32695 | 32696 | CUR_HARM_AVGa11 | 3sec 11st Phase A Current Harmonics Average Value | float | 2 | R
0x7FB9 | 0x7FBA | 32697 | 32698 | CUR_HARM_AVGa12 | 3sec 12nd Phase A Current Harmonics Average Value | float | 2 | R
0x7FBB | 0x7FBC | 32699 | 32700 | CUR_HARM_AVGa13 | 3sec 13rd Phase A Current Harmonics Average Value | float | 2 | R
0x7FBD | 0x7FBE | 32701 | 32702 | CUR_HARM_AVGa14 | 3sec 14th Phase A Current Harmonics Average Value | float | 2 | R
0x7FBF | 0x7FC0 | 32703 | 32704 | CUR_HARM_AVGa15 | 3sec 15th Phase A Current Harmonics Average Value | float | 2 | R
0x7FC1 | 0x7FC2 | 32705 | 32706 | CUR_HARM_AVGa16 | 3sec 16th Phase A Current Harmonics Average Value | float | 2 | R
0x7FC3 | 0x7FC4 | 32707 | 32708 | CUR_HARM_AVGa17 | 3sec 17th Phase A Current Harmonics Average Value | float | 2 | R
0x7FC5 | 0x7FC6 | 32709 | 32710 | CUR_HARM_AVGa18 | 3sec 18th Phase A Current Harmonics Average Value | float | 2 | R
0x7FC7 | 0x7FC8 | 32711 | 32712 | CUR_HARM_AVGa19 | 3sec 19th Phase A Current Harmonics Average Value | float | 2 | R
0x7FC9 | 0x7FCA | 32713 | 32714 | CUR_HARM_AVGa20 | 3sec 20th Phase A Current Harmonics Average Value | float | 2 | R
0x7FCB | 0x7FCC | 32715 | 32716 | CUR_HARM_AVGa21 | 3sec 21st Phase A Current Harmonics Average Value | float | 2 | R
0x7FCD | 0x7FCE | 32717 | 32718 | CUR_HARM_AVGa22 | 3sec 22nd Phase A Current Harmonics Average Value | float | 2 | R
0x7FCF | 0x7FD0 | 32719 | 32720 | CUR_HARM_AVGa23 | 3sec 23rd Phase A Current Harmonics Average Value | float | 2 | R
0x7FD1 | 0x7FD2 | 32721 | 32722 | CUR_HARM_AVGa24 | 3sec 24th Phase A Current Harmonics Average Value | float | 2 | R
0x7FD3 | 0x7FD4 | 32723 | 32724 | CUR_HARM_AVGa25 | 3sec 25th Phase A Current Harmonics Average Value | float | 2 | R
0x7FD5 | 0x7FD6 | 32725 | 32726 | CUR_HARM_AVGa26 | 3sec 26th Phase A Current Harmonics Average Value | float | 2 | R
0x7FD7 | 0x7FD8 | 32727 | 32728 | CUR_HARM_AVGa27 | 3sec 27th Phase A Current Harmonics Average Value | float | 2 | R
0x7FD9 | 0x7FDA | 32729 | 32730 | CUR_HARM_AVGa28 | 3sec 28th Phase A Current Harmonics Average Value | float | 2 | R
0x7FDB | 0x7FDC | 32731 | 32732 | CUR_HARM_AVGa29 | 3sec 29th Phase A Current Harmonics Average Value | float | 2 | R
0x7FDD | 0x7FDE | 32733 | 32734 | CUR_HARM_AVGa30 | 3sec 30th Phase A Current Harmonics Average Value | float | 2 | R
0x7FDF | 0x7FE0 | 32735 | 32736 | CUR_HARM_AVGa31 | 3sec 31st Phase A Current Harmonics Average Value | float | 2 | R
0x7FE1 | 0x7FE2 | 32737 | 32738 | CUR_HARM_AVGa32 | 3sec 32nd Phase A Current Harmonics Average Value | float | 2 | R
0x7FE3 | 0x7FE4 | 32739 | 32740 | CUR_HARM_AVGa33 | 3sec 33rd Phase A Current Harmonics Average Value | float | 2 | R
0x7FE5 | 0x7FE6 | 32741 | 32742 | CUR_HARM_AVGa34 | 3sec 34th Phase A Current Harmonics Average Value | float | 2 | R
0x7FE7 | 0x7FE8 | 32743 | 32744 | CUR_HARM_AVGa35 | 3sec 35th Phase A Current Harmonics Average Value | float | 2 | R
0x7FE9 | 0x7FEA | 32745 | 32746 | CUR_HARM_AVGa36 | 3sec 36th Phase A Current Harmonics Average Value | float | 2 | R
0x7FEB | 0x7FEC | 32747 | 32748 | CUR_HARM_AVGa37 | 3sec 37th Phase A Current Harmonics Average Value | float | 2 | R
0x7FED | 0x7FEE | 32749 | 32750 | CUR_HARM_AVGa38 | 3sec 38th Phase A Current Harmonics Average Value | float | 2 | R
0x7FEF | 0x7FF0 | 32751 | 32752 | CUR_HARM_AVGa39 | 3sec 39th Phase A Current Harmonics Average Value | float | 2 | R
0x7FF1 | 0x7FF2 | 32753 | 32754 | CUR_HARM_AVGa40 | 3sec 40th Phase A Current Harmonics Average Value | float | 2 | R
0x7FF3 | 0x7FF4 | 32755 | 32756 | CUR_HARM_AVGa41 | 3sec 41st Phase A Current Harmonics Average Value | float | 2 | R
0x7FF5 | 0x7FF6 | 32757 | 32758 | CUR_HARM_AVGa42 | 3sec 42nd Phase A Current Harmonics Average Value | float | 2 | R
0x7FF7 | 0x7FF8 | 32759 | 32760 | CUR_HARM_AVGa43 | 3sec 43rd Phase A Current Harmonics Average Value | float | 2 | R
0x7FF9 | 0x7FFA | 32761 | 32762 | CUR_HARM_AVGa44 | 3sec 44th Phase A Current Harmonics Average Value | float | 2 | R
0x7FFB | 0x7FFC | 32763 | 32764 | CUR_HARM_AVGa45 | 3sec 45th Phase A Current Harmonics Average Value | float | 2 | R
0x7FFD | 0x7FFE | 32765 | 32766 | CUR_HARM_AVGa46 | 3sec 46th Phase A Current Harmonics Average Value | float | 2 | R
0x7FFF | 0x8000 | 32767 | 32768 | CUR_HARM_AVGa47 | 3sec 47th Phase A Current Harmonics Average Value | float | 2 | R
0x8001 | 0x8002 | 32769 | 32770 | CUR_HARM_AVGa48 | 3sec 48th Phase A Current Harmonics Average Value | float | 2 | R
0x8003 | 0x8004 | 32771 | 32772 | CUR_HARM_AVGa49 | 3sec 49th Phase A Current Harmonics Average Value | float | 2 | R
0x8005 | 0x8006 | 32773 | 32774 | CUR_HARM_AVGa50 | 3sec 50th Phase A Current Harmonics Average Value | float | 2 | R
0x8007 | 0x8008 | 32775 | 32776 | CUR_HARM_AVGb2 | 3sec 2nd Phase B Current Harmonics Average Value | float | 2 | R
0x8009 | 0x800A | 32777 | 32778 | CUR_HARM_AVGb3 | 3sec 3rd Phase B Current Harmonics Average Value | float | 2 | R
0x800B | 0x800C | 32779 | 32780 | CUR_HARM_AVGb4 | 3sec 4th Phase B Current Harmonics Average Value | float | 2 | R
0x800D | 0x800E | 32781 | 32782 | CUR_HARM_AVGb5 | 3sec 5th Phase B Current Harmonics Average Value | float | 2 | R
0x800F | 0x8010 | 32783 | 32784 | CUR_HARM_AVGb6 | 3sec 6th Phase B Current Harmonics Average Value | float | 2 | R
0x8011 | 0x8012 | 32785 | 32786 | CUR_HARM_AVGb7 | 3sec 7th Phase B Current Harmonics Average Value | float | 2 | R
0x8013 | 0x8014 | 32787 | 32788 | CUR_HARM_AVGb8 | 3sec 8th Phase B Current Harmonics Average Value | float | 2 | R
0x8015 | 0x8016 | 32789 | 32790 | CUR_HARM_AVGb9 | 3sec 9th Phase B Current Harmonics Average Value | float | 2 | R
0x8017 | 0x8018 | 32791 | 32792 | CUR_HARM_AVGb10 | 3sec 10th Phase B Current Harmonics Average Value | float | 2 | R
0x8019 | 0x801A | 32793 | 32794 | CUR_HARM_AVGb11 | 3sec 11st Phase B Current Harmonics Average Value | float | 2 | R
0x801B | 0x801C | 32795 | 32796 | CUR_HARM_AVGb12 | 3sec 12nd Phase B Current Harmonics Average Value | float | 2 | R
0x801D | 0x801E | 32797 | 32798 | CUR_HARM_AVGb13 | 3sec 13rd Phase B Current Harmonics Average Value | float | 2 | R
0x801F | 0x8020 | 32799 | 32800 | CUR_HARM_AVGb14 | 3sec 14th Phase B Current Harmonics Average Value | float | 2 | R
0x8021 | 0x8022 | 32801 | 32802 | CUR_HARM_AVGb15 | 3sec 15th Phase B Current Harmonics Average Value | float | 2 | R
0x8023 | 0x8024 | 32803 | 32804 | CUR_HARM_AVGb16 | 3sec 16th Phase B Current Harmonics Average Value | float | 2 | R
0x8025 | 0x8026 | 32805 | 32806 | CUR_HARM_AVGb17 | 3sec 17th Phase B Current Harmonics Average Value | float | 2 | R
0x8027 | 0x8028 | 32807 | 32808 | CUR_HARM_AVGb18 | 3sec 18th Phase B Current Harmonics Average Value | float | 2 | R
0x8029 | 0x802A | 32809 | 32810 | CUR_HARM_AVGb19 | 3sec 19th Phase B Current Harmonics Average Value | float | 2 | R
0x802B | 0x802C | 32811 | 32812 | CUR_HARM_AVGb20 | 3sec 20th Phase B Current Harmonics Average Value | float | 2 | R
0x802D | 0x802E | 32813 | 32814 | CUR_HARM_AVGb21 | 3sec 21st Phase B Current Harmonics Average Value | float | 2 | R
0x802F | 0x8030 | 32815 | 32816 | CUR_HARM_AVGb22 | 3sec 22nd Phase B Current Harmonics Average Value | float | 2 | R
0x8031 | 0x8032 | 32817 | 32818 | CUR_HARM_AVGb23 | 3sec 23rd Phase B Current Harmonics Average Value | float | 2 | R
0x8033 | 0x8034 | 32819 | 32820 | CUR_HARM_AVGb24 | 3sec 24th Phase B Current Harmonics Average Value | float | 2 | R
0x8035 | 0x8036 | 32821 | 32822 | CUR_HARM_AVGb25 | 3sec 25th Phase B Current Harmonics Average Value | float | 2 | R
0x8037 | 0x8038 | 32823 | 32824 | CUR_HARM_AVGb26 | 3sec 26th Phase B Current Harmonics Average Value | float | 2 | R
0x8039 | 0x803A | 32825 | 32826 | CUR_HARM_AVGb27 | 3sec 27th Phase B Current Harmonics Average Value | float | 2 | R
0x803B | 0x803C | 32827 | 32828 | CUR_HARM_AVGb28 | 3sec 28th Phase B Current Harmonics Average Value | float | 2 | R
0x803D | 0x803E | 32829 | 32830 | CUR_HARM_AVGb29 | 3sec 29th Phase B Current Harmonics Average Value | float | 2 | R
0x803F | 0x8040 | 32831 | 32832 | CUR_HARM_AVGb30 | 3sec 30th Phase B Current Harmonics Average Value | float | 2 | R
0x8041 | 0x8042 | 32833 | 32834 | CUR_HARM_AVGb31 | 3sec 31st Phase B Current Harmonics Average Value | float | 2 | R
0x8043 | 0x8044 | 32835 | 32836 | CUR_HARM_AVGb32 | 3sec 32nd Phase B Current Harmonics Average Value | float | 2 | R
0x8045 | 0x8046 | 32837 | 32838 | CUR_HARM_AVGb33 | 3sec 33rd Phase B Current Harmonics Average Value | float | 2 | R
0x8047 | 0x8048 | 32839 | 32840 | CUR_HARM_AVGb34 | 3sec 34th Phase B Current Harmonics Average Value | float | 2 | R
0x8049 | 0x804A | 32841 | 32842 | CUR_HARM_AVGb35 | 3sec 35th Phase B Current Harmonics Average Value | float | 2 | R
0x804B | 0x804C | 32843 | 32844 | CUR_HARM_AVGb36 | 3sec 36th Phase B Current Harmonics Average Value | float | 2 | R
0x804D | 0x804E | 32845 | 32846 | CUR_HARM_AVGb37 | 3sec 37th Phase B Current Harmonics Average Value | float | 2 | R
0x804F | 0x8050 | 32847 | 32848 | CUR_HARM_AVGb38 | 3sec 38th Phase B Current Harmonics Average Value | float | 2 | R
0x8051 | 0x8052 | 32849 | 32850 | CUR_HARM_AVGb39 | 3sec 39th Phase B Current Harmonics Average Value | float | 2 | R
0x8053 | 0x8054 | 32851 | 32852 | CUR_HARM_AVGb40 | 3sec 40th Phase B Current Harmonics Average Value | float | 2 | R
0x8055 | 0x8056 | 32853 | 32854 | CUR_HARM_AVGb41 | 3sec 41st Phase B Current Harmonics Average Value | float | 2 | R
0x8057 | 0x8058 | 32855 | 32856 | CUR_HARM_AVGb42 | 3sec 42nd Phase B Current Harmonics Average Value | float | 2 | R
0x8059 | 0x805A | 32857 | 32858 | CUR_HARM_AVGb43 | 3sec 43rd Phase B Current Harmonics Average Value | float | 2 | R
0x805B | 0x805C | 32859 | 32860 | CUR_HARM_AVGb44 | 3sec 44th Phase B Current Harmonics Average Value | float | 2 | R
0x805D | 0x805E | 32861 | 32862 | CUR_HARM_AVGb45 | 3sec 45th Phase B Current Harmonics Average Value | float | 2 | R
0x805F | 0x8060 | 32863 | 32864 | CUR_HARM_AVGb46 | 3sec 46th Phase B Current Harmonics Average Value | float | 2 | R
0x8061 | 0x8062 | 32865 | 32866 | CUR_HARM_AVGb47 | 3sec 47th Phase B Current Harmonics Average Value | float | 2 | R
0x8063 | 0x8064 | 32867 | 32868 | CUR_HARM_AVGb48 | 3sec 48th Phase B Current Harmonics Average Value | float | 2 | R
0x8065 | 0x8066 | 32869 | 32870 | CUR_HARM_AVGb49 | 3sec 49th Phase B Current Harmonics Average Value | float | 2 | R
0x8067 | 0x8068 | 32871 | 32872 | CUR_HARM_AVGb50 | 3sec 50th Phase B Current Harmonics Average Value | float | 2 | R
0x8069 | 0x806A | 32873 | 32874 | CUR_HARM_AVGc2 | 3sec 2nd Phase C Current Harmonics Average Value | float | 2 | R
0x806B | 0x806C | 32875 | 32876 | CUR_HARM_AVGc3 | 3sec 3rd Phase C Current Harmonics Average Value | float | 2 | R
0x806D | 0x806E | 32877 | 32878 | CUR_HARM_AVGc4 | 3sec 4th Phase C Current Harmonics Average Value | float | 2 | R
0x806F | 0x8070 | 32879 | 32880 | CUR_HARM_AVGc5 | 3sec 5th Phase C Current Harmonics Average Value | float | 2 | R
0x8071 | 0x8072 | 32881 | 32882 | CUR_HARM_AVGc6 | 3sec 6th Phase C Current Harmonics Average Value | float | 2 | R
0x8073 | 0x8074 | 32883 | 32884 | CUR_HARM_AVGc7 | 3sec 7th Phase C Current Harmonics Average Value | float | 2 | R
0x8075 | 0x8076 | 32885 | 32886 | CUR_HARM_AVGc8 | 3sec 8th Phase C Current Harmonics Average Value | float | 2 | R
0x8077 | 0x8078 | 32887 | 32888 | CUR_HARM_AVGc9 | 3sec 9th Phase C Current Harmonics Average Value | float | 2 | R
0x8079 | 0x807A | 32889 | 32890 | CUR_HARM_AVGc10 | 3sec 10th Phase C Current Harmonics Average Value | float | 2 | R
0x807B | 0x807C | 32891 | 32892 | CUR_HARM_AVGc11 | 3sec 11st Phase C Current Harmonics Average Value | float | 2 | R
0x807D | 0x807E | 32893 | 32894 | CUR_HARM_AVGc12 | 3sec 12nd Phase C Current Harmonics Average Value | float | 2 | R
0x807F | 0x8080 | 32895 | 32896 | CUR_HARM_AVGc13 | 3sec 13rd Phase C Current Harmonics Average Value | float | 2 | R
0x8081 | 0x8082 | 32897 | 32898 | CUR_HARM_AVGc14 | 3sec 14th Phase C Current Harmonics Average Value | float | 2 | R
0x8083 | 0x8084 | 32899 | 32900 | CUR_HARM_AVGc15 | 3sec 15th Phase C Current Harmonics Average Value | float | 2 | R
0x8085 | 0x8086 | 32901 | 32902 | CUR_HARM_AVGc16 | 3sec 16th Phase C Current Harmonics Average Value | float | 2 | R
0x8087 | 0x8088 | 32903 | 32904 | CUR_HARM_AVGc17 | 3sec 17th Phase C Current Harmonics Average Value | float | 2 | R
0x8089 | 0x808A | 32905 | 32906 | CUR_HARM_AVGc18 | 3sec 18th Phase C Current Harmonics Average Value | float | 2 | R
0x808B | 0x808C | 32907 | 32908 | CUR_HARM_AVGc19 | 3sec 19th Phase C Current Harmonics Average Value | float | 2 | R
0x808D | 0x808E | 32909 | 32910 | CUR_HARM_AVGc20 | 3sec 20th Phase C Current Harmonics Average Value | float | 2 | R
0x808F | 0x8090 | 32911 | 32912 | CUR_HARM_AVGc21 | 3sec 21st Phase C Current Harmonics Average Value | float | 2 | R
0x8091 | 0x8092 | 32913 | 32914 | CUR_HARM_AVGc22 | 3sec 22nd Phase C Current Harmonics Average Value | float | 2 | R
0x8093 | 0x8094 | 32915 | 32916 | CUR_HARM_AVGc23 | 3sec 23rd Phase C Current Harmonics Average Value | float | 2 | R
0x8095 | 0x8096 | 32917 | 32918 | CUR_HARM_AVGc24 | 3sec 24th Phase C Current Harmonics Average Value | float | 2 | R
0x8097 | 0x8098 | 32919 | 32920 | CUR_HARM_AVGc25 | 3sec 25th Phase C Current Harmonics Average Value | float | 2 | R
0x8099 | 0x809A | 32921 | 32922 | CUR_HARM_AVGc26 | 3sec 26th Phase C Current Harmonics Average Value | float | 2 | R
0x809B | 0x809C | 32923 | 32924 | CUR_HARM_AVGc27 | 3sec 27th Phase C Current Harmonics Average Value | float | 2 | R
0x809D | 0x809E | 32925 | 32926 | CUR_HARM_AVGc28 | 3sec 28th Phase C Current Harmonics Average Value | float | 2 | R
0x809F | 0x80A0 | 32927 | 32928 | CUR_HARM_AVGc29 | 3sec 29th Phase C Current Harmonics Average Value | float | 2 | R
0x80A1 | 0x80A2 | 32929 | 32930 | CUR_HARM_AVGc30 | 3sec 30th Phase C Current Harmonics Average Value | float | 2 | R
0x80A3 | 0x80A4 | 32931 | 32932 | CUR_HARM_AVGc31 | 3sec 31st Phase C Current Harmonics Average Value | float | 2 | R
0x80A5 | 0x80A6 | 32933 | 32934 | CUR_HARM_AVGc32 | 3sec 32nd Phase C Current Harmonics Average Value | float | 2 | R
0x80A7 | 0x80A8 | 32935 | 32936 | CUR_HARM_AVGc33 | 3sec 33rd Phase C Current Harmonics Average Value | float | 2 | R
0x80A9 | 0x80AA | 32937 | 32938 | CUR_HARM_AVGc34 | 3sec 34th Phase C Current Harmonics Average Value | float | 2 | R
0x80AB | 0x80AC | 32939 | 32940 | CUR_HARM_AVGc35 | 3sec 35th Phase C Current Harmonics Average Value | float | 2 | R
0x80AD | 0x80AE | 32941 | 32942 | CUR_HARM_AVGc36 | 3sec 36th Phase C Current Harmonics Average Value | float | 2 | R
0x80AF | 0x80B0 | 32943 | 32944 | CUR_HARM_AVGc37 | 3sec 37th Phase C Current Harmonics Average Value | float | 2 | R
0x80B1 | 0x80B2 | 32945 | 32946 | CUR_HARM_AVGc38 | 3sec 38th Phase C Current Harmonics Average Value | float | 2 | R
0x80B3 | 0x80B4 | 32947 | 32948 | CUR_HARM_AVGc39 | 3sec 39th Phase C Current Harmonics Average Value | float | 2 | R
0x80B5 | 0x80B6 | 32949 | 32950 | CUR_HARM_AVGc40 | 3sec 40th Phase C Current Harmonics Average Value | float | 2 | R
0x80B7 | 0x80B8 | 32951 | 32952 | CUR_HARM_AVGc41 | 3sec 41st Phase C Current Harmonics Average Value | float | 2 | R
0x80B9 | 0x80BA | 32953 | 32954 | CUR_HARM_AVGc42 | 3sec 42nd Phase C Current Harmonics Average Value | float | 2 | R
0x80BB | 0x80BC | 32955 | 32956 | CUR_HARM_AVGc43 | 3sec 43rd Phase C Current Harmonics Average Value | float | 2 | R
0x80BD | 0x80BE | 32957 | 32958 | CUR_HARM_AVGc44 | 3sec 44th Phase C Current Harmonics Average Value | float | 2 | R
0x80BF | 0x80C0 | 32959 | 32960 | CUR_HARM_AVGc45 | 3sec 45th Phase C Current Harmonics Average Value | float | 2 | R
0x80C1 | 0x80C2 | 32961 | 32962 | CUR_HARM_AVGc46 | 3sec 46th Phase C Current Harmonics Average Value | float | 2 | R
0x80C3 | 0x80C4 | 32963 | 32964 | CUR_HARM_AVGc47 | 3sec 47th Phase C Current Harmonics Average Value | float | 2 | R
0x80C5 | 0x80C6 | 32965 | 32966 | CUR_HARM_AVGc48 | 3sec 48th Phase C Current Harmonics Average Value | float | 2 | R
0x80C7 | 0x80C8 | 32967 | 32968 | CUR_HARM_AVGc49 | 3sec 49th Phase C Current Harmonics Average Value | float | 2 | R
0x80C9 | 0x80CA | 32969 | 32970 | CUR_HARM_AVGc50 | 3sec 50th Phase C Current Harmonics Average Value | float | 2 | R
0x80CB | 0x80CB | 32971 | 32971 | N_TDD_99a | 3sec Phase A TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0x80CC | 0x80CC | 32972 | 32972 | N_TDD_99b | 3sec Phase B TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0x80CD | 0x80CD | 32973 | 32973 | N_TDD_99c | 3sec Phase C TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0x80CE | 0x80CF | 32974 | 32975 | TDD_99_PASSa | 3sec Phase A TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0x80D0 | 0x80D1 | 32976 | 32977 | TDD_99_PASSb | 3sec Phase B TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0x80D2 | 0x80D3 | 32978 | 32979 | TDD_99_PASSc | 3sec Phase C TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0x80D4 | 0x80D4 | 32980 | 32980 | N_CUR_HARM_99a2 | 3sec 2nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80D5 | 0x80D5 | 32981 | 32981 | N_CUR_HARM_99a3 | 3sec 3rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80D6 | 0x80D6 | 32982 | 32982 | N_CUR_HARM_99a4 | 3sec 4th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80D7 | 0x80D7 | 32983 | 32983 | N_CUR_HARM_99a5 | 3sec 5th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80D8 | 0x80D8 | 32984 | 32984 | N_CUR_HARM_99a6 | 3sec 6th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80D9 | 0x80D9 | 32985 | 32985 | N_CUR_HARM_99a7 | 3sec 7th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80DA | 0x80DA | 32986 | 32986 | N_CUR_HARM_99a8 | 3sec 8th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80DB | 0x80DB | 32987 | 32987 | N_CUR_HARM_99a9 | 3sec 9th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80DC | 0x80DC | 32988 | 32988 | N_CUR_HARM_99a10 | 3sec 10th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80DD | 0x80DD | 32989 | 32989 | N_CUR_HARM_99a11 | 3sec 11st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80DE | 0x80DE | 32990 | 32990 | N_CUR_HARM_99a12 | 3sec 12nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80DF | 0x80DF | 32991 | 32991 | N_CUR_HARM_99a13 | 3sec 13rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80E0 | 0x80E0 | 32992 | 32992 | N_CUR_HARM_99a14 | 3sec 14th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80E1 | 0x80E1 | 32993 | 32993 | N_CUR_HARM_99a15 | 3sec 15th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80E2 | 0x80E2 | 32994 | 32994 | N_CUR_HARM_99a16 | 3sec 16th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80E3 | 0x80E3 | 32995 | 32995 | N_CUR_HARM_99a17 | 3sec 17th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80E4 | 0x80E4 | 32996 | 32996 | N_CUR_HARM_99a18 | 3sec 18th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80E5 | 0x80E5 | 32997 | 32997 | N_CUR_HARM_99a19 | 3sec 19th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80E6 | 0x80E6 | 32998 | 32998 | N_CUR_HARM_99a20 | 3sec 20th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80E7 | 0x80E7 | 32999 | 32999 | N_CUR_HARM_99a21 | 3sec 21st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80E8 | 0x80E8 | 33000 | 33000 | N_CUR_HARM_99a22 | 3sec 22nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80E9 | 0x80E9 | 33001 | 33001 | N_CUR_HARM_99a23 | 3sec 23rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80EA | 0x80EA | 33002 | 33002 | N_CUR_HARM_99a24 | 3sec 24th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80EB | 0x80EB | 33003 | 33003 | N_CUR_HARM_99a25 | 3sec 25th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80EC | 0x80EC | 33004 | 33004 | N_CUR_HARM_99a26 | 3sec 26th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80ED | 0x80ED | 33005 | 33005 | N_CUR_HARM_99a27 | 3sec 27th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80EE | 0x80EE | 33006 | 33006 | N_CUR_HARM_99a28 | 3sec 28th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80EF | 0x80EF | 33007 | 33007 | N_CUR_HARM_99a29 | 3sec 29th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80F0 | 0x80F0 | 33008 | 33008 | N_CUR_HARM_99a30 | 3sec 30th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80F1 | 0x80F1 | 33009 | 33009 | N_CUR_HARM_99a31 | 3sec 31st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80F2 | 0x80F2 | 33010 | 33010 | N_CUR_HARM_99a32 | 3sec 32nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80F3 | 0x80F3 | 33011 | 33011 | N_CUR_HARM_99a33 | 3sec 33rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80F4 | 0x80F4 | 33012 | 33012 | N_CUR_HARM_99a34 | 3sec 34th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80F5 | 0x80F5 | 33013 | 33013 | N_CUR_HARM_99a35 | 3sec 35th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80F6 | 0x80F6 | 33014 | 33014 | N_CUR_HARM_99a36 | 3sec 36th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80F7 | 0x80F7 | 33015 | 33015 | N_CUR_HARM_99a37 | 3sec 37th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80F8 | 0x80F8 | 33016 | 33016 | N_CUR_HARM_99a38 | 3sec 38th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80F9 | 0x80F9 | 33017 | 33017 | N_CUR_HARM_99a39 | 3sec 39th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80FA | 0x80FA | 33018 | 33018 | N_CUR_HARM_99a40 | 3sec 40th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80FB | 0x80FB | 33019 | 33019 | N_CUR_HARM_99a41 | 3sec 41st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80FC | 0x80FC | 33020 | 33020 | N_CUR_HARM_99a42 | 3sec 42nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80FD | 0x80FD | 33021 | 33021 | N_CUR_HARM_99a43 | 3sec 43rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80FE | 0x80FE | 33022 | 33022 | N_CUR_HARM_99a44 | 3sec 44th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x80FF | 0x80FF | 33023 | 33023 | N_CUR_HARM_99a45 | 3sec 45th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8100 | 0x8100 | 33024 | 33024 | N_CUR_HARM_99a46 | 3sec 46th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8101 | 0x8101 | 33025 | 33025 | N_CUR_HARM_99a47 | 3sec 47th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8102 | 0x8102 | 33026 | 33026 | N_CUR_HARM_99a48 | 3sec 48th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8103 | 0x8103 | 33027 | 33027 | N_CUR_HARM_99a49 | 3sec 49th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8104 | 0x8104 | 33028 | 33028 | N_CUR_HARM_99a50 | 3sec 50th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8105 | 0x8105 | 33029 | 33029 | N_CUR_HARM_99b2 | 3sec 2nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8106 | 0x8106 | 33030 | 33030 | N_CUR_HARM_99b3 | 3sec 3rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8107 | 0x8107 | 33031 | 33031 | N_CUR_HARM_99b4 | 3sec 4th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8108 | 0x8108 | 33032 | 33032 | N_CUR_HARM_99b5 | 3sec 5th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8109 | 0x8109 | 33033 | 33033 | N_CUR_HARM_99b6 | 3sec 6th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x810A | 0x810A | 33034 | 33034 | N_CUR_HARM_99b7 | 3sec 7th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x810B | 0x810B | 33035 | 33035 | N_CUR_HARM_99b8 | 3sec 8th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x810C | 0x810C | 33036 | 33036 | N_CUR_HARM_99b9 | 3sec 9th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x810D | 0x810D | 33037 | 33037 | N_CUR_HARM_99b10 | 3sec 10th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x810E | 0x810E | 33038 | 33038 | N_CUR_HARM_99b11 | 3sec 11st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x810F | 0x810F | 33039 | 33039 | N_CUR_HARM_99b12 | 3sec 12nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8110 | 0x8110 | 33040 | 33040 | N_CUR_HARM_99b13 | 3sec 13rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8111 | 0x8111 | 33041 | 33041 | N_CUR_HARM_99b14 | 3sec 14th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8112 | 0x8112 | 33042 | 33042 | N_CUR_HARM_99b15 | 3sec 15th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8113 | 0x8113 | 33043 | 33043 | N_CUR_HARM_99b16 | 3sec 16th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8114 | 0x8114 | 33044 | 33044 | N_CUR_HARM_99b17 | 3sec 17th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8115 | 0x8115 | 33045 | 33045 | N_CUR_HARM_99b18 | 3sec 18th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8116 | 0x8116 | 33046 | 33046 | N_CUR_HARM_99b19 | 3sec 19th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8117 | 0x8117 | 33047 | 33047 | N_CUR_HARM_99b20 | 3sec 20th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8118 | 0x8118 | 33048 | 33048 | N_CUR_HARM_99b21 | 3sec 21st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8119 | 0x8119 | 33049 | 33049 | N_CUR_HARM_99b22 | 3sec 22nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x811A | 0x811A | 33050 | 33050 | N_CUR_HARM_99b23 | 3sec 23rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x811B | 0x811B | 33051 | 33051 | N_CUR_HARM_99b24 | 3sec 24th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x811C | 0x811C | 33052 | 33052 | N_CUR_HARM_99b25 | 3sec 25th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x811D | 0x811D | 33053 | 33053 | N_CUR_HARM_99b26 | 3sec 26th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x811E | 0x811E | 33054 | 33054 | N_CUR_HARM_99b27 | 3sec 27th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x811F | 0x811F | 33055 | 33055 | N_CUR_HARM_99b28 | 3sec 28th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8120 | 0x8120 | 33056 | 33056 | N_CUR_HARM_99b29 | 3sec 29th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8121 | 0x8121 | 33057 | 33057 | N_CUR_HARM_99b30 | 3sec 30th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8122 | 0x8122 | 33058 | 33058 | N_CUR_HARM_99b31 | 3sec 31st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8123 | 0x8123 | 33059 | 33059 | N_CUR_HARM_99b32 | 3sec 32nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8124 | 0x8124 | 33060 | 33060 | N_CUR_HARM_99b33 | 3sec 33rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8125 | 0x8125 | 33061 | 33061 | N_CUR_HARM_99b34 | 3sec 34th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8126 | 0x8126 | 33062 | 33062 | N_CUR_HARM_99b35 | 3sec 35th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8127 | 0x8127 | 33063 | 33063 | N_CUR_HARM_99b36 | 3sec 36th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8128 | 0x8128 | 33064 | 33064 | N_CUR_HARM_99b37 | 3sec 37th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8129 | 0x8129 | 33065 | 33065 | N_CUR_HARM_99b38 | 3sec 38th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x812A | 0x812A | 33066 | 33066 | N_CUR_HARM_99b39 | 3sec 39th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x812B | 0x812B | 33067 | 33067 | N_CUR_HARM_99b40 | 3sec 40th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x812C | 0x812C | 33068 | 33068 | N_CUR_HARM_99b41 | 3sec 41st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x812D | 0x812D | 33069 | 33069 | N_CUR_HARM_99b42 | 3sec 42nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x812E | 0x812E | 33070 | 33070 | N_CUR_HARM_99b43 | 3sec 43rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x812F | 0x812F | 33071 | 33071 | N_CUR_HARM_99b44 | 3sec 44th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8130 | 0x8130 | 33072 | 33072 | N_CUR_HARM_99b45 | 3sec 45th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8131 | 0x8131 | 33073 | 33073 | N_CUR_HARM_99b46 | 3sec 46th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8132 | 0x8132 | 33074 | 33074 | N_CUR_HARM_99b47 | 3sec 47th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8133 | 0x8133 | 33075 | 33075 | N_CUR_HARM_99b48 | 3sec 48th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8134 | 0x8134 | 33076 | 33076 | N_CUR_HARM_99b49 | 3sec 49th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8135 | 0x8135 | 33077 | 33077 | N_CUR_HARM_99b50 | 3sec 50th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8136 | 0x8136 | 33078 | 33078 | N_CUR_HARM_99c2 | 3sec 2nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8137 | 0x8137 | 33079 | 33079 | N_CUR_HARM_99c3 | 3sec 3rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8138 | 0x8138 | 33080 | 33080 | N_CUR_HARM_99c4 | 3sec 4th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8139 | 0x8139 | 33081 | 33081 | N_CUR_HARM_99c5 | 3sec 5th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x813A | 0x813A | 33082 | 33082 | N_CUR_HARM_99c6 | 3sec 6th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x813B | 0x813B | 33083 | 33083 | N_CUR_HARM_99c7 | 3sec 7th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x813C | 0x813C | 33084 | 33084 | N_CUR_HARM_99c8 | 3sec 8th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x813D | 0x813D | 33085 | 33085 | N_CUR_HARM_99c9 | 3sec 9th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x813E | 0x813E | 33086 | 33086 | N_CUR_HARM_99c10 | 3sec 10th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x813F | 0x813F | 33087 | 33087 | N_CUR_HARM_99c11 | 3sec 11st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8140 | 0x8140 | 33088 | 33088 | N_CUR_HARM_99c12 | 3sec 12nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8141 | 0x8141 | 33089 | 33089 | N_CUR_HARM_99c13 | 3sec 13rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8142 | 0x8142 | 33090 | 33090 | N_CUR_HARM_99c14 | 3sec 14th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8143 | 0x8143 | 33091 | 33091 | N_CUR_HARM_99c15 | 3sec 15th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8144 | 0x8144 | 33092 | 33092 | N_CUR_HARM_99c16 | 3sec 16th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8145 | 0x8145 | 33093 | 33093 | N_CUR_HARM_99c17 | 3sec 17th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8146 | 0x8146 | 33094 | 33094 | N_CUR_HARM_99c18 | 3sec 18th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8147 | 0x8147 | 33095 | 33095 | N_CUR_HARM_99c19 | 3sec 19th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8148 | 0x8148 | 33096 | 33096 | N_CUR_HARM_99c20 | 3sec 20th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8149 | 0x8149 | 33097 | 33097 | N_CUR_HARM_99c21 | 3sec 21st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x814A | 0x814A | 33098 | 33098 | N_CUR_HARM_99c22 | 3sec 22nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x814B | 0x814B | 33099 | 33099 | N_CUR_HARM_99c23 | 3sec 23rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x814C | 0x814C | 33100 | 33100 | N_CUR_HARM_99c24 | 3sec 24th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x814D | 0x814D | 33101 | 33101 | N_CUR_HARM_99c25 | 3sec 25th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x814E | 0x814E | 33102 | 33102 | N_CUR_HARM_99c26 | 3sec 26th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x814F | 0x814F | 33103 | 33103 | N_CUR_HARM_99c27 | 3sec 27th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8150 | 0x8150 | 33104 | 33104 | N_CUR_HARM_99c28 | 3sec 28th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8151 | 0x8151 | 33105 | 33105 | N_CUR_HARM_99c29 | 3sec 29th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8152 | 0x8152 | 33106 | 33106 | N_CUR_HARM_99c30 | 3sec 30th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8153 | 0x8153 | 33107 | 33107 | N_CUR_HARM_99c31 | 3sec 31st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8154 | 0x8154 | 33108 | 33108 | N_CUR_HARM_99c32 | 3sec 32nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8155 | 0x8155 | 33109 | 33109 | N_CUR_HARM_99c33 | 3sec 33rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8156 | 0x8156 | 33110 | 33110 | N_CUR_HARM_99c34 | 3sec 34th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8157 | 0x8157 | 33111 | 33111 | N_CUR_HARM_99c35 | 3sec 35th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8158 | 0x8158 | 33112 | 33112 | N_CUR_HARM_99c36 | 3sec 36th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8159 | 0x8159 | 33113 | 33113 | N_CUR_HARM_99c37 | 3sec 37th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x815A | 0x815A | 33114 | 33114 | N_CUR_HARM_99c38 | 3sec 38th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x815B | 0x815B | 33115 | 33115 | N_CUR_HARM_99c39 | 3sec 39th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x815C | 0x815C | 33116 | 33116 | N_CUR_HARM_99c40 | 3sec 40th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x815D | 0x815D | 33117 | 33117 | N_CUR_HARM_99c41 | 3sec 41st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x815E | 0x815E | 33118 | 33118 | N_CUR_HARM_99c42 | 3sec 42nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x815F | 0x815F | 33119 | 33119 | N_CUR_HARM_99c43 | 3sec 43rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8160 | 0x8160 | 33120 | 33120 | N_CUR_HARM_99c44 | 3sec 44th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8161 | 0x8161 | 33121 | 33121 | N_CUR_HARM_99c45 | 3sec 45th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8162 | 0x8162 | 33122 | 33122 | N_CUR_HARM_99c46 | 3sec 46th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8163 | 0x8163 | 33123 | 33123 | N_CUR_HARM_99c47 | 3sec 47th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8164 | 0x8164 | 33124 | 33124 | N_CUR_HARM_99c48 | 3sec 48th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8165 | 0x8165 | 33125 | 33125 | N_CUR_HARM_99c49 | 3sec 49th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8166 | 0x8166 | 33126 | 33126 | N_CUR_HARM_99c50 | 3sec 50th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8167 | 0x8168 | 33127 | 33128 | CUR_HARM_99_PASSa2 | 3sec 2nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8169 | 0x816A | 33129 | 33130 | CUR_HARM_99_PASSa3 | 3sec 3rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x816B | 0x816C | 33131 | 33132 | CUR_HARM_99_PASSa4 | 3sec 4th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x816D | 0x816E | 33133 | 33134 | CUR_HARM_99_PASSa5 | 3sec 5th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x816F | 0x8170 | 33135 | 33136 | CUR_HARM_99_PASSa6 | 3sec 6th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8171 | 0x8172 | 33137 | 33138 | CUR_HARM_99_PASSa7 | 3sec 7th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8173 | 0x8174 | 33139 | 33140 | CUR_HARM_99_PASSa8 | 3sec 8th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8175 | 0x8176 | 33141 | 33142 | CUR_HARM_99_PASSa9 | 3sec 9th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8177 | 0x8178 | 33143 | 33144 | CUR_HARM_99_PASSa10 | 3sec 10th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8179 | 0x817A | 33145 | 33146 | CUR_HARM_99_PASSa11 | 3sec 11st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x817B | 0x817C | 33147 | 33148 | CUR_HARM_99_PASSa12 | 3sec 12nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x817D | 0x817E | 33149 | 33150 | CUR_HARM_99_PASSa13 | 3sec 13rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x817F | 0x8180 | 33151 | 33152 | CUR_HARM_99_PASSa14 | 3sec 14th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8181 | 0x8182 | 33153 | 33154 | CUR_HARM_99_PASSa15 | 3sec 15th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8183 | 0x8184 | 33155 | 33156 | CUR_HARM_99_PASSa16 | 3sec 16th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8185 | 0x8186 | 33157 | 33158 | CUR_HARM_99_PASSa17 | 3sec 17th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8187 | 0x8188 | 33159 | 33160 | CUR_HARM_99_PASSa18 | 3sec 18th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8189 | 0x818A | 33161 | 33162 | CUR_HARM_99_PASSa19 | 3sec 19th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x818B | 0x818C | 33163 | 33164 | CUR_HARM_99_PASSa20 | 3sec 20th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x818D | 0x818E | 33165 | 33166 | CUR_HARM_99_PASSa21 | 3sec 21st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x818F | 0x8190 | 33167 | 33168 | CUR_HARM_99_PASSa22 | 3sec 22nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8191 | 0x8192 | 33169 | 33170 | CUR_HARM_99_PASSa23 | 3sec 23rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8193 | 0x8194 | 33171 | 33172 | CUR_HARM_99_PASSa24 | 3sec 24th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8195 | 0x8196 | 33173 | 33174 | CUR_HARM_99_PASSa25 | 3sec 25th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8197 | 0x8198 | 33175 | 33176 | CUR_HARM_99_PASSa26 | 3sec 26th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8199 | 0x819A | 33177 | 33178 | CUR_HARM_99_PASSa27 | 3sec 27th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x819B | 0x819C | 33179 | 33180 | CUR_HARM_99_PASSa28 | 3sec 28th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x819D | 0x819E | 33181 | 33182 | CUR_HARM_99_PASSa29 | 3sec 29th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x819F | 0x81A0 | 33183 | 33184 | CUR_HARM_99_PASSa30 | 3sec 30th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81A1 | 0x81A2 | 33185 | 33186 | CUR_HARM_99_PASSa31 | 3sec 31st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81A3 | 0x81A4 | 33187 | 33188 | CUR_HARM_99_PASSa32 | 3sec 32nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81A5 | 0x81A6 | 33189 | 33190 | CUR_HARM_99_PASSa33 | 3sec 33rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81A7 | 0x81A8 | 33191 | 33192 | CUR_HARM_99_PASSa34 | 3sec 34th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81A9 | 0x81AA | 33193 | 33194 | CUR_HARM_99_PASSa35 | 3sec 35th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81AB | 0x81AC | 33195 | 33196 | CUR_HARM_99_PASSa36 | 3sec 36th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81AD | 0x81AE | 33197 | 33198 | CUR_HARM_99_PASSa37 | 3sec 37th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81AF | 0x81B0 | 33199 | 33200 | CUR_HARM_99_PASSa38 | 3sec 38th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81B1 | 0x81B2 | 33201 | 33202 | CUR_HARM_99_PASSa39 | 3sec 39th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81B3 | 0x81B4 | 33203 | 33204 | CUR_HARM_99_PASSa40 | 3sec 40th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81B5 | 0x81B6 | 33205 | 33206 | CUR_HARM_99_PASSa41 | 3sec 41st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81B7 | 0x81B8 | 33207 | 33208 | CUR_HARM_99_PASSa42 | 3sec 42nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81B9 | 0x81BA | 33209 | 33210 | CUR_HARM_99_PASSa43 | 3sec 43rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81BB | 0x81BC | 33211 | 33212 | CUR_HARM_99_PASSa44 | 3sec 44th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81BD | 0x81BE | 33213 | 33214 | CUR_HARM_99_PASSa45 | 3sec 45th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81BF | 0x81C0 | 33215 | 33216 | CUR_HARM_99_PASSa46 | 3sec 46th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81C1 | 0x81C2 | 33217 | 33218 | CUR_HARM_99_PASSa47 | 3sec 47th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81C3 | 0x81C4 | 33219 | 33220 | CUR_HARM_99_PASSa48 | 3sec 48th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81C5 | 0x81C6 | 33221 | 33222 | CUR_HARM_99_PASSa49 | 3sec 49th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81C7 | 0x81C8 | 33223 | 33224 | CUR_HARM_99_PASSa50 | 3sec 50th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81C9 | 0x81CA | 33225 | 33226 | CUR_HARM_99_PASSb2 | 3sec 2nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81CB | 0x81CC | 33227 | 33228 | CUR_HARM_99_PASSb3 | 3sec 3rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81CD | 0x81CE | 33229 | 33230 | CUR_HARM_99_PASSb4 | 3sec 4th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81CF | 0x81D0 | 33231 | 33232 | CUR_HARM_99_PASSb5 | 3sec 5th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81D1 | 0x81D2 | 33233 | 33234 | CUR_HARM_99_PASSb6 | 3sec 6th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81D3 | 0x81D4 | 33235 | 33236 | CUR_HARM_99_PASSb7 | 3sec 7th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81D5 | 0x81D6 | 33237 | 33238 | CUR_HARM_99_PASSb8 | 3sec 8th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81D7 | 0x81D8 | 33239 | 33240 | CUR_HARM_99_PASSb9 | 3sec 9th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81D9 | 0x81DA | 33241 | 33242 | CUR_HARM_99_PASSb10 | 3sec 10th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81DB | 0x81DC | 33243 | 33244 | CUR_HARM_99_PASSb11 | 3sec 11st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81DD | 0x81DE | 33245 | 33246 | CUR_HARM_99_PASSb12 | 3sec 12nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81DF | 0x81E0 | 33247 | 33248 | CUR_HARM_99_PASSb13 | 3sec 13rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81E1 | 0x81E2 | 33249 | 33250 | CUR_HARM_99_PASSb14 | 3sec 14th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81E3 | 0x81E4 | 33251 | 33252 | CUR_HARM_99_PASSb15 | 3sec 15th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81E5 | 0x81E6 | 33253 | 33254 | CUR_HARM_99_PASSb16 | 3sec 16th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81E7 | 0x81E8 | 33255 | 33256 | CUR_HARM_99_PASSb17 | 3sec 17th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81E9 | 0x81EA | 33257 | 33258 | CUR_HARM_99_PASSb18 | 3sec 18th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81EB | 0x81EC | 33259 | 33260 | CUR_HARM_99_PASSb19 | 3sec 19th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81ED | 0x81EE | 33261 | 33262 | CUR_HARM_99_PASSb20 | 3sec 20th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81EF | 0x81F0 | 33263 | 33264 | CUR_HARM_99_PASSb21 | 3sec 21st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81F1 | 0x81F2 | 33265 | 33266 | CUR_HARM_99_PASSb22 | 3sec 22nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81F3 | 0x81F4 | 33267 | 33268 | CUR_HARM_99_PASSb23 | 3sec 23rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81F5 | 0x81F6 | 33269 | 33270 | CUR_HARM_99_PASSb24 | 3sec 24th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81F7 | 0x81F8 | 33271 | 33272 | CUR_HARM_99_PASSb25 | 3sec 25th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81F9 | 0x81FA | 33273 | 33274 | CUR_HARM_99_PASSb26 | 3sec 26th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81FB | 0x81FC | 33275 | 33276 | CUR_HARM_99_PASSb27 | 3sec 27th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81FD | 0x81FE | 33277 | 33278 | CUR_HARM_99_PASSb28 | 3sec 28th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x81FF | 0x8200 | 33279 | 33280 | CUR_HARM_99_PASSb29 | 3sec 29th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8201 | 0x8202 | 33281 | 33282 | CUR_HARM_99_PASSb30 | 3sec 30th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8203 | 0x8204 | 33283 | 33284 | CUR_HARM_99_PASSb31 | 3sec 31st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8205 | 0x8206 | 33285 | 33286 | CUR_HARM_99_PASSb32 | 3sec 32nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8207 | 0x8208 | 33287 | 33288 | CUR_HARM_99_PASSb33 | 3sec 33rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8209 | 0x820A | 33289 | 33290 | CUR_HARM_99_PASSb34 | 3sec 34th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x820B | 0x820C | 33291 | 33292 | CUR_HARM_99_PASSb35 | 3sec 35th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x820D | 0x820E | 33293 | 33294 | CUR_HARM_99_PASSb36 | 3sec 36th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x820F | 0x8210 | 33295 | 33296 | CUR_HARM_99_PASSb37 | 3sec 37th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8211 | 0x8212 | 33297 | 33298 | CUR_HARM_99_PASSb38 | 3sec 38th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8213 | 0x8214 | 33299 | 33300 | CUR_HARM_99_PASSb39 | 3sec 39th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8215 | 0x8216 | 33301 | 33302 | CUR_HARM_99_PASSb40 | 3sec 40th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8217 | 0x8218 | 33303 | 33304 | CUR_HARM_99_PASSb41 | 3sec 41st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8219 | 0x821A | 33305 | 33306 | CUR_HARM_99_PASSb42 | 3sec 42nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x821B | 0x821C | 33307 | 33308 | CUR_HARM_99_PASSb43 | 3sec 43rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x821D | 0x821E | 33309 | 33310 | CUR_HARM_99_PASSb44 | 3sec 44th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x821F | 0x8220 | 33311 | 33312 | CUR_HARM_99_PASSb45 | 3sec 45th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8221 | 0x8222 | 33313 | 33314 | CUR_HARM_99_PASSb46 | 3sec 46th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8223 | 0x8224 | 33315 | 33316 | CUR_HARM_99_PASSb47 | 3sec 47th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8225 | 0x8226 | 33317 | 33318 | CUR_HARM_99_PASSb48 | 3sec 48th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8227 | 0x8228 | 33319 | 33320 | CUR_HARM_99_PASSb49 | 3sec 49th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8229 | 0x822A | 33321 | 33322 | CUR_HARM_99_PASSb50 | 3sec 50th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x822B | 0x822C | 33323 | 33324 | CUR_HARM_99_PASSc2 | 3sec 2nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x822D | 0x822E | 33325 | 33326 | CUR_HARM_99_PASSc3 | 3sec 3rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x822F | 0x8230 | 33327 | 33328 | CUR_HARM_99_PASSc4 | 3sec 4th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8231 | 0x8232 | 33329 | 33330 | CUR_HARM_99_PASSc5 | 3sec 5th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8233 | 0x8234 | 33331 | 33332 | CUR_HARM_99_PASSc6 | 3sec 6th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8235 | 0x8236 | 33333 | 33334 | CUR_HARM_99_PASSc7 | 3sec 7th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8237 | 0x8238 | 33335 | 33336 | CUR_HARM_99_PASSc8 | 3sec 8th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8239 | 0x823A | 33337 | 33338 | CUR_HARM_99_PASSc9 | 3sec 9th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x823B | 0x823C | 33339 | 33340 | CUR_HARM_99_PASSc10 | 3sec 10th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x823D | 0x823E | 33341 | 33342 | CUR_HARM_99_PASSc11 | 3sec 11st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x823F | 0x8240 | 33343 | 33344 | CUR_HARM_99_PASSc12 | 3sec 12nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8241 | 0x8242 | 33345 | 33346 | CUR_HARM_99_PASSc13 | 3sec 13rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8243 | 0x8244 | 33347 | 33348 | CUR_HARM_99_PASSc14 | 3sec 14th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8245 | 0x8246 | 33349 | 33350 | CUR_HARM_99_PASSc15 | 3sec 15th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8247 | 0x8248 | 33351 | 33352 | CUR_HARM_99_PASSc16 | 3sec 16th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8249 | 0x824A | 33353 | 33354 | CUR_HARM_99_PASSc17 | 3sec 17th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x824B | 0x824C | 33355 | 33356 | CUR_HARM_99_PASSc18 | 3sec 18th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x824D | 0x824E | 33357 | 33358 | CUR_HARM_99_PASSc19 | 3sec 19th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x824F | 0x8250 | 33359 | 33360 | CUR_HARM_99_PASSc20 | 3sec 20th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8251 | 0x8252 | 33361 | 33362 | CUR_HARM_99_PASSc21 | 3sec 21st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8253 | 0x8254 | 33363 | 33364 | CUR_HARM_99_PASSc22 | 3sec 22nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8255 | 0x8256 | 33365 | 33366 | CUR_HARM_99_PASSc23 | 3sec 23rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8257 | 0x8258 | 33367 | 33368 | CUR_HARM_99_PASSc24 | 3sec 24th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8259 | 0x825A | 33369 | 33370 | CUR_HARM_99_PASSc25 | 3sec 25th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x825B | 0x825C | 33371 | 33372 | CUR_HARM_99_PASSc26 | 3sec 26th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x825D | 0x825E | 33373 | 33374 | CUR_HARM_99_PASSc27 | 3sec 27th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x825F | 0x8260 | 33375 | 33376 | CUR_HARM_99_PASSc28 | 3sec 28th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8261 | 0x8262 | 33377 | 33378 | CUR_HARM_99_PASSc29 | 3sec 29th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8263 | 0x8264 | 33379 | 33380 | CUR_HARM_99_PASSc30 | 3sec 30th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8265 | 0x8266 | 33381 | 33382 | CUR_HARM_99_PASSc31 | 3sec 31st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8267 | 0x8268 | 33383 | 33384 | CUR_HARM_99_PASSc32 | 3sec 32nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8269 | 0x826A | 33385 | 33386 | CUR_HARM_99_PASSc33 | 3sec 33rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x826B | 0x826C | 33387 | 33388 | CUR_HARM_99_PASSc34 | 3sec 34th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x826D | 0x826E | 33389 | 33390 | CUR_HARM_99_PASSc35 | 3sec 35th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x826F | 0x8270 | 33391 | 33392 | CUR_HARM_99_PASSc36 | 3sec 36th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8271 | 0x8272 | 33393 | 33394 | CUR_HARM_99_PASSc37 | 3sec 37th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8273 | 0x8274 | 33395 | 33396 | CUR_HARM_99_PASSc38 | 3sec 38th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8275 | 0x8276 | 33397 | 33398 | CUR_HARM_99_PASSc39 | 3sec 39th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8277 | 0x8278 | 33399 | 33400 | CUR_HARM_99_PASSc40 | 3sec 40th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8279 | 0x827A | 33401 | 33402 | CUR_HARM_99_PASSc41 | 3sec 41st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x827B | 0x827C | 33403 | 33404 | CUR_HARM_99_PASSc42 | 3sec 42nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x827D | 0x827E | 33405 | 33406 | CUR_HARM_99_PASSc43 | 3sec 43rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x827F | 0x8280 | 33407 | 33408 | CUR_HARM_99_PASSc44 | 3sec 44th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8281 | 0x8282 | 33409 | 33410 | CUR_HARM_99_PASSc45 | 3sec 45th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8283 | 0x8284 | 33411 | 33412 | CUR_HARM_99_PASSc46 | 3sec 46th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8285 | 0x8286 | 33413 | 33414 | CUR_HARM_99_PASSc47 | 3sec 47th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8287 | 0x8288 | 33415 | 33416 | CUR_HARM_99_PASSc48 | 3sec 48th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8289 | 0x828A | 33417 | 33418 | CUR_HARM_99_PASSc49 | 3sec 49th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x828B | 0x828C | 33419 | 33420 | CUR_HARM_99_PASSc50 | 3sec 50th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
PQ Report 519 Daily Last | [5 empty] | FALSE
0x8300 | 0x8300 | 33536 | 33536 | LAST_N_VALID | Last Period 3sec 519 Report Valid Circle Counter | uint16 | 1 | R
0x8301 | 0x8301 | 33537 | 33537 | LAST_N_THDa | Last Period 3sec Phase A THD Counter | uint16 | 1 | R
0x8302 | 0x8302 | 33538 | 33538 | LAST_N_THDb | Last Period 3sec Phase B THD Counter | uint16 | 1 | R
0x8303 | 0x8303 | 33539 | 33539 | LAST_N_THDc | Last Period 3sec Phase C THD Counter | uint16 | 1 | R
0x8304 | 0x8305 | 33540 | 33541 | LAST_THD_PASSa | Last Period 3sec Phase A THD Trigger Pass Rate | float | 2 | R
0x8306 | 0x8307 | 33542 | 33543 | LAST_THD_PASSb | Last Period 3sec Phase B THD Trigger Pass Rate | float | 2 | R
0x8308 | 0x8309 | 33544 | 33545 | LAST_THD_PASSc | Last Period 3sec Phase C THD Trigger Pass Rate | float | 2 | R
0x830A | 0x830B | 33546 | 33547 | LAST_THD_MAXa | Last Period 3sec Phase A THD Maximum Value | float | 2 | R
0x830C | 0x830D | 33548 | 33549 | LAST_THD_MAXb | Last Period 3sec Phase B THD Maximum Value | float | 2 | R
0x830E | 0x830F | 33550 | 33551 | LAST_THD_MAXc | Last Period 3sec Phase C THD Maximum Value | float | 2 | R
0x8310 | 0x8311 | 33552 | 33553 | LAST_THD_MINa | Last Period 3sec Phase A THD Minimum Value | float | 2 | R
0x8312 | 0x8313 | 33554 | 33555 | LAST_THD_MINb | Last Period 3sec Phase B THD Minimum Value | float | 2 | R
0x8314 | 0x8315 | 33556 | 33557 | LAST_THD_MINc | Last Period 3sec Phase C THD Minimum Value | float | 2 | R
0x8316 | 0x8317 | 33558 | 33559 | LAST_THD_AVGa | Last Period 3sec Phase A THD Average Value | float | 2 | R
0x8318 | 0x8319 | 33560 | 33561 | LAST_THD_AVGb | Last Period 3sec Phase B THD Average Value | float | 2 | R
0x831A | 0x831B | 33562 | 33563 | LAST_THD_AVGc | Last Period 3sec Phase C THD Average Value | float | 2 | R
0x831C | 0x831C | 33564 | 33564 | LAST_N_VOL_HARMa2 | Last Period 3sec 2nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x831D | 0x831D | 33565 | 33565 | LAST_N_VOL_HARMa3 | Last Period 3sec 3rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x831E | 0x831E | 33566 | 33566 | LAST_N_VOL_HARMa4 | Last Period 3sec 4th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x831F | 0x831F | 33567 | 33567 | LAST_N_VOL_HARMa5 | Last Period 3sec 5th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8320 | 0x8320 | 33568 | 33568 | LAST_N_VOL_HARMa6 | Last Period 3sec 6th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8321 | 0x8321 | 33569 | 33569 | LAST_N_VOL_HARMa7 | Last Period 3sec 7th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8322 | 0x8322 | 33570 | 33570 | LAST_N_VOL_HARMa8 | Last Period 3sec 8th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8323 | 0x8323 | 33571 | 33571 | LAST_N_VOL_HARMa9 | Last Period 3sec 9th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8324 | 0x8324 | 33572 | 33572 | LAST_N_VOL_HARMa10 | Last Period 3sec 10th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8325 | 0x8325 | 33573 | 33573 | LAST_N_VOL_HARMa11 | Last Period 3sec 11st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8326 | 0x8326 | 33574 | 33574 | LAST_N_VOL_HARMa12 | Last Period 3sec 12nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8327 | 0x8327 | 33575 | 33575 | LAST_N_VOL_HARMa13 | Last Period 3sec 13rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8328 | 0x8328 | 33576 | 33576 | LAST_N_VOL_HARMa14 | Last Period 3sec 14th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8329 | 0x8329 | 33577 | 33577 | LAST_N_VOL_HARMa15 | Last Period 3sec 15th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x832A | 0x832A | 33578 | 33578 | LAST_N_VOL_HARMa16 | Last Period 3sec 16th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x832B | 0x832B | 33579 | 33579 | LAST_N_VOL_HARMa17 | Last Period 3sec 17th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x832C | 0x832C | 33580 | 33580 | LAST_N_VOL_HARMa18 | Last Period 3sec 18th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x832D | 0x832D | 33581 | 33581 | LAST_N_VOL_HARMa19 | Last Period 3sec 19th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x832E | 0x832E | 33582 | 33582 | LAST_N_VOL_HARMa20 | Last Period 3sec 20th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x832F | 0x832F | 33583 | 33583 | LAST_N_VOL_HARMa21 | Last Period 3sec 21st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8330 | 0x8330 | 33584 | 33584 | LAST_N_VOL_HARMa22 | Last Period 3sec 22nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8331 | 0x8331 | 33585 | 33585 | LAST_N_VOL_HARMa23 | Last Period 3sec 23rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8332 | 0x8332 | 33586 | 33586 | LAST_N_VOL_HARMa24 | Last Period 3sec 24th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8333 | 0x8333 | 33587 | 33587 | LAST_N_VOL_HARMa25 | Last Period 3sec 25th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8334 | 0x8334 | 33588 | 33588 | LAST_N_VOL_HARMa26 | Last Period 3sec 26th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8335 | 0x8335 | 33589 | 33589 | LAST_N_VOL_HARMa27 | Last Period 3sec 27th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8336 | 0x8336 | 33590 | 33590 | LAST_N_VOL_HARMa28 | Last Period 3sec 28th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8337 | 0x8337 | 33591 | 33591 | LAST_N_VOL_HARMa29 | Last Period 3sec 29th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8338 | 0x8338 | 33592 | 33592 | LAST_N_VOL_HARMa30 | Last Period 3sec 30th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8339 | 0x8339 | 33593 | 33593 | LAST_N_VOL_HARMa31 | Last Period 3sec 31st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x833A | 0x833A | 33594 | 33594 | LAST_N_VOL_HARMa32 | Last Period 3sec 32nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x833B | 0x833B | 33595 | 33595 | LAST_N_VOL_HARMa33 | Last Period 3sec 33rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x833C | 0x833C | 33596 | 33596 | LAST_N_VOL_HARMa34 | Last Period 3sec 34th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x833D | 0x833D | 33597 | 33597 | LAST_N_VOL_HARMa35 | Last Period 3sec 35th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x833E | 0x833E | 33598 | 33598 | LAST_N_VOL_HARMa36 | Last Period 3sec 36th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x833F | 0x833F | 33599 | 33599 | LAST_N_VOL_HARMa37 | Last Period 3sec 37th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8340 | 0x8340 | 33600 | 33600 | LAST_N_VOL_HARMa38 | Last Period 3sec 38th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8341 | 0x8341 | 33601 | 33601 | LAST_N_VOL_HARMa39 | Last Period 3sec 39th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8342 | 0x8342 | 33602 | 33602 | LAST_N_VOL_HARMa40 | Last Period 3sec 40th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8343 | 0x8343 | 33603 | 33603 | LAST_N_VOL_HARMa41 | Last Period 3sec 41st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8344 | 0x8344 | 33604 | 33604 | LAST_N_VOL_HARMa42 | Last Period 3sec 42nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8345 | 0x8345 | 33605 | 33605 | LAST_N_VOL_HARMa43 | Last Period 3sec 43rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8346 | 0x8346 | 33606 | 33606 | LAST_N_VOL_HARMa44 | Last Period 3sec 44th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8347 | 0x8347 | 33607 | 33607 | LAST_N_VOL_HARMa45 | Last Period 3sec 45th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8348 | 0x8348 | 33608 | 33608 | LAST_N_VOL_HARMa46 | Last Period 3sec 46th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8349 | 0x8349 | 33609 | 33609 | LAST_N_VOL_HARMa47 | Last Period 3sec 47th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x834A | 0x834A | 33610 | 33610 | LAST_N_VOL_HARMa48 | Last Period 3sec 48th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x834B | 0x834B | 33611 | 33611 | LAST_N_VOL_HARMa49 | Last Period 3sec 49th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x834C | 0x834C | 33612 | 33612 | LAST_N_VOL_HARMa50 | Last Period 3sec 50th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x834D | 0x834D | 33613 | 33613 | LAST_N_VOL_HARMb2 | Last Period 3sec 2nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x834E | 0x834E | 33614 | 33614 | LAST_N_VOL_HARMb3 | Last Period 3sec 3rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x834F | 0x834F | 33615 | 33615 | LAST_N_VOL_HARMb4 | Last Period 3sec 4th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8350 | 0x8350 | 33616 | 33616 | LAST_N_VOL_HARMb5 | Last Period 3sec 5th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8351 | 0x8351 | 33617 | 33617 | LAST_N_VOL_HARMb6 | Last Period 3sec 6th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8352 | 0x8352 | 33618 | 33618 | LAST_N_VOL_HARMb7 | Last Period 3sec 7th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8353 | 0x8353 | 33619 | 33619 | LAST_N_VOL_HARMb8 | Last Period 3sec 8th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8354 | 0x8354 | 33620 | 33620 | LAST_N_VOL_HARMb9 | Last Period 3sec 9th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8355 | 0x8355 | 33621 | 33621 | LAST_N_VOL_HARMb10 | Last Period 3sec 10th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8356 | 0x8356 | 33622 | 33622 | LAST_N_VOL_HARMb11 | Last Period 3sec 11st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8357 | 0x8357 | 33623 | 33623 | LAST_N_VOL_HARMb12 | Last Period 3sec 12nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8358 | 0x8358 | 33624 | 33624 | LAST_N_VOL_HARMb13 | Last Period 3sec 13rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8359 | 0x8359 | 33625 | 33625 | LAST_N_VOL_HARMb14 | Last Period 3sec 14th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x835A | 0x835A | 33626 | 33626 | LAST_N_VOL_HARMb15 | Last Period 3sec 15th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x835B | 0x835B | 33627 | 33627 | LAST_N_VOL_HARMb16 | Last Period 3sec 16th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x835C | 0x835C | 33628 | 33628 | LAST_N_VOL_HARMb17 | Last Period 3sec 17th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x835D | 0x835D | 33629 | 33629 | LAST_N_VOL_HARMb18 | Last Period 3sec 18th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x835E | 0x835E | 33630 | 33630 | LAST_N_VOL_HARMb19 | Last Period 3sec 19th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x835F | 0x835F | 33631 | 33631 | LAST_N_VOL_HARMb20 | Last Period 3sec 20th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8360 | 0x8360 | 33632 | 33632 | LAST_N_VOL_HARMb21 | Last Period 3sec 21st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8361 | 0x8361 | 33633 | 33633 | LAST_N_VOL_HARMb22 | Last Period 3sec 22nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8362 | 0x8362 | 33634 | 33634 | LAST_N_VOL_HARMb23 | Last Period 3sec 23rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8363 | 0x8363 | 33635 | 33635 | LAST_N_VOL_HARMb24 | Last Period 3sec 24th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8364 | 0x8364 | 33636 | 33636 | LAST_N_VOL_HARMb25 | Last Period 3sec 25th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8365 | 0x8365 | 33637 | 33637 | LAST_N_VOL_HARMb26 | Last Period 3sec 26th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8366 | 0x8366 | 33638 | 33638 | LAST_N_VOL_HARMb27 | Last Period 3sec 27th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8367 | 0x8367 | 33639 | 33639 | LAST_N_VOL_HARMb28 | Last Period 3sec 28th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8368 | 0x8368 | 33640 | 33640 | LAST_N_VOL_HARMb29 | Last Period 3sec 29th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8369 | 0x8369 | 33641 | 33641 | LAST_N_VOL_HARMb30 | Last Period 3sec 30th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x836A | 0x836A | 33642 | 33642 | LAST_N_VOL_HARMb31 | Last Period 3sec 31st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x836B | 0x836B | 33643 | 33643 | LAST_N_VOL_HARMb32 | Last Period 3sec 32nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x836C | 0x836C | 33644 | 33644 | LAST_N_VOL_HARMb33 | Last Period 3sec 33rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x836D | 0x836D | 33645 | 33645 | LAST_N_VOL_HARMb34 | Last Period 3sec 34th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x836E | 0x836E | 33646 | 33646 | LAST_N_VOL_HARMb35 | Last Period 3sec 35th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x836F | 0x836F | 33647 | 33647 | LAST_N_VOL_HARMb36 | Last Period 3sec 36th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8370 | 0x8370 | 33648 | 33648 | LAST_N_VOL_HARMb37 | Last Period 3sec 37th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8371 | 0x8371 | 33649 | 33649 | LAST_N_VOL_HARMb38 | Last Period 3sec 38th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8372 | 0x8372 | 33650 | 33650 | LAST_N_VOL_HARMb39 | Last Period 3sec 39th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8373 | 0x8373 | 33651 | 33651 | LAST_N_VOL_HARMb40 | Last Period 3sec 40th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8374 | 0x8374 | 33652 | 33652 | LAST_N_VOL_HARMb41 | Last Period 3sec 41st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8375 | 0x8375 | 33653 | 33653 | LAST_N_VOL_HARMb42 | Last Period 3sec 42nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8376 | 0x8376 | 33654 | 33654 | LAST_N_VOL_HARMb43 | Last Period 3sec 43rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8377 | 0x8377 | 33655 | 33655 | LAST_N_VOL_HARMb44 | Last Period 3sec 44th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8378 | 0x8378 | 33656 | 33656 | LAST_N_VOL_HARMb45 | Last Period 3sec 45th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8379 | 0x8379 | 33657 | 33657 | LAST_N_VOL_HARMb46 | Last Period 3sec 46th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x837A | 0x837A | 33658 | 33658 | LAST_N_VOL_HARMb47 | Last Period 3sec 47th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x837B | 0x837B | 33659 | 33659 | LAST_N_VOL_HARMb48 | Last Period 3sec 48th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x837C | 0x837C | 33660 | 33660 | LAST_N_VOL_HARMb49 | Last Period 3sec 49th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x837D | 0x837D | 33661 | 33661 | LAST_N_VOL_HARMb50 | Last Period 3sec 50th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x837E | 0x837E | 33662 | 33662 | LAST_N_VOL_HARMc2 | Last Period 3sec 2nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x837F | 0x837F | 33663 | 33663 | LAST_N_VOL_HARMc3 | Last Period 3sec 3rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8380 | 0x8380 | 33664 | 33664 | LAST_N_VOL_HARMc4 | Last Period 3sec 4th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8381 | 0x8381 | 33665 | 33665 | LAST_N_VOL_HARMc5 | Last Period 3sec 5th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8382 | 0x8382 | 33666 | 33666 | LAST_N_VOL_HARMc6 | Last Period 3sec 6th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8383 | 0x8383 | 33667 | 33667 | LAST_N_VOL_HARMc7 | Last Period 3sec 7th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8384 | 0x8384 | 33668 | 33668 | LAST_N_VOL_HARMc8 | Last Period 3sec 8th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8385 | 0x8385 | 33669 | 33669 | LAST_N_VOL_HARMc9 | Last Period 3sec 9th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8386 | 0x8386 | 33670 | 33670 | LAST_N_VOL_HARMc10 | Last Period 3sec 10th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8387 | 0x8387 | 33671 | 33671 | LAST_N_VOL_HARMc11 | Last Period 3sec 11st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8388 | 0x8388 | 33672 | 33672 | LAST_N_VOL_HARMc12 | Last Period 3sec 12nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8389 | 0x8389 | 33673 | 33673 | LAST_N_VOL_HARMc13 | Last Period 3sec 13rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x838A | 0x838A | 33674 | 33674 | LAST_N_VOL_HARMc14 | Last Period 3sec 14th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x838B | 0x838B | 33675 | 33675 | LAST_N_VOL_HARMc15 | Last Period 3sec 15th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x838C | 0x838C | 33676 | 33676 | LAST_N_VOL_HARMc16 | Last Period 3sec 16th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x838D | 0x838D | 33677 | 33677 | LAST_N_VOL_HARMc17 | Last Period 3sec 17th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x838E | 0x838E | 33678 | 33678 | LAST_N_VOL_HARMc18 | Last Period 3sec 18th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x838F | 0x838F | 33679 | 33679 | LAST_N_VOL_HARMc19 | Last Period 3sec 19th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8390 | 0x8390 | 33680 | 33680 | LAST_N_VOL_HARMc20 | Last Period 3sec 20th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8391 | 0x8391 | 33681 | 33681 | LAST_N_VOL_HARMc21 | Last Period 3sec 21st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8392 | 0x8392 | 33682 | 33682 | LAST_N_VOL_HARMc22 | Last Period 3sec 22nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8393 | 0x8393 | 33683 | 33683 | LAST_N_VOL_HARMc23 | Last Period 3sec 23rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8394 | 0x8394 | 33684 | 33684 | LAST_N_VOL_HARMc24 | Last Period 3sec 24th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8395 | 0x8395 | 33685 | 33685 | LAST_N_VOL_HARMc25 | Last Period 3sec 25th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8396 | 0x8396 | 33686 | 33686 | LAST_N_VOL_HARMc26 | Last Period 3sec 26th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8397 | 0x8397 | 33687 | 33687 | LAST_N_VOL_HARMc27 | Last Period 3sec 27th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8398 | 0x8398 | 33688 | 33688 | LAST_N_VOL_HARMc28 | Last Period 3sec 28th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8399 | 0x8399 | 33689 | 33689 | LAST_N_VOL_HARMc29 | Last Period 3sec 29th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x839A | 0x839A | 33690 | 33690 | LAST_N_VOL_HARMc30 | Last Period 3sec 30th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x839B | 0x839B | 33691 | 33691 | LAST_N_VOL_HARMc31 | Last Period 3sec 31st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x839C | 0x839C | 33692 | 33692 | LAST_N_VOL_HARMc32 | Last Period 3sec 32nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x839D | 0x839D | 33693 | 33693 | LAST_N_VOL_HARMc33 | Last Period 3sec 33rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x839E | 0x839E | 33694 | 33694 | LAST_N_VOL_HARMc34 | Last Period 3sec 34th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x839F | 0x839F | 33695 | 33695 | LAST_N_VOL_HARMc35 | Last Period 3sec 35th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83A0 | 0x83A0 | 33696 | 33696 | LAST_N_VOL_HARMc36 | Last Period 3sec 36th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83A1 | 0x83A1 | 33697 | 33697 | LAST_N_VOL_HARMc37 | Last Period 3sec 37th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83A2 | 0x83A2 | 33698 | 33698 | LAST_N_VOL_HARMc38 | Last Period 3sec 38th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83A3 | 0x83A3 | 33699 | 33699 | LAST_N_VOL_HARMc39 | Last Period 3sec 39th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83A4 | 0x83A4 | 33700 | 33700 | LAST_N_VOL_HARMc40 | Last Period 3sec 40th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83A5 | 0x83A5 | 33701 | 33701 | LAST_N_VOL_HARMc41 | Last Period 3sec 41st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83A6 | 0x83A6 | 33702 | 33702 | LAST_N_VOL_HARMc42 | Last Period 3sec 42nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83A7 | 0x83A7 | 33703 | 33703 | LAST_N_VOL_HARMc43 | Last Period 3sec 43rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83A8 | 0x83A8 | 33704 | 33704 | LAST_N_VOL_HARMc44 | Last Period 3sec 44th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83A9 | 0x83A9 | 33705 | 33705 | LAST_N_VOL_HARMc45 | Last Period 3sec 45th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83AA | 0x83AA | 33706 | 33706 | LAST_N_VOL_HARMc46 | Last Period 3sec 46th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83AB | 0x83AB | 33707 | 33707 | LAST_N_VOL_HARMc47 | Last Period 3sec 47th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83AC | 0x83AC | 33708 | 33708 | LAST_N_VOL_HARMc48 | Last Period 3sec 48th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83AD | 0x83AD | 33709 | 33709 | LAST_N_VOL_HARMc49 | Last Period 3sec 49th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83AE | 0x83AE | 33710 | 33710 | LAST_N_VOL_HARMc50 | Last Period 3sec 50th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x83AF | 0x83B0 | 33711 | 33712 | LAST_VOL_HARM_PASSa2 | Last Period 3sec 2nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83B1 | 0x83B2 | 33713 | 33714 | LAST_VOL_HARM_PASSa3 | Last Period 3sec 3rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83B3 | 0x83B4 | 33715 | 33716 | LAST_VOL_HARM_PASSa4 | Last Period 3sec 4th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83B5 | 0x83B6 | 33717 | 33718 | LAST_VOL_HARM_PASSa5 | Last Period 3sec 5th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83B7 | 0x83B8 | 33719 | 33720 | LAST_VOL_HARM_PASSa6 | Last Period 3sec 6th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83B9 | 0x83BA | 33721 | 33722 | LAST_VOL_HARM_PASSa7 | Last Period 3sec 7th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83BB | 0x83BC | 33723 | 33724 | LAST_VOL_HARM_PASSa8 | Last Period 3sec 8th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83BD | 0x83BE | 33725 | 33726 | LAST_VOL_HARM_PASSa9 | Last Period 3sec 9th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83BF | 0x83C0 | 33727 | 33728 | LAST_VOL_HARM_PASSa10 | Last Period 3sec 10th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83C1 | 0x83C2 | 33729 | 33730 | LAST_VOL_HARM_PASSa11 | Last Period 3sec 11st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83C3 | 0x83C4 | 33731 | 33732 | LAST_VOL_HARM_PASSa12 | Last Period 3sec 12nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83C5 | 0x83C6 | 33733 | 33734 | LAST_VOL_HARM_PASSa13 | Last Period 3sec 13rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83C7 | 0x83C8 | 33735 | 33736 | LAST_VOL_HARM_PASSa14 | Last Period 3sec 14th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83C9 | 0x83CA | 33737 | 33738 | LAST_VOL_HARM_PASSa15 | Last Period 3sec 15th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83CB | 0x83CC | 33739 | 33740 | LAST_VOL_HARM_PASSa16 | Last Period 3sec 16th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83CD | 0x83CE | 33741 | 33742 | LAST_VOL_HARM_PASSa17 | Last Period 3sec 17th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83CF | 0x83D0 | 33743 | 33744 | LAST_VOL_HARM_PASSa18 | Last Period 3sec 18th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83D1 | 0x83D2 | 33745 | 33746 | LAST_VOL_HARM_PASSa19 | Last Period 3sec 19th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83D3 | 0x83D4 | 33747 | 33748 | LAST_VOL_HARM_PASSa20 | Last Period 3sec 20th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83D5 | 0x83D6 | 33749 | 33750 | LAST_VOL_HARM_PASSa21 | Last Period 3sec 21st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83D7 | 0x83D8 | 33751 | 33752 | LAST_VOL_HARM_PASSa22 | Last Period 3sec 22nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83D9 | 0x83DA | 33753 | 33754 | LAST_VOL_HARM_PASSa23 | Last Period 3sec 23rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83DB | 0x83DC | 33755 | 33756 | LAST_VOL_HARM_PASSa24 | Last Period 3sec 24th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83DD | 0x83DE | 33757 | 33758 | LAST_VOL_HARM_PASSa25 | Last Period 3sec 25th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83DF | 0x83E0 | 33759 | 33760 | LAST_VOL_HARM_PASSa26 | Last Period 3sec 26th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83E1 | 0x83E2 | 33761 | 33762 | LAST_VOL_HARM_PASSa27 | Last Period 3sec 27th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83E3 | 0x83E4 | 33763 | 33764 | LAST_VOL_HARM_PASSa28 | Last Period 3sec 28th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83E5 | 0x83E6 | 33765 | 33766 | LAST_VOL_HARM_PASSa29 | Last Period 3sec 29th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83E7 | 0x83E8 | 33767 | 33768 | LAST_VOL_HARM_PASSa30 | Last Period 3sec 30th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83E9 | 0x83EA | 33769 | 33770 | LAST_VOL_HARM_PASSa31 | Last Period 3sec 31st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83EB | 0x83EC | 33771 | 33772 | LAST_VOL_HARM_PASSa32 | Last Period 3sec 32nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83ED | 0x83EE | 33773 | 33774 | LAST_VOL_HARM_PASSa33 | Last Period 3sec 33rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83EF | 0x83F0 | 33775 | 33776 | LAST_VOL_HARM_PASSa34 | Last Period 3sec 34th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83F1 | 0x83F2 | 33777 | 33778 | LAST_VOL_HARM_PASSa35 | Last Period 3sec 35th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83F3 | 0x83F4 | 33779 | 33780 | LAST_VOL_HARM_PASSa36 | Last Period 3sec 36th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83F5 | 0x83F6 | 33781 | 33782 | LAST_VOL_HARM_PASSa37 | Last Period 3sec 37th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83F7 | 0x83F8 | 33783 | 33784 | LAST_VOL_HARM_PASSa38 | Last Period 3sec 38th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83F9 | 0x83FA | 33785 | 33786 | LAST_VOL_HARM_PASSa39 | Last Period 3sec 39th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83FB | 0x83FC | 33787 | 33788 | LAST_VOL_HARM_PASSa40 | Last Period 3sec 40th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83FD | 0x83FE | 33789 | 33790 | LAST_VOL_HARM_PASSa41 | Last Period 3sec 41st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x83FF | 0x8400 | 33791 | 33792 | LAST_VOL_HARM_PASSa42 | Last Period 3sec 42nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8401 | 0x8402 | 33793 | 33794 | LAST_VOL_HARM_PASSa43 | Last Period 3sec 43rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8403 | 0x8404 | 33795 | 33796 | LAST_VOL_HARM_PASSa44 | Last Period 3sec 44th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8405 | 0x8406 | 33797 | 33798 | LAST_VOL_HARM_PASSa45 | Last Period 3sec 45th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8407 | 0x8408 | 33799 | 33800 | LAST_VOL_HARM_PASSa46 | Last Period 3sec 46th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8409 | 0x840A | 33801 | 33802 | LAST_VOL_HARM_PASSa47 | Last Period 3sec 47th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x840B | 0x840C | 33803 | 33804 | LAST_VOL_HARM_PASSa48 | Last Period 3sec 48th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x840D | 0x840E | 33805 | 33806 | LAST_VOL_HARM_PASSa49 | Last Period 3sec 49th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x840F | 0x8410 | 33807 | 33808 | LAST_VOL_HARM_PASSa50 | Last Period 3sec 50th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8411 | 0x8412 | 33809 | 33810 | LAST_VOL_HARM_PASSb2 | Last Period 3sec 2nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8413 | 0x8414 | 33811 | 33812 | LAST_VOL_HARM_PASSb3 | Last Period 3sec 3rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8415 | 0x8416 | 33813 | 33814 | LAST_VOL_HARM_PASSb4 | Last Period 3sec 4th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8417 | 0x8418 | 33815 | 33816 | LAST_VOL_HARM_PASSb5 | Last Period 3sec 5th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8419 | 0x841A | 33817 | 33818 | LAST_VOL_HARM_PASSb6 | Last Period 3sec 6th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x841B | 0x841C | 33819 | 33820 | LAST_VOL_HARM_PASSb7 | Last Period 3sec 7th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x841D | 0x841E | 33821 | 33822 | LAST_VOL_HARM_PASSb8 | Last Period 3sec 8th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x841F | 0x8420 | 33823 | 33824 | LAST_VOL_HARM_PASSb9 | Last Period 3sec 9th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8421 | 0x8422 | 33825 | 33826 | LAST_VOL_HARM_PASSb10 | Last Period 3sec 10th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8423 | 0x8424 | 33827 | 33828 | LAST_VOL_HARM_PASSb11 | Last Period 3sec 11st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8425 | 0x8426 | 33829 | 33830 | LAST_VOL_HARM_PASSb12 | Last Period 3sec 12nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8427 | 0x8428 | 33831 | 33832 | LAST_VOL_HARM_PASSb13 | Last Period 3sec 13rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8429 | 0x842A | 33833 | 33834 | LAST_VOL_HARM_PASSb14 | Last Period 3sec 14th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x842B | 0x842C | 33835 | 33836 | LAST_VOL_HARM_PASSb15 | Last Period 3sec 15th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x842D | 0x842E | 33837 | 33838 | LAST_VOL_HARM_PASSb16 | Last Period 3sec 16th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x842F | 0x8430 | 33839 | 33840 | LAST_VOL_HARM_PASSb17 | Last Period 3sec 17th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8431 | 0x8432 | 33841 | 33842 | LAST_VOL_HARM_PASSb18 | Last Period 3sec 18th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8433 | 0x8434 | 33843 | 33844 | LAST_VOL_HARM_PASSb19 | Last Period 3sec 19th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8435 | 0x8436 | 33845 | 33846 | LAST_VOL_HARM_PASSb20 | Last Period 3sec 20th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8437 | 0x8438 | 33847 | 33848 | LAST_VOL_HARM_PASSb21 | Last Period 3sec 21st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8439 | 0x843A | 33849 | 33850 | LAST_VOL_HARM_PASSb22 | Last Period 3sec 22nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x843B | 0x843C | 33851 | 33852 | LAST_VOL_HARM_PASSb23 | Last Period 3sec 23rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x843D | 0x843E | 33853 | 33854 | LAST_VOL_HARM_PASSb24 | Last Period 3sec 24th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x843F | 0x8440 | 33855 | 33856 | LAST_VOL_HARM_PASSb25 | Last Period 3sec 25th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8441 | 0x8442 | 33857 | 33858 | LAST_VOL_HARM_PASSb26 | Last Period 3sec 26th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8443 | 0x8444 | 33859 | 33860 | LAST_VOL_HARM_PASSb27 | Last Period 3sec 27th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8445 | 0x8446 | 33861 | 33862 | LAST_VOL_HARM_PASSb28 | Last Period 3sec 28th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8447 | 0x8448 | 33863 | 33864 | LAST_VOL_HARM_PASSb29 | Last Period 3sec 29th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8449 | 0x844A | 33865 | 33866 | LAST_VOL_HARM_PASSb30 | Last Period 3sec 30th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x844B | 0x844C | 33867 | 33868 | LAST_VOL_HARM_PASSb31 | Last Period 3sec 31st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x844D | 0x844E | 33869 | 33870 | LAST_VOL_HARM_PASSb32 | Last Period 3sec 32nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x844F | 0x8450 | 33871 | 33872 | LAST_VOL_HARM_PASSb33 | Last Period 3sec 33rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8451 | 0x8452 | 33873 | 33874 | LAST_VOL_HARM_PASSb34 | Last Period 3sec 34th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8453 | 0x8454 | 33875 | 33876 | LAST_VOL_HARM_PASSb35 | Last Period 3sec 35th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8455 | 0x8456 | 33877 | 33878 | LAST_VOL_HARM_PASSb36 | Last Period 3sec 36th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8457 | 0x8458 | 33879 | 33880 | LAST_VOL_HARM_PASSb37 | Last Period 3sec 37th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8459 | 0x845A | 33881 | 33882 | LAST_VOL_HARM_PASSb38 | Last Period 3sec 38th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x845B | 0x845C | 33883 | 33884 | LAST_VOL_HARM_PASSb39 | Last Period 3sec 39th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x845D | 0x845E | 33885 | 33886 | LAST_VOL_HARM_PASSb40 | Last Period 3sec 40th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x845F | 0x8460 | 33887 | 33888 | LAST_VOL_HARM_PASSb41 | Last Period 3sec 41st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8461 | 0x8462 | 33889 | 33890 | LAST_VOL_HARM_PASSb42 | Last Period 3sec 42nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8463 | 0x8464 | 33891 | 33892 | LAST_VOL_HARM_PASSb43 | Last Period 3sec 43rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8465 | 0x8466 | 33893 | 33894 | LAST_VOL_HARM_PASSb44 | Last Period 3sec 44th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8467 | 0x8468 | 33895 | 33896 | LAST_VOL_HARM_PASSb45 | Last Period 3sec 45th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8469 | 0x846A | 33897 | 33898 | LAST_VOL_HARM_PASSb46 | Last Period 3sec 46th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x846B | 0x846C | 33899 | 33900 | LAST_VOL_HARM_PASSb47 | Last Period 3sec 47th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x846D | 0x846E | 33901 | 33902 | LAST_VOL_HARM_PASSb48 | Last Period 3sec 48th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x846F | 0x8470 | 33903 | 33904 | LAST_VOL_HARM_PASSb49 | Last Period 3sec 49th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8471 | 0x8472 | 33905 | 33906 | LAST_VOL_HARM_PASSb50 | Last Period 3sec 50th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8473 | 0x8474 | 33907 | 33908 | LAST_VOL_HARM_PASSc2 | Last Period 3sec 2nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8475 | 0x8476 | 33909 | 33910 | LAST_VOL_HARM_PASSc3 | Last Period 3sec 3rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8477 | 0x8478 | 33911 | 33912 | LAST_VOL_HARM_PASSc4 | Last Period 3sec 4th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8479 | 0x847A | 33913 | 33914 | LAST_VOL_HARM_PASSc5 | Last Period 3sec 5th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x847B | 0x847C | 33915 | 33916 | LAST_VOL_HARM_PASSc6 | Last Period 3sec 6th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x847D | 0x847E | 33917 | 33918 | LAST_VOL_HARM_PASSc7 | Last Period 3sec 7th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x847F | 0x8480 | 33919 | 33920 | LAST_VOL_HARM_PASSc8 | Last Period 3sec 8th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8481 | 0x8482 | 33921 | 33922 | LAST_VOL_HARM_PASSc9 | Last Period 3sec 9th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8483 | 0x8484 | 33923 | 33924 | LAST_VOL_HARM_PASSc10 | Last Period 3sec 10th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8485 | 0x8486 | 33925 | 33926 | LAST_VOL_HARM_PASSc11 | Last Period 3sec 11st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8487 | 0x8488 | 33927 | 33928 | LAST_VOL_HARM_PASSc12 | Last Period 3sec 12nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8489 | 0x848A | 33929 | 33930 | LAST_VOL_HARM_PASSc13 | Last Period 3sec 13rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x848B | 0x848C | 33931 | 33932 | LAST_VOL_HARM_PASSc14 | Last Period 3sec 14th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x848D | 0x848E | 33933 | 33934 | LAST_VOL_HARM_PASSc15 | Last Period 3sec 15th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x848F | 0x8490 | 33935 | 33936 | LAST_VOL_HARM_PASSc16 | Last Period 3sec 16th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8491 | 0x8492 | 33937 | 33938 | LAST_VOL_HARM_PASSc17 | Last Period 3sec 17th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8493 | 0x8494 | 33939 | 33940 | LAST_VOL_HARM_PASSc18 | Last Period 3sec 18th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8495 | 0x8496 | 33941 | 33942 | LAST_VOL_HARM_PASSc19 | Last Period 3sec 19th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8497 | 0x8498 | 33943 | 33944 | LAST_VOL_HARM_PASSc20 | Last Period 3sec 20th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8499 | 0x849A | 33945 | 33946 | LAST_VOL_HARM_PASSc21 | Last Period 3sec 21st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x849B | 0x849C | 33947 | 33948 | LAST_VOL_HARM_PASSc22 | Last Period 3sec 22nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x849D | 0x849E | 33949 | 33950 | LAST_VOL_HARM_PASSc23 | Last Period 3sec 23rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x849F | 0x84A0 | 33951 | 33952 | LAST_VOL_HARM_PASSc24 | Last Period 3sec 24th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84A1 | 0x84A2 | 33953 | 33954 | LAST_VOL_HARM_PASSc25 | Last Period 3sec 25th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84A3 | 0x84A4 | 33955 | 33956 | LAST_VOL_HARM_PASSc26 | Last Period 3sec 26th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84A5 | 0x84A6 | 33957 | 33958 | LAST_VOL_HARM_PASSc27 | Last Period 3sec 27th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84A7 | 0x84A8 | 33959 | 33960 | LAST_VOL_HARM_PASSc28 | Last Period 3sec 28th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84A9 | 0x84AA | 33961 | 33962 | LAST_VOL_HARM_PASSc29 | Last Period 3sec 29th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84AB | 0x84AC | 33963 | 33964 | LAST_VOL_HARM_PASSc30 | Last Period 3sec 30th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84AD | 0x84AE | 33965 | 33966 | LAST_VOL_HARM_PASSc31 | Last Period 3sec 31st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84AF | 0x84B0 | 33967 | 33968 | LAST_VOL_HARM_PASSc32 | Last Period 3sec 32nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84B1 | 0x84B2 | 33969 | 33970 | LAST_VOL_HARM_PASSc33 | Last Period 3sec 33rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84B3 | 0x84B4 | 33971 | 33972 | LAST_VOL_HARM_PASSc34 | Last Period 3sec 34th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84B5 | 0x84B6 | 33973 | 33974 | LAST_VOL_HARM_PASSc35 | Last Period 3sec 35th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84B7 | 0x84B8 | 33975 | 33976 | LAST_VOL_HARM_PASSc36 | Last Period 3sec 36th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84B9 | 0x84BA | 33977 | 33978 | LAST_VOL_HARM_PASSc37 | Last Period 3sec 37th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84BB | 0x84BC | 33979 | 33980 | LAST_VOL_HARM_PASSc38 | Last Period 3sec 38th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84BD | 0x84BE | 33981 | 33982 | LAST_VOL_HARM_PASSc39 | Last Period 3sec 39th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84BF | 0x84C0 | 33983 | 33984 | LAST_VOL_HARM_PASSc40 | Last Period 3sec 40th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84C1 | 0x84C2 | 33985 | 33986 | LAST_VOL_HARM_PASSc41 | Last Period 3sec 41st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84C3 | 0x84C4 | 33987 | 33988 | LAST_VOL_HARM_PASSc42 | Last Period 3sec 42nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84C5 | 0x84C6 | 33989 | 33990 | LAST_VOL_HARM_PASSc43 | Last Period 3sec 43rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84C7 | 0x84C8 | 33991 | 33992 | LAST_VOL_HARM_PASSc44 | Last Period 3sec 44th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84C9 | 0x84CA | 33993 | 33994 | LAST_VOL_HARM_PASSc45 | Last Period 3sec 45th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84CB | 0x84CC | 33995 | 33996 | LAST_VOL_HARM_PASSc46 | Last Period 3sec 46th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84CD | 0x84CE | 33997 | 33998 | LAST_VOL_HARM_PASSc47 | Last Period 3sec 47th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84CF | 0x84D0 | 33999 | 34000 | LAST_VOL_HARM_PASSc48 | Last Period 3sec 48th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84D1 | 0x84D2 | 34001 | 34002 | LAST_VOL_HARM_PASSc49 | Last Period 3sec 49th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84D3 | 0x84D4 | 34003 | 34004 | LAST_VOL_HARM_PASSc50 | Last Period 3sec 50th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x84D5 | 0x84D6 | 34005 | 34006 | LAST_VOL_HARM_MAXa2 | Last Period 3sec 2nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84D7 | 0x84D8 | 34007 | 34008 | LAST_VOL_HARM_MAXa3 | Last Period 3sec 3rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84D9 | 0x84DA | 34009 | 34010 | LAST_VOL_HARM_MAXa4 | Last Period 3sec 4th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84DB | 0x84DC | 34011 | 34012 | LAST_VOL_HARM_MAXa5 | Last Period 3sec 5th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84DD | 0x84DE | 34013 | 34014 | LAST_VOL_HARM_MAXa6 | Last Period 3sec 6th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84DF | 0x84E0 | 34015 | 34016 | LAST_VOL_HARM_MAXa7 | Last Period 3sec 7th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84E1 | 0x84E2 | 34017 | 34018 | LAST_VOL_HARM_MAXa8 | Last Period 3sec 8th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84E3 | 0x84E4 | 34019 | 34020 | LAST_VOL_HARM_MAXa9 | Last Period 3sec 9th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84E5 | 0x84E6 | 34021 | 34022 | LAST_VOL_HARM_MAXa10 | Last Period 3sec 10th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84E7 | 0x84E8 | 34023 | 34024 | LAST_VOL_HARM_MAXa11 | Last Period 3sec 11st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84E9 | 0x84EA | 34025 | 34026 | LAST_VOL_HARM_MAXa12 | Last Period 3sec 12nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84EB | 0x84EC | 34027 | 34028 | LAST_VOL_HARM_MAXa13 | Last Period 3sec 13rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84ED | 0x84EE | 34029 | 34030 | LAST_VOL_HARM_MAXa14 | Last Period 3sec 14th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84EF | 0x84F0 | 34031 | 34032 | LAST_VOL_HARM_MAXa15 | Last Period 3sec 15th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84F1 | 0x84F2 | 34033 | 34034 | LAST_VOL_HARM_MAXa16 | Last Period 3sec 16th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84F3 | 0x84F4 | 34035 | 34036 | LAST_VOL_HARM_MAXa17 | Last Period 3sec 17th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84F5 | 0x84F6 | 34037 | 34038 | LAST_VOL_HARM_MAXa18 | Last Period 3sec 18th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84F7 | 0x84F8 | 34039 | 34040 | LAST_VOL_HARM_MAXa19 | Last Period 3sec 19th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84F9 | 0x84FA | 34041 | 34042 | LAST_VOL_HARM_MAXa20 | Last Period 3sec 20th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84FB | 0x84FC | 34043 | 34044 | LAST_VOL_HARM_MAXa21 | Last Period 3sec 21st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84FD | 0x84FE | 34045 | 34046 | LAST_VOL_HARM_MAXa22 | Last Period 3sec 22nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x84FF | 0x8500 | 34047 | 34048 | LAST_VOL_HARM_MAXa23 | Last Period 3sec 23rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8501 | 0x8502 | 34049 | 34050 | LAST_VOL_HARM_MAXa24 | Last Period 3sec 24th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8503 | 0x8504 | 34051 | 34052 | LAST_VOL_HARM_MAXa25 | Last Period 3sec 25th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8505 | 0x8506 | 34053 | 34054 | LAST_VOL_HARM_MAXa26 | Last Period 3sec 26th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8507 | 0x8508 | 34055 | 34056 | LAST_VOL_HARM_MAXa27 | Last Period 3sec 27th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8509 | 0x850A | 34057 | 34058 | LAST_VOL_HARM_MAXa28 | Last Period 3sec 28th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x850B | 0x850C | 34059 | 34060 | LAST_VOL_HARM_MAXa29 | Last Period 3sec 29th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x850D | 0x850E | 34061 | 34062 | LAST_VOL_HARM_MAXa30 | Last Period 3sec 30th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x850F | 0x8510 | 34063 | 34064 | LAST_VOL_HARM_MAXa31 | Last Period 3sec 31st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8511 | 0x8512 | 34065 | 34066 | LAST_VOL_HARM_MAXa32 | Last Period 3sec 32nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8513 | 0x8514 | 34067 | 34068 | LAST_VOL_HARM_MAXa33 | Last Period 3sec 33rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8515 | 0x8516 | 34069 | 34070 | LAST_VOL_HARM_MAXa34 | Last Period 3sec 34th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8517 | 0x8518 | 34071 | 34072 | LAST_VOL_HARM_MAXa35 | Last Period 3sec 35th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8519 | 0x851A | 34073 | 34074 | LAST_VOL_HARM_MAXa36 | Last Period 3sec 36th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x851B | 0x851C | 34075 | 34076 | LAST_VOL_HARM_MAXa37 | Last Period 3sec 37th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x851D | 0x851E | 34077 | 34078 | LAST_VOL_HARM_MAXa38 | Last Period 3sec 38th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x851F | 0x8520 | 34079 | 34080 | LAST_VOL_HARM_MAXa39 | Last Period 3sec 39th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8521 | 0x8522 | 34081 | 34082 | LAST_VOL_HARM_MAXa40 | Last Period 3sec 40th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8523 | 0x8524 | 34083 | 34084 | LAST_VOL_HARM_MAXa41 | Last Period 3sec 41st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8525 | 0x8526 | 34085 | 34086 | LAST_VOL_HARM_MAXa42 | Last Period 3sec 42nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8527 | 0x8528 | 34087 | 34088 | LAST_VOL_HARM_MAXa43 | Last Period 3sec 43rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8529 | 0x852A | 34089 | 34090 | LAST_VOL_HARM_MAXa44 | Last Period 3sec 44th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x852B | 0x852C | 34091 | 34092 | LAST_VOL_HARM_MAXa45 | Last Period 3sec 45th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x852D | 0x852E | 34093 | 34094 | LAST_VOL_HARM_MAXa46 | Last Period 3sec 46th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x852F | 0x8530 | 34095 | 34096 | LAST_VOL_HARM_MAXa47 | Last Period 3sec 47th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8531 | 0x8532 | 34097 | 34098 | LAST_VOL_HARM_MAXa48 | Last Period 3sec 48th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8533 | 0x8534 | 34099 | 34100 | LAST_VOL_HARM_MAXa49 | Last Period 3sec 49th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8535 | 0x8536 | 34101 | 34102 | LAST_VOL_HARM_MAXa50 | Last Period 3sec 50th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8537 | 0x8538 | 34103 | 34104 | LAST_VOL_HARM_MAXb2 | Last Period 3sec 2nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8539 | 0x853A | 34105 | 34106 | LAST_VOL_HARM_MAXb3 | Last Period 3sec 3rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x853B | 0x853C | 34107 | 34108 | LAST_VOL_HARM_MAXb4 | Last Period 3sec 4th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x853D | 0x853E | 34109 | 34110 | LAST_VOL_HARM_MAXb5 | Last Period 3sec 5th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x853F | 0x8540 | 34111 | 34112 | LAST_VOL_HARM_MAXb6 | Last Period 3sec 6th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8541 | 0x8542 | 34113 | 34114 | LAST_VOL_HARM_MAXb7 | Last Period 3sec 7th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8543 | 0x8544 | 34115 | 34116 | LAST_VOL_HARM_MAXb8 | Last Period 3sec 8th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8545 | 0x8546 | 34117 | 34118 | LAST_VOL_HARM_MAXb9 | Last Period 3sec 9th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8547 | 0x8548 | 34119 | 34120 | LAST_VOL_HARM_MAXb10 | Last Period 3sec 10th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8549 | 0x854A | 34121 | 34122 | LAST_VOL_HARM_MAXb11 | Last Period 3sec 11st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x854B | 0x854C | 34123 | 34124 | LAST_VOL_HARM_MAXb12 | Last Period 3sec 12nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x854D | 0x854E | 34125 | 34126 | LAST_VOL_HARM_MAXb13 | Last Period 3sec 13rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x854F | 0x8550 | 34127 | 34128 | LAST_VOL_HARM_MAXb14 | Last Period 3sec 14th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8551 | 0x8552 | 34129 | 34130 | LAST_VOL_HARM_MAXb15 | Last Period 3sec 15th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8553 | 0x8554 | 34131 | 34132 | LAST_VOL_HARM_MAXb16 | Last Period 3sec 16th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8555 | 0x8556 | 34133 | 34134 | LAST_VOL_HARM_MAXb17 | Last Period 3sec 17th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8557 | 0x8558 | 34135 | 34136 | LAST_VOL_HARM_MAXb18 | Last Period 3sec 18th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8559 | 0x855A | 34137 | 34138 | LAST_VOL_HARM_MAXb19 | Last Period 3sec 19th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x855B | 0x855C | 34139 | 34140 | LAST_VOL_HARM_MAXb20 | Last Period 3sec 20th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x855D | 0x855E | 34141 | 34142 | LAST_VOL_HARM_MAXb21 | Last Period 3sec 21st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x855F | 0x8560 | 34143 | 34144 | LAST_VOL_HARM_MAXb22 | Last Period 3sec 22nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8561 | 0x8562 | 34145 | 34146 | LAST_VOL_HARM_MAXb23 | Last Period 3sec 23rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8563 | 0x8564 | 34147 | 34148 | LAST_VOL_HARM_MAXb24 | Last Period 3sec 24th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8565 | 0x8566 | 34149 | 34150 | LAST_VOL_HARM_MAXb25 | Last Period 3sec 25th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8567 | 0x8568 | 34151 | 34152 | LAST_VOL_HARM_MAXb26 | Last Period 3sec 26th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8569 | 0x856A | 34153 | 34154 | LAST_VOL_HARM_MAXb27 | Last Period 3sec 27th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x856B | 0x856C | 34155 | 34156 | LAST_VOL_HARM_MAXb28 | Last Period 3sec 28th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x856D | 0x856E | 34157 | 34158 | LAST_VOL_HARM_MAXb29 | Last Period 3sec 29th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x856F | 0x8570 | 34159 | 34160 | LAST_VOL_HARM_MAXb30 | Last Period 3sec 30th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8571 | 0x8572 | 34161 | 34162 | LAST_VOL_HARM_MAXb31 | Last Period 3sec 31st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8573 | 0x8574 | 34163 | 34164 | LAST_VOL_HARM_MAXb32 | Last Period 3sec 32nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8575 | 0x8576 | 34165 | 34166 | LAST_VOL_HARM_MAXb33 | Last Period 3sec 33rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8577 | 0x8578 | 34167 | 34168 | LAST_VOL_HARM_MAXb34 | Last Period 3sec 34th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8579 | 0x857A | 34169 | 34170 | LAST_VOL_HARM_MAXb35 | Last Period 3sec 35th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x857B | 0x857C | 34171 | 34172 | LAST_VOL_HARM_MAXb36 | Last Period 3sec 36th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x857D | 0x857E | 34173 | 34174 | LAST_VOL_HARM_MAXb37 | Last Period 3sec 37th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x857F | 0x8580 | 34175 | 34176 | LAST_VOL_HARM_MAXb38 | Last Period 3sec 38th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8581 | 0x8582 | 34177 | 34178 | LAST_VOL_HARM_MAXb39 | Last Period 3sec 39th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8583 | 0x8584 | 34179 | 34180 | LAST_VOL_HARM_MAXb40 | Last Period 3sec 40th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8585 | 0x8586 | 34181 | 34182 | LAST_VOL_HARM_MAXb41 | Last Period 3sec 41st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8587 | 0x8588 | 34183 | 34184 | LAST_VOL_HARM_MAXb42 | Last Period 3sec 42nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8589 | 0x858A | 34185 | 34186 | LAST_VOL_HARM_MAXb43 | Last Period 3sec 43rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x858B | 0x858C | 34187 | 34188 | LAST_VOL_HARM_MAXb44 | Last Period 3sec 44th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x858D | 0x858E | 34189 | 34190 | LAST_VOL_HARM_MAXb45 | Last Period 3sec 45th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x858F | 0x8590 | 34191 | 34192 | LAST_VOL_HARM_MAXb46 | Last Period 3sec 46th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8591 | 0x8592 | 34193 | 34194 | LAST_VOL_HARM_MAXb47 | Last Period 3sec 47th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8593 | 0x8594 | 34195 | 34196 | LAST_VOL_HARM_MAXb48 | Last Period 3sec 48th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8595 | 0x8596 | 34197 | 34198 | LAST_VOL_HARM_MAXb49 | Last Period 3sec 49th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8597 | 0x8598 | 34199 | 34200 | LAST_VOL_HARM_MAXb50 | Last Period 3sec 50th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x8599 | 0x859A | 34201 | 34202 | LAST_VOL_HARM_MAXc2 | Last Period 3sec 2nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x859B | 0x859C | 34203 | 34204 | LAST_VOL_HARM_MAXc3 | Last Period 3sec 3rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x859D | 0x859E | 34205 | 34206 | LAST_VOL_HARM_MAXc4 | Last Period 3sec 4th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x859F | 0x85A0 | 34207 | 34208 | LAST_VOL_HARM_MAXc5 | Last Period 3sec 5th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85A1 | 0x85A2 | 34209 | 34210 | LAST_VOL_HARM_MAXc6 | Last Period 3sec 6th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85A3 | 0x85A4 | 34211 | 34212 | LAST_VOL_HARM_MAXc7 | Last Period 3sec 7th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85A5 | 0x85A6 | 34213 | 34214 | LAST_VOL_HARM_MAXc8 | Last Period 3sec 8th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85A7 | 0x85A8 | 34215 | 34216 | LAST_VOL_HARM_MAXc9 | Last Period 3sec 9th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85A9 | 0x85AA | 34217 | 34218 | LAST_VOL_HARM_MAXc10 | Last Period 3sec 10th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85AB | 0x85AC | 34219 | 34220 | LAST_VOL_HARM_MAXc11 | Last Period 3sec 11st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85AD | 0x85AE | 34221 | 34222 | LAST_VOL_HARM_MAXc12 | Last Period 3sec 12nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85AF | 0x85B0 | 34223 | 34224 | LAST_VOL_HARM_MAXc13 | Last Period 3sec 13rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85B1 | 0x85B2 | 34225 | 34226 | LAST_VOL_HARM_MAXc14 | Last Period 3sec 14th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85B3 | 0x85B4 | 34227 | 34228 | LAST_VOL_HARM_MAXc15 | Last Period 3sec 15th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85B5 | 0x85B6 | 34229 | 34230 | LAST_VOL_HARM_MAXc16 | Last Period 3sec 16th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85B7 | 0x85B8 | 34231 | 34232 | LAST_VOL_HARM_MAXc17 | Last Period 3sec 17th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85B9 | 0x85BA | 34233 | 34234 | LAST_VOL_HARM_MAXc18 | Last Period 3sec 18th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85BB | 0x85BC | 34235 | 34236 | LAST_VOL_HARM_MAXc19 | Last Period 3sec 19th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85BD | 0x85BE | 34237 | 34238 | LAST_VOL_HARM_MAXc20 | Last Period 3sec 20th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85BF | 0x85C0 | 34239 | 34240 | LAST_VOL_HARM_MAXc21 | Last Period 3sec 21st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85C1 | 0x85C2 | 34241 | 34242 | LAST_VOL_HARM_MAXc22 | Last Period 3sec 22nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85C3 | 0x85C4 | 34243 | 34244 | LAST_VOL_HARM_MAXc23 | Last Period 3sec 23rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85C5 | 0x85C6 | 34245 | 34246 | LAST_VOL_HARM_MAXc24 | Last Period 3sec 24th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85C7 | 0x85C8 | 34247 | 34248 | LAST_VOL_HARM_MAXc25 | Last Period 3sec 25th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85C9 | 0x85CA | 34249 | 34250 | LAST_VOL_HARM_MAXc26 | Last Period 3sec 26th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85CB | 0x85CC | 34251 | 34252 | LAST_VOL_HARM_MAXc27 | Last Period 3sec 27th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85CD | 0x85CE | 34253 | 34254 | LAST_VOL_HARM_MAXc28 | Last Period 3sec 28th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85CF | 0x85D0 | 34255 | 34256 | LAST_VOL_HARM_MAXc29 | Last Period 3sec 29th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85D1 | 0x85D2 | 34257 | 34258 | LAST_VOL_HARM_MAXc30 | Last Period 3sec 30th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85D3 | 0x85D4 | 34259 | 34260 | LAST_VOL_HARM_MAXc31 | Last Period 3sec 31st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85D5 | 0x85D6 | 34261 | 34262 | LAST_VOL_HARM_MAXc32 | Last Period 3sec 32nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85D7 | 0x85D8 | 34263 | 34264 | LAST_VOL_HARM_MAXc33 | Last Period 3sec 33rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85D9 | 0x85DA | 34265 | 34266 | LAST_VOL_HARM_MAXc34 | Last Period 3sec 34th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85DB | 0x85DC | 34267 | 34268 | LAST_VOL_HARM_MAXc35 | Last Period 3sec 35th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85DD | 0x85DE | 34269 | 34270 | LAST_VOL_HARM_MAXc36 | Last Period 3sec 36th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85DF | 0x85E0 | 34271 | 34272 | LAST_VOL_HARM_MAXc37 | Last Period 3sec 37th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85E1 | 0x85E2 | 34273 | 34274 | LAST_VOL_HARM_MAXc38 | Last Period 3sec 38th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85E3 | 0x85E4 | 34275 | 34276 | LAST_VOL_HARM_MAXc39 | Last Period 3sec 39th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85E5 | 0x85E6 | 34277 | 34278 | LAST_VOL_HARM_MAXc40 | Last Period 3sec 40th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85E7 | 0x85E8 | 34279 | 34280 | LAST_VOL_HARM_MAXc41 | Last Period 3sec 41st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85E9 | 0x85EA | 34281 | 34282 | LAST_VOL_HARM_MAXc42 | Last Period 3sec 42nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85EB | 0x85EC | 34283 | 34284 | LAST_VOL_HARM_MAXc43 | Last Period 3sec 43rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85ED | 0x85EE | 34285 | 34286 | LAST_VOL_HARM_MAXc44 | Last Period 3sec 44th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85EF | 0x85F0 | 34287 | 34288 | LAST_VOL_HARM_MAXc45 | Last Period 3sec 45th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85F1 | 0x85F2 | 34289 | 34290 | LAST_VOL_HARM_MAXc46 | Last Period 3sec 46th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85F3 | 0x85F4 | 34291 | 34292 | LAST_VOL_HARM_MAXc47 | Last Period 3sec 47th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85F5 | 0x85F6 | 34293 | 34294 | LAST_VOL_HARM_MAXc48 | Last Period 3sec 48th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85F7 | 0x85F8 | 34295 | 34296 | LAST_VOL_HARM_MAXc49 | Last Period 3sec 49th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85F9 | 0x85FA | 34297 | 34298 | LAST_VOL_HARM_MAXc50 | Last Period 3sec 50th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x85FB | 0x85FC | 34299 | 34300 | LAST_VOL_HARM_MINa2 | Last Period 3sec 2nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x85FD | 0x85FE | 34301 | 34302 | LAST_VOL_HARM_MINa3 | Last Period 3sec 3rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x85FF | 0x8600 | 34303 | 34304 | LAST_VOL_HARM_MINa4 | Last Period 3sec 4th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8601 | 0x8602 | 34305 | 34306 | LAST_VOL_HARM_MINa5 | Last Period 3sec 5th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8603 | 0x8604 | 34307 | 34308 | LAST_VOL_HARM_MINa6 | Last Period 3sec 6th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8605 | 0x8606 | 34309 | 34310 | LAST_VOL_HARM_MINa7 | Last Period 3sec 7th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8607 | 0x8608 | 34311 | 34312 | LAST_VOL_HARM_MINa8 | Last Period 3sec 8th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8609 | 0x860A | 34313 | 34314 | LAST_VOL_HARM_MINa9 | Last Period 3sec 9th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x860B | 0x860C | 34315 | 34316 | LAST_VOL_HARM_MINa10 | Last Period 3sec 10th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x860D | 0x860E | 34317 | 34318 | LAST_VOL_HARM_MINa11 | Last Period 3sec 11st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x860F | 0x8610 | 34319 | 34320 | LAST_VOL_HARM_MINa12 | Last Period 3sec 12nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8611 | 0x8612 | 34321 | 34322 | LAST_VOL_HARM_MINa13 | Last Period 3sec 13rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8613 | 0x8614 | 34323 | 34324 | LAST_VOL_HARM_MINa14 | Last Period 3sec 14th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8615 | 0x8616 | 34325 | 34326 | LAST_VOL_HARM_MINa15 | Last Period 3sec 15th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8617 | 0x8618 | 34327 | 34328 | LAST_VOL_HARM_MINa16 | Last Period 3sec 16th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8619 | 0x861A | 34329 | 34330 | LAST_VOL_HARM_MINa17 | Last Period 3sec 17th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x861B | 0x861C | 34331 | 34332 | LAST_VOL_HARM_MINa18 | Last Period 3sec 18th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x861D | 0x861E | 34333 | 34334 | LAST_VOL_HARM_MINa19 | Last Period 3sec 19th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x861F | 0x8620 | 34335 | 34336 | LAST_VOL_HARM_MINa20 | Last Period 3sec 20th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8621 | 0x8622 | 34337 | 34338 | LAST_VOL_HARM_MINa21 | Last Period 3sec 21st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8623 | 0x8624 | 34339 | 34340 | LAST_VOL_HARM_MINa22 | Last Period 3sec 22nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8625 | 0x8626 | 34341 | 34342 | LAST_VOL_HARM_MINa23 | Last Period 3sec 23rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8627 | 0x8628 | 34343 | 34344 | LAST_VOL_HARM_MINa24 | Last Period 3sec 24th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8629 | 0x862A | 34345 | 34346 | LAST_VOL_HARM_MINa25 | Last Period 3sec 25th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x862B | 0x862C | 34347 | 34348 | LAST_VOL_HARM_MINa26 | Last Period 3sec 26th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x862D | 0x862E | 34349 | 34350 | LAST_VOL_HARM_MINa27 | Last Period 3sec 27th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x862F | 0x8630 | 34351 | 34352 | LAST_VOL_HARM_MINa28 | Last Period 3sec 28th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8631 | 0x8632 | 34353 | 34354 | LAST_VOL_HARM_MINa29 | Last Period 3sec 29th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8633 | 0x8634 | 34355 | 34356 | LAST_VOL_HARM_MINa30 | Last Period 3sec 30th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8635 | 0x8636 | 34357 | 34358 | LAST_VOL_HARM_MINa31 | Last Period 3sec 31st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8637 | 0x8638 | 34359 | 34360 | LAST_VOL_HARM_MINa32 | Last Period 3sec 32nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8639 | 0x863A | 34361 | 34362 | LAST_VOL_HARM_MINa33 | Last Period 3sec 33rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x863B | 0x863C | 34363 | 34364 | LAST_VOL_HARM_MINa34 | Last Period 3sec 34th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x863D | 0x863E | 34365 | 34366 | LAST_VOL_HARM_MINa35 | Last Period 3sec 35th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x863F | 0x8640 | 34367 | 34368 | LAST_VOL_HARM_MINa36 | Last Period 3sec 36th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8641 | 0x8642 | 34369 | 34370 | LAST_VOL_HARM_MINa37 | Last Period 3sec 37th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8643 | 0x8644 | 34371 | 34372 | LAST_VOL_HARM_MINa38 | Last Period 3sec 38th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8645 | 0x8646 | 34373 | 34374 | LAST_VOL_HARM_MINa39 | Last Period 3sec 39th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8647 | 0x8648 | 34375 | 34376 | LAST_VOL_HARM_MINa40 | Last Period 3sec 40th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8649 | 0x864A | 34377 | 34378 | LAST_VOL_HARM_MINa41 | Last Period 3sec 41st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x864B | 0x864C | 34379 | 34380 | LAST_VOL_HARM_MINa42 | Last Period 3sec 42nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x864D | 0x864E | 34381 | 34382 | LAST_VOL_HARM_MINa43 | Last Period 3sec 43rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x864F | 0x8650 | 34383 | 34384 | LAST_VOL_HARM_MINa44 | Last Period 3sec 44th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8651 | 0x8652 | 34385 | 34386 | LAST_VOL_HARM_MINa45 | Last Period 3sec 45th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8653 | 0x8654 | 34387 | 34388 | LAST_VOL_HARM_MINa46 | Last Period 3sec 46th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8655 | 0x8656 | 34389 | 34390 | LAST_VOL_HARM_MINa47 | Last Period 3sec 47th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8657 | 0x8658 | 34391 | 34392 | LAST_VOL_HARM_MINa48 | Last Period 3sec 48th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x8659 | 0x865A | 34393 | 34394 | LAST_VOL_HARM_MINa49 | Last Period 3sec 49th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x865B | 0x865C | 34395 | 34396 | LAST_VOL_HARM_MINa50 | Last Period 3sec 50th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x865D | 0x865E | 34397 | 34398 | LAST_VOL_HARM_MINb2 | Last Period 3sec 2nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x865F | 0x8660 | 34399 | 34400 | LAST_VOL_HARM_MINb3 | Last Period 3sec 3rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8661 | 0x8662 | 34401 | 34402 | LAST_VOL_HARM_MINb4 | Last Period 3sec 4th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8663 | 0x8664 | 34403 | 34404 | LAST_VOL_HARM_MINb5 | Last Period 3sec 5th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8665 | 0x8666 | 34405 | 34406 | LAST_VOL_HARM_MINb6 | Last Period 3sec 6th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8667 | 0x8668 | 34407 | 34408 | LAST_VOL_HARM_MINb7 | Last Period 3sec 7th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8669 | 0x866A | 34409 | 34410 | LAST_VOL_HARM_MINb8 | Last Period 3sec 8th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x866B | 0x866C | 34411 | 34412 | LAST_VOL_HARM_MINb9 | Last Period 3sec 9th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x866D | 0x866E | 34413 | 34414 | LAST_VOL_HARM_MINb10 | Last Period 3sec 10th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x866F | 0x8670 | 34415 | 34416 | LAST_VOL_HARM_MINb11 | Last Period 3sec 11st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8671 | 0x8672 | 34417 | 34418 | LAST_VOL_HARM_MINb12 | Last Period 3sec 12nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8673 | 0x8674 | 34419 | 34420 | LAST_VOL_HARM_MINb13 | Last Period 3sec 13rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8675 | 0x8676 | 34421 | 34422 | LAST_VOL_HARM_MINb14 | Last Period 3sec 14th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8677 | 0x8678 | 34423 | 34424 | LAST_VOL_HARM_MINb15 | Last Period 3sec 15th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8679 | 0x867A | 34425 | 34426 | LAST_VOL_HARM_MINb16 | Last Period 3sec 16th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x867B | 0x867C | 34427 | 34428 | LAST_VOL_HARM_MINb17 | Last Period 3sec 17th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x867D | 0x867E | 34429 | 34430 | LAST_VOL_HARM_MINb18 | Last Period 3sec 18th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x867F | 0x8680 | 34431 | 34432 | LAST_VOL_HARM_MINb19 | Last Period 3sec 19th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8681 | 0x8682 | 34433 | 34434 | LAST_VOL_HARM_MINb20 | Last Period 3sec 20th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8683 | 0x8684 | 34435 | 34436 | LAST_VOL_HARM_MINb21 | Last Period 3sec 21st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8685 | 0x8686 | 34437 | 34438 | LAST_VOL_HARM_MINb22 | Last Period 3sec 22nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8687 | 0x8688 | 34439 | 34440 | LAST_VOL_HARM_MINb23 | Last Period 3sec 23rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8689 | 0x868A | 34441 | 34442 | LAST_VOL_HARM_MINb24 | Last Period 3sec 24th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x868B | 0x868C | 34443 | 34444 | LAST_VOL_HARM_MINb25 | Last Period 3sec 25th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x868D | 0x868E | 34445 | 34446 | LAST_VOL_HARM_MINb26 | Last Period 3sec 26th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x868F | 0x8690 | 34447 | 34448 | LAST_VOL_HARM_MINb27 | Last Period 3sec 27th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8691 | 0x8692 | 34449 | 34450 | LAST_VOL_HARM_MINb28 | Last Period 3sec 28th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8693 | 0x8694 | 34451 | 34452 | LAST_VOL_HARM_MINb29 | Last Period 3sec 29th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8695 | 0x8696 | 34453 | 34454 | LAST_VOL_HARM_MINb30 | Last Period 3sec 30th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8697 | 0x8698 | 34455 | 34456 | LAST_VOL_HARM_MINb31 | Last Period 3sec 31st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x8699 | 0x869A | 34457 | 34458 | LAST_VOL_HARM_MINb32 | Last Period 3sec 32nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x869B | 0x869C | 34459 | 34460 | LAST_VOL_HARM_MINb33 | Last Period 3sec 33rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x869D | 0x869E | 34461 | 34462 | LAST_VOL_HARM_MINb34 | Last Period 3sec 34th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x869F | 0x86A0 | 34463 | 34464 | LAST_VOL_HARM_MINb35 | Last Period 3sec 35th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86A1 | 0x86A2 | 34465 | 34466 | LAST_VOL_HARM_MINb36 | Last Period 3sec 36th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86A3 | 0x86A4 | 34467 | 34468 | LAST_VOL_HARM_MINb37 | Last Period 3sec 37th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86A5 | 0x86A6 | 34469 | 34470 | LAST_VOL_HARM_MINb38 | Last Period 3sec 38th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86A7 | 0x86A8 | 34471 | 34472 | LAST_VOL_HARM_MINb39 | Last Period 3sec 39th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86A9 | 0x86AA | 34473 | 34474 | LAST_VOL_HARM_MINb40 | Last Period 3sec 40th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86AB | 0x86AC | 34475 | 34476 | LAST_VOL_HARM_MINb41 | Last Period 3sec 41st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86AD | 0x86AE | 34477 | 34478 | LAST_VOL_HARM_MINb42 | Last Period 3sec 42nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86AF | 0x86B0 | 34479 | 34480 | LAST_VOL_HARM_MINb43 | Last Period 3sec 43rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86B1 | 0x86B2 | 34481 | 34482 | LAST_VOL_HARM_MINb44 | Last Period 3sec 44th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86B3 | 0x86B4 | 34483 | 34484 | LAST_VOL_HARM_MINb45 | Last Period 3sec 45th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86B5 | 0x86B6 | 34485 | 34486 | LAST_VOL_HARM_MINb46 | Last Period 3sec 46th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86B7 | 0x86B8 | 34487 | 34488 | LAST_VOL_HARM_MINb47 | Last Period 3sec 47th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86B9 | 0x86BA | 34489 | 34490 | LAST_VOL_HARM_MINb48 | Last Period 3sec 48th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86BB | 0x86BC | 34491 | 34492 | LAST_VOL_HARM_MINb49 | Last Period 3sec 49th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86BD | 0x86BE | 34493 | 34494 | LAST_VOL_HARM_MINb50 | Last Period 3sec 50th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x86BF | 0x86C0 | 34495 | 34496 | LAST_VOL_HARM_MINc2 | Last Period 3sec 2nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86C1 | 0x86C2 | 34497 | 34498 | LAST_VOL_HARM_MINc3 | Last Period 3sec 3rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86C3 | 0x86C4 | 34499 | 34500 | LAST_VOL_HARM_MINc4 | Last Period 3sec 4th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86C5 | 0x86C6 | 34501 | 34502 | LAST_VOL_HARM_MINc5 | Last Period 3sec 5th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86C7 | 0x86C8 | 34503 | 34504 | LAST_VOL_HARM_MINc6 | Last Period 3sec 6th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86C9 | 0x86CA | 34505 | 34506 | LAST_VOL_HARM_MINc7 | Last Period 3sec 7th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86CB | 0x86CC | 34507 | 34508 | LAST_VOL_HARM_MINc8 | Last Period 3sec 8th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86CD | 0x86CE | 34509 | 34510 | LAST_VOL_HARM_MINc9 | Last Period 3sec 9th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86CF | 0x86D0 | 34511 | 34512 | LAST_VOL_HARM_MINc10 | Last Period 3sec 10th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86D1 | 0x86D2 | 34513 | 34514 | LAST_VOL_HARM_MINc11 | Last Period 3sec 11st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86D3 | 0x86D4 | 34515 | 34516 | LAST_VOL_HARM_MINc12 | Last Period 3sec 12nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86D5 | 0x86D6 | 34517 | 34518 | LAST_VOL_HARM_MINc13 | Last Period 3sec 13rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86D7 | 0x86D8 | 34519 | 34520 | LAST_VOL_HARM_MINc14 | Last Period 3sec 14th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86D9 | 0x86DA | 34521 | 34522 | LAST_VOL_HARM_MINc15 | Last Period 3sec 15th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86DB | 0x86DC | 34523 | 34524 | LAST_VOL_HARM_MINc16 | Last Period 3sec 16th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86DD | 0x86DE | 34525 | 34526 | LAST_VOL_HARM_MINc17 | Last Period 3sec 17th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86DF | 0x86E0 | 34527 | 34528 | LAST_VOL_HARM_MINc18 | Last Period 3sec 18th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86E1 | 0x86E2 | 34529 | 34530 | LAST_VOL_HARM_MINc19 | Last Period 3sec 19th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86E3 | 0x86E4 | 34531 | 34532 | LAST_VOL_HARM_MINc20 | Last Period 3sec 20th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86E5 | 0x86E6 | 34533 | 34534 | LAST_VOL_HARM_MINc21 | Last Period 3sec 21st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86E7 | 0x86E8 | 34535 | 34536 | LAST_VOL_HARM_MINc22 | Last Period 3sec 22nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86E9 | 0x86EA | 34537 | 34538 | LAST_VOL_HARM_MINc23 | Last Period 3sec 23rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86EB | 0x86EC | 34539 | 34540 | LAST_VOL_HARM_MINc24 | Last Period 3sec 24th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86ED | 0x86EE | 34541 | 34542 | LAST_VOL_HARM_MINc25 | Last Period 3sec 25th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86EF | 0x86F0 | 34543 | 34544 | LAST_VOL_HARM_MINc26 | Last Period 3sec 26th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86F1 | 0x86F2 | 34545 | 34546 | LAST_VOL_HARM_MINc27 | Last Period 3sec 27th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86F3 | 0x86F4 | 34547 | 34548 | LAST_VOL_HARM_MINc28 | Last Period 3sec 28th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86F5 | 0x86F6 | 34549 | 34550 | LAST_VOL_HARM_MINc29 | Last Period 3sec 29th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86F7 | 0x86F8 | 34551 | 34552 | LAST_VOL_HARM_MINc30 | Last Period 3sec 30th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86F9 | 0x86FA | 34553 | 34554 | LAST_VOL_HARM_MINc31 | Last Period 3sec 31st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86FB | 0x86FC | 34555 | 34556 | LAST_VOL_HARM_MINc32 | Last Period 3sec 32nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86FD | 0x86FE | 34557 | 34558 | LAST_VOL_HARM_MINc33 | Last Period 3sec 33rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x86FF | 0x8700 | 34559 | 34560 | LAST_VOL_HARM_MINc34 | Last Period 3sec 34th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x8701 | 0x8702 | 34561 | 34562 | LAST_VOL_HARM_MINc35 | Last Period 3sec 35th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x8703 | 0x8704 | 34563 | 34564 | LAST_VOL_HARM_MINc36 | Last Period 3sec 36th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x8705 | 0x8706 | 34565 | 34566 | LAST_VOL_HARM_MINc37 | Last Period 3sec 37th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x8707 | 0x8708 | 34567 | 34568 | LAST_VOL_HARM_MINc38 | Last Period 3sec 38th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x8709 | 0x870A | 34569 | 34570 | LAST_VOL_HARM_MINc39 | Last Period 3sec 39th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x870B | 0x870C | 34571 | 34572 | LAST_VOL_HARM_MINc40 | Last Period 3sec 40th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x870D | 0x870E | 34573 | 34574 | LAST_VOL_HARM_MINc41 | Last Period 3sec 41st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x870F | 0x8710 | 34575 | 34576 | LAST_VOL_HARM_MINc42 | Last Period 3sec 42nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x8711 | 0x8712 | 34577 | 34578 | LAST_VOL_HARM_MINc43 | Last Period 3sec 43rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x8713 | 0x8714 | 34579 | 34580 | LAST_VOL_HARM_MINc44 | Last Period 3sec 44th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x8715 | 0x8716 | 34581 | 34582 | LAST_VOL_HARM_MINc45 | Last Period 3sec 45th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x8717 | 0x8718 | 34583 | 34584 | LAST_VOL_HARM_MINc46 | Last Period 3sec 46th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x8719 | 0x871A | 34585 | 34586 | LAST_VOL_HARM_MINc47 | Last Period 3sec 47th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x871B | 0x871C | 34587 | 34588 | LAST_VOL_HARM_MINc48 | Last Period 3sec 48th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x871D | 0x871E | 34589 | 34590 | LAST_VOL_HARM_MINc49 | Last Period 3sec 49th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x871F | 0x8720 | 34591 | 34592 | LAST_VOL_HARM_MINc50 | Last Period 3sec 50th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x8721 | 0x8722 | 34593 | 34594 | LAST_VOL_HARM_AVGa2 | Last Period 3sec 2nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x8723 | 0x8724 | 34595 | 34596 | LAST_VOL_HARM_AVGa3 | Last Period 3sec 3rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x8725 | 0x8726 | 34597 | 34598 | LAST_VOL_HARM_AVGa4 | Last Period 3sec 4th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8727 | 0x8728 | 34599 | 34600 | LAST_VOL_HARM_AVGa5 | Last Period 3sec 5th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8729 | 0x872A | 34601 | 34602 | LAST_VOL_HARM_AVGa6 | Last Period 3sec 6th Phase A Voltage Harmonics Average Value | float | 2 | R
0x872B | 0x872C | 34603 | 34604 | LAST_VOL_HARM_AVGa7 | Last Period 3sec 7th Phase A Voltage Harmonics Average Value | float | 2 | R
0x872D | 0x872E | 34605 | 34606 | LAST_VOL_HARM_AVGa8 | Last Period 3sec 8th Phase A Voltage Harmonics Average Value | float | 2 | R
0x872F | 0x8730 | 34607 | 34608 | LAST_VOL_HARM_AVGa9 | Last Period 3sec 9th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8731 | 0x8732 | 34609 | 34610 | LAST_VOL_HARM_AVGa10 | Last Period 3sec 10th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8733 | 0x8734 | 34611 | 34612 | LAST_VOL_HARM_AVGa11 | Last Period 3sec 11st Phase A Voltage Harmonics Average Value | float | 2 | R
0x8735 | 0x8736 | 34613 | 34614 | LAST_VOL_HARM_AVGa12 | Last Period 3sec 12nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x8737 | 0x8738 | 34615 | 34616 | LAST_VOL_HARM_AVGa13 | Last Period 3sec 13rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x8739 | 0x873A | 34617 | 34618 | LAST_VOL_HARM_AVGa14 | Last Period 3sec 14th Phase A Voltage Harmonics Average Value | float | 2 | R
0x873B | 0x873C | 34619 | 34620 | LAST_VOL_HARM_AVGa15 | Last Period 3sec 15th Phase A Voltage Harmonics Average Value | float | 2 | R
0x873D | 0x873E | 34621 | 34622 | LAST_VOL_HARM_AVGa16 | Last Period 3sec 16th Phase A Voltage Harmonics Average Value | float | 2 | R
0x873F | 0x8740 | 34623 | 34624 | LAST_VOL_HARM_AVGa17 | Last Period 3sec 17th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8741 | 0x8742 | 34625 | 34626 | LAST_VOL_HARM_AVGa18 | Last Period 3sec 18th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8743 | 0x8744 | 34627 | 34628 | LAST_VOL_HARM_AVGa19 | Last Period 3sec 19th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8745 | 0x8746 | 34629 | 34630 | LAST_VOL_HARM_AVGa20 | Last Period 3sec 20th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8747 | 0x8748 | 34631 | 34632 | LAST_VOL_HARM_AVGa21 | Last Period 3sec 21st Phase A Voltage Harmonics Average Value | float | 2 | R
0x8749 | 0x874A | 34633 | 34634 | LAST_VOL_HARM_AVGa22 | Last Period 3sec 22nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x874B | 0x874C | 34635 | 34636 | LAST_VOL_HARM_AVGa23 | Last Period 3sec 23rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x874D | 0x874E | 34637 | 34638 | LAST_VOL_HARM_AVGa24 | Last Period 3sec 24th Phase A Voltage Harmonics Average Value | float | 2 | R
0x874F | 0x8750 | 34639 | 34640 | LAST_VOL_HARM_AVGa25 | Last Period 3sec 25th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8751 | 0x8752 | 34641 | 34642 | LAST_VOL_HARM_AVGa26 | Last Period 3sec 26th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8753 | 0x8754 | 34643 | 34644 | LAST_VOL_HARM_AVGa27 | Last Period 3sec 27th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8755 | 0x8756 | 34645 | 34646 | LAST_VOL_HARM_AVGa28 | Last Period 3sec 28th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8757 | 0x8758 | 34647 | 34648 | LAST_VOL_HARM_AVGa29 | Last Period 3sec 29th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8759 | 0x875A | 34649 | 34650 | LAST_VOL_HARM_AVGa30 | Last Period 3sec 30th Phase A Voltage Harmonics Average Value | float | 2 | R
0x875B | 0x875C | 34651 | 34652 | LAST_VOL_HARM_AVGa31 | Last Period 3sec 31st Phase A Voltage Harmonics Average Value | float | 2 | R
0x875D | 0x875E | 34653 | 34654 | LAST_VOL_HARM_AVGa32 | Last Period 3sec 32nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x875F | 0x8760 | 34655 | 34656 | LAST_VOL_HARM_AVGa33 | Last Period 3sec 33rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x8761 | 0x8762 | 34657 | 34658 | LAST_VOL_HARM_AVGa34 | Last Period 3sec 34th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8763 | 0x8764 | 34659 | 34660 | LAST_VOL_HARM_AVGa35 | Last Period 3sec 35th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8765 | 0x8766 | 34661 | 34662 | LAST_VOL_HARM_AVGa36 | Last Period 3sec 36th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8767 | 0x8768 | 34663 | 34664 | LAST_VOL_HARM_AVGa37 | Last Period 3sec 37th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8769 | 0x876A | 34665 | 34666 | LAST_VOL_HARM_AVGa38 | Last Period 3sec 38th Phase A Voltage Harmonics Average Value | float | 2 | R
0x876B | 0x876C | 34667 | 34668 | LAST_VOL_HARM_AVGa39 | Last Period 3sec 39th Phase A Voltage Harmonics Average Value | float | 2 | R
0x876D | 0x876E | 34669 | 34670 | LAST_VOL_HARM_AVGa40 | Last Period 3sec 40th Phase A Voltage Harmonics Average Value | float | 2 | R
0x876F | 0x8770 | 34671 | 34672 | LAST_VOL_HARM_AVGa41 | Last Period 3sec 41st Phase A Voltage Harmonics Average Value | float | 2 | R
0x8771 | 0x8772 | 34673 | 34674 | LAST_VOL_HARM_AVGa42 | Last Period 3sec 42nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x8773 | 0x8774 | 34675 | 34676 | LAST_VOL_HARM_AVGa43 | Last Period 3sec 43rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x8775 | 0x8776 | 34677 | 34678 | LAST_VOL_HARM_AVGa44 | Last Period 3sec 44th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8777 | 0x8778 | 34679 | 34680 | LAST_VOL_HARM_AVGa45 | Last Period 3sec 45th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8779 | 0x877A | 34681 | 34682 | LAST_VOL_HARM_AVGa46 | Last Period 3sec 46th Phase A Voltage Harmonics Average Value | float | 2 | R
0x877B | 0x877C | 34683 | 34684 | LAST_VOL_HARM_AVGa47 | Last Period 3sec 47th Phase A Voltage Harmonics Average Value | float | 2 | R
0x877D | 0x877E | 34685 | 34686 | LAST_VOL_HARM_AVGa48 | Last Period 3sec 48th Phase A Voltage Harmonics Average Value | float | 2 | R
0x877F | 0x8780 | 34687 | 34688 | LAST_VOL_HARM_AVGa49 | Last Period 3sec 49th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8781 | 0x8782 | 34689 | 34690 | LAST_VOL_HARM_AVGa50 | Last Period 3sec 50th Phase A Voltage Harmonics Average Value | float | 2 | R
0x8783 | 0x8784 | 34691 | 34692 | LAST_VOL_HARM_AVGb2 | Last Period 3sec 2nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x8785 | 0x8786 | 34693 | 34694 | LAST_VOL_HARM_AVGb3 | Last Period 3sec 3rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x8787 | 0x8788 | 34695 | 34696 | LAST_VOL_HARM_AVGb4 | Last Period 3sec 4th Phase B Voltage Harmonics Average Value | float | 2 | R
0x8789 | 0x878A | 34697 | 34698 | LAST_VOL_HARM_AVGb5 | Last Period 3sec 5th Phase B Voltage Harmonics Average Value | float | 2 | R
0x878B | 0x878C | 34699 | 34700 | LAST_VOL_HARM_AVGb6 | Last Period 3sec 6th Phase B Voltage Harmonics Average Value | float | 2 | R
0x878D | 0x878E | 34701 | 34702 | LAST_VOL_HARM_AVGb7 | Last Period 3sec 7th Phase B Voltage Harmonics Average Value | float | 2 | R
0x878F | 0x8790 | 34703 | 34704 | LAST_VOL_HARM_AVGb8 | Last Period 3sec 8th Phase B Voltage Harmonics Average Value | float | 2 | R
0x8791 | 0x8792 | 34705 | 34706 | LAST_VOL_HARM_AVGb9 | Last Period 3sec 9th Phase B Voltage Harmonics Average Value | float | 2 | R
0x8793 | 0x8794 | 34707 | 34708 | LAST_VOL_HARM_AVGb10 | Last Period 3sec 10th Phase B Voltage Harmonics Average Value | float | 2 | R
0x8795 | 0x8796 | 34709 | 34710 | LAST_VOL_HARM_AVGb11 | Last Period 3sec 11st Phase B Voltage Harmonics Average Value | float | 2 | R
0x8797 | 0x8798 | 34711 | 34712 | LAST_VOL_HARM_AVGb12 | Last Period 3sec 12nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x8799 | 0x879A | 34713 | 34714 | LAST_VOL_HARM_AVGb13 | Last Period 3sec 13rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x879B | 0x879C | 34715 | 34716 | LAST_VOL_HARM_AVGb14 | Last Period 3sec 14th Phase B Voltage Harmonics Average Value | float | 2 | R
0x879D | 0x879E | 34717 | 34718 | LAST_VOL_HARM_AVGb15 | Last Period 3sec 15th Phase B Voltage Harmonics Average Value | float | 2 | R
0x879F | 0x87A0 | 34719 | 34720 | LAST_VOL_HARM_AVGb16 | Last Period 3sec 16th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87A1 | 0x87A2 | 34721 | 34722 | LAST_VOL_HARM_AVGb17 | Last Period 3sec 17th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87A3 | 0x87A4 | 34723 | 34724 | LAST_VOL_HARM_AVGb18 | Last Period 3sec 18th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87A5 | 0x87A6 | 34725 | 34726 | LAST_VOL_HARM_AVGb19 | Last Period 3sec 19th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87A7 | 0x87A8 | 34727 | 34728 | LAST_VOL_HARM_AVGb20 | Last Period 3sec 20th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87A9 | 0x87AA | 34729 | 34730 | LAST_VOL_HARM_AVGb21 | Last Period 3sec 21st Phase B Voltage Harmonics Average Value | float | 2 | R
0x87AB | 0x87AC | 34731 | 34732 | LAST_VOL_HARM_AVGb22 | Last Period 3sec 22nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x87AD | 0x87AE | 34733 | 34734 | LAST_VOL_HARM_AVGb23 | Last Period 3sec 23rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x87AF | 0x87B0 | 34735 | 34736 | LAST_VOL_HARM_AVGb24 | Last Period 3sec 24th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87B1 | 0x87B2 | 34737 | 34738 | LAST_VOL_HARM_AVGb25 | Last Period 3sec 25th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87B3 | 0x87B4 | 34739 | 34740 | LAST_VOL_HARM_AVGb26 | Last Period 3sec 26th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87B5 | 0x87B6 | 34741 | 34742 | LAST_VOL_HARM_AVGb27 | Last Period 3sec 27th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87B7 | 0x87B8 | 34743 | 34744 | LAST_VOL_HARM_AVGb28 | Last Period 3sec 28th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87B9 | 0x87BA | 34745 | 34746 | LAST_VOL_HARM_AVGb29 | Last Period 3sec 29th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87BB | 0x87BC | 34747 | 34748 | LAST_VOL_HARM_AVGb30 | Last Period 3sec 30th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87BD | 0x87BE | 34749 | 34750 | LAST_VOL_HARM_AVGb31 | Last Period 3sec 31st Phase B Voltage Harmonics Average Value | float | 2 | R
0x87BF | 0x87C0 | 34751 | 34752 | LAST_VOL_HARM_AVGb32 | Last Period 3sec 32nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x87C1 | 0x87C2 | 34753 | 34754 | LAST_VOL_HARM_AVGb33 | Last Period 3sec 33rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x87C3 | 0x87C4 | 34755 | 34756 | LAST_VOL_HARM_AVGb34 | Last Period 3sec 34th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87C5 | 0x87C6 | 34757 | 34758 | LAST_VOL_HARM_AVGb35 | Last Period 3sec 35th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87C7 | 0x87C8 | 34759 | 34760 | LAST_VOL_HARM_AVGb36 | Last Period 3sec 36th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87C9 | 0x87CA | 34761 | 34762 | LAST_VOL_HARM_AVGb37 | Last Period 3sec 37th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87CB | 0x87CC | 34763 | 34764 | LAST_VOL_HARM_AVGb38 | Last Period 3sec 38th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87CD | 0x87CE | 34765 | 34766 | LAST_VOL_HARM_AVGb39 | Last Period 3sec 39th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87CF | 0x87D0 | 34767 | 34768 | LAST_VOL_HARM_AVGb40 | Last Period 3sec 40th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87D1 | 0x87D2 | 34769 | 34770 | LAST_VOL_HARM_AVGb41 | Last Period 3sec 41st Phase B Voltage Harmonics Average Value | float | 2 | R
0x87D3 | 0x87D4 | 34771 | 34772 | LAST_VOL_HARM_AVGb42 | Last Period 3sec 42nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x87D5 | 0x87D6 | 34773 | 34774 | LAST_VOL_HARM_AVGb43 | Last Period 3sec 43rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x87D7 | 0x87D8 | 34775 | 34776 | LAST_VOL_HARM_AVGb44 | Last Period 3sec 44th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87D9 | 0x87DA | 34777 | 34778 | LAST_VOL_HARM_AVGb45 | Last Period 3sec 45th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87DB | 0x87DC | 34779 | 34780 | LAST_VOL_HARM_AVGb46 | Last Period 3sec 46th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87DD | 0x87DE | 34781 | 34782 | LAST_VOL_HARM_AVGb47 | Last Period 3sec 47th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87DF | 0x87E0 | 34783 | 34784 | LAST_VOL_HARM_AVGb48 | Last Period 3sec 48th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87E1 | 0x87E2 | 34785 | 34786 | LAST_VOL_HARM_AVGb49 | Last Period 3sec 49th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87E3 | 0x87E4 | 34787 | 34788 | LAST_VOL_HARM_AVGb50 | Last Period 3sec 50th Phase B Voltage Harmonics Average Value | float | 2 | R
0x87E5 | 0x87E6 | 34789 | 34790 | LAST_VOL_HARM_AVGc2 | Last Period 3sec 2nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x87E7 | 0x87E8 | 34791 | 34792 | LAST_VOL_HARM_AVGc3 | Last Period 3sec 3rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x87E9 | 0x87EA | 34793 | 34794 | LAST_VOL_HARM_AVGc4 | Last Period 3sec 4th Phase C Voltage Harmonics Average Value | float | 2 | R
0x87EB | 0x87EC | 34795 | 34796 | LAST_VOL_HARM_AVGc5 | Last Period 3sec 5th Phase C Voltage Harmonics Average Value | float | 2 | R
0x87ED | 0x87EE | 34797 | 34798 | LAST_VOL_HARM_AVGc6 | Last Period 3sec 6th Phase C Voltage Harmonics Average Value | float | 2 | R
0x87EF | 0x87F0 | 34799 | 34800 | LAST_VOL_HARM_AVGc7 | Last Period 3sec 7th Phase C Voltage Harmonics Average Value | float | 2 | R
0x87F1 | 0x87F2 | 34801 | 34802 | LAST_VOL_HARM_AVGc8 | Last Period 3sec 8th Phase C Voltage Harmonics Average Value | float | 2 | R
0x87F3 | 0x87F4 | 34803 | 34804 | LAST_VOL_HARM_AVGc9 | Last Period 3sec 9th Phase C Voltage Harmonics Average Value | float | 2 | R
0x87F5 | 0x87F6 | 34805 | 34806 | LAST_VOL_HARM_AVGc10 | Last Period 3sec 10th Phase C Voltage Harmonics Average Value | float | 2 | R
0x87F7 | 0x87F8 | 34807 | 34808 | LAST_VOL_HARM_AVGc11 | Last Period 3sec 11st Phase C Voltage Harmonics Average Value | float | 2 | R
0x87F9 | 0x87FA | 34809 | 34810 | LAST_VOL_HARM_AVGc12 | Last Period 3sec 12nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x87FB | 0x87FC | 34811 | 34812 | LAST_VOL_HARM_AVGc13 | Last Period 3sec 13rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x87FD | 0x87FE | 34813 | 34814 | LAST_VOL_HARM_AVGc14 | Last Period 3sec 14th Phase C Voltage Harmonics Average Value | float | 2 | R
0x87FF | 0x8800 | 34815 | 34816 | LAST_VOL_HARM_AVGc15 | Last Period 3sec 15th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8801 | 0x8802 | 34817 | 34818 | LAST_VOL_HARM_AVGc16 | Last Period 3sec 16th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8803 | 0x8804 | 34819 | 34820 | LAST_VOL_HARM_AVGc17 | Last Period 3sec 17th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8805 | 0x8806 | 34821 | 34822 | LAST_VOL_HARM_AVGc18 | Last Period 3sec 18th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8807 | 0x8808 | 34823 | 34824 | LAST_VOL_HARM_AVGc19 | Last Period 3sec 19th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8809 | 0x880A | 34825 | 34826 | LAST_VOL_HARM_AVGc20 | Last Period 3sec 20th Phase C Voltage Harmonics Average Value | float | 2 | R
0x880B | 0x880C | 34827 | 34828 | LAST_VOL_HARM_AVGc21 | Last Period 3sec 21st Phase C Voltage Harmonics Average Value | float | 2 | R
0x880D | 0x880E | 34829 | 34830 | LAST_VOL_HARM_AVGc22 | Last Period 3sec 22nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x880F | 0x8810 | 34831 | 34832 | LAST_VOL_HARM_AVGc23 | Last Period 3sec 23rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x8811 | 0x8812 | 34833 | 34834 | LAST_VOL_HARM_AVGc24 | Last Period 3sec 24th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8813 | 0x8814 | 34835 | 34836 | LAST_VOL_HARM_AVGc25 | Last Period 3sec 25th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8815 | 0x8816 | 34837 | 34838 | LAST_VOL_HARM_AVGc26 | Last Period 3sec 26th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8817 | 0x8818 | 34839 | 34840 | LAST_VOL_HARM_AVGc27 | Last Period 3sec 27th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8819 | 0x881A | 34841 | 34842 | LAST_VOL_HARM_AVGc28 | Last Period 3sec 28th Phase C Voltage Harmonics Average Value | float | 2 | R
0x881B | 0x881C | 34843 | 34844 | LAST_VOL_HARM_AVGc29 | Last Period 3sec 29th Phase C Voltage Harmonics Average Value | float | 2 | R
0x881D | 0x881E | 34845 | 34846 | LAST_VOL_HARM_AVGc30 | Last Period 3sec 30th Phase C Voltage Harmonics Average Value | float | 2 | R
0x881F | 0x8820 | 34847 | 34848 | LAST_VOL_HARM_AVGc31 | Last Period 3sec 31st Phase C Voltage Harmonics Average Value | float | 2 | R
0x8821 | 0x8822 | 34849 | 34850 | LAST_VOL_HARM_AVGc32 | Last Period 3sec 32nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x8823 | 0x8824 | 34851 | 34852 | LAST_VOL_HARM_AVGc33 | Last Period 3sec 33rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x8825 | 0x8826 | 34853 | 34854 | LAST_VOL_HARM_AVGc34 | Last Period 3sec 34th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8827 | 0x8828 | 34855 | 34856 | LAST_VOL_HARM_AVGc35 | Last Period 3sec 35th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8829 | 0x882A | 34857 | 34858 | LAST_VOL_HARM_AVGc36 | Last Period 3sec 36th Phase C Voltage Harmonics Average Value | float | 2 | R
0x882B | 0x882C | 34859 | 34860 | LAST_VOL_HARM_AVGc37 | Last Period 3sec 37th Phase C Voltage Harmonics Average Value | float | 2 | R
0x882D | 0x882E | 34861 | 34862 | LAST_VOL_HARM_AVGc38 | Last Period 3sec 38th Phase C Voltage Harmonics Average Value | float | 2 | R
0x882F | 0x8830 | 34863 | 34864 | LAST_VOL_HARM_AVGc39 | Last Period 3sec 39th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8831 | 0x8832 | 34865 | 34866 | LAST_VOL_HARM_AVGc40 | Last Period 3sec 40th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8833 | 0x8834 | 34867 | 34868 | LAST_VOL_HARM_AVGc41 | Last Period 3sec 41st Phase C Voltage Harmonics Average Value | float | 2 | R
0x8835 | 0x8836 | 34869 | 34870 | LAST_VOL_HARM_AVGc42 | Last Period 3sec 42nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x8837 | 0x8838 | 34871 | 34872 | LAST_VOL_HARM_AVGc43 | Last Period 3sec 43rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x8839 | 0x883A | 34873 | 34874 | LAST_VOL_HARM_AVGc44 | Last Period 3sec 44th Phase C Voltage Harmonics Average Value | float | 2 | R
0x883B | 0x883C | 34875 | 34876 | LAST_VOL_HARM_AVGc45 | Last Period 3sec 45th Phase C Voltage Harmonics Average Value | float | 2 | R
0x883D | 0x883E | 34877 | 34878 | LAST_VOL_HARM_AVGc46 | Last Period 3sec 46th Phase C Voltage Harmonics Average Value | float | 2 | R
0x883F | 0x8840 | 34879 | 34880 | LAST_VOL_HARM_AVGc47 | Last Period 3sec 47th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8841 | 0x8842 | 34881 | 34882 | LAST_VOL_HARM_AVGc48 | Last Period 3sec 48th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8843 | 0x8844 | 34883 | 34884 | LAST_VOL_HARM_AVGc49 | Last Period 3sec 49th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8845 | 0x8846 | 34885 | 34886 | LAST_VOL_HARM_AVGc50 | Last Period 3sec 50th Phase C Voltage Harmonics Average Value | float | 2 | R
0x8847 | 0x8848 | 34887 | 34888 | LAST_TDD_MAXa | Last Period 3sec Phase A TDD Maximum Value | float | 2 | R
0x8849 | 0x884A | 34889 | 34890 | LAST_TDD_MAXb | Last Period 3sec Phase B TDD Maximum Value | float | 2 | R
0x884B | 0x884C | 34891 | 34892 | LAST_TDD_MAXc | Last Period 3sec Phase C TDD Maximum Value | float | 2 | R
0x884D | 0x884E | 34893 | 34894 | LAST_TDD_MINa | Last Period 3sec Phase A TDD Minimum Value | float | 2 | R
0x884F | 0x8850 | 34895 | 34896 | LAST_TDD_MINb | Last Period 3sec Phase B TDD Minimum Value | float | 2 | R
0x8851 | 0x8852 | 34897 | 34898 | LAST_TDD_MINc | Last Period 3sec Phase C TDD Minimum Value | float | 2 | R
0x8853 | 0x8854 | 34899 | 34900 | LAST_TDD_AVGa | Last Period 3sec Phase A TDD Average Value | float | 2 | R
0x8855 | 0x8856 | 34901 | 34902 | LAST_TDD_AVGb | Last Period 3sec Phase B TDD Average Value | float | 2 | R
0x8857 | 0x8858 | 34903 | 34904 | LAST_TDD_AVGc | Last Period 3sec Phase C TDD Average Value | float | 2 | R
0x8859 | 0x885A | 34905 | 34906 | LAST_CUR_HARM_MAXa2 | Last Period 3sec 2nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x885B | 0x885C | 34907 | 34908 | LAST_CUR_HARM_MAXa3 | Last Period 3sec 3rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x885D | 0x885E | 34909 | 34910 | LAST_CUR_HARM_MAXa4 | Last Period 3sec 4th Phase A Current Harmonics Maximum Value | float | 2 | R
0x885F | 0x8860 | 34911 | 34912 | LAST_CUR_HARM_MAXa5 | Last Period 3sec 5th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8861 | 0x8862 | 34913 | 34914 | LAST_CUR_HARM_MAXa6 | Last Period 3sec 6th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8863 | 0x8864 | 34915 | 34916 | LAST_CUR_HARM_MAXa7 | Last Period 3sec 7th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8865 | 0x8866 | 34917 | 34918 | LAST_CUR_HARM_MAXa8 | Last Period 3sec 8th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8867 | 0x8868 | 34919 | 34920 | LAST_CUR_HARM_MAXa9 | Last Period 3sec 9th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8869 | 0x886A | 34921 | 34922 | LAST_CUR_HARM_MAXa10 | Last Period 3sec 10th Phase A Current Harmonics Maximum Value | float | 2 | R
0x886B | 0x886C | 34923 | 34924 | LAST_CUR_HARM_MAXa11 | Last Period 3sec 11st Phase A Current Harmonics Maximum Value | float | 2 | R
0x886D | 0x886E | 34925 | 34926 | LAST_CUR_HARM_MAXa12 | Last Period 3sec 12nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x886F | 0x8870 | 34927 | 34928 | LAST_CUR_HARM_MAXa13 | Last Period 3sec 13rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x8871 | 0x8872 | 34929 | 34930 | LAST_CUR_HARM_MAXa14 | Last Period 3sec 14th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8873 | 0x8874 | 34931 | 34932 | LAST_CUR_HARM_MAXa15 | Last Period 3sec 15th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8875 | 0x8876 | 34933 | 34934 | LAST_CUR_HARM_MAXa16 | Last Period 3sec 16th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8877 | 0x8878 | 34935 | 34936 | LAST_CUR_HARM_MAXa17 | Last Period 3sec 17th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8879 | 0x887A | 34937 | 34938 | LAST_CUR_HARM_MAXa18 | Last Period 3sec 18th Phase A Current Harmonics Maximum Value | float | 2 | R
0x887B | 0x887C | 34939 | 34940 | LAST_CUR_HARM_MAXa19 | Last Period 3sec 19th Phase A Current Harmonics Maximum Value | float | 2 | R
0x887D | 0x887E | 34941 | 34942 | LAST_CUR_HARM_MAXa20 | Last Period 3sec 20th Phase A Current Harmonics Maximum Value | float | 2 | R
0x887F | 0x8880 | 34943 | 34944 | LAST_CUR_HARM_MAXa21 | Last Period 3sec 21st Phase A Current Harmonics Maximum Value | float | 2 | R
0x8881 | 0x8882 | 34945 | 34946 | LAST_CUR_HARM_MAXa22 | Last Period 3sec 22nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x8883 | 0x8884 | 34947 | 34948 | LAST_CUR_HARM_MAXa23 | Last Period 3sec 23rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x8885 | 0x8886 | 34949 | 34950 | LAST_CUR_HARM_MAXa24 | Last Period 3sec 24th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8887 | 0x8888 | 34951 | 34952 | LAST_CUR_HARM_MAXa25 | Last Period 3sec 25th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8889 | 0x888A | 34953 | 34954 | LAST_CUR_HARM_MAXa26 | Last Period 3sec 26th Phase A Current Harmonics Maximum Value | float | 2 | R
0x888B | 0x888C | 34955 | 34956 | LAST_CUR_HARM_MAXa27 | Last Period 3sec 27th Phase A Current Harmonics Maximum Value | float | 2 | R
0x888D | 0x888E | 34957 | 34958 | LAST_CUR_HARM_MAXa28 | Last Period 3sec 28th Phase A Current Harmonics Maximum Value | float | 2 | R
0x888F | 0x8890 | 34959 | 34960 | LAST_CUR_HARM_MAXa29 | Last Period 3sec 29th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8891 | 0x8892 | 34961 | 34962 | LAST_CUR_HARM_MAXa30 | Last Period 3sec 30th Phase A Current Harmonics Maximum Value | float | 2 | R
0x8893 | 0x8894 | 34963 | 34964 | LAST_CUR_HARM_MAXa31 | Last Period 3sec 31st Phase A Current Harmonics Maximum Value | float | 2 | R
0x8895 | 0x8896 | 34965 | 34966 | LAST_CUR_HARM_MAXa32 | Last Period 3sec 32nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x8897 | 0x8898 | 34967 | 34968 | LAST_CUR_HARM_MAXa33 | Last Period 3sec 33rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x8899 | 0x889A | 34969 | 34970 | LAST_CUR_HARM_MAXa34 | Last Period 3sec 34th Phase A Current Harmonics Maximum Value | float | 2 | R
0x889B | 0x889C | 34971 | 34972 | LAST_CUR_HARM_MAXa35 | Last Period 3sec 35th Phase A Current Harmonics Maximum Value | float | 2 | R
0x889D | 0x889E | 34973 | 34974 | LAST_CUR_HARM_MAXa36 | Last Period 3sec 36th Phase A Current Harmonics Maximum Value | float | 2 | R
0x889F | 0x88A0 | 34975 | 34976 | LAST_CUR_HARM_MAXa37 | Last Period 3sec 37th Phase A Current Harmonics Maximum Value | float | 2 | R
0x88A1 | 0x88A2 | 34977 | 34978 | LAST_CUR_HARM_MAXa38 | Last Period 3sec 38th Phase A Current Harmonics Maximum Value | float | 2 | R
0x88A3 | 0x88A4 | 34979 | 34980 | LAST_CUR_HARM_MAXa39 | Last Period 3sec 39th Phase A Current Harmonics Maximum Value | float | 2 | R
0x88A5 | 0x88A6 | 34981 | 34982 | LAST_CUR_HARM_MAXa40 | Last Period 3sec 40th Phase A Current Harmonics Maximum Value | float | 2 | R
0x88A7 | 0x88A8 | 34983 | 34984 | LAST_CUR_HARM_MAXa41 | Last Period 3sec 41st Phase A Current Harmonics Maximum Value | float | 2 | R
0x88A9 | 0x88AA | 34985 | 34986 | LAST_CUR_HARM_MAXa42 | Last Period 3sec 42nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x88AB | 0x88AC | 34987 | 34988 | LAST_CUR_HARM_MAXa43 | Last Period 3sec 43rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x88AD | 0x88AE | 34989 | 34990 | LAST_CUR_HARM_MAXa44 | Last Period 3sec 44th Phase A Current Harmonics Maximum Value | float | 2 | R
0x88AF | 0x88B0 | 34991 | 34992 | LAST_CUR_HARM_MAXa45 | Last Period 3sec 45th Phase A Current Harmonics Maximum Value | float | 2 | R
0x88B1 | 0x88B2 | 34993 | 34994 | LAST_CUR_HARM_MAXa46 | Last Period 3sec 46th Phase A Current Harmonics Maximum Value | float | 2 | R
0x88B3 | 0x88B4 | 34995 | 34996 | LAST_CUR_HARM_MAXa47 | Last Period 3sec 47th Phase A Current Harmonics Maximum Value | float | 2 | R
0x88B5 | 0x88B6 | 34997 | 34998 | LAST_CUR_HARM_MAXa48 | Last Period 3sec 48th Phase A Current Harmonics Maximum Value | float | 2 | R
0x88B7 | 0x88B8 | 34999 | 35000 | LAST_CUR_HARM_MAXa49 | Last Period 3sec 49th Phase A Current Harmonics Maximum Value | float | 2 | R
0x88B9 | 0x88BA | 35001 | 35002 | LAST_CUR_HARM_MAXa50 | Last Period 3sec 50th Phase A Current Harmonics Maximum Value | float | 2 | R
0x88BB | 0x88BC | 35003 | 35004 | LAST_CUR_HARM_MAXb2 | Last Period 3sec 2nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x88BD | 0x88BE | 35005 | 35006 | LAST_CUR_HARM_MAXb3 | Last Period 3sec 3rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x88BF | 0x88C0 | 35007 | 35008 | LAST_CUR_HARM_MAXb4 | Last Period 3sec 4th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88C1 | 0x88C2 | 35009 | 35010 | LAST_CUR_HARM_MAXb5 | Last Period 3sec 5th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88C3 | 0x88C4 | 35011 | 35012 | LAST_CUR_HARM_MAXb6 | Last Period 3sec 6th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88C5 | 0x88C6 | 35013 | 35014 | LAST_CUR_HARM_MAXb7 | Last Period 3sec 7th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88C7 | 0x88C8 | 35015 | 35016 | LAST_CUR_HARM_MAXb8 | Last Period 3sec 8th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88C9 | 0x88CA | 35017 | 35018 | LAST_CUR_HARM_MAXb9 | Last Period 3sec 9th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88CB | 0x88CC | 35019 | 35020 | LAST_CUR_HARM_MAXb10 | Last Period 3sec 10th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88CD | 0x88CE | 35021 | 35022 | LAST_CUR_HARM_MAXb11 | Last Period 3sec 11st Phase B Current Harmonics Maximum Value | float | 2 | R
0x88CF | 0x88D0 | 35023 | 35024 | LAST_CUR_HARM_MAXb12 | Last Period 3sec 12nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x88D1 | 0x88D2 | 35025 | 35026 | LAST_CUR_HARM_MAXb13 | Last Period 3sec 13rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x88D3 | 0x88D4 | 35027 | 35028 | LAST_CUR_HARM_MAXb14 | Last Period 3sec 14th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88D5 | 0x88D6 | 35029 | 35030 | LAST_CUR_HARM_MAXb15 | Last Period 3sec 15th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88D7 | 0x88D8 | 35031 | 35032 | LAST_CUR_HARM_MAXb16 | Last Period 3sec 16th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88D9 | 0x88DA | 35033 | 35034 | LAST_CUR_HARM_MAXb17 | Last Period 3sec 17th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88DB | 0x88DC | 35035 | 35036 | LAST_CUR_HARM_MAXb18 | Last Period 3sec 18th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88DD | 0x88DE | 35037 | 35038 | LAST_CUR_HARM_MAXb19 | Last Period 3sec 19th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88DF | 0x88E0 | 35039 | 35040 | LAST_CUR_HARM_MAXb20 | Last Period 3sec 20th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88E1 | 0x88E2 | 35041 | 35042 | LAST_CUR_HARM_MAXb21 | Last Period 3sec 21st Phase B Current Harmonics Maximum Value | float | 2 | R
0x88E3 | 0x88E4 | 35043 | 35044 | LAST_CUR_HARM_MAXb22 | Last Period 3sec 22nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x88E5 | 0x88E6 | 35045 | 35046 | LAST_CUR_HARM_MAXb23 | Last Period 3sec 23rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x88E7 | 0x88E8 | 35047 | 35048 | LAST_CUR_HARM_MAXb24 | Last Period 3sec 24th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88E9 | 0x88EA | 35049 | 35050 | LAST_CUR_HARM_MAXb25 | Last Period 3sec 25th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88EB | 0x88EC | 35051 | 35052 | LAST_CUR_HARM_MAXb26 | Last Period 3sec 26th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88ED | 0x88EE | 35053 | 35054 | LAST_CUR_HARM_MAXb27 | Last Period 3sec 27th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88EF | 0x88F0 | 35055 | 35056 | LAST_CUR_HARM_MAXb28 | Last Period 3sec 28th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88F1 | 0x88F2 | 35057 | 35058 | LAST_CUR_HARM_MAXb29 | Last Period 3sec 29th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88F3 | 0x88F4 | 35059 | 35060 | LAST_CUR_HARM_MAXb30 | Last Period 3sec 30th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88F5 | 0x88F6 | 35061 | 35062 | LAST_CUR_HARM_MAXb31 | Last Period 3sec 31st Phase B Current Harmonics Maximum Value | float | 2 | R
0x88F7 | 0x88F8 | 35063 | 35064 | LAST_CUR_HARM_MAXb32 | Last Period 3sec 32nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x88F9 | 0x88FA | 35065 | 35066 | LAST_CUR_HARM_MAXb33 | Last Period 3sec 33rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x88FB | 0x88FC | 35067 | 35068 | LAST_CUR_HARM_MAXb34 | Last Period 3sec 34th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88FD | 0x88FE | 35069 | 35070 | LAST_CUR_HARM_MAXb35 | Last Period 3sec 35th Phase B Current Harmonics Maximum Value | float | 2 | R
0x88FF | 0x8900 | 35071 | 35072 | LAST_CUR_HARM_MAXb36 | Last Period 3sec 36th Phase B Current Harmonics Maximum Value | float | 2 | R
0x8901 | 0x8902 | 35073 | 35074 | LAST_CUR_HARM_MAXb37 | Last Period 3sec 37th Phase B Current Harmonics Maximum Value | float | 2 | R
0x8903 | 0x8904 | 35075 | 35076 | LAST_CUR_HARM_MAXb38 | Last Period 3sec 38th Phase B Current Harmonics Maximum Value | float | 2 | R
0x8905 | 0x8906 | 35077 | 35078 | LAST_CUR_HARM_MAXb39 | Last Period 3sec 39th Phase B Current Harmonics Maximum Value | float | 2 | R
0x8907 | 0x8908 | 35079 | 35080 | LAST_CUR_HARM_MAXb40 | Last Period 3sec 40th Phase B Current Harmonics Maximum Value | float | 2 | R
0x8909 | 0x890A | 35081 | 35082 | LAST_CUR_HARM_MAXb41 | Last Period 3sec 41st Phase B Current Harmonics Maximum Value | float | 2 | R
0x890B | 0x890C | 35083 | 35084 | LAST_CUR_HARM_MAXb42 | Last Period 3sec 42nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x890D | 0x890E | 35085 | 35086 | LAST_CUR_HARM_MAXb43 | Last Period 3sec 43rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x890F | 0x8910 | 35087 | 35088 | LAST_CUR_HARM_MAXb44 | Last Period 3sec 44th Phase B Current Harmonics Maximum Value | float | 2 | R
0x8911 | 0x8912 | 35089 | 35090 | LAST_CUR_HARM_MAXb45 | Last Period 3sec 45th Phase B Current Harmonics Maximum Value | float | 2 | R
0x8913 | 0x8914 | 35091 | 35092 | LAST_CUR_HARM_MAXb46 | Last Period 3sec 46th Phase B Current Harmonics Maximum Value | float | 2 | R
0x8915 | 0x8916 | 35093 | 35094 | LAST_CUR_HARM_MAXb47 | Last Period 3sec 47th Phase B Current Harmonics Maximum Value | float | 2 | R
0x8917 | 0x8918 | 35095 | 35096 | LAST_CUR_HARM_MAXb48 | Last Period 3sec 48th Phase B Current Harmonics Maximum Value | float | 2 | R
0x8919 | 0x891A | 35097 | 35098 | LAST_CUR_HARM_MAXb49 | Last Period 3sec 49th Phase B Current Harmonics Maximum Value | float | 2 | R
0x891B | 0x891C | 35099 | 35100 | LAST_CUR_HARM_MAXb50 | Last Period 3sec 50th Phase B Current Harmonics Maximum Value | float | 2 | R
0x891D | 0x891E | 35101 | 35102 | LAST_CUR_HARM_MAXc2 | Last Period 3sec 2nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x891F | 0x8920 | 35103 | 35104 | LAST_CUR_HARM_MAXc3 | Last Period 3sec 3rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x8921 | 0x8922 | 35105 | 35106 | LAST_CUR_HARM_MAXc4 | Last Period 3sec 4th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8923 | 0x8924 | 35107 | 35108 | LAST_CUR_HARM_MAXc5 | Last Period 3sec 5th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8925 | 0x8926 | 35109 | 35110 | LAST_CUR_HARM_MAXc6 | Last Period 3sec 6th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8927 | 0x8928 | 35111 | 35112 | LAST_CUR_HARM_MAXc7 | Last Period 3sec 7th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8929 | 0x892A | 35113 | 35114 | LAST_CUR_HARM_MAXc8 | Last Period 3sec 8th Phase C Current Harmonics Maximum Value | float | 2 | R
0x892B | 0x892C | 35115 | 35116 | LAST_CUR_HARM_MAXc9 | Last Period 3sec 9th Phase C Current Harmonics Maximum Value | float | 2 | R
0x892D | 0x892E | 35117 | 35118 | LAST_CUR_HARM_MAXc10 | Last Period 3sec 10th Phase C Current Harmonics Maximum Value | float | 2 | R
0x892F | 0x8930 | 35119 | 35120 | LAST_CUR_HARM_MAXc11 | Last Period 3sec 11st Phase C Current Harmonics Maximum Value | float | 2 | R
0x8931 | 0x8932 | 35121 | 35122 | LAST_CUR_HARM_MAXc12 | Last Period 3sec 12nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x8933 | 0x8934 | 35123 | 35124 | LAST_CUR_HARM_MAXc13 | Last Period 3sec 13rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x8935 | 0x8936 | 35125 | 35126 | LAST_CUR_HARM_MAXc14 | Last Period 3sec 14th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8937 | 0x8938 | 35127 | 35128 | LAST_CUR_HARM_MAXc15 | Last Period 3sec 15th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8939 | 0x893A | 35129 | 35130 | LAST_CUR_HARM_MAXc16 | Last Period 3sec 16th Phase C Current Harmonics Maximum Value | float | 2 | R
0x893B | 0x893C | 35131 | 35132 | LAST_CUR_HARM_MAXc17 | Last Period 3sec 17th Phase C Current Harmonics Maximum Value | float | 2 | R
0x893D | 0x893E | 35133 | 35134 | LAST_CUR_HARM_MAXc18 | Last Period 3sec 18th Phase C Current Harmonics Maximum Value | float | 2 | R
0x893F | 0x8940 | 35135 | 35136 | LAST_CUR_HARM_MAXc19 | Last Period 3sec 19th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8941 | 0x8942 | 35137 | 35138 | LAST_CUR_HARM_MAXc20 | Last Period 3sec 20th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8943 | 0x8944 | 35139 | 35140 | LAST_CUR_HARM_MAXc21 | Last Period 3sec 21st Phase C Current Harmonics Maximum Value | float | 2 | R
0x8945 | 0x8946 | 35141 | 35142 | LAST_CUR_HARM_MAXc22 | Last Period 3sec 22nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x8947 | 0x8948 | 35143 | 35144 | LAST_CUR_HARM_MAXc23 | Last Period 3sec 23rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x8949 | 0x894A | 35145 | 35146 | LAST_CUR_HARM_MAXc24 | Last Period 3sec 24th Phase C Current Harmonics Maximum Value | float | 2 | R
0x894B | 0x894C | 35147 | 35148 | LAST_CUR_HARM_MAXc25 | Last Period 3sec 25th Phase C Current Harmonics Maximum Value | float | 2 | R
0x894D | 0x894E | 35149 | 35150 | LAST_CUR_HARM_MAXc26 | Last Period 3sec 26th Phase C Current Harmonics Maximum Value | float | 2 | R
0x894F | 0x8950 | 35151 | 35152 | LAST_CUR_HARM_MAXc27 | Last Period 3sec 27th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8951 | 0x8952 | 35153 | 35154 | LAST_CUR_HARM_MAXc28 | Last Period 3sec 28th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8953 | 0x8954 | 35155 | 35156 | LAST_CUR_HARM_MAXc29 | Last Period 3sec 29th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8955 | 0x8956 | 35157 | 35158 | LAST_CUR_HARM_MAXc30 | Last Period 3sec 30th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8957 | 0x8958 | 35159 | 35160 | LAST_CUR_HARM_MAXc31 | Last Period 3sec 31st Phase C Current Harmonics Maximum Value | float | 2 | R
0x8959 | 0x895A | 35161 | 35162 | LAST_CUR_HARM_MAXc32 | Last Period 3sec 32nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x895B | 0x895C | 35163 | 35164 | LAST_CUR_HARM_MAXc33 | Last Period 3sec 33rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x895D | 0x895E | 35165 | 35166 | LAST_CUR_HARM_MAXc34 | Last Period 3sec 34th Phase C Current Harmonics Maximum Value | float | 2 | R
0x895F | 0x8960 | 35167 | 35168 | LAST_CUR_HARM_MAXc35 | Last Period 3sec 35th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8961 | 0x8962 | 35169 | 35170 | LAST_CUR_HARM_MAXc36 | Last Period 3sec 36th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8963 | 0x8964 | 35171 | 35172 | LAST_CUR_HARM_MAXc37 | Last Period 3sec 37th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8965 | 0x8966 | 35173 | 35174 | LAST_CUR_HARM_MAXc38 | Last Period 3sec 38th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8967 | 0x8968 | 35175 | 35176 | LAST_CUR_HARM_MAXc39 | Last Period 3sec 39th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8969 | 0x896A | 35177 | 35178 | LAST_CUR_HARM_MAXc40 | Last Period 3sec 40th Phase C Current Harmonics Maximum Value | float | 2 | R
0x896B | 0x896C | 35179 | 35180 | LAST_CUR_HARM_MAXc41 | Last Period 3sec 41st Phase C Current Harmonics Maximum Value | float | 2 | R
0x896D | 0x896E | 35181 | 35182 | LAST_CUR_HARM_MAXc42 | Last Period 3sec 42nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x896F | 0x8970 | 35183 | 35184 | LAST_CUR_HARM_MAXc43 | Last Period 3sec 43rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x8971 | 0x8972 | 35185 | 35186 | LAST_CUR_HARM_MAXc44 | Last Period 3sec 44th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8973 | 0x8974 | 35187 | 35188 | LAST_CUR_HARM_MAXc45 | Last Period 3sec 45th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8975 | 0x8976 | 35189 | 35190 | LAST_CUR_HARM_MAXc46 | Last Period 3sec 46th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8977 | 0x8978 | 35191 | 35192 | LAST_CUR_HARM_MAXc47 | Last Period 3sec 47th Phase C Current Harmonics Maximum Value | float | 2 | R
0x8979 | 0x897A | 35193 | 35194 | LAST_CUR_HARM_MAXc48 | Last Period 3sec 48th Phase C Current Harmonics Maximum Value | float | 2 | R
0x897B | 0x897C | 35195 | 35196 | LAST_CUR_HARM_MAXc49 | Last Period 3sec 49th Phase C Current Harmonics Maximum Value | float | 2 | R
0x897D | 0x897E | 35197 | 35198 | LAST_CUR_HARM_MAXc50 | Last Period 3sec 50th Phase C Current Harmonics Maximum Value | float | 2 | R
0x897F | 0x8980 | 35199 | 35200 | LAST_CUR_HARM_MINa2 | Last Period 3sec 2nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x8981 | 0x8982 | 35201 | 35202 | LAST_CUR_HARM_MINa3 | Last Period 3sec 3rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x8983 | 0x8984 | 35203 | 35204 | LAST_CUR_HARM_MINa4 | Last Period 3sec 4th Phase A Current Harmonics Minimum Value | float | 2 | R
0x8985 | 0x8986 | 35205 | 35206 | LAST_CUR_HARM_MINa5 | Last Period 3sec 5th Phase A Current Harmonics Minimum Value | float | 2 | R
0x8987 | 0x8988 | 35207 | 35208 | LAST_CUR_HARM_MINa6 | Last Period 3sec 6th Phase A Current Harmonics Minimum Value | float | 2 | R
0x8989 | 0x898A | 35209 | 35210 | LAST_CUR_HARM_MINa7 | Last Period 3sec 7th Phase A Current Harmonics Minimum Value | float | 2 | R
0x898B | 0x898C | 35211 | 35212 | LAST_CUR_HARM_MINa8 | Last Period 3sec 8th Phase A Current Harmonics Minimum Value | float | 2 | R
0x898D | 0x898E | 35213 | 35214 | LAST_CUR_HARM_MINa9 | Last Period 3sec 9th Phase A Current Harmonics Minimum Value | float | 2 | R
0x898F | 0x8990 | 35215 | 35216 | LAST_CUR_HARM_MINa10 | Last Period 3sec 10th Phase A Current Harmonics Minimum Value | float | 2 | R
0x8991 | 0x8992 | 35217 | 35218 | LAST_CUR_HARM_MINa11 | Last Period 3sec 11st Phase A Current Harmonics Minimum Value | float | 2 | R
0x8993 | 0x8994 | 35219 | 35220 | LAST_CUR_HARM_MINa12 | Last Period 3sec 12nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x8995 | 0x8996 | 35221 | 35222 | LAST_CUR_HARM_MINa13 | Last Period 3sec 13rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x8997 | 0x8998 | 35223 | 35224 | LAST_CUR_HARM_MINa14 | Last Period 3sec 14th Phase A Current Harmonics Minimum Value | float | 2 | R
0x8999 | 0x899A | 35225 | 35226 | LAST_CUR_HARM_MINa15 | Last Period 3sec 15th Phase A Current Harmonics Minimum Value | float | 2 | R
0x899B | 0x899C | 35227 | 35228 | LAST_CUR_HARM_MINa16 | Last Period 3sec 16th Phase A Current Harmonics Minimum Value | float | 2 | R
0x899D | 0x899E | 35229 | 35230 | LAST_CUR_HARM_MINa17 | Last Period 3sec 17th Phase A Current Harmonics Minimum Value | float | 2 | R
0x899F | 0x89A0 | 35231 | 35232 | LAST_CUR_HARM_MINa18 | Last Period 3sec 18th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89A1 | 0x89A2 | 35233 | 35234 | LAST_CUR_HARM_MINa19 | Last Period 3sec 19th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89A3 | 0x89A4 | 35235 | 35236 | LAST_CUR_HARM_MINa20 | Last Period 3sec 20th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89A5 | 0x89A6 | 35237 | 35238 | LAST_CUR_HARM_MINa21 | Last Period 3sec 21st Phase A Current Harmonics Minimum Value | float | 2 | R
0x89A7 | 0x89A8 | 35239 | 35240 | LAST_CUR_HARM_MINa22 | Last Period 3sec 22nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x89A9 | 0x89AA | 35241 | 35242 | LAST_CUR_HARM_MINa23 | Last Period 3sec 23rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x89AB | 0x89AC | 35243 | 35244 | LAST_CUR_HARM_MINa24 | Last Period 3sec 24th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89AD | 0x89AE | 35245 | 35246 | LAST_CUR_HARM_MINa25 | Last Period 3sec 25th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89AF | 0x89B0 | 35247 | 35248 | LAST_CUR_HARM_MINa26 | Last Period 3sec 26th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89B1 | 0x89B2 | 35249 | 35250 | LAST_CUR_HARM_MINa27 | Last Period 3sec 27th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89B3 | 0x89B4 | 35251 | 35252 | LAST_CUR_HARM_MINa28 | Last Period 3sec 28th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89B5 | 0x89B6 | 35253 | 35254 | LAST_CUR_HARM_MINa29 | Last Period 3sec 29th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89B7 | 0x89B8 | 35255 | 35256 | LAST_CUR_HARM_MINa30 | Last Period 3sec 30th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89B9 | 0x89BA | 35257 | 35258 | LAST_CUR_HARM_MINa31 | Last Period 3sec 31st Phase A Current Harmonics Minimum Value | float | 2 | R
0x89BB | 0x89BC | 35259 | 35260 | LAST_CUR_HARM_MINa32 | Last Period 3sec 32nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x89BD | 0x89BE | 35261 | 35262 | LAST_CUR_HARM_MINa33 | Last Period 3sec 33rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x89BF | 0x89C0 | 35263 | 35264 | LAST_CUR_HARM_MINa34 | Last Period 3sec 34th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89C1 | 0x89C2 | 35265 | 35266 | LAST_CUR_HARM_MINa35 | Last Period 3sec 35th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89C3 | 0x89C4 | 35267 | 35268 | LAST_CUR_HARM_MINa36 | Last Period 3sec 36th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89C5 | 0x89C6 | 35269 | 35270 | LAST_CUR_HARM_MINa37 | Last Period 3sec 37th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89C7 | 0x89C8 | 35271 | 35272 | LAST_CUR_HARM_MINa38 | Last Period 3sec 38th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89C9 | 0x89CA | 35273 | 35274 | LAST_CUR_HARM_MINa39 | Last Period 3sec 39th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89CB | 0x89CC | 35275 | 35276 | LAST_CUR_HARM_MINa40 | Last Period 3sec 40th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89CD | 0x89CE | 35277 | 35278 | LAST_CUR_HARM_MINa41 | Last Period 3sec 41st Phase A Current Harmonics Minimum Value | float | 2 | R
0x89CF | 0x89D0 | 35279 | 35280 | LAST_CUR_HARM_MINa42 | Last Period 3sec 42nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x89D1 | 0x89D2 | 35281 | 35282 | LAST_CUR_HARM_MINa43 | Last Period 3sec 43rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x89D3 | 0x89D4 | 35283 | 35284 | LAST_CUR_HARM_MINa44 | Last Period 3sec 44th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89D5 | 0x89D6 | 35285 | 35286 | LAST_CUR_HARM_MINa45 | Last Period 3sec 45th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89D7 | 0x89D8 | 35287 | 35288 | LAST_CUR_HARM_MINa46 | Last Period 3sec 46th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89D9 | 0x89DA | 35289 | 35290 | LAST_CUR_HARM_MINa47 | Last Period 3sec 47th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89DB | 0x89DC | 35291 | 35292 | LAST_CUR_HARM_MINa48 | Last Period 3sec 48th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89DD | 0x89DE | 35293 | 35294 | LAST_CUR_HARM_MINa49 | Last Period 3sec 49th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89DF | 0x89E0 | 35295 | 35296 | LAST_CUR_HARM_MINa50 | Last Period 3sec 50th Phase A Current Harmonics Minimum Value | float | 2 | R
0x89E1 | 0x89E2 | 35297 | 35298 | LAST_CUR_HARM_MINb2 | Last Period 3sec 2nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x89E3 | 0x89E4 | 35299 | 35300 | LAST_CUR_HARM_MINb3 | Last Period 3sec 3rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x89E5 | 0x89E6 | 35301 | 35302 | LAST_CUR_HARM_MINb4 | Last Period 3sec 4th Phase B Current Harmonics Minimum Value | float | 2 | R
0x89E7 | 0x89E8 | 35303 | 35304 | LAST_CUR_HARM_MINb5 | Last Period 3sec 5th Phase B Current Harmonics Minimum Value | float | 2 | R
0x89E9 | 0x89EA | 35305 | 35306 | LAST_CUR_HARM_MINb6 | Last Period 3sec 6th Phase B Current Harmonics Minimum Value | float | 2 | R
0x89EB | 0x89EC | 35307 | 35308 | LAST_CUR_HARM_MINb7 | Last Period 3sec 7th Phase B Current Harmonics Minimum Value | float | 2 | R
0x89ED | 0x89EE | 35309 | 35310 | LAST_CUR_HARM_MINb8 | Last Period 3sec 8th Phase B Current Harmonics Minimum Value | float | 2 | R
0x89EF | 0x89F0 | 35311 | 35312 | LAST_CUR_HARM_MINb9 | Last Period 3sec 9th Phase B Current Harmonics Minimum Value | float | 2 | R
0x89F1 | 0x89F2 | 35313 | 35314 | LAST_CUR_HARM_MINb10 | Last Period 3sec 10th Phase B Current Harmonics Minimum Value | float | 2 | R
0x89F3 | 0x89F4 | 35315 | 35316 | LAST_CUR_HARM_MINb11 | Last Period 3sec 11st Phase B Current Harmonics Minimum Value | float | 2 | R
0x89F5 | 0x89F6 | 35317 | 35318 | LAST_CUR_HARM_MINb12 | Last Period 3sec 12nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x89F7 | 0x89F8 | 35319 | 35320 | LAST_CUR_HARM_MINb13 | Last Period 3sec 13rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x89F9 | 0x89FA | 35321 | 35322 | LAST_CUR_HARM_MINb14 | Last Period 3sec 14th Phase B Current Harmonics Minimum Value | float | 2 | R
0x89FB | 0x89FC | 35323 | 35324 | LAST_CUR_HARM_MINb15 | Last Period 3sec 15th Phase B Current Harmonics Minimum Value | float | 2 | R
0x89FD | 0x89FE | 35325 | 35326 | LAST_CUR_HARM_MINb16 | Last Period 3sec 16th Phase B Current Harmonics Minimum Value | float | 2 | R
0x89FF | 0x8A00 | 35327 | 35328 | LAST_CUR_HARM_MINb17 | Last Period 3sec 17th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A01 | 0x8A02 | 35329 | 35330 | LAST_CUR_HARM_MINb18 | Last Period 3sec 18th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A03 | 0x8A04 | 35331 | 35332 | LAST_CUR_HARM_MINb19 | Last Period 3sec 19th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A05 | 0x8A06 | 35333 | 35334 | LAST_CUR_HARM_MINb20 | Last Period 3sec 20th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A07 | 0x8A08 | 35335 | 35336 | LAST_CUR_HARM_MINb21 | Last Period 3sec 21st Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A09 | 0x8A0A | 35337 | 35338 | LAST_CUR_HARM_MINb22 | Last Period 3sec 22nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A0B | 0x8A0C | 35339 | 35340 | LAST_CUR_HARM_MINb23 | Last Period 3sec 23rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A0D | 0x8A0E | 35341 | 35342 | LAST_CUR_HARM_MINb24 | Last Period 3sec 24th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A0F | 0x8A10 | 35343 | 35344 | LAST_CUR_HARM_MINb25 | Last Period 3sec 25th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A11 | 0x8A12 | 35345 | 35346 | LAST_CUR_HARM_MINb26 | Last Period 3sec 26th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A13 | 0x8A14 | 35347 | 35348 | LAST_CUR_HARM_MINb27 | Last Period 3sec 27th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A15 | 0x8A16 | 35349 | 35350 | LAST_CUR_HARM_MINb28 | Last Period 3sec 28th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A17 | 0x8A18 | 35351 | 35352 | LAST_CUR_HARM_MINb29 | Last Period 3sec 29th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A19 | 0x8A1A | 35353 | 35354 | LAST_CUR_HARM_MINb30 | Last Period 3sec 30th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A1B | 0x8A1C | 35355 | 35356 | LAST_CUR_HARM_MINb31 | Last Period 3sec 31st Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A1D | 0x8A1E | 35357 | 35358 | LAST_CUR_HARM_MINb32 | Last Period 3sec 32nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A1F | 0x8A20 | 35359 | 35360 | LAST_CUR_HARM_MINb33 | Last Period 3sec 33rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A21 | 0x8A22 | 35361 | 35362 | LAST_CUR_HARM_MINb34 | Last Period 3sec 34th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A23 | 0x8A24 | 35363 | 35364 | LAST_CUR_HARM_MINb35 | Last Period 3sec 35th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A25 | 0x8A26 | 35365 | 35366 | LAST_CUR_HARM_MINb36 | Last Period 3sec 36th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A27 | 0x8A28 | 35367 | 35368 | LAST_CUR_HARM_MINb37 | Last Period 3sec 37th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A29 | 0x8A2A | 35369 | 35370 | LAST_CUR_HARM_MINb38 | Last Period 3sec 38th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A2B | 0x8A2C | 35371 | 35372 | LAST_CUR_HARM_MINb39 | Last Period 3sec 39th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A2D | 0x8A2E | 35373 | 35374 | LAST_CUR_HARM_MINb40 | Last Period 3sec 40th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A2F | 0x8A30 | 35375 | 35376 | LAST_CUR_HARM_MINb41 | Last Period 3sec 41st Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A31 | 0x8A32 | 35377 | 35378 | LAST_CUR_HARM_MINb42 | Last Period 3sec 42nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A33 | 0x8A34 | 35379 | 35380 | LAST_CUR_HARM_MINb43 | Last Period 3sec 43rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A35 | 0x8A36 | 35381 | 35382 | LAST_CUR_HARM_MINb44 | Last Period 3sec 44th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A37 | 0x8A38 | 35383 | 35384 | LAST_CUR_HARM_MINb45 | Last Period 3sec 45th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A39 | 0x8A3A | 35385 | 35386 | LAST_CUR_HARM_MINb46 | Last Period 3sec 46th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A3B | 0x8A3C | 35387 | 35388 | LAST_CUR_HARM_MINb47 | Last Period 3sec 47th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A3D | 0x8A3E | 35389 | 35390 | LAST_CUR_HARM_MINb48 | Last Period 3sec 48th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A3F | 0x8A40 | 35391 | 35392 | LAST_CUR_HARM_MINb49 | Last Period 3sec 49th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A41 | 0x8A42 | 35393 | 35394 | LAST_CUR_HARM_MINb50 | Last Period 3sec 50th Phase B Current Harmonics Minimum Value | float | 2 | R
0x8A43 | 0x8A44 | 35395 | 35396 | LAST_CUR_HARM_MINc2 | Last Period 3sec 2nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A45 | 0x8A46 | 35397 | 35398 | LAST_CUR_HARM_MINc3 | Last Period 3sec 3rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A47 | 0x8A48 | 35399 | 35400 | LAST_CUR_HARM_MINc4 | Last Period 3sec 4th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A49 | 0x8A4A | 35401 | 35402 | LAST_CUR_HARM_MINc5 | Last Period 3sec 5th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A4B | 0x8A4C | 35403 | 35404 | LAST_CUR_HARM_MINc6 | Last Period 3sec 6th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A4D | 0x8A4E | 35405 | 35406 | LAST_CUR_HARM_MINc7 | Last Period 3sec 7th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A4F | 0x8A50 | 35407 | 35408 | LAST_CUR_HARM_MINc8 | Last Period 3sec 8th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A51 | 0x8A52 | 35409 | 35410 | LAST_CUR_HARM_MINc9 | Last Period 3sec 9th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A53 | 0x8A54 | 35411 | 35412 | LAST_CUR_HARM_MINc10 | Last Period 3sec 10th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A55 | 0x8A56 | 35413 | 35414 | LAST_CUR_HARM_MINc11 | Last Period 3sec 11st Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A57 | 0x8A58 | 35415 | 35416 | LAST_CUR_HARM_MINc12 | Last Period 3sec 12nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A59 | 0x8A5A | 35417 | 35418 | LAST_CUR_HARM_MINc13 | Last Period 3sec 13rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A5B | 0x8A5C | 35419 | 35420 | LAST_CUR_HARM_MINc14 | Last Period 3sec 14th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A5D | 0x8A5E | 35421 | 35422 | LAST_CUR_HARM_MINc15 | Last Period 3sec 15th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A5F | 0x8A60 | 35423 | 35424 | LAST_CUR_HARM_MINc16 | Last Period 3sec 16th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A61 | 0x8A62 | 35425 | 35426 | LAST_CUR_HARM_MINc17 | Last Period 3sec 17th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A63 | 0x8A64 | 35427 | 35428 | LAST_CUR_HARM_MINc18 | Last Period 3sec 18th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A65 | 0x8A66 | 35429 | 35430 | LAST_CUR_HARM_MINc19 | Last Period 3sec 19th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A67 | 0x8A68 | 35431 | 35432 | LAST_CUR_HARM_MINc20 | Last Period 3sec 20th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A69 | 0x8A6A | 35433 | 35434 | LAST_CUR_HARM_MINc21 | Last Period 3sec 21st Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A6B | 0x8A6C | 35435 | 35436 | LAST_CUR_HARM_MINc22 | Last Period 3sec 22nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A6D | 0x8A6E | 35437 | 35438 | LAST_CUR_HARM_MINc23 | Last Period 3sec 23rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A6F | 0x8A70 | 35439 | 35440 | LAST_CUR_HARM_MINc24 | Last Period 3sec 24th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A71 | 0x8A72 | 35441 | 35442 | LAST_CUR_HARM_MINc25 | Last Period 3sec 25th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A73 | 0x8A74 | 35443 | 35444 | LAST_CUR_HARM_MINc26 | Last Period 3sec 26th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A75 | 0x8A76 | 35445 | 35446 | LAST_CUR_HARM_MINc27 | Last Period 3sec 27th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A77 | 0x8A78 | 35447 | 35448 | LAST_CUR_HARM_MINc28 | Last Period 3sec 28th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A79 | 0x8A7A | 35449 | 35450 | LAST_CUR_HARM_MINc29 | Last Period 3sec 29th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A7B | 0x8A7C | 35451 | 35452 | LAST_CUR_HARM_MINc30 | Last Period 3sec 30th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A7D | 0x8A7E | 35453 | 35454 | LAST_CUR_HARM_MINc31 | Last Period 3sec 31st Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A7F | 0x8A80 | 35455 | 35456 | LAST_CUR_HARM_MINc32 | Last Period 3sec 32nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A81 | 0x8A82 | 35457 | 35458 | LAST_CUR_HARM_MINc33 | Last Period 3sec 33rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A83 | 0x8A84 | 35459 | 35460 | LAST_CUR_HARM_MINc34 | Last Period 3sec 34th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A85 | 0x8A86 | 35461 | 35462 | LAST_CUR_HARM_MINc35 | Last Period 3sec 35th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A87 | 0x8A88 | 35463 | 35464 | LAST_CUR_HARM_MINc36 | Last Period 3sec 36th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A89 | 0x8A8A | 35465 | 35466 | LAST_CUR_HARM_MINc37 | Last Period 3sec 37th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A8B | 0x8A8C | 35467 | 35468 | LAST_CUR_HARM_MINc38 | Last Period 3sec 38th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A8D | 0x8A8E | 35469 | 35470 | LAST_CUR_HARM_MINc39 | Last Period 3sec 39th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A8F | 0x8A90 | 35471 | 35472 | LAST_CUR_HARM_MINc40 | Last Period 3sec 40th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A91 | 0x8A92 | 35473 | 35474 | LAST_CUR_HARM_MINc41 | Last Period 3sec 41st Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A93 | 0x8A94 | 35475 | 35476 | LAST_CUR_HARM_MINc42 | Last Period 3sec 42nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A95 | 0x8A96 | 35477 | 35478 | LAST_CUR_HARM_MINc43 | Last Period 3sec 43rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A97 | 0x8A98 | 35479 | 35480 | LAST_CUR_HARM_MINc44 | Last Period 3sec 44th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A99 | 0x8A9A | 35481 | 35482 | LAST_CUR_HARM_MINc45 | Last Period 3sec 45th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A9B | 0x8A9C | 35483 | 35484 | LAST_CUR_HARM_MINc46 | Last Period 3sec 46th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A9D | 0x8A9E | 35485 | 35486 | LAST_CUR_HARM_MINc47 | Last Period 3sec 47th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8A9F | 0x8AA0 | 35487 | 35488 | LAST_CUR_HARM_MINc48 | Last Period 3sec 48th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8AA1 | 0x8AA2 | 35489 | 35490 | LAST_CUR_HARM_MINc49 | Last Period 3sec 49th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8AA3 | 0x8AA4 | 35491 | 35492 | LAST_CUR_HARM_MINc50 | Last Period 3sec 50th Phase C Current Harmonics Minimum Value | float | 2 | R
0x8AA5 | 0x8AA6 | 35493 | 35494 | LAST_CUR_HARM_AVGa2 | Last Period 3sec 2nd Phase A Current Harmonics Average Value | float | 2 | R
0x8AA7 | 0x8AA8 | 35495 | 35496 | LAST_CUR_HARM_AVGa3 | Last Period 3sec 3rd Phase A Current Harmonics Average Value | float | 2 | R
0x8AA9 | 0x8AAA | 35497 | 35498 | LAST_CUR_HARM_AVGa4 | Last Period 3sec 4th Phase A Current Harmonics Average Value | float | 2 | R
0x8AAB | 0x8AAC | 35499 | 35500 | LAST_CUR_HARM_AVGa5 | Last Period 3sec 5th Phase A Current Harmonics Average Value | float | 2 | R
0x8AAD | 0x8AAE | 35501 | 35502 | LAST_CUR_HARM_AVGa6 | Last Period 3sec 6th Phase A Current Harmonics Average Value | float | 2 | R
0x8AAF | 0x8AB0 | 35503 | 35504 | LAST_CUR_HARM_AVGa7 | Last Period 3sec 7th Phase A Current Harmonics Average Value | float | 2 | R
0x8AB1 | 0x8AB2 | 35505 | 35506 | LAST_CUR_HARM_AVGa8 | Last Period 3sec 8th Phase A Current Harmonics Average Value | float | 2 | R
0x8AB3 | 0x8AB4 | 35507 | 35508 | LAST_CUR_HARM_AVGa9 | Last Period 3sec 9th Phase A Current Harmonics Average Value | float | 2 | R
0x8AB5 | 0x8AB6 | 35509 | 35510 | LAST_CUR_HARM_AVGa10 | Last Period 3sec 10th Phase A Current Harmonics Average Value | float | 2 | R
0x8AB7 | 0x8AB8 | 35511 | 35512 | LAST_CUR_HARM_AVGa11 | Last Period 3sec 11st Phase A Current Harmonics Average Value | float | 2 | R
0x8AB9 | 0x8ABA | 35513 | 35514 | LAST_CUR_HARM_AVGa12 | Last Period 3sec 12nd Phase A Current Harmonics Average Value | float | 2 | R
0x8ABB | 0x8ABC | 35515 | 35516 | LAST_CUR_HARM_AVGa13 | Last Period 3sec 13rd Phase A Current Harmonics Average Value | float | 2 | R
0x8ABD | 0x8ABE | 35517 | 35518 | LAST_CUR_HARM_AVGa14 | Last Period 3sec 14th Phase A Current Harmonics Average Value | float | 2 | R
0x8ABF | 0x8AC0 | 35519 | 35520 | LAST_CUR_HARM_AVGa15 | Last Period 3sec 15th Phase A Current Harmonics Average Value | float | 2 | R
0x8AC1 | 0x8AC2 | 35521 | 35522 | LAST_CUR_HARM_AVGa16 | Last Period 3sec 16th Phase A Current Harmonics Average Value | float | 2 | R
0x8AC3 | 0x8AC4 | 35523 | 35524 | LAST_CUR_HARM_AVGa17 | Last Period 3sec 17th Phase A Current Harmonics Average Value | float | 2 | R
0x8AC5 | 0x8AC6 | 35525 | 35526 | LAST_CUR_HARM_AVGa18 | Last Period 3sec 18th Phase A Current Harmonics Average Value | float | 2 | R
0x8AC7 | 0x8AC8 | 35527 | 35528 | LAST_CUR_HARM_AVGa19 | Last Period 3sec 19th Phase A Current Harmonics Average Value | float | 2 | R
0x8AC9 | 0x8ACA | 35529 | 35530 | LAST_CUR_HARM_AVGa20 | Last Period 3sec 20th Phase A Current Harmonics Average Value | float | 2 | R
0x8ACB | 0x8ACC | 35531 | 35532 | LAST_CUR_HARM_AVGa21 | Last Period 3sec 21st Phase A Current Harmonics Average Value | float | 2 | R
0x8ACD | 0x8ACE | 35533 | 35534 | LAST_CUR_HARM_AVGa22 | Last Period 3sec 22nd Phase A Current Harmonics Average Value | float | 2 | R
0x8ACF | 0x8AD0 | 35535 | 35536 | LAST_CUR_HARM_AVGa23 | Last Period 3sec 23rd Phase A Current Harmonics Average Value | float | 2 | R
0x8AD1 | 0x8AD2 | 35537 | 35538 | LAST_CUR_HARM_AVGa24 | Last Period 3sec 24th Phase A Current Harmonics Average Value | float | 2 | R
0x8AD3 | 0x8AD4 | 35539 | 35540 | LAST_CUR_HARM_AVGa25 | Last Period 3sec 25th Phase A Current Harmonics Average Value | float | 2 | R
0x8AD5 | 0x8AD6 | 35541 | 35542 | LAST_CUR_HARM_AVGa26 | Last Period 3sec 26th Phase A Current Harmonics Average Value | float | 2 | R
0x8AD7 | 0x8AD8 | 35543 | 35544 | LAST_CUR_HARM_AVGa27 | Last Period 3sec 27th Phase A Current Harmonics Average Value | float | 2 | R
0x8AD9 | 0x8ADA | 35545 | 35546 | LAST_CUR_HARM_AVGa28 | Last Period 3sec 28th Phase A Current Harmonics Average Value | float | 2 | R
0x8ADB | 0x8ADC | 35547 | 35548 | LAST_CUR_HARM_AVGa29 | Last Period 3sec 29th Phase A Current Harmonics Average Value | float | 2 | R
0x8ADD | 0x8ADE | 35549 | 35550 | LAST_CUR_HARM_AVGa30 | Last Period 3sec 30th Phase A Current Harmonics Average Value | float | 2 | R
0x8ADF | 0x8AE0 | 35551 | 35552 | LAST_CUR_HARM_AVGa31 | Last Period 3sec 31st Phase A Current Harmonics Average Value | float | 2 | R
0x8AE1 | 0x8AE2 | 35553 | 35554 | LAST_CUR_HARM_AVGa32 | Last Period 3sec 32nd Phase A Current Harmonics Average Value | float | 2 | R
0x8AE3 | 0x8AE4 | 35555 | 35556 | LAST_CUR_HARM_AVGa33 | Last Period 3sec 33rd Phase A Current Harmonics Average Value | float | 2 | R
0x8AE5 | 0x8AE6 | 35557 | 35558 | LAST_CUR_HARM_AVGa34 | Last Period 3sec 34th Phase A Current Harmonics Average Value | float | 2 | R
0x8AE7 | 0x8AE8 | 35559 | 35560 | LAST_CUR_HARM_AVGa35 | Last Period 3sec 35th Phase A Current Harmonics Average Value | float | 2 | R
0x8AE9 | 0x8AEA | 35561 | 35562 | LAST_CUR_HARM_AVGa36 | Last Period 3sec 36th Phase A Current Harmonics Average Value | float | 2 | R
0x8AEB | 0x8AEC | 35563 | 35564 | LAST_CUR_HARM_AVGa37 | Last Period 3sec 37th Phase A Current Harmonics Average Value | float | 2 | R
0x8AED | 0x8AEE | 35565 | 35566 | LAST_CUR_HARM_AVGa38 | Last Period 3sec 38th Phase A Current Harmonics Average Value | float | 2 | R
0x8AEF | 0x8AF0 | 35567 | 35568 | LAST_CUR_HARM_AVGa39 | Last Period 3sec 39th Phase A Current Harmonics Average Value | float | 2 | R
0x8AF1 | 0x8AF2 | 35569 | 35570 | LAST_CUR_HARM_AVGa40 | Last Period 3sec 40th Phase A Current Harmonics Average Value | float | 2 | R
0x8AF3 | 0x8AF4 | 35571 | 35572 | LAST_CUR_HARM_AVGa41 | Last Period 3sec 41st Phase A Current Harmonics Average Value | float | 2 | R
0x8AF5 | 0x8AF6 | 35573 | 35574 | LAST_CUR_HARM_AVGa42 | Last Period 3sec 42nd Phase A Current Harmonics Average Value | float | 2 | R
0x8AF7 | 0x8AF8 | 35575 | 35576 | LAST_CUR_HARM_AVGa43 | Last Period 3sec 43rd Phase A Current Harmonics Average Value | float | 2 | R
0x8AF9 | 0x8AFA | 35577 | 35578 | LAST_CUR_HARM_AVGa44 | Last Period 3sec 44th Phase A Current Harmonics Average Value | float | 2 | R
0x8AFB | 0x8AFC | 35579 | 35580 | LAST_CUR_HARM_AVGa45 | Last Period 3sec 45th Phase A Current Harmonics Average Value | float | 2 | R
0x8AFD | 0x8AFE | 35581 | 35582 | LAST_CUR_HARM_AVGa46 | Last Period 3sec 46th Phase A Current Harmonics Average Value | float | 2 | R
0x8AFF | 0x8B00 | 35583 | 35584 | LAST_CUR_HARM_AVGa47 | Last Period 3sec 47th Phase A Current Harmonics Average Value | float | 2 | R
0x8B01 | 0x8B02 | 35585 | 35586 | LAST_CUR_HARM_AVGa48 | Last Period 3sec 48th Phase A Current Harmonics Average Value | float | 2 | R
0x8B03 | 0x8B04 | 35587 | 35588 | LAST_CUR_HARM_AVGa49 | Last Period 3sec 49th Phase A Current Harmonics Average Value | float | 2 | R
0x8B05 | 0x8B06 | 35589 | 35590 | LAST_CUR_HARM_AVGa50 | Last Period 3sec 50th Phase A Current Harmonics Average Value | float | 2 | R
0x8B07 | 0x8B08 | 35591 | 35592 | LAST_CUR_HARM_AVGb2 | Last Period 3sec 2nd Phase B Current Harmonics Average Value | float | 2 | R
0x8B09 | 0x8B0A | 35593 | 35594 | LAST_CUR_HARM_AVGb3 | Last Period 3sec 3rd Phase B Current Harmonics Average Value | float | 2 | R
0x8B0B | 0x8B0C | 35595 | 35596 | LAST_CUR_HARM_AVGb4 | Last Period 3sec 4th Phase B Current Harmonics Average Value | float | 2 | R
0x8B0D | 0x8B0E | 35597 | 35598 | LAST_CUR_HARM_AVGb5 | Last Period 3sec 5th Phase B Current Harmonics Average Value | float | 2 | R
0x8B0F | 0x8B10 | 35599 | 35600 | LAST_CUR_HARM_AVGb6 | Last Period 3sec 6th Phase B Current Harmonics Average Value | float | 2 | R
0x8B11 | 0x8B12 | 35601 | 35602 | LAST_CUR_HARM_AVGb7 | Last Period 3sec 7th Phase B Current Harmonics Average Value | float | 2 | R
0x8B13 | 0x8B14 | 35603 | 35604 | LAST_CUR_HARM_AVGb8 | Last Period 3sec 8th Phase B Current Harmonics Average Value | float | 2 | R
0x8B15 | 0x8B16 | 35605 | 35606 | LAST_CUR_HARM_AVGb9 | Last Period 3sec 9th Phase B Current Harmonics Average Value | float | 2 | R
0x8B17 | 0x8B18 | 35607 | 35608 | LAST_CUR_HARM_AVGb10 | Last Period 3sec 10th Phase B Current Harmonics Average Value | float | 2 | R
0x8B19 | 0x8B1A | 35609 | 35610 | LAST_CUR_HARM_AVGb11 | Last Period 3sec 11st Phase B Current Harmonics Average Value | float | 2 | R
0x8B1B | 0x8B1C | 35611 | 35612 | LAST_CUR_HARM_AVGb12 | Last Period 3sec 12nd Phase B Current Harmonics Average Value | float | 2 | R
0x8B1D | 0x8B1E | 35613 | 35614 | LAST_CUR_HARM_AVGb13 | Last Period 3sec 13rd Phase B Current Harmonics Average Value | float | 2 | R
0x8B1F | 0x8B20 | 35615 | 35616 | LAST_CUR_HARM_AVGb14 | Last Period 3sec 14th Phase B Current Harmonics Average Value | float | 2 | R
0x8B21 | 0x8B22 | 35617 | 35618 | LAST_CUR_HARM_AVGb15 | Last Period 3sec 15th Phase B Current Harmonics Average Value | float | 2 | R
0x8B23 | 0x8B24 | 35619 | 35620 | LAST_CUR_HARM_AVGb16 | Last Period 3sec 16th Phase B Current Harmonics Average Value | float | 2 | R
0x8B25 | 0x8B26 | 35621 | 35622 | LAST_CUR_HARM_AVGb17 | Last Period 3sec 17th Phase B Current Harmonics Average Value | float | 2 | R
0x8B27 | 0x8B28 | 35623 | 35624 | LAST_CUR_HARM_AVGb18 | Last Period 3sec 18th Phase B Current Harmonics Average Value | float | 2 | R
0x8B29 | 0x8B2A | 35625 | 35626 | LAST_CUR_HARM_AVGb19 | Last Period 3sec 19th Phase B Current Harmonics Average Value | float | 2 | R
0x8B2B | 0x8B2C | 35627 | 35628 | LAST_CUR_HARM_AVGb20 | Last Period 3sec 20th Phase B Current Harmonics Average Value | float | 2 | R
0x8B2D | 0x8B2E | 35629 | 35630 | LAST_CUR_HARM_AVGb21 | Last Period 3sec 21st Phase B Current Harmonics Average Value | float | 2 | R
0x8B2F | 0x8B30 | 35631 | 35632 | LAST_CUR_HARM_AVGb22 | Last Period 3sec 22nd Phase B Current Harmonics Average Value | float | 2 | R
0x8B31 | 0x8B32 | 35633 | 35634 | LAST_CUR_HARM_AVGb23 | Last Period 3sec 23rd Phase B Current Harmonics Average Value | float | 2 | R
0x8B33 | 0x8B34 | 35635 | 35636 | LAST_CUR_HARM_AVGb24 | Last Period 3sec 24th Phase B Current Harmonics Average Value | float | 2 | R
0x8B35 | 0x8B36 | 35637 | 35638 | LAST_CUR_HARM_AVGb25 | Last Period 3sec 25th Phase B Current Harmonics Average Value | float | 2 | R
0x8B37 | 0x8B38 | 35639 | 35640 | LAST_CUR_HARM_AVGb26 | Last Period 3sec 26th Phase B Current Harmonics Average Value | float | 2 | R
0x8B39 | 0x8B3A | 35641 | 35642 | LAST_CUR_HARM_AVGb27 | Last Period 3sec 27th Phase B Current Harmonics Average Value | float | 2 | R
0x8B3B | 0x8B3C | 35643 | 35644 | LAST_CUR_HARM_AVGb28 | Last Period 3sec 28th Phase B Current Harmonics Average Value | float | 2 | R
0x8B3D | 0x8B3E | 35645 | 35646 | LAST_CUR_HARM_AVGb29 | Last Period 3sec 29th Phase B Current Harmonics Average Value | float | 2 | R
0x8B3F | 0x8B40 | 35647 | 35648 | LAST_CUR_HARM_AVGb30 | Last Period 3sec 30th Phase B Current Harmonics Average Value | float | 2 | R
0x8B41 | 0x8B42 | 35649 | 35650 | LAST_CUR_HARM_AVGb31 | Last Period 3sec 31st Phase B Current Harmonics Average Value | float | 2 | R
0x8B43 | 0x8B44 | 35651 | 35652 | LAST_CUR_HARM_AVGb32 | Last Period 3sec 32nd Phase B Current Harmonics Average Value | float | 2 | R
0x8B45 | 0x8B46 | 35653 | 35654 | LAST_CUR_HARM_AVGb33 | Last Period 3sec 33rd Phase B Current Harmonics Average Value | float | 2 | R
0x8B47 | 0x8B48 | 35655 | 35656 | LAST_CUR_HARM_AVGb34 | Last Period 3sec 34th Phase B Current Harmonics Average Value | float | 2 | R
0x8B49 | 0x8B4A | 35657 | 35658 | LAST_CUR_HARM_AVGb35 | Last Period 3sec 35th Phase B Current Harmonics Average Value | float | 2 | R
0x8B4B | 0x8B4C | 35659 | 35660 | LAST_CUR_HARM_AVGb36 | Last Period 3sec 36th Phase B Current Harmonics Average Value | float | 2 | R
0x8B4D | 0x8B4E | 35661 | 35662 | LAST_CUR_HARM_AVGb37 | Last Period 3sec 37th Phase B Current Harmonics Average Value | float | 2 | R
0x8B4F | 0x8B50 | 35663 | 35664 | LAST_CUR_HARM_AVGb38 | Last Period 3sec 38th Phase B Current Harmonics Average Value | float | 2 | R
0x8B51 | 0x8B52 | 35665 | 35666 | LAST_CUR_HARM_AVGb39 | Last Period 3sec 39th Phase B Current Harmonics Average Value | float | 2 | R
0x8B53 | 0x8B54 | 35667 | 35668 | LAST_CUR_HARM_AVGb40 | Last Period 3sec 40th Phase B Current Harmonics Average Value | float | 2 | R
0x8B55 | 0x8B56 | 35669 | 35670 | LAST_CUR_HARM_AVGb41 | Last Period 3sec 41st Phase B Current Harmonics Average Value | float | 2 | R
0x8B57 | 0x8B58 | 35671 | 35672 | LAST_CUR_HARM_AVGb42 | Last Period 3sec 42nd Phase B Current Harmonics Average Value | float | 2 | R
0x8B59 | 0x8B5A | 35673 | 35674 | LAST_CUR_HARM_AVGb43 | Last Period 3sec 43rd Phase B Current Harmonics Average Value | float | 2 | R
0x8B5B | 0x8B5C | 35675 | 35676 | LAST_CUR_HARM_AVGb44 | Last Period 3sec 44th Phase B Current Harmonics Average Value | float | 2 | R
0x8B5D | 0x8B5E | 35677 | 35678 | LAST_CUR_HARM_AVGb45 | Last Period 3sec 45th Phase B Current Harmonics Average Value | float | 2 | R
0x8B5F | 0x8B60 | 35679 | 35680 | LAST_CUR_HARM_AVGb46 | Last Period 3sec 46th Phase B Current Harmonics Average Value | float | 2 | R
0x8B61 | 0x8B62 | 35681 | 35682 | LAST_CUR_HARM_AVGb47 | Last Period 3sec 47th Phase B Current Harmonics Average Value | float | 2 | R
0x8B63 | 0x8B64 | 35683 | 35684 | LAST_CUR_HARM_AVGb48 | Last Period 3sec 48th Phase B Current Harmonics Average Value | float | 2 | R
0x8B65 | 0x8B66 | 35685 | 35686 | LAST_CUR_HARM_AVGb49 | Last Period 3sec 49th Phase B Current Harmonics Average Value | float | 2 | R
0x8B67 | 0x8B68 | 35687 | 35688 | LAST_CUR_HARM_AVGb50 | Last Period 3sec 50th Phase B Current Harmonics Average Value | float | 2 | R
0x8B69 | 0x8B6A | 35689 | 35690 | LAST_CUR_HARM_AVGc2 | Last Period 3sec 2nd Phase C Current Harmonics Average Value | float | 2 | R
0x8B6B | 0x8B6C | 35691 | 35692 | LAST_CUR_HARM_AVGc3 | Last Period 3sec 3rd Phase C Current Harmonics Average Value | float | 2 | R
0x8B6D | 0x8B6E | 35693 | 35694 | LAST_CUR_HARM_AVGc4 | Last Period 3sec 4th Phase C Current Harmonics Average Value | float | 2 | R
0x8B6F | 0x8B70 | 35695 | 35696 | LAST_CUR_HARM_AVGc5 | Last Period 3sec 5th Phase C Current Harmonics Average Value | float | 2 | R
0x8B71 | 0x8B72 | 35697 | 35698 | LAST_CUR_HARM_AVGc6 | Last Period 3sec 6th Phase C Current Harmonics Average Value | float | 2 | R
0x8B73 | 0x8B74 | 35699 | 35700 | LAST_CUR_HARM_AVGc7 | Last Period 3sec 7th Phase C Current Harmonics Average Value | float | 2 | R
0x8B75 | 0x8B76 | 35701 | 35702 | LAST_CUR_HARM_AVGc8 | Last Period 3sec 8th Phase C Current Harmonics Average Value | float | 2 | R
0x8B77 | 0x8B78 | 35703 | 35704 | LAST_CUR_HARM_AVGc9 | Last Period 3sec 9th Phase C Current Harmonics Average Value | float | 2 | R
0x8B79 | 0x8B7A | 35705 | 35706 | LAST_CUR_HARM_AVGc10 | Last Period 3sec 10th Phase C Current Harmonics Average Value | float | 2 | R
0x8B7B | 0x8B7C | 35707 | 35708 | LAST_CUR_HARM_AVGc11 | Last Period 3sec 11st Phase C Current Harmonics Average Value | float | 2 | R
0x8B7D | 0x8B7E | 35709 | 35710 | LAST_CUR_HARM_AVGc12 | Last Period 3sec 12nd Phase C Current Harmonics Average Value | float | 2 | R
0x8B7F | 0x8B80 | 35711 | 35712 | LAST_CUR_HARM_AVGc13 | Last Period 3sec 13rd Phase C Current Harmonics Average Value | float | 2 | R
0x8B81 | 0x8B82 | 35713 | 35714 | LAST_CUR_HARM_AVGc14 | Last Period 3sec 14th Phase C Current Harmonics Average Value | float | 2 | R
0x8B83 | 0x8B84 | 35715 | 35716 | LAST_CUR_HARM_AVGc15 | Last Period 3sec 15th Phase C Current Harmonics Average Value | float | 2 | R
0x8B85 | 0x8B86 | 35717 | 35718 | LAST_CUR_HARM_AVGc16 | Last Period 3sec 16th Phase C Current Harmonics Average Value | float | 2 | R
0x8B87 | 0x8B88 | 35719 | 35720 | LAST_CUR_HARM_AVGc17 | Last Period 3sec 17th Phase C Current Harmonics Average Value | float | 2 | R
0x8B89 | 0x8B8A | 35721 | 35722 | LAST_CUR_HARM_AVGc18 | Last Period 3sec 18th Phase C Current Harmonics Average Value | float | 2 | R
0x8B8B | 0x8B8C | 35723 | 35724 | LAST_CUR_HARM_AVGc19 | Last Period 3sec 19th Phase C Current Harmonics Average Value | float | 2 | R
0x8B8D | 0x8B8E | 35725 | 35726 | LAST_CUR_HARM_AVGc20 | Last Period 3sec 20th Phase C Current Harmonics Average Value | float | 2 | R
0x8B8F | 0x8B90 | 35727 | 35728 | LAST_CUR_HARM_AVGc21 | Last Period 3sec 21st Phase C Current Harmonics Average Value | float | 2 | R
0x8B91 | 0x8B92 | 35729 | 35730 | LAST_CUR_HARM_AVGc22 | Last Period 3sec 22nd Phase C Current Harmonics Average Value | float | 2 | R
0x8B93 | 0x8B94 | 35731 | 35732 | LAST_CUR_HARM_AVGc23 | Last Period 3sec 23rd Phase C Current Harmonics Average Value | float | 2 | R
0x8B95 | 0x8B96 | 35733 | 35734 | LAST_CUR_HARM_AVGc24 | Last Period 3sec 24th Phase C Current Harmonics Average Value | float | 2 | R
0x8B97 | 0x8B98 | 35735 | 35736 | LAST_CUR_HARM_AVGc25 | Last Period 3sec 25th Phase C Current Harmonics Average Value | float | 2 | R
0x8B99 | 0x8B9A | 35737 | 35738 | LAST_CUR_HARM_AVGc26 | Last Period 3sec 26th Phase C Current Harmonics Average Value | float | 2 | R
0x8B9B | 0x8B9C | 35739 | 35740 | LAST_CUR_HARM_AVGc27 | Last Period 3sec 27th Phase C Current Harmonics Average Value | float | 2 | R
0x8B9D | 0x8B9E | 35741 | 35742 | LAST_CUR_HARM_AVGc28 | Last Period 3sec 28th Phase C Current Harmonics Average Value | float | 2 | R
0x8B9F | 0x8BA0 | 35743 | 35744 | LAST_CUR_HARM_AVGc29 | Last Period 3sec 29th Phase C Current Harmonics Average Value | float | 2 | R
0x8BA1 | 0x8BA2 | 35745 | 35746 | LAST_CUR_HARM_AVGc30 | Last Period 3sec 30th Phase C Current Harmonics Average Value | float | 2 | R
0x8BA3 | 0x8BA4 | 35747 | 35748 | LAST_CUR_HARM_AVGc31 | Last Period 3sec 31st Phase C Current Harmonics Average Value | float | 2 | R
0x8BA5 | 0x8BA6 | 35749 | 35750 | LAST_CUR_HARM_AVGc32 | Last Period 3sec 32nd Phase C Current Harmonics Average Value | float | 2 | R
0x8BA7 | 0x8BA8 | 35751 | 35752 | LAST_CUR_HARM_AVGc33 | Last Period 3sec 33rd Phase C Current Harmonics Average Value | float | 2 | R
0x8BA9 | 0x8BAA | 35753 | 35754 | LAST_CUR_HARM_AVGc34 | Last Period 3sec 34th Phase C Current Harmonics Average Value | float | 2 | R
0x8BAB | 0x8BAC | 35755 | 35756 | LAST_CUR_HARM_AVGc35 | Last Period 3sec 35th Phase C Current Harmonics Average Value | float | 2 | R
0x8BAD | 0x8BAE | 35757 | 35758 | LAST_CUR_HARM_AVGc36 | Last Period 3sec 36th Phase C Current Harmonics Average Value | float | 2 | R
0x8BAF | 0x8BB0 | 35759 | 35760 | LAST_CUR_HARM_AVGc37 | Last Period 3sec 37th Phase C Current Harmonics Average Value | float | 2 | R
0x8BB1 | 0x8BB2 | 35761 | 35762 | LAST_CUR_HARM_AVGc38 | Last Period 3sec 38th Phase C Current Harmonics Average Value | float | 2 | R
0x8BB3 | 0x8BB4 | 35763 | 35764 | LAST_CUR_HARM_AVGc39 | Last Period 3sec 39th Phase C Current Harmonics Average Value | float | 2 | R
0x8BB5 | 0x8BB6 | 35765 | 35766 | LAST_CUR_HARM_AVGc40 | Last Period 3sec 40th Phase C Current Harmonics Average Value | float | 2 | R
0x8BB7 | 0x8BB8 | 35767 | 35768 | LAST_CUR_HARM_AVGc41 | Last Period 3sec 41st Phase C Current Harmonics Average Value | float | 2 | R
0x8BB9 | 0x8BBA | 35769 | 35770 | LAST_CUR_HARM_AVGc42 | Last Period 3sec 42nd Phase C Current Harmonics Average Value | float | 2 | R
0x8BBB | 0x8BBC | 35771 | 35772 | LAST_CUR_HARM_AVGc43 | Last Period 3sec 43rd Phase C Current Harmonics Average Value | float | 2 | R
0x8BBD | 0x8BBE | 35773 | 35774 | LAST_CUR_HARM_AVGc44 | Last Period 3sec 44th Phase C Current Harmonics Average Value | float | 2 | R
0x8BBF | 0x8BC0 | 35775 | 35776 | LAST_CUR_HARM_AVGc45 | Last Period 3sec 45th Phase C Current Harmonics Average Value | float | 2 | R
0x8BC1 | 0x8BC2 | 35777 | 35778 | LAST_CUR_HARM_AVGc46 | Last Period 3sec 46th Phase C Current Harmonics Average Value | float | 2 | R
0x8BC3 | 0x8BC4 | 35779 | 35780 | LAST_CUR_HARM_AVGc47 | Last Period 3sec 47th Phase C Current Harmonics Average Value | float | 2 | R
0x8BC5 | 0x8BC6 | 35781 | 35782 | LAST_CUR_HARM_AVGc48 | Last Period 3sec 48th Phase C Current Harmonics Average Value | float | 2 | R
0x8BC7 | 0x8BC8 | 35783 | 35784 | LAST_CUR_HARM_AVGc49 | Last Period 3sec 49th Phase C Current Harmonics Average Value | float | 2 | R
0x8BC9 | 0x8BCA | 35785 | 35786 | LAST_CUR_HARM_AVGc50 | Last Period 3sec 50th Phase C Current Harmonics Average Value | float | 2 | R
0x8BCB | 0x8BCB | 35787 | 35787 | LAST_N_TDD_99a | Last Period 3sec Phase A TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BCC | 0x8BCC | 35788 | 35788 | LAST_N_TDD_99b | Last Period 3sec Phase B TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BCD | 0x8BCD | 35789 | 35789 | LAST_N_TDD_99c | Last Period 3sec Phase C TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BCE | 0x8BCF | 35790 | 35791 | LAST_TDD_99_PASSa | Last Period 3sec Phase A TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0x8BD0 | 0x8BD1 | 35792 | 35793 | LAST_TDD_99_PASSb | Last Period 3sec Phase B TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0x8BD2 | 0x8BD3 | 35794 | 35795 | LAST_TDD_99_PASSc | Last Period 3sec Phase C TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0x8BD4 | 0x8BD4 | 35796 | 35796 | LAST_N_CUR_HARM_99a2 | Last Period 3sec 2nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BD5 | 0x8BD5 | 35797 | 35797 | LAST_N_CUR_HARM_99a3 | Last Period 3sec 3rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BD6 | 0x8BD6 | 35798 | 35798 | LAST_N_CUR_HARM_99a4 | Last Period 3sec 4th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BD7 | 0x8BD7 | 35799 | 35799 | LAST_N_CUR_HARM_99a5 | Last Period 3sec 5th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BD8 | 0x8BD8 | 35800 | 35800 | LAST_N_CUR_HARM_99a6 | Last Period 3sec 6th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BD9 | 0x8BD9 | 35801 | 35801 | LAST_N_CUR_HARM_99a7 | Last Period 3sec 7th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BDA | 0x8BDA | 35802 | 35802 | LAST_N_CUR_HARM_99a8 | Last Period 3sec 8th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BDB | 0x8BDB | 35803 | 35803 | LAST_N_CUR_HARM_99a9 | Last Period 3sec 9th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BDC | 0x8BDC | 35804 | 35804 | LAST_N_CUR_HARM_99a10 | Last Period 3sec 10th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BDD | 0x8BDD | 35805 | 35805 | LAST_N_CUR_HARM_99a11 | Last Period 3sec 11st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BDE | 0x8BDE | 35806 | 35806 | LAST_N_CUR_HARM_99a12 | Last Period 3sec 12nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BDF | 0x8BDF | 35807 | 35807 | LAST_N_CUR_HARM_99a13 | Last Period 3sec 13rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BE0 | 0x8BE0 | 35808 | 35808 | LAST_N_CUR_HARM_99a14 | Last Period 3sec 14th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BE1 | 0x8BE1 | 35809 | 35809 | LAST_N_CUR_HARM_99a15 | Last Period 3sec 15th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BE2 | 0x8BE2 | 35810 | 35810 | LAST_N_CUR_HARM_99a16 | Last Period 3sec 16th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BE3 | 0x8BE3 | 35811 | 35811 | LAST_N_CUR_HARM_99a17 | Last Period 3sec 17th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BE4 | 0x8BE4 | 35812 | 35812 | LAST_N_CUR_HARM_99a18 | Last Period 3sec 18th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BE5 | 0x8BE5 | 35813 | 35813 | LAST_N_CUR_HARM_99a19 | Last Period 3sec 19th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BE6 | 0x8BE6 | 35814 | 35814 | LAST_N_CUR_HARM_99a20 | Last Period 3sec 20th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BE7 | 0x8BE7 | 35815 | 35815 | LAST_N_CUR_HARM_99a21 | Last Period 3sec 21st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BE8 | 0x8BE8 | 35816 | 35816 | LAST_N_CUR_HARM_99a22 | Last Period 3sec 22nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BE9 | 0x8BE9 | 35817 | 35817 | LAST_N_CUR_HARM_99a23 | Last Period 3sec 23rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BEA | 0x8BEA | 35818 | 35818 | LAST_N_CUR_HARM_99a24 | Last Period 3sec 24th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BEB | 0x8BEB | 35819 | 35819 | LAST_N_CUR_HARM_99a25 | Last Period 3sec 25th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BEC | 0x8BEC | 35820 | 35820 | LAST_N_CUR_HARM_99a26 | Last Period 3sec 26th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BED | 0x8BED | 35821 | 35821 | LAST_N_CUR_HARM_99a27 | Last Period 3sec 27th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BEE | 0x8BEE | 35822 | 35822 | LAST_N_CUR_HARM_99a28 | Last Period 3sec 28th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BEF | 0x8BEF | 35823 | 35823 | LAST_N_CUR_HARM_99a29 | Last Period 3sec 29th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BF0 | 0x8BF0 | 35824 | 35824 | LAST_N_CUR_HARM_99a30 | Last Period 3sec 30th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BF1 | 0x8BF1 | 35825 | 35825 | LAST_N_CUR_HARM_99a31 | Last Period 3sec 31st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BF2 | 0x8BF2 | 35826 | 35826 | LAST_N_CUR_HARM_99a32 | Last Period 3sec 32nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BF3 | 0x8BF3 | 35827 | 35827 | LAST_N_CUR_HARM_99a33 | Last Period 3sec 33rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BF4 | 0x8BF4 | 35828 | 35828 | LAST_N_CUR_HARM_99a34 | Last Period 3sec 34th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BF5 | 0x8BF5 | 35829 | 35829 | LAST_N_CUR_HARM_99a35 | Last Period 3sec 35th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BF6 | 0x8BF6 | 35830 | 35830 | LAST_N_CUR_HARM_99a36 | Last Period 3sec 36th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BF7 | 0x8BF7 | 35831 | 35831 | LAST_N_CUR_HARM_99a37 | Last Period 3sec 37th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BF8 | 0x8BF8 | 35832 | 35832 | LAST_N_CUR_HARM_99a38 | Last Period 3sec 38th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BF9 | 0x8BF9 | 35833 | 35833 | LAST_N_CUR_HARM_99a39 | Last Period 3sec 39th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BFA | 0x8BFA | 35834 | 35834 | LAST_N_CUR_HARM_99a40 | Last Period 3sec 40th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BFB | 0x8BFB | 35835 | 35835 | LAST_N_CUR_HARM_99a41 | Last Period 3sec 41st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BFC | 0x8BFC | 35836 | 35836 | LAST_N_CUR_HARM_99a42 | Last Period 3sec 42nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BFD | 0x8BFD | 35837 | 35837 | LAST_N_CUR_HARM_99a43 | Last Period 3sec 43rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BFE | 0x8BFE | 35838 | 35838 | LAST_N_CUR_HARM_99a44 | Last Period 3sec 44th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8BFF | 0x8BFF | 35839 | 35839 | LAST_N_CUR_HARM_99a45 | Last Period 3sec 45th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C00 | 0x8C00 | 35840 | 35840 | LAST_N_CUR_HARM_99a46 | Last Period 3sec 46th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C01 | 0x8C01 | 35841 | 35841 | LAST_N_CUR_HARM_99a47 | Last Period 3sec 47th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C02 | 0x8C02 | 35842 | 35842 | LAST_N_CUR_HARM_99a48 | Last Period 3sec 48th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C03 | 0x8C03 | 35843 | 35843 | LAST_N_CUR_HARM_99a49 | Last Period 3sec 49th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C04 | 0x8C04 | 35844 | 35844 | LAST_N_CUR_HARM_99a50 | Last Period 3sec 50th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C05 | 0x8C05 | 35845 | 35845 | LAST_N_CUR_HARM_99b2 | Last Period 3sec 2nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C06 | 0x8C06 | 35846 | 35846 | LAST_N_CUR_HARM_99b3 | Last Period 3sec 3rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C07 | 0x8C07 | 35847 | 35847 | LAST_N_CUR_HARM_99b4 | Last Period 3sec 4th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C08 | 0x8C08 | 35848 | 35848 | LAST_N_CUR_HARM_99b5 | Last Period 3sec 5th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C09 | 0x8C09 | 35849 | 35849 | LAST_N_CUR_HARM_99b6 | Last Period 3sec 6th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C0A | 0x8C0A | 35850 | 35850 | LAST_N_CUR_HARM_99b7 | Last Period 3sec 7th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C0B | 0x8C0B | 35851 | 35851 | LAST_N_CUR_HARM_99b8 | Last Period 3sec 8th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C0C | 0x8C0C | 35852 | 35852 | LAST_N_CUR_HARM_99b9 | Last Period 3sec 9th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C0D | 0x8C0D | 35853 | 35853 | LAST_N_CUR_HARM_99b10 | Last Period 3sec 10th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C0E | 0x8C0E | 35854 | 35854 | LAST_N_CUR_HARM_99b11 | Last Period 3sec 11st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C0F | 0x8C0F | 35855 | 35855 | LAST_N_CUR_HARM_99b12 | Last Period 3sec 12nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C10 | 0x8C10 | 35856 | 35856 | LAST_N_CUR_HARM_99b13 | Last Period 3sec 13rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C11 | 0x8C11 | 35857 | 35857 | LAST_N_CUR_HARM_99b14 | Last Period 3sec 14th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C12 | 0x8C12 | 35858 | 35858 | LAST_N_CUR_HARM_99b15 | Last Period 3sec 15th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C13 | 0x8C13 | 35859 | 35859 | LAST_N_CUR_HARM_99b16 | Last Period 3sec 16th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C14 | 0x8C14 | 35860 | 35860 | LAST_N_CUR_HARM_99b17 | Last Period 3sec 17th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C15 | 0x8C15 | 35861 | 35861 | LAST_N_CUR_HARM_99b18 | Last Period 3sec 18th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C16 | 0x8C16 | 35862 | 35862 | LAST_N_CUR_HARM_99b19 | Last Period 3sec 19th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C17 | 0x8C17 | 35863 | 35863 | LAST_N_CUR_HARM_99b20 | Last Period 3sec 20th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C18 | 0x8C18 | 35864 | 35864 | LAST_N_CUR_HARM_99b21 | Last Period 3sec 21st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C19 | 0x8C19 | 35865 | 35865 | LAST_N_CUR_HARM_99b22 | Last Period 3sec 22nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C1A | 0x8C1A | 35866 | 35866 | LAST_N_CUR_HARM_99b23 | Last Period 3sec 23rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C1B | 0x8C1B | 35867 | 35867 | LAST_N_CUR_HARM_99b24 | Last Period 3sec 24th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C1C | 0x8C1C | 35868 | 35868 | LAST_N_CUR_HARM_99b25 | Last Period 3sec 25th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C1D | 0x8C1D | 35869 | 35869 | LAST_N_CUR_HARM_99b26 | Last Period 3sec 26th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C1E | 0x8C1E | 35870 | 35870 | LAST_N_CUR_HARM_99b27 | Last Period 3sec 27th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C1F | 0x8C1F | 35871 | 35871 | LAST_N_CUR_HARM_99b28 | Last Period 3sec 28th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C20 | 0x8C20 | 35872 | 35872 | LAST_N_CUR_HARM_99b29 | Last Period 3sec 29th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C21 | 0x8C21 | 35873 | 35873 | LAST_N_CUR_HARM_99b30 | Last Period 3sec 30th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C22 | 0x8C22 | 35874 | 35874 | LAST_N_CUR_HARM_99b31 | Last Period 3sec 31st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C23 | 0x8C23 | 35875 | 35875 | LAST_N_CUR_HARM_99b32 | Last Period 3sec 32nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C24 | 0x8C24 | 35876 | 35876 | LAST_N_CUR_HARM_99b33 | Last Period 3sec 33rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C25 | 0x8C25 | 35877 | 35877 | LAST_N_CUR_HARM_99b34 | Last Period 3sec 34th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C26 | 0x8C26 | 35878 | 35878 | LAST_N_CUR_HARM_99b35 | Last Period 3sec 35th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C27 | 0x8C27 | 35879 | 35879 | LAST_N_CUR_HARM_99b36 | Last Period 3sec 36th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C28 | 0x8C28 | 35880 | 35880 | LAST_N_CUR_HARM_99b37 | Last Period 3sec 37th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C29 | 0x8C29 | 35881 | 35881 | LAST_N_CUR_HARM_99b38 | Last Period 3sec 38th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C2A | 0x8C2A | 35882 | 35882 | LAST_N_CUR_HARM_99b39 | Last Period 3sec 39th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C2B | 0x8C2B | 35883 | 35883 | LAST_N_CUR_HARM_99b40 | Last Period 3sec 40th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C2C | 0x8C2C | 35884 | 35884 | LAST_N_CUR_HARM_99b41 | Last Period 3sec 41st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C2D | 0x8C2D | 35885 | 35885 | LAST_N_CUR_HARM_99b42 | Last Period 3sec 42nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C2E | 0x8C2E | 35886 | 35886 | LAST_N_CUR_HARM_99b43 | Last Period 3sec 43rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C2F | 0x8C2F | 35887 | 35887 | LAST_N_CUR_HARM_99b44 | Last Period 3sec 44th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C30 | 0x8C30 | 35888 | 35888 | LAST_N_CUR_HARM_99b45 | Last Period 3sec 45th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C31 | 0x8C31 | 35889 | 35889 | LAST_N_CUR_HARM_99b46 | Last Period 3sec 46th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C32 | 0x8C32 | 35890 | 35890 | LAST_N_CUR_HARM_99b47 | Last Period 3sec 47th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C33 | 0x8C33 | 35891 | 35891 | LAST_N_CUR_HARM_99b48 | Last Period 3sec 48th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C34 | 0x8C34 | 35892 | 35892 | LAST_N_CUR_HARM_99b49 | Last Period 3sec 49th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C35 | 0x8C35 | 35893 | 35893 | LAST_N_CUR_HARM_99b50 | Last Period 3sec 50th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C36 | 0x8C36 | 35894 | 35894 | LAST_N_CUR_HARM_99c2 | Last Period 3sec 2nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C37 | 0x8C37 | 35895 | 35895 | LAST_N_CUR_HARM_99c3 | Last Period 3sec 3rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C38 | 0x8C38 | 35896 | 35896 | LAST_N_CUR_HARM_99c4 | Last Period 3sec 4th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C39 | 0x8C39 | 35897 | 35897 | LAST_N_CUR_HARM_99c5 | Last Period 3sec 5th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C3A | 0x8C3A | 35898 | 35898 | LAST_N_CUR_HARM_99c6 | Last Period 3sec 6th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C3B | 0x8C3B | 35899 | 35899 | LAST_N_CUR_HARM_99c7 | Last Period 3sec 7th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C3C | 0x8C3C | 35900 | 35900 | LAST_N_CUR_HARM_99c8 | Last Period 3sec 8th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C3D | 0x8C3D | 35901 | 35901 | LAST_N_CUR_HARM_99c9 | Last Period 3sec 9th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C3E | 0x8C3E | 35902 | 35902 | LAST_N_CUR_HARM_99c10 | Last Period 3sec 10th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C3F | 0x8C3F | 35903 | 35903 | LAST_N_CUR_HARM_99c11 | Last Period 3sec 11st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C40 | 0x8C40 | 35904 | 35904 | LAST_N_CUR_HARM_99c12 | Last Period 3sec 12nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C41 | 0x8C41 | 35905 | 35905 | LAST_N_CUR_HARM_99c13 | Last Period 3sec 13rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C42 | 0x8C42 | 35906 | 35906 | LAST_N_CUR_HARM_99c14 | Last Period 3sec 14th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C43 | 0x8C43 | 35907 | 35907 | LAST_N_CUR_HARM_99c15 | Last Period 3sec 15th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C44 | 0x8C44 | 35908 | 35908 | LAST_N_CUR_HARM_99c16 | Last Period 3sec 16th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C45 | 0x8C45 | 35909 | 35909 | LAST_N_CUR_HARM_99c17 | Last Period 3sec 17th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C46 | 0x8C46 | 35910 | 35910 | LAST_N_CUR_HARM_99c18 | Last Period 3sec 18th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C47 | 0x8C47 | 35911 | 35911 | LAST_N_CUR_HARM_99c19 | Last Period 3sec 19th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C48 | 0x8C48 | 35912 | 35912 | LAST_N_CUR_HARM_99c20 | Last Period 3sec 20th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C49 | 0x8C49 | 35913 | 35913 | LAST_N_CUR_HARM_99c21 | Last Period 3sec 21st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C4A | 0x8C4A | 35914 | 35914 | LAST_N_CUR_HARM_99c22 | Last Period 3sec 22nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C4B | 0x8C4B | 35915 | 35915 | LAST_N_CUR_HARM_99c23 | Last Period 3sec 23rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C4C | 0x8C4C | 35916 | 35916 | LAST_N_CUR_HARM_99c24 | Last Period 3sec 24th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C4D | 0x8C4D | 35917 | 35917 | LAST_N_CUR_HARM_99c25 | Last Period 3sec 25th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C4E | 0x8C4E | 35918 | 35918 | LAST_N_CUR_HARM_99c26 | Last Period 3sec 26th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C4F | 0x8C4F | 35919 | 35919 | LAST_N_CUR_HARM_99c27 | Last Period 3sec 27th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C50 | 0x8C50 | 35920 | 35920 | LAST_N_CUR_HARM_99c28 | Last Period 3sec 28th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C51 | 0x8C51 | 35921 | 35921 | LAST_N_CUR_HARM_99c29 | Last Period 3sec 29th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C52 | 0x8C52 | 35922 | 35922 | LAST_N_CUR_HARM_99c30 | Last Period 3sec 30th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C53 | 0x8C53 | 35923 | 35923 | LAST_N_CUR_HARM_99c31 | Last Period 3sec 31st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C54 | 0x8C54 | 35924 | 35924 | LAST_N_CUR_HARM_99c32 | Last Period 3sec 32nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C55 | 0x8C55 | 35925 | 35925 | LAST_N_CUR_HARM_99c33 | Last Period 3sec 33rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C56 | 0x8C56 | 35926 | 35926 | LAST_N_CUR_HARM_99c34 | Last Period 3sec 34th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C57 | 0x8C57 | 35927 | 35927 | LAST_N_CUR_HARM_99c35 | Last Period 3sec 35th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C58 | 0x8C58 | 35928 | 35928 | LAST_N_CUR_HARM_99c36 | Last Period 3sec 36th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C59 | 0x8C59 | 35929 | 35929 | LAST_N_CUR_HARM_99c37 | Last Period 3sec 37th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C5A | 0x8C5A | 35930 | 35930 | LAST_N_CUR_HARM_99c38 | Last Period 3sec 38th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C5B | 0x8C5B | 35931 | 35931 | LAST_N_CUR_HARM_99c39 | Last Period 3sec 39th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C5C | 0x8C5C | 35932 | 35932 | LAST_N_CUR_HARM_99c40 | Last Period 3sec 40th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C5D | 0x8C5D | 35933 | 35933 | LAST_N_CUR_HARM_99c41 | Last Period 3sec 41st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C5E | 0x8C5E | 35934 | 35934 | LAST_N_CUR_HARM_99c42 | Last Period 3sec 42nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C5F | 0x8C5F | 35935 | 35935 | LAST_N_CUR_HARM_99c43 | Last Period 3sec 43rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C60 | 0x8C60 | 35936 | 35936 | LAST_N_CUR_HARM_99c44 | Last Period 3sec 44th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C61 | 0x8C61 | 35937 | 35937 | LAST_N_CUR_HARM_99c45 | Last Period 3sec 45th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C62 | 0x8C62 | 35938 | 35938 | LAST_N_CUR_HARM_99c46 | Last Period 3sec 46th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C63 | 0x8C63 | 35939 | 35939 | LAST_N_CUR_HARM_99c47 | Last Period 3sec 47th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C64 | 0x8C64 | 35940 | 35940 | LAST_N_CUR_HARM_99c48 | Last Period 3sec 48th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C65 | 0x8C65 | 35941 | 35941 | LAST_N_CUR_HARM_99c49 | Last Period 3sec 49th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C66 | 0x8C66 | 35942 | 35942 | LAST_N_CUR_HARM_99c50 | Last Period 3sec 50th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x8C67 | 0x8C68 | 35943 | 35944 | LAST_CUR_HARM_99_PASSa2 | Last Period 3sec 2nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C69 | 0x8C6A | 35945 | 35946 | LAST_CUR_HARM_99_PASSa3 | Last Period 3sec 3rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C6B | 0x8C6C | 35947 | 35948 | LAST_CUR_HARM_99_PASSa4 | Last Period 3sec 4th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C6D | 0x8C6E | 35949 | 35950 | LAST_CUR_HARM_99_PASSa5 | Last Period 3sec 5th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C6F | 0x8C70 | 35951 | 35952 | LAST_CUR_HARM_99_PASSa6 | Last Period 3sec 6th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C71 | 0x8C72 | 35953 | 35954 | LAST_CUR_HARM_99_PASSa7 | Last Period 3sec 7th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C73 | 0x8C74 | 35955 | 35956 | LAST_CUR_HARM_99_PASSa8 | Last Period 3sec 8th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C75 | 0x8C76 | 35957 | 35958 | LAST_CUR_HARM_99_PASSa9 | Last Period 3sec 9th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C77 | 0x8C78 | 35959 | 35960 | LAST_CUR_HARM_99_PASSa10 | Last Period 3sec 10th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C79 | 0x8C7A | 35961 | 35962 | LAST_CUR_HARM_99_PASSa11 | Last Period 3sec 11st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C7B | 0x8C7C | 35963 | 35964 | LAST_CUR_HARM_99_PASSa12 | Last Period 3sec 12nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C7D | 0x8C7E | 35965 | 35966 | LAST_CUR_HARM_99_PASSa13 | Last Period 3sec 13rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C7F | 0x8C80 | 35967 | 35968 | LAST_CUR_HARM_99_PASSa14 | Last Period 3sec 14th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C81 | 0x8C82 | 35969 | 35970 | LAST_CUR_HARM_99_PASSa15 | Last Period 3sec 15th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C83 | 0x8C84 | 35971 | 35972 | LAST_CUR_HARM_99_PASSa16 | Last Period 3sec 16th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C85 | 0x8C86 | 35973 | 35974 | LAST_CUR_HARM_99_PASSa17 | Last Period 3sec 17th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C87 | 0x8C88 | 35975 | 35976 | LAST_CUR_HARM_99_PASSa18 | Last Period 3sec 18th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C89 | 0x8C8A | 35977 | 35978 | LAST_CUR_HARM_99_PASSa19 | Last Period 3sec 19th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C8B | 0x8C8C | 35979 | 35980 | LAST_CUR_HARM_99_PASSa20 | Last Period 3sec 20th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C8D | 0x8C8E | 35981 | 35982 | LAST_CUR_HARM_99_PASSa21 | Last Period 3sec 21st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C8F | 0x8C90 | 35983 | 35984 | LAST_CUR_HARM_99_PASSa22 | Last Period 3sec 22nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C91 | 0x8C92 | 35985 | 35986 | LAST_CUR_HARM_99_PASSa23 | Last Period 3sec 23rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C93 | 0x8C94 | 35987 | 35988 | LAST_CUR_HARM_99_PASSa24 | Last Period 3sec 24th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C95 | 0x8C96 | 35989 | 35990 | LAST_CUR_HARM_99_PASSa25 | Last Period 3sec 25th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C97 | 0x8C98 | 35991 | 35992 | LAST_CUR_HARM_99_PASSa26 | Last Period 3sec 26th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C99 | 0x8C9A | 35993 | 35994 | LAST_CUR_HARM_99_PASSa27 | Last Period 3sec 27th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C9B | 0x8C9C | 35995 | 35996 | LAST_CUR_HARM_99_PASSa28 | Last Period 3sec 28th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C9D | 0x8C9E | 35997 | 35998 | LAST_CUR_HARM_99_PASSa29 | Last Period 3sec 29th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8C9F | 0x8CA0 | 35999 | 36000 | LAST_CUR_HARM_99_PASSa30 | Last Period 3sec 30th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CA1 | 0x8CA2 | 36001 | 36002 | LAST_CUR_HARM_99_PASSa31 | Last Period 3sec 31st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CA3 | 0x8CA4 | 36003 | 36004 | LAST_CUR_HARM_99_PASSa32 | Last Period 3sec 32nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CA5 | 0x8CA6 | 36005 | 36006 | LAST_CUR_HARM_99_PASSa33 | Last Period 3sec 33rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CA7 | 0x8CA8 | 36007 | 36008 | LAST_CUR_HARM_99_PASSa34 | Last Period 3sec 34th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CA9 | 0x8CAA | 36009 | 36010 | LAST_CUR_HARM_99_PASSa35 | Last Period 3sec 35th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CAB | 0x8CAC | 36011 | 36012 | LAST_CUR_HARM_99_PASSa36 | Last Period 3sec 36th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CAD | 0x8CAE | 36013 | 36014 | LAST_CUR_HARM_99_PASSa37 | Last Period 3sec 37th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CAF | 0x8CB0 | 36015 | 36016 | LAST_CUR_HARM_99_PASSa38 | Last Period 3sec 38th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CB1 | 0x8CB2 | 36017 | 36018 | LAST_CUR_HARM_99_PASSa39 | Last Period 3sec 39th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CB3 | 0x8CB4 | 36019 | 36020 | LAST_CUR_HARM_99_PASSa40 | Last Period 3sec 40th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CB5 | 0x8CB6 | 36021 | 36022 | LAST_CUR_HARM_99_PASSa41 | Last Period 3sec 41st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CB7 | 0x8CB8 | 36023 | 36024 | LAST_CUR_HARM_99_PASSa42 | Last Period 3sec 42nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CB9 | 0x8CBA | 36025 | 36026 | LAST_CUR_HARM_99_PASSa43 | Last Period 3sec 43rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CBB | 0x8CBC | 36027 | 36028 | LAST_CUR_HARM_99_PASSa44 | Last Period 3sec 44th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CBD | 0x8CBE | 36029 | 36030 | LAST_CUR_HARM_99_PASSa45 | Last Period 3sec 45th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CBF | 0x8CC0 | 36031 | 36032 | LAST_CUR_HARM_99_PASSa46 | Last Period 3sec 46th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CC1 | 0x8CC2 | 36033 | 36034 | LAST_CUR_HARM_99_PASSa47 | Last Period 3sec 47th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CC3 | 0x8CC4 | 36035 | 36036 | LAST_CUR_HARM_99_PASSa48 | Last Period 3sec 48th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CC5 | 0x8CC6 | 36037 | 36038 | LAST_CUR_HARM_99_PASSa49 | Last Period 3sec 49th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CC7 | 0x8CC8 | 36039 | 36040 | LAST_CUR_HARM_99_PASSa50 | Last Period 3sec 50th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CC9 | 0x8CCA | 36041 | 36042 | LAST_CUR_HARM_99_PASSb2 | Last Period 3sec 2nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CCB | 0x8CCC | 36043 | 36044 | LAST_CUR_HARM_99_PASSb3 | Last Period 3sec 3rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CCD | 0x8CCE | 36045 | 36046 | LAST_CUR_HARM_99_PASSb4 | Last Period 3sec 4th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CCF | 0x8CD0 | 36047 | 36048 | LAST_CUR_HARM_99_PASSb5 | Last Period 3sec 5th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CD1 | 0x8CD2 | 36049 | 36050 | LAST_CUR_HARM_99_PASSb6 | Last Period 3sec 6th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CD3 | 0x8CD4 | 36051 | 36052 | LAST_CUR_HARM_99_PASSb7 | Last Period 3sec 7th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CD5 | 0x8CD6 | 36053 | 36054 | LAST_CUR_HARM_99_PASSb8 | Last Period 3sec 8th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CD7 | 0x8CD8 | 36055 | 36056 | LAST_CUR_HARM_99_PASSb9 | Last Period 3sec 9th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CD9 | 0x8CDA | 36057 | 36058 | LAST_CUR_HARM_99_PASSb10 | Last Period 3sec 10th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CDB | 0x8CDC | 36059 | 36060 | LAST_CUR_HARM_99_PASSb11 | Last Period 3sec 11st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CDD | 0x8CDE | 36061 | 36062 | LAST_CUR_HARM_99_PASSb12 | Last Period 3sec 12nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CDF | 0x8CE0 | 36063 | 36064 | LAST_CUR_HARM_99_PASSb13 | Last Period 3sec 13rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CE1 | 0x8CE2 | 36065 | 36066 | LAST_CUR_HARM_99_PASSb14 | Last Period 3sec 14th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CE3 | 0x8CE4 | 36067 | 36068 | LAST_CUR_HARM_99_PASSb15 | Last Period 3sec 15th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CE5 | 0x8CE6 | 36069 | 36070 | LAST_CUR_HARM_99_PASSb16 | Last Period 3sec 16th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CE7 | 0x8CE8 | 36071 | 36072 | LAST_CUR_HARM_99_PASSb17 | Last Period 3sec 17th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CE9 | 0x8CEA | 36073 | 36074 | LAST_CUR_HARM_99_PASSb18 | Last Period 3sec 18th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CEB | 0x8CEC | 36075 | 36076 | LAST_CUR_HARM_99_PASSb19 | Last Period 3sec 19th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CED | 0x8CEE | 36077 | 36078 | LAST_CUR_HARM_99_PASSb20 | Last Period 3sec 20th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CEF | 0x8CF0 | 36079 | 36080 | LAST_CUR_HARM_99_PASSb21 | Last Period 3sec 21st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CF1 | 0x8CF2 | 36081 | 36082 | LAST_CUR_HARM_99_PASSb22 | Last Period 3sec 22nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CF3 | 0x8CF4 | 36083 | 36084 | LAST_CUR_HARM_99_PASSb23 | Last Period 3sec 23rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CF5 | 0x8CF6 | 36085 | 36086 | LAST_CUR_HARM_99_PASSb24 | Last Period 3sec 24th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CF7 | 0x8CF8 | 36087 | 36088 | LAST_CUR_HARM_99_PASSb25 | Last Period 3sec 25th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CF9 | 0x8CFA | 36089 | 36090 | LAST_CUR_HARM_99_PASSb26 | Last Period 3sec 26th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CFB | 0x8CFC | 36091 | 36092 | LAST_CUR_HARM_99_PASSb27 | Last Period 3sec 27th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CFD | 0x8CFE | 36093 | 36094 | LAST_CUR_HARM_99_PASSb28 | Last Period 3sec 28th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8CFF | 0x8D00 | 36095 | 36096 | LAST_CUR_HARM_99_PASSb29 | Last Period 3sec 29th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D01 | 0x8D02 | 36097 | 36098 | LAST_CUR_HARM_99_PASSb30 | Last Period 3sec 30th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D03 | 0x8D04 | 36099 | 36100 | LAST_CUR_HARM_99_PASSb31 | Last Period 3sec 31st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D05 | 0x8D06 | 36101 | 36102 | LAST_CUR_HARM_99_PASSb32 | Last Period 3sec 32nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D07 | 0x8D08 | 36103 | 36104 | LAST_CUR_HARM_99_PASSb33 | Last Period 3sec 33rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D09 | 0x8D0A | 36105 | 36106 | LAST_CUR_HARM_99_PASSb34 | Last Period 3sec 34th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D0B | 0x8D0C | 36107 | 36108 | LAST_CUR_HARM_99_PASSb35 | Last Period 3sec 35th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D0D | 0x8D0E | 36109 | 36110 | LAST_CUR_HARM_99_PASSb36 | Last Period 3sec 36th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D0F | 0x8D10 | 36111 | 36112 | LAST_CUR_HARM_99_PASSb37 | Last Period 3sec 37th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D11 | 0x8D12 | 36113 | 36114 | LAST_CUR_HARM_99_PASSb38 | Last Period 3sec 38th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D13 | 0x8D14 | 36115 | 36116 | LAST_CUR_HARM_99_PASSb39 | Last Period 3sec 39th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D15 | 0x8D16 | 36117 | 36118 | LAST_CUR_HARM_99_PASSb40 | Last Period 3sec 40th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D17 | 0x8D18 | 36119 | 36120 | LAST_CUR_HARM_99_PASSb41 | Last Period 3sec 41st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D19 | 0x8D1A | 36121 | 36122 | LAST_CUR_HARM_99_PASSb42 | Last Period 3sec 42nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D1B | 0x8D1C | 36123 | 36124 | LAST_CUR_HARM_99_PASSb43 | Last Period 3sec 43rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D1D | 0x8D1E | 36125 | 36126 | LAST_CUR_HARM_99_PASSb44 | Last Period 3sec 44th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D1F | 0x8D20 | 36127 | 36128 | LAST_CUR_HARM_99_PASSb45 | Last Period 3sec 45th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D21 | 0x8D22 | 36129 | 36130 | LAST_CUR_HARM_99_PASSb46 | Last Period 3sec 46th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D23 | 0x8D24 | 36131 | 36132 | LAST_CUR_HARM_99_PASSb47 | Last Period 3sec 47th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D25 | 0x8D26 | 36133 | 36134 | LAST_CUR_HARM_99_PASSb48 | Last Period 3sec 48th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D27 | 0x8D28 | 36135 | 36136 | LAST_CUR_HARM_99_PASSb49 | Last Period 3sec 49th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D29 | 0x8D2A | 36137 | 36138 | LAST_CUR_HARM_99_PASSb50 | Last Period 3sec 50th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D2B | 0x8D2C | 36139 | 36140 | LAST_CUR_HARM_99_PASSc2 | Last Period 3sec 2nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D2D | 0x8D2E | 36141 | 36142 | LAST_CUR_HARM_99_PASSc3 | Last Period 3sec 3rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D2F | 0x8D30 | 36143 | 36144 | LAST_CUR_HARM_99_PASSc4 | Last Period 3sec 4th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D31 | 0x8D32 | 36145 | 36146 | LAST_CUR_HARM_99_PASSc5 | Last Period 3sec 5th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D33 | 0x8D34 | 36147 | 36148 | LAST_CUR_HARM_99_PASSc6 | Last Period 3sec 6th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D35 | 0x8D36 | 36149 | 36150 | LAST_CUR_HARM_99_PASSc7 | Last Period 3sec 7th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D37 | 0x8D38 | 36151 | 36152 | LAST_CUR_HARM_99_PASSc8 | Last Period 3sec 8th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D39 | 0x8D3A | 36153 | 36154 | LAST_CUR_HARM_99_PASSc9 | Last Period 3sec 9th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D3B | 0x8D3C | 36155 | 36156 | LAST_CUR_HARM_99_PASSc10 | Last Period 3sec 10th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D3D | 0x8D3E | 36157 | 36158 | LAST_CUR_HARM_99_PASSc11 | Last Period 3sec 11st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D3F | 0x8D40 | 36159 | 36160 | LAST_CUR_HARM_99_PASSc12 | Last Period 3sec 12nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D41 | 0x8D42 | 36161 | 36162 | LAST_CUR_HARM_99_PASSc13 | Last Period 3sec 13rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D43 | 0x8D44 | 36163 | 36164 | LAST_CUR_HARM_99_PASSc14 | Last Period 3sec 14th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D45 | 0x8D46 | 36165 | 36166 | LAST_CUR_HARM_99_PASSc15 | Last Period 3sec 15th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D47 | 0x8D48 | 36167 | 36168 | LAST_CUR_HARM_99_PASSc16 | Last Period 3sec 16th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D49 | 0x8D4A | 36169 | 36170 | LAST_CUR_HARM_99_PASSc17 | Last Period 3sec 17th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D4B | 0x8D4C | 36171 | 36172 | LAST_CUR_HARM_99_PASSc18 | Last Period 3sec 18th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D4D | 0x8D4E | 36173 | 36174 | LAST_CUR_HARM_99_PASSc19 | Last Period 3sec 19th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D4F | 0x8D50 | 36175 | 36176 | LAST_CUR_HARM_99_PASSc20 | Last Period 3sec 20th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D51 | 0x8D52 | 36177 | 36178 | LAST_CUR_HARM_99_PASSc21 | Last Period 3sec 21st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D53 | 0x8D54 | 36179 | 36180 | LAST_CUR_HARM_99_PASSc22 | Last Period 3sec 22nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D55 | 0x8D56 | 36181 | 36182 | LAST_CUR_HARM_99_PASSc23 | Last Period 3sec 23rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D57 | 0x8D58 | 36183 | 36184 | LAST_CUR_HARM_99_PASSc24 | Last Period 3sec 24th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D59 | 0x8D5A | 36185 | 36186 | LAST_CUR_HARM_99_PASSc25 | Last Period 3sec 25th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D5B | 0x8D5C | 36187 | 36188 | LAST_CUR_HARM_99_PASSc26 | Last Period 3sec 26th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D5D | 0x8D5E | 36189 | 36190 | LAST_CUR_HARM_99_PASSc27 | Last Period 3sec 27th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D5F | 0x8D60 | 36191 | 36192 | LAST_CUR_HARM_99_PASSc28 | Last Period 3sec 28th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D61 | 0x8D62 | 36193 | 36194 | LAST_CUR_HARM_99_PASSc29 | Last Period 3sec 29th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D63 | 0x8D64 | 36195 | 36196 | LAST_CUR_HARM_99_PASSc30 | Last Period 3sec 30th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D65 | 0x8D66 | 36197 | 36198 | LAST_CUR_HARM_99_PASSc31 | Last Period 3sec 31st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D67 | 0x8D68 | 36199 | 36200 | LAST_CUR_HARM_99_PASSc32 | Last Period 3sec 32nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D69 | 0x8D6A | 36201 | 36202 | LAST_CUR_HARM_99_PASSc33 | Last Period 3sec 33rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D6B | 0x8D6C | 36203 | 36204 | LAST_CUR_HARM_99_PASSc34 | Last Period 3sec 34th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D6D | 0x8D6E | 36205 | 36206 | LAST_CUR_HARM_99_PASSc35 | Last Period 3sec 35th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D6F | 0x8D70 | 36207 | 36208 | LAST_CUR_HARM_99_PASSc36 | Last Period 3sec 36th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D71 | 0x8D72 | 36209 | 36210 | LAST_CUR_HARM_99_PASSc37 | Last Period 3sec 37th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D73 | 0x8D74 | 36211 | 36212 | LAST_CUR_HARM_99_PASSc38 | Last Period 3sec 38th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D75 | 0x8D76 | 36213 | 36214 | LAST_CUR_HARM_99_PASSc39 | Last Period 3sec 39th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D77 | 0x8D78 | 36215 | 36216 | LAST_CUR_HARM_99_PASSc40 | Last Period 3sec 40th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D79 | 0x8D7A | 36217 | 36218 | LAST_CUR_HARM_99_PASSc41 | Last Period 3sec 41st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D7B | 0x8D7C | 36219 | 36220 | LAST_CUR_HARM_99_PASSc42 | Last Period 3sec 42nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D7D | 0x8D7E | 36221 | 36222 | LAST_CUR_HARM_99_PASSc43 | Last Period 3sec 43rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D7F | 0x8D80 | 36223 | 36224 | LAST_CUR_HARM_99_PASSc44 | Last Period 3sec 44th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D81 | 0x8D82 | 36225 | 36226 | LAST_CUR_HARM_99_PASSc45 | Last Period 3sec 45th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D83 | 0x8D84 | 36227 | 36228 | LAST_CUR_HARM_99_PASSc46 | Last Period 3sec 46th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D85 | 0x8D86 | 36229 | 36230 | LAST_CUR_HARM_99_PASSc47 | Last Period 3sec 47th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D87 | 0x8D88 | 36231 | 36232 | LAST_CUR_HARM_99_PASSc48 | Last Period 3sec 48th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D89 | 0x8D8A | 36233 | 36234 | LAST_CUR_HARM_99_PASSc49 | Last Period 3sec 49th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x8D8B | 0x8D8C | 36235 | 36236 | LAST_CUR_HARM_99_PASSc50 | Last Period 3sec 50th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R

## PQ Report 519 Weekly
Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Param Name | Description | Data Type | Reg | RW | Range | Default | Factory Default
PQ Report 519 Weekly Current
0x8E00 | 0x8E00 | 36352 | 36352 | N_VALID | 10min 519 Report Valid Circle Counter | uint16 | 1 | R
0x8E01 | 0x8E01 | 36353 | 36353 | N_THDa | 10min Phase A THD Counter | uint16 | 1 | R
0x8E02 | 0x8E02 | 36354 | 36354 | N_THDb | 10min Phase B THD Counter | uint16 | 1 | R
0x8E03 | 0x8E03 | 36355 | 36355 | N_THDc | 10min Phase C THD Counter | uint16 | 1 | R
0x8E04 | 0x8E05 | 36356 | 36357 | THD_PASSa | 10min Phase A THD Trigger Pass Rate | float | 2 | R
0x8E06 | 0x8E07 | 36358 | 36359 | THD_PASSb | 10min Phase B THD Trigger Pass Rate | float | 2 | R
0x8E08 | 0x8E09 | 36360 | 36361 | THD_PASSc | 10min Phase C THD Trigger Pass Rate | float | 2 | R
0x8E0A | 0x8E0B | 36362 | 36363 | THD_MAXa | 10min Phase A THD Maximum Value | float | 2 | R
0x8E0C | 0x8E0D | 36364 | 36365 | THD_MAXb | 10min Phase B THD Maximum Value | float | 2 | R
0x8E0E | 0x8E0F | 36366 | 36367 | THD_MAXc | 10min Phase C THD Maximum Value | float | 2 | R
0x8E10 | 0x8E11 | 36368 | 36369 | THD_MINa | 10min Phase A THD Minimum Value | float | 2 | R
0x8E12 | 0x8E13 | 36370 | 36371 | THD_MINb | 10min Phase B THD Minimum Value | float | 2 | R
0x8E14 | 0x8E15 | 36372 | 36373 | THD_MINc | 10min Phase C THD Minimum Value | float | 2 | R
0x8E16 | 0x8E17 | 36374 | 36375 | THD_AVGa | 10min Phase A THD Average Value | float | 2 | R
0x8E18 | 0x8E19 | 36376 | 36377 | THD_AVGb | 10min Phase B THD Average Value | float | 2 | R
0x8E1A | 0x8E1B | 36378 | 36379 | THD_AVGc | 10min Phase C THD Average Value | float | 2 | R
0x8E1C | 0x8E1C | 36380 | 36380 | N_VOL_HARMa2 | 10min 2nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E1D | 0x8E1D | 36381 | 36381 | N_VOL_HARMa3 | 10min 3rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E1E | 0x8E1E | 36382 | 36382 | N_VOL_HARMa4 | 10min 4th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E1F | 0x8E1F | 36383 | 36383 | N_VOL_HARMa5 | 10min 5th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E20 | 0x8E20 | 36384 | 36384 | N_VOL_HARMa6 | 10min 6th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E21 | 0x8E21 | 36385 | 36385 | N_VOL_HARMa7 | 10min 7th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E22 | 0x8E22 | 36386 | 36386 | N_VOL_HARMa8 | 10min 8th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E23 | 0x8E23 | 36387 | 36387 | N_VOL_HARMa9 | 10min 9th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E24 | 0x8E24 | 36388 | 36388 | N_VOL_HARMa10 | 10min 10th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E25 | 0x8E25 | 36389 | 36389 | N_VOL_HARMa11 | 10min 11st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E26 | 0x8E26 | 36390 | 36390 | N_VOL_HARMa12 | 10min 12nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E27 | 0x8E27 | 36391 | 36391 | N_VOL_HARMa13 | 10min 13rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E28 | 0x8E28 | 36392 | 36392 | N_VOL_HARMa14 | 10min 14th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E29 | 0x8E29 | 36393 | 36393 | N_VOL_HARMa15 | 10min 15th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E2A | 0x8E2A | 36394 | 36394 | N_VOL_HARMa16 | 10min 16th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E2B | 0x8E2B | 36395 | 36395 | N_VOL_HARMa17 | 10min 17th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E2C | 0x8E2C | 36396 | 36396 | N_VOL_HARMa18 | 10min 18th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E2D | 0x8E2D | 36397 | 36397 | N_VOL_HARMa19 | 10min 19th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E2E | 0x8E2E | 36398 | 36398 | N_VOL_HARMa20 | 10min 20th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E2F | 0x8E2F | 36399 | 36399 | N_VOL_HARMa21 | 10min 21st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E30 | 0x8E30 | 36400 | 36400 | N_VOL_HARMa22 | 10min 22nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E31 | 0x8E31 | 36401 | 36401 | N_VOL_HARMa23 | 10min 23rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E32 | 0x8E32 | 36402 | 36402 | N_VOL_HARMa24 | 10min 24th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E33 | 0x8E33 | 36403 | 36403 | N_VOL_HARMa25 | 10min 25th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E34 | 0x8E34 | 36404 | 36404 | N_VOL_HARMa26 | 10min 26th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E35 | 0x8E35 | 36405 | 36405 | N_VOL_HARMa27 | 10min 27th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E36 | 0x8E36 | 36406 | 36406 | N_VOL_HARMa28 | 10min 28th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E37 | 0x8E37 | 36407 | 36407 | N_VOL_HARMa29 | 10min 29th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E38 | 0x8E38 | 36408 | 36408 | N_VOL_HARMa30 | 10min 30th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E39 | 0x8E39 | 36409 | 36409 | N_VOL_HARMa31 | 10min 31st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E3A | 0x8E3A | 36410 | 36410 | N_VOL_HARMa32 | 10min 32nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E3B | 0x8E3B | 36411 | 36411 | N_VOL_HARMa33 | 10min 33rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E3C | 0x8E3C | 36412 | 36412 | N_VOL_HARMa34 | 10min 34th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E3D | 0x8E3D | 36413 | 36413 | N_VOL_HARMa35 | 10min 35th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E3E | 0x8E3E | 36414 | 36414 | N_VOL_HARMa36 | 10min 36th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E3F | 0x8E3F | 36415 | 36415 | N_VOL_HARMa37 | 10min 37th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E40 | 0x8E40 | 36416 | 36416 | N_VOL_HARMa38 | 10min 38th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E41 | 0x8E41 | 36417 | 36417 | N_VOL_HARMa39 | 10min 39th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E42 | 0x8E42 | 36418 | 36418 | N_VOL_HARMa40 | 10min 40th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E43 | 0x8E43 | 36419 | 36419 | N_VOL_HARMa41 | 10min 41st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E44 | 0x8E44 | 36420 | 36420 | N_VOL_HARMa42 | 10min 42nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E45 | 0x8E45 | 36421 | 36421 | N_VOL_HARMa43 | 10min 43rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E46 | 0x8E46 | 36422 | 36422 | N_VOL_HARMa44 | 10min 44th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E47 | 0x8E47 | 36423 | 36423 | N_VOL_HARMa45 | 10min 45th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E48 | 0x8E48 | 36424 | 36424 | N_VOL_HARMa46 | 10min 46th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E49 | 0x8E49 | 36425 | 36425 | N_VOL_HARMa47 | 10min 47th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E4A | 0x8E4A | 36426 | 36426 | N_VOL_HARMa48 | 10min 48th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E4B | 0x8E4B | 36427 | 36427 | N_VOL_HARMa49 | 10min 49th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E4C | 0x8E4C | 36428 | 36428 | N_VOL_HARMa50 | 10min 50th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x8E4D | 0x8E4D | 36429 | 36429 | N_VOL_HARMb2 | 10min 2nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E4E | 0x8E4E | 36430 | 36430 | N_VOL_HARMb3 | 10min 3rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E4F | 0x8E4F | 36431 | 36431 | N_VOL_HARMb4 | 10min 4th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E50 | 0x8E50 | 36432 | 36432 | N_VOL_HARMb5 | 10min 5th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E51 | 0x8E51 | 36433 | 36433 | N_VOL_HARMb6 | 10min 6th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E52 | 0x8E52 | 36434 | 36434 | N_VOL_HARMb7 | 10min 7th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E53 | 0x8E53 | 36435 | 36435 | N_VOL_HARMb8 | 10min 8th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E54 | 0x8E54 | 36436 | 36436 | N_VOL_HARMb9 | 10min 9th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E55 | 0x8E55 | 36437 | 36437 | N_VOL_HARMb10 | 10min 10th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E56 | 0x8E56 | 36438 | 36438 | N_VOL_HARMb11 | 10min 11st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E57 | 0x8E57 | 36439 | 36439 | N_VOL_HARMb12 | 10min 12nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E58 | 0x8E58 | 36440 | 36440 | N_VOL_HARMb13 | 10min 13rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E59 | 0x8E59 | 36441 | 36441 | N_VOL_HARMb14 | 10min 14th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E5A | 0x8E5A | 36442 | 36442 | N_VOL_HARMb15 | 10min 15th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E5B | 0x8E5B | 36443 | 36443 | N_VOL_HARMb16 | 10min 16th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E5C | 0x8E5C | 36444 | 36444 | N_VOL_HARMb17 | 10min 17th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E5D | 0x8E5D | 36445 | 36445 | N_VOL_HARMb18 | 10min 18th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E5E | 0x8E5E | 36446 | 36446 | N_VOL_HARMb19 | 10min 19th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E5F | 0x8E5F | 36447 | 36447 | N_VOL_HARMb20 | 10min 20th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E60 | 0x8E60 | 36448 | 36448 | N_VOL_HARMb21 | 10min 21st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E61 | 0x8E61 | 36449 | 36449 | N_VOL_HARMb22 | 10min 22nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E62 | 0x8E62 | 36450 | 36450 | N_VOL_HARMb23 | 10min 23rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E63 | 0x8E63 | 36451 | 36451 | N_VOL_HARMb24 | 10min 24th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E64 | 0x8E64 | 36452 | 36452 | N_VOL_HARMb25 | 10min 25th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E65 | 0x8E65 | 36453 | 36453 | N_VOL_HARMb26 | 10min 26th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E66 | 0x8E66 | 36454 | 36454 | N_VOL_HARMb27 | 10min 27th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E67 | 0x8E67 | 36455 | 36455 | N_VOL_HARMb28 | 10min 28th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E68 | 0x8E68 | 36456 | 36456 | N_VOL_HARMb29 | 10min 29th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E69 | 0x8E69 | 36457 | 36457 | N_VOL_HARMb30 | 10min 30th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E6A | 0x8E6A | 36458 | 36458 | N_VOL_HARMb31 | 10min 31st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E6B | 0x8E6B | 36459 | 36459 | N_VOL_HARMb32 | 10min 32nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E6C | 0x8E6C | 36460 | 36460 | N_VOL_HARMb33 | 10min 33rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E6D | 0x8E6D | 36461 | 36461 | N_VOL_HARMb34 | 10min 34th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E6E | 0x8E6E | 36462 | 36462 | N_VOL_HARMb35 | 10min 35th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E6F | 0x8E6F | 36463 | 36463 | N_VOL_HARMb36 | 10min 36th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E70 | 0x8E70 | 36464 | 36464 | N_VOL_HARMb37 | 10min 37th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E71 | 0x8E71 | 36465 | 36465 | N_VOL_HARMb38 | 10min 38th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E72 | 0x8E72 | 36466 | 36466 | N_VOL_HARMb39 | 10min 39th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E73 | 0x8E73 | 36467 | 36467 | N_VOL_HARMb40 | 10min 40th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E74 | 0x8E74 | 36468 | 36468 | N_VOL_HARMb41 | 10min 41st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E75 | 0x8E75 | 36469 | 36469 | N_VOL_HARMb42 | 10min 42nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E76 | 0x8E76 | 36470 | 36470 | N_VOL_HARMb43 | 10min 43rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E77 | 0x8E77 | 36471 | 36471 | N_VOL_HARMb44 | 10min 44th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E78 | 0x8E78 | 36472 | 36472 | N_VOL_HARMb45 | 10min 45th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E79 | 0x8E79 | 36473 | 36473 | N_VOL_HARMb46 | 10min 46th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E7A | 0x8E7A | 36474 | 36474 | N_VOL_HARMb47 | 10min 47th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E7B | 0x8E7B | 36475 | 36475 | N_VOL_HARMb48 | 10min 48th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E7C | 0x8E7C | 36476 | 36476 | N_VOL_HARMb49 | 10min 49th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E7D | 0x8E7D | 36477 | 36477 | N_VOL_HARMb50 | 10min 50th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x8E7E | 0x8E7E | 36478 | 36478 | N_VOL_HARMc2 | 10min 2nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E7F | 0x8E7F | 36479 | 36479 | N_VOL_HARMc3 | 10min 3rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E80 | 0x8E80 | 36480 | 36480 | N_VOL_HARMc4 | 10min 4th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E81 | 0x8E81 | 36481 | 36481 | N_VOL_HARMc5 | 10min 5th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E82 | 0x8E82 | 36482 | 36482 | N_VOL_HARMc6 | 10min 6th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E83 | 0x8E83 | 36483 | 36483 | N_VOL_HARMc7 | 10min 7th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E84 | 0x8E84 | 36484 | 36484 | N_VOL_HARMc8 | 10min 8th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E85 | 0x8E85 | 36485 | 36485 | N_VOL_HARMc9 | 10min 9th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E86 | 0x8E86 | 36486 | 36486 | N_VOL_HARMc10 | 10min 10th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E87 | 0x8E87 | 36487 | 36487 | N_VOL_HARMc11 | 10min 11st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E88 | 0x8E88 | 36488 | 36488 | N_VOL_HARMc12 | 10min 12nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E89 | 0x8E89 | 36489 | 36489 | N_VOL_HARMc13 | 10min 13rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E8A | 0x8E8A | 36490 | 36490 | N_VOL_HARMc14 | 10min 14th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E8B | 0x8E8B | 36491 | 36491 | N_VOL_HARMc15 | 10min 15th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E8C | 0x8E8C | 36492 | 36492 | N_VOL_HARMc16 | 10min 16th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E8D | 0x8E8D | 36493 | 36493 | N_VOL_HARMc17 | 10min 17th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E8E | 0x8E8E | 36494 | 36494 | N_VOL_HARMc18 | 10min 18th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E8F | 0x8E8F | 36495 | 36495 | N_VOL_HARMc19 | 10min 19th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E90 | 0x8E90 | 36496 | 36496 | N_VOL_HARMc20 | 10min 20th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E91 | 0x8E91 | 36497 | 36497 | N_VOL_HARMc21 | 10min 21st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E92 | 0x8E92 | 36498 | 36498 | N_VOL_HARMc22 | 10min 22nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E93 | 0x8E93 | 36499 | 36499 | N_VOL_HARMc23 | 10min 23rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E94 | 0x8E94 | 36500 | 36500 | N_VOL_HARMc24 | 10min 24th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E95 | 0x8E95 | 36501 | 36501 | N_VOL_HARMc25 | 10min 25th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E96 | 0x8E96 | 36502 | 36502 | N_VOL_HARMc26 | 10min 26th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E97 | 0x8E97 | 36503 | 36503 | N_VOL_HARMc27 | 10min 27th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E98 | 0x8E98 | 36504 | 36504 | N_VOL_HARMc28 | 10min 28th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E99 | 0x8E99 | 36505 | 36505 | N_VOL_HARMc29 | 10min 29th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E9A | 0x8E9A | 36506 | 36506 | N_VOL_HARMc30 | 10min 30th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E9B | 0x8E9B | 36507 | 36507 | N_VOL_HARMc31 | 10min 31st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E9C | 0x8E9C | 36508 | 36508 | N_VOL_HARMc32 | 10min 32nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E9D | 0x8E9D | 36509 | 36509 | N_VOL_HARMc33 | 10min 33rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E9E | 0x8E9E | 36510 | 36510 | N_VOL_HARMc34 | 10min 34th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8E9F | 0x8E9F | 36511 | 36511 | N_VOL_HARMc35 | 10min 35th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EA0 | 0x8EA0 | 36512 | 36512 | N_VOL_HARMc36 | 10min 36th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EA1 | 0x8EA1 | 36513 | 36513 | N_VOL_HARMc37 | 10min 37th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EA2 | 0x8EA2 | 36514 | 36514 | N_VOL_HARMc38 | 10min 38th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EA3 | 0x8EA3 | 36515 | 36515 | N_VOL_HARMc39 | 10min 39th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EA4 | 0x8EA4 | 36516 | 36516 | N_VOL_HARMc40 | 10min 40th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EA5 | 0x8EA5 | 36517 | 36517 | N_VOL_HARMc41 | 10min 41st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EA6 | 0x8EA6 | 36518 | 36518 | N_VOL_HARMc42 | 10min 42nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EA7 | 0x8EA7 | 36519 | 36519 | N_VOL_HARMc43 | 10min 43rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EA8 | 0x8EA8 | 36520 | 36520 | N_VOL_HARMc44 | 10min 44th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EA9 | 0x8EA9 | 36521 | 36521 | N_VOL_HARMc45 | 10min 45th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EAA | 0x8EAA | 36522 | 36522 | N_VOL_HARMc46 | 10min 46th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EAB | 0x8EAB | 36523 | 36523 | N_VOL_HARMc47 | 10min 47th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EAC | 0x8EAC | 36524 | 36524 | N_VOL_HARMc48 | 10min 48th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EAD | 0x8EAD | 36525 | 36525 | N_VOL_HARMc49 | 10min 49th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EAE | 0x8EAE | 36526 | 36526 | N_VOL_HARMc50 | 10min 50th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x8EAF | 0x8EB0 | 36527 | 36528 | VOL_HARM_PASSa2 | 10min 2nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EB1 | 0x8EB2 | 36529 | 36530 | VOL_HARM_PASSa3 | 10min 3rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EB3 | 0x8EB4 | 36531 | 36532 | VOL_HARM_PASSa4 | 10min 4th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EB5 | 0x8EB6 | 36533 | 36534 | VOL_HARM_PASSa5 | 10min 5th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EB7 | 0x8EB8 | 36535 | 36536 | VOL_HARM_PASSa6 | 10min 6th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EB9 | 0x8EBA | 36537 | 36538 | VOL_HARM_PASSa7 | 10min 7th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EBB | 0x8EBC | 36539 | 36540 | VOL_HARM_PASSa8 | 10min 8th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EBD | 0x8EBE | 36541 | 36542 | VOL_HARM_PASSa9 | 10min 9th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EBF | 0x8EC0 | 36543 | 36544 | VOL_HARM_PASSa10 | 10min 10th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EC1 | 0x8EC2 | 36545 | 36546 | VOL_HARM_PASSa11 | 10min 11st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EC3 | 0x8EC4 | 36547 | 36548 | VOL_HARM_PASSa12 | 10min 12nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EC5 | 0x8EC6 | 36549 | 36550 | VOL_HARM_PASSa13 | 10min 13rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EC7 | 0x8EC8 | 36551 | 36552 | VOL_HARM_PASSa14 | 10min 14th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EC9 | 0x8ECA | 36553 | 36554 | VOL_HARM_PASSa15 | 10min 15th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8ECB | 0x8ECC | 36555 | 36556 | VOL_HARM_PASSa16 | 10min 16th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8ECD | 0x8ECE | 36557 | 36558 | VOL_HARM_PASSa17 | 10min 17th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8ECF | 0x8ED0 | 36559 | 36560 | VOL_HARM_PASSa18 | 10min 18th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8ED1 | 0x8ED2 | 36561 | 36562 | VOL_HARM_PASSa19 | 10min 19th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8ED3 | 0x8ED4 | 36563 | 36564 | VOL_HARM_PASSa20 | 10min 20th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8ED5 | 0x8ED6 | 36565 | 36566 | VOL_HARM_PASSa21 | 10min 21st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8ED7 | 0x8ED8 | 36567 | 36568 | VOL_HARM_PASSa22 | 10min 22nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8ED9 | 0x8EDA | 36569 | 36570 | VOL_HARM_PASSa23 | 10min 23rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EDB | 0x8EDC | 36571 | 36572 | VOL_HARM_PASSa24 | 10min 24th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EDD | 0x8EDE | 36573 | 36574 | VOL_HARM_PASSa25 | 10min 25th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EDF | 0x8EE0 | 36575 | 36576 | VOL_HARM_PASSa26 | 10min 26th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EE1 | 0x8EE2 | 36577 | 36578 | VOL_HARM_PASSa27 | 10min 27th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EE3 | 0x8EE4 | 36579 | 36580 | VOL_HARM_PASSa28 | 10min 28th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EE5 | 0x8EE6 | 36581 | 36582 | VOL_HARM_PASSa29 | 10min 29th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EE7 | 0x8EE8 | 36583 | 36584 | VOL_HARM_PASSa30 | 10min 30th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EE9 | 0x8EEA | 36585 | 36586 | VOL_HARM_PASSa31 | 10min 31st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EEB | 0x8EEC | 36587 | 36588 | VOL_HARM_PASSa32 | 10min 32nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EED | 0x8EEE | 36589 | 36590 | VOL_HARM_PASSa33 | 10min 33rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EEF | 0x8EF0 | 36591 | 36592 | VOL_HARM_PASSa34 | 10min 34th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EF1 | 0x8EF2 | 36593 | 36594 | VOL_HARM_PASSa35 | 10min 35th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EF3 | 0x8EF4 | 36595 | 36596 | VOL_HARM_PASSa36 | 10min 36th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EF5 | 0x8EF6 | 36597 | 36598 | VOL_HARM_PASSa37 | 10min 37th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EF7 | 0x8EF8 | 36599 | 36600 | VOL_HARM_PASSa38 | 10min 38th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EF9 | 0x8EFA | 36601 | 36602 | VOL_HARM_PASSa39 | 10min 39th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EFB | 0x8EFC | 36603 | 36604 | VOL_HARM_PASSa40 | 10min 40th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EFD | 0x8EFE | 36605 | 36606 | VOL_HARM_PASSa41 | 10min 41st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8EFF | 0x8F00 | 36607 | 36608 | VOL_HARM_PASSa42 | 10min 42nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8F01 | 0x8F02 | 36609 | 36610 | VOL_HARM_PASSa43 | 10min 43rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8F03 | 0x8F04 | 36611 | 36612 | VOL_HARM_PASSa44 | 10min 44th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8F05 | 0x8F06 | 36613 | 36614 | VOL_HARM_PASSa45 | 10min 45th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8F07 | 0x8F08 | 36615 | 36616 | VOL_HARM_PASSa46 | 10min 46th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8F09 | 0x8F0A | 36617 | 36618 | VOL_HARM_PASSa47 | 10min 47th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8F0B | 0x8F0C | 36619 | 36620 | VOL_HARM_PASSa48 | 10min 48th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8F0D | 0x8F0E | 36621 | 36622 | VOL_HARM_PASSa49 | 10min 49th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8F0F | 0x8F10 | 36623 | 36624 | VOL_HARM_PASSa50 | 10min 50th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x8F11 | 0x8F12 | 36625 | 36626 | VOL_HARM_PASSb2 | 10min 2nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F13 | 0x8F14 | 36627 | 36628 | VOL_HARM_PASSb3 | 10min 3rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F15 | 0x8F16 | 36629 | 36630 | VOL_HARM_PASSb4 | 10min 4th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F17 | 0x8F18 | 36631 | 36632 | VOL_HARM_PASSb5 | 10min 5th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F19 | 0x8F1A | 36633 | 36634 | VOL_HARM_PASSb6 | 10min 6th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F1B | 0x8F1C | 36635 | 36636 | VOL_HARM_PASSb7 | 10min 7th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F1D | 0x8F1E | 36637 | 36638 | VOL_HARM_PASSb8 | 10min 8th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F1F | 0x8F20 | 36639 | 36640 | VOL_HARM_PASSb9 | 10min 9th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F21 | 0x8F22 | 36641 | 36642 | VOL_HARM_PASSb10 | 10min 10th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F23 | 0x8F24 | 36643 | 36644 | VOL_HARM_PASSb11 | 10min 11st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F25 | 0x8F26 | 36645 | 36646 | VOL_HARM_PASSb12 | 10min 12nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F27 | 0x8F28 | 36647 | 36648 | VOL_HARM_PASSb13 | 10min 13rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F29 | 0x8F2A | 36649 | 36650 | VOL_HARM_PASSb14 | 10min 14th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F2B | 0x8F2C | 36651 | 36652 | VOL_HARM_PASSb15 | 10min 15th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F2D | 0x8F2E | 36653 | 36654 | VOL_HARM_PASSb16 | 10min 16th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F2F | 0x8F30 | 36655 | 36656 | VOL_HARM_PASSb17 | 10min 17th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F31 | 0x8F32 | 36657 | 36658 | VOL_HARM_PASSb18 | 10min 18th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F33 | 0x8F34 | 36659 | 36660 | VOL_HARM_PASSb19 | 10min 19th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F35 | 0x8F36 | 36661 | 36662 | VOL_HARM_PASSb20 | 10min 20th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F37 | 0x8F38 | 36663 | 36664 | VOL_HARM_PASSb21 | 10min 21st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F39 | 0x8F3A | 36665 | 36666 | VOL_HARM_PASSb22 | 10min 22nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F3B | 0x8F3C | 36667 | 36668 | VOL_HARM_PASSb23 | 10min 23rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F3D | 0x8F3E | 36669 | 36670 | VOL_HARM_PASSb24 | 10min 24th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F3F | 0x8F40 | 36671 | 36672 | VOL_HARM_PASSb25 | 10min 25th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F41 | 0x8F42 | 36673 | 36674 | VOL_HARM_PASSb26 | 10min 26th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F43 | 0x8F44 | 36675 | 36676 | VOL_HARM_PASSb27 | 10min 27th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F45 | 0x8F46 | 36677 | 36678 | VOL_HARM_PASSb28 | 10min 28th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F47 | 0x8F48 | 36679 | 36680 | VOL_HARM_PASSb29 | 10min 29th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F49 | 0x8F4A | 36681 | 36682 | VOL_HARM_PASSb30 | 10min 30th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F4B | 0x8F4C | 36683 | 36684 | VOL_HARM_PASSb31 | 10min 31st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F4D | 0x8F4E | 36685 | 36686 | VOL_HARM_PASSb32 | 10min 32nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F4F | 0x8F50 | 36687 | 36688 | VOL_HARM_PASSb33 | 10min 33rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F51 | 0x8F52 | 36689 | 36690 | VOL_HARM_PASSb34 | 10min 34th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F53 | 0x8F54 | 36691 | 36692 | VOL_HARM_PASSb35 | 10min 35th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F55 | 0x8F56 | 36693 | 36694 | VOL_HARM_PASSb36 | 10min 36th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F57 | 0x8F58 | 36695 | 36696 | VOL_HARM_PASSb37 | 10min 37th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F59 | 0x8F5A | 36697 | 36698 | VOL_HARM_PASSb38 | 10min 38th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F5B | 0x8F5C | 36699 | 36700 | VOL_HARM_PASSb39 | 10min 39th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F5D | 0x8F5E | 36701 | 36702 | VOL_HARM_PASSb40 | 10min 40th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F5F | 0x8F60 | 36703 | 36704 | VOL_HARM_PASSb41 | 10min 41st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F61 | 0x8F62 | 36705 | 36706 | VOL_HARM_PASSb42 | 10min 42nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F63 | 0x8F64 | 36707 | 36708 | VOL_HARM_PASSb43 | 10min 43rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F65 | 0x8F66 | 36709 | 36710 | VOL_HARM_PASSb44 | 10min 44th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F67 | 0x8F68 | 36711 | 36712 | VOL_HARM_PASSb45 | 10min 45th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F69 | 0x8F6A | 36713 | 36714 | VOL_HARM_PASSb46 | 10min 46th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F6B | 0x8F6C | 36715 | 36716 | VOL_HARM_PASSb47 | 10min 47th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F6D | 0x8F6E | 36717 | 36718 | VOL_HARM_PASSb48 | 10min 48th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F6F | 0x8F70 | 36719 | 36720 | VOL_HARM_PASSb49 | 10min 49th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F71 | 0x8F72 | 36721 | 36722 | VOL_HARM_PASSb50 | 10min 50th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x8F73 | 0x8F74 | 36723 | 36724 | VOL_HARM_PASSc2 | 10min 2nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F75 | 0x8F76 | 36725 | 36726 | VOL_HARM_PASSc3 | 10min 3rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F77 | 0x8F78 | 36727 | 36728 | VOL_HARM_PASSc4 | 10min 4th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F79 | 0x8F7A | 36729 | 36730 | VOL_HARM_PASSc5 | 10min 5th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F7B | 0x8F7C | 36731 | 36732 | VOL_HARM_PASSc6 | 10min 6th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F7D | 0x8F7E | 36733 | 36734 | VOL_HARM_PASSc7 | 10min 7th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F7F | 0x8F80 | 36735 | 36736 | VOL_HARM_PASSc8 | 10min 8th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F81 | 0x8F82 | 36737 | 36738 | VOL_HARM_PASSc9 | 10min 9th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F83 | 0x8F84 | 36739 | 36740 | VOL_HARM_PASSc10 | 10min 10th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F85 | 0x8F86 | 36741 | 36742 | VOL_HARM_PASSc11 | 10min 11st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F87 | 0x8F88 | 36743 | 36744 | VOL_HARM_PASSc12 | 10min 12nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F89 | 0x8F8A | 36745 | 36746 | VOL_HARM_PASSc13 | 10min 13rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F8B | 0x8F8C | 36747 | 36748 | VOL_HARM_PASSc14 | 10min 14th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F8D | 0x8F8E | 36749 | 36750 | VOL_HARM_PASSc15 | 10min 15th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F8F | 0x8F90 | 36751 | 36752 | VOL_HARM_PASSc16 | 10min 16th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F91 | 0x8F92 | 36753 | 36754 | VOL_HARM_PASSc17 | 10min 17th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F93 | 0x8F94 | 36755 | 36756 | VOL_HARM_PASSc18 | 10min 18th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F95 | 0x8F96 | 36757 | 36758 | VOL_HARM_PASSc19 | 10min 19th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F97 | 0x8F98 | 36759 | 36760 | VOL_HARM_PASSc20 | 10min 20th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F99 | 0x8F9A | 36761 | 36762 | VOL_HARM_PASSc21 | 10min 21st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F9B | 0x8F9C | 36763 | 36764 | VOL_HARM_PASSc22 | 10min 22nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F9D | 0x8F9E | 36765 | 36766 | VOL_HARM_PASSc23 | 10min 23rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8F9F | 0x8FA0 | 36767 | 36768 | VOL_HARM_PASSc24 | 10min 24th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FA1 | 0x8FA2 | 36769 | 36770 | VOL_HARM_PASSc25 | 10min 25th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FA3 | 0x8FA4 | 36771 | 36772 | VOL_HARM_PASSc26 | 10min 26th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FA5 | 0x8FA6 | 36773 | 36774 | VOL_HARM_PASSc27 | 10min 27th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FA7 | 0x8FA8 | 36775 | 36776 | VOL_HARM_PASSc28 | 10min 28th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FA9 | 0x8FAA | 36777 | 36778 | VOL_HARM_PASSc29 | 10min 29th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FAB | 0x8FAC | 36779 | 36780 | VOL_HARM_PASSc30 | 10min 30th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FAD | 0x8FAE | 36781 | 36782 | VOL_HARM_PASSc31 | 10min 31st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FAF | 0x8FB0 | 36783 | 36784 | VOL_HARM_PASSc32 | 10min 32nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FB1 | 0x8FB2 | 36785 | 36786 | VOL_HARM_PASSc33 | 10min 33rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FB3 | 0x8FB4 | 36787 | 36788 | VOL_HARM_PASSc34 | 10min 34th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FB5 | 0x8FB6 | 36789 | 36790 | VOL_HARM_PASSc35 | 10min 35th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FB7 | 0x8FB8 | 36791 | 36792 | VOL_HARM_PASSc36 | 10min 36th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FB9 | 0x8FBA | 36793 | 36794 | VOL_HARM_PASSc37 | 10min 37th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FBB | 0x8FBC | 36795 | 36796 | VOL_HARM_PASSc38 | 10min 38th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FBD | 0x8FBE | 36797 | 36798 | VOL_HARM_PASSc39 | 10min 39th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FBF | 0x8FC0 | 36799 | 36800 | VOL_HARM_PASSc40 | 10min 40th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FC1 | 0x8FC2 | 36801 | 36802 | VOL_HARM_PASSc41 | 10min 41st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FC3 | 0x8FC4 | 36803 | 36804 | VOL_HARM_PASSc42 | 10min 42nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FC5 | 0x8FC6 | 36805 | 36806 | VOL_HARM_PASSc43 | 10min 43rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FC7 | 0x8FC8 | 36807 | 36808 | VOL_HARM_PASSc44 | 10min 44th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FC9 | 0x8FCA | 36809 | 36810 | VOL_HARM_PASSc45 | 10min 45th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FCB | 0x8FCC | 36811 | 36812 | VOL_HARM_PASSc46 | 10min 46th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FCD | 0x8FCE | 36813 | 36814 | VOL_HARM_PASSc47 | 10min 47th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FCF | 0x8FD0 | 36815 | 36816 | VOL_HARM_PASSc48 | 10min 48th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FD1 | 0x8FD2 | 36817 | 36818 | VOL_HARM_PASSc49 | 10min 49th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FD3 | 0x8FD4 | 36819 | 36820 | VOL_HARM_PASSc50 | 10min 50th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x8FD5 | 0x8FD6 | 36821 | 36822 | VOL_HARM_MAXa2 | 10min 2nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FD7 | 0x8FD8 | 36823 | 36824 | VOL_HARM_MAXa3 | 10min 3rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FD9 | 0x8FDA | 36825 | 36826 | VOL_HARM_MAXa4 | 10min 4th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FDB | 0x8FDC | 36827 | 36828 | VOL_HARM_MAXa5 | 10min 5th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FDD | 0x8FDE | 36829 | 36830 | VOL_HARM_MAXa6 | 10min 6th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FDF | 0x8FE0 | 36831 | 36832 | VOL_HARM_MAXa7 | 10min 7th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FE1 | 0x8FE2 | 36833 | 36834 | VOL_HARM_MAXa8 | 10min 8th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FE3 | 0x8FE4 | 36835 | 36836 | VOL_HARM_MAXa9 | 10min 9th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FE5 | 0x8FE6 | 36837 | 36838 | VOL_HARM_MAXa10 | 10min 10th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FE7 | 0x8FE8 | 36839 | 36840 | VOL_HARM_MAXa11 | 10min 11st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FE9 | 0x8FEA | 36841 | 36842 | VOL_HARM_MAXa12 | 10min 12nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FEB | 0x8FEC | 36843 | 36844 | VOL_HARM_MAXa13 | 10min 13rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FED | 0x8FEE | 36845 | 36846 | VOL_HARM_MAXa14 | 10min 14th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FEF | 0x8FF0 | 36847 | 36848 | VOL_HARM_MAXa15 | 10min 15th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FF1 | 0x8FF2 | 36849 | 36850 | VOL_HARM_MAXa16 | 10min 16th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FF3 | 0x8FF4 | 36851 | 36852 | VOL_HARM_MAXa17 | 10min 17th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FF5 | 0x8FF6 | 36853 | 36854 | VOL_HARM_MAXa18 | 10min 18th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FF7 | 0x8FF8 | 36855 | 36856 | VOL_HARM_MAXa19 | 10min 19th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FF9 | 0x8FFA | 36857 | 36858 | VOL_HARM_MAXa20 | 10min 20th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FFB | 0x8FFC | 36859 | 36860 | VOL_HARM_MAXa21 | 10min 21st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FFD | 0x8FFE | 36861 | 36862 | VOL_HARM_MAXa22 | 10min 22nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x8FFF | 0x9000 | 36863 | 36864 | VOL_HARM_MAXa23 | 10min 23rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9001 | 0x9002 | 36865 | 36866 | VOL_HARM_MAXa24 | 10min 24th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9003 | 0x9004 | 36867 | 36868 | VOL_HARM_MAXa25 | 10min 25th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9005 | 0x9006 | 36869 | 36870 | VOL_HARM_MAXa26 | 10min 26th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9007 | 0x9008 | 36871 | 36872 | VOL_HARM_MAXa27 | 10min 27th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9009 | 0x900A | 36873 | 36874 | VOL_HARM_MAXa28 | 10min 28th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x900B | 0x900C | 36875 | 36876 | VOL_HARM_MAXa29 | 10min 29th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x900D | 0x900E | 36877 | 36878 | VOL_HARM_MAXa30 | 10min 30th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x900F | 0x9010 | 36879 | 36880 | VOL_HARM_MAXa31 | 10min 31st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9011 | 0x9012 | 36881 | 36882 | VOL_HARM_MAXa32 | 10min 32nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9013 | 0x9014 | 36883 | 36884 | VOL_HARM_MAXa33 | 10min 33rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9015 | 0x9016 | 36885 | 36886 | VOL_HARM_MAXa34 | 10min 34th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9017 | 0x9018 | 36887 | 36888 | VOL_HARM_MAXa35 | 10min 35th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9019 | 0x901A | 36889 | 36890 | VOL_HARM_MAXa36 | 10min 36th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x901B | 0x901C | 36891 | 36892 | VOL_HARM_MAXa37 | 10min 37th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x901D | 0x901E | 36893 | 36894 | VOL_HARM_MAXa38 | 10min 38th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x901F | 0x9020 | 36895 | 36896 | VOL_HARM_MAXa39 | 10min 39th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9021 | 0x9022 | 36897 | 36898 | VOL_HARM_MAXa40 | 10min 40th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9023 | 0x9024 | 36899 | 36900 | VOL_HARM_MAXa41 | 10min 41st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9025 | 0x9026 | 36901 | 36902 | VOL_HARM_MAXa42 | 10min 42nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9027 | 0x9028 | 36903 | 36904 | VOL_HARM_MAXa43 | 10min 43rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9029 | 0x902A | 36905 | 36906 | VOL_HARM_MAXa44 | 10min 44th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x902B | 0x902C | 36907 | 36908 | VOL_HARM_MAXa45 | 10min 45th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x902D | 0x902E | 36909 | 36910 | VOL_HARM_MAXa46 | 10min 46th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x902F | 0x9030 | 36911 | 36912 | VOL_HARM_MAXa47 | 10min 47th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9031 | 0x9032 | 36913 | 36914 | VOL_HARM_MAXa48 | 10min 48th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9033 | 0x9034 | 36915 | 36916 | VOL_HARM_MAXa49 | 10min 49th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9035 | 0x9036 | 36917 | 36918 | VOL_HARM_MAXa50 | 10min 50th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9037 | 0x9038 | 36919 | 36920 | VOL_HARM_MAXb2 | 10min 2nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9039 | 0x903A | 36921 | 36922 | VOL_HARM_MAXb3 | 10min 3rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x903B | 0x903C | 36923 | 36924 | VOL_HARM_MAXb4 | 10min 4th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x903D | 0x903E | 36925 | 36926 | VOL_HARM_MAXb5 | 10min 5th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x903F | 0x9040 | 36927 | 36928 | VOL_HARM_MAXb6 | 10min 6th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9041 | 0x9042 | 36929 | 36930 | VOL_HARM_MAXb7 | 10min 7th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9043 | 0x9044 | 36931 | 36932 | VOL_HARM_MAXb8 | 10min 8th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9045 | 0x9046 | 36933 | 36934 | VOL_HARM_MAXb9 | 10min 9th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9047 | 0x9048 | 36935 | 36936 | VOL_HARM_MAXb10 | 10min 10th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9049 | 0x904A | 36937 | 36938 | VOL_HARM_MAXb11 | 10min 11st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x904B | 0x904C | 36939 | 36940 | VOL_HARM_MAXb12 | 10min 12nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x904D | 0x904E | 36941 | 36942 | VOL_HARM_MAXb13 | 10min 13rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x904F | 0x9050 | 36943 | 36944 | VOL_HARM_MAXb14 | 10min 14th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9051 | 0x9052 | 36945 | 36946 | VOL_HARM_MAXb15 | 10min 15th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9053 | 0x9054 | 36947 | 36948 | VOL_HARM_MAXb16 | 10min 16th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9055 | 0x9056 | 36949 | 36950 | VOL_HARM_MAXb17 | 10min 17th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9057 | 0x9058 | 36951 | 36952 | VOL_HARM_MAXb18 | 10min 18th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9059 | 0x905A | 36953 | 36954 | VOL_HARM_MAXb19 | 10min 19th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x905B | 0x905C | 36955 | 36956 | VOL_HARM_MAXb20 | 10min 20th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x905D | 0x905E | 36957 | 36958 | VOL_HARM_MAXb21 | 10min 21st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x905F | 0x9060 | 36959 | 36960 | VOL_HARM_MAXb22 | 10min 22nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9061 | 0x9062 | 36961 | 36962 | VOL_HARM_MAXb23 | 10min 23rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9063 | 0x9064 | 36963 | 36964 | VOL_HARM_MAXb24 | 10min 24th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9065 | 0x9066 | 36965 | 36966 | VOL_HARM_MAXb25 | 10min 25th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9067 | 0x9068 | 36967 | 36968 | VOL_HARM_MAXb26 | 10min 26th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9069 | 0x906A | 36969 | 36970 | VOL_HARM_MAXb27 | 10min 27th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x906B | 0x906C | 36971 | 36972 | VOL_HARM_MAXb28 | 10min 28th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x906D | 0x906E | 36973 | 36974 | VOL_HARM_MAXb29 | 10min 29th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x906F | 0x9070 | 36975 | 36976 | VOL_HARM_MAXb30 | 10min 30th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9071 | 0x9072 | 36977 | 36978 | VOL_HARM_MAXb31 | 10min 31st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9073 | 0x9074 | 36979 | 36980 | VOL_HARM_MAXb32 | 10min 32nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9075 | 0x9076 | 36981 | 36982 | VOL_HARM_MAXb33 | 10min 33rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9077 | 0x9078 | 36983 | 36984 | VOL_HARM_MAXb34 | 10min 34th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9079 | 0x907A | 36985 | 36986 | VOL_HARM_MAXb35 | 10min 35th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x907B | 0x907C | 36987 | 36988 | VOL_HARM_MAXb36 | 10min 36th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x907D | 0x907E | 36989 | 36990 | VOL_HARM_MAXb37 | 10min 37th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x907F | 0x9080 | 36991 | 36992 | VOL_HARM_MAXb38 | 10min 38th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9081 | 0x9082 | 36993 | 36994 | VOL_HARM_MAXb39 | 10min 39th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9083 | 0x9084 | 36995 | 36996 | VOL_HARM_MAXb40 | 10min 40th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9085 | 0x9086 | 36997 | 36998 | VOL_HARM_MAXb41 | 10min 41st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9087 | 0x9088 | 36999 | 37000 | VOL_HARM_MAXb42 | 10min 42nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9089 | 0x908A | 37001 | 37002 | VOL_HARM_MAXb43 | 10min 43rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x908B | 0x908C | 37003 | 37004 | VOL_HARM_MAXb44 | 10min 44th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x908D | 0x908E | 37005 | 37006 | VOL_HARM_MAXb45 | 10min 45th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x908F | 0x9090 | 37007 | 37008 | VOL_HARM_MAXb46 | 10min 46th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9091 | 0x9092 | 37009 | 37010 | VOL_HARM_MAXb47 | 10min 47th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9093 | 0x9094 | 37011 | 37012 | VOL_HARM_MAXb48 | 10min 48th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9095 | 0x9096 | 37013 | 37014 | VOL_HARM_MAXb49 | 10min 49th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9097 | 0x9098 | 37015 | 37016 | VOL_HARM_MAXb50 | 10min 50th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9099 | 0x909A | 37017 | 37018 | VOL_HARM_MAXc2 | 10min 2nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x909B | 0x909C | 37019 | 37020 | VOL_HARM_MAXc3 | 10min 3rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x909D | 0x909E | 37021 | 37022 | VOL_HARM_MAXc4 | 10min 4th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x909F | 0x90A0 | 37023 | 37024 | VOL_HARM_MAXc5 | 10min 5th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90A1 | 0x90A2 | 37025 | 37026 | VOL_HARM_MAXc6 | 10min 6th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90A3 | 0x90A4 | 37027 | 37028 | VOL_HARM_MAXc7 | 10min 7th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90A5 | 0x90A6 | 37029 | 37030 | VOL_HARM_MAXc8 | 10min 8th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90A7 | 0x90A8 | 37031 | 37032 | VOL_HARM_MAXc9 | 10min 9th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90A9 | 0x90AA | 37033 | 37034 | VOL_HARM_MAXc10 | 10min 10th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90AB | 0x90AC | 37035 | 37036 | VOL_HARM_MAXc11 | 10min 11st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90AD | 0x90AE | 37037 | 37038 | VOL_HARM_MAXc12 | 10min 12nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90AF | 0x90B0 | 37039 | 37040 | VOL_HARM_MAXc13 | 10min 13rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90B1 | 0x90B2 | 37041 | 37042 | VOL_HARM_MAXc14 | 10min 14th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90B3 | 0x90B4 | 37043 | 37044 | VOL_HARM_MAXc15 | 10min 15th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90B5 | 0x90B6 | 37045 | 37046 | VOL_HARM_MAXc16 | 10min 16th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90B7 | 0x90B8 | 37047 | 37048 | VOL_HARM_MAXc17 | 10min 17th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90B9 | 0x90BA | 37049 | 37050 | VOL_HARM_MAXc18 | 10min 18th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90BB | 0x90BC | 37051 | 37052 | VOL_HARM_MAXc19 | 10min 19th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90BD | 0x90BE | 37053 | 37054 | VOL_HARM_MAXc20 | 10min 20th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90BF | 0x90C0 | 37055 | 37056 | VOL_HARM_MAXc21 | 10min 21st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90C1 | 0x90C2 | 37057 | 37058 | VOL_HARM_MAXc22 | 10min 22nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90C3 | 0x90C4 | 37059 | 37060 | VOL_HARM_MAXc23 | 10min 23rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90C5 | 0x90C6 | 37061 | 37062 | VOL_HARM_MAXc24 | 10min 24th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90C7 | 0x90C8 | 37063 | 37064 | VOL_HARM_MAXc25 | 10min 25th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90C9 | 0x90CA | 37065 | 37066 | VOL_HARM_MAXc26 | 10min 26th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90CB | 0x90CC | 37067 | 37068 | VOL_HARM_MAXc27 | 10min 27th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90CD | 0x90CE | 37069 | 37070 | VOL_HARM_MAXc28 | 10min 28th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90CF | 0x90D0 | 37071 | 37072 | VOL_HARM_MAXc29 | 10min 29th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90D1 | 0x90D2 | 37073 | 37074 | VOL_HARM_MAXc30 | 10min 30th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90D3 | 0x90D4 | 37075 | 37076 | VOL_HARM_MAXc31 | 10min 31st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90D5 | 0x90D6 | 37077 | 37078 | VOL_HARM_MAXc32 | 10min 32nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90D7 | 0x90D8 | 37079 | 37080 | VOL_HARM_MAXc33 | 10min 33rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90D9 | 0x90DA | 37081 | 37082 | VOL_HARM_MAXc34 | 10min 34th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90DB | 0x90DC | 37083 | 37084 | VOL_HARM_MAXc35 | 10min 35th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90DD | 0x90DE | 37085 | 37086 | VOL_HARM_MAXc36 | 10min 36th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90DF | 0x90E0 | 37087 | 37088 | VOL_HARM_MAXc37 | 10min 37th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90E1 | 0x90E2 | 37089 | 37090 | VOL_HARM_MAXc38 | 10min 38th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90E3 | 0x90E4 | 37091 | 37092 | VOL_HARM_MAXc39 | 10min 39th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90E5 | 0x90E6 | 37093 | 37094 | VOL_HARM_MAXc40 | 10min 40th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90E7 | 0x90E8 | 37095 | 37096 | VOL_HARM_MAXc41 | 10min 41st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90E9 | 0x90EA | 37097 | 37098 | VOL_HARM_MAXc42 | 10min 42nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90EB | 0x90EC | 37099 | 37100 | VOL_HARM_MAXc43 | 10min 43rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90ED | 0x90EE | 37101 | 37102 | VOL_HARM_MAXc44 | 10min 44th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90EF | 0x90F0 | 37103 | 37104 | VOL_HARM_MAXc45 | 10min 45th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90F1 | 0x90F2 | 37105 | 37106 | VOL_HARM_MAXc46 | 10min 46th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90F3 | 0x90F4 | 37107 | 37108 | VOL_HARM_MAXc47 | 10min 47th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90F5 | 0x90F6 | 37109 | 37110 | VOL_HARM_MAXc48 | 10min 48th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90F7 | 0x90F8 | 37111 | 37112 | VOL_HARM_MAXc49 | 10min 49th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90F9 | 0x90FA | 37113 | 37114 | VOL_HARM_MAXc50 | 10min 50th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x90FB | 0x90FC | 37115 | 37116 | VOL_HARM_MINa2 | 10min 2nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x90FD | 0x90FE | 37117 | 37118 | VOL_HARM_MINa3 | 10min 3rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x90FF | 0x9100 | 37119 | 37120 | VOL_HARM_MINa4 | 10min 4th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9101 | 0x9102 | 37121 | 37122 | VOL_HARM_MINa5 | 10min 5th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9103 | 0x9104 | 37123 | 37124 | VOL_HARM_MINa6 | 10min 6th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9105 | 0x9106 | 37125 | 37126 | VOL_HARM_MINa7 | 10min 7th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9107 | 0x9108 | 37127 | 37128 | VOL_HARM_MINa8 | 10min 8th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9109 | 0x910A | 37129 | 37130 | VOL_HARM_MINa9 | 10min 9th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x910B | 0x910C | 37131 | 37132 | VOL_HARM_MINa10 | 10min 10th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x910D | 0x910E | 37133 | 37134 | VOL_HARM_MINa11 | 10min 11st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x910F | 0x9110 | 37135 | 37136 | VOL_HARM_MINa12 | 10min 12nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9111 | 0x9112 | 37137 | 37138 | VOL_HARM_MINa13 | 10min 13rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9113 | 0x9114 | 37139 | 37140 | VOL_HARM_MINa14 | 10min 14th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9115 | 0x9116 | 37141 | 37142 | VOL_HARM_MINa15 | 10min 15th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9117 | 0x9118 | 37143 | 37144 | VOL_HARM_MINa16 | 10min 16th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9119 | 0x911A | 37145 | 37146 | VOL_HARM_MINa17 | 10min 17th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x911B | 0x911C | 37147 | 37148 | VOL_HARM_MINa18 | 10min 18th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x911D | 0x911E | 37149 | 37150 | VOL_HARM_MINa19 | 10min 19th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x911F | 0x9120 | 37151 | 37152 | VOL_HARM_MINa20 | 10min 20th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9121 | 0x9122 | 37153 | 37154 | VOL_HARM_MINa21 | 10min 21st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9123 | 0x9124 | 37155 | 37156 | VOL_HARM_MINa22 | 10min 22nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9125 | 0x9126 | 37157 | 37158 | VOL_HARM_MINa23 | 10min 23rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9127 | 0x9128 | 37159 | 37160 | VOL_HARM_MINa24 | 10min 24th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9129 | 0x912A | 37161 | 37162 | VOL_HARM_MINa25 | 10min 25th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x912B | 0x912C | 37163 | 37164 | VOL_HARM_MINa26 | 10min 26th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x912D | 0x912E | 37165 | 37166 | VOL_HARM_MINa27 | 10min 27th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x912F | 0x9130 | 37167 | 37168 | VOL_HARM_MINa28 | 10min 28th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9131 | 0x9132 | 37169 | 37170 | VOL_HARM_MINa29 | 10min 29th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9133 | 0x9134 | 37171 | 37172 | VOL_HARM_MINa30 | 10min 30th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9135 | 0x9136 | 37173 | 37174 | VOL_HARM_MINa31 | 10min 31st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9137 | 0x9138 | 37175 | 37176 | VOL_HARM_MINa32 | 10min 32nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9139 | 0x913A | 37177 | 37178 | VOL_HARM_MINa33 | 10min 33rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x913B | 0x913C | 37179 | 37180 | VOL_HARM_MINa34 | 10min 34th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x913D | 0x913E | 37181 | 37182 | VOL_HARM_MINa35 | 10min 35th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x913F | 0x9140 | 37183 | 37184 | VOL_HARM_MINa36 | 10min 36th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9141 | 0x9142 | 37185 | 37186 | VOL_HARM_MINa37 | 10min 37th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9143 | 0x9144 | 37187 | 37188 | VOL_HARM_MINa38 | 10min 38th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9145 | 0x9146 | 37189 | 37190 | VOL_HARM_MINa39 | 10min 39th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9147 | 0x9148 | 37191 | 37192 | VOL_HARM_MINa40 | 10min 40th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9149 | 0x914A | 37193 | 37194 | VOL_HARM_MINa41 | 10min 41st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x914B | 0x914C | 37195 | 37196 | VOL_HARM_MINa42 | 10min 42nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x914D | 0x914E | 37197 | 37198 | VOL_HARM_MINa43 | 10min 43rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x914F | 0x9150 | 37199 | 37200 | VOL_HARM_MINa44 | 10min 44th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9151 | 0x9152 | 37201 | 37202 | VOL_HARM_MINa45 | 10min 45th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9153 | 0x9154 | 37203 | 37204 | VOL_HARM_MINa46 | 10min 46th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9155 | 0x9156 | 37205 | 37206 | VOL_HARM_MINa47 | 10min 47th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9157 | 0x9158 | 37207 | 37208 | VOL_HARM_MINa48 | 10min 48th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9159 | 0x915A | 37209 | 37210 | VOL_HARM_MINa49 | 10min 49th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x915B | 0x915C | 37211 | 37212 | VOL_HARM_MINa50 | 10min 50th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x915D | 0x915E | 37213 | 37214 | VOL_HARM_MINb2 | 10min 2nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x915F | 0x9160 | 37215 | 37216 | VOL_HARM_MINb3 | 10min 3rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9161 | 0x9162 | 37217 | 37218 | VOL_HARM_MINb4 | 10min 4th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9163 | 0x9164 | 37219 | 37220 | VOL_HARM_MINb5 | 10min 5th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9165 | 0x9166 | 37221 | 37222 | VOL_HARM_MINb6 | 10min 6th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9167 | 0x9168 | 37223 | 37224 | VOL_HARM_MINb7 | 10min 7th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9169 | 0x916A | 37225 | 37226 | VOL_HARM_MINb8 | 10min 8th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x916B | 0x916C | 37227 | 37228 | VOL_HARM_MINb9 | 10min 9th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x916D | 0x916E | 37229 | 37230 | VOL_HARM_MINb10 | 10min 10th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x916F | 0x9170 | 37231 | 37232 | VOL_HARM_MINb11 | 10min 11st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9171 | 0x9172 | 37233 | 37234 | VOL_HARM_MINb12 | 10min 12nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9173 | 0x9174 | 37235 | 37236 | VOL_HARM_MINb13 | 10min 13rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9175 | 0x9176 | 37237 | 37238 | VOL_HARM_MINb14 | 10min 14th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9177 | 0x9178 | 37239 | 37240 | VOL_HARM_MINb15 | 10min 15th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9179 | 0x917A | 37241 | 37242 | VOL_HARM_MINb16 | 10min 16th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x917B | 0x917C | 37243 | 37244 | VOL_HARM_MINb17 | 10min 17th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x917D | 0x917E | 37245 | 37246 | VOL_HARM_MINb18 | 10min 18th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x917F | 0x9180 | 37247 | 37248 | VOL_HARM_MINb19 | 10min 19th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9181 | 0x9182 | 37249 | 37250 | VOL_HARM_MINb20 | 10min 20th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9183 | 0x9184 | 37251 | 37252 | VOL_HARM_MINb21 | 10min 21st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9185 | 0x9186 | 37253 | 37254 | VOL_HARM_MINb22 | 10min 22nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9187 | 0x9188 | 37255 | 37256 | VOL_HARM_MINb23 | 10min 23rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9189 | 0x918A | 37257 | 37258 | VOL_HARM_MINb24 | 10min 24th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x918B | 0x918C | 37259 | 37260 | VOL_HARM_MINb25 | 10min 25th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x918D | 0x918E | 37261 | 37262 | VOL_HARM_MINb26 | 10min 26th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x918F | 0x9190 | 37263 | 37264 | VOL_HARM_MINb27 | 10min 27th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9191 | 0x9192 | 37265 | 37266 | VOL_HARM_MINb28 | 10min 28th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9193 | 0x9194 | 37267 | 37268 | VOL_HARM_MINb29 | 10min 29th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9195 | 0x9196 | 37269 | 37270 | VOL_HARM_MINb30 | 10min 30th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9197 | 0x9198 | 37271 | 37272 | VOL_HARM_MINb31 | 10min 31st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9199 | 0x919A | 37273 | 37274 | VOL_HARM_MINb32 | 10min 32nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x919B | 0x919C | 37275 | 37276 | VOL_HARM_MINb33 | 10min 33rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x919D | 0x919E | 37277 | 37278 | VOL_HARM_MINb34 | 10min 34th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x919F | 0x91A0 | 37279 | 37280 | VOL_HARM_MINb35 | 10min 35th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91A1 | 0x91A2 | 37281 | 37282 | VOL_HARM_MINb36 | 10min 36th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91A3 | 0x91A4 | 37283 | 37284 | VOL_HARM_MINb37 | 10min 37th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91A5 | 0x91A6 | 37285 | 37286 | VOL_HARM_MINb38 | 10min 38th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91A7 | 0x91A8 | 37287 | 37288 | VOL_HARM_MINb39 | 10min 39th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91A9 | 0x91AA | 37289 | 37290 | VOL_HARM_MINb40 | 10min 40th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91AB | 0x91AC | 37291 | 37292 | VOL_HARM_MINb41 | 10min 41st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91AD | 0x91AE | 37293 | 37294 | VOL_HARM_MINb42 | 10min 42nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91AF | 0x91B0 | 37295 | 37296 | VOL_HARM_MINb43 | 10min 43rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91B1 | 0x91B2 | 37297 | 37298 | VOL_HARM_MINb44 | 10min 44th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91B3 | 0x91B4 | 37299 | 37300 | VOL_HARM_MINb45 | 10min 45th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91B5 | 0x91B6 | 37301 | 37302 | VOL_HARM_MINb46 | 10min 46th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91B7 | 0x91B8 | 37303 | 37304 | VOL_HARM_MINb47 | 10min 47th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91B9 | 0x91BA | 37305 | 37306 | VOL_HARM_MINb48 | 10min 48th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91BB | 0x91BC | 37307 | 37308 | VOL_HARM_MINb49 | 10min 49th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91BD | 0x91BE | 37309 | 37310 | VOL_HARM_MINb50 | 10min 50th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x91BF | 0x91C0 | 37311 | 37312 | VOL_HARM_MINc2 | 10min 2nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91C1 | 0x91C2 | 37313 | 37314 | VOL_HARM_MINc3 | 10min 3rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91C3 | 0x91C4 | 37315 | 37316 | VOL_HARM_MINc4 | 10min 4th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91C5 | 0x91C6 | 37317 | 37318 | VOL_HARM_MINc5 | 10min 5th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91C7 | 0x91C8 | 37319 | 37320 | VOL_HARM_MINc6 | 10min 6th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91C9 | 0x91CA | 37321 | 37322 | VOL_HARM_MINc7 | 10min 7th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91CB | 0x91CC | 37323 | 37324 | VOL_HARM_MINc8 | 10min 8th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91CD | 0x91CE | 37325 | 37326 | VOL_HARM_MINc9 | 10min 9th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91CF | 0x91D0 | 37327 | 37328 | VOL_HARM_MINc10 | 10min 10th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91D1 | 0x91D2 | 37329 | 37330 | VOL_HARM_MINc11 | 10min 11st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91D3 | 0x91D4 | 37331 | 37332 | VOL_HARM_MINc12 | 10min 12nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91D5 | 0x91D6 | 37333 | 37334 | VOL_HARM_MINc13 | 10min 13rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91D7 | 0x91D8 | 37335 | 37336 | VOL_HARM_MINc14 | 10min 14th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91D9 | 0x91DA | 37337 | 37338 | VOL_HARM_MINc15 | 10min 15th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91DB | 0x91DC | 37339 | 37340 | VOL_HARM_MINc16 | 10min 16th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91DD | 0x91DE | 37341 | 37342 | VOL_HARM_MINc17 | 10min 17th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91DF | 0x91E0 | 37343 | 37344 | VOL_HARM_MINc18 | 10min 18th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91E1 | 0x91E2 | 37345 | 37346 | VOL_HARM_MINc19 | 10min 19th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91E3 | 0x91E4 | 37347 | 37348 | VOL_HARM_MINc20 | 10min 20th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91E5 | 0x91E6 | 37349 | 37350 | VOL_HARM_MINc21 | 10min 21st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91E7 | 0x91E8 | 37351 | 37352 | VOL_HARM_MINc22 | 10min 22nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91E9 | 0x91EA | 37353 | 37354 | VOL_HARM_MINc23 | 10min 23rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91EB | 0x91EC | 37355 | 37356 | VOL_HARM_MINc24 | 10min 24th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91ED | 0x91EE | 37357 | 37358 | VOL_HARM_MINc25 | 10min 25th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91EF | 0x91F0 | 37359 | 37360 | VOL_HARM_MINc26 | 10min 26th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91F1 | 0x91F2 | 37361 | 37362 | VOL_HARM_MINc27 | 10min 27th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91F3 | 0x91F4 | 37363 | 37364 | VOL_HARM_MINc28 | 10min 28th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91F5 | 0x91F6 | 37365 | 37366 | VOL_HARM_MINc29 | 10min 29th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91F7 | 0x91F8 | 37367 | 37368 | VOL_HARM_MINc30 | 10min 30th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91F9 | 0x91FA | 37369 | 37370 | VOL_HARM_MINc31 | 10min 31st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91FB | 0x91FC | 37371 | 37372 | VOL_HARM_MINc32 | 10min 32nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91FD | 0x91FE | 37373 | 37374 | VOL_HARM_MINc33 | 10min 33rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x91FF | 0x9200 | 37375 | 37376 | VOL_HARM_MINc34 | 10min 34th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9201 | 0x9202 | 37377 | 37378 | VOL_HARM_MINc35 | 10min 35th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9203 | 0x9204 | 37379 | 37380 | VOL_HARM_MINc36 | 10min 36th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9205 | 0x9206 | 37381 | 37382 | VOL_HARM_MINc37 | 10min 37th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9207 | 0x9208 | 37383 | 37384 | VOL_HARM_MINc38 | 10min 38th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9209 | 0x920A | 37385 | 37386 | VOL_HARM_MINc39 | 10min 39th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x920B | 0x920C | 37387 | 37388 | VOL_HARM_MINc40 | 10min 40th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x920D | 0x920E | 37389 | 37390 | VOL_HARM_MINc41 | 10min 41st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x920F | 0x9210 | 37391 | 37392 | VOL_HARM_MINc42 | 10min 42nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9211 | 0x9212 | 37393 | 37394 | VOL_HARM_MINc43 | 10min 43rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9213 | 0x9214 | 37395 | 37396 | VOL_HARM_MINc44 | 10min 44th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9215 | 0x9216 | 37397 | 37398 | VOL_HARM_MINc45 | 10min 45th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9217 | 0x9218 | 37399 | 37400 | VOL_HARM_MINc46 | 10min 46th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9219 | 0x921A | 37401 | 37402 | VOL_HARM_MINc47 | 10min 47th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x921B | 0x921C | 37403 | 37404 | VOL_HARM_MINc48 | 10min 48th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x921D | 0x921E | 37405 | 37406 | VOL_HARM_MINc49 | 10min 49th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x921F | 0x9220 | 37407 | 37408 | VOL_HARM_MINc50 | 10min 50th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9221 | 0x9222 | 37409 | 37410 | VOL_HARM_AVGa2 | 10min 2nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9223 | 0x9224 | 37411 | 37412 | VOL_HARM_AVGa3 | 10min 3rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9225 | 0x9226 | 37413 | 37414 | VOL_HARM_AVGa4 | 10min 4th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9227 | 0x9228 | 37415 | 37416 | VOL_HARM_AVGa5 | 10min 5th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9229 | 0x922A | 37417 | 37418 | VOL_HARM_AVGa6 | 10min 6th Phase A Voltage Harmonics Average Value | float | 2 | R
0x922B | 0x922C | 37419 | 37420 | VOL_HARM_AVGa7 | 10min 7th Phase A Voltage Harmonics Average Value | float | 2 | R
0x922D | 0x922E | 37421 | 37422 | VOL_HARM_AVGa8 | 10min 8th Phase A Voltage Harmonics Average Value | float | 2 | R
0x922F | 0x9230 | 37423 | 37424 | VOL_HARM_AVGa9 | 10min 9th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9231 | 0x9232 | 37425 | 37426 | VOL_HARM_AVGa10 | 10min 10th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9233 | 0x9234 | 37427 | 37428 | VOL_HARM_AVGa11 | 10min 11st Phase A Voltage Harmonics Average Value | float | 2 | R
0x9235 | 0x9236 | 37429 | 37430 | VOL_HARM_AVGa12 | 10min 12nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9237 | 0x9238 | 37431 | 37432 | VOL_HARM_AVGa13 | 10min 13rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9239 | 0x923A | 37433 | 37434 | VOL_HARM_AVGa14 | 10min 14th Phase A Voltage Harmonics Average Value | float | 2 | R
0x923B | 0x923C | 37435 | 37436 | VOL_HARM_AVGa15 | 10min 15th Phase A Voltage Harmonics Average Value | float | 2 | R
0x923D | 0x923E | 37437 | 37438 | VOL_HARM_AVGa16 | 10min 16th Phase A Voltage Harmonics Average Value | float | 2 | R
0x923F | 0x9240 | 37439 | 37440 | VOL_HARM_AVGa17 | 10min 17th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9241 | 0x9242 | 37441 | 37442 | VOL_HARM_AVGa18 | 10min 18th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9243 | 0x9244 | 37443 | 37444 | VOL_HARM_AVGa19 | 10min 19th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9245 | 0x9246 | 37445 | 37446 | VOL_HARM_AVGa20 | 10min 20th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9247 | 0x9248 | 37447 | 37448 | VOL_HARM_AVGa21 | 10min 21st Phase A Voltage Harmonics Average Value | float | 2 | R
0x9249 | 0x924A | 37449 | 37450 | VOL_HARM_AVGa22 | 10min 22nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x924B | 0x924C | 37451 | 37452 | VOL_HARM_AVGa23 | 10min 23rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x924D | 0x924E | 37453 | 37454 | VOL_HARM_AVGa24 | 10min 24th Phase A Voltage Harmonics Average Value | float | 2 | R
0x924F | 0x9250 | 37455 | 37456 | VOL_HARM_AVGa25 | 10min 25th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9251 | 0x9252 | 37457 | 37458 | VOL_HARM_AVGa26 | 10min 26th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9253 | 0x9254 | 37459 | 37460 | VOL_HARM_AVGa27 | 10min 27th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9255 | 0x9256 | 37461 | 37462 | VOL_HARM_AVGa28 | 10min 28th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9257 | 0x9258 | 37463 | 37464 | VOL_HARM_AVGa29 | 10min 29th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9259 | 0x925A | 37465 | 37466 | VOL_HARM_AVGa30 | 10min 30th Phase A Voltage Harmonics Average Value | float | 2 | R
0x925B | 0x925C | 37467 | 37468 | VOL_HARM_AVGa31 | 10min 31st Phase A Voltage Harmonics Average Value | float | 2 | R
0x925D | 0x925E | 37469 | 37470 | VOL_HARM_AVGa32 | 10min 32nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x925F | 0x9260 | 37471 | 37472 | VOL_HARM_AVGa33 | 10min 33rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9261 | 0x9262 | 37473 | 37474 | VOL_HARM_AVGa34 | 10min 34th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9263 | 0x9264 | 37475 | 37476 | VOL_HARM_AVGa35 | 10min 35th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9265 | 0x9266 | 37477 | 37478 | VOL_HARM_AVGa36 | 10min 36th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9267 | 0x9268 | 37479 | 37480 | VOL_HARM_AVGa37 | 10min 37th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9269 | 0x926A | 37481 | 37482 | VOL_HARM_AVGa38 | 10min 38th Phase A Voltage Harmonics Average Value | float | 2 | R
0x926B | 0x926C | 37483 | 37484 | VOL_HARM_AVGa39 | 10min 39th Phase A Voltage Harmonics Average Value | float | 2 | R
0x926D | 0x926E | 37485 | 37486 | VOL_HARM_AVGa40 | 10min 40th Phase A Voltage Harmonics Average Value | float | 2 | R
0x926F | 0x9270 | 37487 | 37488 | VOL_HARM_AVGa41 | 10min 41st Phase A Voltage Harmonics Average Value | float | 2 | R
0x9271 | 0x9272 | 37489 | 37490 | VOL_HARM_AVGa42 | 10min 42nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9273 | 0x9274 | 37491 | 37492 | VOL_HARM_AVGa43 | 10min 43rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9275 | 0x9276 | 37493 | 37494 | VOL_HARM_AVGa44 | 10min 44th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9277 | 0x9278 | 37495 | 37496 | VOL_HARM_AVGa45 | 10min 45th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9279 | 0x927A | 37497 | 37498 | VOL_HARM_AVGa46 | 10min 46th Phase A Voltage Harmonics Average Value | float | 2 | R
0x927B | 0x927C | 37499 | 37500 | VOL_HARM_AVGa47 | 10min 47th Phase A Voltage Harmonics Average Value | float | 2 | R
0x927D | 0x927E | 37501 | 37502 | VOL_HARM_AVGa48 | 10min 48th Phase A Voltage Harmonics Average Value | float | 2 | R
0x927F | 0x9280 | 37503 | 37504 | VOL_HARM_AVGa49 | 10min 49th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9281 | 0x9282 | 37505 | 37506 | VOL_HARM_AVGa50 | 10min 50th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9283 | 0x9284 | 37507 | 37508 | VOL_HARM_AVGb2 | 10min 2nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9285 | 0x9286 | 37509 | 37510 | VOL_HARM_AVGb3 | 10min 3rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9287 | 0x9288 | 37511 | 37512 | VOL_HARM_AVGb4 | 10min 4th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9289 | 0x928A | 37513 | 37514 | VOL_HARM_AVGb5 | 10min 5th Phase B Voltage Harmonics Average Value | float | 2 | R
0x928B | 0x928C | 37515 | 37516 | VOL_HARM_AVGb6 | 10min 6th Phase B Voltage Harmonics Average Value | float | 2 | R
0x928D | 0x928E | 37517 | 37518 | VOL_HARM_AVGb7 | 10min 7th Phase B Voltage Harmonics Average Value | float | 2 | R
0x928F | 0x9290 | 37519 | 37520 | VOL_HARM_AVGb8 | 10min 8th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9291 | 0x9292 | 37521 | 37522 | VOL_HARM_AVGb9 | 10min 9th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9293 | 0x9294 | 37523 | 37524 | VOL_HARM_AVGb10 | 10min 10th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9295 | 0x9296 | 37525 | 37526 | VOL_HARM_AVGb11 | 10min 11st Phase B Voltage Harmonics Average Value | float | 2 | R
0x9297 | 0x9298 | 37527 | 37528 | VOL_HARM_AVGb12 | 10min 12nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9299 | 0x929A | 37529 | 37530 | VOL_HARM_AVGb13 | 10min 13rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x929B | 0x929C | 37531 | 37532 | VOL_HARM_AVGb14 | 10min 14th Phase B Voltage Harmonics Average Value | float | 2 | R
0x929D | 0x929E | 37533 | 37534 | VOL_HARM_AVGb15 | 10min 15th Phase B Voltage Harmonics Average Value | float | 2 | R
0x929F | 0x92A0 | 37535 | 37536 | VOL_HARM_AVGb16 | 10min 16th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92A1 | 0x92A2 | 37537 | 37538 | VOL_HARM_AVGb17 | 10min 17th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92A3 | 0x92A4 | 37539 | 37540 | VOL_HARM_AVGb18 | 10min 18th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92A5 | 0x92A6 | 37541 | 37542 | VOL_HARM_AVGb19 | 10min 19th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92A7 | 0x92A8 | 37543 | 37544 | VOL_HARM_AVGb20 | 10min 20th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92A9 | 0x92AA | 37545 | 37546 | VOL_HARM_AVGb21 | 10min 21st Phase B Voltage Harmonics Average Value | float | 2 | R
0x92AB | 0x92AC | 37547 | 37548 | VOL_HARM_AVGb22 | 10min 22nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x92AD | 0x92AE | 37549 | 37550 | VOL_HARM_AVGb23 | 10min 23rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x92AF | 0x92B0 | 37551 | 37552 | VOL_HARM_AVGb24 | 10min 24th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92B1 | 0x92B2 | 37553 | 37554 | VOL_HARM_AVGb25 | 10min 25th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92B3 | 0x92B4 | 37555 | 37556 | VOL_HARM_AVGb26 | 10min 26th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92B5 | 0x92B6 | 37557 | 37558 | VOL_HARM_AVGb27 | 10min 27th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92B7 | 0x92B8 | 37559 | 37560 | VOL_HARM_AVGb28 | 10min 28th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92B9 | 0x92BA | 37561 | 37562 | VOL_HARM_AVGb29 | 10min 29th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92BB | 0x92BC | 37563 | 37564 | VOL_HARM_AVGb30 | 10min 30th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92BD | 0x92BE | 37565 | 37566 | VOL_HARM_AVGb31 | 10min 31st Phase B Voltage Harmonics Average Value | float | 2 | R
0x92BF | 0x92C0 | 37567 | 37568 | VOL_HARM_AVGb32 | 10min 32nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x92C1 | 0x92C2 | 37569 | 37570 | VOL_HARM_AVGb33 | 10min 33rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x92C3 | 0x92C4 | 37571 | 37572 | VOL_HARM_AVGb34 | 10min 34th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92C5 | 0x92C6 | 37573 | 37574 | VOL_HARM_AVGb35 | 10min 35th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92C7 | 0x92C8 | 37575 | 37576 | VOL_HARM_AVGb36 | 10min 36th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92C9 | 0x92CA | 37577 | 37578 | VOL_HARM_AVGb37 | 10min 37th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92CB | 0x92CC | 37579 | 37580 | VOL_HARM_AVGb38 | 10min 38th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92CD | 0x92CE | 37581 | 37582 | VOL_HARM_AVGb39 | 10min 39th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92CF | 0x92D0 | 37583 | 37584 | VOL_HARM_AVGb40 | 10min 40th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92D1 | 0x92D2 | 37585 | 37586 | VOL_HARM_AVGb41 | 10min 41st Phase B Voltage Harmonics Average Value | float | 2 | R
0x92D3 | 0x92D4 | 37587 | 37588 | VOL_HARM_AVGb42 | 10min 42nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x92D5 | 0x92D6 | 37589 | 37590 | VOL_HARM_AVGb43 | 10min 43rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x92D7 | 0x92D8 | 37591 | 37592 | VOL_HARM_AVGb44 | 10min 44th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92D9 | 0x92DA | 37593 | 37594 | VOL_HARM_AVGb45 | 10min 45th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92DB | 0x92DC | 37595 | 37596 | VOL_HARM_AVGb46 | 10min 46th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92DD | 0x92DE | 37597 | 37598 | VOL_HARM_AVGb47 | 10min 47th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92DF | 0x92E0 | 37599 | 37600 | VOL_HARM_AVGb48 | 10min 48th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92E1 | 0x92E2 | 37601 | 37602 | VOL_HARM_AVGb49 | 10min 49th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92E3 | 0x92E4 | 37603 | 37604 | VOL_HARM_AVGb50 | 10min 50th Phase B Voltage Harmonics Average Value | float | 2 | R
0x92E5 | 0x92E6 | 37605 | 37606 | VOL_HARM_AVGc2 | 10min 2nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x92E7 | 0x92E8 | 37607 | 37608 | VOL_HARM_AVGc3 | 10min 3rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x92E9 | 0x92EA | 37609 | 37610 | VOL_HARM_AVGc4 | 10min 4th Phase C Voltage Harmonics Average Value | float | 2 | R
0x92EB | 0x92EC | 37611 | 37612 | VOL_HARM_AVGc5 | 10min 5th Phase C Voltage Harmonics Average Value | float | 2 | R
0x92ED | 0x92EE | 37613 | 37614 | VOL_HARM_AVGc6 | 10min 6th Phase C Voltage Harmonics Average Value | float | 2 | R
0x92EF | 0x92F0 | 37615 | 37616 | VOL_HARM_AVGc7 | 10min 7th Phase C Voltage Harmonics Average Value | float | 2 | R
0x92F1 | 0x92F2 | 37617 | 37618 | VOL_HARM_AVGc8 | 10min 8th Phase C Voltage Harmonics Average Value | float | 2 | R
0x92F3 | 0x92F4 | 37619 | 37620 | VOL_HARM_AVGc9 | 10min 9th Phase C Voltage Harmonics Average Value | float | 2 | R
0x92F5 | 0x92F6 | 37621 | 37622 | VOL_HARM_AVGc10 | 10min 10th Phase C Voltage Harmonics Average Value | float | 2 | R
0x92F7 | 0x92F8 | 37623 | 37624 | VOL_HARM_AVGc11 | 10min 11st Phase C Voltage Harmonics Average Value | float | 2 | R
0x92F9 | 0x92FA | 37625 | 37626 | VOL_HARM_AVGc12 | 10min 12nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x92FB | 0x92FC | 37627 | 37628 | VOL_HARM_AVGc13 | 10min 13rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x92FD | 0x92FE | 37629 | 37630 | VOL_HARM_AVGc14 | 10min 14th Phase C Voltage Harmonics Average Value | float | 2 | R
0x92FF | 0x9300 | 37631 | 37632 | VOL_HARM_AVGc15 | 10min 15th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9301 | 0x9302 | 37633 | 37634 | VOL_HARM_AVGc16 | 10min 16th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9303 | 0x9304 | 37635 | 37636 | VOL_HARM_AVGc17 | 10min 17th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9305 | 0x9306 | 37637 | 37638 | VOL_HARM_AVGc18 | 10min 18th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9307 | 0x9308 | 37639 | 37640 | VOL_HARM_AVGc19 | 10min 19th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9309 | 0x930A | 37641 | 37642 | VOL_HARM_AVGc20 | 10min 20th Phase C Voltage Harmonics Average Value | float | 2 | R
0x930B | 0x930C | 37643 | 37644 | VOL_HARM_AVGc21 | 10min 21st Phase C Voltage Harmonics Average Value | float | 2 | R
0x930D | 0x930E | 37645 | 37646 | VOL_HARM_AVGc22 | 10min 22nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x930F | 0x9310 | 37647 | 37648 | VOL_HARM_AVGc23 | 10min 23rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x9311 | 0x9312 | 37649 | 37650 | VOL_HARM_AVGc24 | 10min 24th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9313 | 0x9314 | 37651 | 37652 | VOL_HARM_AVGc25 | 10min 25th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9315 | 0x9316 | 37653 | 37654 | VOL_HARM_AVGc26 | 10min 26th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9317 | 0x9318 | 37655 | 37656 | VOL_HARM_AVGc27 | 10min 27th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9319 | 0x931A | 37657 | 37658 | VOL_HARM_AVGc28 | 10min 28th Phase C Voltage Harmonics Average Value | float | 2 | R
0x931B | 0x931C | 37659 | 37660 | VOL_HARM_AVGc29 | 10min 29th Phase C Voltage Harmonics Average Value | float | 2 | R
0x931D | 0x931E | 37661 | 37662 | VOL_HARM_AVGc30 | 10min 30th Phase C Voltage Harmonics Average Value | float | 2 | R
0x931F | 0x9320 | 37663 | 37664 | VOL_HARM_AVGc31 | 10min 31st Phase C Voltage Harmonics Average Value | float | 2 | R
0x9321 | 0x9322 | 37665 | 37666 | VOL_HARM_AVGc32 | 10min 32nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x9323 | 0x9324 | 37667 | 37668 | VOL_HARM_AVGc33 | 10min 33rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x9325 | 0x9326 | 37669 | 37670 | VOL_HARM_AVGc34 | 10min 34th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9327 | 0x9328 | 37671 | 37672 | VOL_HARM_AVGc35 | 10min 35th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9329 | 0x932A | 37673 | 37674 | VOL_HARM_AVGc36 | 10min 36th Phase C Voltage Harmonics Average Value | float | 2 | R
0x932B | 0x932C | 37675 | 37676 | VOL_HARM_AVGc37 | 10min 37th Phase C Voltage Harmonics Average Value | float | 2 | R
0x932D | 0x932E | 37677 | 37678 | VOL_HARM_AVGc38 | 10min 38th Phase C Voltage Harmonics Average Value | float | 2 | R
0x932F | 0x9330 | 37679 | 37680 | VOL_HARM_AVGc39 | 10min 39th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9331 | 0x9332 | 37681 | 37682 | VOL_HARM_AVGc40 | 10min 40th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9333 | 0x9334 | 37683 | 37684 | VOL_HARM_AVGc41 | 10min 41st Phase C Voltage Harmonics Average Value | float | 2 | R
0x9335 | 0x9336 | 37685 | 37686 | VOL_HARM_AVGc42 | 10min 42nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x9337 | 0x9338 | 37687 | 37688 | VOL_HARM_AVGc43 | 10min 43rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x9339 | 0x933A | 37689 | 37690 | VOL_HARM_AVGc44 | 10min 44th Phase C Voltage Harmonics Average Value | float | 2 | R
0x933B | 0x933C | 37691 | 37692 | VOL_HARM_AVGc45 | 10min 45th Phase C Voltage Harmonics Average Value | float | 2 | R
0x933D | 0x933E | 37693 | 37694 | VOL_HARM_AVGc46 | 10min 46th Phase C Voltage Harmonics Average Value | float | 2 | R
0x933F | 0x9340 | 37695 | 37696 | VOL_HARM_AVGc47 | 10min 47th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9341 | 0x9342 | 37697 | 37698 | VOL_HARM_AVGc48 | 10min 48th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9343 | 0x9344 | 37699 | 37700 | VOL_HARM_AVGc49 | 10min 49th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9345 | 0x9346 | 37701 | 37702 | VOL_HARM_AVGc50 | 10min 50th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9347 | 0x9348 | 37703 | 37704 | TDD_MAXa | 10min Phase A TDD Maximum Value | float | 2 | R
0x9349 | 0x934A | 37705 | 37706 | TDD_MAXb | 10min Phase B TDD Maximum Value | float | 2 | R
0x934B | 0x934C | 37707 | 37708 | TDD_MAXc | 10min Phase C TDD Maximum Value | float | 2 | R
0x934D | 0x934E | 37709 | 37710 | TDD_MINa | 10min Phase A TDD Minimum Value | float | 2 | R
0x934F | 0x9350 | 37711 | 37712 | TDD_MINb | 10min Phase B TDD Minimum Value | float | 2 | R
0x9351 | 0x9352 | 37713 | 37714 | TDD_MINc | 10min Phase C TDD Minimum Value | float | 2 | R
0x9353 | 0x9354 | 37715 | 37716 | TDD_AVGa | 10min Phase A TDD Average Value | float | 2 | R
0x9355 | 0x9356 | 37717 | 37718 | TDD_AVGb | 10min Phase B TDD Average Value | float | 2 | R
0x9357 | 0x9358 | 37719 | 37720 | TDD_AVGc | 10min Phase C TDD Average Value | float | 2 | R
0x9359 | 0x935A | 37721 | 37722 | CUR_HARM_MAXa2 | 10min 2nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x935B | 0x935C | 37723 | 37724 | CUR_HARM_MAXa3 | 10min 3rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x935D | 0x935E | 37725 | 37726 | CUR_HARM_MAXa4 | 10min 4th Phase A Current Harmonics Maximum Value | float | 2 | R
0x935F | 0x9360 | 37727 | 37728 | CUR_HARM_MAXa5 | 10min 5th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9361 | 0x9362 | 37729 | 37730 | CUR_HARM_MAXa6 | 10min 6th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9363 | 0x9364 | 37731 | 37732 | CUR_HARM_MAXa7 | 10min 7th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9365 | 0x9366 | 37733 | 37734 | CUR_HARM_MAXa8 | 10min 8th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9367 | 0x9368 | 37735 | 37736 | CUR_HARM_MAXa9 | 10min 9th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9369 | 0x936A | 37737 | 37738 | CUR_HARM_MAXa10 | 10min 10th Phase A Current Harmonics Maximum Value | float | 2 | R
0x936B | 0x936C | 37739 | 37740 | CUR_HARM_MAXa11 | 10min 11st Phase A Current Harmonics Maximum Value | float | 2 | R
0x936D | 0x936E | 37741 | 37742 | CUR_HARM_MAXa12 | 10min 12nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x936F | 0x9370 | 37743 | 37744 | CUR_HARM_MAXa13 | 10min 13rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x9371 | 0x9372 | 37745 | 37746 | CUR_HARM_MAXa14 | 10min 14th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9373 | 0x9374 | 37747 | 37748 | CUR_HARM_MAXa15 | 10min 15th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9375 | 0x9376 | 37749 | 37750 | CUR_HARM_MAXa16 | 10min 16th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9377 | 0x9378 | 37751 | 37752 | CUR_HARM_MAXa17 | 10min 17th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9379 | 0x937A | 37753 | 37754 | CUR_HARM_MAXa18 | 10min 18th Phase A Current Harmonics Maximum Value | float | 2 | R
0x937B | 0x937C | 37755 | 37756 | CUR_HARM_MAXa19 | 10min 19th Phase A Current Harmonics Maximum Value | float | 2 | R
0x937D | 0x937E | 37757 | 37758 | CUR_HARM_MAXa20 | 10min 20th Phase A Current Harmonics Maximum Value | float | 2 | R
0x937F | 0x9380 | 37759 | 37760 | CUR_HARM_MAXa21 | 10min 21st Phase A Current Harmonics Maximum Value | float | 2 | R
0x9381 | 0x9382 | 37761 | 37762 | CUR_HARM_MAXa22 | 10min 22nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x9383 | 0x9384 | 37763 | 37764 | CUR_HARM_MAXa23 | 10min 23rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x9385 | 0x9386 | 37765 | 37766 | CUR_HARM_MAXa24 | 10min 24th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9387 | 0x9388 | 37767 | 37768 | CUR_HARM_MAXa25 | 10min 25th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9389 | 0x938A | 37769 | 37770 | CUR_HARM_MAXa26 | 10min 26th Phase A Current Harmonics Maximum Value | float | 2 | R
0x938B | 0x938C | 37771 | 37772 | CUR_HARM_MAXa27 | 10min 27th Phase A Current Harmonics Maximum Value | float | 2 | R
0x938D | 0x938E | 37773 | 37774 | CUR_HARM_MAXa28 | 10min 28th Phase A Current Harmonics Maximum Value | float | 2 | R
0x938F | 0x9390 | 37775 | 37776 | CUR_HARM_MAXa29 | 10min 29th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9391 | 0x9392 | 37777 | 37778 | CUR_HARM_MAXa30 | 10min 30th Phase A Current Harmonics Maximum Value | float | 2 | R
0x9393 | 0x9394 | 37779 | 37780 | CUR_HARM_MAXa31 | 10min 31st Phase A Current Harmonics Maximum Value | float | 2 | R
0x9395 | 0x9396 | 37781 | 37782 | CUR_HARM_MAXa32 | 10min 32nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x9397 | 0x9398 | 37783 | 37784 | CUR_HARM_MAXa33 | 10min 33rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x9399 | 0x939A | 37785 | 37786 | CUR_HARM_MAXa34 | 10min 34th Phase A Current Harmonics Maximum Value | float | 2 | R
0x939B | 0x939C | 37787 | 37788 | CUR_HARM_MAXa35 | 10min 35th Phase A Current Harmonics Maximum Value | float | 2 | R
0x939D | 0x939E | 37789 | 37790 | CUR_HARM_MAXa36 | 10min 36th Phase A Current Harmonics Maximum Value | float | 2 | R
0x939F | 0x93A0 | 37791 | 37792 | CUR_HARM_MAXa37 | 10min 37th Phase A Current Harmonics Maximum Value | float | 2 | R
0x93A1 | 0x93A2 | 37793 | 37794 | CUR_HARM_MAXa38 | 10min 38th Phase A Current Harmonics Maximum Value | float | 2 | R
0x93A3 | 0x93A4 | 37795 | 37796 | CUR_HARM_MAXa39 | 10min 39th Phase A Current Harmonics Maximum Value | float | 2 | R
0x93A5 | 0x93A6 | 37797 | 37798 | CUR_HARM_MAXa40 | 10min 40th Phase A Current Harmonics Maximum Value | float | 2 | R
0x93A7 | 0x93A8 | 37799 | 37800 | CUR_HARM_MAXa41 | 10min 41st Phase A Current Harmonics Maximum Value | float | 2 | R
0x93A9 | 0x93AA | 37801 | 37802 | CUR_HARM_MAXa42 | 10min 42nd Phase A Current Harmonics Maximum Value | float | 2 | R
0x93AB | 0x93AC | 37803 | 37804 | CUR_HARM_MAXa43 | 10min 43rd Phase A Current Harmonics Maximum Value | float | 2 | R
0x93AD | 0x93AE | 37805 | 37806 | CUR_HARM_MAXa44 | 10min 44th Phase A Current Harmonics Maximum Value | float | 2 | R
0x93AF | 0x93B0 | 37807 | 37808 | CUR_HARM_MAXa45 | 10min 45th Phase A Current Harmonics Maximum Value | float | 2 | R
0x93B1 | 0x93B2 | 37809 | 37810 | CUR_HARM_MAXa46 | 10min 46th Phase A Current Harmonics Maximum Value | float | 2 | R
0x93B3 | 0x93B4 | 37811 | 37812 | CUR_HARM_MAXa47 | 10min 47th Phase A Current Harmonics Maximum Value | float | 2 | R
0x93B5 | 0x93B6 | 37813 | 37814 | CUR_HARM_MAXa48 | 10min 48th Phase A Current Harmonics Maximum Value | float | 2 | R
0x93B7 | 0x93B8 | 37815 | 37816 | CUR_HARM_MAXa49 | 10min 49th Phase A Current Harmonics Maximum Value | float | 2 | R
0x93B9 | 0x93BA | 37817 | 37818 | CUR_HARM_MAXa50 | 10min 50th Phase A Current Harmonics Maximum Value | float | 2 | R
0x93BB | 0x93BC | 37819 | 37820 | CUR_HARM_MAXb2 | 10min 2nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x93BD | 0x93BE | 37821 | 37822 | CUR_HARM_MAXb3 | 10min 3rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x93BF | 0x93C0 | 37823 | 37824 | CUR_HARM_MAXb4 | 10min 4th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93C1 | 0x93C2 | 37825 | 37826 | CUR_HARM_MAXb5 | 10min 5th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93C3 | 0x93C4 | 37827 | 37828 | CUR_HARM_MAXb6 | 10min 6th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93C5 | 0x93C6 | 37829 | 37830 | CUR_HARM_MAXb7 | 10min 7th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93C7 | 0x93C8 | 37831 | 37832 | CUR_HARM_MAXb8 | 10min 8th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93C9 | 0x93CA | 37833 | 37834 | CUR_HARM_MAXb9 | 10min 9th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93CB | 0x93CC | 37835 | 37836 | CUR_HARM_MAXb10 | 10min 10th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93CD | 0x93CE | 37837 | 37838 | CUR_HARM_MAXb11 | 10min 11st Phase B Current Harmonics Maximum Value | float | 2 | R
0x93CF | 0x93D0 | 37839 | 37840 | CUR_HARM_MAXb12 | 10min 12nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x93D1 | 0x93D2 | 37841 | 37842 | CUR_HARM_MAXb13 | 10min 13rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x93D3 | 0x93D4 | 37843 | 37844 | CUR_HARM_MAXb14 | 10min 14th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93D5 | 0x93D6 | 37845 | 37846 | CUR_HARM_MAXb15 | 10min 15th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93D7 | 0x93D8 | 37847 | 37848 | CUR_HARM_MAXb16 | 10min 16th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93D9 | 0x93DA | 37849 | 37850 | CUR_HARM_MAXb17 | 10min 17th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93DB | 0x93DC | 37851 | 37852 | CUR_HARM_MAXb18 | 10min 18th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93DD | 0x93DE | 37853 | 37854 | CUR_HARM_MAXb19 | 10min 19th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93DF | 0x93E0 | 37855 | 37856 | CUR_HARM_MAXb20 | 10min 20th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93E1 | 0x93E2 | 37857 | 37858 | CUR_HARM_MAXb21 | 10min 21st Phase B Current Harmonics Maximum Value | float | 2 | R
0x93E3 | 0x93E4 | 37859 | 37860 | CUR_HARM_MAXb22 | 10min 22nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x93E5 | 0x93E6 | 37861 | 37862 | CUR_HARM_MAXb23 | 10min 23rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x93E7 | 0x93E8 | 37863 | 37864 | CUR_HARM_MAXb24 | 10min 24th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93E9 | 0x93EA | 37865 | 37866 | CUR_HARM_MAXb25 | 10min 25th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93EB | 0x93EC | 37867 | 37868 | CUR_HARM_MAXb26 | 10min 26th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93ED | 0x93EE | 37869 | 37870 | CUR_HARM_MAXb27 | 10min 27th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93EF | 0x93F0 | 37871 | 37872 | CUR_HARM_MAXb28 | 10min 28th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93F1 | 0x93F2 | 37873 | 37874 | CUR_HARM_MAXb29 | 10min 29th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93F3 | 0x93F4 | 37875 | 37876 | CUR_HARM_MAXb30 | 10min 30th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93F5 | 0x93F6 | 37877 | 37878 | CUR_HARM_MAXb31 | 10min 31st Phase B Current Harmonics Maximum Value | float | 2 | R
0x93F7 | 0x93F8 | 37879 | 37880 | CUR_HARM_MAXb32 | 10min 32nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x93F9 | 0x93FA | 37881 | 37882 | CUR_HARM_MAXb33 | 10min 33rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x93FB | 0x93FC | 37883 | 37884 | CUR_HARM_MAXb34 | 10min 34th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93FD | 0x93FE | 37885 | 37886 | CUR_HARM_MAXb35 | 10min 35th Phase B Current Harmonics Maximum Value | float | 2 | R
0x93FF | 0x9400 | 37887 | 37888 | CUR_HARM_MAXb36 | 10min 36th Phase B Current Harmonics Maximum Value | float | 2 | R
0x9401 | 0x9402 | 37889 | 37890 | CUR_HARM_MAXb37 | 10min 37th Phase B Current Harmonics Maximum Value | float | 2 | R
0x9403 | 0x9404 | 37891 | 37892 | CUR_HARM_MAXb38 | 10min 38th Phase B Current Harmonics Maximum Value | float | 2 | R
0x9405 | 0x9406 | 37893 | 37894 | CUR_HARM_MAXb39 | 10min 39th Phase B Current Harmonics Maximum Value | float | 2 | R
0x9407 | 0x9408 | 37895 | 37896 | CUR_HARM_MAXb40 | 10min 40th Phase B Current Harmonics Maximum Value | float | 2 | R
0x9409 | 0x940A | 37897 | 37898 | CUR_HARM_MAXb41 | 10min 41st Phase B Current Harmonics Maximum Value | float | 2 | R
0x940B | 0x940C | 37899 | 37900 | CUR_HARM_MAXb42 | 10min 42nd Phase B Current Harmonics Maximum Value | float | 2 | R
0x940D | 0x940E | 37901 | 37902 | CUR_HARM_MAXb43 | 10min 43rd Phase B Current Harmonics Maximum Value | float | 2 | R
0x940F | 0x9410 | 37903 | 37904 | CUR_HARM_MAXb44 | 10min 44th Phase B Current Harmonics Maximum Value | float | 2 | R
0x9411 | 0x9412 | 37905 | 37906 | CUR_HARM_MAXb45 | 10min 45th Phase B Current Harmonics Maximum Value | float | 2 | R
0x9413 | 0x9414 | 37907 | 37908 | CUR_HARM_MAXb46 | 10min 46th Phase B Current Harmonics Maximum Value | float | 2 | R
0x9415 | 0x9416 | 37909 | 37910 | CUR_HARM_MAXb47 | 10min 47th Phase B Current Harmonics Maximum Value | float | 2 | R
0x9417 | 0x9418 | 37911 | 37912 | CUR_HARM_MAXb48 | 10min 48th Phase B Current Harmonics Maximum Value | float | 2 | R
0x9419 | 0x941A | 37913 | 37914 | CUR_HARM_MAXb49 | 10min 49th Phase B Current Harmonics Maximum Value | float | 2 | R
0x941B | 0x941C | 37915 | 37916 | CUR_HARM_MAXb50 | 10min 50th Phase B Current Harmonics Maximum Value | float | 2 | R
0x941D | 0x941E | 37917 | 37918 | CUR_HARM_MAXc2 | 10min 2nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x941F | 0x9420 | 37919 | 37920 | CUR_HARM_MAXc3 | 10min 3rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x9421 | 0x9422 | 37921 | 37922 | CUR_HARM_MAXc4 | 10min 4th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9423 | 0x9424 | 37923 | 37924 | CUR_HARM_MAXc5 | 10min 5th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9425 | 0x9426 | 37925 | 37926 | CUR_HARM_MAXc6 | 10min 6th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9427 | 0x9428 | 37927 | 37928 | CUR_HARM_MAXc7 | 10min 7th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9429 | 0x942A | 37929 | 37930 | CUR_HARM_MAXc8 | 10min 8th Phase C Current Harmonics Maximum Value | float | 2 | R
0x942B | 0x942C | 37931 | 37932 | CUR_HARM_MAXc9 | 10min 9th Phase C Current Harmonics Maximum Value | float | 2 | R
0x942D | 0x942E | 37933 | 37934 | CUR_HARM_MAXc10 | 10min 10th Phase C Current Harmonics Maximum Value | float | 2 | R
0x942F | 0x9430 | 37935 | 37936 | CUR_HARM_MAXc11 | 10min 11st Phase C Current Harmonics Maximum Value | float | 2 | R
0x9431 | 0x9432 | 37937 | 37938 | CUR_HARM_MAXc12 | 10min 12nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x9433 | 0x9434 | 37939 | 37940 | CUR_HARM_MAXc13 | 10min 13rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x9435 | 0x9436 | 37941 | 37942 | CUR_HARM_MAXc14 | 10min 14th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9437 | 0x9438 | 37943 | 37944 | CUR_HARM_MAXc15 | 10min 15th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9439 | 0x943A | 37945 | 37946 | CUR_HARM_MAXc16 | 10min 16th Phase C Current Harmonics Maximum Value | float | 2 | R
0x943B | 0x943C | 37947 | 37948 | CUR_HARM_MAXc17 | 10min 17th Phase C Current Harmonics Maximum Value | float | 2 | R
0x943D | 0x943E | 37949 | 37950 | CUR_HARM_MAXc18 | 10min 18th Phase C Current Harmonics Maximum Value | float | 2 | R
0x943F | 0x9440 | 37951 | 37952 | CUR_HARM_MAXc19 | 10min 19th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9441 | 0x9442 | 37953 | 37954 | CUR_HARM_MAXc20 | 10min 20th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9443 | 0x9444 | 37955 | 37956 | CUR_HARM_MAXc21 | 10min 21st Phase C Current Harmonics Maximum Value | float | 2 | R
0x9445 | 0x9446 | 37957 | 37958 | CUR_HARM_MAXc22 | 10min 22nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x9447 | 0x9448 | 37959 | 37960 | CUR_HARM_MAXc23 | 10min 23rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x9449 | 0x944A | 37961 | 37962 | CUR_HARM_MAXc24 | 10min 24th Phase C Current Harmonics Maximum Value | float | 2 | R
0x944B | 0x944C | 37963 | 37964 | CUR_HARM_MAXc25 | 10min 25th Phase C Current Harmonics Maximum Value | float | 2 | R
0x944D | 0x944E | 37965 | 37966 | CUR_HARM_MAXc26 | 10min 26th Phase C Current Harmonics Maximum Value | float | 2 | R
0x944F | 0x9450 | 37967 | 37968 | CUR_HARM_MAXc27 | 10min 27th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9451 | 0x9452 | 37969 | 37970 | CUR_HARM_MAXc28 | 10min 28th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9453 | 0x9454 | 37971 | 37972 | CUR_HARM_MAXc29 | 10min 29th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9455 | 0x9456 | 37973 | 37974 | CUR_HARM_MAXc30 | 10min 30th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9457 | 0x9458 | 37975 | 37976 | CUR_HARM_MAXc31 | 10min 31st Phase C Current Harmonics Maximum Value | float | 2 | R
0x9459 | 0x945A | 37977 | 37978 | CUR_HARM_MAXc32 | 10min 32nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x945B | 0x945C | 37979 | 37980 | CUR_HARM_MAXc33 | 10min 33rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x945D | 0x945E | 37981 | 37982 | CUR_HARM_MAXc34 | 10min 34th Phase C Current Harmonics Maximum Value | float | 2 | R
0x945F | 0x9460 | 37983 | 37984 | CUR_HARM_MAXc35 | 10min 35th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9461 | 0x9462 | 37985 | 37986 | CUR_HARM_MAXc36 | 10min 36th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9463 | 0x9464 | 37987 | 37988 | CUR_HARM_MAXc37 | 10min 37th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9465 | 0x9466 | 37989 | 37990 | CUR_HARM_MAXc38 | 10min 38th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9467 | 0x9468 | 37991 | 37992 | CUR_HARM_MAXc39 | 10min 39th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9469 | 0x946A | 37993 | 37994 | CUR_HARM_MAXc40 | 10min 40th Phase C Current Harmonics Maximum Value | float | 2 | R
0x946B | 0x946C | 37995 | 37996 | CUR_HARM_MAXc41 | 10min 41st Phase C Current Harmonics Maximum Value | float | 2 | R
0x946D | 0x946E | 37997 | 37998 | CUR_HARM_MAXc42 | 10min 42nd Phase C Current Harmonics Maximum Value | float | 2 | R
0x946F | 0x9470 | 37999 | 38000 | CUR_HARM_MAXc43 | 10min 43rd Phase C Current Harmonics Maximum Value | float | 2 | R
0x9471 | 0x9472 | 38001 | 38002 | CUR_HARM_MAXc44 | 10min 44th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9473 | 0x9474 | 38003 | 38004 | CUR_HARM_MAXc45 | 10min 45th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9475 | 0x9476 | 38005 | 38006 | CUR_HARM_MAXc46 | 10min 46th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9477 | 0x9478 | 38007 | 38008 | CUR_HARM_MAXc47 | 10min 47th Phase C Current Harmonics Maximum Value | float | 2 | R
0x9479 | 0x947A | 38009 | 38010 | CUR_HARM_MAXc48 | 10min 48th Phase C Current Harmonics Maximum Value | float | 2 | R
0x947B | 0x947C | 38011 | 38012 | CUR_HARM_MAXc49 | 10min 49th Phase C Current Harmonics Maximum Value | float | 2 | R
0x947D | 0x947E | 38013 | 38014 | CUR_HARM_MAXc50 | 10min 50th Phase C Current Harmonics Maximum Value | float | 2 | R
0x947F | 0x9480 | 38015 | 38016 | CUR_HARM_MINa2 | 10min 2nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x9481 | 0x9482 | 38017 | 38018 | CUR_HARM_MINa3 | 10min 3rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x9483 | 0x9484 | 38019 | 38020 | CUR_HARM_MINa4 | 10min 4th Phase A Current Harmonics Minimum Value | float | 2 | R
0x9485 | 0x9486 | 38021 | 38022 | CUR_HARM_MINa5 | 10min 5th Phase A Current Harmonics Minimum Value | float | 2 | R
0x9487 | 0x9488 | 38023 | 38024 | CUR_HARM_MINa6 | 10min 6th Phase A Current Harmonics Minimum Value | float | 2 | R
0x9489 | 0x948A | 38025 | 38026 | CUR_HARM_MINa7 | 10min 7th Phase A Current Harmonics Minimum Value | float | 2 | R
0x948B | 0x948C | 38027 | 38028 | CUR_HARM_MINa8 | 10min 8th Phase A Current Harmonics Minimum Value | float | 2 | R
0x948D | 0x948E | 38029 | 38030 | CUR_HARM_MINa9 | 10min 9th Phase A Current Harmonics Minimum Value | float | 2 | R
0x948F | 0x9490 | 38031 | 38032 | CUR_HARM_MINa10 | 10min 10th Phase A Current Harmonics Minimum Value | float | 2 | R
0x9491 | 0x9492 | 38033 | 38034 | CUR_HARM_MINa11 | 10min 11st Phase A Current Harmonics Minimum Value | float | 2 | R
0x9493 | 0x9494 | 38035 | 38036 | CUR_HARM_MINa12 | 10min 12nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x9495 | 0x9496 | 38037 | 38038 | CUR_HARM_MINa13 | 10min 13rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x9497 | 0x9498 | 38039 | 38040 | CUR_HARM_MINa14 | 10min 14th Phase A Current Harmonics Minimum Value | float | 2 | R
0x9499 | 0x949A | 38041 | 38042 | CUR_HARM_MINa15 | 10min 15th Phase A Current Harmonics Minimum Value | float | 2 | R
0x949B | 0x949C | 38043 | 38044 | CUR_HARM_MINa16 | 10min 16th Phase A Current Harmonics Minimum Value | float | 2 | R
0x949D | 0x949E | 38045 | 38046 | CUR_HARM_MINa17 | 10min 17th Phase A Current Harmonics Minimum Value | float | 2 | R
0x949F | 0x94A0 | 38047 | 38048 | CUR_HARM_MINa18 | 10min 18th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94A1 | 0x94A2 | 38049 | 38050 | CUR_HARM_MINa19 | 10min 19th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94A3 | 0x94A4 | 38051 | 38052 | CUR_HARM_MINa20 | 10min 20th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94A5 | 0x94A6 | 38053 | 38054 | CUR_HARM_MINa21 | 10min 21st Phase A Current Harmonics Minimum Value | float | 2 | R
0x94A7 | 0x94A8 | 38055 | 38056 | CUR_HARM_MINa22 | 10min 22nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x94A9 | 0x94AA | 38057 | 38058 | CUR_HARM_MINa23 | 10min 23rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x94AB | 0x94AC | 38059 | 38060 | CUR_HARM_MINa24 | 10min 24th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94AD | 0x94AE | 38061 | 38062 | CUR_HARM_MINa25 | 10min 25th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94AF | 0x94B0 | 38063 | 38064 | CUR_HARM_MINa26 | 10min 26th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94B1 | 0x94B2 | 38065 | 38066 | CUR_HARM_MINa27 | 10min 27th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94B3 | 0x94B4 | 38067 | 38068 | CUR_HARM_MINa28 | 10min 28th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94B5 | 0x94B6 | 38069 | 38070 | CUR_HARM_MINa29 | 10min 29th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94B7 | 0x94B8 | 38071 | 38072 | CUR_HARM_MINa30 | 10min 30th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94B9 | 0x94BA | 38073 | 38074 | CUR_HARM_MINa31 | 10min 31st Phase A Current Harmonics Minimum Value | float | 2 | R
0x94BB | 0x94BC | 38075 | 38076 | CUR_HARM_MINa32 | 10min 32nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x94BD | 0x94BE | 38077 | 38078 | CUR_HARM_MINa33 | 10min 33rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x94BF | 0x94C0 | 38079 | 38080 | CUR_HARM_MINa34 | 10min 34th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94C1 | 0x94C2 | 38081 | 38082 | CUR_HARM_MINa35 | 10min 35th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94C3 | 0x94C4 | 38083 | 38084 | CUR_HARM_MINa36 | 10min 36th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94C5 | 0x94C6 | 38085 | 38086 | CUR_HARM_MINa37 | 10min 37th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94C7 | 0x94C8 | 38087 | 38088 | CUR_HARM_MINa38 | 10min 38th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94C9 | 0x94CA | 38089 | 38090 | CUR_HARM_MINa39 | 10min 39th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94CB | 0x94CC | 38091 | 38092 | CUR_HARM_MINa40 | 10min 40th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94CD | 0x94CE | 38093 | 38094 | CUR_HARM_MINa41 | 10min 41st Phase A Current Harmonics Minimum Value | float | 2 | R
0x94CF | 0x94D0 | 38095 | 38096 | CUR_HARM_MINa42 | 10min 42nd Phase A Current Harmonics Minimum Value | float | 2 | R
0x94D1 | 0x94D2 | 38097 | 38098 | CUR_HARM_MINa43 | 10min 43rd Phase A Current Harmonics Minimum Value | float | 2 | R
0x94D3 | 0x94D4 | 38099 | 38100 | CUR_HARM_MINa44 | 10min 44th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94D5 | 0x94D6 | 38101 | 38102 | CUR_HARM_MINa45 | 10min 45th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94D7 | 0x94D8 | 38103 | 38104 | CUR_HARM_MINa46 | 10min 46th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94D9 | 0x94DA | 38105 | 38106 | CUR_HARM_MINa47 | 10min 47th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94DB | 0x94DC | 38107 | 38108 | CUR_HARM_MINa48 | 10min 48th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94DD | 0x94DE | 38109 | 38110 | CUR_HARM_MINa49 | 10min 49th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94DF | 0x94E0 | 38111 | 38112 | CUR_HARM_MINa50 | 10min 50th Phase A Current Harmonics Minimum Value | float | 2 | R
0x94E1 | 0x94E2 | 38113 | 38114 | CUR_HARM_MINb2 | 10min 2nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x94E3 | 0x94E4 | 38115 | 38116 | CUR_HARM_MINb3 | 10min 3rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x94E5 | 0x94E6 | 38117 | 38118 | CUR_HARM_MINb4 | 10min 4th Phase B Current Harmonics Minimum Value | float | 2 | R
0x94E7 | 0x94E8 | 38119 | 38120 | CUR_HARM_MINb5 | 10min 5th Phase B Current Harmonics Minimum Value | float | 2 | R
0x94E9 | 0x94EA | 38121 | 38122 | CUR_HARM_MINb6 | 10min 6th Phase B Current Harmonics Minimum Value | float | 2 | R
0x94EB | 0x94EC | 38123 | 38124 | CUR_HARM_MINb7 | 10min 7th Phase B Current Harmonics Minimum Value | float | 2 | R
0x94ED | 0x94EE | 38125 | 38126 | CUR_HARM_MINb8 | 10min 8th Phase B Current Harmonics Minimum Value | float | 2 | R
0x94EF | 0x94F0 | 38127 | 38128 | CUR_HARM_MINb9 | 10min 9th Phase B Current Harmonics Minimum Value | float | 2 | R
0x94F1 | 0x94F2 | 38129 | 38130 | CUR_HARM_MINb10 | 10min 10th Phase B Current Harmonics Minimum Value | float | 2 | R
0x94F3 | 0x94F4 | 38131 | 38132 | CUR_HARM_MINb11 | 10min 11st Phase B Current Harmonics Minimum Value | float | 2 | R
0x94F5 | 0x94F6 | 38133 | 38134 | CUR_HARM_MINb12 | 10min 12nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x94F7 | 0x94F8 | 38135 | 38136 | CUR_HARM_MINb13 | 10min 13rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x94F9 | 0x94FA | 38137 | 38138 | CUR_HARM_MINb14 | 10min 14th Phase B Current Harmonics Minimum Value | float | 2 | R
0x94FB | 0x94FC | 38139 | 38140 | CUR_HARM_MINb15 | 10min 15th Phase B Current Harmonics Minimum Value | float | 2 | R
0x94FD | 0x94FE | 38141 | 38142 | CUR_HARM_MINb16 | 10min 16th Phase B Current Harmonics Minimum Value | float | 2 | R
0x94FF | 0x9500 | 38143 | 38144 | CUR_HARM_MINb17 | 10min 17th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9501 | 0x9502 | 38145 | 38146 | CUR_HARM_MINb18 | 10min 18th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9503 | 0x9504 | 38147 | 38148 | CUR_HARM_MINb19 | 10min 19th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9505 | 0x9506 | 38149 | 38150 | CUR_HARM_MINb20 | 10min 20th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9507 | 0x9508 | 38151 | 38152 | CUR_HARM_MINb21 | 10min 21st Phase B Current Harmonics Minimum Value | float | 2 | R
0x9509 | 0x950A | 38153 | 38154 | CUR_HARM_MINb22 | 10min 22nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x950B | 0x950C | 38155 | 38156 | CUR_HARM_MINb23 | 10min 23rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x950D | 0x950E | 38157 | 38158 | CUR_HARM_MINb24 | 10min 24th Phase B Current Harmonics Minimum Value | float | 2 | R
0x950F | 0x9510 | 38159 | 38160 | CUR_HARM_MINb25 | 10min 25th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9511 | 0x9512 | 38161 | 38162 | CUR_HARM_MINb26 | 10min 26th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9513 | 0x9514 | 38163 | 38164 | CUR_HARM_MINb27 | 10min 27th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9515 | 0x9516 | 38165 | 38166 | CUR_HARM_MINb28 | 10min 28th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9517 | 0x9518 | 38167 | 38168 | CUR_HARM_MINb29 | 10min 29th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9519 | 0x951A | 38169 | 38170 | CUR_HARM_MINb30 | 10min 30th Phase B Current Harmonics Minimum Value | float | 2 | R
0x951B | 0x951C | 38171 | 38172 | CUR_HARM_MINb31 | 10min 31st Phase B Current Harmonics Minimum Value | float | 2 | R
0x951D | 0x951E | 38173 | 38174 | CUR_HARM_MINb32 | 10min 32nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x951F | 0x9520 | 38175 | 38176 | CUR_HARM_MINb33 | 10min 33rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x9521 | 0x9522 | 38177 | 38178 | CUR_HARM_MINb34 | 10min 34th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9523 | 0x9524 | 38179 | 38180 | CUR_HARM_MINb35 | 10min 35th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9525 | 0x9526 | 38181 | 38182 | CUR_HARM_MINb36 | 10min 36th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9527 | 0x9528 | 38183 | 38184 | CUR_HARM_MINb37 | 10min 37th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9529 | 0x952A | 38185 | 38186 | CUR_HARM_MINb38 | 10min 38th Phase B Current Harmonics Minimum Value | float | 2 | R
0x952B | 0x952C | 38187 | 38188 | CUR_HARM_MINb39 | 10min 39th Phase B Current Harmonics Minimum Value | float | 2 | R
0x952D | 0x952E | 38189 | 38190 | CUR_HARM_MINb40 | 10min 40th Phase B Current Harmonics Minimum Value | float | 2 | R
0x952F | 0x9530 | 38191 | 38192 | CUR_HARM_MINb41 | 10min 41st Phase B Current Harmonics Minimum Value | float | 2 | R
0x9531 | 0x9532 | 38193 | 38194 | CUR_HARM_MINb42 | 10min 42nd Phase B Current Harmonics Minimum Value | float | 2 | R
0x9533 | 0x9534 | 38195 | 38196 | CUR_HARM_MINb43 | 10min 43rd Phase B Current Harmonics Minimum Value | float | 2 | R
0x9535 | 0x9536 | 38197 | 38198 | CUR_HARM_MINb44 | 10min 44th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9537 | 0x9538 | 38199 | 38200 | CUR_HARM_MINb45 | 10min 45th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9539 | 0x953A | 38201 | 38202 | CUR_HARM_MINb46 | 10min 46th Phase B Current Harmonics Minimum Value | float | 2 | R
0x953B | 0x953C | 38203 | 38204 | CUR_HARM_MINb47 | 10min 47th Phase B Current Harmonics Minimum Value | float | 2 | R
0x953D | 0x953E | 38205 | 38206 | CUR_HARM_MINb48 | 10min 48th Phase B Current Harmonics Minimum Value | float | 2 | R
0x953F | 0x9540 | 38207 | 38208 | CUR_HARM_MINb49 | 10min 49th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9541 | 0x9542 | 38209 | 38210 | CUR_HARM_MINb50 | 10min 50th Phase B Current Harmonics Minimum Value | float | 2 | R
0x9543 | 0x9544 | 38211 | 38212 | CUR_HARM_MINc2 | 10min 2nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x9545 | 0x9546 | 38213 | 38214 | CUR_HARM_MINc3 | 10min 3rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x9547 | 0x9548 | 38215 | 38216 | CUR_HARM_MINc4 | 10min 4th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9549 | 0x954A | 38217 | 38218 | CUR_HARM_MINc5 | 10min 5th Phase C Current Harmonics Minimum Value | float | 2 | R
0x954B | 0x954C | 38219 | 38220 | CUR_HARM_MINc6 | 10min 6th Phase C Current Harmonics Minimum Value | float | 2 | R
0x954D | 0x954E | 38221 | 38222 | CUR_HARM_MINc7 | 10min 7th Phase C Current Harmonics Minimum Value | float | 2 | R
0x954F | 0x9550 | 38223 | 38224 | CUR_HARM_MINc8 | 10min 8th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9551 | 0x9552 | 38225 | 38226 | CUR_HARM_MINc9 | 10min 9th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9553 | 0x9554 | 38227 | 38228 | CUR_HARM_MINc10 | 10min 10th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9555 | 0x9556 | 38229 | 38230 | CUR_HARM_MINc11 | 10min 11st Phase C Current Harmonics Minimum Value | float | 2 | R
0x9557 | 0x9558 | 38231 | 38232 | CUR_HARM_MINc12 | 10min 12nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x9559 | 0x955A | 38233 | 38234 | CUR_HARM_MINc13 | 10min 13rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x955B | 0x955C | 38235 | 38236 | CUR_HARM_MINc14 | 10min 14th Phase C Current Harmonics Minimum Value | float | 2 | R
0x955D | 0x955E | 38237 | 38238 | CUR_HARM_MINc15 | 10min 15th Phase C Current Harmonics Minimum Value | float | 2 | R
0x955F | 0x9560 | 38239 | 38240 | CUR_HARM_MINc16 | 10min 16th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9561 | 0x9562 | 38241 | 38242 | CUR_HARM_MINc17 | 10min 17th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9563 | 0x9564 | 38243 | 38244 | CUR_HARM_MINc18 | 10min 18th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9565 | 0x9566 | 38245 | 38246 | CUR_HARM_MINc19 | 10min 19th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9567 | 0x9568 | 38247 | 38248 | CUR_HARM_MINc20 | 10min 20th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9569 | 0x956A | 38249 | 38250 | CUR_HARM_MINc21 | 10min 21st Phase C Current Harmonics Minimum Value | float | 2 | R
0x956B | 0x956C | 38251 | 38252 | CUR_HARM_MINc22 | 10min 22nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x956D | 0x956E | 38253 | 38254 | CUR_HARM_MINc23 | 10min 23rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x956F | 0x9570 | 38255 | 38256 | CUR_HARM_MINc24 | 10min 24th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9571 | 0x9572 | 38257 | 38258 | CUR_HARM_MINc25 | 10min 25th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9573 | 0x9574 | 38259 | 38260 | CUR_HARM_MINc26 | 10min 26th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9575 | 0x9576 | 38261 | 38262 | CUR_HARM_MINc27 | 10min 27th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9577 | 0x9578 | 38263 | 38264 | CUR_HARM_MINc28 | 10min 28th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9579 | 0x957A | 38265 | 38266 | CUR_HARM_MINc29 | 10min 29th Phase C Current Harmonics Minimum Value | float | 2 | R
0x957B | 0x957C | 38267 | 38268 | CUR_HARM_MINc30 | 10min 30th Phase C Current Harmonics Minimum Value | float | 2 | R
0x957D | 0x957E | 38269 | 38270 | CUR_HARM_MINc31 | 10min 31st Phase C Current Harmonics Minimum Value | float | 2 | R
0x957F | 0x9580 | 38271 | 38272 | CUR_HARM_MINc32 | 10min 32nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x9581 | 0x9582 | 38273 | 38274 | CUR_HARM_MINc33 | 10min 33rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x9583 | 0x9584 | 38275 | 38276 | CUR_HARM_MINc34 | 10min 34th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9585 | 0x9586 | 38277 | 38278 | CUR_HARM_MINc35 | 10min 35th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9587 | 0x9588 | 38279 | 38280 | CUR_HARM_MINc36 | 10min 36th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9589 | 0x958A | 38281 | 38282 | CUR_HARM_MINc37 | 10min 37th Phase C Current Harmonics Minimum Value | float | 2 | R
0x958B | 0x958C | 38283 | 38284 | CUR_HARM_MINc38 | 10min 38th Phase C Current Harmonics Minimum Value | float | 2 | R
0x958D | 0x958E | 38285 | 38286 | CUR_HARM_MINc39 | 10min 39th Phase C Current Harmonics Minimum Value | float | 2 | R
0x958F | 0x9590 | 38287 | 38288 | CUR_HARM_MINc40 | 10min 40th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9591 | 0x9592 | 38289 | 38290 | CUR_HARM_MINc41 | 10min 41st Phase C Current Harmonics Minimum Value | float | 2 | R
0x9593 | 0x9594 | 38291 | 38292 | CUR_HARM_MINc42 | 10min 42nd Phase C Current Harmonics Minimum Value | float | 2 | R
0x9595 | 0x9596 | 38293 | 38294 | CUR_HARM_MINc43 | 10min 43rd Phase C Current Harmonics Minimum Value | float | 2 | R
0x9597 | 0x9598 | 38295 | 38296 | CUR_HARM_MINc44 | 10min 44th Phase C Current Harmonics Minimum Value | float | 2 | R
0x9599 | 0x959A | 38297 | 38298 | CUR_HARM_MINc45 | 10min 45th Phase C Current Harmonics Minimum Value | float | 2 | R
0x959B | 0x959C | 38299 | 38300 | CUR_HARM_MINc46 | 10min 46th Phase C Current Harmonics Minimum Value | float | 2 | R
0x959D | 0x959E | 38301 | 38302 | CUR_HARM_MINc47 | 10min 47th Phase C Current Harmonics Minimum Value | float | 2 | R
0x959F | 0x95A0 | 38303 | 38304 | CUR_HARM_MINc48 | 10min 48th Phase C Current Harmonics Minimum Value | float | 2 | R
0x95A1 | 0x95A2 | 38305 | 38306 | CUR_HARM_MINc49 | 10min 49th Phase C Current Harmonics Minimum Value | float | 2 | R
0x95A3 | 0x95A4 | 38307 | 38308 | CUR_HARM_MINc50 | 10min 50th Phase C Current Harmonics Minimum Value | float | 2 | R
0x95A5 | 0x95A6 | 38309 | 38310 | CUR_HARM_AVGa2 | 10min 2nd Phase A Current Harmonics Average Value | float | 2 | R
0x95A7 | 0x95A8 | 38311 | 38312 | CUR_HARM_AVGa3 | 10min 3rd Phase A Current Harmonics Average Value | float | 2 | R
0x95A9 | 0x95AA | 38313 | 38314 | CUR_HARM_AVGa4 | 10min 4th Phase A Current Harmonics Average Value | float | 2 | R
0x95AB | 0x95AC | 38315 | 38316 | CUR_HARM_AVGa5 | 10min 5th Phase A Current Harmonics Average Value | float | 2 | R
0x95AD | 0x95AE | 38317 | 38318 | CUR_HARM_AVGa6 | 10min 6th Phase A Current Harmonics Average Value | float | 2 | R
0x95AF | 0x95B0 | 38319 | 38320 | CUR_HARM_AVGa7 | 10min 7th Phase A Current Harmonics Average Value | float | 2 | R
0x95B1 | 0x95B2 | 38321 | 38322 | CUR_HARM_AVGa8 | 10min 8th Phase A Current Harmonics Average Value | float | 2 | R
0x95B3 | 0x95B4 | 38323 | 38324 | CUR_HARM_AVGa9 | 10min 9th Phase A Current Harmonics Average Value | float | 2 | R
0x95B5 | 0x95B6 | 38325 | 38326 | CUR_HARM_AVGa10 | 10min 10th Phase A Current Harmonics Average Value | float | 2 | R
0x95B7 | 0x95B8 | 38327 | 38328 | CUR_HARM_AVGa11 | 10min 11st Phase A Current Harmonics Average Value | float | 2 | R
0x95B9 | 0x95BA | 38329 | 38330 | CUR_HARM_AVGa12 | 10min 12nd Phase A Current Harmonics Average Value | float | 2 | R
0x95BB | 0x95BC | 38331 | 38332 | CUR_HARM_AVGa13 | 10min 13rd Phase A Current Harmonics Average Value | float | 2 | R
0x95BD | 0x95BE | 38333 | 38334 | CUR_HARM_AVGa14 | 10min 14th Phase A Current Harmonics Average Value | float | 2 | R
0x95BF | 0x95C0 | 38335 | 38336 | CUR_HARM_AVGa15 | 10min 15th Phase A Current Harmonics Average Value | float | 2 | R
0x95C1 | 0x95C2 | 38337 | 38338 | CUR_HARM_AVGa16 | 10min 16th Phase A Current Harmonics Average Value | float | 2 | R
0x95C3 | 0x95C4 | 38339 | 38340 | CUR_HARM_AVGa17 | 10min 17th Phase A Current Harmonics Average Value | float | 2 | R
0x95C5 | 0x95C6 | 38341 | 38342 | CUR_HARM_AVGa18 | 10min 18th Phase A Current Harmonics Average Value | float | 2 | R
0x95C7 | 0x95C8 | 38343 | 38344 | CUR_HARM_AVGa19 | 10min 19th Phase A Current Harmonics Average Value | float | 2 | R
0x95C9 | 0x95CA | 38345 | 38346 | CUR_HARM_AVGa20 | 10min 20th Phase A Current Harmonics Average Value | float | 2 | R
0x95CB | 0x95CC | 38347 | 38348 | CUR_HARM_AVGa21 | 10min 21st Phase A Current Harmonics Average Value | float | 2 | R
0x95CD | 0x95CE | 38349 | 38350 | CUR_HARM_AVGa22 | 10min 22nd Phase A Current Harmonics Average Value | float | 2 | R
0x95CF | 0x95D0 | 38351 | 38352 | CUR_HARM_AVGa23 | 10min 23rd Phase A Current Harmonics Average Value | float | 2 | R
0x95D1 | 0x95D2 | 38353 | 38354 | CUR_HARM_AVGa24 | 10min 24th Phase A Current Harmonics Average Value | float | 2 | R
0x95D3 | 0x95D4 | 38355 | 38356 | CUR_HARM_AVGa25 | 10min 25th Phase A Current Harmonics Average Value | float | 2 | R
0x95D5 | 0x95D6 | 38357 | 38358 | CUR_HARM_AVGa26 | 10min 26th Phase A Current Harmonics Average Value | float | 2 | R
0x95D7 | 0x95D8 | 38359 | 38360 | CUR_HARM_AVGa27 | 10min 27th Phase A Current Harmonics Average Value | float | 2 | R
0x95D9 | 0x95DA | 38361 | 38362 | CUR_HARM_AVGa28 | 10min 28th Phase A Current Harmonics Average Value | float | 2 | R
0x95DB | 0x95DC | 38363 | 38364 | CUR_HARM_AVGa29 | 10min 29th Phase A Current Harmonics Average Value | float | 2 | R
0x95DD | 0x95DE | 38365 | 38366 | CUR_HARM_AVGa30 | 10min 30th Phase A Current Harmonics Average Value | float | 2 | R
0x95DF | 0x95E0 | 38367 | 38368 | CUR_HARM_AVGa31 | 10min 31st Phase A Current Harmonics Average Value | float | 2 | R
0x95E1 | 0x95E2 | 38369 | 38370 | CUR_HARM_AVGa32 | 10min 32nd Phase A Current Harmonics Average Value | float | 2 | R
0x95E3 | 0x95E4 | 38371 | 38372 | CUR_HARM_AVGa33 | 10min 33rd Phase A Current Harmonics Average Value | float | 2 | R
0x95E5 | 0x95E6 | 38373 | 38374 | CUR_HARM_AVGa34 | 10min 34th Phase A Current Harmonics Average Value | float | 2 | R
0x95E7 | 0x95E8 | 38375 | 38376 | CUR_HARM_AVGa35 | 10min 35th Phase A Current Harmonics Average Value | float | 2 | R
0x95E9 | 0x95EA | 38377 | 38378 | CUR_HARM_AVGa36 | 10min 36th Phase A Current Harmonics Average Value | float | 2 | R
0x95EB | 0x95EC | 38379 | 38380 | CUR_HARM_AVGa37 | 10min 37th Phase A Current Harmonics Average Value | float | 2 | R
0x95ED | 0x95EE | 38381 | 38382 | CUR_HARM_AVGa38 | 10min 38th Phase A Current Harmonics Average Value | float | 2 | R
0x95EF | 0x95F0 | 38383 | 38384 | CUR_HARM_AVGa39 | 10min 39th Phase A Current Harmonics Average Value | float | 2 | R
0x95F1 | 0x95F2 | 38385 | 38386 | CUR_HARM_AVGa40 | 10min 40th Phase A Current Harmonics Average Value | float | 2 | R
0x95F3 | 0x95F4 | 38387 | 38388 | CUR_HARM_AVGa41 | 10min 41st Phase A Current Harmonics Average Value | float | 2 | R
0x95F5 | 0x95F6 | 38389 | 38390 | CUR_HARM_AVGa42 | 10min 42nd Phase A Current Harmonics Average Value | float | 2 | R
0x95F7 | 0x95F8 | 38391 | 38392 | CUR_HARM_AVGa43 | 10min 43rd Phase A Current Harmonics Average Value | float | 2 | R
0x95F9 | 0x95FA | 38393 | 38394 | CUR_HARM_AVGa44 | 10min 44th Phase A Current Harmonics Average Value | float | 2 | R
0x95FB | 0x95FC | 38395 | 38396 | CUR_HARM_AVGa45 | 10min 45th Phase A Current Harmonics Average Value | float | 2 | R
0x95FD | 0x95FE | 38397 | 38398 | CUR_HARM_AVGa46 | 10min 46th Phase A Current Harmonics Average Value | float | 2 | R
0x95FF | 0x9600 | 38399 | 38400 | CUR_HARM_AVGa47 | 10min 47th Phase A Current Harmonics Average Value | float | 2 | R
0x9601 | 0x9602 | 38401 | 38402 | CUR_HARM_AVGa48 | 10min 48th Phase A Current Harmonics Average Value | float | 2 | R
0x9603 | 0x9604 | 38403 | 38404 | CUR_HARM_AVGa49 | 10min 49th Phase A Current Harmonics Average Value | float | 2 | R
0x9605 | 0x9606 | 38405 | 38406 | CUR_HARM_AVGa50 | 10min 50th Phase A Current Harmonics Average Value | float | 2 | R
0x9607 | 0x9608 | 38407 | 38408 | CUR_HARM_AVGb2 | 10min 2nd Phase B Current Harmonics Average Value | float | 2 | R
0x9609 | 0x960A | 38409 | 38410 | CUR_HARM_AVGb3 | 10min 3rd Phase B Current Harmonics Average Value | float | 2 | R
0x960B | 0x960C | 38411 | 38412 | CUR_HARM_AVGb4 | 10min 4th Phase B Current Harmonics Average Value | float | 2 | R
0x960D | 0x960E | 38413 | 38414 | CUR_HARM_AVGb5 | 10min 5th Phase B Current Harmonics Average Value | float | 2 | R
0x960F | 0x9610 | 38415 | 38416 | CUR_HARM_AVGb6 | 10min 6th Phase B Current Harmonics Average Value | float | 2 | R
0x9611 | 0x9612 | 38417 | 38418 | CUR_HARM_AVGb7 | 10min 7th Phase B Current Harmonics Average Value | float | 2 | R
0x9613 | 0x9614 | 38419 | 38420 | CUR_HARM_AVGb8 | 10min 8th Phase B Current Harmonics Average Value | float | 2 | R
0x9615 | 0x9616 | 38421 | 38422 | CUR_HARM_AVGb9 | 10min 9th Phase B Current Harmonics Average Value | float | 2 | R
0x9617 | 0x9618 | 38423 | 38424 | CUR_HARM_AVGb10 | 10min 10th Phase B Current Harmonics Average Value | float | 2 | R
0x9619 | 0x961A | 38425 | 38426 | CUR_HARM_AVGb11 | 10min 11st Phase B Current Harmonics Average Value | float | 2 | R
0x961B | 0x961C | 38427 | 38428 | CUR_HARM_AVGb12 | 10min 12nd Phase B Current Harmonics Average Value | float | 2 | R
0x961D | 0x961E | 38429 | 38430 | CUR_HARM_AVGb13 | 10min 13rd Phase B Current Harmonics Average Value | float | 2 | R
0x961F | 0x9620 | 38431 | 38432 | CUR_HARM_AVGb14 | 10min 14th Phase B Current Harmonics Average Value | float | 2 | R
0x9621 | 0x9622 | 38433 | 38434 | CUR_HARM_AVGb15 | 10min 15th Phase B Current Harmonics Average Value | float | 2 | R
0x9623 | 0x9624 | 38435 | 38436 | CUR_HARM_AVGb16 | 10min 16th Phase B Current Harmonics Average Value | float | 2 | R
0x9625 | 0x9626 | 38437 | 38438 | CUR_HARM_AVGb17 | 10min 17th Phase B Current Harmonics Average Value | float | 2 | R
0x9627 | 0x9628 | 38439 | 38440 | CUR_HARM_AVGb18 | 10min 18th Phase B Current Harmonics Average Value | float | 2 | R
0x9629 | 0x962A | 38441 | 38442 | CUR_HARM_AVGb19 | 10min 19th Phase B Current Harmonics Average Value | float | 2 | R
0x962B | 0x962C | 38443 | 38444 | CUR_HARM_AVGb20 | 10min 20th Phase B Current Harmonics Average Value | float | 2 | R
0x962D | 0x962E | 38445 | 38446 | CUR_HARM_AVGb21 | 10min 21st Phase B Current Harmonics Average Value | float | 2 | R
0x962F | 0x9630 | 38447 | 38448 | CUR_HARM_AVGb22 | 10min 22nd Phase B Current Harmonics Average Value | float | 2 | R
0x9631 | 0x9632 | 38449 | 38450 | CUR_HARM_AVGb23 | 10min 23rd Phase B Current Harmonics Average Value | float | 2 | R
0x9633 | 0x9634 | 38451 | 38452 | CUR_HARM_AVGb24 | 10min 24th Phase B Current Harmonics Average Value | float | 2 | R
0x9635 | 0x9636 | 38453 | 38454 | CUR_HARM_AVGb25 | 10min 25th Phase B Current Harmonics Average Value | float | 2 | R
0x9637 | 0x9638 | 38455 | 38456 | CUR_HARM_AVGb26 | 10min 26th Phase B Current Harmonics Average Value | float | 2 | R
0x9639 | 0x963A | 38457 | 38458 | CUR_HARM_AVGb27 | 10min 27th Phase B Current Harmonics Average Value | float | 2 | R
0x963B | 0x963C | 38459 | 38460 | CUR_HARM_AVGb28 | 10min 28th Phase B Current Harmonics Average Value | float | 2 | R
0x963D | 0x963E | 38461 | 38462 | CUR_HARM_AVGb29 | 10min 29th Phase B Current Harmonics Average Value | float | 2 | R
0x963F | 0x9640 | 38463 | 38464 | CUR_HARM_AVGb30 | 10min 30th Phase B Current Harmonics Average Value | float | 2 | R
0x9641 | 0x9642 | 38465 | 38466 | CUR_HARM_AVGb31 | 10min 31st Phase B Current Harmonics Average Value | float | 2 | R
0x9643 | 0x9644 | 38467 | 38468 | CUR_HARM_AVGb32 | 10min 32nd Phase B Current Harmonics Average Value | float | 2 | R
0x9645 | 0x9646 | 38469 | 38470 | CUR_HARM_AVGb33 | 10min 33rd Phase B Current Harmonics Average Value | float | 2 | R
0x9647 | 0x9648 | 38471 | 38472 | CUR_HARM_AVGb34 | 10min 34th Phase B Current Harmonics Average Value | float | 2 | R
0x9649 | 0x964A | 38473 | 38474 | CUR_HARM_AVGb35 | 10min 35th Phase B Current Harmonics Average Value | float | 2 | R
0x964B | 0x964C | 38475 | 38476 | CUR_HARM_AVGb36 | 10min 36th Phase B Current Harmonics Average Value | float | 2 | R
0x964D | 0x964E | 38477 | 38478 | CUR_HARM_AVGb37 | 10min 37th Phase B Current Harmonics Average Value | float | 2 | R
0x964F | 0x9650 | 38479 | 38480 | CUR_HARM_AVGb38 | 10min 38th Phase B Current Harmonics Average Value | float | 2 | R
0x9651 | 0x9652 | 38481 | 38482 | CUR_HARM_AVGb39 | 10min 39th Phase B Current Harmonics Average Value | float | 2 | R
0x9653 | 0x9654 | 38483 | 38484 | CUR_HARM_AVGb40 | 10min 40th Phase B Current Harmonics Average Value | float | 2 | R
0x9655 | 0x9656 | 38485 | 38486 | CUR_HARM_AVGb41 | 10min 41st Phase B Current Harmonics Average Value | float | 2 | R
0x9657 | 0x9658 | 38487 | 38488 | CUR_HARM_AVGb42 | 10min 42nd Phase B Current Harmonics Average Value | float | 2 | R
0x9659 | 0x965A | 38489 | 38490 | CUR_HARM_AVGb43 | 10min 43rd Phase B Current Harmonics Average Value | float | 2 | R
0x965B | 0x965C | 38491 | 38492 | CUR_HARM_AVGb44 | 10min 44th Phase B Current Harmonics Average Value | float | 2 | R
0x965D | 0x965E | 38493 | 38494 | CUR_HARM_AVGb45 | 10min 45th Phase B Current Harmonics Average Value | float | 2 | R
0x965F | 0x9660 | 38495 | 38496 | CUR_HARM_AVGb46 | 10min 46th Phase B Current Harmonics Average Value | float | 2 | R
0x9661 | 0x9662 | 38497 | 38498 | CUR_HARM_AVGb47 | 10min 47th Phase B Current Harmonics Average Value | float | 2 | R
0x9663 | 0x9664 | 38499 | 38500 | CUR_HARM_AVGb48 | 10min 48th Phase B Current Harmonics Average Value | float | 2 | R
0x9665 | 0x9666 | 38501 | 38502 | CUR_HARM_AVGb49 | 10min 49th Phase B Current Harmonics Average Value | float | 2 | R
0x9667 | 0x9668 | 38503 | 38504 | CUR_HARM_AVGb50 | 10min 50th Phase B Current Harmonics Average Value | float | 2 | R
0x9669 | 0x966A | 38505 | 38506 | CUR_HARM_AVGc2 | 10min 2nd Phase C Current Harmonics Average Value | float | 2 | R
0x966B | 0x966C | 38507 | 38508 | CUR_HARM_AVGc3 | 10min 3rd Phase C Current Harmonics Average Value | float | 2 | R
0x966D | 0x966E | 38509 | 38510 | CUR_HARM_AVGc4 | 10min 4th Phase C Current Harmonics Average Value | float | 2 | R
0x966F | 0x9670 | 38511 | 38512 | CUR_HARM_AVGc5 | 10min 5th Phase C Current Harmonics Average Value | float | 2 | R
0x9671 | 0x9672 | 38513 | 38514 | CUR_HARM_AVGc6 | 10min 6th Phase C Current Harmonics Average Value | float | 2 | R
0x9673 | 0x9674 | 38515 | 38516 | CUR_HARM_AVGc7 | 10min 7th Phase C Current Harmonics Average Value | float | 2 | R
0x9675 | 0x9676 | 38517 | 38518 | CUR_HARM_AVGc8 | 10min 8th Phase C Current Harmonics Average Value | float | 2 | R
0x9677 | 0x9678 | 38519 | 38520 | CUR_HARM_AVGc9 | 10min 9th Phase C Current Harmonics Average Value | float | 2 | R
0x9679 | 0x967A | 38521 | 38522 | CUR_HARM_AVGc10 | 10min 10th Phase C Current Harmonics Average Value | float | 2 | R
0x967B | 0x967C | 38523 | 38524 | CUR_HARM_AVGc11 | 10min 11st Phase C Current Harmonics Average Value | float | 2 | R
0x967D | 0x967E | 38525 | 38526 | CUR_HARM_AVGc12 | 10min 12nd Phase C Current Harmonics Average Value | float | 2 | R
0x967F | 0x9680 | 38527 | 38528 | CUR_HARM_AVGc13 | 10min 13rd Phase C Current Harmonics Average Value | float | 2 | R
0x9681 | 0x9682 | 38529 | 38530 | CUR_HARM_AVGc14 | 10min 14th Phase C Current Harmonics Average Value | float | 2 | R
0x9683 | 0x9684 | 38531 | 38532 | CUR_HARM_AVGc15 | 10min 15th Phase C Current Harmonics Average Value | float | 2 | R
0x9685 | 0x9686 | 38533 | 38534 | CUR_HARM_AVGc16 | 10min 16th Phase C Current Harmonics Average Value | float | 2 | R
0x9687 | 0x9688 | 38535 | 38536 | CUR_HARM_AVGc17 | 10min 17th Phase C Current Harmonics Average Value | float | 2 | R
0x9689 | 0x968A | 38537 | 38538 | CUR_HARM_AVGc18 | 10min 18th Phase C Current Harmonics Average Value | float | 2 | R
0x968B | 0x968C | 38539 | 38540 | CUR_HARM_AVGc19 | 10min 19th Phase C Current Harmonics Average Value | float | 2 | R
0x968D | 0x968E | 38541 | 38542 | CUR_HARM_AVGc20 | 10min 20th Phase C Current Harmonics Average Value | float | 2 | R
0x968F | 0x9690 | 38543 | 38544 | CUR_HARM_AVGc21 | 10min 21st Phase C Current Harmonics Average Value | float | 2 | R
0x9691 | 0x9692 | 38545 | 38546 | CUR_HARM_AVGc22 | 10min 22nd Phase C Current Harmonics Average Value | float | 2 | R
0x9693 | 0x9694 | 38547 | 38548 | CUR_HARM_AVGc23 | 10min 23rd Phase C Current Harmonics Average Value | float | 2 | R
0x9695 | 0x9696 | 38549 | 38550 | CUR_HARM_AVGc24 | 10min 24th Phase C Current Harmonics Average Value | float | 2 | R
0x9697 | 0x9698 | 38551 | 38552 | CUR_HARM_AVGc25 | 10min 25th Phase C Current Harmonics Average Value | float | 2 | R
0x9699 | 0x969A | 38553 | 38554 | CUR_HARM_AVGc26 | 10min 26th Phase C Current Harmonics Average Value | float | 2 | R
0x969B | 0x969C | 38555 | 38556 | CUR_HARM_AVGc27 | 10min 27th Phase C Current Harmonics Average Value | float | 2 | R
0x969D | 0x969E | 38557 | 38558 | CUR_HARM_AVGc28 | 10min 28th Phase C Current Harmonics Average Value | float | 2 | R
0x969F | 0x96A0 | 38559 | 38560 | CUR_HARM_AVGc29 | 10min 29th Phase C Current Harmonics Average Value | float | 2 | R
0x96A1 | 0x96A2 | 38561 | 38562 | CUR_HARM_AVGc30 | 10min 30th Phase C Current Harmonics Average Value | float | 2 | R
0x96A3 | 0x96A4 | 38563 | 38564 | CUR_HARM_AVGc31 | 10min 31st Phase C Current Harmonics Average Value | float | 2 | R
0x96A5 | 0x96A6 | 38565 | 38566 | CUR_HARM_AVGc32 | 10min 32nd Phase C Current Harmonics Average Value | float | 2 | R
0x96A7 | 0x96A8 | 38567 | 38568 | CUR_HARM_AVGc33 | 10min 33rd Phase C Current Harmonics Average Value | float | 2 | R
0x96A9 | 0x96AA | 38569 | 38570 | CUR_HARM_AVGc34 | 10min 34th Phase C Current Harmonics Average Value | float | 2 | R
0x96AB | 0x96AC | 38571 | 38572 | CUR_HARM_AVGc35 | 10min 35th Phase C Current Harmonics Average Value | float | 2 | R
0x96AD | 0x96AE | 38573 | 38574 | CUR_HARM_AVGc36 | 10min 36th Phase C Current Harmonics Average Value | float | 2 | R
0x96AF | 0x96B0 | 38575 | 38576 | CUR_HARM_AVGc37 | 10min 37th Phase C Current Harmonics Average Value | float | 2 | R
0x96B1 | 0x96B2 | 38577 | 38578 | CUR_HARM_AVGc38 | 10min 38th Phase C Current Harmonics Average Value | float | 2 | R
0x96B3 | 0x96B4 | 38579 | 38580 | CUR_HARM_AVGc39 | 10min 39th Phase C Current Harmonics Average Value | float | 2 | R
0x96B5 | 0x96B6 | 38581 | 38582 | CUR_HARM_AVGc40 | 10min 40th Phase C Current Harmonics Average Value | float | 2 | R
0x96B7 | 0x96B8 | 38583 | 38584 | CUR_HARM_AVGc41 | 10min 41st Phase C Current Harmonics Average Value | float | 2 | R
0x96B9 | 0x96BA | 38585 | 38586 | CUR_HARM_AVGc42 | 10min 42nd Phase C Current Harmonics Average Value | float | 2 | R
0x96BB | 0x96BC | 38587 | 38588 | CUR_HARM_AVGc43 | 10min 43rd Phase C Current Harmonics Average Value | float | 2 | R
0x96BD | 0x96BE | 38589 | 38590 | CUR_HARM_AVGc44 | 10min 44th Phase C Current Harmonics Average Value | float | 2 | R
0x96BF | 0x96C0 | 38591 | 38592 | CUR_HARM_AVGc45 | 10min 45th Phase C Current Harmonics Average Value | float | 2 | R
0x96C1 | 0x96C2 | 38593 | 38594 | CUR_HARM_AVGc46 | 10min 46th Phase C Current Harmonics Average Value | float | 2 | R
0x96C3 | 0x96C4 | 38595 | 38596 | CUR_HARM_AVGc47 | 10min 47th Phase C Current Harmonics Average Value | float | 2 | R
0x96C5 | 0x96C6 | 38597 | 38598 | CUR_HARM_AVGc48 | 10min 48th Phase C Current Harmonics Average Value | float | 2 | R
0x96C7 | 0x96C8 | 38599 | 38600 | CUR_HARM_AVGc49 | 10min 49th Phase C Current Harmonics Average Value | float | 2 | R
0x96C9 | 0x96CA | 38601 | 38602 | CUR_HARM_AVGc50 | 10min 50th Phase C Current Harmonics Average Value | float | 2 | R
0x96CB | 0x96CB | 38603 | 38603 | N_TDD_95a | 10min Phase A TDD Counter for 95% Trigger Limit | uint16 | 1 | R
0x96CC | 0x96CC | 38604 | 38604 | N_TDD_95b | 10min Phase B TDD Counter for 95% Trigger Limit | uint16 | 1 | R
0x96CD | 0x96CD | 38605 | 38605 | N_TDD_95c | 10min Phase C TDD Counter for 95% Trigger Limit | uint16 | 1 | R
0x96CE | 0x96CF | 38606 | 38607 | TDD_95_PASSa | 10min Phase A TDD Trigger Pass Rate for 95% Trigger Limit | float | 2 | R
0x96D0 | 0x96D1 | 38608 | 38609 | TDD_95_PASSb | 10min Phase B TDD Trigger Pass Rate for 95% Trigger Limit | float | 2 | R
0x96D2 | 0x96D3 | 38610 | 38611 | TDD_95_PASSc | 10min Phase C TDD Trigger Pass Rate for 95% Trigger Limit | float | 2 | R
0x96D4 | 0x96D4 | 38612 | 38612 | N_CUR_HARM_95a2 | 10min 2nd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96D5 | 0x96D5 | 38613 | 38613 | N_CUR_HARM_95a3 | 10min 3rd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96D6 | 0x96D6 | 38614 | 38614 | N_CUR_HARM_95a4 | 10min 4th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96D7 | 0x96D7 | 38615 | 38615 | N_CUR_HARM_95a5 | 10min 5th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96D8 | 0x96D8 | 38616 | 38616 | N_CUR_HARM_95a6 | 10min 6th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96D9 | 0x96D9 | 38617 | 38617 | N_CUR_HARM_95a7 | 10min 7th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96DA | 0x96DA | 38618 | 38618 | N_CUR_HARM_95a8 | 10min 8th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96DB | 0x96DB | 38619 | 38619 | N_CUR_HARM_95a9 | 10min 9th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96DC | 0x96DC | 38620 | 38620 | N_CUR_HARM_95a10 | 10min 10th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96DD | 0x96DD | 38621 | 38621 | N_CUR_HARM_95a11 | 10min 11st Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96DE | 0x96DE | 38622 | 38622 | N_CUR_HARM_95a12 | 10min 12nd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96DF | 0x96DF | 38623 | 38623 | N_CUR_HARM_95a13 | 10min 13rd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96E0 | 0x96E0 | 38624 | 38624 | N_CUR_HARM_95a14 | 10min 14th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96E1 | 0x96E1 | 38625 | 38625 | N_CUR_HARM_95a15 | 10min 15th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96E2 | 0x96E2 | 38626 | 38626 | N_CUR_HARM_95a16 | 10min 16th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96E3 | 0x96E3 | 38627 | 38627 | N_CUR_HARM_95a17 | 10min 17th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96E4 | 0x96E4 | 38628 | 38628 | N_CUR_HARM_95a18 | 10min 18th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96E5 | 0x96E5 | 38629 | 38629 | N_CUR_HARM_95a19 | 10min 19th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96E6 | 0x96E6 | 38630 | 38630 | N_CUR_HARM_95a20 | 10min 20th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96E7 | 0x96E7 | 38631 | 38631 | N_CUR_HARM_95a21 | 10min 21st Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96E8 | 0x96E8 | 38632 | 38632 | N_CUR_HARM_95a22 | 10min 22nd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96E9 | 0x96E9 | 38633 | 38633 | N_CUR_HARM_95a23 | 10min 23rd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96EA | 0x96EA | 38634 | 38634 | N_CUR_HARM_95a24 | 10min 24th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96EB | 0x96EB | 38635 | 38635 | N_CUR_HARM_95a25 | 10min 25th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96EC | 0x96EC | 38636 | 38636 | N_CUR_HARM_95a26 | 10min 26th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96ED | 0x96ED | 38637 | 38637 | N_CUR_HARM_95a27 | 10min 27th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96EE | 0x96EE | 38638 | 38638 | N_CUR_HARM_95a28 | 10min 28th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96EF | 0x96EF | 38639 | 38639 | N_CUR_HARM_95a29 | 10min 29th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96F0 | 0x96F0 | 38640 | 38640 | N_CUR_HARM_95a30 | 10min 30th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96F1 | 0x96F1 | 38641 | 38641 | N_CUR_HARM_95a31 | 10min 31st Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96F2 | 0x96F2 | 38642 | 38642 | N_CUR_HARM_95a32 | 10min 32nd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96F3 | 0x96F3 | 38643 | 38643 | N_CUR_HARM_95a33 | 10min 33rd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96F4 | 0x96F4 | 38644 | 38644 | N_CUR_HARM_95a34 | 10min 34th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96F5 | 0x96F5 | 38645 | 38645 | N_CUR_HARM_95a35 | 10min 35th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96F6 | 0x96F6 | 38646 | 38646 | N_CUR_HARM_95a36 | 10min 36th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96F7 | 0x96F7 | 38647 | 38647 | N_CUR_HARM_95a37 | 10min 37th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96F8 | 0x96F8 | 38648 | 38648 | N_CUR_HARM_95a38 | 10min 38th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96F9 | 0x96F9 | 38649 | 38649 | N_CUR_HARM_95a39 | 10min 39th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96FA | 0x96FA | 38650 | 38650 | N_CUR_HARM_95a40 | 10min 40th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96FB | 0x96FB | 38651 | 38651 | N_CUR_HARM_95a41 | 10min 41st Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96FC | 0x96FC | 38652 | 38652 | N_CUR_HARM_95a42 | 10min 42nd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96FD | 0x96FD | 38653 | 38653 | N_CUR_HARM_95a43 | 10min 43rd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96FE | 0x96FE | 38654 | 38654 | N_CUR_HARM_95a44 | 10min 44th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x96FF | 0x96FF | 38655 | 38655 | N_CUR_HARM_95a45 | 10min 45th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9700 | 0x9700 | 38656 | 38656 | N_CUR_HARM_95a46 | 10min 46th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9701 | 0x9701 | 38657 | 38657 | N_CUR_HARM_95a47 | 10min 47th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9702 | 0x9702 | 38658 | 38658 | N_CUR_HARM_95a48 | 10min 48th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9703 | 0x9703 | 38659 | 38659 | N_CUR_HARM_95a49 | 10min 49th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9704 | 0x9704 | 38660 | 38660 | N_CUR_HARM_95a50 | 10min 50th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9705 | 0x9705 | 38661 | 38661 | N_CUR_HARM_95b2 | 10min 2nd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9706 | 0x9706 | 38662 | 38662 | N_CUR_HARM_95b3 | 10min 3rd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9707 | 0x9707 | 38663 | 38663 | N_CUR_HARM_95b4 | 10min 4th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9708 | 0x9708 | 38664 | 38664 | N_CUR_HARM_95b5 | 10min 5th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9709 | 0x9709 | 38665 | 38665 | N_CUR_HARM_95b6 | 10min 6th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x970A | 0x970A | 38666 | 38666 | N_CUR_HARM_95b7 | 10min 7th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x970B | 0x970B | 38667 | 38667 | N_CUR_HARM_95b8 | 10min 8th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x970C | 0x970C | 38668 | 38668 | N_CUR_HARM_95b9 | 10min 9th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x970D | 0x970D | 38669 | 38669 | N_CUR_HARM_95b10 | 10min 10th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x970E | 0x970E | 38670 | 38670 | N_CUR_HARM_95b11 | 10min 11st Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x970F | 0x970F | 38671 | 38671 | N_CUR_HARM_95b12 | 10min 12nd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9710 | 0x9710 | 38672 | 38672 | N_CUR_HARM_95b13 | 10min 13rd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9711 | 0x9711 | 38673 | 38673 | N_CUR_HARM_95b14 | 10min 14th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9712 | 0x9712 | 38674 | 38674 | N_CUR_HARM_95b15 | 10min 15th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9713 | 0x9713 | 38675 | 38675 | N_CUR_HARM_95b16 | 10min 16th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9714 | 0x9714 | 38676 | 38676 | N_CUR_HARM_95b17 | 10min 17th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9715 | 0x9715 | 38677 | 38677 | N_CUR_HARM_95b18 | 10min 18th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9716 | 0x9716 | 38678 | 38678 | N_CUR_HARM_95b19 | 10min 19th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9717 | 0x9717 | 38679 | 38679 | N_CUR_HARM_95b20 | 10min 20th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9718 | 0x9718 | 38680 | 38680 | N_CUR_HARM_95b21 | 10min 21st Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9719 | 0x9719 | 38681 | 38681 | N_CUR_HARM_95b22 | 10min 22nd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x971A | 0x971A | 38682 | 38682 | N_CUR_HARM_95b23 | 10min 23rd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x971B | 0x971B | 38683 | 38683 | N_CUR_HARM_95b24 | 10min 24th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x971C | 0x971C | 38684 | 38684 | N_CUR_HARM_95b25 | 10min 25th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x971D | 0x971D | 38685 | 38685 | N_CUR_HARM_95b26 | 10min 26th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x971E | 0x971E | 38686 | 38686 | N_CUR_HARM_95b27 | 10min 27th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x971F | 0x971F | 38687 | 38687 | N_CUR_HARM_95b28 | 10min 28th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9720 | 0x9720 | 38688 | 38688 | N_CUR_HARM_95b29 | 10min 29th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9721 | 0x9721 | 38689 | 38689 | N_CUR_HARM_95b30 | 10min 30th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9722 | 0x9722 | 38690 | 38690 | N_CUR_HARM_95b31 | 10min 31st Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9723 | 0x9723 | 38691 | 38691 | N_CUR_HARM_95b32 | 10min 32nd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9724 | 0x9724 | 38692 | 38692 | N_CUR_HARM_95b33 | 10min 33rd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9725 | 0x9725 | 38693 | 38693 | N_CUR_HARM_95b34 | 10min 34th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9726 | 0x9726 | 38694 | 38694 | N_CUR_HARM_95b35 | 10min 35th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9727 | 0x9727 | 38695 | 38695 | N_CUR_HARM_95b36 | 10min 36th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9728 | 0x9728 | 38696 | 38696 | N_CUR_HARM_95b37 | 10min 37th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9729 | 0x9729 | 38697 | 38697 | N_CUR_HARM_95b38 | 10min 38th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x972A | 0x972A | 38698 | 38698 | N_CUR_HARM_95b39 | 10min 39th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x972B | 0x972B | 38699 | 38699 | N_CUR_HARM_95b40 | 10min 40th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x972C | 0x972C | 38700 | 38700 | N_CUR_HARM_95b41 | 10min 41st Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x972D | 0x972D | 38701 | 38701 | N_CUR_HARM_95b42 | 10min 42nd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x972E | 0x972E | 38702 | 38702 | N_CUR_HARM_95b43 | 10min 43rd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x972F | 0x972F | 38703 | 38703 | N_CUR_HARM_95b44 | 10min 44th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9730 | 0x9730 | 38704 | 38704 | N_CUR_HARM_95b45 | 10min 45th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9731 | 0x9731 | 38705 | 38705 | N_CUR_HARM_95b46 | 10min 46th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9732 | 0x9732 | 38706 | 38706 | N_CUR_HARM_95b47 | 10min 47th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9733 | 0x9733 | 38707 | 38707 | N_CUR_HARM_95b48 | 10min 48th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9734 | 0x9734 | 38708 | 38708 | N_CUR_HARM_95b49 | 10min 49th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9735 | 0x9735 | 38709 | 38709 | N_CUR_HARM_95b50 | 10min 50th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9736 | 0x9736 | 38710 | 38710 | N_CUR_HARM_95c2 | 10min 2nd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9737 | 0x9737 | 38711 | 38711 | N_CUR_HARM_95c3 | 10min 3rd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9738 | 0x9738 | 38712 | 38712 | N_CUR_HARM_95c4 | 10min 4th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9739 | 0x9739 | 38713 | 38713 | N_CUR_HARM_95c5 | 10min 5th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x973A | 0x973A | 38714 | 38714 | N_CUR_HARM_95c6 | 10min 6th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x973B | 0x973B | 38715 | 38715 | N_CUR_HARM_95c7 | 10min 7th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x973C | 0x973C | 38716 | 38716 | N_CUR_HARM_95c8 | 10min 8th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x973D | 0x973D | 38717 | 38717 | N_CUR_HARM_95c9 | 10min 9th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x973E | 0x973E | 38718 | 38718 | N_CUR_HARM_95c10 | 10min 10th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x973F | 0x973F | 38719 | 38719 | N_CUR_HARM_95c11 | 10min 11st Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9740 | 0x9740 | 38720 | 38720 | N_CUR_HARM_95c12 | 10min 12nd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9741 | 0x9741 | 38721 | 38721 | N_CUR_HARM_95c13 | 10min 13rd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9742 | 0x9742 | 38722 | 38722 | N_CUR_HARM_95c14 | 10min 14th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9743 | 0x9743 | 38723 | 38723 | N_CUR_HARM_95c15 | 10min 15th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9744 | 0x9744 | 38724 | 38724 | N_CUR_HARM_95c16 | 10min 16th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9745 | 0x9745 | 38725 | 38725 | N_CUR_HARM_95c17 | 10min 17th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9746 | 0x9746 | 38726 | 38726 | N_CUR_HARM_95c18 | 10min 18th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9747 | 0x9747 | 38727 | 38727 | N_CUR_HARM_95c19 | 10min 19th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9748 | 0x9748 | 38728 | 38728 | N_CUR_HARM_95c20 | 10min 20th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9749 | 0x9749 | 38729 | 38729 | N_CUR_HARM_95c21 | 10min 21st Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x974A | 0x974A | 38730 | 38730 | N_CUR_HARM_95c22 | 10min 22nd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x974B | 0x974B | 38731 | 38731 | N_CUR_HARM_95c23 | 10min 23rd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x974C | 0x974C | 38732 | 38732 | N_CUR_HARM_95c24 | 10min 24th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x974D | 0x974D | 38733 | 38733 | N_CUR_HARM_95c25 | 10min 25th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x974E | 0x974E | 38734 | 38734 | N_CUR_HARM_95c26 | 10min 26th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x974F | 0x974F | 38735 | 38735 | N_CUR_HARM_95c27 | 10min 27th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9750 | 0x9750 | 38736 | 38736 | N_CUR_HARM_95c28 | 10min 28th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9751 | 0x9751 | 38737 | 38737 | N_CUR_HARM_95c29 | 10min 29th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9752 | 0x9752 | 38738 | 38738 | N_CUR_HARM_95c30 | 10min 30th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9753 | 0x9753 | 38739 | 38739 | N_CUR_HARM_95c31 | 10min 31st Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9754 | 0x9754 | 38740 | 38740 | N_CUR_HARM_95c32 | 10min 32nd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9755 | 0x9755 | 38741 | 38741 | N_CUR_HARM_95c33 | 10min 33rd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9756 | 0x9756 | 38742 | 38742 | N_CUR_HARM_95c34 | 10min 34th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9757 | 0x9757 | 38743 | 38743 | N_CUR_HARM_95c35 | 10min 35th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9758 | 0x9758 | 38744 | 38744 | N_CUR_HARM_95c36 | 10min 36th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9759 | 0x9759 | 38745 | 38745 | N_CUR_HARM_95c37 | 10min 37th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x975A | 0x975A | 38746 | 38746 | N_CUR_HARM_95c38 | 10min 38th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x975B | 0x975B | 38747 | 38747 | N_CUR_HARM_95c39 | 10min 39th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x975C | 0x975C | 38748 | 38748 | N_CUR_HARM_95c40 | 10min 40th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x975D | 0x975D | 38749 | 38749 | N_CUR_HARM_95c41 | 10min 41st Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x975E | 0x975E | 38750 | 38750 | N_CUR_HARM_95c42 | 10min 42nd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x975F | 0x975F | 38751 | 38751 | N_CUR_HARM_95c43 | 10min 43rd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9760 | 0x9760 | 38752 | 38752 | N_CUR_HARM_95c44 | 10min 44th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9761 | 0x9761 | 38753 | 38753 | N_CUR_HARM_95c45 | 10min 45th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9762 | 0x9762 | 38754 | 38754 | N_CUR_HARM_95c46 | 10min 46th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9763 | 0x9763 | 38755 | 38755 | N_CUR_HARM_95c47 | 10min 47th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9764 | 0x9764 | 38756 | 38756 | N_CUR_HARM_95c48 | 10min 48th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9765 | 0x9765 | 38757 | 38757 | N_CUR_HARM_95c49 | 10min 49th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9766 | 0x9766 | 38758 | 38758 | N_CUR_HARM_95c50 | 10min 50th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0x9767 | 0x9768 | 38759 | 38760 | CUR_HARM_95_PASSa2 | 10min 2nd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9769 | 0x976A | 38761 | 38762 | CUR_HARM_95_PASSa3 | 10min 3rd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x976B | 0x976C | 38763 | 38764 | CUR_HARM_95_PASSa4 | 10min 4th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x976D | 0x976E | 38765 | 38766 | CUR_HARM_95_PASSa5 | 10min 5th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x976F | 0x9770 | 38767 | 38768 | CUR_HARM_95_PASSa6 | 10min 6th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9771 | 0x9772 | 38769 | 38770 | CUR_HARM_95_PASSa7 | 10min 7th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9773 | 0x9774 | 38771 | 38772 | CUR_HARM_95_PASSa8 | 10min 8th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9775 | 0x9776 | 38773 | 38774 | CUR_HARM_95_PASSa9 | 10min 9th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9777 | 0x9778 | 38775 | 38776 | CUR_HARM_95_PASSa10 | 10min 10th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9779 | 0x977A | 38777 | 38778 | CUR_HARM_95_PASSa11 | 10min 11st Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x977B | 0x977C | 38779 | 38780 | CUR_HARM_95_PASSa12 | 10min 12nd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x977D | 0x977E | 38781 | 38782 | CUR_HARM_95_PASSa13 | 10min 13rd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x977F | 0x9780 | 38783 | 38784 | CUR_HARM_95_PASSa14 | 10min 14th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9781 | 0x9782 | 38785 | 38786 | CUR_HARM_95_PASSa15 | 10min 15th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9783 | 0x9784 | 38787 | 38788 | CUR_HARM_95_PASSa16 | 10min 16th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9785 | 0x9786 | 38789 | 38790 | CUR_HARM_95_PASSa17 | 10min 17th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9787 | 0x9788 | 38791 | 38792 | CUR_HARM_95_PASSa18 | 10min 18th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9789 | 0x978A | 38793 | 38794 | CUR_HARM_95_PASSa19 | 10min 19th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x978B | 0x978C | 38795 | 38796 | CUR_HARM_95_PASSa20 | 10min 20th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x978D | 0x978E | 38797 | 38798 | CUR_HARM_95_PASSa21 | 10min 21st Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x978F | 0x9790 | 38799 | 38800 | CUR_HARM_95_PASSa22 | 10min 22nd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9791 | 0x9792 | 38801 | 38802 | CUR_HARM_95_PASSa23 | 10min 23rd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9793 | 0x9794 | 38803 | 38804 | CUR_HARM_95_PASSa24 | 10min 24th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9795 | 0x9796 | 38805 | 38806 | CUR_HARM_95_PASSa25 | 10min 25th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9797 | 0x9798 | 38807 | 38808 | CUR_HARM_95_PASSa26 | 10min 26th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9799 | 0x979A | 38809 | 38810 | CUR_HARM_95_PASSa27 | 10min 27th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x979B | 0x979C | 38811 | 38812 | CUR_HARM_95_PASSa28 | 10min 28th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x979D | 0x979E | 38813 | 38814 | CUR_HARM_95_PASSa29 | 10min 29th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x979F | 0x97A0 | 38815 | 38816 | CUR_HARM_95_PASSa30 | 10min 30th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97A1 | 0x97A2 | 38817 | 38818 | CUR_HARM_95_PASSa31 | 10min 31st Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97A3 | 0x97A4 | 38819 | 38820 | CUR_HARM_95_PASSa32 | 10min 32nd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97A5 | 0x97A6 | 38821 | 38822 | CUR_HARM_95_PASSa33 | 10min 33rd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97A7 | 0x97A8 | 38823 | 38824 | CUR_HARM_95_PASSa34 | 10min 34th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97A9 | 0x97AA | 38825 | 38826 | CUR_HARM_95_PASSa35 | 10min 35th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97AB | 0x97AC | 38827 | 38828 | CUR_HARM_95_PASSa36 | 10min 36th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97AD | 0x97AE | 38829 | 38830 | CUR_HARM_95_PASSa37 | 10min 37th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97AF | 0x97B0 | 38831 | 38832 | CUR_HARM_95_PASSa38 | 10min 38th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97B1 | 0x97B2 | 38833 | 38834 | CUR_HARM_95_PASSa39 | 10min 39th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97B3 | 0x97B4 | 38835 | 38836 | CUR_HARM_95_PASSa40 | 10min 40th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97B5 | 0x97B6 | 38837 | 38838 | CUR_HARM_95_PASSa41 | 10min 41st Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97B7 | 0x97B8 | 38839 | 38840 | CUR_HARM_95_PASSa42 | 10min 42nd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97B9 | 0x97BA | 38841 | 38842 | CUR_HARM_95_PASSa43 | 10min 43rd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97BB | 0x97BC | 38843 | 38844 | CUR_HARM_95_PASSa44 | 10min 44th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97BD | 0x97BE | 38845 | 38846 | CUR_HARM_95_PASSa45 | 10min 45th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97BF | 0x97C0 | 38847 | 38848 | CUR_HARM_95_PASSa46 | 10min 46th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97C1 | 0x97C2 | 38849 | 38850 | CUR_HARM_95_PASSa47 | 10min 47th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97C3 | 0x97C4 | 38851 | 38852 | CUR_HARM_95_PASSa48 | 10min 48th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97C5 | 0x97C6 | 38853 | 38854 | CUR_HARM_95_PASSa49 | 10min 49th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97C7 | 0x97C8 | 38855 | 38856 | CUR_HARM_95_PASSa50 | 10min 50th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97C9 | 0x97CA | 38857 | 38858 | CUR_HARM_95_PASSb2 | 10min 2nd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97CB | 0x97CC | 38859 | 38860 | CUR_HARM_95_PASSb3 | 10min 3rd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97CD | 0x97CE | 38861 | 38862 | CUR_HARM_95_PASSb4 | 10min 4th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97CF | 0x97D0 | 38863 | 38864 | CUR_HARM_95_PASSb5 | 10min 5th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97D1 | 0x97D2 | 38865 | 38866 | CUR_HARM_95_PASSb6 | 10min 6th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97D3 | 0x97D4 | 38867 | 38868 | CUR_HARM_95_PASSb7 | 10min 7th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97D5 | 0x97D6 | 38869 | 38870 | CUR_HARM_95_PASSb8 | 10min 8th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97D7 | 0x97D8 | 38871 | 38872 | CUR_HARM_95_PASSb9 | 10min 9th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97D9 | 0x97DA | 38873 | 38874 | CUR_HARM_95_PASSb10 | 10min 10th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97DB | 0x97DC | 38875 | 38876 | CUR_HARM_95_PASSb11 | 10min 11st Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97DD | 0x97DE | 38877 | 38878 | CUR_HARM_95_PASSb12 | 10min 12nd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97DF | 0x97E0 | 38879 | 38880 | CUR_HARM_95_PASSb13 | 10min 13rd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97E1 | 0x97E2 | 38881 | 38882 | CUR_HARM_95_PASSb14 | 10min 14th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97E3 | 0x97E4 | 38883 | 38884 | CUR_HARM_95_PASSb15 | 10min 15th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97E5 | 0x97E6 | 38885 | 38886 | CUR_HARM_95_PASSb16 | 10min 16th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97E7 | 0x97E8 | 38887 | 38888 | CUR_HARM_95_PASSb17 | 10min 17th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97E9 | 0x97EA | 38889 | 38890 | CUR_HARM_95_PASSb18 | 10min 18th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97EB | 0x97EC | 38891 | 38892 | CUR_HARM_95_PASSb19 | 10min 19th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97ED | 0x97EE | 38893 | 38894 | CUR_HARM_95_PASSb20 | 10min 20th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97EF | 0x97F0 | 38895 | 38896 | CUR_HARM_95_PASSb21 | 10min 21st Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97F1 | 0x97F2 | 38897 | 38898 | CUR_HARM_95_PASSb22 | 10min 22nd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97F3 | 0x97F4 | 38899 | 38900 | CUR_HARM_95_PASSb23 | 10min 23rd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97F5 | 0x97F6 | 38901 | 38902 | CUR_HARM_95_PASSb24 | 10min 24th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97F7 | 0x97F8 | 38903 | 38904 | CUR_HARM_95_PASSb25 | 10min 25th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97F9 | 0x97FA | 38905 | 38906 | CUR_HARM_95_PASSb26 | 10min 26th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97FB | 0x97FC | 38907 | 38908 | CUR_HARM_95_PASSb27 | 10min 27th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97FD | 0x97FE | 38909 | 38910 | CUR_HARM_95_PASSb28 | 10min 28th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x97FF | 0x9800 | 38911 | 38912 | CUR_HARM_95_PASSb29 | 10min 29th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9801 | 0x9802 | 38913 | 38914 | CUR_HARM_95_PASSb30 | 10min 30th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9803 | 0x9804 | 38915 | 38916 | CUR_HARM_95_PASSb31 | 10min 31st Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9805 | 0x9806 | 38917 | 38918 | CUR_HARM_95_PASSb32 | 10min 32nd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9807 | 0x9808 | 38919 | 38920 | CUR_HARM_95_PASSb33 | 10min 33rd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9809 | 0x980A | 38921 | 38922 | CUR_HARM_95_PASSb34 | 10min 34th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x980B | 0x980C | 38923 | 38924 | CUR_HARM_95_PASSb35 | 10min 35th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x980D | 0x980E | 38925 | 38926 | CUR_HARM_95_PASSb36 | 10min 36th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x980F | 0x9810 | 38927 | 38928 | CUR_HARM_95_PASSb37 | 10min 37th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9811 | 0x9812 | 38929 | 38930 | CUR_HARM_95_PASSb38 | 10min 38th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9813 | 0x9814 | 38931 | 38932 | CUR_HARM_95_PASSb39 | 10min 39th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9815 | 0x9816 | 38933 | 38934 | CUR_HARM_95_PASSb40 | 10min 40th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9817 | 0x9818 | 38935 | 38936 | CUR_HARM_95_PASSb41 | 10min 41st Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9819 | 0x981A | 38937 | 38938 | CUR_HARM_95_PASSb42 | 10min 42nd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x981B | 0x981C | 38939 | 38940 | CUR_HARM_95_PASSb43 | 10min 43rd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x981D | 0x981E | 38941 | 38942 | CUR_HARM_95_PASSb44 | 10min 44th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x981F | 0x9820 | 38943 | 38944 | CUR_HARM_95_PASSb45 | 10min 45th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9821 | 0x9822 | 38945 | 38946 | CUR_HARM_95_PASSb46 | 10min 46th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9823 | 0x9824 | 38947 | 38948 | CUR_HARM_95_PASSb47 | 10min 47th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9825 | 0x9826 | 38949 | 38950 | CUR_HARM_95_PASSb48 | 10min 48th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9827 | 0x9828 | 38951 | 38952 | CUR_HARM_95_PASSb49 | 10min 49th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9829 | 0x982A | 38953 | 38954 | CUR_HARM_95_PASSb50 | 10min 50th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x982B | 0x982C | 38955 | 38956 | CUR_HARM_95_PASSc2 | 10min 2nd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x982D | 0x982E | 38957 | 38958 | CUR_HARM_95_PASSc3 | 10min 3rd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x982F | 0x9830 | 38959 | 38960 | CUR_HARM_95_PASSc4 | 10min 4th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9831 | 0x9832 | 38961 | 38962 | CUR_HARM_95_PASSc5 | 10min 5th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9833 | 0x9834 | 38963 | 38964 | CUR_HARM_95_PASSc6 | 10min 6th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9835 | 0x9836 | 38965 | 38966 | CUR_HARM_95_PASSc7 | 10min 7th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9837 | 0x9838 | 38967 | 38968 | CUR_HARM_95_PASSc8 | 10min 8th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9839 | 0x983A | 38969 | 38970 | CUR_HARM_95_PASSc9 | 10min 9th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x983B | 0x983C | 38971 | 38972 | CUR_HARM_95_PASSc10 | 10min 10th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x983D | 0x983E | 38973 | 38974 | CUR_HARM_95_PASSc11 | 10min 11st Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x983F | 0x9840 | 38975 | 38976 | CUR_HARM_95_PASSc12 | 10min 12nd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9841 | 0x9842 | 38977 | 38978 | CUR_HARM_95_PASSc13 | 10min 13rd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9843 | 0x9844 | 38979 | 38980 | CUR_HARM_95_PASSc14 | 10min 14th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9845 | 0x9846 | 38981 | 38982 | CUR_HARM_95_PASSc15 | 10min 15th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9847 | 0x9848 | 38983 | 38984 | CUR_HARM_95_PASSc16 | 10min 16th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9849 | 0x984A | 38985 | 38986 | CUR_HARM_95_PASSc17 | 10min 17th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x984B | 0x984C | 38987 | 38988 | CUR_HARM_95_PASSc18 | 10min 18th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x984D | 0x984E | 38989 | 38990 | CUR_HARM_95_PASSc19 | 10min 19th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x984F | 0x9850 | 38991 | 38992 | CUR_HARM_95_PASSc20 | 10min 20th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9851 | 0x9852 | 38993 | 38994 | CUR_HARM_95_PASSc21 | 10min 21st Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9853 | 0x9854 | 38995 | 38996 | CUR_HARM_95_PASSc22 | 10min 22nd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9855 | 0x9856 | 38997 | 38998 | CUR_HARM_95_PASSc23 | 10min 23rd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9857 | 0x9858 | 38999 | 39000 | CUR_HARM_95_PASSc24 | 10min 24th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9859 | 0x985A | 39001 | 39002 | CUR_HARM_95_PASSc25 | 10min 25th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x985B | 0x985C | 39003 | 39004 | CUR_HARM_95_PASSc26 | 10min 26th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x985D | 0x985E | 39005 | 39006 | CUR_HARM_95_PASSc27 | 10min 27th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x985F | 0x9860 | 39007 | 39008 | CUR_HARM_95_PASSc28 | 10min 28th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9861 | 0x9862 | 39009 | 39010 | CUR_HARM_95_PASSc29 | 10min 29th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9863 | 0x9864 | 39011 | 39012 | CUR_HARM_95_PASSc30 | 10min 30th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9865 | 0x9866 | 39013 | 39014 | CUR_HARM_95_PASSc31 | 10min 31st Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9867 | 0x9868 | 39015 | 39016 | CUR_HARM_95_PASSc32 | 10min 32nd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9869 | 0x986A | 39017 | 39018 | CUR_HARM_95_PASSc33 | 10min 33rd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x986B | 0x986C | 39019 | 39020 | CUR_HARM_95_PASSc34 | 10min 34th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x986D | 0x986E | 39021 | 39022 | CUR_HARM_95_PASSc35 | 10min 35th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x986F | 0x9870 | 39023 | 39024 | CUR_HARM_95_PASSc36 | 10min 36th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9871 | 0x9872 | 39025 | 39026 | CUR_HARM_95_PASSc37 | 10min 37th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9873 | 0x9874 | 39027 | 39028 | CUR_HARM_95_PASSc38 | 10min 38th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9875 | 0x9876 | 39029 | 39030 | CUR_HARM_95_PASSc39 | 10min 39th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9877 | 0x9878 | 39031 | 39032 | CUR_HARM_95_PASSc40 | 10min 40th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9879 | 0x987A | 39033 | 39034 | CUR_HARM_95_PASSc41 | 10min 41st Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x987B | 0x987C | 39035 | 39036 | CUR_HARM_95_PASSc42 | 10min 42nd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x987D | 0x987E | 39037 | 39038 | CUR_HARM_95_PASSc43 | 10min 43rd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x987F | 0x9880 | 39039 | 39040 | CUR_HARM_95_PASSc44 | 10min 44th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9881 | 0x9882 | 39041 | 39042 | CUR_HARM_95_PASSc45 | 10min 45th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9883 | 0x9884 | 39043 | 39044 | CUR_HARM_95_PASSc46 | 10min 46th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9885 | 0x9886 | 39045 | 39046 | CUR_HARM_95_PASSc47 | 10min 47th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9887 | 0x9888 | 39047 | 39048 | CUR_HARM_95_PASSc48 | 10min 48th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x9889 | 0x988A | 39049 | 39050 | CUR_HARM_95_PASSc49 | 10min 49th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x988B | 0x988C | 39051 | 39052 | CUR_HARM_95_PASSc50 | 10min 50th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0x988D | 0x988D | 39053 | 39053 | N_TDD_99a | 10min Phase A TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0x988E | 0x988E | 39054 | 39054 | N_TDD_99b | 10min Phase B TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0x988F | 0x988F | 39055 | 39055 | N_TDD_99c | 10min Phase C TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0x9890 | 0x9891 | 39056 | 39057 | TDD_99_PASSa | 10min Phase A TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0x9892 | 0x9893 | 39058 | 39059 | TDD_99_PASSb | 10min Phase B TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0x9894 | 0x9895 | 39060 | 39061 | TDD_99_PASSc | 10min Phase C TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0x9896 | 0x9896 | 39062 | 39062 | N_CUR_HARM_99a2 | 10min 2nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9897 | 0x9897 | 39063 | 39063 | N_CUR_HARM_99a3 | 10min 3rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9898 | 0x9898 | 39064 | 39064 | N_CUR_HARM_99a4 | 10min 4th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9899 | 0x9899 | 39065 | 39065 | N_CUR_HARM_99a5 | 10min 5th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x989A | 0x989A | 39066 | 39066 | N_CUR_HARM_99a6 | 10min 6th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x989B | 0x989B | 39067 | 39067 | N_CUR_HARM_99a7 | 10min 7th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x989C | 0x989C | 39068 | 39068 | N_CUR_HARM_99a8 | 10min 8th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x989D | 0x989D | 39069 | 39069 | N_CUR_HARM_99a9 | 10min 9th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x989E | 0x989E | 39070 | 39070 | N_CUR_HARM_99a10 | 10min 10th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x989F | 0x989F | 39071 | 39071 | N_CUR_HARM_99a11 | 10min 11st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98A0 | 0x98A0 | 39072 | 39072 | N_CUR_HARM_99a12 | 10min 12nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98A1 | 0x98A1 | 39073 | 39073 | N_CUR_HARM_99a13 | 10min 13rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98A2 | 0x98A2 | 39074 | 39074 | N_CUR_HARM_99a14 | 10min 14th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98A3 | 0x98A3 | 39075 | 39075 | N_CUR_HARM_99a15 | 10min 15th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98A4 | 0x98A4 | 39076 | 39076 | N_CUR_HARM_99a16 | 10min 16th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98A5 | 0x98A5 | 39077 | 39077 | N_CUR_HARM_99a17 | 10min 17th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98A6 | 0x98A6 | 39078 | 39078 | N_CUR_HARM_99a18 | 10min 18th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98A7 | 0x98A7 | 39079 | 39079 | N_CUR_HARM_99a19 | 10min 19th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98A8 | 0x98A8 | 39080 | 39080 | N_CUR_HARM_99a20 | 10min 20th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98A9 | 0x98A9 | 39081 | 39081 | N_CUR_HARM_99a21 | 10min 21st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98AA | 0x98AA | 39082 | 39082 | N_CUR_HARM_99a22 | 10min 22nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98AB | 0x98AB | 39083 | 39083 | N_CUR_HARM_99a23 | 10min 23rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98AC | 0x98AC | 39084 | 39084 | N_CUR_HARM_99a24 | 10min 24th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98AD | 0x98AD | 39085 | 39085 | N_CUR_HARM_99a25 | 10min 25th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98AE | 0x98AE | 39086 | 39086 | N_CUR_HARM_99a26 | 10min 26th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98AF | 0x98AF | 39087 | 39087 | N_CUR_HARM_99a27 | 10min 27th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98B0 | 0x98B0 | 39088 | 39088 | N_CUR_HARM_99a28 | 10min 28th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98B1 | 0x98B1 | 39089 | 39089 | N_CUR_HARM_99a29 | 10min 29th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98B2 | 0x98B2 | 39090 | 39090 | N_CUR_HARM_99a30 | 10min 30th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98B3 | 0x98B3 | 39091 | 39091 | N_CUR_HARM_99a31 | 10min 31st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98B4 | 0x98B4 | 39092 | 39092 | N_CUR_HARM_99a32 | 10min 32nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98B5 | 0x98B5 | 39093 | 39093 | N_CUR_HARM_99a33 | 10min 33rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98B6 | 0x98B6 | 39094 | 39094 | N_CUR_HARM_99a34 | 10min 34th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98B7 | 0x98B7 | 39095 | 39095 | N_CUR_HARM_99a35 | 10min 35th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98B8 | 0x98B8 | 39096 | 39096 | N_CUR_HARM_99a36 | 10min 36th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98B9 | 0x98B9 | 39097 | 39097 | N_CUR_HARM_99a37 | 10min 37th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98BA | 0x98BA | 39098 | 39098 | N_CUR_HARM_99a38 | 10min 38th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98BB | 0x98BB | 39099 | 39099 | N_CUR_HARM_99a39 | 10min 39th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98BC | 0x98BC | 39100 | 39100 | N_CUR_HARM_99a40 | 10min 40th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98BD | 0x98BD | 39101 | 39101 | N_CUR_HARM_99a41 | 10min 41st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98BE | 0x98BE | 39102 | 39102 | N_CUR_HARM_99a42 | 10min 42nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98BF | 0x98BF | 39103 | 39103 | N_CUR_HARM_99a43 | 10min 43rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98C0 | 0x98C0 | 39104 | 39104 | N_CUR_HARM_99a44 | 10min 44th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98C1 | 0x98C1 | 39105 | 39105 | N_CUR_HARM_99a45 | 10min 45th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98C2 | 0x98C2 | 39106 | 39106 | N_CUR_HARM_99a46 | 10min 46th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98C3 | 0x98C3 | 39107 | 39107 | N_CUR_HARM_99a47 | 10min 47th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98C4 | 0x98C4 | 39108 | 39108 | N_CUR_HARM_99a48 | 10min 48th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98C5 | 0x98C5 | 39109 | 39109 | N_CUR_HARM_99a49 | 10min 49th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98C6 | 0x98C6 | 39110 | 39110 | N_CUR_HARM_99a50 | 10min 50th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98C7 | 0x98C7 | 39111 | 39111 | N_CUR_HARM_99b2 | 10min 2nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98C8 | 0x98C8 | 39112 | 39112 | N_CUR_HARM_99b3 | 10min 3rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98C9 | 0x98C9 | 39113 | 39113 | N_CUR_HARM_99b4 | 10min 4th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98CA | 0x98CA | 39114 | 39114 | N_CUR_HARM_99b5 | 10min 5th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98CB | 0x98CB | 39115 | 39115 | N_CUR_HARM_99b6 | 10min 6th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98CC | 0x98CC | 39116 | 39116 | N_CUR_HARM_99b7 | 10min 7th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98CD | 0x98CD | 39117 | 39117 | N_CUR_HARM_99b8 | 10min 8th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98CE | 0x98CE | 39118 | 39118 | N_CUR_HARM_99b9 | 10min 9th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98CF | 0x98CF | 39119 | 39119 | N_CUR_HARM_99b10 | 10min 10th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98D0 | 0x98D0 | 39120 | 39120 | N_CUR_HARM_99b11 | 10min 11st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98D1 | 0x98D1 | 39121 | 39121 | N_CUR_HARM_99b12 | 10min 12nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98D2 | 0x98D2 | 39122 | 39122 | N_CUR_HARM_99b13 | 10min 13rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98D3 | 0x98D3 | 39123 | 39123 | N_CUR_HARM_99b14 | 10min 14th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98D4 | 0x98D4 | 39124 | 39124 | N_CUR_HARM_99b15 | 10min 15th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98D5 | 0x98D5 | 39125 | 39125 | N_CUR_HARM_99b16 | 10min 16th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98D6 | 0x98D6 | 39126 | 39126 | N_CUR_HARM_99b17 | 10min 17th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98D7 | 0x98D7 | 39127 | 39127 | N_CUR_HARM_99b18 | 10min 18th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98D8 | 0x98D8 | 39128 | 39128 | N_CUR_HARM_99b19 | 10min 19th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98D9 | 0x98D9 | 39129 | 39129 | N_CUR_HARM_99b20 | 10min 20th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98DA | 0x98DA | 39130 | 39130 | N_CUR_HARM_99b21 | 10min 21st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98DB | 0x98DB | 39131 | 39131 | N_CUR_HARM_99b22 | 10min 22nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98DC | 0x98DC | 39132 | 39132 | N_CUR_HARM_99b23 | 10min 23rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98DD | 0x98DD | 39133 | 39133 | N_CUR_HARM_99b24 | 10min 24th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98DE | 0x98DE | 39134 | 39134 | N_CUR_HARM_99b25 | 10min 25th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98DF | 0x98DF | 39135 | 39135 | N_CUR_HARM_99b26 | 10min 26th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98E0 | 0x98E0 | 39136 | 39136 | N_CUR_HARM_99b27 | 10min 27th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98E1 | 0x98E1 | 39137 | 39137 | N_CUR_HARM_99b28 | 10min 28th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98E2 | 0x98E2 | 39138 | 39138 | N_CUR_HARM_99b29 | 10min 29th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98E3 | 0x98E3 | 39139 | 39139 | N_CUR_HARM_99b30 | 10min 30th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98E4 | 0x98E4 | 39140 | 39140 | N_CUR_HARM_99b31 | 10min 31st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98E5 | 0x98E5 | 39141 | 39141 | N_CUR_HARM_99b32 | 10min 32nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98E6 | 0x98E6 | 39142 | 39142 | N_CUR_HARM_99b33 | 10min 33rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98E7 | 0x98E7 | 39143 | 39143 | N_CUR_HARM_99b34 | 10min 34th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98E8 | 0x98E8 | 39144 | 39144 | N_CUR_HARM_99b35 | 10min 35th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98E9 | 0x98E9 | 39145 | 39145 | N_CUR_HARM_99b36 | 10min 36th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98EA | 0x98EA | 39146 | 39146 | N_CUR_HARM_99b37 | 10min 37th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98EB | 0x98EB | 39147 | 39147 | N_CUR_HARM_99b38 | 10min 38th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98EC | 0x98EC | 39148 | 39148 | N_CUR_HARM_99b39 | 10min 39th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98ED | 0x98ED | 39149 | 39149 | N_CUR_HARM_99b40 | 10min 40th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98EE | 0x98EE | 39150 | 39150 | N_CUR_HARM_99b41 | 10min 41st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98EF | 0x98EF | 39151 | 39151 | N_CUR_HARM_99b42 | 10min 42nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98F0 | 0x98F0 | 39152 | 39152 | N_CUR_HARM_99b43 | 10min 43rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98F1 | 0x98F1 | 39153 | 39153 | N_CUR_HARM_99b44 | 10min 44th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98F2 | 0x98F2 | 39154 | 39154 | N_CUR_HARM_99b45 | 10min 45th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98F3 | 0x98F3 | 39155 | 39155 | N_CUR_HARM_99b46 | 10min 46th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98F4 | 0x98F4 | 39156 | 39156 | N_CUR_HARM_99b47 | 10min 47th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98F5 | 0x98F5 | 39157 | 39157 | N_CUR_HARM_99b48 | 10min 48th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98F6 | 0x98F6 | 39158 | 39158 | N_CUR_HARM_99b49 | 10min 49th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98F7 | 0x98F7 | 39159 | 39159 | N_CUR_HARM_99b50 | 10min 50th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98F8 | 0x98F8 | 39160 | 39160 | N_CUR_HARM_99c2 | 10min 2nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98F9 | 0x98F9 | 39161 | 39161 | N_CUR_HARM_99c3 | 10min 3rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98FA | 0x98FA | 39162 | 39162 | N_CUR_HARM_99c4 | 10min 4th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98FB | 0x98FB | 39163 | 39163 | N_CUR_HARM_99c5 | 10min 5th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98FC | 0x98FC | 39164 | 39164 | N_CUR_HARM_99c6 | 10min 6th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98FD | 0x98FD | 39165 | 39165 | N_CUR_HARM_99c7 | 10min 7th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98FE | 0x98FE | 39166 | 39166 | N_CUR_HARM_99c8 | 10min 8th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x98FF | 0x98FF | 39167 | 39167 | N_CUR_HARM_99c9 | 10min 9th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9900 | 0x9900 | 39168 | 39168 | N_CUR_HARM_99c10 | 10min 10th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9901 | 0x9901 | 39169 | 39169 | N_CUR_HARM_99c11 | 10min 11st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9902 | 0x9902 | 39170 | 39170 | N_CUR_HARM_99c12 | 10min 12nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9903 | 0x9903 | 39171 | 39171 | N_CUR_HARM_99c13 | 10min 13rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9904 | 0x9904 | 39172 | 39172 | N_CUR_HARM_99c14 | 10min 14th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9905 | 0x9905 | 39173 | 39173 | N_CUR_HARM_99c15 | 10min 15th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9906 | 0x9906 | 39174 | 39174 | N_CUR_HARM_99c16 | 10min 16th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9907 | 0x9907 | 39175 | 39175 | N_CUR_HARM_99c17 | 10min 17th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9908 | 0x9908 | 39176 | 39176 | N_CUR_HARM_99c18 | 10min 18th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9909 | 0x9909 | 39177 | 39177 | N_CUR_HARM_99c19 | 10min 19th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x990A | 0x990A | 39178 | 39178 | N_CUR_HARM_99c20 | 10min 20th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x990B | 0x990B | 39179 | 39179 | N_CUR_HARM_99c21 | 10min 21st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x990C | 0x990C | 39180 | 39180 | N_CUR_HARM_99c22 | 10min 22nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x990D | 0x990D | 39181 | 39181 | N_CUR_HARM_99c23 | 10min 23rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x990E | 0x990E | 39182 | 39182 | N_CUR_HARM_99c24 | 10min 24th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x990F | 0x990F | 39183 | 39183 | N_CUR_HARM_99c25 | 10min 25th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9910 | 0x9910 | 39184 | 39184 | N_CUR_HARM_99c26 | 10min 26th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9911 | 0x9911 | 39185 | 39185 | N_CUR_HARM_99c27 | 10min 27th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9912 | 0x9912 | 39186 | 39186 | N_CUR_HARM_99c28 | 10min 28th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9913 | 0x9913 | 39187 | 39187 | N_CUR_HARM_99c29 | 10min 29th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9914 | 0x9914 | 39188 | 39188 | N_CUR_HARM_99c30 | 10min 30th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9915 | 0x9915 | 39189 | 39189 | N_CUR_HARM_99c31 | 10min 31st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9916 | 0x9916 | 39190 | 39190 | N_CUR_HARM_99c32 | 10min 32nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9917 | 0x9917 | 39191 | 39191 | N_CUR_HARM_99c33 | 10min 33rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9918 | 0x9918 | 39192 | 39192 | N_CUR_HARM_99c34 | 10min 34th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9919 | 0x9919 | 39193 | 39193 | N_CUR_HARM_99c35 | 10min 35th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x991A | 0x991A | 39194 | 39194 | N_CUR_HARM_99c36 | 10min 36th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x991B | 0x991B | 39195 | 39195 | N_CUR_HARM_99c37 | 10min 37th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x991C | 0x991C | 39196 | 39196 | N_CUR_HARM_99c38 | 10min 38th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x991D | 0x991D | 39197 | 39197 | N_CUR_HARM_99c39 | 10min 39th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x991E | 0x991E | 39198 | 39198 | N_CUR_HARM_99c40 | 10min 40th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x991F | 0x991F | 39199 | 39199 | N_CUR_HARM_99c41 | 10min 41st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9920 | 0x9920 | 39200 | 39200 | N_CUR_HARM_99c42 | 10min 42nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9921 | 0x9921 | 39201 | 39201 | N_CUR_HARM_99c43 | 10min 43rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9922 | 0x9922 | 39202 | 39202 | N_CUR_HARM_99c44 | 10min 44th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9923 | 0x9923 | 39203 | 39203 | N_CUR_HARM_99c45 | 10min 45th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9924 | 0x9924 | 39204 | 39204 | N_CUR_HARM_99c46 | 10min 46th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9925 | 0x9925 | 39205 | 39205 | N_CUR_HARM_99c47 | 10min 47th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9926 | 0x9926 | 39206 | 39206 | N_CUR_HARM_99c48 | 10min 48th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9927 | 0x9927 | 39207 | 39207 | N_CUR_HARM_99c49 | 10min 49th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9928 | 0x9928 | 39208 | 39208 | N_CUR_HARM_99c50 | 10min 50th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0x9929 | 0x992A | 39209 | 39210 | CUR_HARM_99_PASSa2 | 10min 2nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x992B | 0x992C | 39211 | 39212 | CUR_HARM_99_PASSa3 | 10min 3rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x992D | 0x992E | 39213 | 39214 | CUR_HARM_99_PASSa4 | 10min 4th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x992F | 0x9930 | 39215 | 39216 | CUR_HARM_99_PASSa5 | 10min 5th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9931 | 0x9932 | 39217 | 39218 | CUR_HARM_99_PASSa6 | 10min 6th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9933 | 0x9934 | 39219 | 39220 | CUR_HARM_99_PASSa7 | 10min 7th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9935 | 0x9936 | 39221 | 39222 | CUR_HARM_99_PASSa8 | 10min 8th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9937 | 0x9938 | 39223 | 39224 | CUR_HARM_99_PASSa9 | 10min 9th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9939 | 0x993A | 39225 | 39226 | CUR_HARM_99_PASSa10 | 10min 10th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x993B | 0x993C | 39227 | 39228 | CUR_HARM_99_PASSa11 | 10min 11st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x993D | 0x993E | 39229 | 39230 | CUR_HARM_99_PASSa12 | 10min 12nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x993F | 0x9940 | 39231 | 39232 | CUR_HARM_99_PASSa13 | 10min 13rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9941 | 0x9942 | 39233 | 39234 | CUR_HARM_99_PASSa14 | 10min 14th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9943 | 0x9944 | 39235 | 39236 | CUR_HARM_99_PASSa15 | 10min 15th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9945 | 0x9946 | 39237 | 39238 | CUR_HARM_99_PASSa16 | 10min 16th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9947 | 0x9948 | 39239 | 39240 | CUR_HARM_99_PASSa17 | 10min 17th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9949 | 0x994A | 39241 | 39242 | CUR_HARM_99_PASSa18 | 10min 18th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x994B | 0x994C | 39243 | 39244 | CUR_HARM_99_PASSa19 | 10min 19th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x994D | 0x994E | 39245 | 39246 | CUR_HARM_99_PASSa20 | 10min 20th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x994F | 0x9950 | 39247 | 39248 | CUR_HARM_99_PASSa21 | 10min 21st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9951 | 0x9952 | 39249 | 39250 | CUR_HARM_99_PASSa22 | 10min 22nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9953 | 0x9954 | 39251 | 39252 | CUR_HARM_99_PASSa23 | 10min 23rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9955 | 0x9956 | 39253 | 39254 | CUR_HARM_99_PASSa24 | 10min 24th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9957 | 0x9958 | 39255 | 39256 | CUR_HARM_99_PASSa25 | 10min 25th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9959 | 0x995A | 39257 | 39258 | CUR_HARM_99_PASSa26 | 10min 26th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x995B | 0x995C | 39259 | 39260 | CUR_HARM_99_PASSa27 | 10min 27th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x995D | 0x995E | 39261 | 39262 | CUR_HARM_99_PASSa28 | 10min 28th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x995F | 0x9960 | 39263 | 39264 | CUR_HARM_99_PASSa29 | 10min 29th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9961 | 0x9962 | 39265 | 39266 | CUR_HARM_99_PASSa30 | 10min 30th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9963 | 0x9964 | 39267 | 39268 | CUR_HARM_99_PASSa31 | 10min 31st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9965 | 0x9966 | 39269 | 39270 | CUR_HARM_99_PASSa32 | 10min 32nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9967 | 0x9968 | 39271 | 39272 | CUR_HARM_99_PASSa33 | 10min 33rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9969 | 0x996A | 39273 | 39274 | CUR_HARM_99_PASSa34 | 10min 34th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x996B | 0x996C | 39275 | 39276 | CUR_HARM_99_PASSa35 | 10min 35th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x996D | 0x996E | 39277 | 39278 | CUR_HARM_99_PASSa36 | 10min 36th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x996F | 0x9970 | 39279 | 39280 | CUR_HARM_99_PASSa37 | 10min 37th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9971 | 0x9972 | 39281 | 39282 | CUR_HARM_99_PASSa38 | 10min 38th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9973 | 0x9974 | 39283 | 39284 | CUR_HARM_99_PASSa39 | 10min 39th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9975 | 0x9976 | 39285 | 39286 | CUR_HARM_99_PASSa40 | 10min 40th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9977 | 0x9978 | 39287 | 39288 | CUR_HARM_99_PASSa41 | 10min 41st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9979 | 0x997A | 39289 | 39290 | CUR_HARM_99_PASSa42 | 10min 42nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x997B | 0x997C | 39291 | 39292 | CUR_HARM_99_PASSa43 | 10min 43rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x997D | 0x997E | 39293 | 39294 | CUR_HARM_99_PASSa44 | 10min 44th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x997F | 0x9980 | 39295 | 39296 | CUR_HARM_99_PASSa45 | 10min 45th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9981 | 0x9982 | 39297 | 39298 | CUR_HARM_99_PASSa46 | 10min 46th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9983 | 0x9984 | 39299 | 39300 | CUR_HARM_99_PASSa47 | 10min 47th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9985 | 0x9986 | 39301 | 39302 | CUR_HARM_99_PASSa48 | 10min 48th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9987 | 0x9988 | 39303 | 39304 | CUR_HARM_99_PASSa49 | 10min 49th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9989 | 0x998A | 39305 | 39306 | CUR_HARM_99_PASSa50 | 10min 50th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x998B | 0x998C | 39307 | 39308 | CUR_HARM_99_PASSb2 | 10min 2nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x998D | 0x998E | 39309 | 39310 | CUR_HARM_99_PASSb3 | 10min 3rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x998F | 0x9990 | 39311 | 39312 | CUR_HARM_99_PASSb4 | 10min 4th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9991 | 0x9992 | 39313 | 39314 | CUR_HARM_99_PASSb5 | 10min 5th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9993 | 0x9994 | 39315 | 39316 | CUR_HARM_99_PASSb6 | 10min 6th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9995 | 0x9996 | 39317 | 39318 | CUR_HARM_99_PASSb7 | 10min 7th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9997 | 0x9998 | 39319 | 39320 | CUR_HARM_99_PASSb8 | 10min 8th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9999 | 0x999A | 39321 | 39322 | CUR_HARM_99_PASSb9 | 10min 9th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x999B | 0x999C | 39323 | 39324 | CUR_HARM_99_PASSb10 | 10min 10th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x999D | 0x999E | 39325 | 39326 | CUR_HARM_99_PASSb11 | 10min 11st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x999F | 0x99A0 | 39327 | 39328 | CUR_HARM_99_PASSb12 | 10min 12nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99A1 | 0x99A2 | 39329 | 39330 | CUR_HARM_99_PASSb13 | 10min 13rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99A3 | 0x99A4 | 39331 | 39332 | CUR_HARM_99_PASSb14 | 10min 14th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99A5 | 0x99A6 | 39333 | 39334 | CUR_HARM_99_PASSb15 | 10min 15th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99A7 | 0x99A8 | 39335 | 39336 | CUR_HARM_99_PASSb16 | 10min 16th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99A9 | 0x99AA | 39337 | 39338 | CUR_HARM_99_PASSb17 | 10min 17th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99AB | 0x99AC | 39339 | 39340 | CUR_HARM_99_PASSb18 | 10min 18th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99AD | 0x99AE | 39341 | 39342 | CUR_HARM_99_PASSb19 | 10min 19th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99AF | 0x99B0 | 39343 | 39344 | CUR_HARM_99_PASSb20 | 10min 20th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99B1 | 0x99B2 | 39345 | 39346 | CUR_HARM_99_PASSb21 | 10min 21st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99B3 | 0x99B4 | 39347 | 39348 | CUR_HARM_99_PASSb22 | 10min 22nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99B5 | 0x99B6 | 39349 | 39350 | CUR_HARM_99_PASSb23 | 10min 23rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99B7 | 0x99B8 | 39351 | 39352 | CUR_HARM_99_PASSb24 | 10min 24th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99B9 | 0x99BA | 39353 | 39354 | CUR_HARM_99_PASSb25 | 10min 25th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99BB | 0x99BC | 39355 | 39356 | CUR_HARM_99_PASSb26 | 10min 26th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99BD | 0x99BE | 39357 | 39358 | CUR_HARM_99_PASSb27 | 10min 27th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99BF | 0x99C0 | 39359 | 39360 | CUR_HARM_99_PASSb28 | 10min 28th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99C1 | 0x99C2 | 39361 | 39362 | CUR_HARM_99_PASSb29 | 10min 29th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99C3 | 0x99C4 | 39363 | 39364 | CUR_HARM_99_PASSb30 | 10min 30th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99C5 | 0x99C6 | 39365 | 39366 | CUR_HARM_99_PASSb31 | 10min 31st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99C7 | 0x99C8 | 39367 | 39368 | CUR_HARM_99_PASSb32 | 10min 32nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99C9 | 0x99CA | 39369 | 39370 | CUR_HARM_99_PASSb33 | 10min 33rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99CB | 0x99CC | 39371 | 39372 | CUR_HARM_99_PASSb34 | 10min 34th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99CD | 0x99CE | 39373 | 39374 | CUR_HARM_99_PASSb35 | 10min 35th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99CF | 0x99D0 | 39375 | 39376 | CUR_HARM_99_PASSb36 | 10min 36th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99D1 | 0x99D2 | 39377 | 39378 | CUR_HARM_99_PASSb37 | 10min 37th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99D3 | 0x99D4 | 39379 | 39380 | CUR_HARM_99_PASSb38 | 10min 38th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99D5 | 0x99D6 | 39381 | 39382 | CUR_HARM_99_PASSb39 | 10min 39th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99D7 | 0x99D8 | 39383 | 39384 | CUR_HARM_99_PASSb40 | 10min 40th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99D9 | 0x99DA | 39385 | 39386 | CUR_HARM_99_PASSb41 | 10min 41st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99DB | 0x99DC | 39387 | 39388 | CUR_HARM_99_PASSb42 | 10min 42nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99DD | 0x99DE | 39389 | 39390 | CUR_HARM_99_PASSb43 | 10min 43rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99DF | 0x99E0 | 39391 | 39392 | CUR_HARM_99_PASSb44 | 10min 44th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99E1 | 0x99E2 | 39393 | 39394 | CUR_HARM_99_PASSb45 | 10min 45th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99E3 | 0x99E4 | 39395 | 39396 | CUR_HARM_99_PASSb46 | 10min 46th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99E5 | 0x99E6 | 39397 | 39398 | CUR_HARM_99_PASSb47 | 10min 47th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99E7 | 0x99E8 | 39399 | 39400 | CUR_HARM_99_PASSb48 | 10min 48th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99E9 | 0x99EA | 39401 | 39402 | CUR_HARM_99_PASSb49 | 10min 49th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99EB | 0x99EC | 39403 | 39404 | CUR_HARM_99_PASSb50 | 10min 50th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99ED | 0x99EE | 39405 | 39406 | CUR_HARM_99_PASSc2 | 10min 2nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99EF | 0x99F0 | 39407 | 39408 | CUR_HARM_99_PASSc3 | 10min 3rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99F1 | 0x99F2 | 39409 | 39410 | CUR_HARM_99_PASSc4 | 10min 4th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99F3 | 0x99F4 | 39411 | 39412 | CUR_HARM_99_PASSc5 | 10min 5th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99F5 | 0x99F6 | 39413 | 39414 | CUR_HARM_99_PASSc6 | 10min 6th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99F7 | 0x99F8 | 39415 | 39416 | CUR_HARM_99_PASSc7 | 10min 7th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99F9 | 0x99FA | 39417 | 39418 | CUR_HARM_99_PASSc8 | 10min 8th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99FB | 0x99FC | 39419 | 39420 | CUR_HARM_99_PASSc9 | 10min 9th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99FD | 0x99FE | 39421 | 39422 | CUR_HARM_99_PASSc10 | 10min 10th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x99FF | 0x9A00 | 39423 | 39424 | CUR_HARM_99_PASSc11 | 10min 11st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A01 | 0x9A02 | 39425 | 39426 | CUR_HARM_99_PASSc12 | 10min 12nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A03 | 0x9A04 | 39427 | 39428 | CUR_HARM_99_PASSc13 | 10min 13rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A05 | 0x9A06 | 39429 | 39430 | CUR_HARM_99_PASSc14 | 10min 14th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A07 | 0x9A08 | 39431 | 39432 | CUR_HARM_99_PASSc15 | 10min 15th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A09 | 0x9A0A | 39433 | 39434 | CUR_HARM_99_PASSc16 | 10min 16th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A0B | 0x9A0C | 39435 | 39436 | CUR_HARM_99_PASSc17 | 10min 17th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A0D | 0x9A0E | 39437 | 39438 | CUR_HARM_99_PASSc18 | 10min 18th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A0F | 0x9A10 | 39439 | 39440 | CUR_HARM_99_PASSc19 | 10min 19th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A11 | 0x9A12 | 39441 | 39442 | CUR_HARM_99_PASSc20 | 10min 20th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A13 | 0x9A14 | 39443 | 39444 | CUR_HARM_99_PASSc21 | 10min 21st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A15 | 0x9A16 | 39445 | 39446 | CUR_HARM_99_PASSc22 | 10min 22nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A17 | 0x9A18 | 39447 | 39448 | CUR_HARM_99_PASSc23 | 10min 23rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A19 | 0x9A1A | 39449 | 39450 | CUR_HARM_99_PASSc24 | 10min 24th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A1B | 0x9A1C | 39451 | 39452 | CUR_HARM_99_PASSc25 | 10min 25th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A1D | 0x9A1E | 39453 | 39454 | CUR_HARM_99_PASSc26 | 10min 26th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A1F | 0x9A20 | 39455 | 39456 | CUR_HARM_99_PASSc27 | 10min 27th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A21 | 0x9A22 | 39457 | 39458 | CUR_HARM_99_PASSc28 | 10min 28th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A23 | 0x9A24 | 39459 | 39460 | CUR_HARM_99_PASSc29 | 10min 29th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A25 | 0x9A26 | 39461 | 39462 | CUR_HARM_99_PASSc30 | 10min 30th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A27 | 0x9A28 | 39463 | 39464 | CUR_HARM_99_PASSc31 | 10min 31st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A29 | 0x9A2A | 39465 | 39466 | CUR_HARM_99_PASSc32 | 10min 32nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A2B | 0x9A2C | 39467 | 39468 | CUR_HARM_99_PASSc33 | 10min 33rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A2D | 0x9A2E | 39469 | 39470 | CUR_HARM_99_PASSc34 | 10min 34th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A2F | 0x9A30 | 39471 | 39472 | CUR_HARM_99_PASSc35 | 10min 35th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A31 | 0x9A32 | 39473 | 39474 | CUR_HARM_99_PASSc36 | 10min 36th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A33 | 0x9A34 | 39475 | 39476 | CUR_HARM_99_PASSc37 | 10min 37th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A35 | 0x9A36 | 39477 | 39478 | CUR_HARM_99_PASSc38 | 10min 38th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A37 | 0x9A38 | 39479 | 39480 | CUR_HARM_99_PASSc39 | 10min 39th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A39 | 0x9A3A | 39481 | 39482 | CUR_HARM_99_PASSc40 | 10min 40th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A3B | 0x9A3C | 39483 | 39484 | CUR_HARM_99_PASSc41 | 10min 41st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A3D | 0x9A3E | 39485 | 39486 | CUR_HARM_99_PASSc42 | 10min 42nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A3F | 0x9A40 | 39487 | 39488 | CUR_HARM_99_PASSc43 | 10min 43rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A41 | 0x9A42 | 39489 | 39490 | CUR_HARM_99_PASSc44 | 10min 44th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A43 | 0x9A44 | 39491 | 39492 | CUR_HARM_99_PASSc45 | 10min 45th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A45 | 0x9A46 | 39493 | 39494 | CUR_HARM_99_PASSc46 | 10min 46th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A47 | 0x9A48 | 39495 | 39496 | CUR_HARM_99_PASSc47 | 10min 47th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A49 | 0x9A4A | 39497 | 39498 | CUR_HARM_99_PASSc48 | 10min 48th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A4B | 0x9A4C | 39499 | 39500 | CUR_HARM_99_PASSc49 | 10min 49th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0x9A4D | 0x9A4E | 39501 | 39502 | CUR_HARM_99_PASSc50 | 10min 50th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
PQ Report 519 Weekly Past | [5 empty] | FALSE
0x9B00 | 0x9B00 | 39680 | 39680 | LAST_N_VALID | Last Period 10min 519 Report Valid Circle Counter | uint16 | 1 | R
0x9B01 | 0x9B01 | 39681 | 39681 | LAST_N_THDa | Last Period 10min Phase A THD Counter | uint16 | 1 | R
0x9B02 | 0x9B02 | 39682 | 39682 | LAST_N_THDb | Last Period 10min Phase B THD Counter | uint16 | 1 | R
0x9B03 | 0x9B03 | 39683 | 39683 | LAST_N_THDc | Last Period 10min Phase C THD Counter | uint16 | 1 | R
0x9B04 | 0x9B05 | 39684 | 39685 | LAST_THD_PASSa | Last Period 10min Phase A THD Trigger Pass Rate | float | 2 | R
0x9B06 | 0x9B07 | 39686 | 39687 | LAST_THD_PASSb | Last Period 10min Phase B THD Trigger Pass Rate | float | 2 | R
0x9B08 | 0x9B09 | 39688 | 39689 | LAST_THD_PASSc | Last Period 10min Phase C THD Trigger Pass Rate | float | 2 | R
0x9B0A | 0x9B0B | 39690 | 39691 | LAST_THD_MAXa | Last Period 10min Phase A THD Maximum Value | float | 2 | R
0x9B0C | 0x9B0D | 39692 | 39693 | LAST_THD_MAXb | Last Period 10min Phase B THD Maximum Value | float | 2 | R
0x9B0E | 0x9B0F | 39694 | 39695 | LAST_THD_MAXc | Last Period 10min Phase C THD Maximum Value | float | 2 | R
0x9B10 | 0x9B11 | 39696 | 39697 | LAST_THD_MINa | Last Period 10min Phase A THD Minimum Value | float | 2 | R
0x9B12 | 0x9B13 | 39698 | 39699 | LAST_THD_MINb | Last Period 10min Phase B THD Minimum Value | float | 2 | R
0x9B14 | 0x9B15 | 39700 | 39701 | LAST_THD_MINc | Last Period 10min Phase C THD Minimum Value | float | 2 | R
0x9B16 | 0x9B17 | 39702 | 39703 | LAST_THD_AVGa | Last Period 10min Phase A THD Average Value | float | 2 | R
0x9B18 | 0x9B19 | 39704 | 39705 | LAST_THD_AVGb | Last Period 10min Phase B THD Average Value | float | 2 | R
0x9B1A | 0x9B1B | 39706 | 39707 | LAST_THD_AVGc | Last Period 10min Phase C THD Average Value | float | 2 | R
0x9B1C | 0x9B1C | 39708 | 39708 | LAST_N_VOL_HARMa2 | Last Period 10min 2nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B1D | 0x9B1D | 39709 | 39709 | LAST_N_VOL_HARMa3 | Last Period 10min 3rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B1E | 0x9B1E | 39710 | 39710 | LAST_N_VOL_HARMa4 | Last Period 10min 4th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B1F | 0x9B1F | 39711 | 39711 | LAST_N_VOL_HARMa5 | Last Period 10min 5th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B20 | 0x9B20 | 39712 | 39712 | LAST_N_VOL_HARMa6 | Last Period 10min 6th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B21 | 0x9B21 | 39713 | 39713 | LAST_N_VOL_HARMa7 | Last Period 10min 7th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B22 | 0x9B22 | 39714 | 39714 | LAST_N_VOL_HARMa8 | Last Period 10min 8th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B23 | 0x9B23 | 39715 | 39715 | LAST_N_VOL_HARMa9 | Last Period 10min 9th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B24 | 0x9B24 | 39716 | 39716 | LAST_N_VOL_HARMa10 | Last Period 10min 10th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B25 | 0x9B25 | 39717 | 39717 | LAST_N_VOL_HARMa11 | Last Period 10min 11st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B26 | 0x9B26 | 39718 | 39718 | LAST_N_VOL_HARMa12 | Last Period 10min 12nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B27 | 0x9B27 | 39719 | 39719 | LAST_N_VOL_HARMa13 | Last Period 10min 13rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B28 | 0x9B28 | 39720 | 39720 | LAST_N_VOL_HARMa14 | Last Period 10min 14th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B29 | 0x9B29 | 39721 | 39721 | LAST_N_VOL_HARMa15 | Last Period 10min 15th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B2A | 0x9B2A | 39722 | 39722 | LAST_N_VOL_HARMa16 | Last Period 10min 16th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B2B | 0x9B2B | 39723 | 39723 | LAST_N_VOL_HARMa17 | Last Period 10min 17th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B2C | 0x9B2C | 39724 | 39724 | LAST_N_VOL_HARMa18 | Last Period 10min 18th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B2D | 0x9B2D | 39725 | 39725 | LAST_N_VOL_HARMa19 | Last Period 10min 19th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B2E | 0x9B2E | 39726 | 39726 | LAST_N_VOL_HARMa20 | Last Period 10min 20th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B2F | 0x9B2F | 39727 | 39727 | LAST_N_VOL_HARMa21 | Last Period 10min 21st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B30 | 0x9B30 | 39728 | 39728 | LAST_N_VOL_HARMa22 | Last Period 10min 22nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B31 | 0x9B31 | 39729 | 39729 | LAST_N_VOL_HARMa23 | Last Period 10min 23rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B32 | 0x9B32 | 39730 | 39730 | LAST_N_VOL_HARMa24 | Last Period 10min 24th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B33 | 0x9B33 | 39731 | 39731 | LAST_N_VOL_HARMa25 | Last Period 10min 25th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B34 | 0x9B34 | 39732 | 39732 | LAST_N_VOL_HARMa26 | Last Period 10min 26th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B35 | 0x9B35 | 39733 | 39733 | LAST_N_VOL_HARMa27 | Last Period 10min 27th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B36 | 0x9B36 | 39734 | 39734 | LAST_N_VOL_HARMa28 | Last Period 10min 28th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B37 | 0x9B37 | 39735 | 39735 | LAST_N_VOL_HARMa29 | Last Period 10min 29th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B38 | 0x9B38 | 39736 | 39736 | LAST_N_VOL_HARMa30 | Last Period 10min 30th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B39 | 0x9B39 | 39737 | 39737 | LAST_N_VOL_HARMa31 | Last Period 10min 31st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B3A | 0x9B3A | 39738 | 39738 | LAST_N_VOL_HARMa32 | Last Period 10min 32nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B3B | 0x9B3B | 39739 | 39739 | LAST_N_VOL_HARMa33 | Last Period 10min 33rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B3C | 0x9B3C | 39740 | 39740 | LAST_N_VOL_HARMa34 | Last Period 10min 34th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B3D | 0x9B3D | 39741 | 39741 | LAST_N_VOL_HARMa35 | Last Period 10min 35th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B3E | 0x9B3E | 39742 | 39742 | LAST_N_VOL_HARMa36 | Last Period 10min 36th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B3F | 0x9B3F | 39743 | 39743 | LAST_N_VOL_HARMa37 | Last Period 10min 37th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B40 | 0x9B40 | 39744 | 39744 | LAST_N_VOL_HARMa38 | Last Period 10min 38th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B41 | 0x9B41 | 39745 | 39745 | LAST_N_VOL_HARMa39 | Last Period 10min 39th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B42 | 0x9B42 | 39746 | 39746 | LAST_N_VOL_HARMa40 | Last Period 10min 40th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B43 | 0x9B43 | 39747 | 39747 | LAST_N_VOL_HARMa41 | Last Period 10min 41st Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B44 | 0x9B44 | 39748 | 39748 | LAST_N_VOL_HARMa42 | Last Period 10min 42nd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B45 | 0x9B45 | 39749 | 39749 | LAST_N_VOL_HARMa43 | Last Period 10min 43rd Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B46 | 0x9B46 | 39750 | 39750 | LAST_N_VOL_HARMa44 | Last Period 10min 44th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B47 | 0x9B47 | 39751 | 39751 | LAST_N_VOL_HARMa45 | Last Period 10min 45th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B48 | 0x9B48 | 39752 | 39752 | LAST_N_VOL_HARMa46 | Last Period 10min 46th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B49 | 0x9B49 | 39753 | 39753 | LAST_N_VOL_HARMa47 | Last Period 10min 47th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B4A | 0x9B4A | 39754 | 39754 | LAST_N_VOL_HARMa48 | Last Period 10min 48th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B4B | 0x9B4B | 39755 | 39755 | LAST_N_VOL_HARMa49 | Last Period 10min 49th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B4C | 0x9B4C | 39756 | 39756 | LAST_N_VOL_HARMa50 | Last Period 10min 50th Phase A Voltage Harmonics Counter | uint16 | 1 | R
0x9B4D | 0x9B4D | 39757 | 39757 | LAST_N_VOL_HARMb2 | Last Period 10min 2nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B4E | 0x9B4E | 39758 | 39758 | LAST_N_VOL_HARMb3 | Last Period 10min 3rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B4F | 0x9B4F | 39759 | 39759 | LAST_N_VOL_HARMb4 | Last Period 10min 4th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B50 | 0x9B50 | 39760 | 39760 | LAST_N_VOL_HARMb5 | Last Period 10min 5th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B51 | 0x9B51 | 39761 | 39761 | LAST_N_VOL_HARMb6 | Last Period 10min 6th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B52 | 0x9B52 | 39762 | 39762 | LAST_N_VOL_HARMb7 | Last Period 10min 7th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B53 | 0x9B53 | 39763 | 39763 | LAST_N_VOL_HARMb8 | Last Period 10min 8th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B54 | 0x9B54 | 39764 | 39764 | LAST_N_VOL_HARMb9 | Last Period 10min 9th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B55 | 0x9B55 | 39765 | 39765 | LAST_N_VOL_HARMb10 | Last Period 10min 10th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B56 | 0x9B56 | 39766 | 39766 | LAST_N_VOL_HARMb11 | Last Period 10min 11st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B57 | 0x9B57 | 39767 | 39767 | LAST_N_VOL_HARMb12 | Last Period 10min 12nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B58 | 0x9B58 | 39768 | 39768 | LAST_N_VOL_HARMb13 | Last Period 10min 13rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B59 | 0x9B59 | 39769 | 39769 | LAST_N_VOL_HARMb14 | Last Period 10min 14th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B5A | 0x9B5A | 39770 | 39770 | LAST_N_VOL_HARMb15 | Last Period 10min 15th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B5B | 0x9B5B | 39771 | 39771 | LAST_N_VOL_HARMb16 | Last Period 10min 16th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B5C | 0x9B5C | 39772 | 39772 | LAST_N_VOL_HARMb17 | Last Period 10min 17th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B5D | 0x9B5D | 39773 | 39773 | LAST_N_VOL_HARMb18 | Last Period 10min 18th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B5E | 0x9B5E | 39774 | 39774 | LAST_N_VOL_HARMb19 | Last Period 10min 19th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B5F | 0x9B5F | 39775 | 39775 | LAST_N_VOL_HARMb20 | Last Period 10min 20th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B60 | 0x9B60 | 39776 | 39776 | LAST_N_VOL_HARMb21 | Last Period 10min 21st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B61 | 0x9B61 | 39777 | 39777 | LAST_N_VOL_HARMb22 | Last Period 10min 22nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B62 | 0x9B62 | 39778 | 39778 | LAST_N_VOL_HARMb23 | Last Period 10min 23rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B63 | 0x9B63 | 39779 | 39779 | LAST_N_VOL_HARMb24 | Last Period 10min 24th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B64 | 0x9B64 | 39780 | 39780 | LAST_N_VOL_HARMb25 | Last Period 10min 25th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B65 | 0x9B65 | 39781 | 39781 | LAST_N_VOL_HARMb26 | Last Period 10min 26th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B66 | 0x9B66 | 39782 | 39782 | LAST_N_VOL_HARMb27 | Last Period 10min 27th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B67 | 0x9B67 | 39783 | 39783 | LAST_N_VOL_HARMb28 | Last Period 10min 28th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B68 | 0x9B68 | 39784 | 39784 | LAST_N_VOL_HARMb29 | Last Period 10min 29th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B69 | 0x9B69 | 39785 | 39785 | LAST_N_VOL_HARMb30 | Last Period 10min 30th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B6A | 0x9B6A | 39786 | 39786 | LAST_N_VOL_HARMb31 | Last Period 10min 31st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B6B | 0x9B6B | 39787 | 39787 | LAST_N_VOL_HARMb32 | Last Period 10min 32nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B6C | 0x9B6C | 39788 | 39788 | LAST_N_VOL_HARMb33 | Last Period 10min 33rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B6D | 0x9B6D | 39789 | 39789 | LAST_N_VOL_HARMb34 | Last Period 10min 34th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B6E | 0x9B6E | 39790 | 39790 | LAST_N_VOL_HARMb35 | Last Period 10min 35th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B6F | 0x9B6F | 39791 | 39791 | LAST_N_VOL_HARMb36 | Last Period 10min 36th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B70 | 0x9B70 | 39792 | 39792 | LAST_N_VOL_HARMb37 | Last Period 10min 37th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B71 | 0x9B71 | 39793 | 39793 | LAST_N_VOL_HARMb38 | Last Period 10min 38th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B72 | 0x9B72 | 39794 | 39794 | LAST_N_VOL_HARMb39 | Last Period 10min 39th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B73 | 0x9B73 | 39795 | 39795 | LAST_N_VOL_HARMb40 | Last Period 10min 40th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B74 | 0x9B74 | 39796 | 39796 | LAST_N_VOL_HARMb41 | Last Period 10min 41st Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B75 | 0x9B75 | 39797 | 39797 | LAST_N_VOL_HARMb42 | Last Period 10min 42nd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B76 | 0x9B76 | 39798 | 39798 | LAST_N_VOL_HARMb43 | Last Period 10min 43rd Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B77 | 0x9B77 | 39799 | 39799 | LAST_N_VOL_HARMb44 | Last Period 10min 44th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B78 | 0x9B78 | 39800 | 39800 | LAST_N_VOL_HARMb45 | Last Period 10min 45th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B79 | 0x9B79 | 39801 | 39801 | LAST_N_VOL_HARMb46 | Last Period 10min 46th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B7A | 0x9B7A | 39802 | 39802 | LAST_N_VOL_HARMb47 | Last Period 10min 47th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B7B | 0x9B7B | 39803 | 39803 | LAST_N_VOL_HARMb48 | Last Period 10min 48th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B7C | 0x9B7C | 39804 | 39804 | LAST_N_VOL_HARMb49 | Last Period 10min 49th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B7D | 0x9B7D | 39805 | 39805 | LAST_N_VOL_HARMb50 | Last Period 10min 50th Phase B Voltage Harmonics Counter | uint16 | 1 | R
0x9B7E | 0x9B7E | 39806 | 39806 | LAST_N_VOL_HARMc2 | Last Period 10min 2nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B7F | 0x9B7F | 39807 | 39807 | LAST_N_VOL_HARMc3 | Last Period 10min 3rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B80 | 0x9B80 | 39808 | 39808 | LAST_N_VOL_HARMc4 | Last Period 10min 4th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B81 | 0x9B81 | 39809 | 39809 | LAST_N_VOL_HARMc5 | Last Period 10min 5th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B82 | 0x9B82 | 39810 | 39810 | LAST_N_VOL_HARMc6 | Last Period 10min 6th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B83 | 0x9B83 | 39811 | 39811 | LAST_N_VOL_HARMc7 | Last Period 10min 7th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B84 | 0x9B84 | 39812 | 39812 | LAST_N_VOL_HARMc8 | Last Period 10min 8th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B85 | 0x9B85 | 39813 | 39813 | LAST_N_VOL_HARMc9 | Last Period 10min 9th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B86 | 0x9B86 | 39814 | 39814 | LAST_N_VOL_HARMc10 | Last Period 10min 10th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B87 | 0x9B87 | 39815 | 39815 | LAST_N_VOL_HARMc11 | Last Period 10min 11st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B88 | 0x9B88 | 39816 | 39816 | LAST_N_VOL_HARMc12 | Last Period 10min 12nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B89 | 0x9B89 | 39817 | 39817 | LAST_N_VOL_HARMc13 | Last Period 10min 13rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B8A | 0x9B8A | 39818 | 39818 | LAST_N_VOL_HARMc14 | Last Period 10min 14th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B8B | 0x9B8B | 39819 | 39819 | LAST_N_VOL_HARMc15 | Last Period 10min 15th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B8C | 0x9B8C | 39820 | 39820 | LAST_N_VOL_HARMc16 | Last Period 10min 16th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B8D | 0x9B8D | 39821 | 39821 | LAST_N_VOL_HARMc17 | Last Period 10min 17th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B8E | 0x9B8E | 39822 | 39822 | LAST_N_VOL_HARMc18 | Last Period 10min 18th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B8F | 0x9B8F | 39823 | 39823 | LAST_N_VOL_HARMc19 | Last Period 10min 19th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B90 | 0x9B90 | 39824 | 39824 | LAST_N_VOL_HARMc20 | Last Period 10min 20th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B91 | 0x9B91 | 39825 | 39825 | LAST_N_VOL_HARMc21 | Last Period 10min 21st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B92 | 0x9B92 | 39826 | 39826 | LAST_N_VOL_HARMc22 | Last Period 10min 22nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B93 | 0x9B93 | 39827 | 39827 | LAST_N_VOL_HARMc23 | Last Period 10min 23rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B94 | 0x9B94 | 39828 | 39828 | LAST_N_VOL_HARMc24 | Last Period 10min 24th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B95 | 0x9B95 | 39829 | 39829 | LAST_N_VOL_HARMc25 | Last Period 10min 25th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B96 | 0x9B96 | 39830 | 39830 | LAST_N_VOL_HARMc26 | Last Period 10min 26th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B97 | 0x9B97 | 39831 | 39831 | LAST_N_VOL_HARMc27 | Last Period 10min 27th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B98 | 0x9B98 | 39832 | 39832 | LAST_N_VOL_HARMc28 | Last Period 10min 28th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B99 | 0x9B99 | 39833 | 39833 | LAST_N_VOL_HARMc29 | Last Period 10min 29th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B9A | 0x9B9A | 39834 | 39834 | LAST_N_VOL_HARMc30 | Last Period 10min 30th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B9B | 0x9B9B | 39835 | 39835 | LAST_N_VOL_HARMc31 | Last Period 10min 31st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B9C | 0x9B9C | 39836 | 39836 | LAST_N_VOL_HARMc32 | Last Period 10min 32nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B9D | 0x9B9D | 39837 | 39837 | LAST_N_VOL_HARMc33 | Last Period 10min 33rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B9E | 0x9B9E | 39838 | 39838 | LAST_N_VOL_HARMc34 | Last Period 10min 34th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9B9F | 0x9B9F | 39839 | 39839 | LAST_N_VOL_HARMc35 | Last Period 10min 35th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BA0 | 0x9BA0 | 39840 | 39840 | LAST_N_VOL_HARMc36 | Last Period 10min 36th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BA1 | 0x9BA1 | 39841 | 39841 | LAST_N_VOL_HARMc37 | Last Period 10min 37th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BA2 | 0x9BA2 | 39842 | 39842 | LAST_N_VOL_HARMc38 | Last Period 10min 38th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BA3 | 0x9BA3 | 39843 | 39843 | LAST_N_VOL_HARMc39 | Last Period 10min 39th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BA4 | 0x9BA4 | 39844 | 39844 | LAST_N_VOL_HARMc40 | Last Period 10min 40th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BA5 | 0x9BA5 | 39845 | 39845 | LAST_N_VOL_HARMc41 | Last Period 10min 41st Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BA6 | 0x9BA6 | 39846 | 39846 | LAST_N_VOL_HARMc42 | Last Period 10min 42nd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BA7 | 0x9BA7 | 39847 | 39847 | LAST_N_VOL_HARMc43 | Last Period 10min 43rd Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BA8 | 0x9BA8 | 39848 | 39848 | LAST_N_VOL_HARMc44 | Last Period 10min 44th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BA9 | 0x9BA9 | 39849 | 39849 | LAST_N_VOL_HARMc45 | Last Period 10min 45th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BAA | 0x9BAA | 39850 | 39850 | LAST_N_VOL_HARMc46 | Last Period 10min 46th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BAB | 0x9BAB | 39851 | 39851 | LAST_N_VOL_HARMc47 | Last Period 10min 47th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BAC | 0x9BAC | 39852 | 39852 | LAST_N_VOL_HARMc48 | Last Period 10min 48th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BAD | 0x9BAD | 39853 | 39853 | LAST_N_VOL_HARMc49 | Last Period 10min 49th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BAE | 0x9BAE | 39854 | 39854 | LAST_N_VOL_HARMc50 | Last Period 10min 50th Phase C Voltage Harmonics Counter | uint16 | 1 | R
0x9BAF | 0x9BB0 | 39855 | 39856 | LAST_VOL_HARM_PASSa2 | Last Period 10min 2nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BB1 | 0x9BB2 | 39857 | 39858 | LAST_VOL_HARM_PASSa3 | Last Period 10min 3rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BB3 | 0x9BB4 | 39859 | 39860 | LAST_VOL_HARM_PASSa4 | Last Period 10min 4th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BB5 | 0x9BB6 | 39861 | 39862 | LAST_VOL_HARM_PASSa5 | Last Period 10min 5th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BB7 | 0x9BB8 | 39863 | 39864 | LAST_VOL_HARM_PASSa6 | Last Period 10min 6th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BB9 | 0x9BBA | 39865 | 39866 | LAST_VOL_HARM_PASSa7 | Last Period 10min 7th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BBB | 0x9BBC | 39867 | 39868 | LAST_VOL_HARM_PASSa8 | Last Period 10min 8th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BBD | 0x9BBE | 39869 | 39870 | LAST_VOL_HARM_PASSa9 | Last Period 10min 9th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BBF | 0x9BC0 | 39871 | 39872 | LAST_VOL_HARM_PASSa10 | Last Period 10min 10th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BC1 | 0x9BC2 | 39873 | 39874 | LAST_VOL_HARM_PASSa11 | Last Period 10min 11st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BC3 | 0x9BC4 | 39875 | 39876 | LAST_VOL_HARM_PASSa12 | Last Period 10min 12nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BC5 | 0x9BC6 | 39877 | 39878 | LAST_VOL_HARM_PASSa13 | Last Period 10min 13rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BC7 | 0x9BC8 | 39879 | 39880 | LAST_VOL_HARM_PASSa14 | Last Period 10min 14th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BC9 | 0x9BCA | 39881 | 39882 | LAST_VOL_HARM_PASSa15 | Last Period 10min 15th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BCB | 0x9BCC | 39883 | 39884 | LAST_VOL_HARM_PASSa16 | Last Period 10min 16th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BCD | 0x9BCE | 39885 | 39886 | LAST_VOL_HARM_PASSa17 | Last Period 10min 17th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BCF | 0x9BD0 | 39887 | 39888 | LAST_VOL_HARM_PASSa18 | Last Period 10min 18th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BD1 | 0x9BD2 | 39889 | 39890 | LAST_VOL_HARM_PASSa19 | Last Period 10min 19th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BD3 | 0x9BD4 | 39891 | 39892 | LAST_VOL_HARM_PASSa20 | Last Period 10min 20th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BD5 | 0x9BD6 | 39893 | 39894 | LAST_VOL_HARM_PASSa21 | Last Period 10min 21st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BD7 | 0x9BD8 | 39895 | 39896 | LAST_VOL_HARM_PASSa22 | Last Period 10min 22nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BD9 | 0x9BDA | 39897 | 39898 | LAST_VOL_HARM_PASSa23 | Last Period 10min 23rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BDB | 0x9BDC | 39899 | 39900 | LAST_VOL_HARM_PASSa24 | Last Period 10min 24th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BDD | 0x9BDE | 39901 | 39902 | LAST_VOL_HARM_PASSa25 | Last Period 10min 25th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BDF | 0x9BE0 | 39903 | 39904 | LAST_VOL_HARM_PASSa26 | Last Period 10min 26th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BE1 | 0x9BE2 | 39905 | 39906 | LAST_VOL_HARM_PASSa27 | Last Period 10min 27th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BE3 | 0x9BE4 | 39907 | 39908 | LAST_VOL_HARM_PASSa28 | Last Period 10min 28th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BE5 | 0x9BE6 | 39909 | 39910 | LAST_VOL_HARM_PASSa29 | Last Period 10min 29th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BE7 | 0x9BE8 | 39911 | 39912 | LAST_VOL_HARM_PASSa30 | Last Period 10min 30th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BE9 | 0x9BEA | 39913 | 39914 | LAST_VOL_HARM_PASSa31 | Last Period 10min 31st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BEB | 0x9BEC | 39915 | 39916 | LAST_VOL_HARM_PASSa32 | Last Period 10min 32nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BED | 0x9BEE | 39917 | 39918 | LAST_VOL_HARM_PASSa33 | Last Period 10min 33rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BEF | 0x9BF0 | 39919 | 39920 | LAST_VOL_HARM_PASSa34 | Last Period 10min 34th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BF1 | 0x9BF2 | 39921 | 39922 | LAST_VOL_HARM_PASSa35 | Last Period 10min 35th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BF3 | 0x9BF4 | 39923 | 39924 | LAST_VOL_HARM_PASSa36 | Last Period 10min 36th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BF5 | 0x9BF6 | 39925 | 39926 | LAST_VOL_HARM_PASSa37 | Last Period 10min 37th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BF7 | 0x9BF8 | 39927 | 39928 | LAST_VOL_HARM_PASSa38 | Last Period 10min 38th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BF9 | 0x9BFA | 39929 | 39930 | LAST_VOL_HARM_PASSa39 | Last Period 10min 39th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BFB | 0x9BFC | 39931 | 39932 | LAST_VOL_HARM_PASSa40 | Last Period 10min 40th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BFD | 0x9BFE | 39933 | 39934 | LAST_VOL_HARM_PASSa41 | Last Period 10min 41st Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9BFF | 0x9C00 | 39935 | 39936 | LAST_VOL_HARM_PASSa42 | Last Period 10min 42nd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9C01 | 0x9C02 | 39937 | 39938 | LAST_VOL_HARM_PASSa43 | Last Period 10min 43rd Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9C03 | 0x9C04 | 39939 | 39940 | LAST_VOL_HARM_PASSa44 | Last Period 10min 44th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9C05 | 0x9C06 | 39941 | 39942 | LAST_VOL_HARM_PASSa45 | Last Period 10min 45th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9C07 | 0x9C08 | 39943 | 39944 | LAST_VOL_HARM_PASSa46 | Last Period 10min 46th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9C09 | 0x9C0A | 39945 | 39946 | LAST_VOL_HARM_PASSa47 | Last Period 10min 47th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9C0B | 0x9C0C | 39947 | 39948 | LAST_VOL_HARM_PASSa48 | Last Period 10min 48th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9C0D | 0x9C0E | 39949 | 39950 | LAST_VOL_HARM_PASSa49 | Last Period 10min 49th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9C0F | 0x9C10 | 39951 | 39952 | LAST_VOL_HARM_PASSa50 | Last Period 10min 50th Phase A Voltage Harmonics Pass Rate | float | 2 | R
0x9C11 | 0x9C12 | 39953 | 39954 | LAST_VOL_HARM_PASSb2 | Last Period 10min 2nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C13 | 0x9C14 | 39955 | 39956 | LAST_VOL_HARM_PASSb3 | Last Period 10min 3rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C15 | 0x9C16 | 39957 | 39958 | LAST_VOL_HARM_PASSb4 | Last Period 10min 4th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C17 | 0x9C18 | 39959 | 39960 | LAST_VOL_HARM_PASSb5 | Last Period 10min 5th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C19 | 0x9C1A | 39961 | 39962 | LAST_VOL_HARM_PASSb6 | Last Period 10min 6th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C1B | 0x9C1C | 39963 | 39964 | LAST_VOL_HARM_PASSb7 | Last Period 10min 7th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C1D | 0x9C1E | 39965 | 39966 | LAST_VOL_HARM_PASSb8 | Last Period 10min 8th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C1F | 0x9C20 | 39967 | 39968 | LAST_VOL_HARM_PASSb9 | Last Period 10min 9th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C21 | 0x9C22 | 39969 | 39970 | LAST_VOL_HARM_PASSb10 | Last Period 10min 10th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C23 | 0x9C24 | 39971 | 39972 | LAST_VOL_HARM_PASSb11 | Last Period 10min 11st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C25 | 0x9C26 | 39973 | 39974 | LAST_VOL_HARM_PASSb12 | Last Period 10min 12nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C27 | 0x9C28 | 39975 | 39976 | LAST_VOL_HARM_PASSb13 | Last Period 10min 13rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C29 | 0x9C2A | 39977 | 39978 | LAST_VOL_HARM_PASSb14 | Last Period 10min 14th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C2B | 0x9C2C | 39979 | 39980 | LAST_VOL_HARM_PASSb15 | Last Period 10min 15th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C2D | 0x9C2E | 39981 | 39982 | LAST_VOL_HARM_PASSb16 | Last Period 10min 16th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C2F | 0x9C30 | 39983 | 39984 | LAST_VOL_HARM_PASSb17 | Last Period 10min 17th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C31 | 0x9C32 | 39985 | 39986 | LAST_VOL_HARM_PASSb18 | Last Period 10min 18th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C33 | 0x9C34 | 39987 | 39988 | LAST_VOL_HARM_PASSb19 | Last Period 10min 19th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C35 | 0x9C36 | 39989 | 39990 | LAST_VOL_HARM_PASSb20 | Last Period 10min 20th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C37 | 0x9C38 | 39991 | 39992 | LAST_VOL_HARM_PASSb21 | Last Period 10min 21st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C39 | 0x9C3A | 39993 | 39994 | LAST_VOL_HARM_PASSb22 | Last Period 10min 22nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C3B | 0x9C3C | 39995 | 39996 | LAST_VOL_HARM_PASSb23 | Last Period 10min 23rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C3D | 0x9C3E | 39997 | 39998 | LAST_VOL_HARM_PASSb24 | Last Period 10min 24th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C3F | 0x9C40 | 39999 | 40000 | LAST_VOL_HARM_PASSb25 | Last Period 10min 25th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C41 | 0x9C42 | 40001 | 40002 | LAST_VOL_HARM_PASSb26 | Last Period 10min 26th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C43 | 0x9C44 | 40003 | 40004 | LAST_VOL_HARM_PASSb27 | Last Period 10min 27th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C45 | 0x9C46 | 40005 | 40006 | LAST_VOL_HARM_PASSb28 | Last Period 10min 28th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C47 | 0x9C48 | 40007 | 40008 | LAST_VOL_HARM_PASSb29 | Last Period 10min 29th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C49 | 0x9C4A | 40009 | 40010 | LAST_VOL_HARM_PASSb30 | Last Period 10min 30th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C4B | 0x9C4C | 40011 | 40012 | LAST_VOL_HARM_PASSb31 | Last Period 10min 31st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C4D | 0x9C4E | 40013 | 40014 | LAST_VOL_HARM_PASSb32 | Last Period 10min 32nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C4F | 0x9C50 | 40015 | 40016 | LAST_VOL_HARM_PASSb33 | Last Period 10min 33rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C51 | 0x9C52 | 40017 | 40018 | LAST_VOL_HARM_PASSb34 | Last Period 10min 34th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C53 | 0x9C54 | 40019 | 40020 | LAST_VOL_HARM_PASSb35 | Last Period 10min 35th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C55 | 0x9C56 | 40021 | 40022 | LAST_VOL_HARM_PASSb36 | Last Period 10min 36th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C57 | 0x9C58 | 40023 | 40024 | LAST_VOL_HARM_PASSb37 | Last Period 10min 37th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C59 | 0x9C5A | 40025 | 40026 | LAST_VOL_HARM_PASSb38 | Last Period 10min 38th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C5B | 0x9C5C | 40027 | 40028 | LAST_VOL_HARM_PASSb39 | Last Period 10min 39th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C5D | 0x9C5E | 40029 | 40030 | LAST_VOL_HARM_PASSb40 | Last Period 10min 40th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C5F | 0x9C60 | 40031 | 40032 | LAST_VOL_HARM_PASSb41 | Last Period 10min 41st Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C61 | 0x9C62 | 40033 | 40034 | LAST_VOL_HARM_PASSb42 | Last Period 10min 42nd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C63 | 0x9C64 | 40035 | 40036 | LAST_VOL_HARM_PASSb43 | Last Period 10min 43rd Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C65 | 0x9C66 | 40037 | 40038 | LAST_VOL_HARM_PASSb44 | Last Period 10min 44th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C67 | 0x9C68 | 40039 | 40040 | LAST_VOL_HARM_PASSb45 | Last Period 10min 45th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C69 | 0x9C6A | 40041 | 40042 | LAST_VOL_HARM_PASSb46 | Last Period 10min 46th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C6B | 0x9C6C | 40043 | 40044 | LAST_VOL_HARM_PASSb47 | Last Period 10min 47th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C6D | 0x9C6E | 40045 | 40046 | LAST_VOL_HARM_PASSb48 | Last Period 10min 48th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C6F | 0x9C70 | 40047 | 40048 | LAST_VOL_HARM_PASSb49 | Last Period 10min 49th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C71 | 0x9C72 | 40049 | 40050 | LAST_VOL_HARM_PASSb50 | Last Period 10min 50th Phase B Voltage Harmonics Pass Rate | float | 2 | R
0x9C73 | 0x9C74 | 40051 | 40052 | LAST_VOL_HARM_PASSc2 | Last Period 10min 2nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C75 | 0x9C76 | 40053 | 40054 | LAST_VOL_HARM_PASSc3 | Last Period 10min 3rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C77 | 0x9C78 | 40055 | 40056 | LAST_VOL_HARM_PASSc4 | Last Period 10min 4th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C79 | 0x9C7A | 40057 | 40058 | LAST_VOL_HARM_PASSc5 | Last Period 10min 5th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C7B | 0x9C7C | 40059 | 40060 | LAST_VOL_HARM_PASSc6 | Last Period 10min 6th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C7D | 0x9C7E | 40061 | 40062 | LAST_VOL_HARM_PASSc7 | Last Period 10min 7th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C7F | 0x9C80 | 40063 | 40064 | LAST_VOL_HARM_PASSc8 | Last Period 10min 8th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C81 | 0x9C82 | 40065 | 40066 | LAST_VOL_HARM_PASSc9 | Last Period 10min 9th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C83 | 0x9C84 | 40067 | 40068 | LAST_VOL_HARM_PASSc10 | Last Period 10min 10th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C85 | 0x9C86 | 40069 | 40070 | LAST_VOL_HARM_PASSc11 | Last Period 10min 11st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C87 | 0x9C88 | 40071 | 40072 | LAST_VOL_HARM_PASSc12 | Last Period 10min 12nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C89 | 0x9C8A | 40073 | 40074 | LAST_VOL_HARM_PASSc13 | Last Period 10min 13rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C8B | 0x9C8C | 40075 | 40076 | LAST_VOL_HARM_PASSc14 | Last Period 10min 14th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C8D | 0x9C8E | 40077 | 40078 | LAST_VOL_HARM_PASSc15 | Last Period 10min 15th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C8F | 0x9C90 | 40079 | 40080 | LAST_VOL_HARM_PASSc16 | Last Period 10min 16th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C91 | 0x9C92 | 40081 | 40082 | LAST_VOL_HARM_PASSc17 | Last Period 10min 17th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C93 | 0x9C94 | 40083 | 40084 | LAST_VOL_HARM_PASSc18 | Last Period 10min 18th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C95 | 0x9C96 | 40085 | 40086 | LAST_VOL_HARM_PASSc19 | Last Period 10min 19th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C97 | 0x9C98 | 40087 | 40088 | LAST_VOL_HARM_PASSc20 | Last Period 10min 20th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C99 | 0x9C9A | 40089 | 40090 | LAST_VOL_HARM_PASSc21 | Last Period 10min 21st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C9B | 0x9C9C | 40091 | 40092 | LAST_VOL_HARM_PASSc22 | Last Period 10min 22nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C9D | 0x9C9E | 40093 | 40094 | LAST_VOL_HARM_PASSc23 | Last Period 10min 23rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9C9F | 0x9CA0 | 40095 | 40096 | LAST_VOL_HARM_PASSc24 | Last Period 10min 24th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CA1 | 0x9CA2 | 40097 | 40098 | LAST_VOL_HARM_PASSc25 | Last Period 10min 25th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CA3 | 0x9CA4 | 40099 | 40100 | LAST_VOL_HARM_PASSc26 | Last Period 10min 26th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CA5 | 0x9CA6 | 40101 | 40102 | LAST_VOL_HARM_PASSc27 | Last Period 10min 27th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CA7 | 0x9CA8 | 40103 | 40104 | LAST_VOL_HARM_PASSc28 | Last Period 10min 28th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CA9 | 0x9CAA | 40105 | 40106 | LAST_VOL_HARM_PASSc29 | Last Period 10min 29th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CAB | 0x9CAC | 40107 | 40108 | LAST_VOL_HARM_PASSc30 | Last Period 10min 30th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CAD | 0x9CAE | 40109 | 40110 | LAST_VOL_HARM_PASSc31 | Last Period 10min 31st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CAF | 0x9CB0 | 40111 | 40112 | LAST_VOL_HARM_PASSc32 | Last Period 10min 32nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CB1 | 0x9CB2 | 40113 | 40114 | LAST_VOL_HARM_PASSc33 | Last Period 10min 33rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CB3 | 0x9CB4 | 40115 | 40116 | LAST_VOL_HARM_PASSc34 | Last Period 10min 34th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CB5 | 0x9CB6 | 40117 | 40118 | LAST_VOL_HARM_PASSc35 | Last Period 10min 35th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CB7 | 0x9CB8 | 40119 | 40120 | LAST_VOL_HARM_PASSc36 | Last Period 10min 36th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CB9 | 0x9CBA | 40121 | 40122 | LAST_VOL_HARM_PASSc37 | Last Period 10min 37th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CBB | 0x9CBC | 40123 | 40124 | LAST_VOL_HARM_PASSc38 | Last Period 10min 38th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CBD | 0x9CBE | 40125 | 40126 | LAST_VOL_HARM_PASSc39 | Last Period 10min 39th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CBF | 0x9CC0 | 40127 | 40128 | LAST_VOL_HARM_PASSc40 | Last Period 10min 40th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CC1 | 0x9CC2 | 40129 | 40130 | LAST_VOL_HARM_PASSc41 | Last Period 10min 41st Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CC3 | 0x9CC4 | 40131 | 40132 | LAST_VOL_HARM_PASSc42 | Last Period 10min 42nd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CC5 | 0x9CC6 | 40133 | 40134 | LAST_VOL_HARM_PASSc43 | Last Period 10min 43rd Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CC7 | 0x9CC8 | 40135 | 40136 | LAST_VOL_HARM_PASSc44 | Last Period 10min 44th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CC9 | 0x9CCA | 40137 | 40138 | LAST_VOL_HARM_PASSc45 | Last Period 10min 45th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CCB | 0x9CCC | 40139 | 40140 | LAST_VOL_HARM_PASSc46 | Last Period 10min 46th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CCD | 0x9CCE | 40141 | 40142 | LAST_VOL_HARM_PASSc47 | Last Period 10min 47th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CCF | 0x9CD0 | 40143 | 40144 | LAST_VOL_HARM_PASSc48 | Last Period 10min 48th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CD1 | 0x9CD2 | 40145 | 40146 | LAST_VOL_HARM_PASSc49 | Last Period 10min 49th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CD3 | 0x9CD4 | 40147 | 40148 | LAST_VOL_HARM_PASSc50 | Last Period 10min 50th Phase C Voltage Harmonics Pass Rate | float | 2 | R
0x9CD5 | 0x9CD6 | 40149 | 40150 | LAST_VOL_HARM_MAXa2 | Last Period 10min 2nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CD7 | 0x9CD8 | 40151 | 40152 | LAST_VOL_HARM_MAXa3 | Last Period 10min 3rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CD9 | 0x9CDA | 40153 | 40154 | LAST_VOL_HARM_MAXa4 | Last Period 10min 4th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CDB | 0x9CDC | 40155 | 40156 | LAST_VOL_HARM_MAXa5 | Last Period 10min 5th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CDD | 0x9CDE | 40157 | 40158 | LAST_VOL_HARM_MAXa6 | Last Period 10min 6th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CDF | 0x9CE0 | 40159 | 40160 | LAST_VOL_HARM_MAXa7 | Last Period 10min 7th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CE1 | 0x9CE2 | 40161 | 40162 | LAST_VOL_HARM_MAXa8 | Last Period 10min 8th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CE3 | 0x9CE4 | 40163 | 40164 | LAST_VOL_HARM_MAXa9 | Last Period 10min 9th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CE5 | 0x9CE6 | 40165 | 40166 | LAST_VOL_HARM_MAXa10 | Last Period 10min 10th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CE7 | 0x9CE8 | 40167 | 40168 | LAST_VOL_HARM_MAXa11 | Last Period 10min 11st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CE9 | 0x9CEA | 40169 | 40170 | LAST_VOL_HARM_MAXa12 | Last Period 10min 12nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CEB | 0x9CEC | 40171 | 40172 | LAST_VOL_HARM_MAXa13 | Last Period 10min 13rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CED | 0x9CEE | 40173 | 40174 | LAST_VOL_HARM_MAXa14 | Last Period 10min 14th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CEF | 0x9CF0 | 40175 | 40176 | LAST_VOL_HARM_MAXa15 | Last Period 10min 15th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CF1 | 0x9CF2 | 40177 | 40178 | LAST_VOL_HARM_MAXa16 | Last Period 10min 16th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CF3 | 0x9CF4 | 40179 | 40180 | LAST_VOL_HARM_MAXa17 | Last Period 10min 17th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CF5 | 0x9CF6 | 40181 | 40182 | LAST_VOL_HARM_MAXa18 | Last Period 10min 18th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CF7 | 0x9CF8 | 40183 | 40184 | LAST_VOL_HARM_MAXa19 | Last Period 10min 19th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CF9 | 0x9CFA | 40185 | 40186 | LAST_VOL_HARM_MAXa20 | Last Period 10min 20th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CFB | 0x9CFC | 40187 | 40188 | LAST_VOL_HARM_MAXa21 | Last Period 10min 21st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CFD | 0x9CFE | 40189 | 40190 | LAST_VOL_HARM_MAXa22 | Last Period 10min 22nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9CFF | 0x9D00 | 40191 | 40192 | LAST_VOL_HARM_MAXa23 | Last Period 10min 23rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D01 | 0x9D02 | 40193 | 40194 | LAST_VOL_HARM_MAXa24 | Last Period 10min 24th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D03 | 0x9D04 | 40195 | 40196 | LAST_VOL_HARM_MAXa25 | Last Period 10min 25th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D05 | 0x9D06 | 40197 | 40198 | LAST_VOL_HARM_MAXa26 | Last Period 10min 26th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D07 | 0x9D08 | 40199 | 40200 | LAST_VOL_HARM_MAXa27 | Last Period 10min 27th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D09 | 0x9D0A | 40201 | 40202 | LAST_VOL_HARM_MAXa28 | Last Period 10min 28th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D0B | 0x9D0C | 40203 | 40204 | LAST_VOL_HARM_MAXa29 | Last Period 10min 29th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D0D | 0x9D0E | 40205 | 40206 | LAST_VOL_HARM_MAXa30 | Last Period 10min 30th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D0F | 0x9D10 | 40207 | 40208 | LAST_VOL_HARM_MAXa31 | Last Period 10min 31st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D11 | 0x9D12 | 40209 | 40210 | LAST_VOL_HARM_MAXa32 | Last Period 10min 32nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D13 | 0x9D14 | 40211 | 40212 | LAST_VOL_HARM_MAXa33 | Last Period 10min 33rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D15 | 0x9D16 | 40213 | 40214 | LAST_VOL_HARM_MAXa34 | Last Period 10min 34th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D17 | 0x9D18 | 40215 | 40216 | LAST_VOL_HARM_MAXa35 | Last Period 10min 35th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D19 | 0x9D1A | 40217 | 40218 | LAST_VOL_HARM_MAXa36 | Last Period 10min 36th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D1B | 0x9D1C | 40219 | 40220 | LAST_VOL_HARM_MAXa37 | Last Period 10min 37th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D1D | 0x9D1E | 40221 | 40222 | LAST_VOL_HARM_MAXa38 | Last Period 10min 38th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D1F | 0x9D20 | 40223 | 40224 | LAST_VOL_HARM_MAXa39 | Last Period 10min 39th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D21 | 0x9D22 | 40225 | 40226 | LAST_VOL_HARM_MAXa40 | Last Period 10min 40th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D23 | 0x9D24 | 40227 | 40228 | LAST_VOL_HARM_MAXa41 | Last Period 10min 41st Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D25 | 0x9D26 | 40229 | 40230 | LAST_VOL_HARM_MAXa42 | Last Period 10min 42nd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D27 | 0x9D28 | 40231 | 40232 | LAST_VOL_HARM_MAXa43 | Last Period 10min 43rd Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D29 | 0x9D2A | 40233 | 40234 | LAST_VOL_HARM_MAXa44 | Last Period 10min 44th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D2B | 0x9D2C | 40235 | 40236 | LAST_VOL_HARM_MAXa45 | Last Period 10min 45th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D2D | 0x9D2E | 40237 | 40238 | LAST_VOL_HARM_MAXa46 | Last Period 10min 46th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D2F | 0x9D30 | 40239 | 40240 | LAST_VOL_HARM_MAXa47 | Last Period 10min 47th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D31 | 0x9D32 | 40241 | 40242 | LAST_VOL_HARM_MAXa48 | Last Period 10min 48th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D33 | 0x9D34 | 40243 | 40244 | LAST_VOL_HARM_MAXa49 | Last Period 10min 49th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D35 | 0x9D36 | 40245 | 40246 | LAST_VOL_HARM_MAXa50 | Last Period 10min 50th Phase A Voltage Harmonics Maximum Value | float | 2 | R
0x9D37 | 0x9D38 | 40247 | 40248 | LAST_VOL_HARM_MAXb2 | Last Period 10min 2nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D39 | 0x9D3A | 40249 | 40250 | LAST_VOL_HARM_MAXb3 | Last Period 10min 3rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D3B | 0x9D3C | 40251 | 40252 | LAST_VOL_HARM_MAXb4 | Last Period 10min 4th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D3D | 0x9D3E | 40253 | 40254 | LAST_VOL_HARM_MAXb5 | Last Period 10min 5th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D3F | 0x9D40 | 40255 | 40256 | LAST_VOL_HARM_MAXb6 | Last Period 10min 6th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D41 | 0x9D42 | 40257 | 40258 | LAST_VOL_HARM_MAXb7 | Last Period 10min 7th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D43 | 0x9D44 | 40259 | 40260 | LAST_VOL_HARM_MAXb8 | Last Period 10min 8th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D45 | 0x9D46 | 40261 | 40262 | LAST_VOL_HARM_MAXb9 | Last Period 10min 9th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D47 | 0x9D48 | 40263 | 40264 | LAST_VOL_HARM_MAXb10 | Last Period 10min 10th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D49 | 0x9D4A | 40265 | 40266 | LAST_VOL_HARM_MAXb11 | Last Period 10min 11st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D4B | 0x9D4C | 40267 | 40268 | LAST_VOL_HARM_MAXb12 | Last Period 10min 12nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D4D | 0x9D4E | 40269 | 40270 | LAST_VOL_HARM_MAXb13 | Last Period 10min 13rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D4F | 0x9D50 | 40271 | 40272 | LAST_VOL_HARM_MAXb14 | Last Period 10min 14th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D51 | 0x9D52 | 40273 | 40274 | LAST_VOL_HARM_MAXb15 | Last Period 10min 15th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D53 | 0x9D54 | 40275 | 40276 | LAST_VOL_HARM_MAXb16 | Last Period 10min 16th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D55 | 0x9D56 | 40277 | 40278 | LAST_VOL_HARM_MAXb17 | Last Period 10min 17th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D57 | 0x9D58 | 40279 | 40280 | LAST_VOL_HARM_MAXb18 | Last Period 10min 18th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D59 | 0x9D5A | 40281 | 40282 | LAST_VOL_HARM_MAXb19 | Last Period 10min 19th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D5B | 0x9D5C | 40283 | 40284 | LAST_VOL_HARM_MAXb20 | Last Period 10min 20th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D5D | 0x9D5E | 40285 | 40286 | LAST_VOL_HARM_MAXb21 | Last Period 10min 21st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D5F | 0x9D60 | 40287 | 40288 | LAST_VOL_HARM_MAXb22 | Last Period 10min 22nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D61 | 0x9D62 | 40289 | 40290 | LAST_VOL_HARM_MAXb23 | Last Period 10min 23rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D63 | 0x9D64 | 40291 | 40292 | LAST_VOL_HARM_MAXb24 | Last Period 10min 24th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D65 | 0x9D66 | 40293 | 40294 | LAST_VOL_HARM_MAXb25 | Last Period 10min 25th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D67 | 0x9D68 | 40295 | 40296 | LAST_VOL_HARM_MAXb26 | Last Period 10min 26th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D69 | 0x9D6A | 40297 | 40298 | LAST_VOL_HARM_MAXb27 | Last Period 10min 27th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D6B | 0x9D6C | 40299 | 40300 | LAST_VOL_HARM_MAXb28 | Last Period 10min 28th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D6D | 0x9D6E | 40301 | 40302 | LAST_VOL_HARM_MAXb29 | Last Period 10min 29th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D6F | 0x9D70 | 40303 | 40304 | LAST_VOL_HARM_MAXb30 | Last Period 10min 30th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D71 | 0x9D72 | 40305 | 40306 | LAST_VOL_HARM_MAXb31 | Last Period 10min 31st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D73 | 0x9D74 | 40307 | 40308 | LAST_VOL_HARM_MAXb32 | Last Period 10min 32nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D75 | 0x9D76 | 40309 | 40310 | LAST_VOL_HARM_MAXb33 | Last Period 10min 33rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D77 | 0x9D78 | 40311 | 40312 | LAST_VOL_HARM_MAXb34 | Last Period 10min 34th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D79 | 0x9D7A | 40313 | 40314 | LAST_VOL_HARM_MAXb35 | Last Period 10min 35th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D7B | 0x9D7C | 40315 | 40316 | LAST_VOL_HARM_MAXb36 | Last Period 10min 36th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D7D | 0x9D7E | 40317 | 40318 | LAST_VOL_HARM_MAXb37 | Last Period 10min 37th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D7F | 0x9D80 | 40319 | 40320 | LAST_VOL_HARM_MAXb38 | Last Period 10min 38th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D81 | 0x9D82 | 40321 | 40322 | LAST_VOL_HARM_MAXb39 | Last Period 10min 39th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D83 | 0x9D84 | 40323 | 40324 | LAST_VOL_HARM_MAXb40 | Last Period 10min 40th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D85 | 0x9D86 | 40325 | 40326 | LAST_VOL_HARM_MAXb41 | Last Period 10min 41st Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D87 | 0x9D88 | 40327 | 40328 | LAST_VOL_HARM_MAXb42 | Last Period 10min 42nd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D89 | 0x9D8A | 40329 | 40330 | LAST_VOL_HARM_MAXb43 | Last Period 10min 43rd Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D8B | 0x9D8C | 40331 | 40332 | LAST_VOL_HARM_MAXb44 | Last Period 10min 44th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D8D | 0x9D8E | 40333 | 40334 | LAST_VOL_HARM_MAXb45 | Last Period 10min 45th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D8F | 0x9D90 | 40335 | 40336 | LAST_VOL_HARM_MAXb46 | Last Period 10min 46th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D91 | 0x9D92 | 40337 | 40338 | LAST_VOL_HARM_MAXb47 | Last Period 10min 47th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D93 | 0x9D94 | 40339 | 40340 | LAST_VOL_HARM_MAXb48 | Last Period 10min 48th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D95 | 0x9D96 | 40341 | 40342 | LAST_VOL_HARM_MAXb49 | Last Period 10min 49th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D97 | 0x9D98 | 40343 | 40344 | LAST_VOL_HARM_MAXb50 | Last Period 10min 50th Phase B Voltage Harmonics Maximum Value | float | 2 | R
0x9D99 | 0x9D9A | 40345 | 40346 | LAST_VOL_HARM_MAXc2 | Last Period 10min 2nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9D9B | 0x9D9C | 40347 | 40348 | LAST_VOL_HARM_MAXc3 | Last Period 10min 3rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9D9D | 0x9D9E | 40349 | 40350 | LAST_VOL_HARM_MAXc4 | Last Period 10min 4th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9D9F | 0x9DA0 | 40351 | 40352 | LAST_VOL_HARM_MAXc5 | Last Period 10min 5th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DA1 | 0x9DA2 | 40353 | 40354 | LAST_VOL_HARM_MAXc6 | Last Period 10min 6th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DA3 | 0x9DA4 | 40355 | 40356 | LAST_VOL_HARM_MAXc7 | Last Period 10min 7th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DA5 | 0x9DA6 | 40357 | 40358 | LAST_VOL_HARM_MAXc8 | Last Period 10min 8th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DA7 | 0x9DA8 | 40359 | 40360 | LAST_VOL_HARM_MAXc9 | Last Period 10min 9th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DA9 | 0x9DAA | 40361 | 40362 | LAST_VOL_HARM_MAXc10 | Last Period 10min 10th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DAB | 0x9DAC | 40363 | 40364 | LAST_VOL_HARM_MAXc11 | Last Period 10min 11st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DAD | 0x9DAE | 40365 | 40366 | LAST_VOL_HARM_MAXc12 | Last Period 10min 12nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DAF | 0x9DB0 | 40367 | 40368 | LAST_VOL_HARM_MAXc13 | Last Period 10min 13rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DB1 | 0x9DB2 | 40369 | 40370 | LAST_VOL_HARM_MAXc14 | Last Period 10min 14th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DB3 | 0x9DB4 | 40371 | 40372 | LAST_VOL_HARM_MAXc15 | Last Period 10min 15th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DB5 | 0x9DB6 | 40373 | 40374 | LAST_VOL_HARM_MAXc16 | Last Period 10min 16th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DB7 | 0x9DB8 | 40375 | 40376 | LAST_VOL_HARM_MAXc17 | Last Period 10min 17th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DB9 | 0x9DBA | 40377 | 40378 | LAST_VOL_HARM_MAXc18 | Last Period 10min 18th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DBB | 0x9DBC | 40379 | 40380 | LAST_VOL_HARM_MAXc19 | Last Period 10min 19th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DBD | 0x9DBE | 40381 | 40382 | LAST_VOL_HARM_MAXc20 | Last Period 10min 20th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DBF | 0x9DC0 | 40383 | 40384 | LAST_VOL_HARM_MAXc21 | Last Period 10min 21st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DC1 | 0x9DC2 | 40385 | 40386 | LAST_VOL_HARM_MAXc22 | Last Period 10min 22nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DC3 | 0x9DC4 | 40387 | 40388 | LAST_VOL_HARM_MAXc23 | Last Period 10min 23rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DC5 | 0x9DC6 | 40389 | 40390 | LAST_VOL_HARM_MAXc24 | Last Period 10min 24th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DC7 | 0x9DC8 | 40391 | 40392 | LAST_VOL_HARM_MAXc25 | Last Period 10min 25th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DC9 | 0x9DCA | 40393 | 40394 | LAST_VOL_HARM_MAXc26 | Last Period 10min 26th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DCB | 0x9DCC | 40395 | 40396 | LAST_VOL_HARM_MAXc27 | Last Period 10min 27th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DCD | 0x9DCE | 40397 | 40398 | LAST_VOL_HARM_MAXc28 | Last Period 10min 28th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DCF | 0x9DD0 | 40399 | 40400 | LAST_VOL_HARM_MAXc29 | Last Period 10min 29th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DD1 | 0x9DD2 | 40401 | 40402 | LAST_VOL_HARM_MAXc30 | Last Period 10min 30th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DD3 | 0x9DD4 | 40403 | 40404 | LAST_VOL_HARM_MAXc31 | Last Period 10min 31st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DD5 | 0x9DD6 | 40405 | 40406 | LAST_VOL_HARM_MAXc32 | Last Period 10min 32nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DD7 | 0x9DD8 | 40407 | 40408 | LAST_VOL_HARM_MAXc33 | Last Period 10min 33rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DD9 | 0x9DDA | 40409 | 40410 | LAST_VOL_HARM_MAXc34 | Last Period 10min 34th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DDB | 0x9DDC | 40411 | 40412 | LAST_VOL_HARM_MAXc35 | Last Period 10min 35th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DDD | 0x9DDE | 40413 | 40414 | LAST_VOL_HARM_MAXc36 | Last Period 10min 36th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DDF | 0x9DE0 | 40415 | 40416 | LAST_VOL_HARM_MAXc37 | Last Period 10min 37th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DE1 | 0x9DE2 | 40417 | 40418 | LAST_VOL_HARM_MAXc38 | Last Period 10min 38th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DE3 | 0x9DE4 | 40419 | 40420 | LAST_VOL_HARM_MAXc39 | Last Period 10min 39th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DE5 | 0x9DE6 | 40421 | 40422 | LAST_VOL_HARM_MAXc40 | Last Period 10min 40th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DE7 | 0x9DE8 | 40423 | 40424 | LAST_VOL_HARM_MAXc41 | Last Period 10min 41st Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DE9 | 0x9DEA | 40425 | 40426 | LAST_VOL_HARM_MAXc42 | Last Period 10min 42nd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DEB | 0x9DEC | 40427 | 40428 | LAST_VOL_HARM_MAXc43 | Last Period 10min 43rd Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DED | 0x9DEE | 40429 | 40430 | LAST_VOL_HARM_MAXc44 | Last Period 10min 44th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DEF | 0x9DF0 | 40431 | 40432 | LAST_VOL_HARM_MAXc45 | Last Period 10min 45th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DF1 | 0x9DF2 | 40433 | 40434 | LAST_VOL_HARM_MAXc46 | Last Period 10min 46th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DF3 | 0x9DF4 | 40435 | 40436 | LAST_VOL_HARM_MAXc47 | Last Period 10min 47th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DF5 | 0x9DF6 | 40437 | 40438 | LAST_VOL_HARM_MAXc48 | Last Period 10min 48th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DF7 | 0x9DF8 | 40439 | 40440 | LAST_VOL_HARM_MAXc49 | Last Period 10min 49th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DF9 | 0x9DFA | 40441 | 40442 | LAST_VOL_HARM_MAXc50 | Last Period 10min 50th Phase C Voltage Harmonics Maximum Value | float | 2 | R
0x9DFB | 0x9DFC | 40443 | 40444 | LAST_VOL_HARM_MINa2 | Last Period 10min 2nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9DFD | 0x9DFE | 40445 | 40446 | LAST_VOL_HARM_MINa3 | Last Period 10min 3rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9DFF | 0x9E00 | 40447 | 40448 | LAST_VOL_HARM_MINa4 | Last Period 10min 4th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E01 | 0x9E02 | 40449 | 40450 | LAST_VOL_HARM_MINa5 | Last Period 10min 5th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E03 | 0x9E04 | 40451 | 40452 | LAST_VOL_HARM_MINa6 | Last Period 10min 6th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E05 | 0x9E06 | 40453 | 40454 | LAST_VOL_HARM_MINa7 | Last Period 10min 7th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E07 | 0x9E08 | 40455 | 40456 | LAST_VOL_HARM_MINa8 | Last Period 10min 8th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E09 | 0x9E0A | 40457 | 40458 | LAST_VOL_HARM_MINa9 | Last Period 10min 9th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E0B | 0x9E0C | 40459 | 40460 | LAST_VOL_HARM_MINa10 | Last Period 10min 10th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E0D | 0x9E0E | 40461 | 40462 | LAST_VOL_HARM_MINa11 | Last Period 10min 11st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E0F | 0x9E10 | 40463 | 40464 | LAST_VOL_HARM_MINa12 | Last Period 10min 12nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E11 | 0x9E12 | 40465 | 40466 | LAST_VOL_HARM_MINa13 | Last Period 10min 13rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E13 | 0x9E14 | 40467 | 40468 | LAST_VOL_HARM_MINa14 | Last Period 10min 14th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E15 | 0x9E16 | 40469 | 40470 | LAST_VOL_HARM_MINa15 | Last Period 10min 15th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E17 | 0x9E18 | 40471 | 40472 | LAST_VOL_HARM_MINa16 | Last Period 10min 16th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E19 | 0x9E1A | 40473 | 40474 | LAST_VOL_HARM_MINa17 | Last Period 10min 17th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E1B | 0x9E1C | 40475 | 40476 | LAST_VOL_HARM_MINa18 | Last Period 10min 18th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E1D | 0x9E1E | 40477 | 40478 | LAST_VOL_HARM_MINa19 | Last Period 10min 19th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E1F | 0x9E20 | 40479 | 40480 | LAST_VOL_HARM_MINa20 | Last Period 10min 20th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E21 | 0x9E22 | 40481 | 40482 | LAST_VOL_HARM_MINa21 | Last Period 10min 21st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E23 | 0x9E24 | 40483 | 40484 | LAST_VOL_HARM_MINa22 | Last Period 10min 22nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E25 | 0x9E26 | 40485 | 40486 | LAST_VOL_HARM_MINa23 | Last Period 10min 23rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E27 | 0x9E28 | 40487 | 40488 | LAST_VOL_HARM_MINa24 | Last Period 10min 24th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E29 | 0x9E2A | 40489 | 40490 | LAST_VOL_HARM_MINa25 | Last Period 10min 25th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E2B | 0x9E2C | 40491 | 40492 | LAST_VOL_HARM_MINa26 | Last Period 10min 26th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E2D | 0x9E2E | 40493 | 40494 | LAST_VOL_HARM_MINa27 | Last Period 10min 27th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E2F | 0x9E30 | 40495 | 40496 | LAST_VOL_HARM_MINa28 | Last Period 10min 28th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E31 | 0x9E32 | 40497 | 40498 | LAST_VOL_HARM_MINa29 | Last Period 10min 29th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E33 | 0x9E34 | 40499 | 40500 | LAST_VOL_HARM_MINa30 | Last Period 10min 30th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E35 | 0x9E36 | 40501 | 40502 | LAST_VOL_HARM_MINa31 | Last Period 10min 31st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E37 | 0x9E38 | 40503 | 40504 | LAST_VOL_HARM_MINa32 | Last Period 10min 32nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E39 | 0x9E3A | 40505 | 40506 | LAST_VOL_HARM_MINa33 | Last Period 10min 33rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E3B | 0x9E3C | 40507 | 40508 | LAST_VOL_HARM_MINa34 | Last Period 10min 34th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E3D | 0x9E3E | 40509 | 40510 | LAST_VOL_HARM_MINa35 | Last Period 10min 35th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E3F | 0x9E40 | 40511 | 40512 | LAST_VOL_HARM_MINa36 | Last Period 10min 36th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E41 | 0x9E42 | 40513 | 40514 | LAST_VOL_HARM_MINa37 | Last Period 10min 37th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E43 | 0x9E44 | 40515 | 40516 | LAST_VOL_HARM_MINa38 | Last Period 10min 38th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E45 | 0x9E46 | 40517 | 40518 | LAST_VOL_HARM_MINa39 | Last Period 10min 39th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E47 | 0x9E48 | 40519 | 40520 | LAST_VOL_HARM_MINa40 | Last Period 10min 40th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E49 | 0x9E4A | 40521 | 40522 | LAST_VOL_HARM_MINa41 | Last Period 10min 41st Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E4B | 0x9E4C | 40523 | 40524 | LAST_VOL_HARM_MINa42 | Last Period 10min 42nd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E4D | 0x9E4E | 40525 | 40526 | LAST_VOL_HARM_MINa43 | Last Period 10min 43rd Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E4F | 0x9E50 | 40527 | 40528 | LAST_VOL_HARM_MINa44 | Last Period 10min 44th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E51 | 0x9E52 | 40529 | 40530 | LAST_VOL_HARM_MINa45 | Last Period 10min 45th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E53 | 0x9E54 | 40531 | 40532 | LAST_VOL_HARM_MINa46 | Last Period 10min 46th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E55 | 0x9E56 | 40533 | 40534 | LAST_VOL_HARM_MINa47 | Last Period 10min 47th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E57 | 0x9E58 | 40535 | 40536 | LAST_VOL_HARM_MINa48 | Last Period 10min 48th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E59 | 0x9E5A | 40537 | 40538 | LAST_VOL_HARM_MINa49 | Last Period 10min 49th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E5B | 0x9E5C | 40539 | 40540 | LAST_VOL_HARM_MINa50 | Last Period 10min 50th Phase A Voltage Harmonics Minimum Value | float | 2 | R
0x9E5D | 0x9E5E | 40541 | 40542 | LAST_VOL_HARM_MINb2 | Last Period 10min 2nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E5F | 0x9E60 | 40543 | 40544 | LAST_VOL_HARM_MINb3 | Last Period 10min 3rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E61 | 0x9E62 | 40545 | 40546 | LAST_VOL_HARM_MINb4 | Last Period 10min 4th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E63 | 0x9E64 | 40547 | 40548 | LAST_VOL_HARM_MINb5 | Last Period 10min 5th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E65 | 0x9E66 | 40549 | 40550 | LAST_VOL_HARM_MINb6 | Last Period 10min 6th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E67 | 0x9E68 | 40551 | 40552 | LAST_VOL_HARM_MINb7 | Last Period 10min 7th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E69 | 0x9E6A | 40553 | 40554 | LAST_VOL_HARM_MINb8 | Last Period 10min 8th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E6B | 0x9E6C | 40555 | 40556 | LAST_VOL_HARM_MINb9 | Last Period 10min 9th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E6D | 0x9E6E | 40557 | 40558 | LAST_VOL_HARM_MINb10 | Last Period 10min 10th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E6F | 0x9E70 | 40559 | 40560 | LAST_VOL_HARM_MINb11 | Last Period 10min 11st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E71 | 0x9E72 | 40561 | 40562 | LAST_VOL_HARM_MINb12 | Last Period 10min 12nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E73 | 0x9E74 | 40563 | 40564 | LAST_VOL_HARM_MINb13 | Last Period 10min 13rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E75 | 0x9E76 | 40565 | 40566 | LAST_VOL_HARM_MINb14 | Last Period 10min 14th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E77 | 0x9E78 | 40567 | 40568 | LAST_VOL_HARM_MINb15 | Last Period 10min 15th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E79 | 0x9E7A | 40569 | 40570 | LAST_VOL_HARM_MINb16 | Last Period 10min 16th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E7B | 0x9E7C | 40571 | 40572 | LAST_VOL_HARM_MINb17 | Last Period 10min 17th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E7D | 0x9E7E | 40573 | 40574 | LAST_VOL_HARM_MINb18 | Last Period 10min 18th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E7F | 0x9E80 | 40575 | 40576 | LAST_VOL_HARM_MINb19 | Last Period 10min 19th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E81 | 0x9E82 | 40577 | 40578 | LAST_VOL_HARM_MINb20 | Last Period 10min 20th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E83 | 0x9E84 | 40579 | 40580 | LAST_VOL_HARM_MINb21 | Last Period 10min 21st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E85 | 0x9E86 | 40581 | 40582 | LAST_VOL_HARM_MINb22 | Last Period 10min 22nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E87 | 0x9E88 | 40583 | 40584 | LAST_VOL_HARM_MINb23 | Last Period 10min 23rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E89 | 0x9E8A | 40585 | 40586 | LAST_VOL_HARM_MINb24 | Last Period 10min 24th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E8B | 0x9E8C | 40587 | 40588 | LAST_VOL_HARM_MINb25 | Last Period 10min 25th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E8D | 0x9E8E | 40589 | 40590 | LAST_VOL_HARM_MINb26 | Last Period 10min 26th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E8F | 0x9E90 | 40591 | 40592 | LAST_VOL_HARM_MINb27 | Last Period 10min 27th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E91 | 0x9E92 | 40593 | 40594 | LAST_VOL_HARM_MINb28 | Last Period 10min 28th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E93 | 0x9E94 | 40595 | 40596 | LAST_VOL_HARM_MINb29 | Last Period 10min 29th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E95 | 0x9E96 | 40597 | 40598 | LAST_VOL_HARM_MINb30 | Last Period 10min 30th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E97 | 0x9E98 | 40599 | 40600 | LAST_VOL_HARM_MINb31 | Last Period 10min 31st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E99 | 0x9E9A | 40601 | 40602 | LAST_VOL_HARM_MINb32 | Last Period 10min 32nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E9B | 0x9E9C | 40603 | 40604 | LAST_VOL_HARM_MINb33 | Last Period 10min 33rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E9D | 0x9E9E | 40605 | 40606 | LAST_VOL_HARM_MINb34 | Last Period 10min 34th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9E9F | 0x9EA0 | 40607 | 40608 | LAST_VOL_HARM_MINb35 | Last Period 10min 35th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EA1 | 0x9EA2 | 40609 | 40610 | LAST_VOL_HARM_MINb36 | Last Period 10min 36th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EA3 | 0x9EA4 | 40611 | 40612 | LAST_VOL_HARM_MINb37 | Last Period 10min 37th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EA5 | 0x9EA6 | 40613 | 40614 | LAST_VOL_HARM_MINb38 | Last Period 10min 38th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EA7 | 0x9EA8 | 40615 | 40616 | LAST_VOL_HARM_MINb39 | Last Period 10min 39th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EA9 | 0x9EAA | 40617 | 40618 | LAST_VOL_HARM_MINb40 | Last Period 10min 40th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EAB | 0x9EAC | 40619 | 40620 | LAST_VOL_HARM_MINb41 | Last Period 10min 41st Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EAD | 0x9EAE | 40621 | 40622 | LAST_VOL_HARM_MINb42 | Last Period 10min 42nd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EAF | 0x9EB0 | 40623 | 40624 | LAST_VOL_HARM_MINb43 | Last Period 10min 43rd Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EB1 | 0x9EB2 | 40625 | 40626 | LAST_VOL_HARM_MINb44 | Last Period 10min 44th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EB3 | 0x9EB4 | 40627 | 40628 | LAST_VOL_HARM_MINb45 | Last Period 10min 45th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EB5 | 0x9EB6 | 40629 | 40630 | LAST_VOL_HARM_MINb46 | Last Period 10min 46th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EB7 | 0x9EB8 | 40631 | 40632 | LAST_VOL_HARM_MINb47 | Last Period 10min 47th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EB9 | 0x9EBA | 40633 | 40634 | LAST_VOL_HARM_MINb48 | Last Period 10min 48th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EBB | 0x9EBC | 40635 | 40636 | LAST_VOL_HARM_MINb49 | Last Period 10min 49th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EBD | 0x9EBE | 40637 | 40638 | LAST_VOL_HARM_MINb50 | Last Period 10min 50th Phase B Voltage Harmonics Minimum Value | float | 2 | R
0x9EBF | 0x9EC0 | 40639 | 40640 | LAST_VOL_HARM_MINc2 | Last Period 10min 2nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EC1 | 0x9EC2 | 40641 | 40642 | LAST_VOL_HARM_MINc3 | Last Period 10min 3rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EC3 | 0x9EC4 | 40643 | 40644 | LAST_VOL_HARM_MINc4 | Last Period 10min 4th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EC5 | 0x9EC6 | 40645 | 40646 | LAST_VOL_HARM_MINc5 | Last Period 10min 5th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EC7 | 0x9EC8 | 40647 | 40648 | LAST_VOL_HARM_MINc6 | Last Period 10min 6th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EC9 | 0x9ECA | 40649 | 40650 | LAST_VOL_HARM_MINc7 | Last Period 10min 7th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9ECB | 0x9ECC | 40651 | 40652 | LAST_VOL_HARM_MINc8 | Last Period 10min 8th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9ECD | 0x9ECE | 40653 | 40654 | LAST_VOL_HARM_MINc9 | Last Period 10min 9th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9ECF | 0x9ED0 | 40655 | 40656 | LAST_VOL_HARM_MINc10 | Last Period 10min 10th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9ED1 | 0x9ED2 | 40657 | 40658 | LAST_VOL_HARM_MINc11 | Last Period 10min 11st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9ED3 | 0x9ED4 | 40659 | 40660 | LAST_VOL_HARM_MINc12 | Last Period 10min 12nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9ED5 | 0x9ED6 | 40661 | 40662 | LAST_VOL_HARM_MINc13 | Last Period 10min 13rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9ED7 | 0x9ED8 | 40663 | 40664 | LAST_VOL_HARM_MINc14 | Last Period 10min 14th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9ED9 | 0x9EDA | 40665 | 40666 | LAST_VOL_HARM_MINc15 | Last Period 10min 15th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EDB | 0x9EDC | 40667 | 40668 | LAST_VOL_HARM_MINc16 | Last Period 10min 16th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EDD | 0x9EDE | 40669 | 40670 | LAST_VOL_HARM_MINc17 | Last Period 10min 17th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EDF | 0x9EE0 | 40671 | 40672 | LAST_VOL_HARM_MINc18 | Last Period 10min 18th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EE1 | 0x9EE2 | 40673 | 40674 | LAST_VOL_HARM_MINc19 | Last Period 10min 19th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EE3 | 0x9EE4 | 40675 | 40676 | LAST_VOL_HARM_MINc20 | Last Period 10min 20th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EE5 | 0x9EE6 | 40677 | 40678 | LAST_VOL_HARM_MINc21 | Last Period 10min 21st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EE7 | 0x9EE8 | 40679 | 40680 | LAST_VOL_HARM_MINc22 | Last Period 10min 22nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EE9 | 0x9EEA | 40681 | 40682 | LAST_VOL_HARM_MINc23 | Last Period 10min 23rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EEB | 0x9EEC | 40683 | 40684 | LAST_VOL_HARM_MINc24 | Last Period 10min 24th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EED | 0x9EEE | 40685 | 40686 | LAST_VOL_HARM_MINc25 | Last Period 10min 25th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EEF | 0x9EF0 | 40687 | 40688 | LAST_VOL_HARM_MINc26 | Last Period 10min 26th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EF1 | 0x9EF2 | 40689 | 40690 | LAST_VOL_HARM_MINc27 | Last Period 10min 27th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EF3 | 0x9EF4 | 40691 | 40692 | LAST_VOL_HARM_MINc28 | Last Period 10min 28th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EF5 | 0x9EF6 | 40693 | 40694 | LAST_VOL_HARM_MINc29 | Last Period 10min 29th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EF7 | 0x9EF8 | 40695 | 40696 | LAST_VOL_HARM_MINc30 | Last Period 10min 30th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EF9 | 0x9EFA | 40697 | 40698 | LAST_VOL_HARM_MINc31 | Last Period 10min 31st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EFB | 0x9EFC | 40699 | 40700 | LAST_VOL_HARM_MINc32 | Last Period 10min 32nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EFD | 0x9EFE | 40701 | 40702 | LAST_VOL_HARM_MINc33 | Last Period 10min 33rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9EFF | 0x9F00 | 40703 | 40704 | LAST_VOL_HARM_MINc34 | Last Period 10min 34th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F01 | 0x9F02 | 40705 | 40706 | LAST_VOL_HARM_MINc35 | Last Period 10min 35th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F03 | 0x9F04 | 40707 | 40708 | LAST_VOL_HARM_MINc36 | Last Period 10min 36th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F05 | 0x9F06 | 40709 | 40710 | LAST_VOL_HARM_MINc37 | Last Period 10min 37th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F07 | 0x9F08 | 40711 | 40712 | LAST_VOL_HARM_MINc38 | Last Period 10min 38th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F09 | 0x9F0A | 40713 | 40714 | LAST_VOL_HARM_MINc39 | Last Period 10min 39th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F0B | 0x9F0C | 40715 | 40716 | LAST_VOL_HARM_MINc40 | Last Period 10min 40th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F0D | 0x9F0E | 40717 | 40718 | LAST_VOL_HARM_MINc41 | Last Period 10min 41st Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F0F | 0x9F10 | 40719 | 40720 | LAST_VOL_HARM_MINc42 | Last Period 10min 42nd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F11 | 0x9F12 | 40721 | 40722 | LAST_VOL_HARM_MINc43 | Last Period 10min 43rd Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F13 | 0x9F14 | 40723 | 40724 | LAST_VOL_HARM_MINc44 | Last Period 10min 44th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F15 | 0x9F16 | 40725 | 40726 | LAST_VOL_HARM_MINc45 | Last Period 10min 45th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F17 | 0x9F18 | 40727 | 40728 | LAST_VOL_HARM_MINc46 | Last Period 10min 46th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F19 | 0x9F1A | 40729 | 40730 | LAST_VOL_HARM_MINc47 | Last Period 10min 47th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F1B | 0x9F1C | 40731 | 40732 | LAST_VOL_HARM_MINc48 | Last Period 10min 48th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F1D | 0x9F1E | 40733 | 40734 | LAST_VOL_HARM_MINc49 | Last Period 10min 49th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F1F | 0x9F20 | 40735 | 40736 | LAST_VOL_HARM_MINc50 | Last Period 10min 50th Phase C Voltage Harmonics Minimum Value | float | 2 | R
0x9F21 | 0x9F22 | 40737 | 40738 | LAST_VOL_HARM_AVGa2 | Last Period 10min 2nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F23 | 0x9F24 | 40739 | 40740 | LAST_VOL_HARM_AVGa3 | Last Period 10min 3rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F25 | 0x9F26 | 40741 | 40742 | LAST_VOL_HARM_AVGa4 | Last Period 10min 4th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F27 | 0x9F28 | 40743 | 40744 | LAST_VOL_HARM_AVGa5 | Last Period 10min 5th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F29 | 0x9F2A | 40745 | 40746 | LAST_VOL_HARM_AVGa6 | Last Period 10min 6th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F2B | 0x9F2C | 40747 | 40748 | LAST_VOL_HARM_AVGa7 | Last Period 10min 7th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F2D | 0x9F2E | 40749 | 40750 | LAST_VOL_HARM_AVGa8 | Last Period 10min 8th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F2F | 0x9F30 | 40751 | 40752 | LAST_VOL_HARM_AVGa9 | Last Period 10min 9th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F31 | 0x9F32 | 40753 | 40754 | LAST_VOL_HARM_AVGa10 | Last Period 10min 10th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F33 | 0x9F34 | 40755 | 40756 | LAST_VOL_HARM_AVGa11 | Last Period 10min 11st Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F35 | 0x9F36 | 40757 | 40758 | LAST_VOL_HARM_AVGa12 | Last Period 10min 12nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F37 | 0x9F38 | 40759 | 40760 | LAST_VOL_HARM_AVGa13 | Last Period 10min 13rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F39 | 0x9F3A | 40761 | 40762 | LAST_VOL_HARM_AVGa14 | Last Period 10min 14th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F3B | 0x9F3C | 40763 | 40764 | LAST_VOL_HARM_AVGa15 | Last Period 10min 15th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F3D | 0x9F3E | 40765 | 40766 | LAST_VOL_HARM_AVGa16 | Last Period 10min 16th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F3F | 0x9F40 | 40767 | 40768 | LAST_VOL_HARM_AVGa17 | Last Period 10min 17th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F41 | 0x9F42 | 40769 | 40770 | LAST_VOL_HARM_AVGa18 | Last Period 10min 18th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F43 | 0x9F44 | 40771 | 40772 | LAST_VOL_HARM_AVGa19 | Last Period 10min 19th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F45 | 0x9F46 | 40773 | 40774 | LAST_VOL_HARM_AVGa20 | Last Period 10min 20th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F47 | 0x9F48 | 40775 | 40776 | LAST_VOL_HARM_AVGa21 | Last Period 10min 21st Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F49 | 0x9F4A | 40777 | 40778 | LAST_VOL_HARM_AVGa22 | Last Period 10min 22nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F4B | 0x9F4C | 40779 | 40780 | LAST_VOL_HARM_AVGa23 | Last Period 10min 23rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F4D | 0x9F4E | 40781 | 40782 | LAST_VOL_HARM_AVGa24 | Last Period 10min 24th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F4F | 0x9F50 | 40783 | 40784 | LAST_VOL_HARM_AVGa25 | Last Period 10min 25th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F51 | 0x9F52 | 40785 | 40786 | LAST_VOL_HARM_AVGa26 | Last Period 10min 26th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F53 | 0x9F54 | 40787 | 40788 | LAST_VOL_HARM_AVGa27 | Last Period 10min 27th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F55 | 0x9F56 | 40789 | 40790 | LAST_VOL_HARM_AVGa28 | Last Period 10min 28th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F57 | 0x9F58 | 40791 | 40792 | LAST_VOL_HARM_AVGa29 | Last Period 10min 29th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F59 | 0x9F5A | 40793 | 40794 | LAST_VOL_HARM_AVGa30 | Last Period 10min 30th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F5B | 0x9F5C | 40795 | 40796 | LAST_VOL_HARM_AVGa31 | Last Period 10min 31st Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F5D | 0x9F5E | 40797 | 40798 | LAST_VOL_HARM_AVGa32 | Last Period 10min 32nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F5F | 0x9F60 | 40799 | 40800 | LAST_VOL_HARM_AVGa33 | Last Period 10min 33rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F61 | 0x9F62 | 40801 | 40802 | LAST_VOL_HARM_AVGa34 | Last Period 10min 34th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F63 | 0x9F64 | 40803 | 40804 | LAST_VOL_HARM_AVGa35 | Last Period 10min 35th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F65 | 0x9F66 | 40805 | 40806 | LAST_VOL_HARM_AVGa36 | Last Period 10min 36th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F67 | 0x9F68 | 40807 | 40808 | LAST_VOL_HARM_AVGa37 | Last Period 10min 37th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F69 | 0x9F6A | 40809 | 40810 | LAST_VOL_HARM_AVGa38 | Last Period 10min 38th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F6B | 0x9F6C | 40811 | 40812 | LAST_VOL_HARM_AVGa39 | Last Period 10min 39th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F6D | 0x9F6E | 40813 | 40814 | LAST_VOL_HARM_AVGa40 | Last Period 10min 40th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F6F | 0x9F70 | 40815 | 40816 | LAST_VOL_HARM_AVGa41 | Last Period 10min 41st Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F71 | 0x9F72 | 40817 | 40818 | LAST_VOL_HARM_AVGa42 | Last Period 10min 42nd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F73 | 0x9F74 | 40819 | 40820 | LAST_VOL_HARM_AVGa43 | Last Period 10min 43rd Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F75 | 0x9F76 | 40821 | 40822 | LAST_VOL_HARM_AVGa44 | Last Period 10min 44th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F77 | 0x9F78 | 40823 | 40824 | LAST_VOL_HARM_AVGa45 | Last Period 10min 45th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F79 | 0x9F7A | 40825 | 40826 | LAST_VOL_HARM_AVGa46 | Last Period 10min 46th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F7B | 0x9F7C | 40827 | 40828 | LAST_VOL_HARM_AVGa47 | Last Period 10min 47th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F7D | 0x9F7E | 40829 | 40830 | LAST_VOL_HARM_AVGa48 | Last Period 10min 48th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F7F | 0x9F80 | 40831 | 40832 | LAST_VOL_HARM_AVGa49 | Last Period 10min 49th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F81 | 0x9F82 | 40833 | 40834 | LAST_VOL_HARM_AVGa50 | Last Period 10min 50th Phase A Voltage Harmonics Average Value | float | 2 | R
0x9F83 | 0x9F84 | 40835 | 40836 | LAST_VOL_HARM_AVGb2 | Last Period 10min 2nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F85 | 0x9F86 | 40837 | 40838 | LAST_VOL_HARM_AVGb3 | Last Period 10min 3rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F87 | 0x9F88 | 40839 | 40840 | LAST_VOL_HARM_AVGb4 | Last Period 10min 4th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F89 | 0x9F8A | 40841 | 40842 | LAST_VOL_HARM_AVGb5 | Last Period 10min 5th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F8B | 0x9F8C | 40843 | 40844 | LAST_VOL_HARM_AVGb6 | Last Period 10min 6th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F8D | 0x9F8E | 40845 | 40846 | LAST_VOL_HARM_AVGb7 | Last Period 10min 7th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F8F | 0x9F90 | 40847 | 40848 | LAST_VOL_HARM_AVGb8 | Last Period 10min 8th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F91 | 0x9F92 | 40849 | 40850 | LAST_VOL_HARM_AVGb9 | Last Period 10min 9th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F93 | 0x9F94 | 40851 | 40852 | LAST_VOL_HARM_AVGb10 | Last Period 10min 10th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F95 | 0x9F96 | 40853 | 40854 | LAST_VOL_HARM_AVGb11 | Last Period 10min 11st Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F97 | 0x9F98 | 40855 | 40856 | LAST_VOL_HARM_AVGb12 | Last Period 10min 12nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F99 | 0x9F9A | 40857 | 40858 | LAST_VOL_HARM_AVGb13 | Last Period 10min 13rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F9B | 0x9F9C | 40859 | 40860 | LAST_VOL_HARM_AVGb14 | Last Period 10min 14th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F9D | 0x9F9E | 40861 | 40862 | LAST_VOL_HARM_AVGb15 | Last Period 10min 15th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9F9F | 0x9FA0 | 40863 | 40864 | LAST_VOL_HARM_AVGb16 | Last Period 10min 16th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FA1 | 0x9FA2 | 40865 | 40866 | LAST_VOL_HARM_AVGb17 | Last Period 10min 17th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FA3 | 0x9FA4 | 40867 | 40868 | LAST_VOL_HARM_AVGb18 | Last Period 10min 18th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FA5 | 0x9FA6 | 40869 | 40870 | LAST_VOL_HARM_AVGb19 | Last Period 10min 19th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FA7 | 0x9FA8 | 40871 | 40872 | LAST_VOL_HARM_AVGb20 | Last Period 10min 20th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FA9 | 0x9FAA | 40873 | 40874 | LAST_VOL_HARM_AVGb21 | Last Period 10min 21st Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FAB | 0x9FAC | 40875 | 40876 | LAST_VOL_HARM_AVGb22 | Last Period 10min 22nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FAD | 0x9FAE | 40877 | 40878 | LAST_VOL_HARM_AVGb23 | Last Period 10min 23rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FAF | 0x9FB0 | 40879 | 40880 | LAST_VOL_HARM_AVGb24 | Last Period 10min 24th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FB1 | 0x9FB2 | 40881 | 40882 | LAST_VOL_HARM_AVGb25 | Last Period 10min 25th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FB3 | 0x9FB4 | 40883 | 40884 | LAST_VOL_HARM_AVGb26 | Last Period 10min 26th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FB5 | 0x9FB6 | 40885 | 40886 | LAST_VOL_HARM_AVGb27 | Last Period 10min 27th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FB7 | 0x9FB8 | 40887 | 40888 | LAST_VOL_HARM_AVGb28 | Last Period 10min 28th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FB9 | 0x9FBA | 40889 | 40890 | LAST_VOL_HARM_AVGb29 | Last Period 10min 29th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FBB | 0x9FBC | 40891 | 40892 | LAST_VOL_HARM_AVGb30 | Last Period 10min 30th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FBD | 0x9FBE | 40893 | 40894 | LAST_VOL_HARM_AVGb31 | Last Period 10min 31st Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FBF | 0x9FC0 | 40895 | 40896 | LAST_VOL_HARM_AVGb32 | Last Period 10min 32nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FC1 | 0x9FC2 | 40897 | 40898 | LAST_VOL_HARM_AVGb33 | Last Period 10min 33rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FC3 | 0x9FC4 | 40899 | 40900 | LAST_VOL_HARM_AVGb34 | Last Period 10min 34th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FC5 | 0x9FC6 | 40901 | 40902 | LAST_VOL_HARM_AVGb35 | Last Period 10min 35th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FC7 | 0x9FC8 | 40903 | 40904 | LAST_VOL_HARM_AVGb36 | Last Period 10min 36th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FC9 | 0x9FCA | 40905 | 40906 | LAST_VOL_HARM_AVGb37 | Last Period 10min 37th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FCB | 0x9FCC | 40907 | 40908 | LAST_VOL_HARM_AVGb38 | Last Period 10min 38th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FCD | 0x9FCE | 40909 | 40910 | LAST_VOL_HARM_AVGb39 | Last Period 10min 39th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FCF | 0x9FD0 | 40911 | 40912 | LAST_VOL_HARM_AVGb40 | Last Period 10min 40th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FD1 | 0x9FD2 | 40913 | 40914 | LAST_VOL_HARM_AVGb41 | Last Period 10min 41st Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FD3 | 0x9FD4 | 40915 | 40916 | LAST_VOL_HARM_AVGb42 | Last Period 10min 42nd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FD5 | 0x9FD6 | 40917 | 40918 | LAST_VOL_HARM_AVGb43 | Last Period 10min 43rd Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FD7 | 0x9FD8 | 40919 | 40920 | LAST_VOL_HARM_AVGb44 | Last Period 10min 44th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FD9 | 0x9FDA | 40921 | 40922 | LAST_VOL_HARM_AVGb45 | Last Period 10min 45th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FDB | 0x9FDC | 40923 | 40924 | LAST_VOL_HARM_AVGb46 | Last Period 10min 46th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FDD | 0x9FDE | 40925 | 40926 | LAST_VOL_HARM_AVGb47 | Last Period 10min 47th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FDF | 0x9FE0 | 40927 | 40928 | LAST_VOL_HARM_AVGb48 | Last Period 10min 48th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FE1 | 0x9FE2 | 40929 | 40930 | LAST_VOL_HARM_AVGb49 | Last Period 10min 49th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FE3 | 0x9FE4 | 40931 | 40932 | LAST_VOL_HARM_AVGb50 | Last Period 10min 50th Phase B Voltage Harmonics Average Value | float | 2 | R
0x9FE5 | 0x9FE6 | 40933 | 40934 | LAST_VOL_HARM_AVGc2 | Last Period 10min 2nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FE7 | 0x9FE8 | 40935 | 40936 | LAST_VOL_HARM_AVGc3 | Last Period 10min 3rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FE9 | 0x9FEA | 40937 | 40938 | LAST_VOL_HARM_AVGc4 | Last Period 10min 4th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FEB | 0x9FEC | 40939 | 40940 | LAST_VOL_HARM_AVGc5 | Last Period 10min 5th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FED | 0x9FEE | 40941 | 40942 | LAST_VOL_HARM_AVGc6 | Last Period 10min 6th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FEF | 0x9FF0 | 40943 | 40944 | LAST_VOL_HARM_AVGc7 | Last Period 10min 7th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FF1 | 0x9FF2 | 40945 | 40946 | LAST_VOL_HARM_AVGc8 | Last Period 10min 8th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FF3 | 0x9FF4 | 40947 | 40948 | LAST_VOL_HARM_AVGc9 | Last Period 10min 9th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FF5 | 0x9FF6 | 40949 | 40950 | LAST_VOL_HARM_AVGc10 | Last Period 10min 10th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FF7 | 0x9FF8 | 40951 | 40952 | LAST_VOL_HARM_AVGc11 | Last Period 10min 11st Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FF9 | 0x9FFA | 40953 | 40954 | LAST_VOL_HARM_AVGc12 | Last Period 10min 12nd Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FFB | 0x9FFC | 40955 | 40956 | LAST_VOL_HARM_AVGc13 | Last Period 10min 13rd Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FFD | 0x9FFE | 40957 | 40958 | LAST_VOL_HARM_AVGc14 | Last Period 10min 14th Phase C Voltage Harmonics Average Value | float | 2 | R
0x9FFF | 0xA000 | 40959 | 40960 | LAST_VOL_HARM_AVGc15 | Last Period 10min 15th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA001 | 0xA002 | 40961 | 40962 | LAST_VOL_HARM_AVGc16 | Last Period 10min 16th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA003 | 0xA004 | 40963 | 40964 | LAST_VOL_HARM_AVGc17 | Last Period 10min 17th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA005 | 0xA006 | 40965 | 40966 | LAST_VOL_HARM_AVGc18 | Last Period 10min 18th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA007 | 0xA008 | 40967 | 40968 | LAST_VOL_HARM_AVGc19 | Last Period 10min 19th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA009 | 0xA00A | 40969 | 40970 | LAST_VOL_HARM_AVGc20 | Last Period 10min 20th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA00B | 0xA00C | 40971 | 40972 | LAST_VOL_HARM_AVGc21 | Last Period 10min 21st Phase C Voltage Harmonics Average Value | float | 2 | R
0xA00D | 0xA00E | 40973 | 40974 | LAST_VOL_HARM_AVGc22 | Last Period 10min 22nd Phase C Voltage Harmonics Average Value | float | 2 | R
0xA00F | 0xA010 | 40975 | 40976 | LAST_VOL_HARM_AVGc23 | Last Period 10min 23rd Phase C Voltage Harmonics Average Value | float | 2 | R
0xA011 | 0xA012 | 40977 | 40978 | LAST_VOL_HARM_AVGc24 | Last Period 10min 24th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA013 | 0xA014 | 40979 | 40980 | LAST_VOL_HARM_AVGc25 | Last Period 10min 25th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA015 | 0xA016 | 40981 | 40982 | LAST_VOL_HARM_AVGc26 | Last Period 10min 26th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA017 | 0xA018 | 40983 | 40984 | LAST_VOL_HARM_AVGc27 | Last Period 10min 27th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA019 | 0xA01A | 40985 | 40986 | LAST_VOL_HARM_AVGc28 | Last Period 10min 28th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA01B | 0xA01C | 40987 | 40988 | LAST_VOL_HARM_AVGc29 | Last Period 10min 29th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA01D | 0xA01E | 40989 | 40990 | LAST_VOL_HARM_AVGc30 | Last Period 10min 30th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA01F | 0xA020 | 40991 | 40992 | LAST_VOL_HARM_AVGc31 | Last Period 10min 31st Phase C Voltage Harmonics Average Value | float | 2 | R
0xA021 | 0xA022 | 40993 | 40994 | LAST_VOL_HARM_AVGc32 | Last Period 10min 32nd Phase C Voltage Harmonics Average Value | float | 2 | R
0xA023 | 0xA024 | 40995 | 40996 | LAST_VOL_HARM_AVGc33 | Last Period 10min 33rd Phase C Voltage Harmonics Average Value | float | 2 | R
0xA025 | 0xA026 | 40997 | 40998 | LAST_VOL_HARM_AVGc34 | Last Period 10min 34th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA027 | 0xA028 | 40999 | 41000 | LAST_VOL_HARM_AVGc35 | Last Period 10min 35th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA029 | 0xA02A | 41001 | 41002 | LAST_VOL_HARM_AVGc36 | Last Period 10min 36th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA02B | 0xA02C | 41003 | 41004 | LAST_VOL_HARM_AVGc37 | Last Period 10min 37th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA02D | 0xA02E | 41005 | 41006 | LAST_VOL_HARM_AVGc38 | Last Period 10min 38th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA02F | 0xA030 | 41007 | 41008 | LAST_VOL_HARM_AVGc39 | Last Period 10min 39th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA031 | 0xA032 | 41009 | 41010 | LAST_VOL_HARM_AVGc40 | Last Period 10min 40th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA033 | 0xA034 | 41011 | 41012 | LAST_VOL_HARM_AVGc41 | Last Period 10min 41st Phase C Voltage Harmonics Average Value | float | 2 | R
0xA035 | 0xA036 | 41013 | 41014 | LAST_VOL_HARM_AVGc42 | Last Period 10min 42nd Phase C Voltage Harmonics Average Value | float | 2 | R
0xA037 | 0xA038 | 41015 | 41016 | LAST_VOL_HARM_AVGc43 | Last Period 10min 43rd Phase C Voltage Harmonics Average Value | float | 2 | R
0xA039 | 0xA03A | 41017 | 41018 | LAST_VOL_HARM_AVGc44 | Last Period 10min 44th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA03B | 0xA03C | 41019 | 41020 | LAST_VOL_HARM_AVGc45 | Last Period 10min 45th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA03D | 0xA03E | 41021 | 41022 | LAST_VOL_HARM_AVGc46 | Last Period 10min 46th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA03F | 0xA040 | 41023 | 41024 | LAST_VOL_HARM_AVGc47 | Last Period 10min 47th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA041 | 0xA042 | 41025 | 41026 | LAST_VOL_HARM_AVGc48 | Last Period 10min 48th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA043 | 0xA044 | 41027 | 41028 | LAST_VOL_HARM_AVGc49 | Last Period 10min 49th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA045 | 0xA046 | 41029 | 41030 | LAST_VOL_HARM_AVGc50 | Last Period 10min 50th Phase C Voltage Harmonics Average Value | float | 2 | R
0xA047 | 0xA048 | 41031 | 41032 | LAST_TDD_MAXa | Last Period 10min Phase A TDD Maximum Value | float | 2 | R
0xA049 | 0xA04A | 41033 | 41034 | LAST_TDD_MAXb | Last Period 10min Phase B TDD Maximum Value | float | 2 | R
0xA04B | 0xA04C | 41035 | 41036 | LAST_TDD_MAXc | Last Period 10min Phase C TDD Maximum Value | float | 2 | R
0xA04D | 0xA04E | 41037 | 41038 | LAST_TDD_MINa | Last Period 10min Phase A TDD Minimum Value | float | 2 | R
0xA04F | 0xA050 | 41039 | 41040 | LAST_TDD_MINb | Last Period 10min Phase B TDD Minimum Value | float | 2 | R
0xA051 | 0xA052 | 41041 | 41042 | LAST_TDD_MINc | Last Period 10min Phase C TDD Minimum Value | float | 2 | R
0xA053 | 0xA054 | 41043 | 41044 | LAST_TDD_AVGa | Last Period 10min Phase A TDD Average Value | float | 2 | R
0xA055 | 0xA056 | 41045 | 41046 | LAST_TDD_AVGb | Last Period 10min Phase B TDD Average Value | float | 2 | R
0xA057 | 0xA058 | 41047 | 41048 | LAST_TDD_AVGc | Last Period 10min Phase C TDD Average Value | float | 2 | R
0xA059 | 0xA05A | 41049 | 41050 | LAST_CUR_HARM_MAXa2 | Last Period 10min 2nd Phase A Current Harmonics Maximum Value | float | 2 | R
0xA05B | 0xA05C | 41051 | 41052 | LAST_CUR_HARM_MAXa3 | Last Period 10min 3rd Phase A Current Harmonics Maximum Value | float | 2 | R
0xA05D | 0xA05E | 41053 | 41054 | LAST_CUR_HARM_MAXa4 | Last Period 10min 4th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA05F | 0xA060 | 41055 | 41056 | LAST_CUR_HARM_MAXa5 | Last Period 10min 5th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA061 | 0xA062 | 41057 | 41058 | LAST_CUR_HARM_MAXa6 | Last Period 10min 6th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA063 | 0xA064 | 41059 | 41060 | LAST_CUR_HARM_MAXa7 | Last Period 10min 7th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA065 | 0xA066 | 41061 | 41062 | LAST_CUR_HARM_MAXa8 | Last Period 10min 8th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA067 | 0xA068 | 41063 | 41064 | LAST_CUR_HARM_MAXa9 | Last Period 10min 9th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA069 | 0xA06A | 41065 | 41066 | LAST_CUR_HARM_MAXa10 | Last Period 10min 10th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA06B | 0xA06C | 41067 | 41068 | LAST_CUR_HARM_MAXa11 | Last Period 10min 11st Phase A Current Harmonics Maximum Value | float | 2 | R
0xA06D | 0xA06E | 41069 | 41070 | LAST_CUR_HARM_MAXa12 | Last Period 10min 12nd Phase A Current Harmonics Maximum Value | float | 2 | R
0xA06F | 0xA070 | 41071 | 41072 | LAST_CUR_HARM_MAXa13 | Last Period 10min 13rd Phase A Current Harmonics Maximum Value | float | 2 | R
0xA071 | 0xA072 | 41073 | 41074 | LAST_CUR_HARM_MAXa14 | Last Period 10min 14th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA073 | 0xA074 | 41075 | 41076 | LAST_CUR_HARM_MAXa15 | Last Period 10min 15th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA075 | 0xA076 | 41077 | 41078 | LAST_CUR_HARM_MAXa16 | Last Period 10min 16th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA077 | 0xA078 | 41079 | 41080 | LAST_CUR_HARM_MAXa17 | Last Period 10min 17th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA079 | 0xA07A | 41081 | 41082 | LAST_CUR_HARM_MAXa18 | Last Period 10min 18th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA07B | 0xA07C | 41083 | 41084 | LAST_CUR_HARM_MAXa19 | Last Period 10min 19th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA07D | 0xA07E | 41085 | 41086 | LAST_CUR_HARM_MAXa20 | Last Period 10min 20th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA07F | 0xA080 | 41087 | 41088 | LAST_CUR_HARM_MAXa21 | Last Period 10min 21st Phase A Current Harmonics Maximum Value | float | 2 | R
0xA081 | 0xA082 | 41089 | 41090 | LAST_CUR_HARM_MAXa22 | Last Period 10min 22nd Phase A Current Harmonics Maximum Value | float | 2 | R
0xA083 | 0xA084 | 41091 | 41092 | LAST_CUR_HARM_MAXa23 | Last Period 10min 23rd Phase A Current Harmonics Maximum Value | float | 2 | R
0xA085 | 0xA086 | 41093 | 41094 | LAST_CUR_HARM_MAXa24 | Last Period 10min 24th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA087 | 0xA088 | 41095 | 41096 | LAST_CUR_HARM_MAXa25 | Last Period 10min 25th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA089 | 0xA08A | 41097 | 41098 | LAST_CUR_HARM_MAXa26 | Last Period 10min 26th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA08B | 0xA08C | 41099 | 41100 | LAST_CUR_HARM_MAXa27 | Last Period 10min 27th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA08D | 0xA08E | 41101 | 41102 | LAST_CUR_HARM_MAXa28 | Last Period 10min 28th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA08F | 0xA090 | 41103 | 41104 | LAST_CUR_HARM_MAXa29 | Last Period 10min 29th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA091 | 0xA092 | 41105 | 41106 | LAST_CUR_HARM_MAXa30 | Last Period 10min 30th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA093 | 0xA094 | 41107 | 41108 | LAST_CUR_HARM_MAXa31 | Last Period 10min 31st Phase A Current Harmonics Maximum Value | float | 2 | R
0xA095 | 0xA096 | 41109 | 41110 | LAST_CUR_HARM_MAXa32 | Last Period 10min 32nd Phase A Current Harmonics Maximum Value | float | 2 | R
0xA097 | 0xA098 | 41111 | 41112 | LAST_CUR_HARM_MAXa33 | Last Period 10min 33rd Phase A Current Harmonics Maximum Value | float | 2 | R
0xA099 | 0xA09A | 41113 | 41114 | LAST_CUR_HARM_MAXa34 | Last Period 10min 34th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA09B | 0xA09C | 41115 | 41116 | LAST_CUR_HARM_MAXa35 | Last Period 10min 35th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA09D | 0xA09E | 41117 | 41118 | LAST_CUR_HARM_MAXa36 | Last Period 10min 36th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA09F | 0xA0A0 | 41119 | 41120 | LAST_CUR_HARM_MAXa37 | Last Period 10min 37th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0A1 | 0xA0A2 | 41121 | 41122 | LAST_CUR_HARM_MAXa38 | Last Period 10min 38th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0A3 | 0xA0A4 | 41123 | 41124 | LAST_CUR_HARM_MAXa39 | Last Period 10min 39th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0A5 | 0xA0A6 | 41125 | 41126 | LAST_CUR_HARM_MAXa40 | Last Period 10min 40th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0A7 | 0xA0A8 | 41127 | 41128 | LAST_CUR_HARM_MAXa41 | Last Period 10min 41st Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0A9 | 0xA0AA | 41129 | 41130 | LAST_CUR_HARM_MAXa42 | Last Period 10min 42nd Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0AB | 0xA0AC | 41131 | 41132 | LAST_CUR_HARM_MAXa43 | Last Period 10min 43rd Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0AD | 0xA0AE | 41133 | 41134 | LAST_CUR_HARM_MAXa44 | Last Period 10min 44th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0AF | 0xA0B0 | 41135 | 41136 | LAST_CUR_HARM_MAXa45 | Last Period 10min 45th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0B1 | 0xA0B2 | 41137 | 41138 | LAST_CUR_HARM_MAXa46 | Last Period 10min 46th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0B3 | 0xA0B4 | 41139 | 41140 | LAST_CUR_HARM_MAXa47 | Last Period 10min 47th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0B5 | 0xA0B6 | 41141 | 41142 | LAST_CUR_HARM_MAXa48 | Last Period 10min 48th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0B7 | 0xA0B8 | 41143 | 41144 | LAST_CUR_HARM_MAXa49 | Last Period 10min 49th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0B9 | 0xA0BA | 41145 | 41146 | LAST_CUR_HARM_MAXa50 | Last Period 10min 50th Phase A Current Harmonics Maximum Value | float | 2 | R
0xA0BB | 0xA0BC | 41147 | 41148 | LAST_CUR_HARM_MAXb2 | Last Period 10min 2nd Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0BD | 0xA0BE | 41149 | 41150 | LAST_CUR_HARM_MAXb3 | Last Period 10min 3rd Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0BF | 0xA0C0 | 41151 | 41152 | LAST_CUR_HARM_MAXb4 | Last Period 10min 4th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0C1 | 0xA0C2 | 41153 | 41154 | LAST_CUR_HARM_MAXb5 | Last Period 10min 5th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0C3 | 0xA0C4 | 41155 | 41156 | LAST_CUR_HARM_MAXb6 | Last Period 10min 6th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0C5 | 0xA0C6 | 41157 | 41158 | LAST_CUR_HARM_MAXb7 | Last Period 10min 7th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0C7 | 0xA0C8 | 41159 | 41160 | LAST_CUR_HARM_MAXb8 | Last Period 10min 8th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0C9 | 0xA0CA | 41161 | 41162 | LAST_CUR_HARM_MAXb9 | Last Period 10min 9th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0CB | 0xA0CC | 41163 | 41164 | LAST_CUR_HARM_MAXb10 | Last Period 10min 10th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0CD | 0xA0CE | 41165 | 41166 | LAST_CUR_HARM_MAXb11 | Last Period 10min 11st Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0CF | 0xA0D0 | 41167 | 41168 | LAST_CUR_HARM_MAXb12 | Last Period 10min 12nd Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0D1 | 0xA0D2 | 41169 | 41170 | LAST_CUR_HARM_MAXb13 | Last Period 10min 13rd Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0D3 | 0xA0D4 | 41171 | 41172 | LAST_CUR_HARM_MAXb14 | Last Period 10min 14th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0D5 | 0xA0D6 | 41173 | 41174 | LAST_CUR_HARM_MAXb15 | Last Period 10min 15th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0D7 | 0xA0D8 | 41175 | 41176 | LAST_CUR_HARM_MAXb16 | Last Period 10min 16th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0D9 | 0xA0DA | 41177 | 41178 | LAST_CUR_HARM_MAXb17 | Last Period 10min 17th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0DB | 0xA0DC | 41179 | 41180 | LAST_CUR_HARM_MAXb18 | Last Period 10min 18th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0DD | 0xA0DE | 41181 | 41182 | LAST_CUR_HARM_MAXb19 | Last Period 10min 19th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0DF | 0xA0E0 | 41183 | 41184 | LAST_CUR_HARM_MAXb20 | Last Period 10min 20th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0E1 | 0xA0E2 | 41185 | 41186 | LAST_CUR_HARM_MAXb21 | Last Period 10min 21st Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0E3 | 0xA0E4 | 41187 | 41188 | LAST_CUR_HARM_MAXb22 | Last Period 10min 22nd Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0E5 | 0xA0E6 | 41189 | 41190 | LAST_CUR_HARM_MAXb23 | Last Period 10min 23rd Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0E7 | 0xA0E8 | 41191 | 41192 | LAST_CUR_HARM_MAXb24 | Last Period 10min 24th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0E9 | 0xA0EA | 41193 | 41194 | LAST_CUR_HARM_MAXb25 | Last Period 10min 25th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0EB | 0xA0EC | 41195 | 41196 | LAST_CUR_HARM_MAXb26 | Last Period 10min 26th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0ED | 0xA0EE | 41197 | 41198 | LAST_CUR_HARM_MAXb27 | Last Period 10min 27th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0EF | 0xA0F0 | 41199 | 41200 | LAST_CUR_HARM_MAXb28 | Last Period 10min 28th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0F1 | 0xA0F2 | 41201 | 41202 | LAST_CUR_HARM_MAXb29 | Last Period 10min 29th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0F3 | 0xA0F4 | 41203 | 41204 | LAST_CUR_HARM_MAXb30 | Last Period 10min 30th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0F5 | 0xA0F6 | 41205 | 41206 | LAST_CUR_HARM_MAXb31 | Last Period 10min 31st Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0F7 | 0xA0F8 | 41207 | 41208 | LAST_CUR_HARM_MAXb32 | Last Period 10min 32nd Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0F9 | 0xA0FA | 41209 | 41210 | LAST_CUR_HARM_MAXb33 | Last Period 10min 33rd Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0FB | 0xA0FC | 41211 | 41212 | LAST_CUR_HARM_MAXb34 | Last Period 10min 34th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0FD | 0xA0FE | 41213 | 41214 | LAST_CUR_HARM_MAXb35 | Last Period 10min 35th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA0FF | 0xA100 | 41215 | 41216 | LAST_CUR_HARM_MAXb36 | Last Period 10min 36th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA101 | 0xA102 | 41217 | 41218 | LAST_CUR_HARM_MAXb37 | Last Period 10min 37th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA103 | 0xA104 | 41219 | 41220 | LAST_CUR_HARM_MAXb38 | Last Period 10min 38th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA105 | 0xA106 | 41221 | 41222 | LAST_CUR_HARM_MAXb39 | Last Period 10min 39th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA107 | 0xA108 | 41223 | 41224 | LAST_CUR_HARM_MAXb40 | Last Period 10min 40th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA109 | 0xA10A | 41225 | 41226 | LAST_CUR_HARM_MAXb41 | Last Period 10min 41st Phase B Current Harmonics Maximum Value | float | 2 | R
0xA10B | 0xA10C | 41227 | 41228 | LAST_CUR_HARM_MAXb42 | Last Period 10min 42nd Phase B Current Harmonics Maximum Value | float | 2 | R
0xA10D | 0xA10E | 41229 | 41230 | LAST_CUR_HARM_MAXb43 | Last Period 10min 43rd Phase B Current Harmonics Maximum Value | float | 2 | R
0xA10F | 0xA110 | 41231 | 41232 | LAST_CUR_HARM_MAXb44 | Last Period 10min 44th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA111 | 0xA112 | 41233 | 41234 | LAST_CUR_HARM_MAXb45 | Last Period 10min 45th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA113 | 0xA114 | 41235 | 41236 | LAST_CUR_HARM_MAXb46 | Last Period 10min 46th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA115 | 0xA116 | 41237 | 41238 | LAST_CUR_HARM_MAXb47 | Last Period 10min 47th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA117 | 0xA118 | 41239 | 41240 | LAST_CUR_HARM_MAXb48 | Last Period 10min 48th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA119 | 0xA11A | 41241 | 41242 | LAST_CUR_HARM_MAXb49 | Last Period 10min 49th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA11B | 0xA11C | 41243 | 41244 | LAST_CUR_HARM_MAXb50 | Last Period 10min 50th Phase B Current Harmonics Maximum Value | float | 2 | R
0xA11D | 0xA11E | 41245 | 41246 | LAST_CUR_HARM_MAXc2 | Last Period 10min 2nd Phase C Current Harmonics Maximum Value | float | 2 | R
0xA11F | 0xA120 | 41247 | 41248 | LAST_CUR_HARM_MAXc3 | Last Period 10min 3rd Phase C Current Harmonics Maximum Value | float | 2 | R
0xA121 | 0xA122 | 41249 | 41250 | LAST_CUR_HARM_MAXc4 | Last Period 10min 4th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA123 | 0xA124 | 41251 | 41252 | LAST_CUR_HARM_MAXc5 | Last Period 10min 5th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA125 | 0xA126 | 41253 | 41254 | LAST_CUR_HARM_MAXc6 | Last Period 10min 6th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA127 | 0xA128 | 41255 | 41256 | LAST_CUR_HARM_MAXc7 | Last Period 10min 7th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA129 | 0xA12A | 41257 | 41258 | LAST_CUR_HARM_MAXc8 | Last Period 10min 8th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA12B | 0xA12C | 41259 | 41260 | LAST_CUR_HARM_MAXc9 | Last Period 10min 9th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA12D | 0xA12E | 41261 | 41262 | LAST_CUR_HARM_MAXc10 | Last Period 10min 10th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA12F | 0xA130 | 41263 | 41264 | LAST_CUR_HARM_MAXc11 | Last Period 10min 11st Phase C Current Harmonics Maximum Value | float | 2 | R
0xA131 | 0xA132 | 41265 | 41266 | LAST_CUR_HARM_MAXc12 | Last Period 10min 12nd Phase C Current Harmonics Maximum Value | float | 2 | R
0xA133 | 0xA134 | 41267 | 41268 | LAST_CUR_HARM_MAXc13 | Last Period 10min 13rd Phase C Current Harmonics Maximum Value | float | 2 | R
0xA135 | 0xA136 | 41269 | 41270 | LAST_CUR_HARM_MAXc14 | Last Period 10min 14th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA137 | 0xA138 | 41271 | 41272 | LAST_CUR_HARM_MAXc15 | Last Period 10min 15th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA139 | 0xA13A | 41273 | 41274 | LAST_CUR_HARM_MAXc16 | Last Period 10min 16th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA13B | 0xA13C | 41275 | 41276 | LAST_CUR_HARM_MAXc17 | Last Period 10min 17th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA13D | 0xA13E | 41277 | 41278 | LAST_CUR_HARM_MAXc18 | Last Period 10min 18th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA13F | 0xA140 | 41279 | 41280 | LAST_CUR_HARM_MAXc19 | Last Period 10min 19th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA141 | 0xA142 | 41281 | 41282 | LAST_CUR_HARM_MAXc20 | Last Period 10min 20th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA143 | 0xA144 | 41283 | 41284 | LAST_CUR_HARM_MAXc21 | Last Period 10min 21st Phase C Current Harmonics Maximum Value | float | 2 | R
0xA145 | 0xA146 | 41285 | 41286 | LAST_CUR_HARM_MAXc22 | Last Period 10min 22nd Phase C Current Harmonics Maximum Value | float | 2 | R
0xA147 | 0xA148 | 41287 | 41288 | LAST_CUR_HARM_MAXc23 | Last Period 10min 23rd Phase C Current Harmonics Maximum Value | float | 2 | R
0xA149 | 0xA14A | 41289 | 41290 | LAST_CUR_HARM_MAXc24 | Last Period 10min 24th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA14B | 0xA14C | 41291 | 41292 | LAST_CUR_HARM_MAXc25 | Last Period 10min 25th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA14D | 0xA14E | 41293 | 41294 | LAST_CUR_HARM_MAXc26 | Last Period 10min 26th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA14F | 0xA150 | 41295 | 41296 | LAST_CUR_HARM_MAXc27 | Last Period 10min 27th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA151 | 0xA152 | 41297 | 41298 | LAST_CUR_HARM_MAXc28 | Last Period 10min 28th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA153 | 0xA154 | 41299 | 41300 | LAST_CUR_HARM_MAXc29 | Last Period 10min 29th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA155 | 0xA156 | 41301 | 41302 | LAST_CUR_HARM_MAXc30 | Last Period 10min 30th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA157 | 0xA158 | 41303 | 41304 | LAST_CUR_HARM_MAXc31 | Last Period 10min 31st Phase C Current Harmonics Maximum Value | float | 2 | R
0xA159 | 0xA15A | 41305 | 41306 | LAST_CUR_HARM_MAXc32 | Last Period 10min 32nd Phase C Current Harmonics Maximum Value | float | 2 | R
0xA15B | 0xA15C | 41307 | 41308 | LAST_CUR_HARM_MAXc33 | Last Period 10min 33rd Phase C Current Harmonics Maximum Value | float | 2 | R
0xA15D | 0xA15E | 41309 | 41310 | LAST_CUR_HARM_MAXc34 | Last Period 10min 34th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA15F | 0xA160 | 41311 | 41312 | LAST_CUR_HARM_MAXc35 | Last Period 10min 35th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA161 | 0xA162 | 41313 | 41314 | LAST_CUR_HARM_MAXc36 | Last Period 10min 36th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA163 | 0xA164 | 41315 | 41316 | LAST_CUR_HARM_MAXc37 | Last Period 10min 37th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA165 | 0xA166 | 41317 | 41318 | LAST_CUR_HARM_MAXc38 | Last Period 10min 38th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA167 | 0xA168 | 41319 | 41320 | LAST_CUR_HARM_MAXc39 | Last Period 10min 39th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA169 | 0xA16A | 41321 | 41322 | LAST_CUR_HARM_MAXc40 | Last Period 10min 40th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA16B | 0xA16C | 41323 | 41324 | LAST_CUR_HARM_MAXc41 | Last Period 10min 41st Phase C Current Harmonics Maximum Value | float | 2 | R
0xA16D | 0xA16E | 41325 | 41326 | LAST_CUR_HARM_MAXc42 | Last Period 10min 42nd Phase C Current Harmonics Maximum Value | float | 2 | R
0xA16F | 0xA170 | 41327 | 41328 | LAST_CUR_HARM_MAXc43 | Last Period 10min 43rd Phase C Current Harmonics Maximum Value | float | 2 | R
0xA171 | 0xA172 | 41329 | 41330 | LAST_CUR_HARM_MAXc44 | Last Period 10min 44th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA173 | 0xA174 | 41331 | 41332 | LAST_CUR_HARM_MAXc45 | Last Period 10min 45th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA175 | 0xA176 | 41333 | 41334 | LAST_CUR_HARM_MAXc46 | Last Period 10min 46th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA177 | 0xA178 | 41335 | 41336 | LAST_CUR_HARM_MAXc47 | Last Period 10min 47th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA179 | 0xA17A | 41337 | 41338 | LAST_CUR_HARM_MAXc48 | Last Period 10min 48th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA17B | 0xA17C | 41339 | 41340 | LAST_CUR_HARM_MAXc49 | Last Period 10min 49th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA17D | 0xA17E | 41341 | 41342 | LAST_CUR_HARM_MAXc50 | Last Period 10min 50th Phase C Current Harmonics Maximum Value | float | 2 | R
0xA17F | 0xA180 | 41343 | 41344 | LAST_CUR_HARM_MINa2 | Last Period 10min 2nd Phase A Current Harmonics Minimum Value | float | 2 | R
0xA181 | 0xA182 | 41345 | 41346 | LAST_CUR_HARM_MINa3 | Last Period 10min 3rd Phase A Current Harmonics Minimum Value | float | 2 | R
0xA183 | 0xA184 | 41347 | 41348 | LAST_CUR_HARM_MINa4 | Last Period 10min 4th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA185 | 0xA186 | 41349 | 41350 | LAST_CUR_HARM_MINa5 | Last Period 10min 5th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA187 | 0xA188 | 41351 | 41352 | LAST_CUR_HARM_MINa6 | Last Period 10min 6th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA189 | 0xA18A | 41353 | 41354 | LAST_CUR_HARM_MINa7 | Last Period 10min 7th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA18B | 0xA18C | 41355 | 41356 | LAST_CUR_HARM_MINa8 | Last Period 10min 8th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA18D | 0xA18E | 41357 | 41358 | LAST_CUR_HARM_MINa9 | Last Period 10min 9th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA18F | 0xA190 | 41359 | 41360 | LAST_CUR_HARM_MINa10 | Last Period 10min 10th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA191 | 0xA192 | 41361 | 41362 | LAST_CUR_HARM_MINa11 | Last Period 10min 11st Phase A Current Harmonics Minimum Value | float | 2 | R
0xA193 | 0xA194 | 41363 | 41364 | LAST_CUR_HARM_MINa12 | Last Period 10min 12nd Phase A Current Harmonics Minimum Value | float | 2 | R
0xA195 | 0xA196 | 41365 | 41366 | LAST_CUR_HARM_MINa13 | Last Period 10min 13rd Phase A Current Harmonics Minimum Value | float | 2 | R
0xA197 | 0xA198 | 41367 | 41368 | LAST_CUR_HARM_MINa14 | Last Period 10min 14th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA199 | 0xA19A | 41369 | 41370 | LAST_CUR_HARM_MINa15 | Last Period 10min 15th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA19B | 0xA19C | 41371 | 41372 | LAST_CUR_HARM_MINa16 | Last Period 10min 16th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA19D | 0xA19E | 41373 | 41374 | LAST_CUR_HARM_MINa17 | Last Period 10min 17th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA19F | 0xA1A0 | 41375 | 41376 | LAST_CUR_HARM_MINa18 | Last Period 10min 18th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1A1 | 0xA1A2 | 41377 | 41378 | LAST_CUR_HARM_MINa19 | Last Period 10min 19th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1A3 | 0xA1A4 | 41379 | 41380 | LAST_CUR_HARM_MINa20 | Last Period 10min 20th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1A5 | 0xA1A6 | 41381 | 41382 | LAST_CUR_HARM_MINa21 | Last Period 10min 21st Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1A7 | 0xA1A8 | 41383 | 41384 | LAST_CUR_HARM_MINa22 | Last Period 10min 22nd Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1A9 | 0xA1AA | 41385 | 41386 | LAST_CUR_HARM_MINa23 | Last Period 10min 23rd Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1AB | 0xA1AC | 41387 | 41388 | LAST_CUR_HARM_MINa24 | Last Period 10min 24th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1AD | 0xA1AE | 41389 | 41390 | LAST_CUR_HARM_MINa25 | Last Period 10min 25th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1AF | 0xA1B0 | 41391 | 41392 | LAST_CUR_HARM_MINa26 | Last Period 10min 26th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1B1 | 0xA1B2 | 41393 | 41394 | LAST_CUR_HARM_MINa27 | Last Period 10min 27th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1B3 | 0xA1B4 | 41395 | 41396 | LAST_CUR_HARM_MINa28 | Last Period 10min 28th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1B5 | 0xA1B6 | 41397 | 41398 | LAST_CUR_HARM_MINa29 | Last Period 10min 29th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1B7 | 0xA1B8 | 41399 | 41400 | LAST_CUR_HARM_MINa30 | Last Period 10min 30th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1B9 | 0xA1BA | 41401 | 41402 | LAST_CUR_HARM_MINa31 | Last Period 10min 31st Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1BB | 0xA1BC | 41403 | 41404 | LAST_CUR_HARM_MINa32 | Last Period 10min 32nd Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1BD | 0xA1BE | 41405 | 41406 | LAST_CUR_HARM_MINa33 | Last Period 10min 33rd Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1BF | 0xA1C0 | 41407 | 41408 | LAST_CUR_HARM_MINa34 | Last Period 10min 34th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1C1 | 0xA1C2 | 41409 | 41410 | LAST_CUR_HARM_MINa35 | Last Period 10min 35th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1C3 | 0xA1C4 | 41411 | 41412 | LAST_CUR_HARM_MINa36 | Last Period 10min 36th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1C5 | 0xA1C6 | 41413 | 41414 | LAST_CUR_HARM_MINa37 | Last Period 10min 37th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1C7 | 0xA1C8 | 41415 | 41416 | LAST_CUR_HARM_MINa38 | Last Period 10min 38th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1C9 | 0xA1CA | 41417 | 41418 | LAST_CUR_HARM_MINa39 | Last Period 10min 39th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1CB | 0xA1CC | 41419 | 41420 | LAST_CUR_HARM_MINa40 | Last Period 10min 40th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1CD | 0xA1CE | 41421 | 41422 | LAST_CUR_HARM_MINa41 | Last Period 10min 41st Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1CF | 0xA1D0 | 41423 | 41424 | LAST_CUR_HARM_MINa42 | Last Period 10min 42nd Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1D1 | 0xA1D2 | 41425 | 41426 | LAST_CUR_HARM_MINa43 | Last Period 10min 43rd Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1D3 | 0xA1D4 | 41427 | 41428 | LAST_CUR_HARM_MINa44 | Last Period 10min 44th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1D5 | 0xA1D6 | 41429 | 41430 | LAST_CUR_HARM_MINa45 | Last Period 10min 45th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1D7 | 0xA1D8 | 41431 | 41432 | LAST_CUR_HARM_MINa46 | Last Period 10min 46th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1D9 | 0xA1DA | 41433 | 41434 | LAST_CUR_HARM_MINa47 | Last Period 10min 47th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1DB | 0xA1DC | 41435 | 41436 | LAST_CUR_HARM_MINa48 | Last Period 10min 48th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1DD | 0xA1DE | 41437 | 41438 | LAST_CUR_HARM_MINa49 | Last Period 10min 49th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1DF | 0xA1E0 | 41439 | 41440 | LAST_CUR_HARM_MINa50 | Last Period 10min 50th Phase A Current Harmonics Minimum Value | float | 2 | R
0xA1E1 | 0xA1E2 | 41441 | 41442 | LAST_CUR_HARM_MINb2 | Last Period 10min 2nd Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1E3 | 0xA1E4 | 41443 | 41444 | LAST_CUR_HARM_MINb3 | Last Period 10min 3rd Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1E5 | 0xA1E6 | 41445 | 41446 | LAST_CUR_HARM_MINb4 | Last Period 10min 4th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1E7 | 0xA1E8 | 41447 | 41448 | LAST_CUR_HARM_MINb5 | Last Period 10min 5th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1E9 | 0xA1EA | 41449 | 41450 | LAST_CUR_HARM_MINb6 | Last Period 10min 6th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1EB | 0xA1EC | 41451 | 41452 | LAST_CUR_HARM_MINb7 | Last Period 10min 7th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1ED | 0xA1EE | 41453 | 41454 | LAST_CUR_HARM_MINb8 | Last Period 10min 8th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1EF | 0xA1F0 | 41455 | 41456 | LAST_CUR_HARM_MINb9 | Last Period 10min 9th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1F1 | 0xA1F2 | 41457 | 41458 | LAST_CUR_HARM_MINb10 | Last Period 10min 10th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1F3 | 0xA1F4 | 41459 | 41460 | LAST_CUR_HARM_MINb11 | Last Period 10min 11st Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1F5 | 0xA1F6 | 41461 | 41462 | LAST_CUR_HARM_MINb12 | Last Period 10min 12nd Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1F7 | 0xA1F8 | 41463 | 41464 | LAST_CUR_HARM_MINb13 | Last Period 10min 13rd Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1F9 | 0xA1FA | 41465 | 41466 | LAST_CUR_HARM_MINb14 | Last Period 10min 14th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1FB | 0xA1FC | 41467 | 41468 | LAST_CUR_HARM_MINb15 | Last Period 10min 15th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1FD | 0xA1FE | 41469 | 41470 | LAST_CUR_HARM_MINb16 | Last Period 10min 16th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA1FF | 0xA200 | 41471 | 41472 | LAST_CUR_HARM_MINb17 | Last Period 10min 17th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA201 | 0xA202 | 41473 | 41474 | LAST_CUR_HARM_MINb18 | Last Period 10min 18th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA203 | 0xA204 | 41475 | 41476 | LAST_CUR_HARM_MINb19 | Last Period 10min 19th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA205 | 0xA206 | 41477 | 41478 | LAST_CUR_HARM_MINb20 | Last Period 10min 20th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA207 | 0xA208 | 41479 | 41480 | LAST_CUR_HARM_MINb21 | Last Period 10min 21st Phase B Current Harmonics Minimum Value | float | 2 | R
0xA209 | 0xA20A | 41481 | 41482 | LAST_CUR_HARM_MINb22 | Last Period 10min 22nd Phase B Current Harmonics Minimum Value | float | 2 | R
0xA20B | 0xA20C | 41483 | 41484 | LAST_CUR_HARM_MINb23 | Last Period 10min 23rd Phase B Current Harmonics Minimum Value | float | 2 | R
0xA20D | 0xA20E | 41485 | 41486 | LAST_CUR_HARM_MINb24 | Last Period 10min 24th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA20F | 0xA210 | 41487 | 41488 | LAST_CUR_HARM_MINb25 | Last Period 10min 25th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA211 | 0xA212 | 41489 | 41490 | LAST_CUR_HARM_MINb26 | Last Period 10min 26th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA213 | 0xA214 | 41491 | 41492 | LAST_CUR_HARM_MINb27 | Last Period 10min 27th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA215 | 0xA216 | 41493 | 41494 | LAST_CUR_HARM_MINb28 | Last Period 10min 28th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA217 | 0xA218 | 41495 | 41496 | LAST_CUR_HARM_MINb29 | Last Period 10min 29th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA219 | 0xA21A | 41497 | 41498 | LAST_CUR_HARM_MINb30 | Last Period 10min 30th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA21B | 0xA21C | 41499 | 41500 | LAST_CUR_HARM_MINb31 | Last Period 10min 31st Phase B Current Harmonics Minimum Value | float | 2 | R
0xA21D | 0xA21E | 41501 | 41502 | LAST_CUR_HARM_MINb32 | Last Period 10min 32nd Phase B Current Harmonics Minimum Value | float | 2 | R
0xA21F | 0xA220 | 41503 | 41504 | LAST_CUR_HARM_MINb33 | Last Period 10min 33rd Phase B Current Harmonics Minimum Value | float | 2 | R
0xA221 | 0xA222 | 41505 | 41506 | LAST_CUR_HARM_MINb34 | Last Period 10min 34th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA223 | 0xA224 | 41507 | 41508 | LAST_CUR_HARM_MINb35 | Last Period 10min 35th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA225 | 0xA226 | 41509 | 41510 | LAST_CUR_HARM_MINb36 | Last Period 10min 36th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA227 | 0xA228 | 41511 | 41512 | LAST_CUR_HARM_MINb37 | Last Period 10min 37th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA229 | 0xA22A | 41513 | 41514 | LAST_CUR_HARM_MINb38 | Last Period 10min 38th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA22B | 0xA22C | 41515 | 41516 | LAST_CUR_HARM_MINb39 | Last Period 10min 39th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA22D | 0xA22E | 41517 | 41518 | LAST_CUR_HARM_MINb40 | Last Period 10min 40th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA22F | 0xA230 | 41519 | 41520 | LAST_CUR_HARM_MINb41 | Last Period 10min 41st Phase B Current Harmonics Minimum Value | float | 2 | R
0xA231 | 0xA232 | 41521 | 41522 | LAST_CUR_HARM_MINb42 | Last Period 10min 42nd Phase B Current Harmonics Minimum Value | float | 2 | R
0xA233 | 0xA234 | 41523 | 41524 | LAST_CUR_HARM_MINb43 | Last Period 10min 43rd Phase B Current Harmonics Minimum Value | float | 2 | R
0xA235 | 0xA236 | 41525 | 41526 | LAST_CUR_HARM_MINb44 | Last Period 10min 44th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA237 | 0xA238 | 41527 | 41528 | LAST_CUR_HARM_MINb45 | Last Period 10min 45th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA239 | 0xA23A | 41529 | 41530 | LAST_CUR_HARM_MINb46 | Last Period 10min 46th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA23B | 0xA23C | 41531 | 41532 | LAST_CUR_HARM_MINb47 | Last Period 10min 47th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA23D | 0xA23E | 41533 | 41534 | LAST_CUR_HARM_MINb48 | Last Period 10min 48th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA23F | 0xA240 | 41535 | 41536 | LAST_CUR_HARM_MINb49 | Last Period 10min 49th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA241 | 0xA242 | 41537 | 41538 | LAST_CUR_HARM_MINb50 | Last Period 10min 50th Phase B Current Harmonics Minimum Value | float | 2 | R
0xA243 | 0xA244 | 41539 | 41540 | LAST_CUR_HARM_MINc2 | Last Period 10min 2nd Phase C Current Harmonics Minimum Value | float | 2 | R
0xA245 | 0xA246 | 41541 | 41542 | LAST_CUR_HARM_MINc3 | Last Period 10min 3rd Phase C Current Harmonics Minimum Value | float | 2 | R
0xA247 | 0xA248 | 41543 | 41544 | LAST_CUR_HARM_MINc4 | Last Period 10min 4th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA249 | 0xA24A | 41545 | 41546 | LAST_CUR_HARM_MINc5 | Last Period 10min 5th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA24B | 0xA24C | 41547 | 41548 | LAST_CUR_HARM_MINc6 | Last Period 10min 6th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA24D | 0xA24E | 41549 | 41550 | LAST_CUR_HARM_MINc7 | Last Period 10min 7th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA24F | 0xA250 | 41551 | 41552 | LAST_CUR_HARM_MINc8 | Last Period 10min 8th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA251 | 0xA252 | 41553 | 41554 | LAST_CUR_HARM_MINc9 | Last Period 10min 9th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA253 | 0xA254 | 41555 | 41556 | LAST_CUR_HARM_MINc10 | Last Period 10min 10th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA255 | 0xA256 | 41557 | 41558 | LAST_CUR_HARM_MINc11 | Last Period 10min 11st Phase C Current Harmonics Minimum Value | float | 2 | R
0xA257 | 0xA258 | 41559 | 41560 | LAST_CUR_HARM_MINc12 | Last Period 10min 12nd Phase C Current Harmonics Minimum Value | float | 2 | R
0xA259 | 0xA25A | 41561 | 41562 | LAST_CUR_HARM_MINc13 | Last Period 10min 13rd Phase C Current Harmonics Minimum Value | float | 2 | R
0xA25B | 0xA25C | 41563 | 41564 | LAST_CUR_HARM_MINc14 | Last Period 10min 14th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA25D | 0xA25E | 41565 | 41566 | LAST_CUR_HARM_MINc15 | Last Period 10min 15th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA25F | 0xA260 | 41567 | 41568 | LAST_CUR_HARM_MINc16 | Last Period 10min 16th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA261 | 0xA262 | 41569 | 41570 | LAST_CUR_HARM_MINc17 | Last Period 10min 17th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA263 | 0xA264 | 41571 | 41572 | LAST_CUR_HARM_MINc18 | Last Period 10min 18th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA265 | 0xA266 | 41573 | 41574 | LAST_CUR_HARM_MINc19 | Last Period 10min 19th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA267 | 0xA268 | 41575 | 41576 | LAST_CUR_HARM_MINc20 | Last Period 10min 20th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA269 | 0xA26A | 41577 | 41578 | LAST_CUR_HARM_MINc21 | Last Period 10min 21st Phase C Current Harmonics Minimum Value | float | 2 | R
0xA26B | 0xA26C | 41579 | 41580 | LAST_CUR_HARM_MINc22 | Last Period 10min 22nd Phase C Current Harmonics Minimum Value | float | 2 | R
0xA26D | 0xA26E | 41581 | 41582 | LAST_CUR_HARM_MINc23 | Last Period 10min 23rd Phase C Current Harmonics Minimum Value | float | 2 | R
0xA26F | 0xA270 | 41583 | 41584 | LAST_CUR_HARM_MINc24 | Last Period 10min 24th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA271 | 0xA272 | 41585 | 41586 | LAST_CUR_HARM_MINc25 | Last Period 10min 25th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA273 | 0xA274 | 41587 | 41588 | LAST_CUR_HARM_MINc26 | Last Period 10min 26th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA275 | 0xA276 | 41589 | 41590 | LAST_CUR_HARM_MINc27 | Last Period 10min 27th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA277 | 0xA278 | 41591 | 41592 | LAST_CUR_HARM_MINc28 | Last Period 10min 28th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA279 | 0xA27A | 41593 | 41594 | LAST_CUR_HARM_MINc29 | Last Period 10min 29th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA27B | 0xA27C | 41595 | 41596 | LAST_CUR_HARM_MINc30 | Last Period 10min 30th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA27D | 0xA27E | 41597 | 41598 | LAST_CUR_HARM_MINc31 | Last Period 10min 31st Phase C Current Harmonics Minimum Value | float | 2 | R
0xA27F | 0xA280 | 41599 | 41600 | LAST_CUR_HARM_MINc32 | Last Period 10min 32nd Phase C Current Harmonics Minimum Value | float | 2 | R
0xA281 | 0xA282 | 41601 | 41602 | LAST_CUR_HARM_MINc33 | Last Period 10min 33rd Phase C Current Harmonics Minimum Value | float | 2 | R
0xA283 | 0xA284 | 41603 | 41604 | LAST_CUR_HARM_MINc34 | Last Period 10min 34th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA285 | 0xA286 | 41605 | 41606 | LAST_CUR_HARM_MINc35 | Last Period 10min 35th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA287 | 0xA288 | 41607 | 41608 | LAST_CUR_HARM_MINc36 | Last Period 10min 36th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA289 | 0xA28A | 41609 | 41610 | LAST_CUR_HARM_MINc37 | Last Period 10min 37th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA28B | 0xA28C | 41611 | 41612 | LAST_CUR_HARM_MINc38 | Last Period 10min 38th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA28D | 0xA28E | 41613 | 41614 | LAST_CUR_HARM_MINc39 | Last Period 10min 39th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA28F | 0xA290 | 41615 | 41616 | LAST_CUR_HARM_MINc40 | Last Period 10min 40th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA291 | 0xA292 | 41617 | 41618 | LAST_CUR_HARM_MINc41 | Last Period 10min 41st Phase C Current Harmonics Minimum Value | float | 2 | R
0xA293 | 0xA294 | 41619 | 41620 | LAST_CUR_HARM_MINc42 | Last Period 10min 42nd Phase C Current Harmonics Minimum Value | float | 2 | R
0xA295 | 0xA296 | 41621 | 41622 | LAST_CUR_HARM_MINc43 | Last Period 10min 43rd Phase C Current Harmonics Minimum Value | float | 2 | R
0xA297 | 0xA298 | 41623 | 41624 | LAST_CUR_HARM_MINc44 | Last Period 10min 44th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA299 | 0xA29A | 41625 | 41626 | LAST_CUR_HARM_MINc45 | Last Period 10min 45th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA29B | 0xA29C | 41627 | 41628 | LAST_CUR_HARM_MINc46 | Last Period 10min 46th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA29D | 0xA29E | 41629 | 41630 | LAST_CUR_HARM_MINc47 | Last Period 10min 47th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA29F | 0xA2A0 | 41631 | 41632 | LAST_CUR_HARM_MINc48 | Last Period 10min 48th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA2A1 | 0xA2A2 | 41633 | 41634 | LAST_CUR_HARM_MINc49 | Last Period 10min 49th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA2A3 | 0xA2A4 | 41635 | 41636 | LAST_CUR_HARM_MINc50 | Last Period 10min 50th Phase C Current Harmonics Minimum Value | float | 2 | R
0xA2A5 | 0xA2A6 | 41637 | 41638 | LAST_CUR_HARM_AVGa2 | Last Period 10min 2nd Phase A Current Harmonics Average Value | float | 2 | R
0xA2A7 | 0xA2A8 | 41639 | 41640 | LAST_CUR_HARM_AVGa3 | Last Period 10min 3rd Phase A Current Harmonics Average Value | float | 2 | R
0xA2A9 | 0xA2AA | 41641 | 41642 | LAST_CUR_HARM_AVGa4 | Last Period 10min 4th Phase A Current Harmonics Average Value | float | 2 | R
0xA2AB | 0xA2AC | 41643 | 41644 | LAST_CUR_HARM_AVGa5 | Last Period 10min 5th Phase A Current Harmonics Average Value | float | 2 | R
0xA2AD | 0xA2AE | 41645 | 41646 | LAST_CUR_HARM_AVGa6 | Last Period 10min 6th Phase A Current Harmonics Average Value | float | 2 | R
0xA2AF | 0xA2B0 | 41647 | 41648 | LAST_CUR_HARM_AVGa7 | Last Period 10min 7th Phase A Current Harmonics Average Value | float | 2 | R
0xA2B1 | 0xA2B2 | 41649 | 41650 | LAST_CUR_HARM_AVGa8 | Last Period 10min 8th Phase A Current Harmonics Average Value | float | 2 | R
0xA2B3 | 0xA2B4 | 41651 | 41652 | LAST_CUR_HARM_AVGa9 | Last Period 10min 9th Phase A Current Harmonics Average Value | float | 2 | R
0xA2B5 | 0xA2B6 | 41653 | 41654 | LAST_CUR_HARM_AVGa10 | Last Period 10min 10th Phase A Current Harmonics Average Value | float | 2 | R
0xA2B7 | 0xA2B8 | 41655 | 41656 | LAST_CUR_HARM_AVGa11 | Last Period 10min 11st Phase A Current Harmonics Average Value | float | 2 | R
0xA2B9 | 0xA2BA | 41657 | 41658 | LAST_CUR_HARM_AVGa12 | Last Period 10min 12nd Phase A Current Harmonics Average Value | float | 2 | R
0xA2BB | 0xA2BC | 41659 | 41660 | LAST_CUR_HARM_AVGa13 | Last Period 10min 13rd Phase A Current Harmonics Average Value | float | 2 | R
0xA2BD | 0xA2BE | 41661 | 41662 | LAST_CUR_HARM_AVGa14 | Last Period 10min 14th Phase A Current Harmonics Average Value | float | 2 | R
0xA2BF | 0xA2C0 | 41663 | 41664 | LAST_CUR_HARM_AVGa15 | Last Period 10min 15th Phase A Current Harmonics Average Value | float | 2 | R
0xA2C1 | 0xA2C2 | 41665 | 41666 | LAST_CUR_HARM_AVGa16 | Last Period 10min 16th Phase A Current Harmonics Average Value | float | 2 | R
0xA2C3 | 0xA2C4 | 41667 | 41668 | LAST_CUR_HARM_AVGa17 | Last Period 10min 17th Phase A Current Harmonics Average Value | float | 2 | R
0xA2C5 | 0xA2C6 | 41669 | 41670 | LAST_CUR_HARM_AVGa18 | Last Period 10min 18th Phase A Current Harmonics Average Value | float | 2 | R
0xA2C7 | 0xA2C8 | 41671 | 41672 | LAST_CUR_HARM_AVGa19 | Last Period 10min 19th Phase A Current Harmonics Average Value | float | 2 | R
0xA2C9 | 0xA2CA | 41673 | 41674 | LAST_CUR_HARM_AVGa20 | Last Period 10min 20th Phase A Current Harmonics Average Value | float | 2 | R
0xA2CB | 0xA2CC | 41675 | 41676 | LAST_CUR_HARM_AVGa21 | Last Period 10min 21st Phase A Current Harmonics Average Value | float | 2 | R
0xA2CD | 0xA2CE | 41677 | 41678 | LAST_CUR_HARM_AVGa22 | Last Period 10min 22nd Phase A Current Harmonics Average Value | float | 2 | R
0xA2CF | 0xA2D0 | 41679 | 41680 | LAST_CUR_HARM_AVGa23 | Last Period 10min 23rd Phase A Current Harmonics Average Value | float | 2 | R
0xA2D1 | 0xA2D2 | 41681 | 41682 | LAST_CUR_HARM_AVGa24 | Last Period 10min 24th Phase A Current Harmonics Average Value | float | 2 | R
0xA2D3 | 0xA2D4 | 41683 | 41684 | LAST_CUR_HARM_AVGa25 | Last Period 10min 25th Phase A Current Harmonics Average Value | float | 2 | R
0xA2D5 | 0xA2D6 | 41685 | 41686 | LAST_CUR_HARM_AVGa26 | Last Period 10min 26th Phase A Current Harmonics Average Value | float | 2 | R
0xA2D7 | 0xA2D8 | 41687 | 41688 | LAST_CUR_HARM_AVGa27 | Last Period 10min 27th Phase A Current Harmonics Average Value | float | 2 | R
0xA2D9 | 0xA2DA | 41689 | 41690 | LAST_CUR_HARM_AVGa28 | Last Period 10min 28th Phase A Current Harmonics Average Value | float | 2 | R
0xA2DB | 0xA2DC | 41691 | 41692 | LAST_CUR_HARM_AVGa29 | Last Period 10min 29th Phase A Current Harmonics Average Value | float | 2 | R
0xA2DD | 0xA2DE | 41693 | 41694 | LAST_CUR_HARM_AVGa30 | Last Period 10min 30th Phase A Current Harmonics Average Value | float | 2 | R
0xA2DF | 0xA2E0 | 41695 | 41696 | LAST_CUR_HARM_AVGa31 | Last Period 10min 31st Phase A Current Harmonics Average Value | float | 2 | R
0xA2E1 | 0xA2E2 | 41697 | 41698 | LAST_CUR_HARM_AVGa32 | Last Period 10min 32nd Phase A Current Harmonics Average Value | float | 2 | R
0xA2E3 | 0xA2E4 | 41699 | 41700 | LAST_CUR_HARM_AVGa33 | Last Period 10min 33rd Phase A Current Harmonics Average Value | float | 2 | R
0xA2E5 | 0xA2E6 | 41701 | 41702 | LAST_CUR_HARM_AVGa34 | Last Period 10min 34th Phase A Current Harmonics Average Value | float | 2 | R
0xA2E7 | 0xA2E8 | 41703 | 41704 | LAST_CUR_HARM_AVGa35 | Last Period 10min 35th Phase A Current Harmonics Average Value | float | 2 | R
0xA2E9 | 0xA2EA | 41705 | 41706 | LAST_CUR_HARM_AVGa36 | Last Period 10min 36th Phase A Current Harmonics Average Value | float | 2 | R
0xA2EB | 0xA2EC | 41707 | 41708 | LAST_CUR_HARM_AVGa37 | Last Period 10min 37th Phase A Current Harmonics Average Value | float | 2 | R
0xA2ED | 0xA2EE | 41709 | 41710 | LAST_CUR_HARM_AVGa38 | Last Period 10min 38th Phase A Current Harmonics Average Value | float | 2 | R
0xA2EF | 0xA2F0 | 41711 | 41712 | LAST_CUR_HARM_AVGa39 | Last Period 10min 39th Phase A Current Harmonics Average Value | float | 2 | R
0xA2F1 | 0xA2F2 | 41713 | 41714 | LAST_CUR_HARM_AVGa40 | Last Period 10min 40th Phase A Current Harmonics Average Value | float | 2 | R
0xA2F3 | 0xA2F4 | 41715 | 41716 | LAST_CUR_HARM_AVGa41 | Last Period 10min 41st Phase A Current Harmonics Average Value | float | 2 | R
0xA2F5 | 0xA2F6 | 41717 | 41718 | LAST_CUR_HARM_AVGa42 | Last Period 10min 42nd Phase A Current Harmonics Average Value | float | 2 | R
0xA2F7 | 0xA2F8 | 41719 | 41720 | LAST_CUR_HARM_AVGa43 | Last Period 10min 43rd Phase A Current Harmonics Average Value | float | 2 | R
0xA2F9 | 0xA2FA | 41721 | 41722 | LAST_CUR_HARM_AVGa44 | Last Period 10min 44th Phase A Current Harmonics Average Value | float | 2 | R
0xA2FB | 0xA2FC | 41723 | 41724 | LAST_CUR_HARM_AVGa45 | Last Period 10min 45th Phase A Current Harmonics Average Value | float | 2 | R
0xA2FD | 0xA2FE | 41725 | 41726 | LAST_CUR_HARM_AVGa46 | Last Period 10min 46th Phase A Current Harmonics Average Value | float | 2 | R
0xA2FF | 0xA300 | 41727 | 41728 | LAST_CUR_HARM_AVGa47 | Last Period 10min 47th Phase A Current Harmonics Average Value | float | 2 | R
0xA301 | 0xA302 | 41729 | 41730 | LAST_CUR_HARM_AVGa48 | Last Period 10min 48th Phase A Current Harmonics Average Value | float | 2 | R
0xA303 | 0xA304 | 41731 | 41732 | LAST_CUR_HARM_AVGa49 | Last Period 10min 49th Phase A Current Harmonics Average Value | float | 2 | R
0xA305 | 0xA306 | 41733 | 41734 | LAST_CUR_HARM_AVGa50 | Last Period 10min 50th Phase A Current Harmonics Average Value | float | 2 | R
0xA307 | 0xA308 | 41735 | 41736 | LAST_CUR_HARM_AVGb2 | Last Period 10min 2nd Phase B Current Harmonics Average Value | float | 2 | R
0xA309 | 0xA30A | 41737 | 41738 | LAST_CUR_HARM_AVGb3 | Last Period 10min 3rd Phase B Current Harmonics Average Value | float | 2 | R
0xA30B | 0xA30C | 41739 | 41740 | LAST_CUR_HARM_AVGb4 | Last Period 10min 4th Phase B Current Harmonics Average Value | float | 2 | R
0xA30D | 0xA30E | 41741 | 41742 | LAST_CUR_HARM_AVGb5 | Last Period 10min 5th Phase B Current Harmonics Average Value | float | 2 | R
0xA30F | 0xA310 | 41743 | 41744 | LAST_CUR_HARM_AVGb6 | Last Period 10min 6th Phase B Current Harmonics Average Value | float | 2 | R
0xA311 | 0xA312 | 41745 | 41746 | LAST_CUR_HARM_AVGb7 | Last Period 10min 7th Phase B Current Harmonics Average Value | float | 2 | R
0xA313 | 0xA314 | 41747 | 41748 | LAST_CUR_HARM_AVGb8 | Last Period 10min 8th Phase B Current Harmonics Average Value | float | 2 | R
0xA315 | 0xA316 | 41749 | 41750 | LAST_CUR_HARM_AVGb9 | Last Period 10min 9th Phase B Current Harmonics Average Value | float | 2 | R
0xA317 | 0xA318 | 41751 | 41752 | LAST_CUR_HARM_AVGb10 | Last Period 10min 10th Phase B Current Harmonics Average Value | float | 2 | R
0xA319 | 0xA31A | 41753 | 41754 | LAST_CUR_HARM_AVGb11 | Last Period 10min 11st Phase B Current Harmonics Average Value | float | 2 | R
0xA31B | 0xA31C | 41755 | 41756 | LAST_CUR_HARM_AVGb12 | Last Period 10min 12nd Phase B Current Harmonics Average Value | float | 2 | R
0xA31D | 0xA31E | 41757 | 41758 | LAST_CUR_HARM_AVGb13 | Last Period 10min 13rd Phase B Current Harmonics Average Value | float | 2 | R
0xA31F | 0xA320 | 41759 | 41760 | LAST_CUR_HARM_AVGb14 | Last Period 10min 14th Phase B Current Harmonics Average Value | float | 2 | R
0xA321 | 0xA322 | 41761 | 41762 | LAST_CUR_HARM_AVGb15 | Last Period 10min 15th Phase B Current Harmonics Average Value | float | 2 | R
0xA323 | 0xA324 | 41763 | 41764 | LAST_CUR_HARM_AVGb16 | Last Period 10min 16th Phase B Current Harmonics Average Value | float | 2 | R
0xA325 | 0xA326 | 41765 | 41766 | LAST_CUR_HARM_AVGb17 | Last Period 10min 17th Phase B Current Harmonics Average Value | float | 2 | R
0xA327 | 0xA328 | 41767 | 41768 | LAST_CUR_HARM_AVGb18 | Last Period 10min 18th Phase B Current Harmonics Average Value | float | 2 | R
0xA329 | 0xA32A | 41769 | 41770 | LAST_CUR_HARM_AVGb19 | Last Period 10min 19th Phase B Current Harmonics Average Value | float | 2 | R
0xA32B | 0xA32C | 41771 | 41772 | LAST_CUR_HARM_AVGb20 | Last Period 10min 20th Phase B Current Harmonics Average Value | float | 2 | R
0xA32D | 0xA32E | 41773 | 41774 | LAST_CUR_HARM_AVGb21 | Last Period 10min 21st Phase B Current Harmonics Average Value | float | 2 | R
0xA32F | 0xA330 | 41775 | 41776 | LAST_CUR_HARM_AVGb22 | Last Period 10min 22nd Phase B Current Harmonics Average Value | float | 2 | R
0xA331 | 0xA332 | 41777 | 41778 | LAST_CUR_HARM_AVGb23 | Last Period 10min 23rd Phase B Current Harmonics Average Value | float | 2 | R
0xA333 | 0xA334 | 41779 | 41780 | LAST_CUR_HARM_AVGb24 | Last Period 10min 24th Phase B Current Harmonics Average Value | float | 2 | R
0xA335 | 0xA336 | 41781 | 41782 | LAST_CUR_HARM_AVGb25 | Last Period 10min 25th Phase B Current Harmonics Average Value | float | 2 | R
0xA337 | 0xA338 | 41783 | 41784 | LAST_CUR_HARM_AVGb26 | Last Period 10min 26th Phase B Current Harmonics Average Value | float | 2 | R
0xA339 | 0xA33A | 41785 | 41786 | LAST_CUR_HARM_AVGb27 | Last Period 10min 27th Phase B Current Harmonics Average Value | float | 2 | R
0xA33B | 0xA33C | 41787 | 41788 | LAST_CUR_HARM_AVGb28 | Last Period 10min 28th Phase B Current Harmonics Average Value | float | 2 | R
0xA33D | 0xA33E | 41789 | 41790 | LAST_CUR_HARM_AVGb29 | Last Period 10min 29th Phase B Current Harmonics Average Value | float | 2 | R
0xA33F | 0xA340 | 41791 | 41792 | LAST_CUR_HARM_AVGb30 | Last Period 10min 30th Phase B Current Harmonics Average Value | float | 2 | R
0xA341 | 0xA342 | 41793 | 41794 | LAST_CUR_HARM_AVGb31 | Last Period 10min 31st Phase B Current Harmonics Average Value | float | 2 | R
0xA343 | 0xA344 | 41795 | 41796 | LAST_CUR_HARM_AVGb32 | Last Period 10min 32nd Phase B Current Harmonics Average Value | float | 2 | R
0xA345 | 0xA346 | 41797 | 41798 | LAST_CUR_HARM_AVGb33 | Last Period 10min 33rd Phase B Current Harmonics Average Value | float | 2 | R
0xA347 | 0xA348 | 41799 | 41800 | LAST_CUR_HARM_AVGb34 | Last Period 10min 34th Phase B Current Harmonics Average Value | float | 2 | R
0xA349 | 0xA34A | 41801 | 41802 | LAST_CUR_HARM_AVGb35 | Last Period 10min 35th Phase B Current Harmonics Average Value | float | 2 | R
0xA34B | 0xA34C | 41803 | 41804 | LAST_CUR_HARM_AVGb36 | Last Period 10min 36th Phase B Current Harmonics Average Value | float | 2 | R
0xA34D | 0xA34E | 41805 | 41806 | LAST_CUR_HARM_AVGb37 | Last Period 10min 37th Phase B Current Harmonics Average Value | float | 2 | R
0xA34F | 0xA350 | 41807 | 41808 | LAST_CUR_HARM_AVGb38 | Last Period 10min 38th Phase B Current Harmonics Average Value | float | 2 | R
0xA351 | 0xA352 | 41809 | 41810 | LAST_CUR_HARM_AVGb39 | Last Period 10min 39th Phase B Current Harmonics Average Value | float | 2 | R
0xA353 | 0xA354 | 41811 | 41812 | LAST_CUR_HARM_AVGb40 | Last Period 10min 40th Phase B Current Harmonics Average Value | float | 2 | R
0xA355 | 0xA356 | 41813 | 41814 | LAST_CUR_HARM_AVGb41 | Last Period 10min 41st Phase B Current Harmonics Average Value | float | 2 | R
0xA357 | 0xA358 | 41815 | 41816 | LAST_CUR_HARM_AVGb42 | Last Period 10min 42nd Phase B Current Harmonics Average Value | float | 2 | R
0xA359 | 0xA35A | 41817 | 41818 | LAST_CUR_HARM_AVGb43 | Last Period 10min 43rd Phase B Current Harmonics Average Value | float | 2 | R
0xA35B | 0xA35C | 41819 | 41820 | LAST_CUR_HARM_AVGb44 | Last Period 10min 44th Phase B Current Harmonics Average Value | float | 2 | R
0xA35D | 0xA35E | 41821 | 41822 | LAST_CUR_HARM_AVGb45 | Last Period 10min 45th Phase B Current Harmonics Average Value | float | 2 | R
0xA35F | 0xA360 | 41823 | 41824 | LAST_CUR_HARM_AVGb46 | Last Period 10min 46th Phase B Current Harmonics Average Value | float | 2 | R
0xA361 | 0xA362 | 41825 | 41826 | LAST_CUR_HARM_AVGb47 | Last Period 10min 47th Phase B Current Harmonics Average Value | float | 2 | R
0xA363 | 0xA364 | 41827 | 41828 | LAST_CUR_HARM_AVGb48 | Last Period 10min 48th Phase B Current Harmonics Average Value | float | 2 | R
0xA365 | 0xA366 | 41829 | 41830 | LAST_CUR_HARM_AVGb49 | Last Period 10min 49th Phase B Current Harmonics Average Value | float | 2 | R
0xA367 | 0xA368 | 41831 | 41832 | LAST_CUR_HARM_AVGb50 | Last Period 10min 50th Phase B Current Harmonics Average Value | float | 2 | R
0xA369 | 0xA36A | 41833 | 41834 | LAST_CUR_HARM_AVGc2 | Last Period 10min 2nd Phase C Current Harmonics Average Value | float | 2 | R
0xA36B | 0xA36C | 41835 | 41836 | LAST_CUR_HARM_AVGc3 | Last Period 10min 3rd Phase C Current Harmonics Average Value | float | 2 | R
0xA36D | 0xA36E | 41837 | 41838 | LAST_CUR_HARM_AVGc4 | Last Period 10min 4th Phase C Current Harmonics Average Value | float | 2 | R
0xA36F | 0xA370 | 41839 | 41840 | LAST_CUR_HARM_AVGc5 | Last Period 10min 5th Phase C Current Harmonics Average Value | float | 2 | R
0xA371 | 0xA372 | 41841 | 41842 | LAST_CUR_HARM_AVGc6 | Last Period 10min 6th Phase C Current Harmonics Average Value | float | 2 | R
0xA373 | 0xA374 | 41843 | 41844 | LAST_CUR_HARM_AVGc7 | Last Period 10min 7th Phase C Current Harmonics Average Value | float | 2 | R
0xA375 | 0xA376 | 41845 | 41846 | LAST_CUR_HARM_AVGc8 | Last Period 10min 8th Phase C Current Harmonics Average Value | float | 2 | R
0xA377 | 0xA378 | 41847 | 41848 | LAST_CUR_HARM_AVGc9 | Last Period 10min 9th Phase C Current Harmonics Average Value | float | 2 | R
0xA379 | 0xA37A | 41849 | 41850 | LAST_CUR_HARM_AVGc10 | Last Period 10min 10th Phase C Current Harmonics Average Value | float | 2 | R
0xA37B | 0xA37C | 41851 | 41852 | LAST_CUR_HARM_AVGc11 | Last Period 10min 11st Phase C Current Harmonics Average Value | float | 2 | R
0xA37D | 0xA37E | 41853 | 41854 | LAST_CUR_HARM_AVGc12 | Last Period 10min 12nd Phase C Current Harmonics Average Value | float | 2 | R
0xA37F | 0xA380 | 41855 | 41856 | LAST_CUR_HARM_AVGc13 | Last Period 10min 13rd Phase C Current Harmonics Average Value | float | 2 | R
0xA381 | 0xA382 | 41857 | 41858 | LAST_CUR_HARM_AVGc14 | Last Period 10min 14th Phase C Current Harmonics Average Value | float | 2 | R
0xA383 | 0xA384 | 41859 | 41860 | LAST_CUR_HARM_AVGc15 | Last Period 10min 15th Phase C Current Harmonics Average Value | float | 2 | R
0xA385 | 0xA386 | 41861 | 41862 | LAST_CUR_HARM_AVGc16 | Last Period 10min 16th Phase C Current Harmonics Average Value | float | 2 | R
0xA387 | 0xA388 | 41863 | 41864 | LAST_CUR_HARM_AVGc17 | Last Period 10min 17th Phase C Current Harmonics Average Value | float | 2 | R
0xA389 | 0xA38A | 41865 | 41866 | LAST_CUR_HARM_AVGc18 | Last Period 10min 18th Phase C Current Harmonics Average Value | float | 2 | R
0xA38B | 0xA38C | 41867 | 41868 | LAST_CUR_HARM_AVGc19 | Last Period 10min 19th Phase C Current Harmonics Average Value | float | 2 | R
0xA38D | 0xA38E | 41869 | 41870 | LAST_CUR_HARM_AVGc20 | Last Period 10min 20th Phase C Current Harmonics Average Value | float | 2 | R
0xA38F | 0xA390 | 41871 | 41872 | LAST_CUR_HARM_AVGc21 | Last Period 10min 21st Phase C Current Harmonics Average Value | float | 2 | R
0xA391 | 0xA392 | 41873 | 41874 | LAST_CUR_HARM_AVGc22 | Last Period 10min 22nd Phase C Current Harmonics Average Value | float | 2 | R
0xA393 | 0xA394 | 41875 | 41876 | LAST_CUR_HARM_AVGc23 | Last Period 10min 23rd Phase C Current Harmonics Average Value | float | 2 | R
0xA395 | 0xA396 | 41877 | 41878 | LAST_CUR_HARM_AVGc24 | Last Period 10min 24th Phase C Current Harmonics Average Value | float | 2 | R
0xA397 | 0xA398 | 41879 | 41880 | LAST_CUR_HARM_AVGc25 | Last Period 10min 25th Phase C Current Harmonics Average Value | float | 2 | R
0xA399 | 0xA39A | 41881 | 41882 | LAST_CUR_HARM_AVGc26 | Last Period 10min 26th Phase C Current Harmonics Average Value | float | 2 | R
0xA39B | 0xA39C | 41883 | 41884 | LAST_CUR_HARM_AVGc27 | Last Period 10min 27th Phase C Current Harmonics Average Value | float | 2 | R
0xA39D | 0xA39E | 41885 | 41886 | LAST_CUR_HARM_AVGc28 | Last Period 10min 28th Phase C Current Harmonics Average Value | float | 2 | R
0xA39F | 0xA3A0 | 41887 | 41888 | LAST_CUR_HARM_AVGc29 | Last Period 10min 29th Phase C Current Harmonics Average Value | float | 2 | R
0xA3A1 | 0xA3A2 | 41889 | 41890 | LAST_CUR_HARM_AVGc30 | Last Period 10min 30th Phase C Current Harmonics Average Value | float | 2 | R
0xA3A3 | 0xA3A4 | 41891 | 41892 | LAST_CUR_HARM_AVGc31 | Last Period 10min 31st Phase C Current Harmonics Average Value | float | 2 | R
0xA3A5 | 0xA3A6 | 41893 | 41894 | LAST_CUR_HARM_AVGc32 | Last Period 10min 32nd Phase C Current Harmonics Average Value | float | 2 | R
0xA3A7 | 0xA3A8 | 41895 | 41896 | LAST_CUR_HARM_AVGc33 | Last Period 10min 33rd Phase C Current Harmonics Average Value | float | 2 | R
0xA3A9 | 0xA3AA | 41897 | 41898 | LAST_CUR_HARM_AVGc34 | Last Period 10min 34th Phase C Current Harmonics Average Value | float | 2 | R
0xA3AB | 0xA3AC | 41899 | 41900 | LAST_CUR_HARM_AVGc35 | Last Period 10min 35th Phase C Current Harmonics Average Value | float | 2 | R
0xA3AD | 0xA3AE | 41901 | 41902 | LAST_CUR_HARM_AVGc36 | Last Period 10min 36th Phase C Current Harmonics Average Value | float | 2 | R
0xA3AF | 0xA3B0 | 41903 | 41904 | LAST_CUR_HARM_AVGc37 | Last Period 10min 37th Phase C Current Harmonics Average Value | float | 2 | R
0xA3B1 | 0xA3B2 | 41905 | 41906 | LAST_CUR_HARM_AVGc38 | Last Period 10min 38th Phase C Current Harmonics Average Value | float | 2 | R
0xA3B3 | 0xA3B4 | 41907 | 41908 | LAST_CUR_HARM_AVGc39 | Last Period 10min 39th Phase C Current Harmonics Average Value | float | 2 | R
0xA3B5 | 0xA3B6 | 41909 | 41910 | LAST_CUR_HARM_AVGc40 | Last Period 10min 40th Phase C Current Harmonics Average Value | float | 2 | R
0xA3B7 | 0xA3B8 | 41911 | 41912 | LAST_CUR_HARM_AVGc41 | Last Period 10min 41st Phase C Current Harmonics Average Value | float | 2 | R
0xA3B9 | 0xA3BA | 41913 | 41914 | LAST_CUR_HARM_AVGc42 | Last Period 10min 42nd Phase C Current Harmonics Average Value | float | 2 | R
0xA3BB | 0xA3BC | 41915 | 41916 | LAST_CUR_HARM_AVGc43 | Last Period 10min 43rd Phase C Current Harmonics Average Value | float | 2 | R
0xA3BD | 0xA3BE | 41917 | 41918 | LAST_CUR_HARM_AVGc44 | Last Period 10min 44th Phase C Current Harmonics Average Value | float | 2 | R
0xA3BF | 0xA3C0 | 41919 | 41920 | LAST_CUR_HARM_AVGc45 | Last Period 10min 45th Phase C Current Harmonics Average Value | float | 2 | R
0xA3C1 | 0xA3C2 | 41921 | 41922 | LAST_CUR_HARM_AVGc46 | Last Period 10min 46th Phase C Current Harmonics Average Value | float | 2 | R
0xA3C3 | 0xA3C4 | 41923 | 41924 | LAST_CUR_HARM_AVGc47 | Last Period 10min 47th Phase C Current Harmonics Average Value | float | 2 | R
0xA3C5 | 0xA3C6 | 41925 | 41926 | LAST_CUR_HARM_AVGc48 | Last Period 10min 48th Phase C Current Harmonics Average Value | float | 2 | R
0xA3C7 | 0xA3C8 | 41927 | 41928 | LAST_CUR_HARM_AVGc49 | Last Period 10min 49th Phase C Current Harmonics Average Value | float | 2 | R
0xA3C9 | 0xA3CA | 41929 | 41930 | LAST_CUR_HARM_AVGc50 | Last Period 10min 50th Phase C Current Harmonics Average Value | float | 2 | R
0xA3CB | 0xA3CB | 41931 | 41931 | LAST_N_TDD_95a | Last Period 10min Phase A TDD Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3CC | 0xA3CC | 41932 | 41932 | LAST_N_TDD_95b | Last Period 10min Phase B TDD Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3CD | 0xA3CD | 41933 | 41933 | LAST_N_TDD_95c | Last Period 10min Phase C TDD Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3CE | 0xA3CF | 41934 | 41935 | LAST_TDD_95_PASSa | Last Period 10min Phase A TDD Trigger Pass Rate for 95% Trigger Limit | float | 2 | R
0xA3D0 | 0xA3D1 | 41936 | 41937 | LAST_TDD_95_PASSb | Last Period 10min Phase B TDD Trigger Pass Rate for 95% Trigger Limit | float | 2 | R
0xA3D2 | 0xA3D3 | 41938 | 41939 | LAST_TDD_95_PASSc | Last Period 10min Phase C TDD Trigger Pass Rate for 95% Trigger Limit | float | 2 | R
0xA3D4 | 0xA3D4 | 41940 | 41940 | LAST_N_CUR_HARM_95a2 | Last Period 10min 2nd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3D5 | 0xA3D5 | 41941 | 41941 | LAST_N_CUR_HARM_95a3 | Last Period 10min 3rd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3D6 | 0xA3D6 | 41942 | 41942 | LAST_N_CUR_HARM_95a4 | Last Period 10min 4th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3D7 | 0xA3D7 | 41943 | 41943 | LAST_N_CUR_HARM_95a5 | Last Period 10min 5th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3D8 | 0xA3D8 | 41944 | 41944 | LAST_N_CUR_HARM_95a6 | Last Period 10min 6th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3D9 | 0xA3D9 | 41945 | 41945 | LAST_N_CUR_HARM_95a7 | Last Period 10min 7th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3DA | 0xA3DA | 41946 | 41946 | LAST_N_CUR_HARM_95a8 | Last Period 10min 8th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3DB | 0xA3DB | 41947 | 41947 | LAST_N_CUR_HARM_95a9 | Last Period 10min 9th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3DC | 0xA3DC | 41948 | 41948 | LAST_N_CUR_HARM_95a10 | Last Period 10min 10th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3DD | 0xA3DD | 41949 | 41949 | LAST_N_CUR_HARM_95a11 | Last Period 10min 11st Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3DE | 0xA3DE | 41950 | 41950 | LAST_N_CUR_HARM_95a12 | Last Period 10min 12nd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3DF | 0xA3DF | 41951 | 41951 | LAST_N_CUR_HARM_95a13 | Last Period 10min 13rd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3E0 | 0xA3E0 | 41952 | 41952 | LAST_N_CUR_HARM_95a14 | Last Period 10min 14th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3E1 | 0xA3E1 | 41953 | 41953 | LAST_N_CUR_HARM_95a15 | Last Period 10min 15th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3E2 | 0xA3E2 | 41954 | 41954 | LAST_N_CUR_HARM_95a16 | Last Period 10min 16th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3E3 | 0xA3E3 | 41955 | 41955 | LAST_N_CUR_HARM_95a17 | Last Period 10min 17th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3E4 | 0xA3E4 | 41956 | 41956 | LAST_N_CUR_HARM_95a18 | Last Period 10min 18th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3E5 | 0xA3E5 | 41957 | 41957 | LAST_N_CUR_HARM_95a19 | Last Period 10min 19th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3E6 | 0xA3E6 | 41958 | 41958 | LAST_N_CUR_HARM_95a20 | Last Period 10min 20th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3E7 | 0xA3E7 | 41959 | 41959 | LAST_N_CUR_HARM_95a21 | Last Period 10min 21st Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3E8 | 0xA3E8 | 41960 | 41960 | LAST_N_CUR_HARM_95a22 | Last Period 10min 22nd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3E9 | 0xA3E9 | 41961 | 41961 | LAST_N_CUR_HARM_95a23 | Last Period 10min 23rd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3EA | 0xA3EA | 41962 | 41962 | LAST_N_CUR_HARM_95a24 | Last Period 10min 24th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3EB | 0xA3EB | 41963 | 41963 | LAST_N_CUR_HARM_95a25 | Last Period 10min 25th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3EC | 0xA3EC | 41964 | 41964 | LAST_N_CUR_HARM_95a26 | Last Period 10min 26th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3ED | 0xA3ED | 41965 | 41965 | LAST_N_CUR_HARM_95a27 | Last Period 10min 27th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3EE | 0xA3EE | 41966 | 41966 | LAST_N_CUR_HARM_95a28 | Last Period 10min 28th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3EF | 0xA3EF | 41967 | 41967 | LAST_N_CUR_HARM_95a29 | Last Period 10min 29th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3F0 | 0xA3F0 | 41968 | 41968 | LAST_N_CUR_HARM_95a30 | Last Period 10min 30th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3F1 | 0xA3F1 | 41969 | 41969 | LAST_N_CUR_HARM_95a31 | Last Period 10min 31st Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3F2 | 0xA3F2 | 41970 | 41970 | LAST_N_CUR_HARM_95a32 | Last Period 10min 32nd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3F3 | 0xA3F3 | 41971 | 41971 | LAST_N_CUR_HARM_95a33 | Last Period 10min 33rd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3F4 | 0xA3F4 | 41972 | 41972 | LAST_N_CUR_HARM_95a34 | Last Period 10min 34th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3F5 | 0xA3F5 | 41973 | 41973 | LAST_N_CUR_HARM_95a35 | Last Period 10min 35th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3F6 | 0xA3F6 | 41974 | 41974 | LAST_N_CUR_HARM_95a36 | Last Period 10min 36th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3F7 | 0xA3F7 | 41975 | 41975 | LAST_N_CUR_HARM_95a37 | Last Period 10min 37th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3F8 | 0xA3F8 | 41976 | 41976 | LAST_N_CUR_HARM_95a38 | Last Period 10min 38th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3F9 | 0xA3F9 | 41977 | 41977 | LAST_N_CUR_HARM_95a39 | Last Period 10min 39th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3FA | 0xA3FA | 41978 | 41978 | LAST_N_CUR_HARM_95a40 | Last Period 10min 40th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3FB | 0xA3FB | 41979 | 41979 | LAST_N_CUR_HARM_95a41 | Last Period 10min 41st Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3FC | 0xA3FC | 41980 | 41980 | LAST_N_CUR_HARM_95a42 | Last Period 10min 42nd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3FD | 0xA3FD | 41981 | 41981 | LAST_N_CUR_HARM_95a43 | Last Period 10min 43rd Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3FE | 0xA3FE | 41982 | 41982 | LAST_N_CUR_HARM_95a44 | Last Period 10min 44th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA3FF | 0xA3FF | 41983 | 41983 | LAST_N_CUR_HARM_95a45 | Last Period 10min 45th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA400 | 0xA400 | 41984 | 41984 | LAST_N_CUR_HARM_95a46 | Last Period 10min 46th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA401 | 0xA401 | 41985 | 41985 | LAST_N_CUR_HARM_95a47 | Last Period 10min 47th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA402 | 0xA402 | 41986 | 41986 | LAST_N_CUR_HARM_95a48 | Last Period 10min 48th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA403 | 0xA403 | 41987 | 41987 | LAST_N_CUR_HARM_95a49 | Last Period 10min 49th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA404 | 0xA404 | 41988 | 41988 | LAST_N_CUR_HARM_95a50 | Last Period 10min 50th Phase A Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA405 | 0xA405 | 41989 | 41989 | LAST_N_CUR_HARM_95b2 | Last Period 10min 2nd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA406 | 0xA406 | 41990 | 41990 | LAST_N_CUR_HARM_95b3 | Last Period 10min 3rd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA407 | 0xA407 | 41991 | 41991 | LAST_N_CUR_HARM_95b4 | Last Period 10min 4th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA408 | 0xA408 | 41992 | 41992 | LAST_N_CUR_HARM_95b5 | Last Period 10min 5th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA409 | 0xA409 | 41993 | 41993 | LAST_N_CUR_HARM_95b6 | Last Period 10min 6th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA40A | 0xA40A | 41994 | 41994 | LAST_N_CUR_HARM_95b7 | Last Period 10min 7th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA40B | 0xA40B | 41995 | 41995 | LAST_N_CUR_HARM_95b8 | Last Period 10min 8th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA40C | 0xA40C | 41996 | 41996 | LAST_N_CUR_HARM_95b9 | Last Period 10min 9th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA40D | 0xA40D | 41997 | 41997 | LAST_N_CUR_HARM_95b10 | Last Period 10min 10th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA40E | 0xA40E | 41998 | 41998 | LAST_N_CUR_HARM_95b11 | Last Period 10min 11st Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA40F | 0xA40F | 41999 | 41999 | LAST_N_CUR_HARM_95b12 | Last Period 10min 12nd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA410 | 0xA410 | 42000 | 42000 | LAST_N_CUR_HARM_95b13 | Last Period 10min 13rd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA411 | 0xA411 | 42001 | 42001 | LAST_N_CUR_HARM_95b14 | Last Period 10min 14th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA412 | 0xA412 | 42002 | 42002 | LAST_N_CUR_HARM_95b15 | Last Period 10min 15th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA413 | 0xA413 | 42003 | 42003 | LAST_N_CUR_HARM_95b16 | Last Period 10min 16th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA414 | 0xA414 | 42004 | 42004 | LAST_N_CUR_HARM_95b17 | Last Period 10min 17th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA415 | 0xA415 | 42005 | 42005 | LAST_N_CUR_HARM_95b18 | Last Period 10min 18th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA416 | 0xA416 | 42006 | 42006 | LAST_N_CUR_HARM_95b19 | Last Period 10min 19th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA417 | 0xA417 | 42007 | 42007 | LAST_N_CUR_HARM_95b20 | Last Period 10min 20th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA418 | 0xA418 | 42008 | 42008 | LAST_N_CUR_HARM_95b21 | Last Period 10min 21st Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA419 | 0xA419 | 42009 | 42009 | LAST_N_CUR_HARM_95b22 | Last Period 10min 22nd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA41A | 0xA41A | 42010 | 42010 | LAST_N_CUR_HARM_95b23 | Last Period 10min 23rd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA41B | 0xA41B | 42011 | 42011 | LAST_N_CUR_HARM_95b24 | Last Period 10min 24th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA41C | 0xA41C | 42012 | 42012 | LAST_N_CUR_HARM_95b25 | Last Period 10min 25th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA41D | 0xA41D | 42013 | 42013 | LAST_N_CUR_HARM_95b26 | Last Period 10min 26th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA41E | 0xA41E | 42014 | 42014 | LAST_N_CUR_HARM_95b27 | Last Period 10min 27th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA41F | 0xA41F | 42015 | 42015 | LAST_N_CUR_HARM_95b28 | Last Period 10min 28th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA420 | 0xA420 | 42016 | 42016 | LAST_N_CUR_HARM_95b29 | Last Period 10min 29th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA421 | 0xA421 | 42017 | 42017 | LAST_N_CUR_HARM_95b30 | Last Period 10min 30th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA422 | 0xA422 | 42018 | 42018 | LAST_N_CUR_HARM_95b31 | Last Period 10min 31st Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA423 | 0xA423 | 42019 | 42019 | LAST_N_CUR_HARM_95b32 | Last Period 10min 32nd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA424 | 0xA424 | 42020 | 42020 | LAST_N_CUR_HARM_95b33 | Last Period 10min 33rd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA425 | 0xA425 | 42021 | 42021 | LAST_N_CUR_HARM_95b34 | Last Period 10min 34th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA426 | 0xA426 | 42022 | 42022 | LAST_N_CUR_HARM_95b35 | Last Period 10min 35th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA427 | 0xA427 | 42023 | 42023 | LAST_N_CUR_HARM_95b36 | Last Period 10min 36th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA428 | 0xA428 | 42024 | 42024 | LAST_N_CUR_HARM_95b37 | Last Period 10min 37th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA429 | 0xA429 | 42025 | 42025 | LAST_N_CUR_HARM_95b38 | Last Period 10min 38th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA42A | 0xA42A | 42026 | 42026 | LAST_N_CUR_HARM_95b39 | Last Period 10min 39th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA42B | 0xA42B | 42027 | 42027 | LAST_N_CUR_HARM_95b40 | Last Period 10min 40th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA42C | 0xA42C | 42028 | 42028 | LAST_N_CUR_HARM_95b41 | Last Period 10min 41st Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA42D | 0xA42D | 42029 | 42029 | LAST_N_CUR_HARM_95b42 | Last Period 10min 42nd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA42E | 0xA42E | 42030 | 42030 | LAST_N_CUR_HARM_95b43 | Last Period 10min 43rd Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA42F | 0xA42F | 42031 | 42031 | LAST_N_CUR_HARM_95b44 | Last Period 10min 44th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA430 | 0xA430 | 42032 | 42032 | LAST_N_CUR_HARM_95b45 | Last Period 10min 45th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA431 | 0xA431 | 42033 | 42033 | LAST_N_CUR_HARM_95b46 | Last Period 10min 46th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA432 | 0xA432 | 42034 | 42034 | LAST_N_CUR_HARM_95b47 | Last Period 10min 47th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA433 | 0xA433 | 42035 | 42035 | LAST_N_CUR_HARM_95b48 | Last Period 10min 48th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA434 | 0xA434 | 42036 | 42036 | LAST_N_CUR_HARM_95b49 | Last Period 10min 49th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA435 | 0xA435 | 42037 | 42037 | LAST_N_CUR_HARM_95b50 | Last Period 10min 50th Phase B Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA436 | 0xA436 | 42038 | 42038 | LAST_N_CUR_HARM_95c2 | Last Period 10min 2nd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA437 | 0xA437 | 42039 | 42039 | LAST_N_CUR_HARM_95c3 | Last Period 10min 3rd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA438 | 0xA438 | 42040 | 42040 | LAST_N_CUR_HARM_95c4 | Last Period 10min 4th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA439 | 0xA439 | 42041 | 42041 | LAST_N_CUR_HARM_95c5 | Last Period 10min 5th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA43A | 0xA43A | 42042 | 42042 | LAST_N_CUR_HARM_95c6 | Last Period 10min 6th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA43B | 0xA43B | 42043 | 42043 | LAST_N_CUR_HARM_95c7 | Last Period 10min 7th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA43C | 0xA43C | 42044 | 42044 | LAST_N_CUR_HARM_95c8 | Last Period 10min 8th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA43D | 0xA43D | 42045 | 42045 | LAST_N_CUR_HARM_95c9 | Last Period 10min 9th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA43E | 0xA43E | 42046 | 42046 | LAST_N_CUR_HARM_95c10 | Last Period 10min 10th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA43F | 0xA43F | 42047 | 42047 | LAST_N_CUR_HARM_95c11 | Last Period 10min 11st Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA440 | 0xA440 | 42048 | 42048 | LAST_N_CUR_HARM_95c12 | Last Period 10min 12nd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA441 | 0xA441 | 42049 | 42049 | LAST_N_CUR_HARM_95c13 | Last Period 10min 13rd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA442 | 0xA442 | 42050 | 42050 | LAST_N_CUR_HARM_95c14 | Last Period 10min 14th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA443 | 0xA443 | 42051 | 42051 | LAST_N_CUR_HARM_95c15 | Last Period 10min 15th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA444 | 0xA444 | 42052 | 42052 | LAST_N_CUR_HARM_95c16 | Last Period 10min 16th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA445 | 0xA445 | 42053 | 42053 | LAST_N_CUR_HARM_95c17 | Last Period 10min 17th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA446 | 0xA446 | 42054 | 42054 | LAST_N_CUR_HARM_95c18 | Last Period 10min 18th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA447 | 0xA447 | 42055 | 42055 | LAST_N_CUR_HARM_95c19 | Last Period 10min 19th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA448 | 0xA448 | 42056 | 42056 | LAST_N_CUR_HARM_95c20 | Last Period 10min 20th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA449 | 0xA449 | 42057 | 42057 | LAST_N_CUR_HARM_95c21 | Last Period 10min 21st Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA44A | 0xA44A | 42058 | 42058 | LAST_N_CUR_HARM_95c22 | Last Period 10min 22nd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA44B | 0xA44B | 42059 | 42059 | LAST_N_CUR_HARM_95c23 | Last Period 10min 23rd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA44C | 0xA44C | 42060 | 42060 | LAST_N_CUR_HARM_95c24 | Last Period 10min 24th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA44D | 0xA44D | 42061 | 42061 | LAST_N_CUR_HARM_95c25 | Last Period 10min 25th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA44E | 0xA44E | 42062 | 42062 | LAST_N_CUR_HARM_95c26 | Last Period 10min 26th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA44F | 0xA44F | 42063 | 42063 | LAST_N_CUR_HARM_95c27 | Last Period 10min 27th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA450 | 0xA450 | 42064 | 42064 | LAST_N_CUR_HARM_95c28 | Last Period 10min 28th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA451 | 0xA451 | 42065 | 42065 | LAST_N_CUR_HARM_95c29 | Last Period 10min 29th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA452 | 0xA452 | 42066 | 42066 | LAST_N_CUR_HARM_95c30 | Last Period 10min 30th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA453 | 0xA453 | 42067 | 42067 | LAST_N_CUR_HARM_95c31 | Last Period 10min 31st Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA454 | 0xA454 | 42068 | 42068 | LAST_N_CUR_HARM_95c32 | Last Period 10min 32nd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA455 | 0xA455 | 42069 | 42069 | LAST_N_CUR_HARM_95c33 | Last Period 10min 33rd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA456 | 0xA456 | 42070 | 42070 | LAST_N_CUR_HARM_95c34 | Last Period 10min 34th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA457 | 0xA457 | 42071 | 42071 | LAST_N_CUR_HARM_95c35 | Last Period 10min 35th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA458 | 0xA458 | 42072 | 42072 | LAST_N_CUR_HARM_95c36 | Last Period 10min 36th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA459 | 0xA459 | 42073 | 42073 | LAST_N_CUR_HARM_95c37 | Last Period 10min 37th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA45A | 0xA45A | 42074 | 42074 | LAST_N_CUR_HARM_95c38 | Last Period 10min 38th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA45B | 0xA45B | 42075 | 42075 | LAST_N_CUR_HARM_95c39 | Last Period 10min 39th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA45C | 0xA45C | 42076 | 42076 | LAST_N_CUR_HARM_95c40 | Last Period 10min 40th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA45D | 0xA45D | 42077 | 42077 | LAST_N_CUR_HARM_95c41 | Last Period 10min 41st Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA45E | 0xA45E | 42078 | 42078 | LAST_N_CUR_HARM_95c42 | Last Period 10min 42nd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA45F | 0xA45F | 42079 | 42079 | LAST_N_CUR_HARM_95c43 | Last Period 10min 43rd Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA460 | 0xA460 | 42080 | 42080 | LAST_N_CUR_HARM_95c44 | Last Period 10min 44th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA461 | 0xA461 | 42081 | 42081 | LAST_N_CUR_HARM_95c45 | Last Period 10min 45th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA462 | 0xA462 | 42082 | 42082 | LAST_N_CUR_HARM_95c46 | Last Period 10min 46th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA463 | 0xA463 | 42083 | 42083 | LAST_N_CUR_HARM_95c47 | Last Period 10min 47th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA464 | 0xA464 | 42084 | 42084 | LAST_N_CUR_HARM_95c48 | Last Period 10min 48th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA465 | 0xA465 | 42085 | 42085 | LAST_N_CUR_HARM_95c49 | Last Period 10min 49th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA466 | 0xA466 | 42086 | 42086 | LAST_N_CUR_HARM_95c50 | Last Period 10min 50th Phase C Current Harmonics Counter for 95% Trigger Limit | uint16 | 1 | R
0xA467 | 0xA468 | 42087 | 42088 | LAST_CUR_HARM_95_PASSa2 | Last Period 10min 2nd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA469 | 0xA46A | 42089 | 42090 | LAST_CUR_HARM_95_PASSa3 | Last Period 10min 3rd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA46B | 0xA46C | 42091 | 42092 | LAST_CUR_HARM_95_PASSa4 | Last Period 10min 4th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA46D | 0xA46E | 42093 | 42094 | LAST_CUR_HARM_95_PASSa5 | Last Period 10min 5th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA46F | 0xA470 | 42095 | 42096 | LAST_CUR_HARM_95_PASSa6 | Last Period 10min 6th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA471 | 0xA472 | 42097 | 42098 | LAST_CUR_HARM_95_PASSa7 | Last Period 10min 7th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA473 | 0xA474 | 42099 | 42100 | LAST_CUR_HARM_95_PASSa8 | Last Period 10min 8th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA475 | 0xA476 | 42101 | 42102 | LAST_CUR_HARM_95_PASSa9 | Last Period 10min 9th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA477 | 0xA478 | 42103 | 42104 | LAST_CUR_HARM_95_PASSa10 | Last Period 10min 10th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA479 | 0xA47A | 42105 | 42106 | LAST_CUR_HARM_95_PASSa11 | Last Period 10min 11st Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA47B | 0xA47C | 42107 | 42108 | LAST_CUR_HARM_95_PASSa12 | Last Period 10min 12nd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA47D | 0xA47E | 42109 | 42110 | LAST_CUR_HARM_95_PASSa13 | Last Period 10min 13rd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA47F | 0xA480 | 42111 | 42112 | LAST_CUR_HARM_95_PASSa14 | Last Period 10min 14th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA481 | 0xA482 | 42113 | 42114 | LAST_CUR_HARM_95_PASSa15 | Last Period 10min 15th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA483 | 0xA484 | 42115 | 42116 | LAST_CUR_HARM_95_PASSa16 | Last Period 10min 16th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA485 | 0xA486 | 42117 | 42118 | LAST_CUR_HARM_95_PASSa17 | Last Period 10min 17th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA487 | 0xA488 | 42119 | 42120 | LAST_CUR_HARM_95_PASSa18 | Last Period 10min 18th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA489 | 0xA48A | 42121 | 42122 | LAST_CUR_HARM_95_PASSa19 | Last Period 10min 19th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA48B | 0xA48C | 42123 | 42124 | LAST_CUR_HARM_95_PASSa20 | Last Period 10min 20th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA48D | 0xA48E | 42125 | 42126 | LAST_CUR_HARM_95_PASSa21 | Last Period 10min 21st Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA48F | 0xA490 | 42127 | 42128 | LAST_CUR_HARM_95_PASSa22 | Last Period 10min 22nd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA491 | 0xA492 | 42129 | 42130 | LAST_CUR_HARM_95_PASSa23 | Last Period 10min 23rd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA493 | 0xA494 | 42131 | 42132 | LAST_CUR_HARM_95_PASSa24 | Last Period 10min 24th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA495 | 0xA496 | 42133 | 42134 | LAST_CUR_HARM_95_PASSa25 | Last Period 10min 25th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA497 | 0xA498 | 42135 | 42136 | LAST_CUR_HARM_95_PASSa26 | Last Period 10min 26th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA499 | 0xA49A | 42137 | 42138 | LAST_CUR_HARM_95_PASSa27 | Last Period 10min 27th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA49B | 0xA49C | 42139 | 42140 | LAST_CUR_HARM_95_PASSa28 | Last Period 10min 28th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA49D | 0xA49E | 42141 | 42142 | LAST_CUR_HARM_95_PASSa29 | Last Period 10min 29th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA49F | 0xA4A0 | 42143 | 42144 | LAST_CUR_HARM_95_PASSa30 | Last Period 10min 30th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4A1 | 0xA4A2 | 42145 | 42146 | LAST_CUR_HARM_95_PASSa31 | Last Period 10min 31st Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4A3 | 0xA4A4 | 42147 | 42148 | LAST_CUR_HARM_95_PASSa32 | Last Period 10min 32nd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4A5 | 0xA4A6 | 42149 | 42150 | LAST_CUR_HARM_95_PASSa33 | Last Period 10min 33rd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4A7 | 0xA4A8 | 42151 | 42152 | LAST_CUR_HARM_95_PASSa34 | Last Period 10min 34th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4A9 | 0xA4AA | 42153 | 42154 | LAST_CUR_HARM_95_PASSa35 | Last Period 10min 35th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4AB | 0xA4AC | 42155 | 42156 | LAST_CUR_HARM_95_PASSa36 | Last Period 10min 36th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4AD | 0xA4AE | 42157 | 42158 | LAST_CUR_HARM_95_PASSa37 | Last Period 10min 37th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4AF | 0xA4B0 | 42159 | 42160 | LAST_CUR_HARM_95_PASSa38 | Last Period 10min 38th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4B1 | 0xA4B2 | 42161 | 42162 | LAST_CUR_HARM_95_PASSa39 | Last Period 10min 39th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4B3 | 0xA4B4 | 42163 | 42164 | LAST_CUR_HARM_95_PASSa40 | Last Period 10min 40th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4B5 | 0xA4B6 | 42165 | 42166 | LAST_CUR_HARM_95_PASSa41 | Last Period 10min 41st Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4B7 | 0xA4B8 | 42167 | 42168 | LAST_CUR_HARM_95_PASSa42 | Last Period 10min 42nd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4B9 | 0xA4BA | 42169 | 42170 | LAST_CUR_HARM_95_PASSa43 | Last Period 10min 43rd Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4BB | 0xA4BC | 42171 | 42172 | LAST_CUR_HARM_95_PASSa44 | Last Period 10min 44th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4BD | 0xA4BE | 42173 | 42174 | LAST_CUR_HARM_95_PASSa45 | Last Period 10min 45th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4BF | 0xA4C0 | 42175 | 42176 | LAST_CUR_HARM_95_PASSa46 | Last Period 10min 46th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4C1 | 0xA4C2 | 42177 | 42178 | LAST_CUR_HARM_95_PASSa47 | Last Period 10min 47th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4C3 | 0xA4C4 | 42179 | 42180 | LAST_CUR_HARM_95_PASSa48 | Last Period 10min 48th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4C5 | 0xA4C6 | 42181 | 42182 | LAST_CUR_HARM_95_PASSa49 | Last Period 10min 49th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4C7 | 0xA4C8 | 42183 | 42184 | LAST_CUR_HARM_95_PASSa50 | Last Period 10min 50th Phase A Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4C9 | 0xA4CA | 42185 | 42186 | LAST_CUR_HARM_95_PASSb2 | Last Period 10min 2nd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4CB | 0xA4CC | 42187 | 42188 | LAST_CUR_HARM_95_PASSb3 | Last Period 10min 3rd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4CD | 0xA4CE | 42189 | 42190 | LAST_CUR_HARM_95_PASSb4 | Last Period 10min 4th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4CF | 0xA4D0 | 42191 | 42192 | LAST_CUR_HARM_95_PASSb5 | Last Period 10min 5th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4D1 | 0xA4D2 | 42193 | 42194 | LAST_CUR_HARM_95_PASSb6 | Last Period 10min 6th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4D3 | 0xA4D4 | 42195 | 42196 | LAST_CUR_HARM_95_PASSb7 | Last Period 10min 7th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4D5 | 0xA4D6 | 42197 | 42198 | LAST_CUR_HARM_95_PASSb8 | Last Period 10min 8th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4D7 | 0xA4D8 | 42199 | 42200 | LAST_CUR_HARM_95_PASSb9 | Last Period 10min 9th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4D9 | 0xA4DA | 42201 | 42202 | LAST_CUR_HARM_95_PASSb10 | Last Period 10min 10th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4DB | 0xA4DC | 42203 | 42204 | LAST_CUR_HARM_95_PASSb11 | Last Period 10min 11st Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4DD | 0xA4DE | 42205 | 42206 | LAST_CUR_HARM_95_PASSb12 | Last Period 10min 12nd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4DF | 0xA4E0 | 42207 | 42208 | LAST_CUR_HARM_95_PASSb13 | Last Period 10min 13rd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4E1 | 0xA4E2 | 42209 | 42210 | LAST_CUR_HARM_95_PASSb14 | Last Period 10min 14th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4E3 | 0xA4E4 | 42211 | 42212 | LAST_CUR_HARM_95_PASSb15 | Last Period 10min 15th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4E5 | 0xA4E6 | 42213 | 42214 | LAST_CUR_HARM_95_PASSb16 | Last Period 10min 16th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4E7 | 0xA4E8 | 42215 | 42216 | LAST_CUR_HARM_95_PASSb17 | Last Period 10min 17th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4E9 | 0xA4EA | 42217 | 42218 | LAST_CUR_HARM_95_PASSb18 | Last Period 10min 18th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4EB | 0xA4EC | 42219 | 42220 | LAST_CUR_HARM_95_PASSb19 | Last Period 10min 19th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4ED | 0xA4EE | 42221 | 42222 | LAST_CUR_HARM_95_PASSb20 | Last Period 10min 20th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4EF | 0xA4F0 | 42223 | 42224 | LAST_CUR_HARM_95_PASSb21 | Last Period 10min 21st Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4F1 | 0xA4F2 | 42225 | 42226 | LAST_CUR_HARM_95_PASSb22 | Last Period 10min 22nd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4F3 | 0xA4F4 | 42227 | 42228 | LAST_CUR_HARM_95_PASSb23 | Last Period 10min 23rd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4F5 | 0xA4F6 | 42229 | 42230 | LAST_CUR_HARM_95_PASSb24 | Last Period 10min 24th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4F7 | 0xA4F8 | 42231 | 42232 | LAST_CUR_HARM_95_PASSb25 | Last Period 10min 25th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4F9 | 0xA4FA | 42233 | 42234 | LAST_CUR_HARM_95_PASSb26 | Last Period 10min 26th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4FB | 0xA4FC | 42235 | 42236 | LAST_CUR_HARM_95_PASSb27 | Last Period 10min 27th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4FD | 0xA4FE | 42237 | 42238 | LAST_CUR_HARM_95_PASSb28 | Last Period 10min 28th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA4FF | 0xA500 | 42239 | 42240 | LAST_CUR_HARM_95_PASSb29 | Last Period 10min 29th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA501 | 0xA502 | 42241 | 42242 | LAST_CUR_HARM_95_PASSb30 | Last Period 10min 30th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA503 | 0xA504 | 42243 | 42244 | LAST_CUR_HARM_95_PASSb31 | Last Period 10min 31st Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA505 | 0xA506 | 42245 | 42246 | LAST_CUR_HARM_95_PASSb32 | Last Period 10min 32nd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA507 | 0xA508 | 42247 | 42248 | LAST_CUR_HARM_95_PASSb33 | Last Period 10min 33rd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA509 | 0xA50A | 42249 | 42250 | LAST_CUR_HARM_95_PASSb34 | Last Period 10min 34th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA50B | 0xA50C | 42251 | 42252 | LAST_CUR_HARM_95_PASSb35 | Last Period 10min 35th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA50D | 0xA50E | 42253 | 42254 | LAST_CUR_HARM_95_PASSb36 | Last Period 10min 36th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA50F | 0xA510 | 42255 | 42256 | LAST_CUR_HARM_95_PASSb37 | Last Period 10min 37th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA511 | 0xA512 | 42257 | 42258 | LAST_CUR_HARM_95_PASSb38 | Last Period 10min 38th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA513 | 0xA514 | 42259 | 42260 | LAST_CUR_HARM_95_PASSb39 | Last Period 10min 39th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA515 | 0xA516 | 42261 | 42262 | LAST_CUR_HARM_95_PASSb40 | Last Period 10min 40th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA517 | 0xA518 | 42263 | 42264 | LAST_CUR_HARM_95_PASSb41 | Last Period 10min 41st Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA519 | 0xA51A | 42265 | 42266 | LAST_CUR_HARM_95_PASSb42 | Last Period 10min 42nd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA51B | 0xA51C | 42267 | 42268 | LAST_CUR_HARM_95_PASSb43 | Last Period 10min 43rd Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA51D | 0xA51E | 42269 | 42270 | LAST_CUR_HARM_95_PASSb44 | Last Period 10min 44th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA51F | 0xA520 | 42271 | 42272 | LAST_CUR_HARM_95_PASSb45 | Last Period 10min 45th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA521 | 0xA522 | 42273 | 42274 | LAST_CUR_HARM_95_PASSb46 | Last Period 10min 46th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA523 | 0xA524 | 42275 | 42276 | LAST_CUR_HARM_95_PASSb47 | Last Period 10min 47th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA525 | 0xA526 | 42277 | 42278 | LAST_CUR_HARM_95_PASSb48 | Last Period 10min 48th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA527 | 0xA528 | 42279 | 42280 | LAST_CUR_HARM_95_PASSb49 | Last Period 10min 49th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA529 | 0xA52A | 42281 | 42282 | LAST_CUR_HARM_95_PASSb50 | Last Period 10min 50th Phase B Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA52B | 0xA52C | 42283 | 42284 | LAST_CUR_HARM_95_PASSc2 | Last Period 10min 2nd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA52D | 0xA52E | 42285 | 42286 | LAST_CUR_HARM_95_PASSc3 | Last Period 10min 3rd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA52F | 0xA530 | 42287 | 42288 | LAST_CUR_HARM_95_PASSc4 | Last Period 10min 4th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA531 | 0xA532 | 42289 | 42290 | LAST_CUR_HARM_95_PASSc5 | Last Period 10min 5th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA533 | 0xA534 | 42291 | 42292 | LAST_CUR_HARM_95_PASSc6 | Last Period 10min 6th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA535 | 0xA536 | 42293 | 42294 | LAST_CUR_HARM_95_PASSc7 | Last Period 10min 7th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA537 | 0xA538 | 42295 | 42296 | LAST_CUR_HARM_95_PASSc8 | Last Period 10min 8th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA539 | 0xA53A | 42297 | 42298 | LAST_CUR_HARM_95_PASSc9 | Last Period 10min 9th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA53B | 0xA53C | 42299 | 42300 | LAST_CUR_HARM_95_PASSc10 | Last Period 10min 10th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA53D | 0xA53E | 42301 | 42302 | LAST_CUR_HARM_95_PASSc11 | Last Period 10min 11st Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA53F | 0xA540 | 42303 | 42304 | LAST_CUR_HARM_95_PASSc12 | Last Period 10min 12nd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA541 | 0xA542 | 42305 | 42306 | LAST_CUR_HARM_95_PASSc13 | Last Period 10min 13rd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA543 | 0xA544 | 42307 | 42308 | LAST_CUR_HARM_95_PASSc14 | Last Period 10min 14th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA545 | 0xA546 | 42309 | 42310 | LAST_CUR_HARM_95_PASSc15 | Last Period 10min 15th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA547 | 0xA548 | 42311 | 42312 | LAST_CUR_HARM_95_PASSc16 | Last Period 10min 16th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA549 | 0xA54A | 42313 | 42314 | LAST_CUR_HARM_95_PASSc17 | Last Period 10min 17th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA54B | 0xA54C | 42315 | 42316 | LAST_CUR_HARM_95_PASSc18 | Last Period 10min 18th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA54D | 0xA54E | 42317 | 42318 | LAST_CUR_HARM_95_PASSc19 | Last Period 10min 19th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA54F | 0xA550 | 42319 | 42320 | LAST_CUR_HARM_95_PASSc20 | Last Period 10min 20th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA551 | 0xA552 | 42321 | 42322 | LAST_CUR_HARM_95_PASSc21 | Last Period 10min 21st Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA553 | 0xA554 | 42323 | 42324 | LAST_CUR_HARM_95_PASSc22 | Last Period 10min 22nd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA555 | 0xA556 | 42325 | 42326 | LAST_CUR_HARM_95_PASSc23 | Last Period 10min 23rd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA557 | 0xA558 | 42327 | 42328 | LAST_CUR_HARM_95_PASSc24 | Last Period 10min 24th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA559 | 0xA55A | 42329 | 42330 | LAST_CUR_HARM_95_PASSc25 | Last Period 10min 25th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA55B | 0xA55C | 42331 | 42332 | LAST_CUR_HARM_95_PASSc26 | Last Period 10min 26th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA55D | 0xA55E | 42333 | 42334 | LAST_CUR_HARM_95_PASSc27 | Last Period 10min 27th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA55F | 0xA560 | 42335 | 42336 | LAST_CUR_HARM_95_PASSc28 | Last Period 10min 28th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA561 | 0xA562 | 42337 | 42338 | LAST_CUR_HARM_95_PASSc29 | Last Period 10min 29th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA563 | 0xA564 | 42339 | 42340 | LAST_CUR_HARM_95_PASSc30 | Last Period 10min 30th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA565 | 0xA566 | 42341 | 42342 | LAST_CUR_HARM_95_PASSc31 | Last Period 10min 31st Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA567 | 0xA568 | 42343 | 42344 | LAST_CUR_HARM_95_PASSc32 | Last Period 10min 32nd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA569 | 0xA56A | 42345 | 42346 | LAST_CUR_HARM_95_PASSc33 | Last Period 10min 33rd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA56B | 0xA56C | 42347 | 42348 | LAST_CUR_HARM_95_PASSc34 | Last Period 10min 34th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA56D | 0xA56E | 42349 | 42350 | LAST_CUR_HARM_95_PASSc35 | Last Period 10min 35th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA56F | 0xA570 | 42351 | 42352 | LAST_CUR_HARM_95_PASSc36 | Last Period 10min 36th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA571 | 0xA572 | 42353 | 42354 | LAST_CUR_HARM_95_PASSc37 | Last Period 10min 37th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA573 | 0xA574 | 42355 | 42356 | LAST_CUR_HARM_95_PASSc38 | Last Period 10min 38th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA575 | 0xA576 | 42357 | 42358 | LAST_CUR_HARM_95_PASSc39 | Last Period 10min 39th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA577 | 0xA578 | 42359 | 42360 | LAST_CUR_HARM_95_PASSc40 | Last Period 10min 40th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA579 | 0xA57A | 42361 | 42362 | LAST_CUR_HARM_95_PASSc41 | Last Period 10min 41st Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA57B | 0xA57C | 42363 | 42364 | LAST_CUR_HARM_95_PASSc42 | Last Period 10min 42nd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA57D | 0xA57E | 42365 | 42366 | LAST_CUR_HARM_95_PASSc43 | Last Period 10min 43rd Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA57F | 0xA580 | 42367 | 42368 | LAST_CUR_HARM_95_PASSc44 | Last Period 10min 44th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA581 | 0xA582 | 42369 | 42370 | LAST_CUR_HARM_95_PASSc45 | Last Period 10min 45th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA583 | 0xA584 | 42371 | 42372 | LAST_CUR_HARM_95_PASSc46 | Last Period 10min 46th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA585 | 0xA586 | 42373 | 42374 | LAST_CUR_HARM_95_PASSc47 | Last Period 10min 47th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA587 | 0xA588 | 42375 | 42376 | LAST_CUR_HARM_95_PASSc48 | Last Period 10min 48th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA589 | 0xA58A | 42377 | 42378 | LAST_CUR_HARM_95_PASSc49 | Last Period 10min 49th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA58B | 0xA58C | 42379 | 42380 | LAST_CUR_HARM_95_PASSc50 | Last Period 10min 50th Phase C Current Harmonics Pass Rate for 95% Trigger Limit | float | 2 | R
0xA58D | 0xA58D | 42381 | 42381 | LAST_N_TDD_99a | Last Period 10min Phase A TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0xA58E | 0xA58E | 42382 | 42382 | LAST_N_TDD_99b | Last Period 10min Phase B TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0xA58F | 0xA58F | 42383 | 42383 | LAST_N_TDD_99c | Last Period 10min Phase C TDD Counter for 99% Trigger Limit | uint16 | 1 | R
0xA590 | 0xA591 | 42384 | 42385 | LAST_TDD_99_PASSa | Last Period 10min Phase A TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0xA592 | 0xA593 | 42386 | 42387 | LAST_TDD_99_PASSb | Last Period 10min Phase B TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0xA594 | 0xA595 | 42388 | 42389 | LAST_TDD_99_PASSc | Last Period 10min Phase C TDD Trigger Pass Rate for 99% Trigger Limit | float | 2 | R
0xA596 | 0xA596 | 42390 | 42390 | LAST_N_CUR_HARM_99a2 | Last Period 10min 2nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA597 | 0xA597 | 42391 | 42391 | LAST_N_CUR_HARM_99a3 | Last Period 10min 3rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA598 | 0xA598 | 42392 | 42392 | LAST_N_CUR_HARM_99a4 | Last Period 10min 4th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA599 | 0xA599 | 42393 | 42393 | LAST_N_CUR_HARM_99a5 | Last Period 10min 5th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA59A | 0xA59A | 42394 | 42394 | LAST_N_CUR_HARM_99a6 | Last Period 10min 6th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA59B | 0xA59B | 42395 | 42395 | LAST_N_CUR_HARM_99a7 | Last Period 10min 7th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA59C | 0xA59C | 42396 | 42396 | LAST_N_CUR_HARM_99a8 | Last Period 10min 8th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA59D | 0xA59D | 42397 | 42397 | LAST_N_CUR_HARM_99a9 | Last Period 10min 9th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA59E | 0xA59E | 42398 | 42398 | LAST_N_CUR_HARM_99a10 | Last Period 10min 10th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA59F | 0xA59F | 42399 | 42399 | LAST_N_CUR_HARM_99a11 | Last Period 10min 11st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5A0 | 0xA5A0 | 42400 | 42400 | LAST_N_CUR_HARM_99a12 | Last Period 10min 12nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5A1 | 0xA5A1 | 42401 | 42401 | LAST_N_CUR_HARM_99a13 | Last Period 10min 13rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5A2 | 0xA5A2 | 42402 | 42402 | LAST_N_CUR_HARM_99a14 | Last Period 10min 14th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5A3 | 0xA5A3 | 42403 | 42403 | LAST_N_CUR_HARM_99a15 | Last Period 10min 15th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5A4 | 0xA5A4 | 42404 | 42404 | LAST_N_CUR_HARM_99a16 | Last Period 10min 16th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5A5 | 0xA5A5 | 42405 | 42405 | LAST_N_CUR_HARM_99a17 | Last Period 10min 17th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5A6 | 0xA5A6 | 42406 | 42406 | LAST_N_CUR_HARM_99a18 | Last Period 10min 18th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5A7 | 0xA5A7 | 42407 | 42407 | LAST_N_CUR_HARM_99a19 | Last Period 10min 19th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5A8 | 0xA5A8 | 42408 | 42408 | LAST_N_CUR_HARM_99a20 | Last Period 10min 20th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5A9 | 0xA5A9 | 42409 | 42409 | LAST_N_CUR_HARM_99a21 | Last Period 10min 21st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5AA | 0xA5AA | 42410 | 42410 | LAST_N_CUR_HARM_99a22 | Last Period 10min 22nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5AB | 0xA5AB | 42411 | 42411 | LAST_N_CUR_HARM_99a23 | Last Period 10min 23rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5AC | 0xA5AC | 42412 | 42412 | LAST_N_CUR_HARM_99a24 | Last Period 10min 24th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5AD | 0xA5AD | 42413 | 42413 | LAST_N_CUR_HARM_99a25 | Last Period 10min 25th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5AE | 0xA5AE | 42414 | 42414 | LAST_N_CUR_HARM_99a26 | Last Period 10min 26th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5AF | 0xA5AF | 42415 | 42415 | LAST_N_CUR_HARM_99a27 | Last Period 10min 27th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5B0 | 0xA5B0 | 42416 | 42416 | LAST_N_CUR_HARM_99a28 | Last Period 10min 28th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5B1 | 0xA5B1 | 42417 | 42417 | LAST_N_CUR_HARM_99a29 | Last Period 10min 29th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5B2 | 0xA5B2 | 42418 | 42418 | LAST_N_CUR_HARM_99a30 | Last Period 10min 30th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5B3 | 0xA5B3 | 42419 | 42419 | LAST_N_CUR_HARM_99a31 | Last Period 10min 31st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5B4 | 0xA5B4 | 42420 | 42420 | LAST_N_CUR_HARM_99a32 | Last Period 10min 32nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5B5 | 0xA5B5 | 42421 | 42421 | LAST_N_CUR_HARM_99a33 | Last Period 10min 33rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5B6 | 0xA5B6 | 42422 | 42422 | LAST_N_CUR_HARM_99a34 | Last Period 10min 34th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5B7 | 0xA5B7 | 42423 | 42423 | LAST_N_CUR_HARM_99a35 | Last Period 10min 35th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5B8 | 0xA5B8 | 42424 | 42424 | LAST_N_CUR_HARM_99a36 | Last Period 10min 36th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5B9 | 0xA5B9 | 42425 | 42425 | LAST_N_CUR_HARM_99a37 | Last Period 10min 37th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5BA | 0xA5BA | 42426 | 42426 | LAST_N_CUR_HARM_99a38 | Last Period 10min 38th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5BB | 0xA5BB | 42427 | 42427 | LAST_N_CUR_HARM_99a39 | Last Period 10min 39th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5BC | 0xA5BC | 42428 | 42428 | LAST_N_CUR_HARM_99a40 | Last Period 10min 40th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5BD | 0xA5BD | 42429 | 42429 | LAST_N_CUR_HARM_99a41 | Last Period 10min 41st Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5BE | 0xA5BE | 42430 | 42430 | LAST_N_CUR_HARM_99a42 | Last Period 10min 42nd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5BF | 0xA5BF | 42431 | 42431 | LAST_N_CUR_HARM_99a43 | Last Period 10min 43rd Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5C0 | 0xA5C0 | 42432 | 42432 | LAST_N_CUR_HARM_99a44 | Last Period 10min 44th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5C1 | 0xA5C1 | 42433 | 42433 | LAST_N_CUR_HARM_99a45 | Last Period 10min 45th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5C2 | 0xA5C2 | 42434 | 42434 | LAST_N_CUR_HARM_99a46 | Last Period 10min 46th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5C3 | 0xA5C3 | 42435 | 42435 | LAST_N_CUR_HARM_99a47 | Last Period 10min 47th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5C4 | 0xA5C4 | 42436 | 42436 | LAST_N_CUR_HARM_99a48 | Last Period 10min 48th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5C5 | 0xA5C5 | 42437 | 42437 | LAST_N_CUR_HARM_99a49 | Last Period 10min 49th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5C6 | 0xA5C6 | 42438 | 42438 | LAST_N_CUR_HARM_99a50 | Last Period 10min 50th Phase A Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5C7 | 0xA5C7 | 42439 | 42439 | LAST_N_CUR_HARM_99b2 | Last Period 10min 2nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5C8 | 0xA5C8 | 42440 | 42440 | LAST_N_CUR_HARM_99b3 | Last Period 10min 3rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5C9 | 0xA5C9 | 42441 | 42441 | LAST_N_CUR_HARM_99b4 | Last Period 10min 4th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5CA | 0xA5CA | 42442 | 42442 | LAST_N_CUR_HARM_99b5 | Last Period 10min 5th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5CB | 0xA5CB | 42443 | 42443 | LAST_N_CUR_HARM_99b6 | Last Period 10min 6th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5CC | 0xA5CC | 42444 | 42444 | LAST_N_CUR_HARM_99b7 | Last Period 10min 7th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5CD | 0xA5CD | 42445 | 42445 | LAST_N_CUR_HARM_99b8 | Last Period 10min 8th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5CE | 0xA5CE | 42446 | 42446 | LAST_N_CUR_HARM_99b9 | Last Period 10min 9th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5CF | 0xA5CF | 42447 | 42447 | LAST_N_CUR_HARM_99b10 | Last Period 10min 10th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5D0 | 0xA5D0 | 42448 | 42448 | LAST_N_CUR_HARM_99b11 | Last Period 10min 11st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5D1 | 0xA5D1 | 42449 | 42449 | LAST_N_CUR_HARM_99b12 | Last Period 10min 12nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5D2 | 0xA5D2 | 42450 | 42450 | LAST_N_CUR_HARM_99b13 | Last Period 10min 13rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5D3 | 0xA5D3 | 42451 | 42451 | LAST_N_CUR_HARM_99b14 | Last Period 10min 14th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5D4 | 0xA5D4 | 42452 | 42452 | LAST_N_CUR_HARM_99b15 | Last Period 10min 15th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5D5 | 0xA5D5 | 42453 | 42453 | LAST_N_CUR_HARM_99b16 | Last Period 10min 16th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5D6 | 0xA5D6 | 42454 | 42454 | LAST_N_CUR_HARM_99b17 | Last Period 10min 17th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5D7 | 0xA5D7 | 42455 | 42455 | LAST_N_CUR_HARM_99b18 | Last Period 10min 18th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5D8 | 0xA5D8 | 42456 | 42456 | LAST_N_CUR_HARM_99b19 | Last Period 10min 19th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5D9 | 0xA5D9 | 42457 | 42457 | LAST_N_CUR_HARM_99b20 | Last Period 10min 20th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5DA | 0xA5DA | 42458 | 42458 | LAST_N_CUR_HARM_99b21 | Last Period 10min 21st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5DB | 0xA5DB | 42459 | 42459 | LAST_N_CUR_HARM_99b22 | Last Period 10min 22nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5DC | 0xA5DC | 42460 | 42460 | LAST_N_CUR_HARM_99b23 | Last Period 10min 23rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5DD | 0xA5DD | 42461 | 42461 | LAST_N_CUR_HARM_99b24 | Last Period 10min 24th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5DE | 0xA5DE | 42462 | 42462 | LAST_N_CUR_HARM_99b25 | Last Period 10min 25th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5DF | 0xA5DF | 42463 | 42463 | LAST_N_CUR_HARM_99b26 | Last Period 10min 26th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5E0 | 0xA5E0 | 42464 | 42464 | LAST_N_CUR_HARM_99b27 | Last Period 10min 27th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5E1 | 0xA5E1 | 42465 | 42465 | LAST_N_CUR_HARM_99b28 | Last Period 10min 28th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5E2 | 0xA5E2 | 42466 | 42466 | LAST_N_CUR_HARM_99b29 | Last Period 10min 29th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5E3 | 0xA5E3 | 42467 | 42467 | LAST_N_CUR_HARM_99b30 | Last Period 10min 30th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5E4 | 0xA5E4 | 42468 | 42468 | LAST_N_CUR_HARM_99b31 | Last Period 10min 31st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5E5 | 0xA5E5 | 42469 | 42469 | LAST_N_CUR_HARM_99b32 | Last Period 10min 32nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5E6 | 0xA5E6 | 42470 | 42470 | LAST_N_CUR_HARM_99b33 | Last Period 10min 33rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5E7 | 0xA5E7 | 42471 | 42471 | LAST_N_CUR_HARM_99b34 | Last Period 10min 34th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5E8 | 0xA5E8 | 42472 | 42472 | LAST_N_CUR_HARM_99b35 | Last Period 10min 35th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5E9 | 0xA5E9 | 42473 | 42473 | LAST_N_CUR_HARM_99b36 | Last Period 10min 36th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5EA | 0xA5EA | 42474 | 42474 | LAST_N_CUR_HARM_99b37 | Last Period 10min 37th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5EB | 0xA5EB | 42475 | 42475 | LAST_N_CUR_HARM_99b38 | Last Period 10min 38th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5EC | 0xA5EC | 42476 | 42476 | LAST_N_CUR_HARM_99b39 | Last Period 10min 39th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5ED | 0xA5ED | 42477 | 42477 | LAST_N_CUR_HARM_99b40 | Last Period 10min 40th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5EE | 0xA5EE | 42478 | 42478 | LAST_N_CUR_HARM_99b41 | Last Period 10min 41st Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5EF | 0xA5EF | 42479 | 42479 | LAST_N_CUR_HARM_99b42 | Last Period 10min 42nd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5F0 | 0xA5F0 | 42480 | 42480 | LAST_N_CUR_HARM_99b43 | Last Period 10min 43rd Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5F1 | 0xA5F1 | 42481 | 42481 | LAST_N_CUR_HARM_99b44 | Last Period 10min 44th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5F2 | 0xA5F2 | 42482 | 42482 | LAST_N_CUR_HARM_99b45 | Last Period 10min 45th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5F3 | 0xA5F3 | 42483 | 42483 | LAST_N_CUR_HARM_99b46 | Last Period 10min 46th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5F4 | 0xA5F4 | 42484 | 42484 | LAST_N_CUR_HARM_99b47 | Last Period 10min 47th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5F5 | 0xA5F5 | 42485 | 42485 | LAST_N_CUR_HARM_99b48 | Last Period 10min 48th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5F6 | 0xA5F6 | 42486 | 42486 | LAST_N_CUR_HARM_99b49 | Last Period 10min 49th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5F7 | 0xA5F7 | 42487 | 42487 | LAST_N_CUR_HARM_99b50 | Last Period 10min 50th Phase B Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5F8 | 0xA5F8 | 42488 | 42488 | LAST_N_CUR_HARM_99c2 | Last Period 10min 2nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5F9 | 0xA5F9 | 42489 | 42489 | LAST_N_CUR_HARM_99c3 | Last Period 10min 3rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5FA | 0xA5FA | 42490 | 42490 | LAST_N_CUR_HARM_99c4 | Last Period 10min 4th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5FB | 0xA5FB | 42491 | 42491 | LAST_N_CUR_HARM_99c5 | Last Period 10min 5th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5FC | 0xA5FC | 42492 | 42492 | LAST_N_CUR_HARM_99c6 | Last Period 10min 6th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5FD | 0xA5FD | 42493 | 42493 | LAST_N_CUR_HARM_99c7 | Last Period 10min 7th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5FE | 0xA5FE | 42494 | 42494 | LAST_N_CUR_HARM_99c8 | Last Period 10min 8th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA5FF | 0xA5FF | 42495 | 42495 | LAST_N_CUR_HARM_99c9 | Last Period 10min 9th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA600 | 0xA600 | 42496 | 42496 | LAST_N_CUR_HARM_99c10 | Last Period 10min 10th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA601 | 0xA601 | 42497 | 42497 | LAST_N_CUR_HARM_99c11 | Last Period 10min 11st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA602 | 0xA602 | 42498 | 42498 | LAST_N_CUR_HARM_99c12 | Last Period 10min 12nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA603 | 0xA603 | 42499 | 42499 | LAST_N_CUR_HARM_99c13 | Last Period 10min 13rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA604 | 0xA604 | 42500 | 42500 | LAST_N_CUR_HARM_99c14 | Last Period 10min 14th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA605 | 0xA605 | 42501 | 42501 | LAST_N_CUR_HARM_99c15 | Last Period 10min 15th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA606 | 0xA606 | 42502 | 42502 | LAST_N_CUR_HARM_99c16 | Last Period 10min 16th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA607 | 0xA607 | 42503 | 42503 | LAST_N_CUR_HARM_99c17 | Last Period 10min 17th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA608 | 0xA608 | 42504 | 42504 | LAST_N_CUR_HARM_99c18 | Last Period 10min 18th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA609 | 0xA609 | 42505 | 42505 | LAST_N_CUR_HARM_99c19 | Last Period 10min 19th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA60A | 0xA60A | 42506 | 42506 | LAST_N_CUR_HARM_99c20 | Last Period 10min 20th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA60B | 0xA60B | 42507 | 42507 | LAST_N_CUR_HARM_99c21 | Last Period 10min 21st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA60C | 0xA60C | 42508 | 42508 | LAST_N_CUR_HARM_99c22 | Last Period 10min 22nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA60D | 0xA60D | 42509 | 42509 | LAST_N_CUR_HARM_99c23 | Last Period 10min 23rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA60E | 0xA60E | 42510 | 42510 | LAST_N_CUR_HARM_99c24 | Last Period 10min 24th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA60F | 0xA60F | 42511 | 42511 | LAST_N_CUR_HARM_99c25 | Last Period 10min 25th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA610 | 0xA610 | 42512 | 42512 | LAST_N_CUR_HARM_99c26 | Last Period 10min 26th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA611 | 0xA611 | 42513 | 42513 | LAST_N_CUR_HARM_99c27 | Last Period 10min 27th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA612 | 0xA612 | 42514 | 42514 | LAST_N_CUR_HARM_99c28 | Last Period 10min 28th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA613 | 0xA613 | 42515 | 42515 | LAST_N_CUR_HARM_99c29 | Last Period 10min 29th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA614 | 0xA614 | 42516 | 42516 | LAST_N_CUR_HARM_99c30 | Last Period 10min 30th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA615 | 0xA615 | 42517 | 42517 | LAST_N_CUR_HARM_99c31 | Last Period 10min 31st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA616 | 0xA616 | 42518 | 42518 | LAST_N_CUR_HARM_99c32 | Last Period 10min 32nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA617 | 0xA617 | 42519 | 42519 | LAST_N_CUR_HARM_99c33 | Last Period 10min 33rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA618 | 0xA618 | 42520 | 42520 | LAST_N_CUR_HARM_99c34 | Last Period 10min 34th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA619 | 0xA619 | 42521 | 42521 | LAST_N_CUR_HARM_99c35 | Last Period 10min 35th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA61A | 0xA61A | 42522 | 42522 | LAST_N_CUR_HARM_99c36 | Last Period 10min 36th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA61B | 0xA61B | 42523 | 42523 | LAST_N_CUR_HARM_99c37 | Last Period 10min 37th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA61C | 0xA61C | 42524 | 42524 | LAST_N_CUR_HARM_99c38 | Last Period 10min 38th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA61D | 0xA61D | 42525 | 42525 | LAST_N_CUR_HARM_99c39 | Last Period 10min 39th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA61E | 0xA61E | 42526 | 42526 | LAST_N_CUR_HARM_99c40 | Last Period 10min 40th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA61F | 0xA61F | 42527 | 42527 | LAST_N_CUR_HARM_99c41 | Last Period 10min 41st Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA620 | 0xA620 | 42528 | 42528 | LAST_N_CUR_HARM_99c42 | Last Period 10min 42nd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA621 | 0xA621 | 42529 | 42529 | LAST_N_CUR_HARM_99c43 | Last Period 10min 43rd Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA622 | 0xA622 | 42530 | 42530 | LAST_N_CUR_HARM_99c44 | Last Period 10min 44th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA623 | 0xA623 | 42531 | 42531 | LAST_N_CUR_HARM_99c45 | Last Period 10min 45th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA624 | 0xA624 | 42532 | 42532 | LAST_N_CUR_HARM_99c46 | Last Period 10min 46th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA625 | 0xA625 | 42533 | 42533 | LAST_N_CUR_HARM_99c47 | Last Period 10min 47th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA626 | 0xA626 | 42534 | 42534 | LAST_N_CUR_HARM_99c48 | Last Period 10min 48th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA627 | 0xA627 | 42535 | 42535 | LAST_N_CUR_HARM_99c49 | Last Period 10min 49th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA628 | 0xA628 | 42536 | 42536 | LAST_N_CUR_HARM_99c50 | Last Period 10min 50th Phase C Current Harmonics Counter for 99% Trigger Limit | uint16 | 1 | R
0xA629 | 0xA62A | 42537 | 42538 | LAST_CUR_HARM_99_PASSa2 | Last Period 10min 2nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA62B | 0xA62C | 42539 | 42540 | LAST_CUR_HARM_99_PASSa3 | Last Period 10min 3rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA62D | 0xA62E | 42541 | 42542 | LAST_CUR_HARM_99_PASSa4 | Last Period 10min 4th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA62F | 0xA630 | 42543 | 42544 | LAST_CUR_HARM_99_PASSa5 | Last Period 10min 5th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA631 | 0xA632 | 42545 | 42546 | LAST_CUR_HARM_99_PASSa6 | Last Period 10min 6th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA633 | 0xA634 | 42547 | 42548 | LAST_CUR_HARM_99_PASSa7 | Last Period 10min 7th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA635 | 0xA636 | 42549 | 42550 | LAST_CUR_HARM_99_PASSa8 | Last Period 10min 8th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA637 | 0xA638 | 42551 | 42552 | LAST_CUR_HARM_99_PASSa9 | Last Period 10min 9th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA639 | 0xA63A | 42553 | 42554 | LAST_CUR_HARM_99_PASSa10 | Last Period 10min 10th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA63B | 0xA63C | 42555 | 42556 | LAST_CUR_HARM_99_PASSa11 | Last Period 10min 11st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA63D | 0xA63E | 42557 | 42558 | LAST_CUR_HARM_99_PASSa12 | Last Period 10min 12nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA63F | 0xA640 | 42559 | 42560 | LAST_CUR_HARM_99_PASSa13 | Last Period 10min 13rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA641 | 0xA642 | 42561 | 42562 | LAST_CUR_HARM_99_PASSa14 | Last Period 10min 14th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA643 | 0xA644 | 42563 | 42564 | LAST_CUR_HARM_99_PASSa15 | Last Period 10min 15th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA645 | 0xA646 | 42565 | 42566 | LAST_CUR_HARM_99_PASSa16 | Last Period 10min 16th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA647 | 0xA648 | 42567 | 42568 | LAST_CUR_HARM_99_PASSa17 | Last Period 10min 17th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA649 | 0xA64A | 42569 | 42570 | LAST_CUR_HARM_99_PASSa18 | Last Period 10min 18th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA64B | 0xA64C | 42571 | 42572 | LAST_CUR_HARM_99_PASSa19 | Last Period 10min 19th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA64D | 0xA64E | 42573 | 42574 | LAST_CUR_HARM_99_PASSa20 | Last Period 10min 20th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA64F | 0xA650 | 42575 | 42576 | LAST_CUR_HARM_99_PASSa21 | Last Period 10min 21st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA651 | 0xA652 | 42577 | 42578 | LAST_CUR_HARM_99_PASSa22 | Last Period 10min 22nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA653 | 0xA654 | 42579 | 42580 | LAST_CUR_HARM_99_PASSa23 | Last Period 10min 23rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA655 | 0xA656 | 42581 | 42582 | LAST_CUR_HARM_99_PASSa24 | Last Period 10min 24th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA657 | 0xA658 | 42583 | 42584 | LAST_CUR_HARM_99_PASSa25 | Last Period 10min 25th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA659 | 0xA65A | 42585 | 42586 | LAST_CUR_HARM_99_PASSa26 | Last Period 10min 26th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA65B | 0xA65C | 42587 | 42588 | LAST_CUR_HARM_99_PASSa27 | Last Period 10min 27th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA65D | 0xA65E | 42589 | 42590 | LAST_CUR_HARM_99_PASSa28 | Last Period 10min 28th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA65F | 0xA660 | 42591 | 42592 | LAST_CUR_HARM_99_PASSa29 | Last Period 10min 29th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA661 | 0xA662 | 42593 | 42594 | LAST_CUR_HARM_99_PASSa30 | Last Period 10min 30th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA663 | 0xA664 | 42595 | 42596 | LAST_CUR_HARM_99_PASSa31 | Last Period 10min 31st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA665 | 0xA666 | 42597 | 42598 | LAST_CUR_HARM_99_PASSa32 | Last Period 10min 32nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA667 | 0xA668 | 42599 | 42600 | LAST_CUR_HARM_99_PASSa33 | Last Period 10min 33rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA669 | 0xA66A | 42601 | 42602 | LAST_CUR_HARM_99_PASSa34 | Last Period 10min 34th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA66B | 0xA66C | 42603 | 42604 | LAST_CUR_HARM_99_PASSa35 | Last Period 10min 35th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA66D | 0xA66E | 42605 | 42606 | LAST_CUR_HARM_99_PASSa36 | Last Period 10min 36th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA66F | 0xA670 | 42607 | 42608 | LAST_CUR_HARM_99_PASSa37 | Last Period 10min 37th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA671 | 0xA672 | 42609 | 42610 | LAST_CUR_HARM_99_PASSa38 | Last Period 10min 38th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA673 | 0xA674 | 42611 | 42612 | LAST_CUR_HARM_99_PASSa39 | Last Period 10min 39th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA675 | 0xA676 | 42613 | 42614 | LAST_CUR_HARM_99_PASSa40 | Last Period 10min 40th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA677 | 0xA678 | 42615 | 42616 | LAST_CUR_HARM_99_PASSa41 | Last Period 10min 41st Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA679 | 0xA67A | 42617 | 42618 | LAST_CUR_HARM_99_PASSa42 | Last Period 10min 42nd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA67B | 0xA67C | 42619 | 42620 | LAST_CUR_HARM_99_PASSa43 | Last Period 10min 43rd Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA67D | 0xA67E | 42621 | 42622 | LAST_CUR_HARM_99_PASSa44 | Last Period 10min 44th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA67F | 0xA680 | 42623 | 42624 | LAST_CUR_HARM_99_PASSa45 | Last Period 10min 45th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA681 | 0xA682 | 42625 | 42626 | LAST_CUR_HARM_99_PASSa46 | Last Period 10min 46th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA683 | 0xA684 | 42627 | 42628 | LAST_CUR_HARM_99_PASSa47 | Last Period 10min 47th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA685 | 0xA686 | 42629 | 42630 | LAST_CUR_HARM_99_PASSa48 | Last Period 10min 48th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA687 | 0xA688 | 42631 | 42632 | LAST_CUR_HARM_99_PASSa49 | Last Period 10min 49th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA689 | 0xA68A | 42633 | 42634 | LAST_CUR_HARM_99_PASSa50 | Last Period 10min 50th Phase A Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA68B | 0xA68C | 42635 | 42636 | LAST_CUR_HARM_99_PASSb2 | Last Period 10min 2nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA68D | 0xA68E | 42637 | 42638 | LAST_CUR_HARM_99_PASSb3 | Last Period 10min 3rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA68F | 0xA690 | 42639 | 42640 | LAST_CUR_HARM_99_PASSb4 | Last Period 10min 4th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA691 | 0xA692 | 42641 | 42642 | LAST_CUR_HARM_99_PASSb5 | Last Period 10min 5th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA693 | 0xA694 | 42643 | 42644 | LAST_CUR_HARM_99_PASSb6 | Last Period 10min 6th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA695 | 0xA696 | 42645 | 42646 | LAST_CUR_HARM_99_PASSb7 | Last Period 10min 7th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA697 | 0xA698 | 42647 | 42648 | LAST_CUR_HARM_99_PASSb8 | Last Period 10min 8th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA699 | 0xA69A | 42649 | 42650 | LAST_CUR_HARM_99_PASSb9 | Last Period 10min 9th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA69B | 0xA69C | 42651 | 42652 | LAST_CUR_HARM_99_PASSb10 | Last Period 10min 10th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA69D | 0xA69E | 42653 | 42654 | LAST_CUR_HARM_99_PASSb11 | Last Period 10min 11st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA69F | 0xA6A0 | 42655 | 42656 | LAST_CUR_HARM_99_PASSb12 | Last Period 10min 12nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6A1 | 0xA6A2 | 42657 | 42658 | LAST_CUR_HARM_99_PASSb13 | Last Period 10min 13rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6A3 | 0xA6A4 | 42659 | 42660 | LAST_CUR_HARM_99_PASSb14 | Last Period 10min 14th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6A5 | 0xA6A6 | 42661 | 42662 | LAST_CUR_HARM_99_PASSb15 | Last Period 10min 15th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6A7 | 0xA6A8 | 42663 | 42664 | LAST_CUR_HARM_99_PASSb16 | Last Period 10min 16th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6A9 | 0xA6AA | 42665 | 42666 | LAST_CUR_HARM_99_PASSb17 | Last Period 10min 17th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6AB | 0xA6AC | 42667 | 42668 | LAST_CUR_HARM_99_PASSb18 | Last Period 10min 18th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6AD | 0xA6AE | 42669 | 42670 | LAST_CUR_HARM_99_PASSb19 | Last Period 10min 19th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6AF | 0xA6B0 | 42671 | 42672 | LAST_CUR_HARM_99_PASSb20 | Last Period 10min 20th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6B1 | 0xA6B2 | 42673 | 42674 | LAST_CUR_HARM_99_PASSb21 | Last Period 10min 21st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6B3 | 0xA6B4 | 42675 | 42676 | LAST_CUR_HARM_99_PASSb22 | Last Period 10min 22nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6B5 | 0xA6B6 | 42677 | 42678 | LAST_CUR_HARM_99_PASSb23 | Last Period 10min 23rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6B7 | 0xA6B8 | 42679 | 42680 | LAST_CUR_HARM_99_PASSb24 | Last Period 10min 24th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6B9 | 0xA6BA | 42681 | 42682 | LAST_CUR_HARM_99_PASSb25 | Last Period 10min 25th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6BB | 0xA6BC | 42683 | 42684 | LAST_CUR_HARM_99_PASSb26 | Last Period 10min 26th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6BD | 0xA6BE | 42685 | 42686 | LAST_CUR_HARM_99_PASSb27 | Last Period 10min 27th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6BF | 0xA6C0 | 42687 | 42688 | LAST_CUR_HARM_99_PASSb28 | Last Period 10min 28th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6C1 | 0xA6C2 | 42689 | 42690 | LAST_CUR_HARM_99_PASSb29 | Last Period 10min 29th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6C3 | 0xA6C4 | 42691 | 42692 | LAST_CUR_HARM_99_PASSb30 | Last Period 10min 30th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6C5 | 0xA6C6 | 42693 | 42694 | LAST_CUR_HARM_99_PASSb31 | Last Period 10min 31st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6C7 | 0xA6C8 | 42695 | 42696 | LAST_CUR_HARM_99_PASSb32 | Last Period 10min 32nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6C9 | 0xA6CA | 42697 | 42698 | LAST_CUR_HARM_99_PASSb33 | Last Period 10min 33rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6CB | 0xA6CC | 42699 | 42700 | LAST_CUR_HARM_99_PASSb34 | Last Period 10min 34th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6CD | 0xA6CE | 42701 | 42702 | LAST_CUR_HARM_99_PASSb35 | Last Period 10min 35th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6CF | 0xA6D0 | 42703 | 42704 | LAST_CUR_HARM_99_PASSb36 | Last Period 10min 36th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6D1 | 0xA6D2 | 42705 | 42706 | LAST_CUR_HARM_99_PASSb37 | Last Period 10min 37th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6D3 | 0xA6D4 | 42707 | 42708 | LAST_CUR_HARM_99_PASSb38 | Last Period 10min 38th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6D5 | 0xA6D6 | 42709 | 42710 | LAST_CUR_HARM_99_PASSb39 | Last Period 10min 39th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6D7 | 0xA6D8 | 42711 | 42712 | LAST_CUR_HARM_99_PASSb40 | Last Period 10min 40th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6D9 | 0xA6DA | 42713 | 42714 | LAST_CUR_HARM_99_PASSb41 | Last Period 10min 41st Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6DB | 0xA6DC | 42715 | 42716 | LAST_CUR_HARM_99_PASSb42 | Last Period 10min 42nd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6DD | 0xA6DE | 42717 | 42718 | LAST_CUR_HARM_99_PASSb43 | Last Period 10min 43rd Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6DF | 0xA6E0 | 42719 | 42720 | LAST_CUR_HARM_99_PASSb44 | Last Period 10min 44th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6E1 | 0xA6E2 | 42721 | 42722 | LAST_CUR_HARM_99_PASSb45 | Last Period 10min 45th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6E3 | 0xA6E4 | 42723 | 42724 | LAST_CUR_HARM_99_PASSb46 | Last Period 10min 46th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6E5 | 0xA6E6 | 42725 | 42726 | LAST_CUR_HARM_99_PASSb47 | Last Period 10min 47th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6E7 | 0xA6E8 | 42727 | 42728 | LAST_CUR_HARM_99_PASSb48 | Last Period 10min 48th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6E9 | 0xA6EA | 42729 | 42730 | LAST_CUR_HARM_99_PASSb49 | Last Period 10min 49th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6EB | 0xA6EC | 42731 | 42732 | LAST_CUR_HARM_99_PASSb50 | Last Period 10min 50th Phase B Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6ED | 0xA6EE | 42733 | 42734 | LAST_CUR_HARM_99_PASSc2 | Last Period 10min 2nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6EF | 0xA6F0 | 42735 | 42736 | LAST_CUR_HARM_99_PASSc3 | Last Period 10min 3rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6F1 | 0xA6F2 | 42737 | 42738 | LAST_CUR_HARM_99_PASSc4 | Last Period 10min 4th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6F3 | 0xA6F4 | 42739 | 42740 | LAST_CUR_HARM_99_PASSc5 | Last Period 10min 5th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6F5 | 0xA6F6 | 42741 | 42742 | LAST_CUR_HARM_99_PASSc6 | Last Period 10min 6th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6F7 | 0xA6F8 | 42743 | 42744 | LAST_CUR_HARM_99_PASSc7 | Last Period 10min 7th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6F9 | 0xA6FA | 42745 | 42746 | LAST_CUR_HARM_99_PASSc8 | Last Period 10min 8th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6FB | 0xA6FC | 42747 | 42748 | LAST_CUR_HARM_99_PASSc9 | Last Period 10min 9th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6FD | 0xA6FE | 42749 | 42750 | LAST_CUR_HARM_99_PASSc10 | Last Period 10min 10th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA6FF | 0xA700 | 42751 | 42752 | LAST_CUR_HARM_99_PASSc11 | Last Period 10min 11st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA701 | 0xA702 | 42753 | 42754 | LAST_CUR_HARM_99_PASSc12 | Last Period 10min 12nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA703 | 0xA704 | 42755 | 42756 | LAST_CUR_HARM_99_PASSc13 | Last Period 10min 13rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA705 | 0xA706 | 42757 | 42758 | LAST_CUR_HARM_99_PASSc14 | Last Period 10min 14th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA707 | 0xA708 | 42759 | 42760 | LAST_CUR_HARM_99_PASSc15 | Last Period 10min 15th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA709 | 0xA70A | 42761 | 42762 | LAST_CUR_HARM_99_PASSc16 | Last Period 10min 16th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA70B | 0xA70C | 42763 | 42764 | LAST_CUR_HARM_99_PASSc17 | Last Period 10min 17th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA70D | 0xA70E | 42765 | 42766 | LAST_CUR_HARM_99_PASSc18 | Last Period 10min 18th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA70F | 0xA710 | 42767 | 42768 | LAST_CUR_HARM_99_PASSc19 | Last Period 10min 19th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA711 | 0xA712 | 42769 | 42770 | LAST_CUR_HARM_99_PASSc20 | Last Period 10min 20th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA713 | 0xA714 | 42771 | 42772 | LAST_CUR_HARM_99_PASSc21 | Last Period 10min 21st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA715 | 0xA716 | 42773 | 42774 | LAST_CUR_HARM_99_PASSc22 | Last Period 10min 22nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA717 | 0xA718 | 42775 | 42776 | LAST_CUR_HARM_99_PASSc23 | Last Period 10min 23rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA719 | 0xA71A | 42777 | 42778 | LAST_CUR_HARM_99_PASSc24 | Last Period 10min 24th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA71B | 0xA71C | 42779 | 42780 | LAST_CUR_HARM_99_PASSc25 | Last Period 10min 25th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA71D | 0xA71E | 42781 | 42782 | LAST_CUR_HARM_99_PASSc26 | Last Period 10min 26th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA71F | 0xA720 | 42783 | 42784 | LAST_CUR_HARM_99_PASSc27 | Last Period 10min 27th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA721 | 0xA722 | 42785 | 42786 | LAST_CUR_HARM_99_PASSc28 | Last Period 10min 28th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA723 | 0xA724 | 42787 | 42788 | LAST_CUR_HARM_99_PASSc29 | Last Period 10min 29th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA725 | 0xA726 | 42789 | 42790 | LAST_CUR_HARM_99_PASSc30 | Last Period 10min 30th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA727 | 0xA728 | 42791 | 42792 | LAST_CUR_HARM_99_PASSc31 | Last Period 10min 31st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA729 | 0xA72A | 42793 | 42794 | LAST_CUR_HARM_99_PASSc32 | Last Period 10min 32nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA72B | 0xA72C | 42795 | 42796 | LAST_CUR_HARM_99_PASSc33 | Last Period 10min 33rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA72D | 0xA72E | 42797 | 42798 | LAST_CUR_HARM_99_PASSc34 | Last Period 10min 34th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA72F | 0xA730 | 42799 | 42800 | LAST_CUR_HARM_99_PASSc35 | Last Period 10min 35th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA731 | 0xA732 | 42801 | 42802 | LAST_CUR_HARM_99_PASSc36 | Last Period 10min 36th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA733 | 0xA734 | 42803 | 42804 | LAST_CUR_HARM_99_PASSc37 | Last Period 10min 37th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA735 | 0xA736 | 42805 | 42806 | LAST_CUR_HARM_99_PASSc38 | Last Period 10min 38th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA737 | 0xA738 | 42807 | 42808 | LAST_CUR_HARM_99_PASSc39 | Last Period 10min 39th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA739 | 0xA73A | 42809 | 42810 | LAST_CUR_HARM_99_PASSc40 | Last Period 10min 40th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA73B | 0xA73C | 42811 | 42812 | LAST_CUR_HARM_99_PASSc41 | Last Period 10min 41st Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA73D | 0xA73E | 42813 | 42814 | LAST_CUR_HARM_99_PASSc42 | Last Period 10min 42nd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA73F | 0xA740 | 42815 | 42816 | LAST_CUR_HARM_99_PASSc43 | Last Period 10min 43rd Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA741 | 0xA742 | 42817 | 42818 | LAST_CUR_HARM_99_PASSc44 | Last Period 10min 44th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA743 | 0xA744 | 42819 | 42820 | LAST_CUR_HARM_99_PASSc45 | Last Period 10min 45th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA745 | 0xA746 | 42821 | 42822 | LAST_CUR_HARM_99_PASSc46 | Last Period 10min 46th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA747 | 0xA748 | 42823 | 42824 | LAST_CUR_HARM_99_PASSc47 | Last Period 10min 47th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA749 | 0xA74A | 42825 | 42826 | LAST_CUR_HARM_99_PASSc48 | Last Period 10min 48th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA74B | 0xA74C | 42827 | 42828 | LAST_CUR_HARM_99_PASSc49 | Last Period 10min 49th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R
0xA74D | 0xA74E | 42829 | 42830 | LAST_CUR_HARM_99_PASSc50 | Last Period 10min 50th Phase C Current Harmonics Pass Rate for 99% Trigger Limit | float | 2 | R