## block
blockId | type | start | count | isEnable | NAME
0 | VIRTUAL_BLOCK | 0 | 1 | true | isOnline
1 | HOLDING_REGISTER | 16384 | 72 | true | Real time basic parameters（1S）
2 | HOLDING_REGISTER | 16456 | 18 | true | Energy （1S）
3 | HOLDING_REGISTER | 16474 | 100 | true | Harmonics - THD_1（3S）
4 | HOLDING_REGISTER | 16574 | 109 | true | Harmonics - THD_2（3S）
5 | HOLDING_REGISTER | 17044 | 17 | true | Sequence
6 | HOLDING_REGISTER | 17664 | 100 | true | Harmonics - individual_1（3S）
7 | HOLDING_REGISTER | 17764 | 91 | true | Harmonics - individual_2（3S）
8 | HOLDING_REGISTER | 17952 | 30 | true | Energy - continue（1S）
9 | HOLDING_REGISTER | 4093 | 73 | true | DeviceSetting-Basic
13 | HOLDING_REGISTER | 61555 | 1 | true | DeviceInfo-CT Num
14 | HOLDING_REGISTER | 61936 | 1 | true | DeviceInfo-CT Type

## blockParams
ID | blockId | paramId | Start(Dec) | descrption | paramType | unit | dataType | byteOrder | RW | Reg | scale | analysisUnitId | datalog | trendreal | trendenergy | north | conf | range | readings | Alarm | DataLog | AcuCloud | MQTT | SNMP | BACnetIP |  | paramType_AcuCloud | AcuHMI中模板没有的，AcuCloud中有的字段
1 | 0 | 0-1 | 0 | IsOnline | IsOnline |  | isOnline | 1 | R | 1 | 1 | 0 | [5 empty] | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime |  | DI14 | Digital Input Channel 14
2 | 1 | 1-1 | 16384 | System Frequency | FREQ_Hz | Hz | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Freq_Hz | DI12 | Digital Input Channel 12
3 | 1 | 1-2 | 16386 | Phase A Line-to-Neutral Voltage | VLN_a_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | V1 | AI1 | Analog Input 1
4 | 1 | 1-3 | 16388 | Phase B Line-to-Neutral Voltage | VLN_b_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | V2 | AI2 | Analog Input 2
5 | 1 | 1-4 | 16390 | Phase C Line-to-Neutral Voltage | VLN_c_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | V3 | AI3 | Analog Input 3
6 | 1 | 1-5 | 16392 | Average Line-to-Neutral Voltage | VLN_avg_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Vnavg_V | DMD_I1_A | Phase A Current Demand
7 | 1 | 1-6 | 16394 | Phase A-B Line-to-Line Voltage | VLL_ab_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | V12 | DMD_I2_A | Phase B Current Demand
8 | 1 | 1-7 | 16396 | Phase B-C Line-to-Line Voltage | VLL_bc_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | V23 | DMD_I3_A | Phase C Current Demand
9 | 1 | 1-8 | 16398 | Phase C-A Line-to-Line Voltage | VLL_ca_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | V31 | DI11 | Digital Input Channel 11
10 | 1 | 1-9 | 16400 | Average Line-to-Line Voltage | VLL_avg_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | VIavg_V | DI13 | Digital Input Channel 13
11 | 1 | 1-10 | 16402 | Phase A Line Current | I_a_A | A | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I1 | DI15 | Digital Input Channel 15
12 | 1 | 1-11 | 16404 | Phase B Line Current | I_b_A | A | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I2 | DI16 | Digital Input Channel 16
13 | 1 | 1-12 | 16406 | Phase C Line Current | I_c_A | A | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I3 | LCavg | System Average Load Nature
14 | 1 | 1-13 | 16408 | Average Line Current | I_avg_A | A | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Iavg_A | LoadType | System Load Nature
15 | 1 | 1-14 | 16410 | Neutral Current | I_n_A | A | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | In | Unbl_U | System Voltage Unbalance Factor
16 | 1 | 1-15 | 16412 | Phase A Active Power | P_a_kW | kW | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P1 | AI4 | Analog Input 4
17 | 1 | 1-16 | 16414 | Phase B Active Power | P_b_kW | kW | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P2 | IO21_DI1_C | IO21 DI Counter 1
18 | 1 | 1-17 | 16416 | Phase C Active Power | P_c_kW | kW | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P3 | IO21_DI2_C | IO21 DI Counter 2
19 | 1 | 1-18 | 16418 | System Active Power | P_kW | kW | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Psum_kW | IO21_DI3_C | IO21 DI Counter 3
20 | 1 | 1-19 | 16420 | Phase A Reactive Power | Q_a_kvar | kvar | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q1 | IO31_DI1_C | IO31 DI Counter 1
21 | 1 | 1-20 | 16422 | Phase B Reactive Power | Q_b_kvar | kvar | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q2 | IO31_DI2_C | IO31 DI Counter 2
22 | 1 | 1-21 | 16424 | Phase C Reactive Power | Q_c_kvar | kvar | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q3 | IO31_DI3_C | IO31 DI Counter 3
23 | 1 | 1-22 | 16426 | System Reactive Power | Q_kvar | kvar | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qsum_kvar | IO31_DI4_C | IO31 DI Counter 4
24 | 1 | 1-23 | 16428 | Phase A Apparent Power | S_a_kVA | kVA | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S1 | IO12_DI1_C | IO12 DI Counter 1
25 | 1 | 1-24 | 16430 | Phase B Apparent Power | S_b_kVA | kVA | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S2 | IO12_DI2_C | IO12 DI Counter 2
26 | 1 | 1-25 | 16432 | Phase C Apparent Power | S_c_kVA | kVA | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S3 | IO12_DI3_C | IO12 DI Counter 3
27 | 1 | 1-26 | 16434 | System Apparent Power | S_kVA | kVA | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ssum_kVA | IO12_DI4_C | IO12 DI Counter 4
28 | 1 | 1-27 | 16436 | Phase A Power Factor | PF_a | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF1 | IO12_DI5_C | IO12 DI Counter 5
29 | 1 | 1-28 | 16438 | Phase B Power Factor | PF_b | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF2 | IO12_DI6_C | IO12 DI Counter 6
30 | 1 | 1-29 | 16440 | Phase C Power Factor | PF_c | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF3 | IO22_DI1_C | IO22 DI Counter 1
31 | 1 | 1-30 | 16442 | System Power Factor | PF | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF | IO22_DI2_C | IO22 DI Counter 2
32 | 1 | 1-31 | 16444 | Voltage Unbalance Factor | UNBL_V_% | % | float32 | 12 | R | 2 | 100 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Unbl_V | IO22_DI3_C | IO22 DI Counter 3
33 | 1 | 1-32 | 16446 | Current Unbalance Factor | UNBL_I_% | % | float32 | 12 | R | 2 | 100 | 1 | 1 | 2 |  | 4 |  | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Unbl_I | IO22_DI4_C | IO22 DI Counter 4
34 | 1 | 1-33 | 16448 | Average Load Nature | LC_avg | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 | [10 empty] | Lcavg | IO32_DI1_C | IO32 DI Counter 1
35 | 1 | 1-34 | 16450 | System Active Power Demand | DMD_P_kW | kW | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 7 | 13-14 | demand | demand | demand | demand | demand | demand | demand | DMD_P_kW | IO32_DI2_C | IO32 DI Counter 2
36 | 1 | 1-35 | 16452 | System Reactive Power Demand | DMD_Q_kvar | kvar | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 7 | 13-14 | demand | demand | demand | demand | demand | demand | demand | DMD_Q_kvar | IO32_DI3_C | IO32 DI Counter 3
37 | 1 | 1-36 | 16454 | System Apparent Power Demand | DMD_S_kVA | kVA | float32 | 12 | R | 2 | 0.001 | 1 | 1 | 2 |  | 4 |  | 7 | 13-14 | demand | demand | demand | demand | demand | demand | demand | DMD_S_kVA | IO32_DI4_C | IO32 DI Counter 4
38 | 2 | 2-1 | 16456 | System Import Active Energy | EP_IMP_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8 | 13 | energy | energy | energy | energy | energy | energy | energy | EP_IMP_kWh | IO21_DI4_C | IO21 DI Counter 4
39 | 2 | 2-2 | 16458 | System Export Active Energy | EP_EXP_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8 | 13 | energy | energy | energy | energy | energy | energy | energy | EP_EXP_kWh | IO11_DI1_S | IO11 DI Status 1
40 | 2 | 2-3 | 16460 | System Import Reactive Energy | EQ_IMP_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8 | 13 | energy | energy | energy | energy | energy | energy | energy | EQ_IMP_kvarh | IO11_DI2_S | IO11 DI Status 2
41 | 2 | 2-4 | 16462 | System Export Reactive Energy | EQ_EXP_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8 | 13 | energy | energy | energy | energy | energy | energy | energy | EQ_EXP_kvarh | IO11_DI3_S | IO11 DI Status 3
42 | 2 | 2-5 | 16464 | System Total Active Energy | EP_TOTAL_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8 | 13 | energy | energy | energy | energy | energy | energy | energy | EP_TOTAL_kWh | IO11_DI4_S | IO11 DI Status 4
43 | 2 | 2-6 | 16466 | System Net Active Energy | EP_NET_kWh | kWh | int32 | 11 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8 | 13 | energy | energy | energy | energy | energy | energy | energy | EP_NET_kWh | IO11_DI5_S | IO11 DI Status 5
44 | 2 | 2-7 | 16468 | System Total Reactive Energy | EQ_TOTAL_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8 | 13 | energy | energy | energy | energy | energy | energy | energy | EQ_TOTAL_kvarh | IO11_DI6_S | IO11 DI Status 6
45 | 2 | 2-8 | 16470 | System Net Reactive Energy | EQ_NET_kvarh | kvarh | int32 | 11 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8 | 13 | energy | energy | energy | energy | energy | energy | energy | EQ_NET_kvarh | IO21_DI1_S | IO21 DI Status 1
46 | 2 | 2-9 | 16472 | System Apparent Energy | ES_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8 | 13 | energy | energy | energy | energy | energy | energy | energy | ES_kVAh | IO21_DI2_S | IO21 DI Status 2
47 | 3 | 3-1 | 16474 | Phase A Voltage THD | THD_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | THD_Va | IO21_DI3_S | IO21 DI Status 3
48 | 3 | 3-2 | 16475 | Phase B Voltage THD | THD_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | THD_Vb | IO21_DI4_S | IO21 DI Status 4
49 | 3 | 3-3 | 16476 | Phase C Voltage THD | THD_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | THD_Vc | IO31_DI1_S | IO31 DI Status 1
50 | 3 | 3-4 | 16477 | Average Voltage THD | THD_V_avg_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | THD_Vavg | IO31_DI2_S | IO31 DI Status 2
51 | 3 | 3-5 | 16478 | Phase A Current THD | THD_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | THD_Ia | IO31_DI3_S | IO31 DI Status 3
52 | 3 | 3-6 | 16479 | Phase B Current THD | THD_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | THD_Ib | IO31_DI4_S | IO31 DI Status 4
53 | 3 | 3-7 | 16480 | Phase C Current THD | THD_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | THD_Ic | IO12_DI1_S | IO12 DI Status 1
54 | 3 | 3-8 | 16481 | Average Current THD | THD_I_avg_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | THD_Iavg | IO12_DI2_S | IO12 DI Status 2
55 | 3 | 3-9 | 16482 | Phase A Voltage 2-th Harmonic | HAR2_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO12_DI3_S | IO12 DI Status 3
56 | 3 | 3-10 | 16483 | Phase A Voltage 3-th Harmonic | HAR3_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO12_DI4_S | IO12 DI Status 4
57 | 3 | 3-11 | 16484 | Phase A Voltage 4-th Harmonic | HAR4_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO12_DI5_S | IO12 DI Status 5
58 | 3 | 3-12 | 16485 | Phase A Voltage 5-th Harmonic | HAR5_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO12_DI6_S | IO12 DI Status 6
59 | 3 | 3-13 | 16486 | Phase A Voltage 6-th Harmonic | HAR6_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO22_DI1_S | IO22 DI Status 1
60 | 3 | 3-14 | 16487 | Phase A Voltage 7-th Harmonic | HAR7_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO22_DI2_S | IO22 DI Status 2
61 | 3 | 3-15 | 16488 | Phase A Voltage 8-th Harmonic | HAR8_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO22_DI3_S | IO22 DI Status 3
62 | 3 | 3-16 | 16489 | Phase A Voltage 9-th Harmonic | HAR9_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO22_DI4_S | IO22 DI Status 4
63 | 3 | 3-17 | 16490 | Phase A Voltage 10-th Harmonic | HAR10_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO32_DI1_S | IO32 DI Status 1
64 | 3 | 3-18 | 16491 | Phase A Voltage 11-th Harmonic | HAR11_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO32_DI2_S | IO32 DI Status 2
65 | 3 | 3-19 | 16492 | Phase A Voltage 12-th Harmonic | HAR12_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO32_DI3_S | IO32 DI Status 3
66 | 3 | 3-20 | 16493 | Phase A Voltage 13-th Harmonic | HAR13_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO32_DI4_S | IO32 DI Status 4
67 | 3 | 3-21 | 16494 | Phase A Voltage 14-th Harmonic | HAR14_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_P_kWh | Energy 1 System Active Energy from the Grid
68 | 3 | 3-22 | 16495 | Phase A Voltage 15-th Harmonic | HAR15_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_PA_kWh | Energy 1 Dual Source Phase A Active Energy from the Grid
69 | 3 | 3-23 | 16496 | Phase A Voltage 16-th Harmonic | HAR16_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_PB_kWh | Energy 1 Dual Source Phase B Active Energy from the Grid
70 | 3 | 3-24 | 16497 | Phase A Voltage 17-th Harmonic | HAR17_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_PC_kWh | Energy 1 Dual Source Phase C Active Energy from the Grid
71 | 3 | 3-25 | 16498 | Phase A Voltage 18-th Harmonic | HAR18_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_Q_kVArh | Energy 1 System Reactive Energy from the Grid
72 | 3 | 3-26 | 16499 | Phase A Voltage 19-th Harmonic | HAR19_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_QA_kVArh | Energy 1 Dual Source Phase A Reactive Energy from the Grid
73 | 3 | 3-27 | 16500 | Phase A Voltage 20-th Harmonic | HAR20_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_QB_kVArh | Energy 1 Dual Source Phase B Reactive Energy from the Grid
74 | 3 | 3-28 | 16501 | Phase A Voltage 21-th Harmonic | HAR21_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_QC_kVArh | Energy 1 Dual Source Phase C Reactive Energy from the Grid
75 | 3 | 3-29 | 16502 | Phase A Voltage 22-th Harmonic | HAR22_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_S_kVAh | Energy 1 System Apparent Energy from the Grid
76 | 3 | 3-30 | 16503 | Phase A Voltage 23-th Harmonic | HAR23_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_SA_kVAh | Energy 1 Dual Source Phase A Apparent Energy from the Grid
77 | 3 | 3-31 | 16504 | Phase A Voltage 24-th Harmonic | HAR24_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_SB_kVAh | Energy 1 Dual Source Phase B Apparent Energy from the Grid
78 | 3 | 3-32 | 16505 | Phase A Voltage 25-th Harmonic | HAR25_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Grid_SC_kVAh | Energy 1 Dual Source Phase C Apparent Energy from the Grid
79 | 3 | 3-33 | 16506 | Phase A Voltage 26-th Harmonic | HAR26_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Gen_PA_kWh | Energy 1 Dual Source Phase A Active Energy from the Generator
80 | 3 | 3-34 | 16507 | Phase A Voltage 27-th Harmonic | HAR27_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Gen_PB_kWh | Energy 1 Dual Source Phase B Active Energy from the Generator
81 | 3 | 3-35 | 16508 | Phase A Voltage 28-th Harmonic | HAR28_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Gen_PC_kWh | Energy 1 Dual Source Phase C Active Energy from the Generator
82 | 3 | 3-36 | 16509 | Phase A Voltage 29-th Harmonic | HAR29_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Gen_QA_kVArh | Energy 1 Dual Source Phase A Reactive Energy from the Generator
83 | 3 | 3-37 | 16510 | Phase A Voltage 30-th Harmonic | HAR30_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Gen_QB_kVArh | Energy 1 Dual Source Phase B Reactive Energy from the Generator
84 | 3 | 3-38 | 16511 | Phase A Voltage 31-th Harmonic | HAR31_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Gen_QC_kVArh | Energy 1 Dual Source Phase C Reactive Energy from the Generator
85 | 3 | 3-39 | 16512 | Phase A Voltage Odd THD | OTHD_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | OTHD_Va | E1_Gen_SA_kVAh | Energy 1 Dual Source Phase A Apparent Energy from the Generator
86 | 3 | 3-40 | 16513 | Phase A Voltage Even THD | ETHD_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | ETHD_Va | E1_Gen_SB_kVAh | Energy 1 Dual Source Phase B Apparent Energy from the Generator
87 | 3 | 3-41 | 16514 | Phase A Voltage Crest Factor | CF_V_a_% | % | int16 | 12 | R | 1 | 0.001 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | CF_Va | E1_Gen_SC_kVAh | Energy 1 Dual Source Phase C Apparent Energy from the Generator
88 | 3 | 3-42 | 16515 | Phase A Voltage Telephone Harmonic Form Factor | THFF_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | THFF_Va | E2_Grid_P_kWh | Energy 2 System Active Energy from the Grid
89 | 3 | 3-43 | 16516 | Phase B Voltage 2-th Harmonic | HAR2_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Grid_PA_kWh | Energy 2 Dual Source Phase A Active Energy from the Grid
90 | 3 | 3-44 | 16517 | Phase B Voltage 3-th Harmonic | HAR3_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Grid_PB_kWh | Energy 2 Dual Source Phase B Active Energy from the Grid
91 | 3 | 3-45 | 16518 | Phase B Voltage 4-th Harmonic | HAR4_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Grid_PC_kWh | Energy 2 Dual Source Phase C Active Energy from the Grid
92 | 3 | 3-46 | 16519 | Phase B Voltage 5-th Harmonic | HAR5_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Grid_Q_kVArh | Energy 2 System Reactive Energy from the Grid
93 | 3 | 3-47 | 16520 | Phase B Voltage 6-th Harmonic | HAR6_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Grid_QA_kVArh | Energy 2 Dual Source Phase A Reactive Energy from the Grid
94 | 3 | 3-48 | 16521 | Phase B Voltage 7-th Harmonic | HAR7_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Grid_QB_kVArh | Energy 2 Dual Source Phase B Reactive Energy from the Grid
95 | 3 | 3-49 | 16522 | Phase B Voltage 8-th Harmonic | HAR8_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Grid_QC_kVArh | Energy 2 Dual Source Phase C Reactive Energy from the Grid
96 | 3 | 3-50 | 16523 | Phase B Voltage 9-th Harmonic | HAR9_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Grid_S_kVAh | Energy 2 System Apparent Energy from the Grid
97 | 3 | 3-51 | 16524 | Phase B Voltage 10-th Harmonic | HAR10_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Grid_SA_kVAh | Energy 2 Dual Source Phase A Apparent Energy from the Grid
98 | 3 | 3-52 | 16525 | Phase B Voltage 11-th Harmonic | HAR11_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Grid_SB_kVAh | Energy 2 Dual Source Phase B Apparent Energy from the Grid
99 | 3 | 3-53 | 16526 | Phase B Voltage 12-th Harmonic | HAR12_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Grid_SC_kVAh | Energy 2 Dual Source Phase C Apparent Energy from the Grid
100 | 3 | 3-54 | 16527 | Phase B Voltage 13-th Harmonic | HAR13_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_PA_kWh | Energy 2 Dual Source Phase A Active Energy from the Generator
101 | 3 | 3-55 | 16528 | Phase B Voltage 14-th Harmonic | HAR14_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_PB_kWh | Energy 2 Dual Source Phase B Active Energy from the Generator
102 | 3 | 3-56 | 16529 | Phase B Voltage 15-th Harmonic | HAR15_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_PC_kWh | Energy 2 Dual Source Phase C Active Energy from the Generator
103 | 3 | 3-57 | 16530 | Phase B Voltage 16-th Harmonic | HAR16_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_QA_kVArh | Energy 2 Dual Source Phase A Reactive Energy from the Generator
104 | 3 | 3-58 | 16531 | Phase B Voltage 17-th Harmonic | HAR17_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_QB_kVArh | Energy 2 Dual Source Phase B Reactive Energy from the Generator
105 | 3 | 3-59 | 16532 | Phase B Voltage 18-th Harmonic | HAR18_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_QC_kVArh | Energy 2 Dual Source Phase C Reactive Energy from the Generator
106 | 3 | 3-60 | 16533 | Phase B Voltage 19-th Harmonic | HAR19_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_SA_kVAh | Energy 2 Dual Source Phase A Apparent Energy from the Generator
107 | 3 | 3-61 | 16534 | Phase B Voltage 20-th Harmonic | HAR20_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_SB_kVAh | Energy 2 Dual Source Phase B Apparent Energy from the Generator
108 | 3 | 3-62 | 16535 | Phase B Voltage 21-th Harmonic | HAR21_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_SC_kVAh | Energy 2 Dual Source Phase C Apparent Energy from the Generator
109 | 3 | 3-63 | 16536 | Phase B Voltage 22-th Harmonic | HAR22_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Grid_P_kWh | Energy 3 System Active Energy from the Grid
110 | 3 | 3-64 | 16537 | Phase B Voltage 23-th Harmonic | HAR23_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Grid_PA_kWh | Energy 3 Dual Source Phase A Active Energy from the Grid
111 | 3 | 3-65 | 16538 | Phase B Voltage 24-th Harmonic | HAR24_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Grid_PB_kWh | Energy 3 Dual Source Phase B Active Energy from the Grid
112 | 3 | 3-66 | 16539 | Phase B Voltage 25-th Harmonic | HAR25_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Grid_PC_kWh | Energy 3 Dual Source Phase C Active Energy from the Grid
113 | 3 | 3-67 | 16540 | Phase B Voltage 26-th Harmonic | HAR26_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Grid_Q_kVArh | Energy 3 System Reactive Energy from the Grid
114 | 3 | 3-68 | 16541 | Phase B Voltage 27-th Harmonic | HAR27_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Grid_QA_kVArh | Energy 3 Dual Source Phase A Reactive Energy from the Grid
115 | 3 | 3-69 | 16542 | Phase B Voltage 28-th Harmonic | HAR28_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Grid_QB_kVArh | Energy 3 Dual Source Phase B Reactive Energy from the Grid
116 | 3 | 3-70 | 16543 | Phase B Voltage 29-th Harmonic | HAR29_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Grid_QC_kVArh | Energy 3 Dual Source Phase C Reactive Energy from the Grid
117 | 3 | 3-71 | 16544 | Phase B Voltage 30-th Harmonic | HAR30_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Grid_S_kVAh | Energy 3 System Apparent Energy from the Grid
118 | 3 | 3-72 | 16545 | Phase B Voltage 31-th Harmonic | HAR31_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Grid_SA_kVAh | Energy 3 Dual Source Phase A Apparent Energy from the Grid
119 | 3 | 3-73 | 16546 | Phase B Voltage Odd THD | OTHD_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | OTHD_Vb | E3_Grid_SB_kVAh | Energy 3 Dual Source Phase B Apparent Energy from the Grid
120 | 3 | 3-74 | 16547 | Phase B Voltage Even THD | ETHD_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | ETHD_Vb | E3_Grid_SC_kVAh | Energy 3 Dual Source Phase C Apparent Energy from the Grid
121 | 3 | 3-75 | 16548 | Phase B Voltage Crest Factor | CF_V_b_% | % | int16 | 12 | R | 1 | 0.001 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | CF_Vb | E3_Gen_PA_kWh | Energy 3 Dual Source Phase A Active Energy from the Generator
122 | 3 | 3-76 | 16549 | Phase B Voltage Telephone Harmonic Form Factor | THFF_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | THFF_Vb | E3_Gen_PB_kWh | Energy 3 Dual Source Phase B Active Energy from the Generator
123 | 3 | 3-77 | 16550 | Phase C Voltage 2-th Harmonic | HAR2_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Gen_PC_kWh | Energy 3 Dual Source Phase C Active Energy from the Generator
124 | 3 | 3-78 | 16551 | Phase C Voltage 3-th Harmonic | HAR3_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Gen_P_kWh | Energy 3 Dual Source Active Energy from the Generator
125 | 3 | 3-79 | 16552 | Phase C Voltage 4-th Harmonic | HAR4_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_Q_kVArh | Energy 2 Dual Source Reactive Energy from the Generator
126 | 3 | 3-80 | 16553 | Phase C Voltage 5-th Harmonic | HAR5_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_S_kVAh | Energy 2 Dual Source Apparent Energy from the Generator
127 | 3 | 3-81 | 16554 | Phase C Voltage 6-th Harmonic | HAR6_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E2_Gen_P_kWh | Energy 2 Dual Source Active Energy from the Generator
128 | 3 | 3-82 | 16555 | Phase C Voltage 7-th Harmonic | HAR7_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Gen_Q_kVArh | Energy 1 Dual Source Reactive Energy from the Generator
129 | 3 | 3-83 | 16556 | Phase C Voltage 8-th Harmonic | HAR8_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Gen_QA_kVArh | Energy 3 Dual Source Phase A Reactive Energy from the Generator
130 | 3 | 3-84 | 16557 | Phase C Voltage 9-th Harmonic | HAR9_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Gen_QB_kVArh | Energy 3 Dual Source Phase B Reactive Energy from the Generator
131 | 3 | 3-85 | 16558 | Phase C Voltage 10-th Harmonic | HAR10_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Gen_QC_kVArh | Energy 3 Dual Source Phase C Reactive Energy from the Generator
132 | 3 | 3-86 | 16559 | Phase C Voltage 11-th Harmonic | HAR11_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Gen_SA_kVAh | Energy 3 Dual Source Phase A Apparent Energy from the Generator
133 | 3 | 3-87 | 16560 | Phase C Voltage 12-th Harmonic | HAR12_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Gen_SB_kVAh | Energy 3 Dual Source Phase B Apparent Energy from the Generator
134 | 3 | 3-88 | 16561 | Phase C Voltage 13-th Harmonic | HAR13_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Gen_SC_kVAh | Energy 3 Dual Source Phase C Apparent Energy from the Generator
135 | 3 | 3-89 | 16562 | Phase C Voltage 14-th Harmonic | HAR14_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Gen_P_kWh | Energy 1 Dual Source Active Energy from the Generator
136 | 3 | 3-90 | 16563 | Phase C Voltage 15-th Harmonic | HAR15_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Gen_Q_kVArh | Energy 3 Dual Source Reactive Energy from the Generator
137 | 3 | 3-91 | 16564 | Phase C Voltage 16-th Harmonic | HAR16_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E3_Gen_S_kVAh | Energy 3 Dual Source Apparent Energy from the Generator
138 | 3 | 3-92 | 16565 | Phase C Voltage 17-th Harmonic | HAR17_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | E1_Gen_S_kVAh | Energy 1 Dual Source Apparent Energy from the Generator
139 | 3 | 3-93 | 16566 | Phase C Voltage 18-th Harmonic | HAR18_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO11_DI1_C | IO11 DI Counter 1
140 | 3 | 3-94 | 16567 | Phase C Voltage 19-th Harmonic | HAR19_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO11_DI2_C | IO11 DI Counter 2
141 | 3 | 3-95 | 16568 | Phase C Voltage 20-th Harmonic | HAR20_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO11_DI3_C | IO11 DI Counter 3
142 | 3 | 3-96 | 16569 | Phase C Voltage 21-th Harmonic | HAR21_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO11_DI4_C | IO11 DI Counter 4
143 | 3 | 3-97 | 16570 | Phase C Voltage 22-th Harmonic | HAR22_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO11_DI5_C | IO11 DI Counter 5
144 | 3 | 3-98 | 16571 | Phase C Voltage 23-th Harmonic | HAR23_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | IO11_DI6_C | IO11 DI Counter 6
145 | 3 | 3-99 | 16572 | Phase C Voltage 24-th Harmonic | HAR24_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | THD_In | channal 4 Current Total Harmonic Distortion
146 | 3 | 3-100 | 16573 | Phase C Voltage 25-th Harmonic | HAR25_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har2_In | channal 4 Current order 2 harmonic
147 | 4 | 4-1 | 16574 | Phase C Voltage 26-th Harmonic | HAR26_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har3_In | channal 4 Current order 3 harmonic
148 | 4 | 4-2 | 16575 | Phase C Voltage 27-th Harmonic | HAR27_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har4_In | channal 4 Current order 4 harmonic
149 | 4 | 4-3 | 16576 | Phase C Voltage 28-th Harmonic | HAR28_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har5_In | channal 4 Current order 5 harmonic
150 | 4 | 4-4 | 16577 | Phase C Voltage 29-th Harmonic | HAR29_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har6_In | channal 4 Current order 6 harmonic
151 | 4 | 4-5 | 16578 | Phase C Voltage 30-th Harmonic | HAR30_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har7_In | channal 4 Current order 7 harmonic
152 | 4 | 4-6 | 16579 | Phase C Voltage 31-th Harmonic | HAR31_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har8_In | channal 4 Current order 8 harmonic
153 | 4 | 4-7 | 16580 | Phase C Voltage Odd THD | OTHD_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | OTHD_Vc | Har9_In | channal 4 Current order 9 harmonic
154 | 4 | 4-8 | 16581 | Phase C Voltage Even THD | ETHD_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | ETHD_Vc | Har10_In | channal 4 Current order 10 harmonic
155 | 4 | 4-9 | 16582 | Phase C Voltage Crest Factor | CF_V_c_% | % | int16 | 12 | R | 1 | 0.001 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | CF_Vc | Har11_In | channal 4 Current order 11 harmonic
156 | 4 | 4-10 | 16583 | Phase C Voltage Telephone Harmonic Form Factor | THFF_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | THFF_Vc | Har12_In | channal 4 Current order 12 harmonic
157 | 4 | 4-11 | 16584 | Phase A Current 2-th Harmonic | HAR2_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har13_In | channal 4 Current order 13 harmonic
158 | 4 | 4-12 | 16585 | Phase A Current 3-th Harmonic | HAR3_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har14_In | channal 4 Current order 14 harmonic
159 | 4 | 4-13 | 16586 | Phase A Current 4-th Harmonic | HAR4_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har15_In | channal 4 Current order 15 harmonic
160 | 4 | 4-14 | 16587 | Phase A Current 5-th Harmonic | HAR5_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har16_In | channal 4 Current order 16 harmonic
161 | 4 | 4-15 | 16588 | Phase A Current 6-th Harmonic | HAR6_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har17_In | channal 4 Current order 17 harmonic
162 | 4 | 4-16 | 16589 | Phase A Current 7-th Harmonic | HAR7_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har18_In | channal 4 Current order 18 harmonic
163 | 4 | 4-17 | 16590 | Phase A Current 8-th Harmonic | HAR8_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har19_In | channal 4 Current order 19 harmonic
164 | 4 | 4-18 | 16591 | Phase A Current 9-th Harmonic | HAR9_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har20_In | channal 4 Current order 20 harmonic
165 | 4 | 4-19 | 16592 | Phase A Current 10-th Harmonic | HAR10_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har21_In | channal 4 Current order 21 harmonic
166 | 4 | 4-20 | 16593 | Phase A Current 11-th Harmonic | HAR11_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har22_In | channal 4 Current order 22 harmonic
167 | 4 | 4-21 | 16594 | Phase A Current 12-th Harmonic | HAR12_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har23_In | channal 4 Current order 23 harmonic
168 | 4 | 4-22 | 16595 | Phase A Current 13-th Harmonic | HAR13_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har24_In | channal 4 Current order 24 harmonic
169 | 4 | 4-23 | 16596 | Phase A Current 14-th Harmonic | HAR14_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har25_In | channal 4 Current order 25 harmonic
170 | 4 | 4-24 | 16597 | Phase A Current 15-th Harmonic | HAR15_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har26_In | channal 4 Current order 26 harmonic
171 | 4 | 4-25 | 16598 | Phase A Current 16-th Harmonic | HAR16_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har27_In | channal 4 Current order 27 harmonic
172 | 4 | 4-26 | 16599 | Phase A Current 17-th Harmonic | HAR17_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har28_In | channal 4 Current order 28 harmonic
173 | 4 | 4-27 | 16600 | Phase A Current 18-th Harmonic | HAR18_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har29_In | channal 4 Current order 29 harmonic
174 | 4 | 4-28 | 16601 | Phase A Current 19-th Harmonic | HAR19_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har30_In | channal 4 Current order 30 harmonic
175 | 4 | 4-29 | 16602 | Phase A Current 20-th Harmonic | HAR20_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har31_In | channal 4 Current order 31 harmonic
176 | 4 | 4-30 | 16603 | Phase A Current 21-th Harmonic | HAR21_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | OTHD_In | channal 4 Current Odd-order Harmonic Distortion
177 | 4 | 4-31 | 16604 | Phase A Current 22-th Harmonic | HAR22_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | ETHD_In | channal 4 Current Even-order Harmonic Distortion
178 | 4 | 4-32 | 16605 | Phase A Current 23-th Harmonic | HAR23_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | KF_In | channal 4 K Factor
179 | 4 | 4-33 | 16606 | Phase A Current 24-th Harmonic | HAR24_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har32_In | channal 4 Current order 32 harmonic
180 | 4 | 4-34 | 16607 | Phase A Current 25-th Harmonic | HAR25_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har33_In | channal 4 Current order 33 harmonic
181 | 4 | 4-35 | 16608 | Phase A Current 26-th Harmonic | HAR26_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har34_In | channal 4 Current order 34 harmonic
182 | 4 | 4-36 | 16609 | Phase A Current 27-th Harmonic | HAR27_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har35_In | channal 4 Current order 35 harmonic
183 | 4 | 4-37 | 16610 | Phase A Current 28-th Harmonic | HAR28_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har36_In | channal 4 Current order 36 harmonic
184 | 4 | 4-38 | 16611 | Phase A Current 29-th Harmonic | HAR29_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har37_In | channal 4 Current order 37 harmonic
185 | 4 | 4-39 | 16612 | Phase A Current 30-th Harmonic | HAR30_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har38_In | channal 4 Current order 38 harmonic
186 | 4 | 4-40 | 16613 | Phase A Current 31-th Harmonic | HAR31_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har39_In | channal 4 Current order 39 harmonic
187 | 4 | 4-41 | 16614 | Phase A Current Odd THD | OTHD_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | OTHD_Ia | Har40_In | channal 4 Current order 40 harmonic
188 | 4 | 4-42 | 16615 | Phase A Current Even THD | ETHD_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | ETHD_Ia | Har41_In | channal 4 Current order 41 harmonic
189 | 4 | 4-43 | 16616 | Phase A Current K Factor | KF_I_a_% | % | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | KF_Ia | Har42_In | channal 4 Current order 42 harmonic
190 | 4 | 4-44 | 16617 | Phase B Current 2-th Harmonic | HAR2_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har43_In | channal 4 Current order 43 harmonic
191 | 4 | 4-45 | 16618 | Phase B Current 3-th Harmonic | HAR3_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har44_In | channal 4 Current order 44 harmonic
192 | 4 | 4-46 | 16619 | Phase B Current 4-th Harmonic | HAR4_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har45_In | channal 4 Current order 45 harmonic
193 | 4 | 4-47 | 16620 | Phase B Current 5-th Harmonic | HAR5_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har46_In | channal 4 Current order 46 harmonic
194 | 4 | 4-48 | 16621 | Phase B Current 6-th Harmonic | HAR6_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har47_In | channal 4 Current order 47 harmonic
195 | 4 | 4-49 | 16622 | Phase B Current 7-th Harmonic | HAR7_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har48_In | channal 4 Current order 48 harmonic
196 | 4 | 4-50 | 16623 | Phase B Current 8-th Harmonic | HAR8_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har49_In | channal 4 Current order 49 harmonic
197 | 4 | 4-51 | 16624 | Phase B Current 9-th Harmonic | HAR9_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har50_In | channal 4 Current order 50 harmonic
198 | 4 | 4-52 | 16625 | Phase B Current 10-th Harmonic | HAR10_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har51_In | channal 4 Current order 51 harmonic
199 | 4 | 4-53 | 16626 | Phase B Current 11-th Harmonic | HAR11_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har52_In | channal 4 Current order 52 harmonic
200 | 4 | 4-54 | 16627 | Phase B Current 12-th Harmonic | HAR12_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har53_In | channal 4 Current order 53 harmonic
201 | 4 | 4-55 | 16628 | Phase B Current 13-th Harmonic | HAR13_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har54_In | channal 4 Current order 54 harmonic
202 | 4 | 4-56 | 16629 | Phase B Current 14-th Harmonic | HAR14_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har55_In | channal 4 Current order 55 harmonic
203 | 4 | 4-57 | 16630 | Phase B Current 15-th Harmonic | HAR15_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har56_In | channal 4 Current order 56 harmonic
204 | 4 | 4-58 | 16631 | Phase B Current 16-th Harmonic | HAR16_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har57_In | channal 4 Current order 57 harmonic
205 | 4 | 4-59 | 16632 | Phase B Current 17-th Harmonic | HAR17_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har58_In | channal 4 Current order 58 harmonic
206 | 4 | 4-60 | 16633 | Phase B Current 18-th Harmonic | HAR18_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har59_In | channal 4 Current order 59 harmonic
207 | 4 | 4-61 | 16634 | Phase B Current 19-th Harmonic | HAR19_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har60_In | channal 4 Current order 60 harmonic
208 | 4 | 4-62 | 16635 | Phase B Current 20-th Harmonic | HAR20_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har61_In | channal 4 Current order 61 harmonic
209 | 4 | 4-63 | 16636 | Phase B Current 21-th Harmonic | HAR21_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har62_In | channal 4 Current order 62 harmonic
210 | 4 | 4-64 | 16637 | Phase B Current 22-th Harmonic | HAR22_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Har63_In | channal 4 Current order 63 harmonic
211 | 4 | 4-65 | 16638 | Phase B Current 23-th Harmonic | HAR23_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_Freq_Hz | Independent Channal System Frequency
212 | 4 | 4-66 | 16639 | Phase B Current 24-th Harmonic | HAR24_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_V1 | Independent Channal 1 Voltage
213 | 4 | 4-67 | 16640 | Phase B Current 25-th Harmonic | HAR25_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_V2 | Independent Channal 2 Voltage
214 | 4 | 4-68 | 16641 | Phase B Current 26-th Harmonic | HAR26_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_V3 | Independent Channal 3 Voltage
215 | 4 | 4-69 | 16642 | Phase B Current 27-th Harmonic | HAR27_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_Vnavg_V | Independent average Line-Netural Voltage
216 | 4 | 4-70 | 16643 | Phase B Current 28-th Harmonic | HAR28_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_V12 | Channal 12 Voltage
217 | 4 | 4-71 | 16644 | Phase B Current 29-th Harmonic | HAR29_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_V23 | Channal 23 Voltage
218 | 4 | 4-72 | 16645 | Phase B Current 30-th Harmonic | HAR30_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_V31 | Channal 31 Voltage
219 | 4 | 4-73 | 16646 | Phase B Current 31-th Harmonic | HAR31_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_VIavg_V | Avg Independent Line-Line Voltage
220 | 4 | 4-74 | 16647 | Phase B Current Odd THD | OTHD_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 9-13-14 | THD | THD | THD | THD | THD | THD | THD | OTHD_Ib | Ind_I1 | Independent Channal 1 Current
221 | 4 | 4-75 | 16648 | Phase B Current Even THD | ETHD_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 9-13-14 | THD | THD | THD | THD | THD | THD | THD | ETHD_Ib | Ind_I2 | Independent Channal 2 Current
222 | 4 | 4-76 | 16649 | Phase B Current K Factor | KF_I_b_% | % | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 9 | 9-13-14 | THD | THD | THD | THD | THD | THD | THD | KF_Ib | Ind_I3 | Independent Channal 3 Current
223 | 4 | 4-77 | 16650 | Phase C Current 2-th Harmonic | HAR2_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_I4 | Independent Channal 4 Current
224 | 4 | 4-78 | 16651 | Phase C Current 3-th Harmonic | HAR3_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_I_Sum1 | Current for Independent Channal 1 Summation 1
225 | 4 | 4-79 | 16652 | Phase C Current 4-th Harmonic | HAR4_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_I_Sum2 | Current for Independent Channal 1 Summation 2
226 | 4 | 4-80 | 16653 | Phase C Current 5-th Harmonic | HAR5_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_P1 | Independent Channal 1 Active Power
227 | 4 | 4-81 | 16654 | Phase C Current 6-th Harmonic | HAR6_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_P2 | Independent Channal 2 Active Power
228 | 4 | 4-82 | 16655 | Phase C Current 7-th Harmonic | HAR7_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_P3 | Independent Channal 3 Active Power
229 | 4 | 4-83 | 16656 | Phase C Current 8-th Harmonic | HAR8_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_P4 | Independent Channal 4 Active Power
230 | 4 | 4-84 | 16657 | Phase C Current 9-th Harmonic | HAR9_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_P_Sum1 | Active Power for Independent Channal Summation 1
231 | 4 | 4-85 | 16658 | Phase C Current 10-th Harmonic | HAR10_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_P_Sum2 | Active Power for Independent Channal Summation 2
232 | 4 | 4-86 | 16659 | Phase C Current 11-th Harmonic | HAR11_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_Q1 | Independent Channal 1 Reactive Power
233 | 4 | 4-87 | 16660 | Phase C Current 12-th Harmonic | HAR12_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_Q2 | Independent Channal 2 Reactive Power
234 | 4 | 4-88 | 16661 | Phase C Current 13-th Harmonic | HAR13_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_Q3 | Independent Channal 3 Reactive Power
235 | 4 | 4-89 | 16662 | Phase C Current 14-th Harmonic | HAR14_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_Q4 | Independent Channal 4 Reactive Power
236 | 4 | 4-90 | 16663 | Phase C Current 15-th Harmonic | HAR15_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_Q_Sum1 | Reactive Power for Independent Channal Summation 1
237 | 4 | 4-91 | 16664 | Phase C Current 16-th Harmonic | HAR16_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_Q_Sum2 | Reactive Power for Independent Channal Summation 2
238 | 4 | 4-92 | 16665 | Phase C Current 17-th Harmonic | HAR17_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_S1 | Independent Channal 1 Apparent Power
239 | 4 | 4-93 | 16666 | Phase C Current 18-th Harmonic | HAR18_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_S2 | Independent Channal 2 Apparent Power
240 | 4 | 4-94 | 16667 | Phase C Current 19-th Harmonic | HAR19_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_S3 | Independent Channal 3 Apparent Power
241 | 4 | 4-95 | 16668 | Phase C Current 20-th Harmonic | HAR20_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_S4 | Independent Channal 4 Apparent Power
242 | 4 | 4-96 | 16669 | Phase C Current 21-th Harmonic | HAR21_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_S_Sum1 | Apparent Power for Independent Channal Summation 1
243 | 4 | 4-97 | 16670 | Phase C Current 22-th Harmonic | HAR22_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_S_Sum2 | Apparent Power for Independent Channal Summation 2
244 | 4 | 4-98 | 16671 | Phase C Current 23-th Harmonic | HAR23_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_PF1 | Independent Channal 1 Power Factor
245 | 4 | 4-99 | 16672 | Phase C Current 24-th Harmonic | HAR24_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_PF2 | Independent Channal 2 Power Factor
246 | 4 | 4-100 | 16673 | Phase C Current 25-th Harmonic | HAR25_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_PF3 | Independent Channal 3 Power Factor
247 | 4 | 4-101 | 16674 | Phase C Current 26-th Harmonic | HAR26_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_PF4 | Independent Channal 4 Power Factor
248 | 4 | 4-102 | 16675 | Phase C Current 27-th Harmonic | HAR27_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_PF_Sum1 | Power Factor for Independent Channal Summation 1
249 | 4 | 4-103 | 16676 | Phase C Current 28-th Harmonic | HAR28_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_PF_Sum2 | Power Factor for Independent Channal Summation 2
250 | 4 | 4-104 | 16677 | Phase C Current 29-th Harmonic | HAR29_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_LN1 | Independent Channel 1 LN (L/C/R)
251 | 4 | 4-105 | 16678 | Phase C Current 30-th Harmonic | HAR30_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_LN2 | Independent Channel 2 LN (L/C/R)
252 | 4 | 4-106 | 16679 | Phase C Current 31-th Harmonic | HAR31_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | Ind_LN3 | IndependentChannel 3 LN (L/C/R)
253 | 4 | 4-107 | 16680 | Phase C Current Odd THD | OTHD_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | OTHD_Ic | Ind_LN4 | Independent Channel 4 LN (L/C/R)
254 | 4 | 4-108 | 16681 | Phase C Current Even THD | ETHD_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | ETHD_Ic | Ind_LN_Sum1 | Load Type for Independent Channal Summation 1
255 | 4 | 4-109 | 16682 | Phase C Current K Factor | KF_I_c_% | % | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 9 | 13-14 | THD | THD | THD | THD | THD | THD | THD | KF_Ic | Ind_LN_Sum2 | Load Type for Independent Channal Summation 2
256 | 5 | 5-1 | 17044 | Real part of Voltage Positive Sequence | SEQ_POS_REAL_V |  | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_POS_REAL_Va | EP1_IMP_kWh | Import Active Energy for Independent Channal 1
257 | 5 | 5-2 | 17045 | Imag part of Voltage Postive Sequence | SEQ_POS_IMG_V |  | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_POS_IMG_Va | EP2_IMP_kWh | Import Active Energy for Independent Channal 2
258 | 5 | 5-3 | 17046 | Real part of Voltage Negative Sequence | SEQ_NEG_REAL_V |  | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_NEG_REAL_Va | EP3_IMP_kWh | Import Active Energy for Independent Channal 3
259 | 5 | 5-4 | 17047 | Imag part of Voltage Negative Sequence | SEQ_NEG_IMG_V |  | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_NEG_IMG_Va | EP4_IMP_kWh | Import Active Energy for Independent Channal 4
260 | 5 | 5-5 | 17048 | Real part of Voltage Zero Sequence | SEQ_ZERO_REAL_V |  | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_ZERO_REAL_Va | EP_Sum1_IMP_kWh | Import Active Energy for Independent Channal Summation 1
261 | 5 | 5-6 | 17049 | Imag part of Voltage Zero Sequence | SEQ_ZERO_IMG_V |  | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_ZERO_IMG_Va | EP_Sum2_IMP_kWh | Import Active Energy for Independent Channal Summation 2
262 | 5 | 5-7 | 17050 | Real part of Current Positive Sequence | SEQ_POS_REAL_I |  | int16 | 12 | R | 1 | 0.001 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_POS_REAL_Ia | EP1_EXP_kWh | Export Active Energy for Independent Channal 1
263 | 5 | 5-8 | 17051 | Imag part of Current Postive Sequence | SEQ_POS_IMG_I |  | int16 | 12 | R | 1 | 0.001 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_POS_IMG_Ia | EP2_EXP_kWh | Export Active Energy for Independent Channal 2
264 | 5 | 5-9 | 17052 | Real part of Current Negative Sequence | SEQ_NEG_REAL_I |  | int16 | 12 | R | 1 | 0.001 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_NEG_REAL_Ia | EP3_EXP_kWh | Export Active Energy for Independent Channal 3
265 | 5 | 5-10 | 17053 | Imag part of Current Negative Sequence | SEQ_NEG_IMG_I |  | int16 | 12 | R | 1 | 0.001 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_NEG_IMG_Ia | EP4_EXP_kWh | Export Active Energy for Independent Channal 4
266 | 5 | 5-11 | 17054 | Real part of Current Zero Sequence | SEQ_ZERO_REAL_I |  | int16 | 12 | R | 1 | 0.001 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_ZERO_REAL_Ia | EP_Sum1_EXP_kWh | Export Active Energy for Independent Channal Summation 1
267 | 5 | 5-12 | 17055 | Imag part of Current Zero Sequence | SEQ_ZERO_IMG_I |  | int16 | 12 | R | 1 | 0.001 | 1 | [5 empty] | 11 | 13-14 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | SEQ_ZERO_IMG_Ia | EP_Sum2_EXP_kWh | Export Active Energy for Independent Channal Summation 2
268 | 5 | 5-13 | 17056 | Phase Angle of V2 to V1 | ANG_VLN_b | ° | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ang_Vb | EP_Sum1_TOTAL_kWh | Total Active Energy for Independent Channal Summation 1
269 | 5 | 5-14 | 17057 | Phase Angle of V3 to V1 | ANG_VLN_c | ° | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ang_Vc | EP_Sum2_TOTAL_kWh | Total Active Energy for Independent Channal Summation 2
270 | 5 | 5-15 | 17058 | Phase Angle of Phase A Current to V1 | ANG_I_a | ° | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ang_Ia | EP_Sum1_NET_kWh | Net Active Energy for Independent Channal Summation 1
271 | 5 | 5-16 | 17059 | Phase Angle of Phase B Current to V1 | ANG_I_b | ° | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ang_Ib | EP_Sum2_NET_kWh | Net Active Energy for Independent Channal Summation 2
272 | 5 | 5-17 | 17060 | Phase Angle of Phase C Current to V1 | ANG_I_c | ° | int16 | 12 | R | 1 | 0.1 | 1 | [5 empty] | 6 | 13-14 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ang_Ic | EQ1_IMP_kvarh | Import Reactive Energy for Independent Channal 1
273 | 6 | 6-1 | 17664 | Phase A Voltage 32-th Harmonic | HAR32_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ2_IMP_kvarh | Import Reactive Energy for Independent Channal 2
274 | 6 | 6-2 | 17665 | Phase A Voltage 33-th Harmonic | HAR33_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ3_IMP_kvarh | Import Reactive Energy for Independent Channal 3
275 | 6 | 6-3 | 17666 | Phase A Voltage 34-th Harmonic | HAR34_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ4_IMP_kvarh | Import Reactive Energy for Independent Channal 4
276 | 6 | 6-4 | 17667 | Phase A Voltage 35-th Harmonic | HAR35_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ_Sum1_IMP_kvarh | Import Reactive Energy for Independent Channal Summation 1
277 | 6 | 6-5 | 17668 | Phase A Voltage 36-th Harmonic | HAR36_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ_Sum2_IMP_kvarh | Import Reactive Energy for Independent Channal Summation 2
278 | 6 | 6-6 | 17669 | Phase A Voltage 37-th Harmonic | HAR37_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ1_EXP_kvarh | Export Active Energy for Independent Channal 1
279 | 6 | 6-7 | 17670 | Phase A Voltage 38-th Harmonic | HAR38_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ2_EXP_kvarh | Export Active Energy for Independent Channal 2
280 | 6 | 6-8 | 17671 | Phase A Voltage 39-th Harmonic | HAR39_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ3_EXP_kvarh | Export Active Energy for Independent Channal 3
281 | 6 | 6-9 | 17672 | Phase A Voltage 40-th Harmonic | HAR40_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ4_EXP_kvarh | Export Active Energy for Independent Channal 4
282 | 6 | 6-10 | 17673 | Phase A Voltage 41-th Harmonic | HAR41_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ_Sum1_EXP_kvarh | Export Active Energy for Independent Channal Summation 1
283 | 6 | 6-11 | 17674 | Phase A Voltage 42-th Harmonic | HAR42_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ_Sum2_EXP_kvarh | Export Active Energy for Independent Channal Summation 2
284 | 6 | 6-12 | 17675 | Phase A Voltage 43-th Harmonic | HAR43_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ_Sum1_TOTAL_kvarh | Total Active Energy for Independent Channal Summation 1
285 | 6 | 6-13 | 17676 | Phase A Voltage 44-th Harmonic | HAR44_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ_Sum2_TOTAL_kvarh | Total Active Energy for Independent Channal Summation 2
286 | 6 | 6-14 | 17677 | Phase A Voltage 45-th Harmonic | HAR45_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ_Sum1_NET_kvarh | Net Active Energy for Independent Channal Summation 1
287 | 6 | 6-15 | 17678 | Phase A Voltage 46-th Harmonic | HAR46_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | EQ_Sum2_NET_kvarh | Net Active Energy for Independent Channal Summation 2
288 | 6 | 6-16 | 17679 | Phase A Voltage 47-th Harmonic | HAR47_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | ES1_kVAh | Apparent Energy for Independent Channal 1
289 | 6 | 6-17 | 17680 | Phase A Voltage 48-th Harmonic | HAR48_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | ES2_kVAh | Apparent Energy for Independent Channal 2
290 | 6 | 6-18 | 17681 | Phase A Voltage 49-th Harmonic | HAR49_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | ES3_kVAh | Apparent Energy for Independent Channal 3
291 | 6 | 6-19 | 17682 | Phase A Voltage 50-th Harmonic | HAR50_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | ES4_kVAh | Apparent Energy for Independent Channal 4
292 | 6 | 6-20 | 17683 | Phase A Voltage 51-th Harmonic | HAR51_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | ES_Sum1_kVAh | Apparent Energy for Independent Channal Summation 1
293 | 6 | 6-21 | 17684 | Phase A Voltage 52-th Harmonic | HAR52_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | ES_Sum2_kVAh | Apparent Energy for Independent Channal Summation 2
294 | 6 | 6-22 | 17685 | Phase A Voltage 53-th Harmonic | HAR53_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_P1_kW | Active Power Demand for Independent Channal 1
295 | 6 | 6-23 | 17686 | Phase A Voltage 54-th Harmonic | HAR54_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_P2_kW | Active Power Demand for Independent Channal 2
296 | 6 | 6-24 | 17687 | Phase A Voltage 55-th Harmonic | HAR55_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_P3_kW | Active Power Demand for Independent Channal 3
297 | 6 | 6-25 | 17688 | Phase A Voltage 56-th Harmonic | HAR56_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_P4_kW | Active Power Demand for Independent Channal 4
298 | 6 | 6-26 | 17689 | Phase A Voltage 57-th Harmonic | HAR57_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_P_Sum1_kW | Active Power Demand for Independent Channal Summation 1
299 | 6 | 6-27 | 17690 | Phase A Voltage 58-th Harmonic | HAR58_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_P_Sum2_kW | Active Power Demand for Independent Channal Summation 2
300 | 6 | 6-28 | 17691 | Phase A Voltage 59-th Harmonic | HAR59_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_Q1_kvar | Reactive Power Demand for Independent Channal 1
301 | 6 | 6-29 | 17692 | Phase A Voltage 60-th Harmonic | HAR60_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_Q2_kvar | Reactive Power Demand for Independent Channal 2
302 | 6 | 6-30 | 17693 | Phase A Voltage 61-th Harmonic | HAR61_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_Q3_kvar | Reactive Power Demand for Independent Channal 3
303 | 6 | 6-31 | 17694 | Phase A Voltage 62-th Harmonic | HAR62_V_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_Q4_kvar | Reactive Power Demand for Independent Channal 4
304 | 6 | 6-32 | 17695 | Phase B Voltage 32-th Harmonic | HAR32_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_Q_Sum1_kvar | Reactive Power Demand for Independent Channal Summation 1
305 | 6 | 6-33 | 17696 | Phase B Voltage 33-th Harmonic | HAR33_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_Q_Sum2_kvar | Reactive Power Demand for Independent Channal Summation 2
306 | 6 | 6-34 | 17697 | Phase B Voltage 34-th Harmonic | HAR34_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_S1_kVA | Apparent Power Demand for Independent Channal 1
307 | 6 | 6-35 | 17698 | Phase B Voltage 35-th Harmonic | HAR35_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_S2_kVA | Apparent Power Demand for Independent Channal 2
308 | 6 | 6-36 | 17699 | Phase B Voltage 36-th Harmonic | HAR36_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_S3_kVA | Apparent Power Demand for Independent Channal 3
309 | 6 | 6-37 | 17700 | Phase B Voltage 37-th Harmonic | HAR37_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_S4_kVA | Apparent Power Demand for Independent Channal 4
310 | 6 | 6-38 | 17701 | Phase B Voltage 38-th Harmonic | HAR38_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_S_Sum1_kVA | Apparent Power Demand for Independent Channel Summation 1
311 | 6 | 6-39 | 17702 | Phase B Voltage 39-th Harmonic | HAR39_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_S_Sum2_kVA | Apparent Power Demand for Independent Channel Summation 2
312 | 6 | 6-40 | 17703 | Phase B Voltage 40-th Harmonic | HAR40_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics |  | DMD_I4_A | Current Demand for Independent Channal 4
313 | 6 | 6-41 | 17704 | Phase B Voltage 41-th Harmonic | HAR41_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
314 | 6 | 6-42 | 17705 | Phase B Voltage 42-th Harmonic | HAR42_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
315 | 6 | 6-43 | 17706 | Phase B Voltage 43-th Harmonic | HAR43_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
316 | 6 | 6-44 | 17707 | Phase B Voltage 44-th Harmonic | HAR44_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
317 | 6 | 6-45 | 17708 | Phase B Voltage 45-th Harmonic | HAR45_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
318 | 6 | 6-46 | 17709 | Phase B Voltage 46-th Harmonic | HAR46_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
319 | 6 | 6-47 | 17710 | Phase B Voltage 47-th Harmonic | HAR47_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
320 | 6 | 6-48 | 17711 | Phase B Voltage 48-th Harmonic | HAR48_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
321 | 6 | 6-49 | 17712 | Phase B Voltage 49-th Harmonic | HAR49_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
322 | 6 | 6-50 | 17713 | Phase B Voltage 50-th Harmonic | HAR50_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
323 | 6 | 6-51 | 17714 | Phase B Voltage 51-th Harmonic | HAR51_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
324 | 6 | 6-52 | 17715 | Phase B Voltage 52-th Harmonic | HAR52_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
325 | 6 | 6-53 | 17716 | Phase B Voltage 53-th Harmonic | HAR53_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
326 | 6 | 6-54 | 17717 | Phase B Voltage 54-th Harmonic | HAR54_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
327 | 6 | 6-55 | 17718 | Phase B Voltage 55-th Harmonic | HAR55_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
328 | 6 | 6-56 | 17719 | Phase B Voltage 56-th Harmonic | HAR56_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
329 | 6 | 6-57 | 17720 | Phase B Voltage 57-th Harmonic | HAR57_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
330 | 6 | 6-58 | 17721 | Phase B Voltage 58-th Harmonic | HAR58_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
331 | 6 | 6-59 | 17722 | Phase B Voltage 59-th Harmonic | HAR59_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
332 | 6 | 6-60 | 17723 | Phase B Voltage 60-th Harmonic | HAR60_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
333 | 6 | 6-61 | 17724 | Phase B Voltage 61-th Harmonic | HAR61_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
334 | 6 | 6-62 | 17725 | Phase B Voltage 62-th Harmonic | HAR62_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
335 | 6 | 6-63 | 17726 | Phase B Voltage 63-th Harmonic | HAR63_V_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
336 | 6 | 6-64 | 17727 | Phase C Voltage 32-th Harmonic | HAR32_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
337 | 6 | 6-65 | 17728 | Phase C Voltage 33-th Harmonic | HAR33_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
338 | 6 | 6-66 | 17729 | Phase C Voltage 34-th Harmonic | HAR34_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
339 | 6 | 6-67 | 17730 | Phase C Voltage 35-th Harmonic | HAR35_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
340 | 6 | 6-68 | 17731 | Phase C Voltage 36-th Harmonic | HAR36_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
341 | 6 | 6-69 | 17732 | Phase C Voltage 37-th Harmonic | HAR37_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
342 | 6 | 6-70 | 17733 | Phase C Voltage 38-th Harmonic | HAR38_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
343 | 6 | 6-71 | 17734 | Phase C Voltage 39-th Harmonic | HAR39_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
344 | 6 | 6-72 | 17735 | Phase C Voltage 40-th Harmonic | HAR40_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
345 | 6 | 6-73 | 17736 | Phase C Voltage 41-th Harmonic | HAR41_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
346 | 6 | 6-74 | 17737 | Phase C Voltage 42-th Harmonic | HAR42_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
347 | 6 | 6-75 | 17738 | Phase C Voltage 43-th Harmonic | HAR43_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
348 | 6 | 6-76 | 17739 | Phase C Voltage 44-th Harmonic | HAR44_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
349 | 6 | 6-77 | 17740 | Phase C Voltage 45-th Harmonic | HAR45_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
350 | 6 | 6-78 | 17741 | Phase C Voltage 46-th Harmonic | HAR46_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
351 | 6 | 6-79 | 17742 | Phase C Voltage 47-th Harmonic | HAR47_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
352 | 6 | 6-80 | 17743 | Phase C Voltage 48-th Harmonic | HAR48_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
353 | 6 | 6-81 | 17744 | Phase C Voltage 49-th Harmonic | HAR49_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
354 | 6 | 6-82 | 17745 | Phase C Voltage 50-th Harmonic | HAR50_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
355 | 6 | 6-83 | 17746 | Phase C Voltage 51-th Harmonic | HAR51_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
356 | 6 | 6-84 | 17747 | Phase C Voltage 52-th Harmonic | HAR52_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
357 | 6 | 6-85 | 17748 | Phase C Voltage 53-th Harmonic | HAR53_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
358 | 6 | 6-86 | 17749 | Phase C Voltage 54-th Harmonic | HAR54_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
359 | 6 | 6-87 | 17750 | Phase C Voltage 55-th Harmonic | HAR55_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
360 | 6 | 6-88 | 17751 | Phase C Voltage 56-th Harmonic | HAR56_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
361 | 6 | 6-89 | 17752 | Phase C Voltage 57-th Harmonic | HAR57_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
362 | 6 | 6-90 | 17753 | Phase C Voltage 58-th Harmonic | HAR58_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
363 | 6 | 6-91 | 17754 | Phase C Voltage 59-th Harmonic | HAR59_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
364 | 6 | 6-92 | 17755 | Phase C Voltage 60-th Harmonic | HAR60_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
365 | 6 | 6-93 | 17756 | Phase C Voltage 61-th Harmonic | HAR61_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
366 | 6 | 6-94 | 17757 | Phase C Voltage 62-th Harmonic | HAR62_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
367 | 6 | 6-95 | 17758 | Phase C Voltage 63-th Harmonic | HAR63_V_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
368 | 6 | 6-96 | 17759 | Phase A Current 32-th Harmonic | HAR32_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
369 | 6 | 6-97 | 17760 | Phase A Current 33-th Harmonic | HAR33_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
370 | 6 | 6-98 | 17761 | Phase A Current 34-th Harmonic | HAR34_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
371 | 6 | 6-99 | 17762 | Phase A Current 35-th Harmonic | HAR35_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
372 | 6 | 6-100 | 17763 | Phase A Current 36-th Harmonic | HAR36_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
373 | 7 | 7-1 | 17764 | Phase A Current 37-th Harmonic | HAR37_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
374 | 7 | 7-2 | 17765 | Phase A Current 38-th Harmonic | HAR38_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
375 | 7 | 7-3 | 17766 | Phase A Current 39-th Harmonic | HAR39_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
376 | 7 | 7-4 | 17767 | Phase A Current 40-th Harmonic | HAR40_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
377 | 7 | 7-5 | 17768 | Phase A Current 41-th Harmonic | HAR41_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
378 | 7 | 7-6 | 17769 | Phase A Current 42-th Harmonic | HAR42_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
379 | 7 | 7-7 | 17770 | Phase A Current 43-th Harmonic | HAR43_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
380 | 7 | 7-8 | 17771 | Phase A Current 44-th Harmonic | HAR44_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
381 | 7 | 7-9 | 17772 | Phase A Current 45-th Harmonic | HAR45_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
382 | 7 | 7-10 | 17773 | Phase A Current 46-th Harmonic | HAR46_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
383 | 7 | 7-11 | 17774 | Phase A Current 47-th Harmonic | HAR47_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
384 | 7 | 7-12 | 17775 | Phase A Current 48-th Harmonic | HAR48_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
385 | 7 | 7-13 | 17776 | Phase A Current 49-th Harmonic | HAR49_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
386 | 7 | 7-14 | 17777 | Phase A Current 50-th Harmonic | HAR50_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
387 | 7 | 7-15 | 17778 | Phase A Current 51-th Harmonic | HAR51_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
388 | 7 | 7-16 | 17779 | Phase A Current 52-th Harmonic | HAR52_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
389 | 7 | 7-17 | 17780 | Phase A Current 53-th Harmonic | HAR53_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
390 | 7 | 7-18 | 17781 | Phase A Current 54-th Harmonic | HAR54_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
391 | 7 | 7-19 | 17782 | Phase A Current 55-th Harmonic | HAR55_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
392 | 7 | 7-20 | 17783 | Phase A Current 56-th Harmonic | HAR56_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
393 | 7 | 7-21 | 17784 | Phase A Current 57-th Harmonic | HAR57_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
394 | 7 | 7-22 | 17785 | Phase A Current 58-th Harmonic | HAR58_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
395 | 7 | 7-23 | 17786 | Phase A Current 59-th Harmonic | HAR59_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
396 | 7 | 7-24 | 17787 | Phase A Current 60-th Harmonic | HAR60_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
397 | 7 | 7-25 | 17788 | Phase A Current 61-th Harmonic | HAR61_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
398 | 7 | 7-26 | 17789 | Phase A Current 62-th Harmonic | HAR62_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
399 | 7 | 7-27 | 17790 | Phase A Current 63-th Harmonic | HAR63_I_a_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
400 | 7 | 7-28 | 17791 | Phase B Current 32-th Harmonic | HAR32_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
401 | 7 | 7-29 | 17792 | Phase B Current 33-th Harmonic | HAR33_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
402 | 7 | 7-30 | 17793 | Phase B Current 34-th Harmonic | HAR34_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
403 | 7 | 7-31 | 17794 | Phase B Current 35-th Harmonic | HAR35_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
404 | 7 | 7-32 | 17795 | Phase B Current 36-th Harmonic | HAR36_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
405 | 7 | 7-33 | 17796 | Phase B Current 37-th Harmonic | HAR37_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
406 | 7 | 7-34 | 17797 | Phase B Current 38-th Harmonic | HAR38_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
407 | 7 | 7-35 | 17798 | Phase B Current 39-th Harmonic | HAR39_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
408 | 7 | 7-36 | 17799 | Phase B Current 40-th Harmonic | HAR40_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
409 | 7 | 7-37 | 17800 | Phase B Current 41-th Harmonic | HAR41_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
410 | 7 | 7-38 | 17801 | Phase B Current 42-th Harmonic | HAR42_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
411 | 7 | 7-39 | 17802 | Phase B Current 43-th Harmonic | HAR43_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
412 | 7 | 7-40 | 17803 | Phase B Current 44-th Harmonic | HAR44_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
413 | 7 | 7-41 | 17804 | Phase B Current 45-th Harmonic | HAR45_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
414 | 7 | 7-42 | 17805 | Phase B Current 46-th Harmonic | HAR46_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
415 | 7 | 7-43 | 17806 | Phase B Current 47-th Harmonic | HAR47_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
416 | 7 | 7-44 | 17807 | Phase B Current 48-th Harmonic | HAR48_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
417 | 7 | 7-45 | 17808 | Phase B Current 49-th Harmonic | HAR49_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
418 | 7 | 7-46 | 17809 | Phase B Current 50-th Harmonic | HAR50_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
419 | 7 | 7-47 | 17810 | Phase B Current 51-th Harmonic | HAR51_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
420 | 7 | 7-48 | 17811 | Phase B Current 52-th Harmonic | HAR52_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
421 | 7 | 7-49 | 17812 | Phase B Current 53-th Harmonic | HAR53_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
422 | 7 | 7-50 | 17813 | Phase B Current 54-th Harmonic | HAR54_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
423 | 7 | 7-51 | 17814 | Phase B Current 55-th Harmonic | HAR55_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
424 | 7 | 7-52 | 17815 | Phase B Current 56-th Harmonic | HAR56_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
425 | 7 | 7-53 | 17816 | Phase B Current 57-th Harmonic | HAR57_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
426 | 7 | 7-54 | 17817 | Phase B Current 58-th Harmonic | HAR58_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
427 | 7 | 7-55 | 17818 | Phase B Current 59-th Harmonic | HAR59_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
428 | 7 | 7-56 | 17819 | Phase B Current 60-th Harmonic | HAR60_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
429 | 7 | 7-57 | 17820 | Phase B Current 61-th Harmonic | HAR61_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
430 | 7 | 7-58 | 17821 | Phase B Current 62-th Harmonic | HAR62_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
431 | 7 | 7-59 | 17822 | Phase B Current 63-th Harmonic | HAR63_I_b_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
432 | 7 | 7-60 | 17823 | Phase C Current 32-th Harmonic | HAR32_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
433 | 7 | 7-61 | 17824 | Phase C Current 33-th Harmonic | HAR33_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
434 | 7 | 7-62 | 17825 | Phase C Current 34-th Harmonic | HAR34_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
435 | 7 | 7-63 | 17826 | Phase C Current 35-th Harmonic | HAR35_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
436 | 7 | 7-64 | 17827 | Phase C Current 36-th Harmonic | HAR36_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
437 | 7 | 7-65 | 17828 | Phase C Current 37-th Harmonic | HAR37_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
438 | 7 | 7-66 | 17829 | Phase C Current 38-th Harmonic | HAR38_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
439 | 7 | 7-67 | 17830 | Phase C Current 39-th Harmonic | HAR39_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
440 | 7 | 7-68 | 17831 | Phase C Current 40-th Harmonic | HAR40_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
441 | 7 | 7-69 | 17832 | Phase C Current 41-th Harmonic | HAR41_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
442 | 7 | 7-70 | 17833 | Phase C Current 42-th Harmonic | HAR42_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
443 | 7 | 7-71 | 17834 | Phase C Current 43-th Harmonic | HAR43_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
444 | 7 | 7-72 | 17835 | Phase C Current 44-th Harmonic | HAR44_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
445 | 7 | 7-73 | 17836 | Phase C Current 45-th Harmonic | HAR45_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
446 | 7 | 7-74 | 17837 | Phase C Current 46-th Harmonic | HAR46_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
447 | 7 | 7-75 | 17838 | Phase C Current 47-th Harmonic | HAR47_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
448 | 7 | 7-76 | 17839 | Phase C Current 48-th Harmonic | HAR48_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
449 | 7 | 7-77 | 17840 | Phase C Current 49-th Harmonic | HAR49_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
450 | 7 | 7-78 | 17841 | Phase C Current 50-th Harmonic | HAR50_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
451 | 7 | 7-79 | 17842 | Phase C Current 51-th Harmonic | HAR51_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
452 | 7 | 7-80 | 17843 | Phase C Current 52-th Harmonic | HAR52_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
453 | 7 | 7-81 | 17844 | Phase C Current 53-th Harmonic | HAR53_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
454 | 7 | 7-82 | 17845 | Phase C Current 54-th Harmonic | HAR54_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
455 | 7 | 7-83 | 17846 | Phase C Current 55-th Harmonic | HAR55_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
456 | 7 | 7-84 | 17847 | Phase C Current 56-th Harmonic | HAR56_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
457 | 7 | 7-85 | 17848 | Phase C Current 57-th Harmonic | HAR57_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
458 | 7 | 7-86 | 17849 | Phase C Current 58-th Harmonic | HAR58_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
459 | 7 | 7-87 | 17850 | Phase C Current 59-th Harmonic | HAR59_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
460 | 7 | 7-88 | 17851 | Phase C Current 60-th Harmonic | HAR60_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
461 | 7 | 7-89 | 17852 | Phase C Current 61-th Harmonic | HAR61_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
462 | 7 | 7-90 | 17853 | Phase C Current 62-th Harmonic | HAR62_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
463 | 7 | 7-91 | 17854 | Phase C Current 63-th Harmonic | HAR63_I_c_% | % | int16 | 12 | R | 1 | 0.01 | 1 | [5 empty] | 10 | [7 empty] | harmonics
464 | 8 | 8-1 | 17952 | Phase A Import Active Energy | EP_IMP_a_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EPa_IMP_kWh
465 | 8 | 8-2 | 17954 | Phase A Export Active Energy | EP_EXP_a_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EPa_EXP_kWh
466 | 8 | 8-3 | 17956 | Phase B Import Active Energy | EP_IMP_b_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EPb_IMP_kWh
467 | 8 | 8-4 | 17958 | Phase B Export Active Energy | EP_EXP_b_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EPb_EXP_kWh
468 | 8 | 8-5 | 17960 | Phase C Import Active Energy | EP_IMP_c_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EPc_IMP_kWh
469 | 8 | 8-6 | 17962 | Phase C Export Active Energy | EP_EXP_c_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EPc_EXP_kWh
470 | 8 | 8-7 | 17964 | Phase A Import Reactive Energy | EQ_IMP_a_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EQa_IMP_kvarh
471 | 8 | 8-8 | 17966 | Phase A Export Reactive Energy | EQ_EXP_a_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EQa_EXP_kvarh
472 | 8 | 8-9 | 17968 | Phase B Import Reactive Energy | EQ_IMP_b_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EQb_IMP_kvarh
473 | 8 | 8-10 | 17970 | Phase B Export Reactive Energy | EQ_EXP_b_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EQb_EXP_kvarh
474 | 8 | 8-11 | 17972 | Phase C Import Reactive Energy | EQ_IMP_c_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EQc_IMP_kvarh
475 | 8 | 8-12 | 17974 | Phase C Export Reactive Energy | EQ_EXP_c_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | EQc_EXP_kvarh
476 | 8 | 8-13 | 17976 | Phase A Apparent Energy | ES_a_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | ESa_kVAh
477 | 8 | 8-14 | 17978 | Phase B Apparent Energy | ES_b_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | ESb_kVAh
478 | 8 | 8-15 | 17980 | Phase C Apparent Energy | ES_c_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 | 1 | 1 |  | 3 | 4 |  | 8-13 | 13 | energy | energy | energy | energy | energy | energy | energy | ESc_kVAh
479 | 9 | 9-1 | 4093 | Nominal Frequency | Conf_NominalFreq |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
480 | 9 | 9-2 | 4094 | Channel 1 Communication Protocol | Conf_Ch1_Proto |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
481 | 9 | 9-3 | 4095 | Channel 1 Parity | Conf_Ch1_Parity |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
482 | 9 | 9-4 | 4096 | Password | Conf_Password |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
483 | 9 | 9-5 | 4097 | Channel 1 Address | Conf_Ch1_Addr |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
484 | 9 | 9-6 | 4098 | Channel 1 Baud Rate | Conf_Ch1_Baud |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
485 | 9 | 9-7 | 4099 | Service Configuration | Conf_ServiceConfig |  | uint32 | 12 | R/W | 2 | 1 | [5 empty] | 5
486 | 9 | 9-8 | 4101 | PT1 | Conf_PT1 |  | uint32 | 12 | R/W | 2 | 0.1 | [5 empty] | 5
487 | 9 | 9-9 | 4103 | PT2 | Conf_PT2 |  | uint16 | 12 | R/W | 1 | 0.1 | [5 empty] | 5
488 | 9 | 9-10 | 4104 | CT1 | Conf_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
489 | 9 | 9-11 | 4105 | CT2 | Conf_CT2 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
490 | 9 | 9-12 | 4106 | KWh Pulse Constant | Conf_Ep_PulseConst |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
491 | 9 | 9-13 | 4107 | Kvarh Pulse Constant | Conf_Eq_PulseConst |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
492 | 9 | 9-14 | 4108 | LCD Backlight Time | Conf_Backlight_Time |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
493 | 9 | 9-15 | 4109 | Demand Window | Conf_Dmd_Window |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
494 | 9 | 9-16 | 4110 | Demand Method | Conf_Dmd_Method |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
495 | 9 | 9-17 | 4111 | Clear Demand | Conf_Clr_Dmd |  | uint16 | 12 | R/W | 1 | 1
496 | 9 | 9-18 | 4112 | Clear Max/Min | Conf_Clr_MaxMin |  | uint16 | 12 | R/W | 1 | 1
497 | 9 | 9-19 | 4113 | Clear Run Hours | Conf_Clr_RunHours |  | uint16 | 12 | R/W | 1 | 1
498 | 9 | 9-20 | 4114 | Current I1 Direction | Conf_I1_Dir |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
499 | 9 | 9-21 | 4115 | Current I2 Direction | Conf_I2_Dir |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
500 | 9 | 9-22 | 4116 | Current I3 Direction | Conf_I3_Dir |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
501 | 9 | 9-23 | 4117 | VAR/PF Convention | Conf_CalcMethod_VarPF |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
502 | 9 | 9-24 | 4118 | Clear Energy | Conf_Clr_Egy |  | uint16 | 12 | R/W | 1 | 1
503 | 9 | 9-25 | 4119 | Energy Calculation Method | Conf_CalcMethod_Energy |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
504 | 9 | 9-26 | 4120 | Reactive Power Calculation Method | Conf_CalcMethod_Q |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
505 | 9 | 9-27 | 4121 | Energy Reading Primary/Secondary | Conf_DispFormat_Energy |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
506 | 9 | 9-28 | 4122 | Reset Ethernet Module | Conf_Rst_EthernetModule |  | uint16 | 12 | R/W | 1 | 1
507 | 9 | 9-29 | 4123 | Enable SOE | Conf_Enable_SOE |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
508 | 9 | 9-30 | 4124 | Clear Pulse Counter | Conf_Clr_PulseCnt |  | uint16 | 12 | R/W | 1 | 1
509 | 9 | 9-31 | 4125 | Basic Reading Display Primary/Secondary | Conf_DispFormat_RealTime |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
510 | 9 | 9-32 | 4126 | Non-Standard Content Seal Option | Conf_Seal_Option |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
511 | 9 | 9-33 | 4127 | Sealing Status | Info_Seal_Status |  | uint16 | 12 | R | 1 | 1 | [5 empty] | 5
512 | 9 | 9-34 | 4128 | Demand Sub-Interval | Conf_Dmd_SubInterval |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
513 | 9 | 9-35 | 4129 | Clear Alarm Records | Conf_Clr_Alarm |  | uint16 | 12 | R/W | 1 | 1
514 | 9 | 9-36 | 4130 | CT41 | Conf_CT41 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
515 | 9 | 9-37 | 4131 | CT42 | Conf_CT42 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
516 | 9 | 9-38 | 4132 | JiGuan Customized PT | Conf_JG_PT |  | uint16 | 12 | R/W | 1 | 1
517 | 9 | 9-39 | 4133 | JiGuan Customized CT | Conf_JG_CT |  | uint16 | 12 | R/W | 1 | 1
518 | 9 | 9-40 | 4134 | Restore Factory Setting | Conf_Restore_FactorySetting |  | uint16 | 12 | R/W | 1 | 1
519 | 9 | 9-41 | 4135 | Line N Current Method | Conf_In_Method |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
520 | 9 | 9-42 | 4136 | Modbus Gateway Enable | Conf_Enable_ModbusGateway |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
521 | 9 | 9-43 | 4137 | Reserve1 | Conf_Rsv1 |  | uint16 | 12 | R/W | 1 | 1
522 | 9 | 9-44 | 4138 | Reserve2 | Conf_Rsv2 |  | uint16 | 12 | R/W | 1 | 1
523 | 9 | 9-45 | 4139 | Reserve3 | Conf_Rsv3 |  | uint16 | 12 | R/W | 1 | 1
524 | 9 | 9-46 | 4140 | Nominal Full Load Power | Conf_Nom_Full_Load_Power |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
525 | 9 | 9-47 | 4141 | Load Display Type | Conf_LoadDispType |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
526 | 9 | 9-48 | 4142 | System Status | Info_Sys_Status |  | uint16 | 12 | R | 1 | 1 | [5 empty] | 5
527 | 9 | 9-49 | 4143 | Channel 2 Baud Rate | Conf_Ch2_Baud |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
528 | 9 | 9-50 | 4144 | Channel 2 Parity | Conf_Ch2_Parity |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
529 | 9 | 9-51 | 4145 | Channel 2 Address | Conf_Ch2_Addr |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
530 | 9 | 9-52 | 4146 | Latest Alarm Group Number | Info_Alm_GroupNumber |  | uint16 | 12 | R | 1 | 1 | [5 empty] | 5
531 | 9 | 9-53 | 4147 | Latest SOE Record Group Number | Info_SOE_GroupNumber |  | uint16 | 12 | R | 1 | 1 | [5 empty] | 5
532 | 9 | 9-54 | 4148 | Run Hour | Info_RunHour |  | uint32 | 12 | R | 2 | 1 | [5 empty] | 5
533 | 9 | 9-55 | 4150 | Module Connection Status | Info_Module_Status |  | uint16 | 12 | R | 1 | 1 | [5 empty] | 5
534 | 9 | 9-56 | 4151 | Temperature (Not in Use) | Info_Old_Temperature |  | uint16 | 12 | R | 1 | 1
535 | 9 | 9-57 | 4152 | Channel 2 Communication Protocol | Conf_Ch2_Proto |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
536 | 9 | 9-58 | 4153 | Enable Downloading TOU Ten Year Configs | Conf_Enable_DL_TOU10YrConfigs |  | uint16 | 12 | R/W | 1 | 1
537 | 9 | 9-59 | 4154 | Clear Max Demand - Sharp Tariff | Conf_Clr_MaxDmd_Sharp |  | uint16 | 12 | R/W | 1 | 1
538 | 9 | 9-60 | 4155 | Clear Max Demand - Peak Tariff | Conf_Clr_MaxDmd_Peak |  | uint16 | 12 | R/W | 1 | 1
539 | 9 | 9-61 | 4156 | Clear Max Demand - Valley Tariff | Conf_Clr_MaxDmd_Valley |  | uint16 | 12 | R/W | 1 | 1
540 | 9 | 9-62 | 4157 | Clear Max Demand - Normal Tariff | Conf_Clr_MaxDmd_Norm |  | uint16 | 12 | R/W | 1 | 1
541 | 9 | 9-63 | 4158 | Clear Max Demand - All Tariffs | Conf_Clr_MaxDmd_All |  | uint16 | 12 | R/W | 1 | 1
542 | 9 | 9-64 | 4159 | Week | Conf_Week |  | uint16 | 12 | R/W | 1 | 1
543 | 9 | 9-65 | 4160 | Year | Conf_Year |  | uint16 | 12 | R/W | 1 | 1
544 | 9 | 9-66 | 4161 | Month | Conf_Month |  | uint16 | 12 | R/W | 1 | 1
545 | 9 | 9-67 | 4162 | Day | Conf_Day |  | uint16 | 12 | R/W | 1 | 1
546 | 9 | 9-68 | 4163 | Hour | Conf_Hr |  | uint16 | 12 | R/W | 1 | 1
547 | 9 | 9-69 | 4164 | Minute | Conf_Min |  | uint16 | 12 | R/W | 1 | 1
548 | 9 | 9-70 | 4165 | Second | Conf_Sec |  | uint16 | 12 | R/W | 1 | 1
549 | 13 | 13-1 | 61555 | Number of CT | Info_CT_Num |  | uint16 | 12 | R | 1 | 1 | [5 empty] | 5
550 | 14 | 14-1 | 61936 | CT2 Type | Info_CT2_Type |  | uint16 | 12 | R | 1 | 1 | [5 empty] | 5

## analysisUnits
analysisUnitId | analysisUnitTypeName
1 | threePhaseMeterAnalysis

## analysisParams
threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis
three_phase_realtime | three_phase_energy_demand | three_phase_thd | three_phase_harmonics | three_phase_sequence
VLN_a_V | EP_IMP_a_kWh | THD_V_a_% | HAR2_V_a_% | SEQ_POS_REAL_I
ANG_VLN_a | EQ_IMP_a_kvarh | OTHD_V_a_% | HAR3_V_a_% | SEQ_NEG_REAL_I
VLL_ab_V | EP_EXP_a_kWh | ETHD_V_a_% | HAR4_V_a_% | SEQ_ZERO_REAL_I
ANG_VLL_ab | EQ_EXP_a_kvarh | CF_V_a_% | HAR5_V_a_% | SEQ_POS_IMG_I
I_a_A | EP_NET_a_kWh | THD_I_a_% | HAR6_V_a_% | SEQ_NEG_IMG_I
ANG_I_a | EQ_NET_a_kvarh | OTHD_I_a_% | HAR7_V_a_% | SEQ_ZERO_IMG_I
P_a_kW | EP_TOTAL_a_kWh | ETHD_I_a_% | HAR8_V_a_% | SEQ_POS_REAL_V
Q_a_kvar | EQ_TOTAL_a_kvarh | TDD_I_a_% | HAR9_V_a_% | SEQ_NEG_REAL_V
S_a_kVA | ES_a_kVAh | CF_I_a_% | HAR10_V_a_% | SEQ_ZERO_REAL_V
LC_a | EP_IMP_b_kWh | KF_I_a_% | HAR11_V_a_% | SEQ_POS_IMG_V
PF_a | EQ_IMP_b_kvarh | THD_V_b_% | HAR12_V_a_% | SEQ_NEG_IMG_V
LEAD_PF_a | EP_EXP_b_kWh | OTHD_V_b_% | HAR13_V_a_% | SEQ_ZERO_IMG_V
LAG_PF_a | EQ_EXP_b_kvarh | ETHD_V_b_% | HAR14_V_a_% | UNBL_V_%
VLN_b_V | EP_NET_b_kWh | CF_V_b_% | HAR15_V_a_% | UNBL_I_%
ANG_VLN_b | EQ_NET_b_kvarh | THD_I_b_% | HAR16_V_a_% | SEQ_ZERO_RATIO_V_%
VLL_bc_V | EP_TOTAL_b_kWh | OTHD_I_b_% | HAR17_V_a_% | SEQ_ZERO_RATIO_I_%
ANG_VLL_bb | EQ_TOTAL_b_kvarh | ETHD_I_b_% | HAR18_V_a_%
I_b_A | ES_b_kVAh | TDD_I_b_% | HAR19_V_a_%
ANG_I_b | EP_IMP_c_kWh | CF_I_b_% | HAR20_V_a_%
P_b_kW | EQ_IMP_c_kvarh | KF_I_b_% | HAR21_V_a_%
Q_b_kvar | EP_EXP_c_kWh | THD_V_c_% | HAR22_V_a_%
S_b_kVA | EQ_EXP_c_kvarh | OTHD_V_c_% | HAR23_V_a_%
LC_b | EP_NET_c_kWh | ETHD_V_c_% | HAR24_V_a_%
PF_b | EQ_NET_c_kvarh | CF_V_c_% | HAR25_V_a_%
LEAD_PF_b | EP_TOTAL_c_kWh | THD_I_c_% | HAR26_V_a_%
LAG_PF_b | EQ_TOTAL_c_kvarh | OTHD_I_c_% | HAR27_V_a_%
VLN_c_V | ES_c_kVAh | ETHD_I_c_% | HAR28_V_a_%
ANG_VLN_c | EP_IMP_kWh | TDD_I_c_% | HAR29_V_a_%
VLL_ca_V | EQ_IMP_kvarh | CF_I_c_% | HAR30_V_a_%
ANG_VLL_cb | EP_EXP_kWh | KF_I_c_% | HAR31_V_a_%
I_c_A | EQ_EXP_kvarh | THD_V_avg_% | HAR32_V_a_%
ANG_I_c | EP_NET_kWh | OTHD_V_avg_% | HAR33_V_a_%
P_c_kW | EQ_NET_kvarh | ETHD_V_avg_% | HAR34_V_a_%
Q_c_kvar | EP_TOTAL_kWh | CF_V_avg_% | HAR35_V_a_%
S_c_kVA | EQ_TOTAL_kvarh | THD_I_avg_% | HAR36_V_a_%
LC_c | ES_kVAh | OTHD_I_avg_% | HAR37_V_a_%
PF_c | DMD_P_a_kW | ETHD_I_avg_% | HAR38_V_a_%
LEAD_PF_c | DMD_Q_a_kvar | TDD_I_avg_% | HAR39_V_a_%
LAG_PF_c | DMD_S_a_kVA | CF_I_avg_% | HAR40_V_a_%
VLN_avg_V | DMD_P_b_kW | KF_I_avg_% | HAR41_V_a_%
VLL_avg_V | DMD_Q_b_kvar |  | HAR42_V_a_%
I_avg_A | DMD_S_b_kVA |  | HAR43_V_a_%
LC_avg | DMD_P_c_kW |  | HAR44_V_a_%
I_n_A | DMD_Q_c_kvar |  | HAR45_V_a_%
P_kW | DMD_S_c_kVA |  | HAR46_V_a_%
Q_kvar | DMD_P_kW |  | HAR47_V_a_%
S_kVA | DMD_Q_kvar |  | HAR48_V_a_%
PF | DMD_S_kVA |  | HAR49_V_a_%
LEAD_PF |  |  | HAR50_V_a_%
LAG_PF |  |  | HAR51_V_a_%
FREQ_Hz |  |  | HAR52_V_a_%
HAR53_V_a_%
HAR54_V_a_%
HAR55_V_a_%
HAR56_V_a_%
HAR57_V_a_%
HAR58_V_a_%
HAR59_V_a_%
HAR60_V_a_%
HAR61_V_a_%
HAR62_V_a_%
HAR63_V_a_%
HAR64_V_a_%
HAR65_V_a_%
HAR66_V_a_%
HAR67_V_a_%
HAR68_V_a_%
HAR69_V_a_%
HAR70_V_a_%
HAR71_V_a_%
HAR72_V_a_%
HAR73_V_a_%
HAR74_V_a_%
HAR75_V_a_%
HAR76_V_a_%
HAR77_V_a_%
HAR78_V_a_%
HAR79_V_a_%
HAR80_V_a_%
HAR81_V_a_%
HAR82_V_a_%
HAR83_V_a_%
HAR84_V_a_%
HAR85_V_a_%
HAR86_V_a_%
HAR87_V_a_%
HAR88_V_a_%
HAR89_V_a_%
HAR90_V_a_%
HAR91_V_a_%
HAR92_V_a_%
HAR93_V_a_%
HAR94_V_a_%
HAR95_V_a_%
HAR96_V_a_%
HAR97_V_a_%
HAR98_V_a_%
HAR99_V_a_%
HAR100_V_a_%
HAR101_V_a_%
HAR102_V_a_%
HAR103_V_a_%
HAR104_V_a_%
HAR105_V_a_%
HAR106_V_a_%
HAR107_V_a_%
HAR108_V_a_%
HAR109_V_a_%
HAR110_V_a_%
HAR111_V_a_%
HAR112_V_a_%
HAR113_V_a_%
HAR114_V_a_%
HAR115_V_a_%
HAR116_V_a_%
HAR117_V_a_%
HAR118_V_a_%
HAR119_V_a_%
HAR120_V_a_%
HAR121_V_a_%
HAR122_V_a_%
HAR123_V_a_%
HAR124_V_a_%
HAR125_V_a_%
HAR126_V_a_%
HAR127_V_a_%
ANG_HAR2_V_a
ANG_HAR3_V_a
ANG_HAR4_V_a
ANG_HAR5_V_a
ANG_HAR6_V_a
ANG_HAR7_V_a
ANG_HAR8_V_a
ANG_HAR9_V_a
ANG_HAR10_V_a
ANG_HAR11_V_a
ANG_HAR12_V_a
ANG_HAR13_V_a
ANG_HAR14_V_a
ANG_HAR15_V_a
ANG_HAR16_V_a
ANG_HAR17_V_a
ANG_HAR18_V_a
ANG_HAR19_V_a
ANG_HAR20_V_a
ANG_HAR21_V_a
ANG_HAR22_V_a
ANG_HAR23_V_a
ANG_HAR24_V_a
ANG_HAR25_V_a
ANG_HAR26_V_a
ANG_HAR27_V_a
ANG_HAR28_V_a
ANG_HAR29_V_a
ANG_HAR30_V_a
ANG_HAR31_V_a
ANG_HAR32_V_a
ANG_HAR33_V_a
ANG_HAR34_V_a
ANG_HAR35_V_a
ANG_HAR36_V_a
ANG_HAR37_V_a
ANG_HAR38_V_a
ANG_HAR39_V_a
ANG_HAR40_V_a
ANG_HAR41_V_a
ANG_HAR42_V_a
ANG_HAR43_V_a
ANG_HAR44_V_a
ANG_HAR45_V_a
ANG_HAR46_V_a
ANG_HAR47_V_a
ANG_HAR48_V_a
ANG_HAR49_V_a
ANG_HAR50_V_a
ANG_HAR51_V_a
ANG_HAR52_V_a
ANG_HAR53_V_a
ANG_HAR54_V_a
ANG_HAR55_V_a
ANG_HAR56_V_a
ANG_HAR57_V_a
ANG_HAR58_V_a
ANG_HAR59_V_a
ANG_HAR60_V_a
ANG_HAR61_V_a
ANG_HAR62_V_a
ANG_HAR63_V_a
ANG_HAR64_V_a
ANG_HAR65_V_a
ANG_HAR66_V_a
ANG_HAR67_V_a
ANG_HAR68_V_a
ANG_HAR69_V_a
ANG_HAR70_V_a
ANG_HAR71_V_a
ANG_HAR72_V_a
ANG_HAR73_V_a
ANG_HAR74_V_a
ANG_HAR75_V_a
ANG_HAR76_V_a
ANG_HAR77_V_a
ANG_HAR78_V_a
ANG_HAR79_V_a
ANG_HAR80_V_a
ANG_HAR81_V_a
ANG_HAR82_V_a
ANG_HAR83_V_a
ANG_HAR84_V_a
ANG_HAR85_V_a
ANG_HAR86_V_a
ANG_HAR87_V_a
ANG_HAR88_V_a
ANG_HAR89_V_a
ANG_HAR90_V_a
ANG_HAR91_V_a
ANG_HAR92_V_a
ANG_HAR93_V_a
ANG_HAR94_V_a
ANG_HAR95_V_a
ANG_HAR96_V_a
ANG_HAR97_V_a
ANG_HAR98_V_a
ANG_HAR99_V_a
ANG_HAR100_V_a
ANG_HAR101_V_a
ANG_HAR102_V_a
ANG_HAR103_V_a
ANG_HAR104_V_a
ANG_HAR105_V_a
ANG_HAR106_V_a
ANG_HAR107_V_a
ANG_HAR108_V_a
ANG_HAR109_V_a
ANG_HAR110_V_a
ANG_HAR111_V_a
ANG_HAR112_V_a
ANG_HAR113_V_a
ANG_HAR114_V_a
ANG_HAR115_V_a
ANG_HAR116_V_a
ANG_HAR117_V_a
ANG_HAR118_V_a
ANG_HAR119_V_a
ANG_HAR120_V_a
ANG_HAR121_V_a
ANG_HAR122_V_a
ANG_HAR123_V_a
ANG_HAR124_V_a
ANG_HAR125_V_a
ANG_HAR126_V_a
ANG_HAR127_V_a
HAR2_V_b_%
HAR3_V_b_%
HAR4_V_b_%
HAR5_V_b_%
HAR6_V_b_%
HAR7_V_b_%
HAR8_V_b_%
HAR9_V_b_%
HAR10_V_b_%
HAR11_V_b_%
HAR12_V_b_%
HAR13_V_b_%
HAR14_V_b_%
HAR15_V_b_%
HAR16_V_b_%
HAR17_V_b_%
HAR18_V_b_%
HAR19_V_b_%
HAR20_V_b_%
HAR21_V_b_%
HAR22_V_b_%
HAR23_V_b_%
HAR24_V_b_%
HAR25_V_b_%
HAR26_V_b_%
HAR27_V_b_%
HAR28_V_b_%
HAR29_V_b_%
HAR30_V_b_%
HAR31_V_b_%
HAR32_V_b_%
HAR33_V_b_%
HAR34_V_b_%
HAR35_V_b_%
HAR36_V_b_%
HAR37_V_b_%
HAR38_V_b_%
HAR39_V_b_%
HAR40_V_b_%
HAR41_V_b_%
HAR42_V_b_%
HAR43_V_b_%
HAR44_V_b_%
HAR45_V_b_%
HAR46_V_b_%
HAR47_V_b_%
HAR48_V_b_%
HAR49_V_b_%
HAR50_V_b_%
HAR51_V_b_%
HAR52_V_b_%
HAR53_V_b_%
HAR54_V_b_%
HAR55_V_b_%
HAR56_V_b_%
HAR57_V_b_%
HAR58_V_b_%
HAR59_V_b_%
HAR60_V_b_%
HAR61_V_b_%
HAR62_V_b_%
HAR63_V_b_%
HAR64_V_b_%
HAR65_V_b_%
HAR66_V_b_%
HAR67_V_b_%
HAR68_V_b_%
HAR69_V_b_%
HAR70_V_b_%
HAR71_V_b_%
HAR72_V_b_%
HAR73_V_b_%
HAR74_V_b_%
HAR75_V_b_%
HAR76_V_b_%
HAR77_V_b_%
HAR78_V_b_%
HAR79_V_b_%
HAR80_V_b_%
HAR81_V_b_%
HAR82_V_b_%
HAR83_V_b_%
HAR84_V_b_%
HAR85_V_b_%
HAR86_V_b_%
HAR87_V_b_%
HAR88_V_b_%
HAR89_V_b_%
HAR90_V_b_%
HAR91_V_b_%
HAR92_V_b_%
HAR93_V_b_%
HAR94_V_b_%
HAR95_V_b_%
HAR96_V_b_%
HAR97_V_b_%
HAR98_V_b_%
HAR99_V_b_%
HAR100_V_b_%
HAR101_V_b_%
HAR102_V_b_%
HAR103_V_b_%
HAR104_V_b_%
HAR105_V_b_%
HAR106_V_b_%
HAR107_V_b_%
HAR108_V_b_%
HAR109_V_b_%
HAR110_V_b_%
HAR111_V_b_%
HAR112_V_b_%
HAR113_V_b_%
HAR114_V_b_%
HAR115_V_b_%
HAR116_V_b_%
HAR117_V_b_%
HAR118_V_b_%
HAR119_V_b_%
HAR120_V_b_%
HAR121_V_b_%
HAR122_V_b_%
HAR123_V_b_%
HAR124_V_b_%
HAR125_V_b_%
HAR126_V_b_%
HAR127_V_b_%
ANG_HAR2_V_b
ANG_HAR3_V_b
ANG_HAR4_V_b
ANG_HAR5_V_b
ANG_HAR6_V_b
ANG_HAR7_V_b
ANG_HAR8_V_b
ANG_HAR9_V_b
ANG_HAR10_V_b
ANG_HAR11_V_b
ANG_HAR12_V_b
ANG_HAR13_V_b
ANG_HAR14_V_b
ANG_HAR15_V_b
ANG_HAR16_V_b
ANG_HAR17_V_b
ANG_HAR18_V_b
ANG_HAR19_V_b
ANG_HAR20_V_b
ANG_HAR21_V_b
ANG_HAR22_V_b
ANG_HAR23_V_b
ANG_HAR24_V_b
ANG_HAR25_V_b
ANG_HAR26_V_b
ANG_HAR27_V_b
ANG_HAR28_V_b
ANG_HAR29_V_b
ANG_HAR30_V_b
ANG_HAR31_V_b
ANG_HAR32_V_b
ANG_HAR33_V_b
ANG_HAR34_V_b
ANG_HAR35_V_b
ANG_HAR36_V_b
ANG_HAR37_V_b
ANG_HAR38_V_b
ANG_HAR39_V_b
ANG_HAR40_V_b
ANG_HAR41_V_b
ANG_HAR42_V_b
ANG_HAR43_V_b
ANG_HAR44_V_b
ANG_HAR45_V_b
ANG_HAR46_V_b
ANG_HAR47_V_b
ANG_HAR48_V_b
ANG_HAR49_V_b
ANG_HAR50_V_b
ANG_HAR51_V_b
ANG_HAR52_V_b
ANG_HAR53_V_b
ANG_HAR54_V_b
ANG_HAR55_V_b
ANG_HAR56_V_b
ANG_HAR57_V_b
ANG_HAR58_V_b
ANG_HAR59_V_b
ANG_HAR60_V_b
ANG_HAR61_V_b
ANG_HAR62_V_b
ANG_HAR63_V_b
ANG_HAR64_V_b
ANG_HAR65_V_b
ANG_HAR66_V_b
ANG_HAR67_V_b
ANG_HAR68_V_b
ANG_HAR69_V_b
ANG_HAR70_V_b
ANG_HAR71_V_b
ANG_HAR72_V_b
ANG_HAR73_V_b
ANG_HAR74_V_b
ANG_HAR75_V_b
ANG_HAR76_V_b
ANG_HAR77_V_b
ANG_HAR78_V_b
ANG_HAR79_V_b
ANG_HAR80_V_b
ANG_HAR81_V_b
ANG_HAR82_V_b
ANG_HAR83_V_b
ANG_HAR84_V_b
ANG_HAR85_V_b
ANG_HAR86_V_b
ANG_HAR87_V_b
ANG_HAR88_V_b
ANG_HAR89_V_b
ANG_HAR90_V_b
ANG_HAR91_V_b
ANG_HAR92_V_b
ANG_HAR93_V_b
ANG_HAR94_V_b
ANG_HAR95_V_b
ANG_HAR96_V_b
ANG_HAR97_V_b
ANG_HAR98_V_b
ANG_HAR99_V_b
ANG_HAR100_V_b
ANG_HAR101_V_b
ANG_HAR102_V_b
ANG_HAR103_V_b
ANG_HAR104_V_b
ANG_HAR105_V_b
ANG_HAR106_V_b
ANG_HAR107_V_b
ANG_HAR108_V_b
ANG_HAR109_V_b
ANG_HAR110_V_b
ANG_HAR111_V_b
ANG_HAR112_V_b
ANG_HAR113_V_b
ANG_HAR114_V_b
ANG_HAR115_V_b
ANG_HAR116_V_b
ANG_HAR117_V_b
ANG_HAR118_V_b
ANG_HAR119_V_b
ANG_HAR120_V_b
ANG_HAR121_V_b
ANG_HAR122_V_b
ANG_HAR123_V_b
ANG_HAR124_V_b
ANG_HAR125_V_b
ANG_HAR126_V_b
ANG_HAR127_V_b
HAR2_V_c_%
HAR3_V_c_%
HAR4_V_c_%
HAR5_V_c_%
HAR6_V_c_%
HAR7_V_c_%
HAR8_V_c_%
HAR9_V_c_%
HAR10_V_c_%
HAR11_V_c_%
HAR12_V_c_%
HAR13_V_c_%
HAR14_V_c_%
HAR15_V_c_%
HAR16_V_c_%
HAR17_V_c_%
HAR18_V_c_%
HAR19_V_c_%
HAR20_V_c_%
HAR21_V_c_%
HAR22_V_c_%
HAR23_V_c_%
HAR24_V_c_%
HAR25_V_c_%
HAR26_V_c_%
HAR27_V_c_%
HAR28_V_c_%
HAR29_V_c_%
HAR30_V_c_%
HAR31_V_c_%
HAR32_V_c_%
HAR33_V_c_%
HAR34_V_c_%
HAR35_V_c_%
HAR36_V_c_%
HAR37_V_c_%
HAR38_V_c_%
HAR39_V_c_%
HAR40_V_c_%
HAR41_V_c_%
HAR42_V_c_%
HAR43_V_c_%
HAR44_V_c_%
HAR45_V_c_%
HAR46_V_c_%
HAR47_V_c_%
HAR48_V_c_%
HAR49_V_c_%
HAR50_V_c_%
HAR51_V_c_%
HAR52_V_c_%
HAR53_V_c_%
HAR54_V_c_%
HAR55_V_c_%
HAR56_V_c_%
HAR57_V_c_%
HAR58_V_c_%
HAR59_V_c_%
HAR60_V_c_%
HAR61_V_c_%
HAR62_V_c_%
HAR63_V_c_%
HAR64_V_c_%
HAR65_V_c_%
HAR66_V_c_%
HAR67_V_c_%
HAR68_V_c_%
HAR69_V_c_%
HAR70_V_c_%
HAR71_V_c_%
HAR72_V_c_%
HAR73_V_c_%
HAR74_V_c_%
HAR75_V_c_%
HAR76_V_c_%
HAR77_V_c_%
HAR78_V_c_%
HAR79_V_c_%
HAR80_V_c_%
HAR81_V_c_%
HAR82_V_c_%
HAR83_V_c_%
HAR84_V_c_%
HAR85_V_c_%
HAR86_V_c_%
HAR87_V_c_%
HAR88_V_c_%
HAR89_V_c_%
HAR90_V_c_%
HAR91_V_c_%
HAR92_V_c_%
HAR93_V_c_%
HAR94_V_c_%
HAR95_V_c_%
HAR96_V_c_%
HAR97_V_c_%
HAR98_V_c_%
HAR99_V_c_%
HAR100_V_c_%
HAR101_V_c_%
HAR102_V_c_%
HAR103_V_c_%
HAR104_V_c_%
HAR105_V_c_%
HAR106_V_c_%
HAR107_V_c_%
HAR108_V_c_%
HAR109_V_c_%
HAR110_V_c_%
HAR111_V_c_%
HAR112_V_c_%
HAR113_V_c_%
HAR114_V_c_%
HAR115_V_c_%
HAR116_V_c_%
HAR117_V_c_%
HAR118_V_c_%
HAR119_V_c_%
HAR120_V_c_%
HAR121_V_c_%
HAR122_V_c_%
HAR123_V_c_%
HAR124_V_c_%
HAR125_V_c_%
HAR126_V_c_%
HAR127_V_c_%
ANG_HAR2_V_c
ANG_HAR3_V_c
ANG_HAR4_V_c
ANG_HAR5_V_c
ANG_HAR6_V_c
ANG_HAR7_V_c
ANG_HAR8_V_c
ANG_HAR9_V_c
ANG_HAR10_V_c
ANG_HAR11_V_c
ANG_HAR12_V_c
ANG_HAR13_V_c
ANG_HAR14_V_c
ANG_HAR15_V_c
ANG_HAR16_V_c
ANG_HAR17_V_c
ANG_HAR18_V_c
ANG_HAR19_V_c
ANG_HAR20_V_c
ANG_HAR21_V_c
ANG_HAR22_V_c
ANG_HAR23_V_c
ANG_HAR24_V_c
ANG_HAR25_V_c
ANG_HAR26_V_c
ANG_HAR27_V_c
ANG_HAR28_V_c
ANG_HAR29_V_c
ANG_HAR30_V_c
ANG_HAR31_V_c
ANG_HAR32_V_c
ANG_HAR33_V_c
ANG_HAR34_V_c
ANG_HAR35_V_c
ANG_HAR36_V_c
ANG_HAR37_V_c
ANG_HAR38_V_c
ANG_HAR39_V_c
ANG_HAR40_V_c
ANG_HAR41_V_c
ANG_HAR42_V_c
ANG_HAR43_V_c
ANG_HAR44_V_c
ANG_HAR45_V_c
ANG_HAR46_V_c
ANG_HAR47_V_c
ANG_HAR48_V_c
ANG_HAR49_V_c
ANG_HAR50_V_c
ANG_HAR51_V_c
ANG_HAR52_V_c
ANG_HAR53_V_c
ANG_HAR54_V_c
ANG_HAR55_V_c
ANG_HAR56_V_c
ANG_HAR57_V_c
ANG_HAR58_V_c
ANG_HAR59_V_c
ANG_HAR60_V_c
ANG_HAR61_V_c
ANG_HAR62_V_c
ANG_HAR63_V_c
ANG_HAR64_V_c
ANG_HAR65_V_c
ANG_HAR66_V_c
ANG_HAR67_V_c
ANG_HAR68_V_c
ANG_HAR69_V_c
ANG_HAR70_V_c
ANG_HAR71_V_c
ANG_HAR72_V_c
ANG_HAR73_V_c
ANG_HAR74_V_c
ANG_HAR75_V_c
ANG_HAR76_V_c
ANG_HAR77_V_c
ANG_HAR78_V_c
ANG_HAR79_V_c
ANG_HAR80_V_c
ANG_HAR81_V_c
ANG_HAR82_V_c
ANG_HAR83_V_c
ANG_HAR84_V_c
ANG_HAR85_V_c
ANG_HAR86_V_c
ANG_HAR87_V_c
ANG_HAR88_V_c
ANG_HAR89_V_c
ANG_HAR90_V_c
ANG_HAR91_V_c
ANG_HAR92_V_c
ANG_HAR93_V_c
ANG_HAR94_V_c
ANG_HAR95_V_c
ANG_HAR96_V_c
ANG_HAR97_V_c
ANG_HAR98_V_c
ANG_HAR99_V_c
ANG_HAR100_V_c
ANG_HAR101_V_c
ANG_HAR102_V_c
ANG_HAR103_V_c
ANG_HAR104_V_c
ANG_HAR105_V_c
ANG_HAR106_V_c
ANG_HAR107_V_c
ANG_HAR108_V_c
ANG_HAR109_V_c
ANG_HAR110_V_c
ANG_HAR111_V_c
ANG_HAR112_V_c
ANG_HAR113_V_c
ANG_HAR114_V_c
ANG_HAR115_V_c
ANG_HAR116_V_c
ANG_HAR117_V_c
ANG_HAR118_V_c
ANG_HAR119_V_c
ANG_HAR120_V_c
ANG_HAR121_V_c
ANG_HAR122_V_c
ANG_HAR123_V_c
ANG_HAR124_V_c
ANG_HAR125_V_c
ANG_HAR126_V_c
ANG_HAR127_V_c
HAR2_I_a_%
HAR3_I_a_%
HAR4_I_a_%
HAR5_I_a_%
HAR6_I_a_%
HAR7_I_a_%
HAR8_I_a_%
HAR9_I_a_%
HAR10_I_a_%
HAR11_I_a_%
HAR12_I_a_%
HAR13_I_a_%
HAR14_I_a_%
HAR15_I_a_%
HAR16_I_a_%
HAR17_I_a_%
HAR18_I_a_%
HAR19_I_a_%
HAR20_I_a_%
HAR21_I_a_%
HAR22_I_a_%
HAR23_I_a_%
HAR24_I_a_%
HAR25_I_a_%
HAR26_I_a_%
HAR27_I_a_%
HAR28_I_a_%
HAR29_I_a_%
HAR30_I_a_%
HAR31_I_a_%
HAR32_I_a_%
HAR33_I_a_%
HAR34_I_a_%
HAR35_I_a_%
HAR36_I_a_%
HAR37_I_a_%
HAR38_I_a_%
HAR39_I_a_%
HAR40_I_a_%
HAR41_I_a_%
HAR42_I_a_%
HAR43_I_a_%
HAR44_I_a_%
HAR45_I_a_%
HAR46_I_a_%
HAR47_I_a_%
HAR48_I_a_%
HAR49_I_a_%
HAR50_I_a_%
HAR51_I_a_%
HAR52_I_a_%
HAR53_I_a_%
HAR54_I_a_%
HAR55_I_a_%
HAR56_I_a_%
HAR57_I_a_%
HAR58_I_a_%
HAR59_I_a_%
HAR60_I_a_%
HAR61_I_a_%
HAR62_I_a_%
HAR63_I_a_%
HAR64_I_a_%
HAR65_I_a_%
HAR66_I_a_%
HAR67_I_a_%
HAR68_I_a_%
HAR69_I_a_%
HAR70_I_a_%
HAR71_I_a_%
HAR72_I_a_%
HAR73_I_a_%
HAR74_I_a_%
HAR75_I_a_%
HAR76_I_a_%
HAR77_I_a_%
HAR78_I_a_%
HAR79_I_a_%
HAR80_I_a_%
HAR81_I_a_%
HAR82_I_a_%
HAR83_I_a_%
HAR84_I_a_%
HAR85_I_a_%
HAR86_I_a_%
HAR87_I_a_%
HAR88_I_a_%
HAR89_I_a_%
HAR90_I_a_%
HAR91_I_a_%
HAR92_I_a_%
HAR93_I_a_%
HAR94_I_a_%
HAR95_I_a_%
HAR96_I_a_%
HAR97_I_a_%
HAR98_I_a_%
HAR99_I_a_%
HAR100_I_a_%
HAR101_I_a_%
HAR102_I_a_%
HAR103_I_a_%
HAR104_I_a_%
HAR105_I_a_%
HAR106_I_a_%
HAR107_I_a_%
HAR108_I_a_%
HAR109_I_a_%
HAR110_I_a_%
HAR111_I_a_%
HAR112_I_a_%
HAR113_I_a_%
HAR114_I_a_%
HAR115_I_a_%
HAR116_I_a_%
HAR117_I_a_%
HAR118_I_a_%
HAR119_I_a_%
HAR120_I_a_%
HAR121_I_a_%
HAR122_I_a_%
HAR123_I_a_%
HAR124_I_a_%
HAR125_I_a_%
HAR126_I_a_%
HAR127_I_a_%
ANG_HAR2_I_a
ANG_HAR3_I_a
ANG_HAR4_I_a
ANG_HAR5_I_a
ANG_HAR6_I_a
ANG_HAR7_I_a
ANG_HAR8_I_a
ANG_HAR9_I_a
ANG_HAR10_I_a
ANG_HAR11_I_a
ANG_HAR12_I_a
ANG_HAR13_I_a
ANG_HAR14_I_a
ANG_HAR15_I_a
ANG_HAR16_I_a
ANG_HAR17_I_a
ANG_HAR18_I_a
ANG_HAR19_I_a
ANG_HAR20_I_a
ANG_HAR21_I_a
ANG_HAR22_I_a
ANG_HAR23_I_a
ANG_HAR24_I_a
ANG_HAR25_I_a
ANG_HAR26_I_a
ANG_HAR27_I_a
ANG_HAR28_I_a
ANG_HAR29_I_a
ANG_HAR30_I_a
ANG_HAR31_I_a
ANG_HAR32_I_a
ANG_HAR33_I_a
ANG_HAR34_I_a
ANG_HAR35_I_a
ANG_HAR36_I_a
ANG_HAR37_I_a
ANG_HAR38_I_a
ANG_HAR39_I_a
ANG_HAR40_I_a
ANG_HAR41_I_a
ANG_HAR42_I_a
ANG_HAR43_I_a
ANG_HAR44_I_a
ANG_HAR45_I_a
ANG_HAR46_I_a
ANG_HAR47_I_a
ANG_HAR48_I_a
ANG_HAR49_I_a
ANG_HAR50_I_a
ANG_HAR51_I_a
ANG_HAR52_I_a
ANG_HAR53_I_a
ANG_HAR54_I_a
ANG_HAR55_I_a
ANG_HAR56_I_a
ANG_HAR57_I_a
ANG_HAR58_I_a
ANG_HAR59_I_a
ANG_HAR60_I_a
ANG_HAR61_I_a
ANG_HAR62_I_a
ANG_HAR63_I_a
ANG_HAR64_I_a
ANG_HAR65_I_a
ANG_HAR66_I_a
ANG_HAR67_I_a
ANG_HAR68_I_a
ANG_HAR69_I_a
ANG_HAR70_I_a
ANG_HAR71_I_a
ANG_HAR72_I_a
ANG_HAR73_I_a
ANG_HAR74_I_a
ANG_HAR75_I_a
ANG_HAR76_I_a
ANG_HAR77_I_a
ANG_HAR78_I_a
ANG_HAR79_I_a
ANG_HAR80_I_a
ANG_HAR81_I_a
ANG_HAR82_I_a
ANG_HAR83_I_a
ANG_HAR84_I_a
ANG_HAR85_I_a
ANG_HAR86_I_a
ANG_HAR87_I_a
ANG_HAR88_I_a
ANG_HAR89_I_a
ANG_HAR90_I_a
ANG_HAR91_I_a
ANG_HAR92_I_a
ANG_HAR93_I_a
ANG_HAR94_I_a
ANG_HAR95_I_a
ANG_HAR96_I_a
ANG_HAR97_I_a
ANG_HAR98_I_a
ANG_HAR99_I_a
ANG_HAR100_I_a
ANG_HAR101_I_a
ANG_HAR102_I_a
ANG_HAR103_I_a
ANG_HAR104_I_a
ANG_HAR105_I_a
ANG_HAR106_I_a
ANG_HAR107_I_a
ANG_HAR108_I_a
ANG_HAR109_I_a
ANG_HAR110_I_a
ANG_HAR111_I_a
ANG_HAR112_I_a
ANG_HAR113_I_a
ANG_HAR114_I_a
ANG_HAR115_I_a
ANG_HAR116_I_a
ANG_HAR117_I_a
ANG_HAR118_I_a
ANG_HAR119_I_a
ANG_HAR120_I_a
ANG_HAR121_I_a
ANG_HAR122_I_a
ANG_HAR123_I_a
ANG_HAR124_I_a
ANG_HAR125_I_a
ANG_HAR126_I_a
ANG_HAR127_I_a
ANG_HAR128_I_a
HAR2_I_b_%
HAR3_I_b_%
HAR4_I_b_%
HAR5_I_b_%
HAR6_I_b_%
HAR7_I_b_%
HAR8_I_b_%
HAR9_I_b_%
HAR10_I_b_%
HAR11_I_b_%
HAR12_I_b_%
HAR13_I_b_%
HAR14_I_b_%
HAR15_I_b_%
HAR16_I_b_%
HAR17_I_b_%
HAR18_I_b_%
HAR19_I_b_%
HAR20_I_b_%
HAR21_I_b_%
HAR22_I_b_%
HAR23_I_b_%
HAR24_I_b_%
HAR25_I_b_%
HAR26_I_b_%
HAR27_I_b_%
HAR28_I_b_%
HAR29_I_b_%
HAR30_I_b_%
HAR31_I_b_%
HAR32_I_b_%
HAR33_I_b_%
HAR34_I_b_%
HAR35_I_b_%
HAR36_I_b_%
HAR37_I_b_%
HAR38_I_b_%
HAR39_I_b_%
HAR40_I_b_%
HAR41_I_b_%
HAR42_I_b_%
HAR43_I_b_%
HAR44_I_b_%
HAR45_I_b_%
HAR46_I_b_%
HAR47_I_b_%
HAR48_I_b_%
HAR49_I_b_%
HAR50_I_b_%
HAR51_I_b_%
HAR52_I_b_%
HAR53_I_b_%
HAR54_I_b_%
HAR55_I_b_%
HAR56_I_b_%
HAR57_I_b_%
HAR58_I_b_%
HAR59_I_b_%
HAR60_I_b_%
HAR61_I_b_%
HAR62_I_b_%
HAR63_I_b_%
HAR64_I_b_%
HAR65_I_b_%
HAR66_I_b_%
HAR67_I_b_%
HAR68_I_b_%
HAR69_I_b_%
HAR70_I_b_%
HAR71_I_b_%
HAR72_I_b_%
HAR73_I_b_%
HAR74_I_b_%
HAR75_I_b_%
HAR76_I_b_%
HAR77_I_b_%
HAR78_I_b_%
HAR79_I_b_%
HAR80_I_b_%
HAR81_I_b_%
HAR82_I_b_%
HAR83_I_b_%
HAR84_I_b_%
HAR85_I_b_%
HAR86_I_b_%
HAR87_I_b_%
HAR88_I_b_%
HAR89_I_b_%
HAR90_I_b_%
HAR91_I_b_%
HAR92_I_b_%
HAR93_I_b_%
HAR94_I_b_%
HAR95_I_b_%
HAR96_I_b_%
HAR97_I_b_%
HAR98_I_b_%
HAR99_I_b_%
HAR100_I_b_%
HAR101_I_b_%
HAR102_I_b_%
HAR103_I_b_%
HAR104_I_b_%
HAR105_I_b_%
HAR106_I_b_%
HAR107_I_b_%
HAR108_I_b_%
HAR109_I_b_%
HAR110_I_b_%
HAR111_I_b_%
HAR112_I_b_%
HAR113_I_b_%
HAR114_I_b_%
HAR115_I_b_%
HAR116_I_b_%
HAR117_I_b_%
HAR118_I_b_%
HAR119_I_b_%
HAR120_I_b_%
HAR121_I_b_%
HAR122_I_b_%
HAR123_I_b_%
HAR124_I_b_%
HAR125_I_b_%
HAR126_I_b_%
HAR127_I_b_%
ANG_HAR2_I_b
ANG_HAR3_I_b
ANG_HAR4_I_b
ANG_HAR5_I_b
ANG_HAR6_I_b
ANG_HAR7_I_b
ANG_HAR8_I_b
ANG_HAR9_I_b
ANG_HAR10_I_b
ANG_HAR11_I_b
ANG_HAR12_I_b
ANG_HAR13_I_b
ANG_HAR14_I_b
ANG_HAR15_I_b
ANG_HAR16_I_b
ANG_HAR17_I_b
ANG_HAR18_I_b
ANG_HAR19_I_b
ANG_HAR20_I_b
ANG_HAR21_I_b
ANG_HAR22_I_b
ANG_HAR23_I_b
ANG_HAR24_I_b
ANG_HAR25_I_b
ANG_HAR26_I_b
ANG_HAR27_I_b
ANG_HAR28_I_b
ANG_HAR29_I_b
ANG_HAR30_I_b
ANG_HAR31_I_b
ANG_HAR32_I_b
ANG_HAR33_I_b
ANG_HAR34_I_b
ANG_HAR35_I_b
ANG_HAR36_I_b
ANG_HAR37_I_b
ANG_HAR38_I_b
ANG_HAR39_I_b
ANG_HAR40_I_b
ANG_HAR41_I_b
ANG_HAR42_I_b
ANG_HAR43_I_b
ANG_HAR44_I_b
ANG_HAR45_I_b
ANG_HAR46_I_b
ANG_HAR47_I_b
ANG_HAR48_I_b
ANG_HAR49_I_b
ANG_HAR50_I_b
ANG_HAR51_I_b
ANG_HAR52_I_b
ANG_HAR53_I_b
ANG_HAR54_I_b
ANG_HAR55_I_b
ANG_HAR56_I_b
ANG_HAR57_I_b
ANG_HAR58_I_b
ANG_HAR59_I_b
ANG_HAR60_I_b
ANG_HAR61_I_b
ANG_HAR62_I_b
ANG_HAR63_I_b
ANG_HAR64_I_b
ANG_HAR65_I_b
ANG_HAR66_I_b
ANG_HAR67_I_b
ANG_HAR68_I_b
ANG_HAR69_I_b
ANG_HAR70_I_b
ANG_HAR71_I_b
ANG_HAR72_I_b
ANG_HAR73_I_b
ANG_HAR74_I_b
ANG_HAR75_I_b
ANG_HAR76_I_b
ANG_HAR77_I_b
ANG_HAR78_I_b
ANG_HAR79_I_b
ANG_HAR80_I_b
ANG_HAR81_I_b
ANG_HAR82_I_b
ANG_HAR83_I_b
ANG_HAR84_I_b
ANG_HAR85_I_b
ANG_HAR86_I_b
ANG_HAR87_I_b
ANG_HAR88_I_b
ANG_HAR89_I_b
ANG_HAR90_I_b
ANG_HAR91_I_b
ANG_HAR92_I_b
ANG_HAR93_I_b
ANG_HAR94_I_b
ANG_HAR95_I_b
ANG_HAR96_I_b
ANG_HAR97_I_b
ANG_HAR98_I_b
ANG_HAR99_I_b
ANG_HAR100_I_b
ANG_HAR101_I_b
ANG_HAR102_I_b
ANG_HAR103_I_b
ANG_HAR104_I_b
ANG_HAR105_I_b
ANG_HAR106_I_b
ANG_HAR107_I_b
ANG_HAR108_I_b
ANG_HAR109_I_b
ANG_HAR110_I_b
ANG_HAR111_I_b
ANG_HAR112_I_b
ANG_HAR113_I_b
ANG_HAR114_I_b
ANG_HAR115_I_b
ANG_HAR116_I_b
ANG_HAR117_I_b
ANG_HAR118_I_b
ANG_HAR119_I_b
ANG_HAR120_I_b
ANG_HAR121_I_b
ANG_HAR122_I_b
ANG_HAR123_I_b
ANG_HAR124_I_b
ANG_HAR125_I_b
ANG_HAR126_I_b
ANG_HAR127_I_b
HAR2_I_c_%
HAR3_I_c_%
HAR4_I_c_%
HAR5_I_c_%
HAR6_I_c_%
HAR7_I_c_%
HAR8_I_c_%
HAR9_I_c_%
HAR10_I_c_%
HAR11_I_c_%
HAR12_I_c_%
HAR13_I_c_%
HAR14_I_c_%
HAR15_I_c_%
HAR16_I_c_%
HAR17_I_c_%
HAR18_I_c_%
HAR19_I_c_%
HAR20_I_c_%
HAR21_I_c_%
HAR22_I_c_%
HAR23_I_c_%
HAR24_I_c_%
HAR25_I_c_%
HAR26_I_c_%
HAR27_I_c_%
HAR28_I_c_%
HAR29_I_c_%
HAR30_I_c_%
HAR31_I_c_%
HAR32_I_c_%
HAR33_I_c_%
HAR34_I_c_%
HAR35_I_c_%
HAR36_I_c_%
HAR37_I_c_%
HAR38_I_c_%
HAR39_I_c_%
HAR40_I_c_%
HAR41_I_c_%
HAR42_I_c_%
HAR43_I_c_%
HAR44_I_c_%
HAR45_I_c_%
HAR46_I_c_%
HAR47_I_c_%
HAR48_I_c_%
HAR49_I_c_%
HAR50_I_c_%
HAR51_I_c_%
HAR52_I_c_%
HAR53_I_c_%
HAR54_I_c_%
HAR55_I_c_%
HAR56_I_c_%
HAR57_I_c_%
HAR58_I_c_%
HAR59_I_c_%
HAR60_I_c_%
HAR61_I_c_%
HAR62_I_c_%
HAR63_I_c_%
HAR64_I_c_%
HAR65_I_c_%
HAR66_I_c_%
HAR67_I_c_%
HAR68_I_c_%
HAR69_I_c_%
HAR70_I_c_%
HAR71_I_c_%
HAR72_I_c_%
HAR73_I_c_%
HAR74_I_c_%
HAR75_I_c_%
HAR76_I_c_%
HAR77_I_c_%
HAR78_I_c_%
HAR79_I_c_%
HAR80_I_c_%
HAR81_I_c_%
HAR82_I_c_%
HAR83_I_c_%
HAR84_I_c_%
HAR85_I_c_%
HAR86_I_c_%
HAR87_I_c_%
HAR88_I_c_%
HAR89_I_c_%
HAR90_I_c_%
HAR91_I_c_%
HAR92_I_c_%
HAR93_I_c_%
HAR94_I_c_%
HAR95_I_c_%
HAR96_I_c_%
HAR97_I_c_%
HAR98_I_c_%
HAR99_I_c_%
HAR100_I_c_%
HAR101_I_c_%
HAR102_I_c_%
HAR103_I_c_%
HAR104_I_c_%
HAR105_I_c_%
HAR106_I_c_%
HAR107_I_c_%
HAR108_I_c_%
HAR109_I_c_%
HAR110_I_c_%
HAR111_I_c_%
HAR112_I_c_%
HAR113_I_c_%
HAR114_I_c_%
HAR115_I_c_%
HAR116_I_c_%
HAR117_I_c_%
HAR118_I_c_%
HAR119_I_c_%
HAR120_I_c_%
HAR121_I_c_%
HAR122_I_c_%
HAR123_I_c_%
HAR124_I_c_%
HAR125_I_c_%
HAR126_I_c_%
HAR127_I_c_%
ANG_HAR2_I_c
ANG_HAR3_I_c
ANG_HAR4_I_c
ANG_HAR5_I_c
ANG_HAR6_I_c
ANG_HAR7_I_c
ANG_HAR8_I_c
ANG_HAR9_I_c
ANG_HAR10_I_c
ANG_HAR11_I_c
ANG_HAR12_I_c
ANG_HAR13_I_c
ANG_HAR14_I_c
ANG_HAR15_I_c
ANG_HAR16_I_c
ANG_HAR17_I_c
ANG_HAR18_I_c
ANG_HAR19_I_c
ANG_HAR20_I_c
ANG_HAR21_I_c
ANG_HAR22_I_c
ANG_HAR23_I_c
ANG_HAR24_I_c
ANG_HAR25_I_c
ANG_HAR26_I_c
ANG_HAR27_I_c
ANG_HAR28_I_c
ANG_HAR29_I_c
ANG_HAR30_I_c
ANG_HAR31_I_c
ANG_HAR32_I_c
ANG_HAR33_I_c
ANG_HAR34_I_c
ANG_HAR35_I_c
ANG_HAR36_I_c
ANG_HAR37_I_c
ANG_HAR38_I_c
ANG_HAR39_I_c
ANG_HAR40_I_c
ANG_HAR41_I_c
ANG_HAR42_I_c
ANG_HAR43_I_c
ANG_HAR44_I_c
ANG_HAR45_I_c
ANG_HAR46_I_c
ANG_HAR47_I_c
ANG_HAR48_I_c
ANG_HAR49_I_c
ANG_HAR50_I_c
ANG_HAR51_I_c
ANG_HAR52_I_c
ANG_HAR53_I_c
ANG_HAR54_I_c
ANG_HAR55_I_c
ANG_HAR56_I_c
ANG_HAR57_I_c
ANG_HAR58_I_c
ANG_HAR59_I_c
ANG_HAR60_I_c
ANG_HAR61_I_c
ANG_HAR62_I_c
ANG_HAR63_I_c
ANG_HAR64_I_c
ANG_HAR65_I_c
ANG_HAR66_I_c
ANG_HAR67_I_c
ANG_HAR68_I_c
ANG_HAR69_I_c
ANG_HAR70_I_c
ANG_HAR71_I_c
ANG_HAR72_I_c
ANG_HAR73_I_c
ANG_HAR74_I_c
ANG_HAR75_I_c
ANG_HAR76_I_c
ANG_HAR77_I_c
ANG_HAR78_I_c
ANG_HAR79_I_c
ANG_HAR80_I_c
ANG_HAR81_I_c
ANG_HAR82_I_c
ANG_HAR83_I_c
ANG_HAR84_I_c
ANG_HAR85_I_c
ANG_HAR86_I_c
ANG_HAR87_I_c
ANG_HAR88_I_c
ANG_HAR89_I_c
ANG_HAR90_I_c
ANG_HAR91_I_c
ANG_HAR92_I_c
ANG_HAR93_I_c
ANG_HAR94_I_c
ANG_HAR95_I_c
ANG_HAR96_I_c
ANG_HAR97_I_c
ANG_HAR98_I_c
ANG_HAR99_I_c
ANG_HAR100_I_c
ANG_HAR101_I_c
ANG_HAR102_I_c
ANG_HAR103_I_c
ANG_HAR104_I_c
ANG_HAR105_I_c
ANG_HAR106_I_c
ANG_HAR107_I_c
ANG_HAR108_I_c
ANG_HAR109_I_c
ANG_HAR110_I_c
ANG_HAR111_I_c
ANG_HAR112_I_c
ANG_HAR113_I_c
ANG_HAR114_I_c
ANG_HAR115_I_c
ANG_HAR116_I_c
ANG_HAR117_I_c
ANG_HAR118_I_c
ANG_HAR119_I_c
ANG_HAR120_I_c
ANG_HAR121_I_c
ANG_HAR122_I_c
ANG_HAR123_I_c
ANG_HAR124_I_c
ANG_HAR125_I_c
ANG_HAR126_I_c
ANG_HAR127_I_c

## analysisNames
analysisId | analysisUnitId | analysisName
1 | 1 | three_phase_realtime
2 | 1 | three_phase_energy_demand
3 | 1 | three_phase_thd
4 | 1 | three_phase_harmonics
5 | 1 | three_phase_sequence

## applications
appId | appName | isTimer | groupId | interval | isEnable | jsonConfig | appType
1 | north | false | 4 | 0 | true | "" | 2
2 | alarm | false | 19 | 0 | true | "" | 2
3 | datalog1 | true | 1 | 3000 | true | "" | 1
4 | datalog2 | true | 1 | 3000 | true | "" | 1
5 | datalog3 | true | 1 | 3000 | true | "" | 1
6 | datalog4 | true | 1 | 3000 | true | "" | 1
7 | trendlogreal | true | 2 | 5000 | true | "" | 1
8 | trendlogenergy | true | 3 | 5000 | true | "" | 1
9 | GeneralSetting | true | 5 | 5000 | true | "" | 1
10 | acucloud | true | 13 | 5000 | true | "" | 1
11 | mqtt | true | 18 | 5000 | true | "" | 1
12 | snmp | true | 14 | 5000 | true | "" | 1
13 | bacnet | true | 14 | 5000 | true | "" | 1

## groups
groupId | groupType | paramCount
1 | datalog |  | 界面配置时生成，模版不配置
2 | trendreal
3 | trendenergy
4 | north
5 | deviceSetting_General
6 | realtimeRange
7 | demandRange
8 | energyRange
9 | thdRange
10 | harmonicsRange
11 | sequenceRange
13 | haveEnergy
14 | haveNoEnergy
15 | datalogRange |  | 暂时用13 haveEnergy
16 | mqttRange |  | 暂时用13 haveEnergy
17 | alarm_range |  | 暂时用14 haveNoEnergy
18 | mqtt |  | 界面配置时生成，模版不配置
19 | alarm |  | 界面配置时生成，模版不配置

## deviceTemplateInfo
label | description | version | firmwareVersion | deviceType | protocol
AcuvimIIR | AcuvimIIR three-phase AC meter | v1.00p01 | v6.27 | threePhaseACMeter | { "type": "Modbus", "transports": ["modbus-tcp", "modbus-rtu"] }