## blockParams
Start(Dec) | descrption | paramType | unit | check | dataType | byteOrder | RW | Reg | scale | Alarm | Data log default parameter | Trend Log | DataLog | AcuCloud | MQTT | SNMP | BACnetIP | North
0 | IsOnline | IsOnline |  |  | isOnline | 1 | R | 1 | 1
8192 | System Frequency | FREQ_Hz | Hz |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8194 | Phase A Line-to-Neutral Voltage | VLN_a_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8196 | Phase B Line-to-Neutral Voltage | VLN_b_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8198 | Phase C Line-to-Neutral Voltage | VLN_c_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8200 | Average Line-to-Neutral Voltage | VLN_avg_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8202 | Phase A-B Line-to-Line Voltage | VLL_ab_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8204 | Phase B-C Line-to-Line Voltage | VLL_bc_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8206 | Phase C-A Line-to-Line Voltage | VLL_ca_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8208 | Average Line-to-Line Voltage | VLL_avg_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8210 | Phase A Line Current | I_a_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8212 | Phase B Line Current | I_b_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8214 | Phase C Line Current | I_c_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8216 | Average Line Current | I_avg_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8218 | System Active Power | P_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8220 | System Reactive Power | Q_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8222 | System Apparent Power | S_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8224 | System Power Factor | PF |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8226 | Average Load Nature | LC_avg |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8228 | Phase A Active Power | P_a_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8230 | Phase B Active Power | P_b_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8232 | Phase C Active Power | P_c_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8234 | Phase A Reactive Power | Q_a_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8236 | Phase B Reactive Power | Q_b_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8238 | Phase C Reactive Power | Q_c_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8240 | Phase A Apparent Power | S_a_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8242 | Phase B Apparent Power | S_b_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8244 | Phase C Apparent Power | S_c_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8246 | Phase A Power Factor | PF_a |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8248 | Phase B Power Factor | PF_b |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8250 | Phase C Power Factor | PF_c |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8252 | Phase A Load Nature | LC_a |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8254 | Phase B Load Nature | LC_b |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8256 | Phase C Load Nature | LC_c |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8448 | Input Channel 1 current | I_001_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8450 | Input Channel 1 Active Power | P_001_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8452 | Input Channel 1 Reactive Power | Q_001_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8454 | Input Channel 1 Apparent Power | S_001_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8456 | Input Channel 1 Power Factor | PF_001 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8458 | Input Channel 1 Load Nature | LC_001 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8460 | Input Channel 2 current | I_002_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8462 | Input Channel 2 Active Power | P_002_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8464 | Input Channel 2 Reactive Power | Q_002_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8466 | Input Channel 2 Apparent Power | S_002_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8468 | Input Channel 2 Power Factor | PF_002 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8470 | Input Channel 2 Load Nature | LC_002 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8472 | Input Channel 3 current | I_003_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8474 | Input Channel 3 Active Power | P_003_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8476 | Input Channel 3 Reactive Power | Q_003_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8478 | Input Channel 3 Apparent Power | S_003_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8480 | Input Channel 3 Power Factor | PF_003 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8482 | Input Channel 3 Load Nature | LC_003 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8484 | Input Channel 4 current | I_004_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8486 | Input Channel 4 Active Power | P_004_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8488 | Input Channel 4 Reactive Power | Q_004_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8490 | Input Channel 4 Apparent Power | S_004_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8492 | Input Channel 4 Power Factor | PF_004 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8494 | Input Channel 4 Load Nature | LC_004 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8496 | Input Channel 5 current | I_005_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8498 | Input Channel 5 Active Power | P_005_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8500 | Input Channel 5 Reactive Power | Q_005_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8502 | Input Channel 5 Apparent Power | S_005_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8504 | Input Channel 5 Power Factor | PF_005 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8506 | Input Channel 5 Load Nature | LC_005 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8508 | Input Channel 6 current | I_006_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8510 | Input Channel 6 Active Power | P_006_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8512 | Input Channel 6 Reactive Power | Q_006_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8514 | Input Channel 6 Apparent Power | S_006_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8516 | Input Channel 6 Power Factor | PF_006 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8518 | Input Channel 6 Load Nature | LC_006 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8520 | Input Channel 7 current | I_007_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8522 | Input Channel 7 Active Power | P_007_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8524 | Input Channel 7 Reactive Power | Q_007_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8526 | Input Channel 7 Apparent Power | S_007_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8528 | Input Channel 7 Power Factor | PF_007 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8530 | Input Channel 7 Load Nature | LC_007 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8532 | Input Channel 8 current | I_008_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8534 | Input Channel 8 Active Power | P_008_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8536 | Input Channel 8 Reactive Power | Q_008_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8538 | Input Channel 8 Apparent Power | S_008_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8540 | Input Channel 8 Power Factor | PF_008 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8542 | Input Channel 8 Load Nature | LC_008 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8544 | Input Channel 9 current | I_009_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8546 | Input Channel 9 Active Power | P_009_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8548 | Input Channel 9 Reactive Power | Q_009_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8550 | Input Channel 9 Apparent Power | S_009_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8552 | Input Channel 9 Power Factor | PF_009 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8554 | Input Channel 9 Load Nature | LC_009 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8556 | Input Channel 10 current | I_010_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8558 | Input Channel 10 Active Power | P_010_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8560 | Input Channel 10 Reactive Power | Q_010_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8562 | Input Channel 10 Apparent Power | S_010_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8564 | Input Channel 10 Power Factor | PF_010 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8566 | Input Channel 10 Load Nature | LC_010 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8568 | Input Channel 11 current | I_011_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8570 | Input Channel 11 Active Power | P_011_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8572 | Input Channel 11 Reactive Power | Q_011_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8574 | Input Channel 11 Apparent Power | S_011_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8576 | Input Channel 11 Power Factor | PF_011 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8578 | Input Channel 11 Load Nature | LC_011 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8580 | Input Channel 12 current | I_012_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8582 | Input Channel 12 Active Power | P_012_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8584 | Input Channel 12 Reactive Power | Q_012_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8586 | Input Channel 12 Apparent Power | S_012_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8588 | Input Channel 12 Power Factor | PF_012 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8590 | Input Channel 12 Load Nature | LC_012 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8592 | Input Channel 13 current | I_013_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8594 | Input Channel 13 Active Power | P_013_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8596 | Input Channel 13 Reactive Power | Q_013_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8598 | Input Channel 13 Apparent Power | S_013_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8600 | Input Channel 13 Power Factor | PF_013 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8602 | Input Channel 13 Load Nature | LC_013 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8604 | Input Channel 14 current | I_014_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8606 | Input Channel 14 Active Power | P_014_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8608 | Input Channel 14 Reactive Power | Q_014_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8610 | Input Channel 14 Apparent Power | S_014_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8612 | Input Channel 14 Power Factor | PF_014 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8614 | Input Channel 14 Load Nature | LC_014 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8616 | Input Channel 15 current | I_015_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8618 | Input Channel 15 Active Power | P_015_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8620 | Input Channel 15 Reactive Power | Q_015_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8622 | Input Channel 15 Apparent Power | S_015_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8624 | Input Channel 15 Power Factor | PF_015 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8626 | Input Channel 15 Load Nature | LC_015 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8628 | Input Channel 16 current | I_016_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8630 | Input Channel 16 Active Power | P_016_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8632 | Input Channel 16 Reactive Power | Q_016_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8634 | Input Channel 16 Apparent Power | S_016_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8636 | Input Channel 16 Power Factor | PF_016 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8638 | Input Channel 16 Load Nature | LC_016 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8640 | Input Channel 17 current | I_017_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8642 | Input Channel 17 Active Power | P_017_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8644 | Input Channel 17 Reactive Power | Q_017_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8646 | Input Channel 17 Apparent Power | S_017_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8648 | Input Channel 17 Power Factor | PF_017 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8650 | Input Channel 17 Load Nature | LC_017 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8652 | Input Channel 18 current | I_018_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8654 | Input Channel 18 Active Power | P_018_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8656 | Input Channel 18 Reactive Power | Q_018_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8658 | Input Channel 18 Apparent Power | S_018_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8660 | Input Channel 18 Power Factor | PF_018 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8662 | Input Channel 18 Load Nature | LC_018 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8664 | User Channel 1 Active Power | P_s001_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8666 | User Channel 1 Reactive Power | Q_s001_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8668 | User Channel 1 Apparent Power | S_s001_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8670 | User Channel 1 Power Factor | PF_s001 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8672 | User Channel 1 Load Nature | LC_s001 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8674 | User Channel 2 Active Power | P_s002_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8676 | User Channel 2 Reactive Power | Q_s002_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8678 | User Channel 2 Apparent Power | S_s002_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8680 | User Channel 2 Power Factor | PF_s002 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8682 | User Channel 2 Load Nature | LC_s002 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8684 | User Channel 3 Active Power | P_s003_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8686 | User Channel 3 Reactive Power | Q_s003_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8688 | User Channel 3 Apparent Power | S_s003_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8690 | User Channel 3 Power Factor | PF_s003 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8692 | User Channel 3 Load Nature | LC_s003 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8694 | User Channel 4 Active Power | P_s004_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8696 | User Channel 4 Reactive Power | Q_s004_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8698 | User Channel 4 Apparent Power | S_s004_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8700 | User Channel 4 Power Factor | PF_s004 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8702 | User Channel 4 Load Nature | LC_s004 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8704 | User Channel 5 Active Power | P_s005_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8706 | User Channel 5 Reactive Power | Q_s005_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8708 | User Channel 5 Apparent Power | S_s005_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8710 | User Channel 5 Power Factor | PF_s005 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8712 | User Channel 5 Load Nature | LC_s005 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8714 | User Channel 6 Active Power | P_s006_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8716 | User Channel 6 Reactive Power | Q_s006_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8718 | User Channel 6 Apparent Power | S_s006_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8720 | User Channel 6 Power Factor | PF_s006 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8722 | User Channel 6 Load Nature | LC_s006 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8724 | User Channel 7 Active Power | P_s007_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8726 | User Channel 7 Reactive Power | Q_s007_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8728 | User Channel 7 Apparent Power | S_s007_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8730 | User Channel 7 Power Factor | PF_s007 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8732 | User Channel 7 Load Nature | LC_s007 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8734 | User Channel 8 Active Power | P_s008_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8736 | User Channel 8 Reactive Power | Q_s008_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8738 | User Channel 8 Apparent Power | S_s008_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8740 | User Channel 8 Power Factor | PF_s008 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8742 | User Channel 8 Load Nature | LC_s008 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
8744 | User Channel 9 Active Power | P_s009_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8746 | User Channel 9 Reactive Power | Q_s009_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8748 | User Channel 9 Apparent Power | S_s009_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8750 | User Channel 9 Power Factor | PF_s009 |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8752 | User Channel 9 Load Nature | LC_s009 |  |  | float32 | 12 | R | 2 | 1 | [9 empty] | realtime
9472 | Phase A Import Active Energy | EP_IMP_a_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9474 | Phase B Import Active Energy | EP_IMP_b_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9476 | Phase C Import Active Energy | EP_IMP_c_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9478 | System Import Active | EP_IMP_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9480 | Input Channel 1 Import Active Energy | EP_IMP_001_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9482 | Input Channel 2 Import Active Energy | EP_IMP_002_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9484 | Input Channel 3 Import Active Energy | EP_IMP_003_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9486 | Input Channel 4 Import Active Energy | EP_IMP_004_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9488 | Input Channel 5 Import Active Energy | EP_IMP_005_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9490 | Input Channel 6 Import Active Energy | EP_IMP_006_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9492 | Input Channel 7 Import Active Energy | EP_IMP_007_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9494 | Input Channel 8 Import Active Energy | EP_IMP_008_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9496 | Input Channel 9 Import Active Energy | EP_IMP_009_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9498 | Input Channel 10 Import Active Energy | EP_IMP_010_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9500 | Input Channel 11 Import Active Energy | EP_IMP_011_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9502 | Input Channel 12 Import Active Energy | EP_IMP_012_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9504 | Input Channel 13 Import Active Energy | EP_IMP_013_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9506 | Input Channel 14 Import Active Energy | EP_IMP_014_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9508 | Input Channel 15 Import Active Energy | EP_IMP_015_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9510 | Input Channel 16 Import Active Energy | EP_IMP_016_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9512 | Input Channel 17 Import Active Energy | EP_IMP_017_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9514 | Input Channel 18 Import Active Energy | EP_IMP_018_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9516 | User Channel 1 Import Active Energy | EP_IMP_s001_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9518 | User Channel 2 Import Active Energy | EP_IMP_s002_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9520 | User Channel 3 Import Active Energy | EP_IMP_s003_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9522 | User Channel 4 Import Active Energy | EP_IMP_s004_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9524 | User Channel 5 Import Active Energy | EP_IMP_s005_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9526 | User Channel 6 Import Active Energy | EP_IMP_s006_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9528 | User Channel 7 Import Active Energy | EP_IMP_s007_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9530 | User Channel 8 Import Active Energy | EP_IMP_s008_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
9532 | User Channel 9 Import Active Energy | EP_IMP_s009_kWh | kWh | 单位kVAh修改为kWh | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
11008 | Phase A Import Reactive Energy | EQ_IMP_a_kvarh | kvarh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11010 | Phase B Import Reactive Energy | EQ_IMP_b_kvarh | kvarh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11012 | Phase C Import Reactive Energy | EQ_IMP_c_kvarh | kvarh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11014 | System Import Reactive Energy | EQ_IMP_kvarh | kvarh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11016 | Input Channel 1 Import Reactive Energy | EQ_IMP_001_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11018 | Input Channel 2 Import Reactive Energy | EQ_IMP_002_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11020 | Input Channel 3 Import Reactive Energy | EQ_IMP_003_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11022 | Input Channel 4 Import Reactive Energy | EQ_IMP_004_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11024 | Input Channel 5 Import Reactive Energy | EQ_IMP_005_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11026 | Input Channel 6 Import Reactive Energy | EQ_IMP_006_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11028 | Input Channel 7 Import Reactive Energy | EQ_IMP_007_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11030 | Input Channel 8 Import Reactive Energy | EQ_IMP_008_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11032 | Input Channel 9 Import Reactive Energy | EQ_IMP_009_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11034 | Input Channel 10 Import Reactive Energy | EQ_IMP_010_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11036 | Input Channel 11 Import Reactive Energy | EQ_IMP_011_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11038 | Input Channel 12 Import Reactive Energy | EQ_IMP_012_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11040 | Input Channel 13 Import Reactive Energy | EQ_IMP_013_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11042 | Input Channel 14 Import Reactive Energy | EQ_IMP_014_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11044 | Input Channel 15 Import Reactive Energy | EQ_IMP_015_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11046 | Input Channel 16 Import Reactive Energy | EQ_IMP_016_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11048 | Input Channel 17 Import Reactive Energy | EQ_IMP_017_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11050 | Input Channel 18 Import Reactive Energy | EQ_IMP_018_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11052 | User Channel 1 Import Reactive Energy | EQ_IMP_s001_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11054 | User Channel 2 Import Reactive Energy | EQ_IMP_s002_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11056 | User Channel 3 Import Reactive Energy | EQ_IMP_s003_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11058 | User Channel 4 Import Reactive Energy | EQ_IMP_s004_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11060 | User Channel 5 Import Reactive Energy | EQ_IMP_s005_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11062 | User Channel 6 Import Reactive Energy | EQ_IMP_s006_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11064 | Phase A Apparent Energy | ES_a_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11066 | Phase B Apparent Energy | ES_b_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11068 | Phase C Apparent Energy | ES_c_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11070 | System Apparent Energy | ES_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11072 | Input Channel 1 Apparent Energy | ES_001_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11074 | Input Channel 2 Apparent Energy | ES_002_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11076 | Input Channel 3 Apparent Energy | ES_003_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11078 | Input Channel 4 Apparent Energy | ES_004_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11080 | Input Channel 5 Apparent Energy | ES_005_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11082 | Input Channel 6 Apparent Energy | ES_006_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11084 | Input Channel 7 Apparent Energy | ES_007_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11086 | Input Channel 8 Apparent Energy | ES_008_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11088 | Input Channel 9 Apparent Energy | ES_009_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11090 | Input Channel 10 Apparent Energy | ES_010_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11092 | Input Channel 11 Apparent Energy | ES_011_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11094 | Input Channel 12 Apparent Energy | ES_012_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11096 | Input Channel 13 Apparent Energy | ES_013_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11098 | Input Channel 14 Apparent Energy | ES_014_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11100 | Input Channel 15 Apparent Energy | ES_015_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11102 | Input Channel 16 Apparent Energy | ES_016_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11104 | Input Channel 17 Apparent Energy | ES_017_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11106 | Input Channel 18 Apparent Energy | ES_018_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11108 | User Channel 1 Apparent Energy | ES_s001_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11110 | User Channel 2 Apparent Energy | ES_s002_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11112 | User Channel 3 Apparent Energy | ES_s003_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11114 | User Channel 4 Apparent Energy | ES_s004_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11116 | User Channel 5 Apparent Energy | ES_s005_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11118 | User Channel 6 Apparent Energy | ES_s006_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11120 | User Channel 7 Import Reactive Energy | EQ_IMP_s007_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11122 | User Channel 8 Import Reactive Energy | EQ_IMP_s008_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11124 | User Channel 9 Import Reactive Energy | EQ_IMP_s009_kvarh | kvarh | 单位kVAh修改为kvarh | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11126 | User Channel 7 Apparent Energy | ES_s007_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11128 | User Channel 8 Apparent Energy | ES_s008_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11130 | User Channel 9 Apparent Energy | ES_s009_kVAh | kVAh |  | uint32 | 12 | R/W | 2 | 0.1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
11520 | System Active Power Demand | DMD_P_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11522 | System Active Power Demand Predict | PRED_DMD_P_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11524 | System Max Active Power Demand | MAX_DMD_P_kW | kW |  | float32 | 12 | R | 2 | 1
11526 | System Max Active Power Demand Timestamp | MAX_DMDTS_P |  |  | word | 12 | R | 3 | 1
11529 | System Reactive Power Demand | DMD_Q_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11531 | System Reactive Power Demand Predict | PRED_DMD_Q_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11533 | System Max Reactive Power Demand | MAX_DMD_Q_kvar | kvar |  | float32 | 12 | R | 2 | 1
11535 | System Max Reactive Power Demand Timestamp | MAX_DMDTS_Q |  |  | word | 12 | R | 3 | 1
11538 | System Apparent Power Demand | DMD_S_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11540 | System Apparent Power Demand Predict | PRED_DMD_S_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11542 | System Max Apparent Power Demand | MAX_DMD_S_kVA | kVA |  | float32 | 12 | R | 2 | 1
11544 | System Max Apparent Power Demand Timestamp | MAX_DMDTS_S |  |  | word | 12 | R | 3 | 1
11547 | Phase A Current Demand | DMD_I_a_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11549 | Phase A Current Demand Predict | PRED_DMD_I_a_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11551 | Phase A Max Current Demand | MAX_DMD_I_a_A | A |  | float32 | 12 | R | 2 | 1
11553 | Phase A Max Current Demand Timestamp | MAX_DMDTS_I_a |  |  | word | 12 | R | 3 | 1
11556 | Phase A Active Power Demand | DMD_P_a_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11558 | Phase A Active Power Demand Predict | PRED_DMD_P_a_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11560 | Phase A Max Active Power Demand | MAX_DMD_P_a_kW | kW |  | float32 | 12 | R | 2 | 1
11562 | Phase A Max Active Power Demand Timestamp | MAX_DMDTS_P_a |  |  | word | 12 | R | 3 | 1
11565 | Phase A Reactive Power Demand | DMD_Q_a_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11567 | Phase A Reactive Power Demand Predict | PRED_DMD_Q_a_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11569 | Phase A Max Reactive Power Demand | MAX_DMD_Q_a_kvar | kvar |  | float32 | 12 | R | 2 | 1
11571 | Phase A Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_a |  |  | word | 12 | R | 3 | 1
11574 | Phase A Apparent Power Demand | DMD_S_a_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11576 | Phase A Apparent Power Demand Predict | PRED_DMD_S_a_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11578 | Phase A Max Apparent Power Demand | MAX_DMD_S_a_kVA | kVA |  | float32 | 12 | R | 2 | 1
11580 | Phase A Max Apparent Power Demand Timestamp | MAX_DMDTS_S_a |  |  | word | 12 | R | 3 | 1
11583 | Phase B Current Demand | DMD_I_b_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11585 | Phase B Current Demand Predict | PRED_DMD_I_b_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11587 | Phase B Max Current Demand | MAX_DMD_I_b_A | A |  | float32 | 12 | R | 2 | 1
11589 | Phase B Max Current Demand Timestamp | MAX_DMDTS_I_b |  |  | word | 12 | R | 3 | 1
11592 | Phase B Active Power Demand | DMD_P_b_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11594 | Phase A Active Power Demand Predict | PRED_DMD_P_b_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11596 | Phase B Max Active Power Demand | MAX_DMD_P_b_kW | kW |  | float32 | 12 | R | 2 | 1
11598 | Phase B Max Active Power Demand Timestamp | MAX_DMDTS_P_b |  |  | word | 12 | R | 3 | 1
11601 | Phase B Reactive Power Demand | DMD_Q_b_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11603 | Phase B Reactive Power Demand Predict | PRED_DMD_Q_b_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11605 | Phase B Max Reactive Power Demand | MAX_DMD_Q_b_kvar | kvar |  | float32 | 12 | R | 2 | 1
11607 | Phase B Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_b |  |  | word | 12 | R | 3 | 1
11610 | Phase B Apparent Power Demand | DMD_S_b_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11612 | Phase B Apparent Power Demand Predict | PRED_DMD_S_b_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11614 | Phase B Max Apparent Power Demand | MAX_DMD_S_b_kVA | kVA |  | float32 | 12 | R | 2 | 1
11616 | Phase B Max Apparent Power Demand Timestamp | MAX_DMDTS_S_b |  |  | word | 12 | R | 3 | 1
11619 | Phase C Current Demand | DMD_I_c_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11621 | Phase C Current Demand Predict | PRED_DMD_I_c_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11623 | Phase C Max Current Demand | MAX_DMD_I_c_A | A |  | float32 | 12 | R | 2 | 1
11625 | Phase C Max Current Demand Timestamp | MAX_DMDTS_I_c |  |  | word | 12 | R | 3 | 1
11628 | Phase C Active Power Demand | DMD_P_c_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11630 | Phase C Active Power Demand Predict | PRED_DMD_P_c_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11632 | Phase C Max Active Power Demand | MAX_DMD_P_c_kW | kW |  | float32 | 12 | R | 2 | 1
11634 | Phase C Max Active Power Demand Timestamp | MAX_DMDTS_P_c |  |  | word | 12 | R | 3 | 1
11637 | Phase C Reactive Power Demand | DMD_Q_c_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11639 | Phase C Reactive Power Demand Predict | PRED_DMD_Q_c_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11641 | Phase C Max Reactive Power Demand | MAX_DMD_Q_c_kvar | kvar |  | float32 | 12 | R | 2 | 1
11643 | Phase C Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_c |  |  | word | 12 | R | 3 | 1
11646 | Phase C Apparent Power Demand | DMD_S_c_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11648 | Phase C Apparent Power Demand Predict | PRED_DMD_S_c_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11650 | Phase C Max Apparent Power Demand | MAX_DMD_S_c_kVA | kVA |  | float32 | 12 | R | 2 | 1
11652 | Phase C Max Apparent Power Demand Timestamp | MAX_DMDTS_S_c |  |  | word | 12 | R | 3 | 1
11655 | Input Channel 1 Current Demand | DMD_I_001_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11657 | Input Channel 1 Current Demand Predict | PRED_DMD_I_001_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11659 | Input Channel 1 Max Current Demand | MAX_DMD_I_001_A | A |  | float32 | 12 | R | 2 | 1
11661 | Input Channel 1 Max Current Demand Timestamp | MAX_DMDTS_I_001 |  |  | word | 12 | R | 3 | 1
11664 | Input Channel 1 Active Power Demand | DMD_P_001_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11666 | Input Channel 1 Active Power Demand Predict | PRED_DMD_P_001_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11668 | Input Channel 1 Max Active Power Demand | MAX_DMD_P_001_kW | kW |  | float32 | 12 | R | 2 | 1
11670 | Input Channel 1 Max Active Power Demand Timestamp | MAX_DMDTS_P_001 |  |  | word | 12 | R | 3 | 1
11673 | Input Channel 1 Reactive Power Demand | DMD_Q_001_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11675 | Input Channel 1 Reactive Power Demand Predict | PRED_DMD_Q_001_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11677 | Input Channel 1 Max Reactive Power Demand | MAX_DMD_Q_001_kvar | kvar |  | float32 | 12 | R | 2 | 1
11679 | Input Channel 1 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_001 |  |  | word | 12 | R | 3 | 1
11682 | Input Channel 1 Apparent Power Demand | DMD_S_001_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11684 | Input Channel 1 Apparent Power Demand Predict | PRED_DMD_S_001_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11686 | Input Channel 1 Max Apparent Power Demand | MAX_DMD_S_001_kVA | kVA |  | float32 | 12 | R | 2 | 1
11688 | Input Channel 1 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_001 |  |  | word | 12 | R | 3 | 1
11691 | Input Channel 2 Current Demand | DMD_I_002_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11693 | Input Channel 2 Current Demand Predict | PRED_DMD_I_002_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11695 | Input Channel 2 Max Current Demand | MAX_DMD_I_002_A | A |  | float32 | 12 | R | 2 | 1
11697 | Input Channel 2 Max Current Demand Timestamp | MAX_DMDTS_I_002 |  |  | word | 12 | R | 3 | 1
11700 | Input Channel 2 Active Power Demand | DMD_P_002_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11702 | Input Channel 2 Active Power Demand Predict | PRED_DMD_P_002_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11704 | Input Channel 2 Max Active Power Demand | MAX_DMD_P_002_kW | kW |  | float32 | 12 | R | 2 | 1
11706 | Input Channel 2 Max Active Power Demand Timestamp | MAX_DMDTS_P_002 |  |  | word | 12 | R | 3 | 1
11709 | Input Channel 2 Reactive Power Demand | DMD_Q_002_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11711 | Input Channel 2 Reactive Power Demand Predict | PRED_DMD_Q_002_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11713 | Input Channel 2 Max Reactive Power Demand | MAX_DMD_Q_002_kvar | kvar |  | float32 | 12 | R | 2 | 1
11715 | Input Channel 2 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_002 |  |  | word | 12 | R | 3 | 1
11718 | Input Channel 2 Apparent Power Demand | DMD_S_002_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11720 | Input Channel 2 Apparent Power Demand Predict | PRED_DMD_S_002_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11722 | Input Channel 2 Max Apparent Power Demand | MAX_DMD_S_002_kVA | kVA |  | float32 | 12 | R | 2 | 1
11724 | Input Channel 2 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_002 |  |  | word | 12 | R | 3 | 1
11727 | Input Channel 3 Current Demand | DMD_I_003_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11729 | Input Channel 3 Current Demand Predict | PRED_DMD_I_003_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11731 | Input Channel 3 Max Current Demand | MAX_DMD_I_003_A | A |  | float32 | 12 | R | 2 | 1
11733 | Input Channel 3 Max Current Demand Timestamp | MAX_DMDTS_I_003 |  |  | word | 12 | R | 3 | 1
11736 | Input Channel 3 Active Power Demand | DMD_P_003_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11738 | Input Channel 3 Active Power Demand Predict | PRED_DMD_P_003_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11740 | Input Channel 3 Max Active Power Demand | MAX_DMD_P_003_kW | kW |  | float32 | 12 | R | 2 | 1
11742 | Input Channel 3 Max Active Power Demand Timestamp | MAX_DMDTS_P_003 |  |  | word | 12 | R | 3 | 1
11745 | Input Channel 3 Reactive Power Demand | DMD_Q_003_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11747 | Input Channel 3 Reactive Power Demand Predict | PRED_DMD_Q_003_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11749 | Input Channel 3 Max Reactive Power Demand | MAX_DMD_Q_003_kvar | kvar |  | float32 | 12 | R | 2 | 1
11751 | Input Channel 3 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_003 |  |  | word | 12 | R | 3 | 1
11754 | Input Channel 3 Apparent Power Demand | DMD_S_003_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11756 | Input Channel 3 Apparent Power Demand Predict | PRED_DMD_S_003_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11758 | Input Channel 3 Max Apparent Power Demand | MAX_DMD_S_003_kVA | kVA |  | float32 | 12 | R | 2 | 1
11760 | Input Channel 3 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_003 |  |  | word | 12 | R | 3 | 1
11763 | Input Channel 4 Current Demand | DMD_I_004_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11765 | Input Channel 4 Current Demand Predict | PRED_DMD_I_004_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11767 | Input Channel 4 Max Current Demand | MAX_DMD_I_004_A | A |  | float32 | 12 | R | 2 | 1
11769 | Input Channel 4 Max Current Demand Timestamp | MAX_DMDTS_I_004 |  |  | word | 12 | R | 3 | 1
11772 | Input Channel 4 Active Power Demand | DMD_P_004_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11774 | Input Channel 4 Active Power Demand Predict | PRED_DMD_P_004_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11776 | Input Channel 4 Max Active Power Demand | MAX_DMD_P_004_kW | kW |  | float32 | 12 | R | 2 | 1
11778 | Input Channel 4 Max Active Power Demand Timestamp | MAX_DMDTS_P_004 |  |  | word | 12 | R | 3 | 1
11781 | Input Channel 4 Reactive Power Demand | DMD_Q_004_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11783 | Input Channel 4 Reactive Power Demand Predict | PRED_DMD_Q_004_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11785 | Input Channel 4 Max Reactive Power Demand | MAX_DMD_Q_004_kvar | kvar |  | float32 | 12 | R | 2 | 1
11787 | Input Channel 4 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_004 |  |  | word | 12 | R | 3 | 1
11790 | Input Channel 4 Apparent Power Demand | DMD_S_004_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11792 | Input Channel 4 Apparent Power Demand Predict | PRED_DMD_S_004_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11794 | Input Channel 4 Max Apparent Power Demand | MAX_DMD_S_004_kVA | kVA |  | float32 | 12 | R | 2 | 1
11796 | Input Channel 4 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_004 |  |  | word | 12 | R | 3 | 1
11799 | Input Channel 5 Current Demand | DMD_I_005_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11801 | Input Channel 5 Current Demand Predict | PRED_DMD_I_005_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11803 | Input Channel 5 Max Current Demand | MAX_DMD_I_005_A | A |  | float32 | 12 | R | 2 | 1
11805 | Input Channel 5 Max Current Demand Timestamp | MAX_DMDTS_I_005 |  |  | word | 12 | R | 3 | 1
11808 | Input Channel 5 Active Power Demand | DMD_P_005_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11810 | Input Channel 5 Active Power Demand Predict | PRED_DMD_P_005_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11812 | Input Channel 5 Max Active Power Demand | MAX_DMD_P_005_kW | kW |  | float32 | 12 | R | 2 | 1
11814 | Input Channel 5 Max Active Power Demand Timestamp | MAX_DMDTS_P_005 |  |  | word | 12 | R | 3 | 1
11817 | Input Channel 5 Reactive Power Demand | DMD_Q_005_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11819 | Input Channel 5 Reactive Power Demand Predict | PRED_DMD_Q_005_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11821 | Input Channel 5 Max Reactive Power Demand | MAX_DMD_Q_005_kvar | kvar |  | float32 | 12 | R | 2 | 1
11823 | Input Channel 5 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_005 |  |  | word | 12 | R | 3 | 1
11826 | Input Channel 5 Apparent Power Demand | DMD_S_005_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11828 | Input Channel 5 Apparent Power Demand Predict | PRED_DMD_S_005_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11830 | Input Channel 5 Max Apparent Power Demand | MAX_DMD_S_005_kVA | kVA |  | float32 | 12 | R | 2 | 1
11832 | Input Channel 5 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_005 |  |  | word | 12 | R | 3 | 1
11835 | Input Channel 6 Current Demand | DMD_I_006_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11837 | Input Channel 6 Current Demand Predict | PRED_DMD_I_006_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11839 | Input Channel 6 Max Current Demand | MAX_DMD_I_006_A | A |  | float32 | 12 | R | 2 | 1
11841 | Input Channel 6 Max Current Demand Timestamp | MAX_DMDTS_I_006 |  |  | word | 12 | R | 3 | 1
11844 | Input Channel 6 Active Power Demand | DMD_P_006_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11846 | Input Channel 6 Active Power Demand Predict | PRED_DMD_P_006_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11848 | Input Channel 6 Max Active Power Demand | MAX_DMD_P_006_kW | kW |  | float32 | 12 | R | 2 | 1
11850 | Input Channel 6 Max Active Power Demand Timestamp | MAX_DMDTS_P_006 |  |  | word | 12 | R | 3 | 1
11853 | Input Channel 6 Reactive Power Demand | DMD_Q_006_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11855 | Input Channel 6 Reactive Power Demand Predict | PRED_DMD_Q_006_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11857 | Input Channel 6 Max Reactive Power Demand | MAX_DMD_Q_006_kvar | kvar |  | float32 | 12 | R | 2 | 1
11859 | Input Channel 6 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_006 |  |  | word | 12 | R | 3 | 1
11862 | Input Channel 6 Apparent Power Demand | DMD_S_006_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11864 | Input Channel 6 Apparent Power Demand Predict | PRED_DMD_S_006_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11866 | Input Channel 6 Max Apparent Power Demand | MAX_DMD_S_006_kVA | kVA |  | float32 | 12 | R | 2 | 1
11868 | Input Channel 6 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_006 |  |  | word | 12 | R | 3 | 1
11871 | Input Channel 7 Current Demand | DMD_I_007_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11873 | Input Channel 7 Current Demand Predict | PRED_DMD_I_007_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11875 | Input Channel 7 Max Current Demand | MAX_DMD_I_007_A | A |  | float32 | 12 | R | 2 | 1
11877 | Input Channel 7 Max Current Demand Timestamp | MAX_DMDTS_I_007 |  |  | word | 12 | R | 3 | 1
11880 | Input Channel 7 Active Power Demand | DMD_P_007_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11882 | Input Channel 7 Active Power Demand Predict | PRED_DMD_P_007_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11884 | Input Channel 7 Max Active Power Demand | MAX_DMD_P_007_kW | kW |  | float32 | 12 | R | 2 | 1
11886 | Input Channel 7 Max Active Power Demand Timestamp | MAX_DMDTS_P_007 |  |  | word | 12 | R | 3 | 1
11889 | Input Channel 7 Reactive Power Demand | DMD_Q_007_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11891 | Input Channel 7 Reactive Power Demand Predict | PRED_DMD_Q_007_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11893 | Input Channel 7 Max Reactive Power Demand | MAX_DMD_Q_007_kvar | kvar |  | float32 | 12 | R | 2 | 1
11895 | Input Channel 7 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_007 |  |  | word | 12 | R | 3 | 1
11898 | Input Channel 7 Apparent Power Demand | DMD_S_007_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11900 | Input Channel 7 Apparent Power Demand Predict | PRED_DMD_S_007_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11902 | Input Channel 7 Max Apparent Power Demand | MAX_DMD_S_007_kVA | kVA |  | float32 | 12 | R | 2 | 1
11904 | Input Channel 7 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_007 |  |  | word | 12 | R | 3 | 1
11907 | Input Channel 8 Current Demand | DMD_I_008_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11909 | Input Channel 8 Current Demand Predict | PRED_DMD_I_008_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11911 | Input Channel 8 Max Current Demand | MAX_DMD_I_008_A | A |  | float32 | 12 | R | 2 | 1
11913 | Input Channel 8 Max Current Demand Timestamp | MAX_DMDTS_I_008 |  |  | word | 12 | R | 3 | 1
11916 | Input Channel 8 Active Power Demand | DMD_P_008_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11918 | Input Channel 8 Active Power Demand Predict | PRED_DMD_P_008_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11920 | Input Channel 8 Max Active Power Demand | MAX_DMD_P_008_kW | kW |  | float32 | 12 | R | 2 | 1
11922 | Input Channel 8 Max Active Power Demand Timestamp | MAX_DMDTS_P_008 |  |  | word | 12 | R | 3 | 1
11925 | Input Channel 8 Reactive Power Demand | DMD_Q_008_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11927 | Input Channel 8 Reactive Power Demand Predict | PRED_DMD_Q_008_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11929 | Input Channel 8 Max Reactive Power Demand | MAX_DMD_Q_008_kvar | kvar |  | float32 | 12 | R | 2 | 1
11931 | Input Channel 8 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_008 |  |  | word | 12 | R | 3 | 1
11934 | Input Channel 8 Apparent Power Demand | DMD_S_008_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11936 | Input Channel 8 Apparent Power Demand Predict | PRED_DMD_S_008_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11938 | Input Channel 8 Max Apparent Power Demand | MAX_DMD_S_008_kVA | kVA |  | float32 | 12 | R | 2 | 1
11940 | Input Channel 8 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_008 |  |  | word | 12 | R | 3 | 1
11943 | Input Channel 9 Current Demand | DMD_I_009_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11945 | Input Channel 9 Current Demand Predict | PRED_DMD_I_009_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11947 | Input Channel 9 Max Current Demand | MAX_DMD_I_009_A | A |  | float32 | 12 | R | 2 | 1
11949 | Input Channel 9 Max Current Demand Timestamp | MAX_DMDTS_I_009 |  |  | word | 12 | R | 3 | 1
11952 | Input Channel 9 Active Power Demand | DMD_P_009_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11954 | Input Channel 9 Active Power Demand Predict | PRED_DMD_P_009_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11956 | Input Channel 9 Max Active Power Demand | MAX_DMD_P_009_kW | kW |  | float32 | 12 | R | 2 | 1
11958 | Input Channel 9 Max Active Power Demand Timestamp | MAX_DMDTS_P_009 |  |  | word | 12 | R | 3 | 1
11961 | Input Channel 9 Reactive Power Demand | DMD_Q_009_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11963 | Input Channel 9 Reactive Power Demand Predict | PRED_DMD_Q_009_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11965 | Input Channel 9 Max Reactive Power Demand | MAX_DMD_Q_009_kvar | kvar |  | float32 | 12 | R | 2 | 1
11967 | Input Channel 9 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_009 |  |  | word | 12 | R | 3 | 1
11970 | Input Channel 9 Apparent Power Demand | DMD_S_009_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11972 | Input Channel 9 Apparent Power Demand Predict | PRED_DMD_S_009_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11974 | Input Channel 9 Max Apparent Power Demand | MAX_DMD_S_009_kVA | kVA |  | float32 | 12 | R | 2 | 1
11976 | Input Channel 9 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_009 |  |  | word | 12 | R | 3 | 1
11979 | Input Channel 10 Current Demand | DMD_I_010_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11981 | Input Channel 10 Current Demand Predict | PRED_DMD_I_010_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11983 | Input Channel 10 Max Current Demand | MAX_DMD_I_010_A | A |  | float32 | 12 | R | 2 | 1
11985 | Input Channel 10 Max Current Demand Timestamp | MAX_DMDTS_I_010 |  |  | word | 12 | R | 3 | 1
11988 | Input Channel 10 Active Power Demand | DMD_P_010_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11990 | Input Channel 10 Active Power Demand Predict | PRED_DMD_P_010_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
11992 | Input Channel 10 Max Active Power Demand | MAX_DMD_P_010_kW | kW |  | float32 | 12 | R | 2 | 1
11994 | Input Channel 10 Max Active Power Demand Timestamp | MAX_DMDTS_P_010 |  |  | word | 12 | R | 3 | 1
11997 | Input Channel 10 Reactive Power Demand | DMD_Q_010_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
11999 | Input Channel 10 Reactive Power Demand Predict | PRED_DMD_Q_010_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12001 | Input Channel 10 Max Reactive Power Demand | MAX_DMD_Q_010_kvar | kvar |  | float32 | 12 | R | 2 | 1
12003 | Input Channel 10 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_010 |  |  | word | 12 | R | 3 | 1
12006 | Input Channel 10 Apparent Power Demand | DMD_S_010_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12008 | Input Channel 10 Apparent Power Demand Predict | PRED_DMD_S_010_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12010 | Input Channel 10 Max Apparent Power Demand | MAX_DMD_S_010_kVA | kVA |  | float32 | 12 | R | 2 | 1
12012 | Input Channel 10 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_010 |  |  | word | 12 | R | 3 | 1
12015 | Input Channel 11 Current Demand | DMD_I_011_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12017 | Input Channel 11 Current Demand Predict | PRED_DMD_I_011_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12019 | Input Channel 11 Max Current Demand | MAX_DMD_I_011_A | A |  | float32 | 12 | R | 2 | 1
12021 | Input Channel 11 Max Current Demand Timestamp | MAX_DMDTS_I_011 |  |  | word | 12 | R | 3 | 1
12024 | Input Channel 11 Active Power Demand | DMD_P_011_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12026 | Input Channel 11 Active Power Demand Predict | PRED_DMD_P_011_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12028 | Input Channel 11 Max Active Power Demand | MAX_DMD_P_011_kW | kW |  | float32 | 12 | R | 2 | 1
12030 | Input Channel 11 Max Active Power Demand Timestamp | MAX_DMDTS_P_011 |  |  | word | 12 | R | 3 | 1
12033 | Input Channel 11 Reactive Power Demand | DMD_Q_011_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12035 | Input Channel 11 Reactive Power Demand Predict | PRED_DMD_Q_011_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12037 | Input Channel 11 Max Reactive Power Demand | MAX_DMD_Q_011_kvar | kvar |  | float32 | 12 | R | 2 | 1
12039 | Input Channel 11 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_011 |  |  | word | 12 | R | 3 | 1
12042 | Input Channel 11 Apparent Power Demand | DMD_S_011_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12044 | Input Channel 11 Apparent Power Demand Predict | PRED_DMD_S_011_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12046 | Input Channel 11 Max Apparent Power Demand | MAX_DMD_S_011_kVA | kVA |  | float32 | 12 | R | 2 | 1
12048 | Input Channel 11 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_011 |  |  | word | 12 | R | 3 | 1
12051 | Input Channel 12 Current Demand | DMD_I_012_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12053 | Input Channel 12 Current Demand Predict | PRED_DMD_I_012_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12055 | Input Channel 12 Max Current Demand | MAX_DMD_I_012_A | A |  | float32 | 12 | R | 2 | 1
12057 | Input Channel 12 Max Current Demand Timestamp | MAX_DMDTS_I_012 |  |  | word | 12 | R | 3 | 1
12060 | Input Channel 12 Active Power Demand | DMD_P_012_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12062 | Input Channel 12 Active Power Demand Predict | PRED_DMD_P_012_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12064 | Input Channel 12 Max Active Power Demand | MAX_DMD_P_012_kW | kW |  | float32 | 12 | R | 2 | 1
12066 | Input Channel 12 Max Active Power Demand Timestamp | MAX_DMDTS_P_012 |  |  | word | 12 | R | 3 | 1
12069 | Input Channel 12 Reactive Power Demand | DMD_Q_012_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12071 | Input Channel 12 Reactive Power Demand Predict | PRED_DMD_Q_012_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12073 | Input Channel 12 Max Reactive Power Demand | MAX_DMD_Q_012_kvar | kvar |  | float32 | 12 | R | 2 | 1
12075 | Input Channel 12 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_012 |  |  | word | 12 | R | 3 | 1
12078 | Input Channel 12 Apparent Power Demand | DMD_S_012_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12080 | Input Channel 12 Apparent Power Demand Predict | PRED_DMD_S_012_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12082 | Input Channel 12 Max Apparent Power Demand | MAX_DMD_S_012_kVA | kVA |  | float32 | 12 | R | 2 | 1
12084 | Input Channel 12 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_012 |  |  | word | 12 | R | 3 | 1
12087 | Input Channel 13 Current Demand | DMD_I_013_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12089 | Input Channel 13 Current Demand Predict | PRED_DMD_I_013_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12091 | Input Channel 13 Max Current Demand | MAX_DMD_I_013_A | A |  | float32 | 12 | R | 2 | 1
12093 | Input Channel 13 Max Current Demand Timestamp | MAX_DMDTS_I_013 |  |  | word | 12 | R | 3 | 1
12096 | Input Channel 13 Active Power Demand | DMD_P_013_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12098 | Input Channel 13 Active Power Demand Predict | PRED_DMD_P_013_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12100 | Input Channel 13 Max Active Power Demand | MAX_DMD_P_013_kW | kW |  | float32 | 12 | R | 2 | 1
12102 | Input Channel 13 Max Active Power Demand Timestamp | MAX_DMDTS_P_013 |  |  | word | 12 | R | 3 | 1
12105 | Input Channel 13 Reactive Power Demand | DMD_Q_013_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12107 | Input Channel 13 Reactive Power Demand Predict | PRED_DMD_Q_013_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12109 | Input Channel 13 Max Reactive Power Demand | MAX_DMD_Q_013_kvar | kvar |  | float32 | 12 | R | 2 | 1
12111 | Input Channel 13 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_013 |  |  | word | 12 | R | 3 | 1
12114 | Input Channel 13 Apparent Power Demand | DMD_S_013_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12116 | Input Channel 13 Apparent Power Demand Predict | PRED_DMD_S_013_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12118 | Input Channel 13 Max Apparent Power Demand | MAX_DMD_S_013_kVA | kVA |  | float32 | 12 | R | 2 | 1
12120 | Input Channel 13 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_013 |  |  | word | 12 | R | 3 | 1
12123 | Input Channel 14 Current Demand | DMD_I_014_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12125 | Input Channel 14 Current Demand Predict | PRED_DMD_I_014_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12127 | Input Channel 14 Max Current Demand | MAX_DMD_I_014_A | A |  | float32 | 12 | R | 2 | 1
12129 | Input Channel 14 Max Current Demand Timestamp | MAX_DMDTS_I_014 |  |  | word | 12 | R | 3 | 1
12132 | Input Channel 14 Active Power Demand | DMD_P_014_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12134 | Input Channel 14 Active Power Demand Predict | PRED_DMD_P_014_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12136 | Input Channel 14 Max Active Power Demand | MAX_DMD_P_014_kW | kW |  | float32 | 12 | R | 2 | 1
12138 | Input Channel 14 Max Active Power Demand Timestamp | MAX_DMDTS_P_014 |  |  | word | 12 | R | 3 | 1
12141 | Input Channel 14 Reactive Power Demand | DMD_Q_014_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12143 | Input Channel 14 Reactive Power Demand Predict | PRED_DMD_Q_014_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12145 | Input Channel 14 Max Reactive Power Demand | MAX_DMD_Q_014_kvar | kvar |  | float32 | 12 | R | 2 | 1
12147 | Input Channel 14 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_014 |  |  | word | 12 | R | 3 | 1
12150 | Input Channel 14 Apparent Power Demand | DMD_S_014_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12152 | Input Channel 14 Apparent Power Demand Predict | PRED_DMD_S_014_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12154 | Input Channel 14 Max Apparent Power Demand | MAX_DMD_S_014_kVA | kVA |  | float32 | 12 | R | 2 | 1
12156 | Input Channel 14 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_014 |  |  | word | 12 | R | 3 | 1
12159 | Input Channel 15 Current Demand | DMD_I_015_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12161 | Input Channel 15 Current Demand Predict | PRED_DMD_I_015_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12163 | Input Channel 15 Max Current Demand | MAX_DMD_I_015_A | A |  | float32 | 12 | R | 2 | 1
12165 | Input Channel 15 Max Current Demand Timestamp | MAX_DMDTS_I_015 |  |  | word | 12 | R | 3 | 1
12168 | Input Channel 15 Active Power Demand | DMD_P_015_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12170 | Input Channel 15 Active Power Demand Predict | PRED_DMD_P_015_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12172 | Input Channel 15 Max Active Power Demand | MAX_DMD_P_015_kW | kW |  | float32 | 12 | R | 2 | 1
12174 | Input Channel 15 Max Active Power Demand Timestamp | MAX_DMDTS_P_015 |  |  | word | 12 | R | 3 | 1
12177 | Input Channel 15 Reactive Power Demand | DMD_Q_015_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12179 | Input Channel 15 Reactive Power Demand Predict | PRED_DMD_Q_015_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12181 | Input Channel 15 Max Reactive Power Demand | MAX_DMD_Q_015_kvar | kvar |  | float32 | 12 | R | 2 | 1
12183 | Input Channel 15 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_015 |  |  | word | 12 | R | 3 | 1
12186 | Input Channel 15 Apparent Power Demand | DMD_S_015_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12188 | Input Channel 15 Apparent Power Demand Predict | PRED_DMD_S_015_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12190 | Input Channel 15 Max Apparent Power Demand | MAX_DMD_S_015_kVA | kVA |  | float32 | 12 | R | 2 | 1
12192 | Input Channel 15 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_015 |  |  | word | 12 | R | 3 | 1
12195 | Input Channel 16 Current Demand | DMD_I_016_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12197 | Input Channel 16 Current Demand Predict | PRED_DMD_I_016_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12199 | Input Channel 16 Max Current Demand | MAX_DMD_I_016_A | A |  | float32 | 12 | R | 2 | 1
12201 | Input Channel 16 Max Current Demand Timestamp | MAX_DMDTS_I_016 |  |  | word | 12 | R | 3 | 1
12204 | Input Channel 16 Active Power Demand | DMD_P_016_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12206 | Input Channel 16 Active Power Demand Predict | PRED_DMD_P_016_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12208 | Input Channel 16 Max Active Power Demand | MAX_DMD_P_016_kW | kW |  | float32 | 12 | R | 2 | 1
12210 | Input Channel 16 Max Active Power Demand Timestamp | MAX_DMDTS_P_016 |  |  | word | 12 | R | 3 | 1
12213 | Input Channel 16 Reactive Power Demand | DMD_Q_016_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12215 | Input Channel 16 Reactive Power Demand Predict | PRED_DMD_Q_016_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12217 | Input Channel 16 Max Reactive Power Demand | MAX_DMD_Q_016_kvar | kvar |  | float32 | 12 | R | 2 | 1
12219 | Input Channel 16 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_016 |  |  | word | 12 | R | 3 | 1
12222 | Input Channel 16 Apparent Power Demand | DMD_S_016_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12224 | Input Channel 16 Apparent Power Demand Predict | PRED_DMD_S_016_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12226 | Input Channel 16 Max Apparent Power Demand | MAX_DMD_S_016_kVA | kVA |  | float32 | 12 | R | 2 | 1
12228 | Input Channel 16 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_016 |  |  | word | 12 | R | 3 | 1
12231 | Input Channel 17 Current Demand | DMD_I_017_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12233 | Input Channel 17 Current Demand Predict | PRED_DMD_I_017_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12235 | Input Channel 17 Max Current Demand | MAX_DMD_I_017_A | A |  | float32 | 12 | R | 2 | 1
12237 | Input Channel 17 Max Current Demand Timestamp | MAX_DMDTS_I_017 |  |  | word | 12 | R | 3 | 1
12240 | Input Channel 17 Active Power Demand | DMD_P_017_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12242 | Input Channel 17 Active Power Demand Predict | PRED_DMD_P_017_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12244 | Input Channel 17 Max Active Power Demand | MAX_DMD_P_017_kW | kW |  | float32 | 12 | R | 2 | 1
12246 | Input Channel 17 Max Active Power Demand Timestamp | MAX_DMDTS_P_017 |  |  | word | 12 | R | 3 | 1
12249 | Input Channel 17 Reactive Power Demand | DMD_Q_017_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12251 | Input Channel 17 Reactive Power Demand Predict | PRED_DMD_Q_017_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12253 | Input Channel 17 Max Reactive Power Demand | MAX_DMD_Q_017_kvar | kvar |  | float32 | 12 | R | 2 | 1
12255 | Input Channel 17 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_017 |  |  | word | 12 | R | 3 | 1
12258 | Input Channel 17 Apparent Power Demand | DMD_S_017_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12260 | Input Channel 17 Apparent Power Demand Predict | PRED_DMD_S_017_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12262 | Input Channel 17 Max Apparent Power Demand | MAX_DMD_S_017_kVA | kVA |  | float32 | 12 | R | 2 | 1
12264 | Input Channel 17 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_017 |  |  | word | 12 | R | 3 | 1
12267 | Input Channel 18 Current Demand | DMD_I_018_A | A |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12269 | Input Channel 18 Current Demand Predict | PRED_DMD_I_018_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12271 | Input Channel 18 Max Current Demand | MAX_DMD_I_018_A | A |  | float32 | 12 | R | 2 | 1
12273 | Input Channel 18 Max Current Demand Timestamp | MAX_DMDTS_I_018 |  |  | word | 12 | R | 3 | 1
12276 | Input Channel 18 Active Power Demand | DMD_P_018_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12278 | Input Channel 18 Active Power Demand Predict | PRED_DMD_P_018_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12280 | Input Channel 18 Max Active Power Demand | MAX_DMD_P_018_kW | kW |  | float32 | 12 | R | 2 | 1
12282 | Input Channel 18 Max Active Power Demand Timestamp | MAX_DMDTS_P_018 |  |  | word | 12 | R | 3 | 1
12285 | Input Channel 18 Reactive Power Demand | DMD_Q_018_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12287 | Input Channel 18 Reactive Power Demand Predict | PRED_DMD_Q_018_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12289 | Input Channel 18 Max Reactive Power Demand | MAX_DMD_Q_018_kvar | kvar |  | float32 | 12 | R | 2 | 1
12291 | Input Channel 18 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_018 |  |  | word | 12 | R | 3 | 1
12294 | Input Channel 18 Apparent Power Demand | DMD_S_018_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12296 | Input Channel 18 Apparent Power Demand Predict | PRED_DMD_S_018_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12298 | Input Channel 18 Max Apparent Power Demand | MAX_DMD_S_018_kVA | kVA |  | float32 | 12 | R | 2 | 1
12300 | Input Channel 18 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_018 |  |  | word | 12 | R | 3 | 1
12303 | User Channel 1 Active Power Demand | DMD_P_s001_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12305 | User Channel 1 Active Power Demand Predict | PRED_DMD_P_s001_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12307 | User Channel 1 Max Active Power Demand | MAX_DMD_P_s001_kW | kW |  | float32 | 12 | R | 2 | 1
12309 | User Channel 1 Max Active Power Demand Timestamp | MAX_DMDTS_P_s001 |  | MAX_DMDTS_P_001修改为MAX_DMDTS_P_s001 | word | 12 | R | 3 | 1
12312 | User Channel 1 Reactive Power Demand | DMD_Q_s001_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12314 | User Channel 1 Reactive Power Demand Predict | PRED_DMD_Q_s001_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12316 | User Channel 1 Max Reactive Power Demand | MAX_DMD_Q_s001_kvar | kvar |  | float32 | 12 | R | 2 | 1
12318 | User Channel 1 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_s001 |  | MAX_DMDTS_Q_001修改为MAX_DMDTS_Q_s001 | word | 12 | R | 3 | 1
12321 | User Channel 1 Apparent Power Demand | DMD_S_s001_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12323 | User Channel 1 Apparent Power Demand Predict | PRED_DMD_S_s001_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12325 | User Channel 1 Max Apparent Power Demand | MAX_DMD_S_s001_kVA | kVA |  | float32 | 12 | R | 2 | 1
12327 | User Channel 1 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_s001 |  | MAX_DMDTS_S_001修改为MAX_DMDTS_S_s001 | word | 12 | R | 3 | 1
12330 | User Channel 2 Active Power Demand | DMD_P_s002_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12332 | User Channel 2 Active Power Demand Predict | PRED_DMD_P_s002_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12334 | User Channel 2 Max Active Power Demand | MAX_DMD_P_s002_kW | kW |  | float32 | 12 | R | 2 | 1
12336 | User Channel 2 Max Active Power Demand Timestamp | MAX_DMDTS_P_s002 |  | MAX_DMDTS_P_002修改为MAX_DMDTS_P_s002 | word | 12 | R | 3 | 1
12339 | User Channel 2 Reactive Power Demand | DMD_Q_s002_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12341 | User Channel 2 Reactive Power Demand Predict | PRED_DMD_Q_s002_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12343 | User Channel 2 Max Reactive Power Demand | MAX_DMD_Q_s002_kvar | kvar |  | float32 | 12 | R | 2 | 1
12345 | User Channel 2 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_s002 |  | MAX_DMDTS_Q_002修改为MAX_DMDTS_Q_s002 | word | 12 | R | 3 | 1
12348 | User Channel 2 Apparent Power Demand | DMD_S_s002_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12350 | User Channel 2 Apparent Power Demand Predict | PRED_DMD_S_s002_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12352 | User Channel 2 Max Apparent Power Demand | MAX_DMD_S_s002_kVA | kVA |  | float32 | 12 | R | 2 | 1
12354 | User Channel 2 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_s002 |  | MAX_DMDTS_S_002修改为MAX_DMDTS_S_s002 | word | 12 | R | 3 | 1
12357 | User Channel 3 Active Power Demand | DMD_P_s003_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12359 | User Channel 3 Active Power Demand Predict | PRED_DMD_P_s003_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12361 | User Channel 3 Max Active Power Demand | MAX_DMD_P_s003_kW | kW |  | float32 | 12 | R | 2 | 1
12363 | User Channel 3 Max Active Power Demand Timestamp | MAX_DMDTS_P_s003 |  | MAX_DMDTS_P_003修改为MAX_DMDTS_P_s003 | word | 12 | R | 3 | 1
12366 | User Channel 3 Reactive Power Demand | DMD_Q_s003_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12368 | User Channel 3 Reactive Power Demand Predict | PRED_DMD_Q_s003_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12370 | User Channel 3 Max Reactive Power Demand | MAX_DMD_Q_s003_kvar | kvar |  | float32 | 12 | R | 2 | 1
12372 | User Channel 3 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_s003 |  | MAX_DMDTS_Q_003修改为MAX_DMDTS_Q_s003 | word | 12 | R | 3 | 1
12375 | User Channel 3 Apparent Power Demand | DMD_S_s003_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12377 | User Channel 3 Apparent Power Demand Predict | PRED_DMD_S_s003_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12379 | User Channel 3 Max Apparent Power Demand | MAX_DMD_S_s003_kVA | kVA |  | float32 | 12 | R | 2 | 1
12381 | User Channel 3 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_s003 |  | MAX_DMDTS_S_003修改为MAX_DMDTS_S_s003 | word | 12 | R | 3 | 1
12384 | User Channel 4 Active Power Demand | DMD_P_s004_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12386 | User Channel 4 Active Power Demand Predict | PRED_DMD_P_s004_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12388 | User Channel 4 Max Active Power Demand | MAX_DMD_P_s004_kW | kW |  | float32 | 12 | R | 2 | 1
12390 | User Channel 4 Max Active Power Demand Timestamp | MAX_DMDTS_P_s004 |  | MAX_DMDTS_P_004修改为MAX_DMDTS_P_s004 | word | 12 | R | 3 | 1
12393 | User Channel 4 Reactive Power Demand | DMD_Q_s004_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12395 | User Channel 4 Reactive Power Demand Predict | PRED_DMD_Q_s004_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12397 | User Channel 4 Max Reactive Power Demand | MAX_DMD_Q_s004_kvar | kvar |  | float32 | 12 | R | 2 | 1
12399 | User Channel 4 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_s004 |  | MAX_DMDTS_Q_004修改为MAX_DMDTS_Q_s004 | word | 12 | R | 3 | 1
12402 | User Channel 4 Apparent Power Demand | DMD_S_s004_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12404 | User Channel 4 Apparent Power Demand Predict | PRED_DMD_S_s004_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12406 | User Channel 4 Max Apparent Power Demand | MAX_DMD_S_s004_kVA | kVA |  | float32 | 12 | R | 2 | 1
12408 | User Channel 4 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_s004 |  | MAX_DMDTS_S_004修改为MAX_DMDTS_S_s004 | word | 12 | R | 3 | 1
12411 | User Channel 5 Active Power Demand | DMD_P_s005_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12413 | User Channel 5 Active Power Demand Predict | PRED_DMD_P_s005_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12415 | User Channel 5 Max Active Power Demand | MAX_DMD_P_s005_kW | kW |  | float32 | 12 | R | 2 | 1
12417 | User Channel 5 Max Active Power Demand Timestamp | MAX_DMDTS_P_s005 |  | MAX_DMDTS_P_005修改为MAX_DMDTS_P_s005 | word | 12 | R | 3 | 1
12420 | User Channel 5 Reactive Power Demand | DMD_Q_s005_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12422 | User Channel 5 Reactive Power Demand Predict | PRED_DMD_Q_s005_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12424 | User Channel 5 Max Reactive Power Demand | MAX_DMD_Q_s005_kvar | kvar |  | float32 | 12 | R | 2 | 1
12426 | User Channel 5 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_s005 |  | MAX_DMDTS_Q_005修改为MAX_DMDTS_Q_s005 | word | 12 | R | 3 | 1
12429 | User Channel 5 Apparent Power Demand | DMD_S_s005_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12431 | User Channel 5 Apparent Power Demand Predict | PRED_DMD_S_s005_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12433 | User Channel 5 Max Apparent Power Demand | MAX_DMD_S_s005_kVA | kVA |  | float32 | 12 | R | 2 | 1
12435 | User Channel 5 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_s005 |  | MAX_DMDTS_S_005修改为MAX_DMDTS_S_s005 | word | 12 | R | 3 | 1
12438 | User Channel 6 Active Power Demand | DMD_P_s006_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12440 | User Channel 6 Active Power Demand Predict | PRED_DMD_P_s006_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12442 | User Channel 6 Max Active Power Demand | MAX_DMD_P_s006_kW | kW |  | float32 | 12 | R | 2 | 1
12444 | User Channel 6 Max Active Power Demand Timestamp | MAX_DMDTS_P_s006 |  | MAX_DMDTS_P_006修改为MAX_DMDTS_P_s006 | word | 12 | R | 3 | 1
12447 | User Channel 6 Reactive Power Demand | DMD_Q_s006_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12449 | User Channel 6 Reactive Power Demand Predict | PRED_DMD_Q_s006_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12451 | User Channel 6 Max Reactive Power Demand | MAX_DMD_Q_s006_kvar | kvar |  | float32 | 12 | R | 2 | 1
12453 | User Channel 6 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_s006 |  | MAX_DMDTS_Q_006修改为MAX_DMDTS_Q_s006 | word | 12 | R | 3 | 1
12456 | User Channel 6 Apparent Power Demand | DMD_S_s006_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12458 | User Channel 6 Apparent Power Demand Predict | PRED_DMD_S_s006_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12460 | User Channel 6 Max Apparent Power Demand | MAX_DMD_S_s006_kVA | kVA |  | float32 | 12 | R | 2 | 1
12462 | User Channel 6 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_s006 |  | MAX_DMDTS_S_006修改为MAX_DMDTS_S_s006 | word | 12 | R | 3 | 1
12465 | User Channel 7 Active Power Demand | DMD_P_s007_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12467 | User Channel 7 Active Power Demand Predict | PRED_DMD_P_s007_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12469 | User Channel 7 Max Active Power Demand | MAX_DMD_P_s007_kW | kW |  | float32 | 12 | R | 2 | 1
12471 | User Channel 7 Max Active Power Demand Timestamp | MAX_DMDTS_P_s007 |  | MAX_DMDTS_P_007修改为MAX_DMDTS_P_s007 | word | 12 | R | 3 | 1
12474 | User Channel 7 Reactive Power Demand | DMD_Q_s007_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12476 | User Channel 7 Reactive Power Demand Predict | PRED_DMD_Q_s007_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12478 | User Channel 7 Max Reactive Power Demand | MAX_DMD_Q_s007_kvar | kvar |  | float32 | 12 | R | 2 | 1
12480 | User Channel 7 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_s007 |  | MAX_DMDTS_Q_007修改为MAX_DMDTS_Q_s007 | word | 12 | R | 3 | 1
12483 | User Channel 7 Apparent Power Demand | DMD_S_s007_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12485 | User Channel 7 Apparent Power Demand Predict | PRED_DMD_S_s007_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12487 | User Channel 7 Max Apparent Power Demand | MAX_DMD_S_s007_kVA | kVA |  | float32 | 12 | R | 2 | 1
12489 | User Channel 7 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_s007 |  | MAX_DMDTS_S_007修改为MAX_DMDTS_S_s007 | word | 12 | R | 3 | 1
12492 | User Channel 8 Active Power Demand | DMD_P_s008_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12494 | User Channel 8 Active Power Demand Predict | PRED_DMD_P_s008_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12496 | User Channel 8 Max Active Power Demand | MAX_DMD_P_s008_kW | kW |  | float32 | 12 | R | 2 | 1
12498 | User Channel 8 Max Active Power Demand Timestamp | MAX_DMDTS_P_s008 |  | MAX_DMDTS_P_008修改为MAX_DMDTS_P_s008 | word | 12 | R | 3 | 1
12501 | User Channel 8 Reactive Power Demand | DMD_Q_s008_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12503 | User Channel 8 Reactive Power Demand Predict | PRED_DMD_Q_s008_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12505 | User Channel 8 Max Reactive Power Demand | MAX_DMD_Q_s008_kvar | kvar |  | float32 | 12 | R | 2 | 1
12507 | User Channel 8 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_s008 |  | MAX_DMDTS_Q_008修改为MAX_DMDTS_Q_s008 | word | 12 | R | 3 | 1
12510 | User Channel 8 Apparent Power Demand | DMD_S_s008_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12512 | User Channel 8 Apparent Power Demand Predict | PRED_DMD_S_s008_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12514 | User Channel 8 Max Apparent Power Demand | MAX_DMD_S_s008_kVA | kVA |  | float32 | 12 | R | 2 | 1
12516 | User Channel 8 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_s008 |  | MAX_DMDTS_S_008修改为MAX_DMDTS_S_s008 | word | 12 | R | 3 | 1
12519 | User Channel 9 Active Power Demand | DMD_P_s009_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12521 | User Channel 9 Active Power Demand Predict | PRED_DMD_P_s009_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12523 | User Channel 9 Max Active Power Demand | MAX_DMD_P_s009_kW | kW |  | float32 | 12 | R | 2 | 1
12525 | User Channel 9 Max Active Power Demand Timestamp | MAX_DMDTS_P_s009 |  | MAX_DMDTS_P_009修改为MAX_DMDTS_P_s009 | word | 12 | R | 3 | 1
12528 | User Channel 9 Reactive Power Demand | DMD_Q_s009_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12530 | User Channel 9 Reactive Power Demand Predict | PRED_DMD_Q_s009_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12532 | User Channel 9 Max Reactive Power Demand | MAX_DMD_Q_s009_kvar | kvar |  | float32 | 12 | R | 2 | 1
12534 | User Channel 9 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_s009 |  | MAX_DMDTS_Q_009修改为MAX_DMDTS_Q_s009 | word | 12 | R | 3 | 1
12537 | User Channel 9 Apparent Power Demand | DMD_S_s009_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
12539 | User Channel 9 Apparent Power Demand Predict | PRED_DMD_S_s009_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
12541 | User Channel 9 Max Apparent Power Demand | MAX_DMD_S_s009_kVA | kVA |  | float32 | 12 | R | 2 | 1
12543 | User Channel 9 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_s009 |  | MAX_DMDTS_S_009修改为MAX_DMDTS_S_s009 | word | 12 | R | 3 | 1
12800 | Voltage Unbalance Factor | UNBL_V_% | % |  | int16 | 12 | R | 1 | 0.1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
12801 | Phase A Voltage THD | THD_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12802 | Phase B Voltage THD | THD_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12803 | Phase C Voltage THD | THD_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12804 | Average Voltage THD | THD_V_avg_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12805 | Phase A Voltage 2-th Harmonic | HAR2_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12806 | Phase A Voltage 3-th Harmonic | HAR3_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12807 | Phase A Voltage 4-th Harmonic | HAR4_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12808 | Phase A Voltage 5-th Harmonic | HAR5_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12809 | Phase A Voltage 6-th Harmonic | HAR6_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12810 | Phase A Voltage 7-th Harmonic | HAR7_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12811 | Phase A Voltage 8-th Harmonic | HAR8_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12812 | Phase A Voltage 9-th Harmonic | HAR9_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12813 | Phase A Voltage 10-th Harmonic | HAR10_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12814 | Phase A Voltage 11-th Harmonic | HAR11_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12815 | Phase A Voltage 12-th Harmonic | HAR12_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12816 | Phase A Voltage 13-th Harmonic | HAR13_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12817 | Phase A Voltage 14-th Harmonic | HAR14_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12818 | Phase A Voltage 15-th Harmonic | HAR15_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12819 | Phase A Voltage 16-th Harmonic | HAR16_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12820 | Phase A Voltage 17-th Harmonic | HAR17_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12821 | Phase A Voltage 18-th Harmonic | HAR18_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12822 | Phase A Voltage 19-th Harmonic | HAR19_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12823 | Phase A Voltage 20-th Harmonic | HAR20_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12824 | Phase A Voltage 21-th Harmonic | HAR21_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12825 | Phase A Voltage 22-th Harmonic | HAR22_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12826 | Phase A Voltage 23-th Harmonic | HAR23_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12827 | Phase A Voltage 24-th Harmonic | HAR24_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12828 | Phase A Voltage 25-th Harmonic | HAR25_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12829 | Phase A Voltage 26-th Harmonic | HAR26_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12830 | Phase A Voltage 27-th Harmonic | HAR27_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12831 | Phase A Voltage 28-th Harmonic | HAR28_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12832 | Phase A Voltage 29-th Harmonic | HAR29_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12833 | Phase A Voltage 30-th Harmonic | HAR30_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12834 | Phase A Voltage 31-th Harmonic | HAR31_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12835 | Phase B Voltage 2-th Harmonic | HAR2_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12836 | Phase B Voltage 3-th Harmonic | HAR3_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12837 | Phase B Voltage 4-th Harmonic | HAR4_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12838 | Phase B Voltage 5-th Harmonic | HAR5_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12839 | Phase B Voltage 6-th Harmonic | HAR6_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12840 | Phase B Voltage 7-th Harmonic | HAR7_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12841 | Phase B Voltage 8-th Harmonic | HAR8_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12842 | Phase B Voltage 9-th Harmonic | HAR9_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12843 | Phase B Voltage 10-th Harmonic | HAR10_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12844 | Phase B Voltage 11-th Harmonic | HAR11_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12845 | Phase B Voltage 12-th Harmonic | HAR12_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12846 | Phase B Voltage 13-th Harmonic | HAR13_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12847 | Phase B Voltage 14-th Harmonic | HAR14_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12848 | Phase B Voltage 15-th Harmonic | HAR15_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12849 | Phase B Voltage 16-th Harmonic | HAR16_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12850 | Phase B Voltage 17-th Harmonic | HAR17_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12851 | Phase B Voltage 18-th Harmonic | HAR18_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12852 | Phase B Voltage 19-th Harmonic | HAR19_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12853 | Phase B Voltage 20-th Harmonic | HAR20_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12854 | Phase B Voltage 21-th Harmonic | HAR21_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12855 | Phase B Voltage 22-th Harmonic | HAR22_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12856 | Phase B Voltage 23-th Harmonic | HAR23_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12857 | Phase B Voltage 24-th Harmonic | HAR24_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12858 | Phase B Voltage 25-th Harmonic | HAR25_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12859 | Phase B Voltage 26-th Harmonic | HAR26_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12860 | Phase B Voltage 27-th Harmonic | HAR27_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12861 | Phase B Voltage 28-th Harmonic | HAR28_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12862 | Phase B Voltage 29-th Harmonic | HAR29_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12863 | Phase B Voltage 30-th Harmonic | HAR30_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12864 | Phase B Voltage 31-th Harmonic | HAR31_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12865 | Phase C Voltage 2-th Harmonic | HAR2_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12866 | Phase C Voltage 3-th Harmonic | HAR3_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12867 | Phase C Voltage 4-th Harmonic | HAR4_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12868 | Phase C Voltage 5-th Harmonic | HAR5_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12869 | Phase C Voltage 6-th Harmonic | HAR6_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12870 | Phase C Voltage 7-th Harmonic | HAR7_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12871 | Phase C Voltage 8-th Harmonic | HAR8_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12872 | Phase C Voltage 9-th Harmonic | HAR9_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12873 | Phase C Voltage 10-th Harmonic | HAR10_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12874 | Phase C Voltage 11-th Harmonic | HAR11_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12875 | Phase C Voltage 12-th Harmonic | HAR12_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12876 | Phase C Voltage 13-th Harmonic | HAR13_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12877 | Phase C Voltage 14-th Harmonic | HAR14_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12878 | Phase C Voltage 15-th Harmonic | HAR15_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12879 | Phase C Voltage 16-th Harmonic | HAR16_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12880 | Phase C Voltage 17-th Harmonic | HAR17_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12881 | Phase C Voltage 18-th Harmonic | HAR18_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12882 | Phase C Voltage 19-th Harmonic | HAR19_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12883 | Phase C Voltage 20-th Harmonic | HAR20_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12884 | Phase C Voltage 21-th Harmonic | HAR21_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12885 | Phase C Voltage 22-th Harmonic | HAR22_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12886 | Phase C Voltage 23-th Harmonic | HAR23_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12887 | Phase C Voltage 24-th Harmonic | HAR24_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12888 | Phase C Voltage 25-th Harmonic | HAR25_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12889 | Phase C Voltage 26-th Harmonic | HAR26_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12890 | Phase C Voltage 27-th Harmonic | HAR27_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12891 | Phase C Voltage 28-th Harmonic | HAR28_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12892 | Phase C Voltage 29-th Harmonic | HAR29_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12893 | Phase C Voltage 30-th Harmonic | HAR30_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12894 | Phase C Voltage 31-th Harmonic | HAR31_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
12895 | Current Unbalance Factor | UNBL_I_% | % |  | int16 | 12 | R | 1 | 100 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
12896 | Phase A Voltage Odd THD | OTHD_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12897 | Phase A Voltage Even THD | ETHD_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12898 | Phase A Voltage Crest Factor | CF_V_a_% | % |  | int16 | 12 | R | 1 | 0.001 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12899 | Phase A Voltage Telephone Harmonic Form Factor | THFF_V_a_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12900 | Phase B Voltage Odd THD | OTHD_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12901 | Phase B Voltage Even THD | ETHD_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12902 | Phase B Voltage Crest Factor | CF_V_b_% | % |  | int16 | 12 | R | 1 | 0.001 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12903 | Phase B Voltage Telephone Harmonic Form Factor | THFF_V_b_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12904 | Phase C Voltage Odd THD | OTHD_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12905 | Phase C Voltage Even THD | ETHD_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12906 | Phase C Voltage Crest Factor | CF_V_c_% | % |  | int16 | 12 | R | 1 | 0.001 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12907 | Phase C Voltage Telephone Harmonic Form Factor | THFF_V_c_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12960 | Input Channel 1 Current Odd THD | OTHD_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12961 | Input Channel 1 Current Even THD | ETHD_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12962 | Input Channel 1 Current K Factor | KF_I_001_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12963 | Input Channel 2 Current Odd THD | OTHD_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12964 | Input Channel 2 Current Even THD | ETHD_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12965 | Input Channel 2 Current K Factor | KF_I_002_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12966 | Input Channel 3 Current Odd THD | OTHD_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12967 | Input Channel 3 Current Even THD | ETHD_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12968 | Input Channel 3 Current K Factor | KF_I_003_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12969 | Input Channel 4 Current Odd THD | OTHD_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12970 | Input Channel 4 Current Even THD | ETHD_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12971 | Input Channel 4 Current K Factor | KF_I_004_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12972 | Input Channel 5 Current Odd THD | OTHD_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12973 | Input Channel 5 Current Even THD | ETHD_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12974 | Input Channel 5 Current K Factor | KF_I_005_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12975 | Input Channel 6 Current Odd THD | OTHD_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12976 | Input Channel 6 Current Even THD | ETHD_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12977 | Input Channel 6 Current K Factor | KF_I_006_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12978 | Input Channel 7 Current Odd THD | OTHD_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12979 | Input Channel 7 Current Even THD | ETHD_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12980 | Input Channel 7 Current K Factor | KF_I_007_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12981 | Input Channel 8 Current Odd THD | OTHD_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12982 | Input Channel 8 Current Even THD | ETHD_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12983 | Input Channel 8 Current K Factor | KF_I_008_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12984 | Input Channel 9 Current Odd THD | OTHD_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12985 | Input Channel 9 Current Even THD | ETHD_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12986 | Input Channel 9 Current K Factor | KF_I_009_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12987 | Input Channel 10 Current Odd THD | OTHD_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12988 | Input Channel 10 Current Even THD | ETHD_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12989 | Input Channel 10 Current K Factor | KF_I_010_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12990 | Input Channel 11 Current Odd THD | OTHD_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12991 | Input Channel 11 Current Even THD | ETHD_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12992 | Input Channel 11 Current K Factor | KF_I_011_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12993 | Input Channel 12 Current Odd THD | OTHD_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12994 | Input Channel 12 Current Even THD | ETHD_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12995 | Input Channel 12 Current K Factor | KF_I_012_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12996 | Input Channel 13 Current Odd THD | OTHD_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12997 | Input Channel 13 Current Even THD | ETHD_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12998 | Input Channel 13 Current K Factor | KF_I_013_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
12999 | Input Channel 14 Current Odd THD | OTHD_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13000 | Input Channel 14 Current Even THD | ETHD_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13001 | Input Channel 14 Current K Factor | KF_I_014_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13002 | Input Channel 15 Current Odd THD | OTHD_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13003 | Input Channel 15 Current Even THD | ETHD_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13004 | Input Channel 15 Current K Factor | KF_I_015_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13005 | Input Channel 16 Current Odd THD | OTHD_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13006 | Input Channel 16 Current Even THD | ETHD_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13007 | Input Channel 16 Current K Factor | KF_I_016_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13008 | Input Channel 17 Current Odd THD | OTHD_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13009 | Input Channel 17 Current Even THD | ETHD_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13010 | Input Channel 17 Current K Factor | KF_I_017_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13011 | Input Channel 18 Current Odd THD | OTHD_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13012 | Input Channel 18 Current Even THD | ETHD_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13013 | Input Channel 18 Current K Factor | KF_I_018_% | % |  | int16 | 12 | R | 1 | 0.1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13056 | Input Channel 1 Current THD | THD_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13057 | Input Channel 1 Current 2-th Harmonic | HAR2_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13058 | Input Channel 1 Current 3-th Harmonic | HAR3_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13059 | Input Channel 1 Current 4-th Harmonic | HAR4_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13060 | Input Channel 1 Current 5-th Harmonic | HAR5_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13061 | Input Channel 1 Current 6-th Harmonic | HAR6_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13062 | Input Channel 1 Current 7-th Harmonic | HAR7_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13063 | Input Channel 1 Current 8-th Harmonic | HAR8_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13064 | Input Channel 1 Current 9-th Harmonic | HAR9_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13065 | Input Channel 1 Current 10-th Harmonic | HAR10_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13066 | Input Channel 1 Current 11-th Harmonic | HAR11_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13067 | Input Channel 1 Current 12-th Harmonic | HAR12_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13068 | Input Channel 1 Current 13-th Harmonic | HAR13_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13069 | Input Channel 1 Current 14-th Harmonic | HAR14_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13070 | Input Channel 1 Current 15-th Harmonic | HAR15_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13071 | Input Channel 1 Current 16-th Harmonic | HAR16_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13072 | Input Channel 1 Current 17-th Harmonic | HAR17_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13073 | Input Channel 1 Current 18-th Harmonic | HAR18_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13074 | Input Channel 1 Current 19-th Harmonic | HAR19_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13075 | Input Channel 1 Current 20-th Harmonic | HAR20_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13076 | Input Channel 1 Current 21-th Harmonic | HAR21_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13077 | Input Channel 1 Current 22-th Harmonic | HAR22_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13078 | Input Channel 1 Current 23-th Harmonic | HAR23_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13079 | Input Channel 1 Current 24-th Harmonic | HAR24_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13080 | Input Channel 1 Current 25-th Harmonic | HAR25_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13081 | Input Channel 1 Current 26-th Harmonic | HAR26_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13082 | Input Channel 1 Current 27-th Harmonic | HAR27_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13083 | Input Channel 1 Current 28-th Harmonic | HAR28_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13084 | Input Channel 1 Current 29-th Harmonic | HAR29_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13085 | Input Channel 1 Current 30-th Harmonic | HAR30_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13086 | Input Channel 1 Current 31-th Harmonic | HAR31_I_001_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13087 | Input Channel 2 Current THD | THD_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13088 | Input Channel 2 Current 2-th Harmonic | HAR2_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13089 | Input Channel 2 Current 3-th Harmonic | HAR3_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13090 | Input Channel 2 Current 4-th Harmonic | HAR4_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13091 | Input Channel 2 Current 5-th Harmonic | HAR5_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13092 | Input Channel 2 Current 6-th Harmonic | HAR6_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13093 | Input Channel 2 Current 7-th Harmonic | HAR7_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13094 | Input Channel 2 Current 8-th Harmonic | HAR8_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13095 | Input Channel 2 Current 9-th Harmonic | HAR9_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13096 | Input Channel 2 Current 10-th Harmonic | HAR10_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13097 | Input Channel 2 Current 11-th Harmonic | HAR11_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13098 | Input Channel 2 Current 12-th Harmonic | HAR12_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13099 | Input Channel 2 Current 13-th Harmonic | HAR13_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13100 | Input Channel 2 Current 14-th Harmonic | HAR14_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13101 | Input Channel 2 Current 15-th Harmonic | HAR15_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13102 | Input Channel 2 Current 16-th Harmonic | HAR16_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13103 | Input Channel 2 Current 17-th Harmonic | HAR17_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13104 | Input Channel 2 Current 18-th Harmonic | HAR18_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13105 | Input Channel 2 Current 19-th Harmonic | HAR19_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13106 | Input Channel 2 Current 20-th Harmonic | HAR20_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13107 | Input Channel 2 Current 21-th Harmonic | HAR21_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13108 | Input Channel 2 Current 22-th Harmonic | HAR22_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13109 | Input Channel 2 Current 23-th Harmonic | HAR23_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13110 | Input Channel 2 Current 24-th Harmonic | HAR24_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13111 | Input Channel 2 Current 25-th Harmonic | HAR25_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13112 | Input Channel 2 Current 26-th Harmonic | HAR26_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13113 | Input Channel 2 Current 27-th Harmonic | HAR27_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13114 | Input Channel 2 Current 28-th Harmonic | HAR28_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13115 | Input Channel 2 Current 29-th Harmonic | HAR29_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13116 | Input Channel 2 Current 30-th Harmonic | HAR30_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13117 | Input Channel 2 Current 31-th Harmonic | HAR31_I_002_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13118 | Input Channel 3 Current THD | THD_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13119 | Input Channel 3 Current 2-th Harmonic | HAR2_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13120 | Input Channel 3 Current 3-th Harmonic | HAR3_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13121 | Input Channel 3 Current 4-th Harmonic | HAR4_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13122 | Input Channel 3 Current 5-th Harmonic | HAR5_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13123 | Input Channel 3 Current 6-th Harmonic | HAR6_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13124 | Input Channel 3 Current 7-th Harmonic | HAR7_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13125 | Input Channel 3 Current 8-th Harmonic | HAR8_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13126 | Input Channel 3 Current 9-th Harmonic | HAR9_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13127 | Input Channel 3 Current 10-th Harmonic | HAR10_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13128 | Input Channel 3 Current 11-th Harmonic | HAR11_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13129 | Input Channel 3 Current 12-th Harmonic | HAR12_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13130 | Input Channel 3 Current 13-th Harmonic | HAR13_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13131 | Input Channel 3 Current 14-th Harmonic | HAR14_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13132 | Input Channel 3 Current 15-th Harmonic | HAR15_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13133 | Input Channel 3 Current 16-th Harmonic | HAR16_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13134 | Input Channel 3 Current 17-th Harmonic | HAR17_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13135 | Input Channel 3 Current 18-th Harmonic | HAR18_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13136 | Input Channel 3 Current 19-th Harmonic | HAR19_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13137 | Input Channel 3 Current 20-th Harmonic | HAR20_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13138 | Input Channel 3 Current 21-th Harmonic | HAR21_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13139 | Input Channel 3 Current 22-th Harmonic | HAR22_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13140 | Input Channel 3 Current 23-th Harmonic | HAR23_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13141 | Input Channel 3 Current 24-th Harmonic | HAR24_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13142 | Input Channel 3 Current 25-th Harmonic | HAR25_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13143 | Input Channel 3 Current 26-th Harmonic | HAR26_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13144 | Input Channel 3 Current 27-th Harmonic | HAR27_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13145 | Input Channel 3 Current 28-th Harmonic | HAR28_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13146 | Input Channel 3 Current 29-th Harmonic | HAR29_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13147 | Input Channel 3 Current 30-th Harmonic | HAR30_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13148 | Input Channel 3 Current 31-th Harmonic | HAR31_I_003_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13149 | Input Channel 4 Current THD | THD_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13150 | Input Channel 4 Current 2-th Harmonic | HAR2_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13151 | Input Channel 4 Current 3-th Harmonic | HAR3_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13152 | Input Channel 4 Current 4-th Harmonic | HAR4_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13153 | Input Channel 4 Current 5-th Harmonic | HAR5_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13154 | Input Channel 4 Current 6-th Harmonic | HAR6_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13155 | Input Channel 4 Current 7-th Harmonic | HAR7_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13156 | Input Channel 4 Current 8-th Harmonic | HAR8_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13157 | Input Channel 4 Current 9-th Harmonic | HAR9_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13158 | Input Channel 4 Current 10-th Harmonic | HAR10_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13159 | Input Channel 4 Current 11-th Harmonic | HAR11_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13160 | Input Channel 4 Current 12-th Harmonic | HAR12_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13161 | Input Channel 4 Current 13-th Harmonic | HAR13_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13162 | Input Channel 4 Current 14-th Harmonic | HAR14_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13163 | Input Channel 4 Current 15-th Harmonic | HAR15_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13164 | Input Channel 4 Current 16-th Harmonic | HAR16_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13165 | Input Channel 4 Current 17-th Harmonic | HAR17_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13166 | Input Channel 4 Current 18-th Harmonic | HAR18_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13167 | Input Channel 4 Current 19-th Harmonic | HAR19_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13168 | Input Channel 4 Current 20-th Harmonic | HAR20_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13169 | Input Channel 4 Current 21-th Harmonic | HAR21_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13170 | Input Channel 4 Current 22-th Harmonic | HAR22_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13171 | Input Channel 4 Current 23-th Harmonic | HAR23_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13172 | Input Channel 4 Current 24-th Harmonic | HAR24_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13173 | Input Channel 4 Current 25-th Harmonic | HAR25_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13174 | Input Channel 4 Current 26-th Harmonic | HAR26_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13175 | Input Channel 4 Current 27-th Harmonic | HAR27_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13176 | Input Channel 4 Current 28-th Harmonic | HAR28_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13177 | Input Channel 4 Current 29-th Harmonic | HAR29_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13178 | Input Channel 4 Current 30-th Harmonic | HAR30_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13179 | Input Channel 4 Current 31-th Harmonic | HAR31_I_004_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13180 | Input Channel 5 Current THD | THD_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13181 | Input Channel 5 Current 2-th Harmonic | HAR2_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13182 | Input Channel 5 Current 3-th Harmonic | HAR3_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13183 | Input Channel 5 Current 4-th Harmonic | HAR4_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13184 | Input Channel 5 Current 5-th Harmonic | HAR5_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13185 | Input Channel 5 Current 6-th Harmonic | HAR6_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13186 | Input Channel 5 Current 7-th Harmonic | HAR7_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13187 | Input Channel 5 Current 8-th Harmonic | HAR8_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13188 | Input Channel 5 Current 9-th Harmonic | HAR9_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13189 | Input Channel 5 Current 10-th Harmonic | HAR10_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13190 | Input Channel 5 Current 11-th Harmonic | HAR11_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13191 | Input Channel 5 Current 12-th Harmonic | HAR12_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13192 | Input Channel 5 Current 13-th Harmonic | HAR13_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13193 | Input Channel 5 Current 14-th Harmonic | HAR14_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13194 | Input Channel 5 Current 15-th Harmonic | HAR15_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13195 | Input Channel 5 Current 16-th Harmonic | HAR16_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13196 | Input Channel 5 Current 17-th Harmonic | HAR17_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13197 | Input Channel 5 Current 18-th Harmonic | HAR18_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13198 | Input Channel 5 Current 19-th Harmonic | HAR19_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13199 | Input Channel 5 Current 20-th Harmonic | HAR20_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13200 | Input Channel 5 Current 21-th Harmonic | HAR21_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13201 | Input Channel 5 Current 22-th Harmonic | HAR22_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13202 | Input Channel 5 Current 23-th Harmonic | HAR23_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13203 | Input Channel 5 Current 24-th Harmonic | HAR24_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13204 | Input Channel 5 Current 25-th Harmonic | HAR25_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13205 | Input Channel 5 Current 26-th Harmonic | HAR26_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13206 | Input Channel 5 Current 27-th Harmonic | HAR27_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13207 | Input Channel 5 Current 28-th Harmonic | HAR28_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13208 | Input Channel 5 Current 29-th Harmonic | HAR29_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13209 | Input Channel 5 Current 30-th Harmonic | HAR30_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13210 | Input Channel 5 Current 31-th Harmonic | HAR31_I_005_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13211 | Input Channel 6 Current THD | THD_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13212 | Input Channel 6 Current 2-th Harmonic | HAR2_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13213 | Input Channel 6 Current 3-th Harmonic | HAR3_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13214 | Input Channel 6 Current 4-th Harmonic | HAR4_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13215 | Input Channel 6 Current 5-th Harmonic | HAR5_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13216 | Input Channel 6 Current 6-th Harmonic | HAR6_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13217 | Input Channel 6 Current 7-th Harmonic | HAR7_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13218 | Input Channel 6 Current 8-th Harmonic | HAR8_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13219 | Input Channel 6 Current 9-th Harmonic | HAR9_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13220 | Input Channel 6 Current 10-th Harmonic | HAR10_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13221 | Input Channel 6 Current 11-th Harmonic | HAR11_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13222 | Input Channel 6 Current 12-th Harmonic | HAR12_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13223 | Input Channel 6 Current 13-th Harmonic | HAR13_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13224 | Input Channel 6 Current 14-th Harmonic | HAR14_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13225 | Input Channel 6 Current 15-th Harmonic | HAR15_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13226 | Input Channel 6 Current 16-th Harmonic | HAR16_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13227 | Input Channel 6 Current 17-th Harmonic | HAR17_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13228 | Input Channel 6 Current 18-th Harmonic | HAR18_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13229 | Input Channel 6 Current 19-th Harmonic | HAR19_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13230 | Input Channel 6 Current 20-th Harmonic | HAR20_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13231 | Input Channel 6 Current 21-th Harmonic | HAR21_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13232 | Input Channel 6 Current 22-th Harmonic | HAR22_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13233 | Input Channel 6 Current 23-th Harmonic | HAR23_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13234 | Input Channel 6 Current 24-th Harmonic | HAR24_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13235 | Input Channel 6 Current 25-th Harmonic | HAR25_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13236 | Input Channel 6 Current 26-th Harmonic | HAR26_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13237 | Input Channel 6 Current 27-th Harmonic | HAR27_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13238 | Input Channel 6 Current 28-th Harmonic | HAR28_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13239 | Input Channel 6 Current 29-th Harmonic | HAR29_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13240 | Input Channel 6 Current 30-th Harmonic | HAR30_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13241 | Input Channel 6 Current 31-th Harmonic | HAR31_I_006_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13242 | Input Channel 7 Current THD | THD_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13243 | Input Channel 7 Current 2-th Harmonic | HAR2_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13244 | Input Channel 7 Current 3-th Harmonic | HAR3_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13245 | Input Channel 7 Current 4-th Harmonic | HAR4_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13246 | Input Channel 7 Current 5-th Harmonic | HAR5_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13247 | Input Channel 7 Current 6-th Harmonic | HAR6_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13248 | Input Channel 7 Current 7-th Harmonic | HAR7_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13249 | Input Channel 7 Current 8-th Harmonic | HAR8_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13250 | Input Channel 7 Current 9-th Harmonic | HAR9_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13251 | Input Channel 7 Current 10-th Harmonic | HAR10_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13252 | Input Channel 7 Current 11-th Harmonic | HAR11_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13253 | Input Channel 7 Current 12-th Harmonic | HAR12_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13254 | Input Channel 7 Current 13-th Harmonic | HAR13_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13255 | Input Channel 7 Current 14-th Harmonic | HAR14_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13256 | Input Channel 7 Current 15-th Harmonic | HAR15_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13257 | Input Channel 7 Current 16-th Harmonic | HAR16_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13258 | Input Channel 7 Current 17-th Harmonic | HAR17_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13259 | Input Channel 7 Current 18-th Harmonic | HAR18_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13260 | Input Channel 7 Current 19-th Harmonic | HAR19_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13261 | Input Channel 7 Current 20-th Harmonic | HAR20_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13262 | Input Channel 7 Current 21-th Harmonic | HAR21_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13263 | Input Channel 7 Current 22-th Harmonic | HAR22_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13264 | Input Channel 7 Current 23-th Harmonic | HAR23_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13265 | Input Channel 7 Current 24-th Harmonic | HAR24_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13266 | Input Channel 7 Current 25-th Harmonic | HAR25_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13267 | Input Channel 7 Current 26-th Harmonic | HAR26_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13268 | Input Channel 7 Current 27-th Harmonic | HAR27_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13269 | Input Channel 7 Current 28-th Harmonic | HAR28_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13270 | Input Channel 7 Current 29-th Harmonic | HAR29_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13271 | Input Channel 7 Current 30-th Harmonic | HAR30_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13272 | Input Channel 7 Current 31-th Harmonic | HAR31_I_007_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13273 | Input Channel 8 Current THD | THD_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13274 | Input Channel 8 Current 2-th Harmonic | HAR2_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13275 | Input Channel 8 Current 3-th Harmonic | HAR3_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13276 | Input Channel 8 Current 4-th Harmonic | HAR4_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13277 | Input Channel 8 Current 5-th Harmonic | HAR5_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13278 | Input Channel 8 Current 6-th Harmonic | HAR6_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13279 | Input Channel 8 Current 7-th Harmonic | HAR7_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13280 | Input Channel 8 Current 8-th Harmonic | HAR8_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13281 | Input Channel 8 Current 9-th Harmonic | HAR9_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13282 | Input Channel 8 Current 10-th Harmonic | HAR10_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13283 | Input Channel 8 Current 11-th Harmonic | HAR11_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13284 | Input Channel 8 Current 12-th Harmonic | HAR12_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13285 | Input Channel 8 Current 13-th Harmonic | HAR13_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13286 | Input Channel 8 Current 14-th Harmonic | HAR14_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13287 | Input Channel 8 Current 15-th Harmonic | HAR15_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13288 | Input Channel 8 Current 16-th Harmonic | HAR16_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13289 | Input Channel 8 Current 17-th Harmonic | HAR17_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13290 | Input Channel 8 Current 18-th Harmonic | HAR18_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13291 | Input Channel 8 Current 19-th Harmonic | HAR19_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13292 | Input Channel 8 Current 20-th Harmonic | HAR20_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13293 | Input Channel 8 Current 21-th Harmonic | HAR21_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13294 | Input Channel 8 Current 22-th Harmonic | HAR22_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13295 | Input Channel 8 Current 23-th Harmonic | HAR23_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13296 | Input Channel 8 Current 24-th Harmonic | HAR24_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13297 | Input Channel 8 Current 25-th Harmonic | HAR25_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13298 | Input Channel 8 Current 26-th Harmonic | HAR26_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13299 | Input Channel 8 Current 27-th Harmonic | HAR27_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13300 | Input Channel 8 Current 28-th Harmonic | HAR28_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13301 | Input Channel 8 Current 29-th Harmonic | HAR29_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13302 | Input Channel 8 Current 30-th Harmonic | HAR30_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13303 | Input Channel 8 Current 31-th Harmonic | HAR31_I_008_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13304 | Input Channel 9 Current THD | THD_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13305 | Input Channel 9 Current 2-th Harmonic | HAR2_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13306 | Input Channel 9 Current 3-th Harmonic | HAR3_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13307 | Input Channel 9 Current 4-th Harmonic | HAR4_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13308 | Input Channel 9 Current 5-th Harmonic | HAR5_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13309 | Input Channel 9 Current 6-th Harmonic | HAR6_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13310 | Input Channel 9 Current 7-th Harmonic | HAR7_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13311 | Input Channel 9 Current 8-th Harmonic | HAR8_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13312 | Input Channel 9 Current 9-th Harmonic | HAR9_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13313 | Input Channel 9 Current 10-th Harmonic | HAR10_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13314 | Input Channel 9 Current 11-th Harmonic | HAR11_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13315 | Input Channel 9 Current 12-th Harmonic | HAR12_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13316 | Input Channel 9 Current 13-th Harmonic | HAR13_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13317 | Input Channel 9 Current 14-th Harmonic | HAR14_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13318 | Input Channel 9 Current 15-th Harmonic | HAR15_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13319 | Input Channel 9 Current 16-th Harmonic | HAR16_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13320 | Input Channel 9 Current 17-th Harmonic | HAR17_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13321 | Input Channel 9 Current 18-th Harmonic | HAR18_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13322 | Input Channel 9 Current 19-th Harmonic | HAR19_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13323 | Input Channel 9 Current 20-th Harmonic | HAR20_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13324 | Input Channel 9 Current 21-th Harmonic | HAR21_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13325 | Input Channel 9 Current 22-th Harmonic | HAR22_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13326 | Input Channel 9 Current 23-th Harmonic | HAR23_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13327 | Input Channel 9 Current 24-th Harmonic | HAR24_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13328 | Input Channel 9 Current 25-th Harmonic | HAR25_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13329 | Input Channel 9 Current 26-th Harmonic | HAR26_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13330 | Input Channel 9 Current 27-th Harmonic | HAR27_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13331 | Input Channel 9 Current 28-th Harmonic | HAR28_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13332 | Input Channel 9 Current 29-th Harmonic | HAR29_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13333 | Input Channel 9 Current 30-th Harmonic | HAR30_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13334 | Input Channel 9 Current 31-th Harmonic | HAR31_I_009_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13335 | Input Channel 10 Current THD | THD_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13336 | Input Channel 10 Current 2-th Harmonic | HAR2_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13337 | Input Channel 10 Current 3-th Harmonic | HAR3_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13338 | Input Channel 10 Current 4-th Harmonic | HAR4_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13339 | Input Channel 10 Current 5-th Harmonic | HAR5_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13340 | Input Channel 10 Current 6-th Harmonic | HAR6_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13341 | Input Channel 10 Current 7-th Harmonic | HAR7_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13342 | Input Channel 10 Current 8-th Harmonic | HAR8_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13343 | Input Channel 10 Current 9-th Harmonic | HAR9_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13344 | Input Channel 10 Current 10-th Harmonic | HAR10_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13345 | Input Channel 10 Current 11-th Harmonic | HAR11_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13346 | Input Channel 10 Current 12-th Harmonic | HAR12_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13347 | Input Channel 10 Current 13-th Harmonic | HAR13_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13348 | Input Channel 10 Current 14-th Harmonic | HAR14_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13349 | Input Channel 10 Current 15-th Harmonic | HAR15_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13350 | Input Channel 10 Current 16-th Harmonic | HAR16_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13351 | Input Channel 10 Current 17-th Harmonic | HAR17_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13352 | Input Channel 10 Current 18-th Harmonic | HAR18_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13353 | Input Channel 10 Current 19-th Harmonic | HAR19_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13354 | Input Channel 10 Current 20-th Harmonic | HAR20_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13355 | Input Channel 10 Current 21-th Harmonic | HAR21_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13356 | Input Channel 10 Current 22-th Harmonic | HAR22_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13357 | Input Channel 10 Current 23-th Harmonic | HAR23_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13358 | Input Channel 10 Current 24-th Harmonic | HAR24_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13359 | Input Channel 10 Current 25-th Harmonic | HAR25_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13360 | Input Channel 10 Current 26-th Harmonic | HAR26_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13361 | Input Channel 10 Current 27-th Harmonic | HAR27_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13362 | Input Channel 10 Current 28-th Harmonic | HAR28_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13363 | Input Channel 10 Current 29-th Harmonic | HAR29_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13364 | Input Channel 10 Current 30-th Harmonic | HAR30_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13365 | Input Channel 10 Current 31-th Harmonic | HAR31_I_010_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13366 | Input Channel 11 Current THD | THD_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13367 | Input Channel 11 Current 2-th Harmonic | HAR2_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13368 | Input Channel 11 Current 3-th Harmonic | HAR3_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13369 | Input Channel 11 Current 4-th Harmonic | HAR4_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13370 | Input Channel 11 Current 5-th Harmonic | HAR5_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13371 | Input Channel 11 Current 6-th Harmonic | HAR6_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13372 | Input Channel 11 Current 7-th Harmonic | HAR7_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13373 | Input Channel 11 Current 8-th Harmonic | HAR8_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13374 | Input Channel 11 Current 9-th Harmonic | HAR9_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13375 | Input Channel 11 Current 10-th Harmonic | HAR10_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13376 | Input Channel 11 Current 11-th Harmonic | HAR11_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13377 | Input Channel 11 Current 12-th Harmonic | HAR12_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13378 | Input Channel 11 Current 13-th Harmonic | HAR13_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13379 | Input Channel 11 Current 14-th Harmonic | HAR14_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13380 | Input Channel 11 Current 15-th Harmonic | HAR15_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13381 | Input Channel 11 Current 16-th Harmonic | HAR16_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13382 | Input Channel 11 Current 17-th Harmonic | HAR17_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13383 | Input Channel 11 Current 18-th Harmonic | HAR18_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13384 | Input Channel 11 Current 19-th Harmonic | HAR19_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13385 | Input Channel 11 Current 20-th Harmonic | HAR20_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13386 | Input Channel 11 Current 21-th Harmonic | HAR21_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13387 | Input Channel 11 Current 22-th Harmonic | HAR22_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13388 | Input Channel 11 Current 23-th Harmonic | HAR23_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13389 | Input Channel 11 Current 24-th Harmonic | HAR24_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13390 | Input Channel 11 Current 25-th Harmonic | HAR25_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13391 | Input Channel 11 Current 26-th Harmonic | HAR26_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13392 | Input Channel 11 Current 27-th Harmonic | HAR27_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13393 | Input Channel 11 Current 28-th Harmonic | HAR28_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13394 | Input Channel 11 Current 29-th Harmonic | HAR29_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13395 | Input Channel 11 Current 30-th Harmonic | HAR30_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13396 | Input Channel 11 Current 31-th Harmonic | HAR31_I_011_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13397 | Input Channel 12 Current THD | THD_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13398 | Input Channel 12 Current 2-th Harmonic | HAR2_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13399 | Input Channel 12 Current 3-th Harmonic | HAR3_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13400 | Input Channel 12 Current 4-th Harmonic | HAR4_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13401 | Input Channel 12 Current 5-th Harmonic | HAR5_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13402 | Input Channel 12 Current 6-th Harmonic | HAR6_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13403 | Input Channel 12 Current 7-th Harmonic | HAR7_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13404 | Input Channel 12 Current 8-th Harmonic | HAR8_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13405 | Input Channel 12 Current 9-th Harmonic | HAR9_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13406 | Input Channel 12 Current 10-th Harmonic | HAR10_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13407 | Input Channel 12 Current 11-th Harmonic | HAR11_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13408 | Input Channel 12 Current 12-th Harmonic | HAR12_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13409 | Input Channel 12 Current 13-th Harmonic | HAR13_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13410 | Input Channel 12 Current 14-th Harmonic | HAR14_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13411 | Input Channel 12 Current 15-th Harmonic | HAR15_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13412 | Input Channel 12 Current 16-th Harmonic | HAR16_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13413 | Input Channel 12 Current 17-th Harmonic | HAR17_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13414 | Input Channel 12 Current 18-th Harmonic | HAR18_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13415 | Input Channel 12 Current 19-th Harmonic | HAR19_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13416 | Input Channel 12 Current 20-th Harmonic | HAR20_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13417 | Input Channel 12 Current 21-th Harmonic | HAR21_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13418 | Input Channel 12 Current 22-th Harmonic | HAR22_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13419 | Input Channel 12 Current 23-th Harmonic | HAR23_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13420 | Input Channel 12 Current 24-th Harmonic | HAR24_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13421 | Input Channel 12 Current 25-th Harmonic | HAR25_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13422 | Input Channel 12 Current 26-th Harmonic | HAR26_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13423 | Input Channel 12 Current 27-th Harmonic | HAR27_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13424 | Input Channel 12 Current 28-th Harmonic | HAR28_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13425 | Input Channel 12 Current 29-th Harmonic | HAR29_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13426 | Input Channel 12 Current 30-th Harmonic | HAR30_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13427 | Input Channel 12 Current 31-th Harmonic | HAR31_I_012_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13428 | Input Channel 13 Current THD | THD_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13429 | Input Channel 13 Current 2-th Harmonic | HAR2_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13430 | Input Channel 13 Current 3-th Harmonic | HAR3_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13431 | Input Channel 13 Current 4-th Harmonic | HAR4_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13432 | Input Channel 13 Current 5-th Harmonic | HAR5_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13433 | Input Channel 13 Current 6-th Harmonic | HAR6_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13434 | Input Channel 13 Current 7-th Harmonic | HAR7_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13435 | Input Channel 13 Current 8-th Harmonic | HAR8_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13436 | Input Channel 13 Current 9-th Harmonic | HAR9_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13437 | Input Channel 13 Current 10-th Harmonic | HAR10_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13438 | Input Channel 13 Current 11-th Harmonic | HAR11_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13439 | Input Channel 13 Current 12-th Harmonic | HAR12_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13440 | Input Channel 13 Current 13-th Harmonic | HAR13_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13441 | Input Channel 13 Current 14-th Harmonic | HAR14_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13442 | Input Channel 13 Current 15-th Harmonic | HAR15_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13443 | Input Channel 13 Current 16-th Harmonic | HAR16_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13444 | Input Channel 13 Current 17-th Harmonic | HAR17_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13445 | Input Channel 13 Current 18-th Harmonic | HAR18_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13446 | Input Channel 13 Current 19-th Harmonic | HAR19_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13447 | Input Channel 13 Current 20-th Harmonic | HAR20_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13448 | Input Channel 13 Current 21-th Harmonic | HAR21_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13449 | Input Channel 13 Current 22-th Harmonic | HAR22_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13450 | Input Channel 13 Current 23-th Harmonic | HAR23_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13451 | Input Channel 13 Current 24-th Harmonic | HAR24_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13452 | Input Channel 13 Current 25-th Harmonic | HAR25_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13453 | Input Channel 13 Current 26-th Harmonic | HAR26_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13454 | Input Channel 13 Current 27-th Harmonic | HAR27_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13455 | Input Channel 13 Current 28-th Harmonic | HAR28_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13456 | Input Channel 13 Current 29-th Harmonic | HAR29_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13457 | Input Channel 13 Current 30-th Harmonic | HAR30_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13458 | Input Channel 13 Current 31-th Harmonic | HAR31_I_013_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13459 | Input Channel 14 Current THD | THD_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13460 | Input Channel 14 Current 2-th Harmonic | HAR2_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13461 | Input Channel 14 Current 3-th Harmonic | HAR3_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13462 | Input Channel 14 Current 4-th Harmonic | HAR4_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13463 | Input Channel 14 Current 5-th Harmonic | HAR5_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13464 | Input Channel 14 Current 6-th Harmonic | HAR6_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13465 | Input Channel 14 Current 7-th Harmonic | HAR7_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13466 | Input Channel 14 Current 8-th Harmonic | HAR8_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13467 | Input Channel 14 Current 9-th Harmonic | HAR9_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13468 | Input Channel 14 Current 10-th Harmonic | HAR10_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13469 | Input Channel 14 Current 11-th Harmonic | HAR11_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13470 | Input Channel 14 Current 12-th Harmonic | HAR12_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13471 | Input Channel 14 Current 13-th Harmonic | HAR13_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13472 | Input Channel 14 Current 14-th Harmonic | HAR14_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13473 | Input Channel 14 Current 15-th Harmonic | HAR15_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13474 | Input Channel 14 Current 16-th Harmonic | HAR16_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13475 | Input Channel 14 Current 17-th Harmonic | HAR17_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13476 | Input Channel 14 Current 18-th Harmonic | HAR18_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13477 | Input Channel 14 Current 19-th Harmonic | HAR19_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13478 | Input Channel 14 Current 20-th Harmonic | HAR20_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13479 | Input Channel 14 Current 21-th Harmonic | HAR21_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13480 | Input Channel 14 Current 22-th Harmonic | HAR22_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13481 | Input Channel 14 Current 23-th Harmonic | HAR23_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13482 | Input Channel 14 Current 24-th Harmonic | HAR24_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13483 | Input Channel 14 Current 25-th Harmonic | HAR25_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13484 | Input Channel 14 Current 26-th Harmonic | HAR26_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13485 | Input Channel 14 Current 27-th Harmonic | HAR27_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13486 | Input Channel 14 Current 28-th Harmonic | HAR28_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13487 | Input Channel 14 Current 29-th Harmonic | HAR29_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13488 | Input Channel 14 Current 30-th Harmonic | HAR30_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13489 | Input Channel 14 Current 31-th Harmonic | HAR31_I_014_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13490 | Input Channel 15 Current THD | THD_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13491 | Input Channel 15 Current 2-th Harmonic | HAR2_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13492 | Input Channel 15 Current 3-th Harmonic | HAR3_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13493 | Input Channel 15 Current 4-th Harmonic | HAR4_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13494 | Input Channel 15 Current 5-th Harmonic | HAR5_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13495 | Input Channel 15 Current 6-th Harmonic | HAR6_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13496 | Input Channel 15 Current 7-th Harmonic | HAR7_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13497 | Input Channel 15 Current 8-th Harmonic | HAR8_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13498 | Input Channel 15 Current 9-th Harmonic | HAR9_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13499 | Input Channel 15 Current 10-th Harmonic | HAR10_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13500 | Input Channel 15 Current 11-th Harmonic | HAR11_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13501 | Input Channel 15 Current 12-th Harmonic | HAR12_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13502 | Input Channel 15 Current 13-th Harmonic | HAR13_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13503 | Input Channel 15 Current 14-th Harmonic | HAR14_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13504 | Input Channel 15 Current 15-th Harmonic | HAR15_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13505 | Input Channel 15 Current 16-th Harmonic | HAR16_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13506 | Input Channel 15 Current 17-th Harmonic | HAR17_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13507 | Input Channel 15 Current 18-th Harmonic | HAR18_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13508 | Input Channel 15 Current 19-th Harmonic | HAR19_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13509 | Input Channel 15 Current 20-th Harmonic | HAR20_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13510 | Input Channel 15 Current 21-th Harmonic | HAR21_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13511 | Input Channel 15 Current 22-th Harmonic | HAR22_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13512 | Input Channel 15 Current 23-th Harmonic | HAR23_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13513 | Input Channel 15 Current 24-th Harmonic | HAR24_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13514 | Input Channel 15 Current 25-th Harmonic | HAR25_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13515 | Input Channel 15 Current 26-th Harmonic | HAR26_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13516 | Input Channel 15 Current 27-th Harmonic | HAR27_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13517 | Input Channel 15 Current 28-th Harmonic | HAR28_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13518 | Input Channel 15 Current 29-th Harmonic | HAR29_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13519 | Input Channel 15 Current 30-th Harmonic | HAR30_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13520 | Input Channel 15 Current 31-th Harmonic | HAR31_I_015_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13521 | Input Channel 16 Current THD | THD_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13522 | Input Channel 16 Current 2-th Harmonic | HAR2_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13523 | Input Channel 16 Current 3-th Harmonic | HAR3_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13524 | Input Channel 16 Current 4-th Harmonic | HAR4_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13525 | Input Channel 16 Current 5-th Harmonic | HAR5_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13526 | Input Channel 16 Current 6-th Harmonic | HAR6_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13527 | Input Channel 16 Current 7-th Harmonic | HAR7_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13528 | Input Channel 16 Current 8-th Harmonic | HAR8_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13529 | Input Channel 16 Current 9-th Harmonic | HAR9_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13530 | Input Channel 16 Current 10-th Harmonic | HAR10_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13531 | Input Channel 16 Current 11-th Harmonic | HAR11_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13532 | Input Channel 16 Current 12-th Harmonic | HAR12_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13533 | Input Channel 16 Current 13-th Harmonic | HAR13_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13534 | Input Channel 16 Current 14-th Harmonic | HAR14_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13535 | Input Channel 16 Current 15-th Harmonic | HAR15_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13536 | Input Channel 16 Current 16-th Harmonic | HAR16_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13537 | Input Channel 16 Current 17-th Harmonic | HAR17_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13538 | Input Channel 16 Current 18-th Harmonic | HAR18_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13539 | Input Channel 16 Current 19-th Harmonic | HAR19_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13540 | Input Channel 16 Current 20-th Harmonic | HAR20_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13541 | Input Channel 16 Current 21-th Harmonic | HAR21_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13542 | Input Channel 16 Current 22-th Harmonic | HAR22_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13543 | Input Channel 16 Current 23-th Harmonic | HAR23_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13544 | Input Channel 16 Current 24-th Harmonic | HAR24_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13545 | Input Channel 16 Current 25-th Harmonic | HAR25_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13546 | Input Channel 16 Current 26-th Harmonic | HAR26_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13547 | Input Channel 16 Current 27-th Harmonic | HAR27_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13548 | Input Channel 16 Current 28-th Harmonic | HAR28_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13549 | Input Channel 16 Current 29-th Harmonic | HAR29_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13550 | Input Channel 16 Current 30-th Harmonic | HAR30_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13551 | Input Channel 16 Current 31-th Harmonic | HAR31_I_016_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13552 | Input Channel 17 Current THD | THD_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13553 | Input Channel 17 Current 2-th Harmonic | HAR2_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13554 | Input Channel 17 Current 3-th Harmonic | HAR3_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13555 | Input Channel 17 Current 4-th Harmonic | HAR4_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13556 | Input Channel 17 Current 5-th Harmonic | HAR5_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13557 | Input Channel 17 Current 6-th Harmonic | HAR6_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13558 | Input Channel 17 Current 7-th Harmonic | HAR7_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13559 | Input Channel 17 Current 8-th Harmonic | HAR8_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13560 | Input Channel 17 Current 9-th Harmonic | HAR9_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13561 | Input Channel 17 Current 10-th Harmonic | HAR10_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13562 | Input Channel 17 Current 11-th Harmonic | HAR11_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13563 | Input Channel 17 Current 12-th Harmonic | HAR12_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13564 | Input Channel 17 Current 13-th Harmonic | HAR13_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13565 | Input Channel 17 Current 14-th Harmonic | HAR14_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13566 | Input Channel 17 Current 15-th Harmonic | HAR15_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13567 | Input Channel 17 Current 16-th Harmonic | HAR16_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13568 | Input Channel 17 Current 17-th Harmonic | HAR17_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13569 | Input Channel 17 Current 18-th Harmonic | HAR18_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13570 | Input Channel 17 Current 19-th Harmonic | HAR19_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13571 | Input Channel 17 Current 20-th Harmonic | HAR20_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13572 | Input Channel 17 Current 21-th Harmonic | HAR21_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13573 | Input Channel 17 Current 22-th Harmonic | HAR22_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13574 | Input Channel 17 Current 23-th Harmonic | HAR23_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13575 | Input Channel 17 Current 24-th Harmonic | HAR24_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13576 | Input Channel 17 Current 25-th Harmonic | HAR25_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13577 | Input Channel 17 Current 26-th Harmonic | HAR26_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13578 | Input Channel 17 Current 27-th Harmonic | HAR27_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13579 | Input Channel 17 Current 28-th Harmonic | HAR28_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13580 | Input Channel 17 Current 29-th Harmonic | HAR29_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13581 | Input Channel 17 Current 30-th Harmonic | HAR30_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13582 | Input Channel 17 Current 31-th Harmonic | HAR31_I_017_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13583 | Input Channel 18 Current THD | THD_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
13584 | Input Channel 18 Current 2-th Harmonic | HAR2_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13585 | Input Channel 18 Current 3-th Harmonic | HAR3_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13586 | Input Channel 18 Current 4-th Harmonic | HAR4_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13587 | Input Channel 18 Current 5-th Harmonic | HAR5_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13588 | Input Channel 18 Current 6-th Harmonic | HAR6_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13589 | Input Channel 18 Current 7-th Harmonic | HAR7_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13590 | Input Channel 18 Current 8-th Harmonic | HAR8_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13591 | Input Channel 18 Current 9-th Harmonic | HAR9_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13592 | Input Channel 18 Current 10-th Harmonic | HAR10_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13593 | Input Channel 18 Current 11-th Harmonic | HAR11_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13594 | Input Channel 18 Current 12-th Harmonic | HAR12_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13595 | Input Channel 18 Current 13-th Harmonic | HAR13_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13596 | Input Channel 18 Current 14-th Harmonic | HAR14_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13597 | Input Channel 18 Current 15-th Harmonic | HAR15_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13598 | Input Channel 18 Current 16-th Harmonic | HAR16_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13599 | Input Channel 18 Current 17-th Harmonic | HAR17_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13600 | Input Channel 18 Current 18-th Harmonic | HAR18_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13601 | Input Channel 18 Current 19-th Harmonic | HAR19_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13602 | Input Channel 18 Current 20-th Harmonic | HAR20_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13603 | Input Channel 18 Current 21-th Harmonic | HAR21_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13604 | Input Channel 18 Current 22-th Harmonic | HAR22_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13605 | Input Channel 18 Current 23-th Harmonic | HAR23_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13606 | Input Channel 18 Current 24-th Harmonic | HAR24_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13607 | Input Channel 18 Current 25-th Harmonic | HAR25_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13608 | Input Channel 18 Current 26-th Harmonic | HAR26_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13609 | Input Channel 18 Current 27-th Harmonic | HAR27_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13610 | Input Channel 18 Current 28-th Harmonic | HAR28_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13611 | Input Channel 18 Current 29-th Harmonic | HAR29_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13612 | Input Channel 18 Current 30-th Harmonic | HAR30_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13613 | Input Channel 18 Current 31-th Harmonic | HAR31_I_018_% | % |  | int16 | 12 | R | 1 | 0.01 | [7 empty] | harmonics |  | harmonics
13614 | User Channel 1 Current Unbalance Factor | UNBL_I_s001_% | % |  | int16 | 12 | R | 1 | 0.01 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
13615 | User Channel 2 Current Unbalance Factor | UNBL_I_s002_% | % |  | int16 | 12 | R | 1 | 0.01 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
13616 | User Channel 3 Current Unbalance Factor | UNBL_I_s003_% | % |  | int16 | 12 | R | 1 | 0.01 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
13617 | User Channel 4 Current Unbalance Factor | UNBL_I_s004_% | % |  | int16 | 12 | R | 1 | 0.01 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
13618 | User Channel 5 Current Unbalance Factor | UNBL_I_s005_% | % |  | int16 | 12 | R | 1 | 0.01 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
13619 | User Channel 6 Current Unbalance Factor | UNBL_I_s006_% | % |  | int16 | 12 | R | 1 | 0.01 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
13620 | User Channel 7 Current Unbalance Factor | UNBL_I_s007_% | % |  | int16 | 12 | R | 1 | 0.01 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
13621 | User Channel 8 Current Unbalance Factor | UNBL_I_s008_% | % |  | int16 | 12 | R | 1 | 0.01 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
13622 | User Channel 9 Current Unbalance Factor | UNBL_I_s009_% | % |  | int16 | 12 | R | 1 | 0.01 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
13824 | Phase Angle of V2 to V1 Vb/Vbc phase angle | ANG_VLN_b | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13825 | Phase Angle of V3 to V1 Vc/Vca phase angle | ANG_VLN_c | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13826 | Phase Angle of Load 1 Current to V1 | ANG_I_001 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13827 | Phase Angle of Load 2 Current to V2 | ANG_I_002 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13828 | Phase Angle of Load 3 Current to V3 | ANG_I_003 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13829 | Phase Angle of Load 4 Current to V4 | ANG_I_004 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13830 | Phase Angle of Load 5 Current to V5 | ANG_I_005 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13831 | Phase Angle of Load 6 Current to V6 | ANG_I_006 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13832 | Phase Angle of Load 7 Current to V7 | ANG_I_007 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13833 | Phase Angle of Load 8 Current to V8 | ANG_I_008 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13834 | Phase Angle of Load 9 Current to V9 | ANG_I_009 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13835 | Phase Angle of Load 10 Current to V10 | ANG_I_010 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13836 | Phase Angle of Load 11 Current to V11 | ANG_I_011 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13837 | Phase Angle of Load 12 Current to V12 | ANG_I_012 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13838 | Phase Angle of Load 13 Current to V13 | ANG_I_013 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13839 | Phase Angle of Load 14 Current to V14 | ANG_I_014 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13840 | Phase Angle of Load 15 Current to V15 | ANG_I_015 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13841 | Phase Angle of Load 16 Current to V16 | ANG_I_016 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13842 | Phase Angle of Load 17 Current to V17 | ANG_I_017 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13843 | Phase Angle of Load 18 Current to V18 | ANG_I_018 | ° |  | int16 | 12 | R | 1 | 0.1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
2048 | Channel 1 Address | Conf_Ch1_Addr |  |  | uint16 | 12 | R/W | 1 | 1
2049 | Channel 1 Parity | Conf_Ch1_Parity |  |  | uint16 | 12 | R/W | 1 | 1
2050 | Channel 2 Parity | Conf_Ch2_Parity |  |  | uint16 | 12 | R/W | 1 | 1
2051 | Channel 1 Baud Rate | Conf_Ch1_Baud |  |  | uint16 | 12 | R/W | 1 | 1
2052 | Channel 2 Baud Rate | Conf_Ch2_Baud |  |  | uint16 | 12 | R/W | 1 | 1
2053 | Password | Conf_Password |  |  | uint16 | 12 | R/W | 1 | 1
2054 | Pulse Constant | Conf_PulseConst |  |  | uint16 | 12 | R/W | 1 | 1
2055 | Pulse Width | Conf_PulseWidth |  |  | uint16 | 12 | R/W | 1 | 1
2056 | Channel 2 Address | Conf_Ch2_Addr |  |  | uint16 | 12 | R/W | 1 | 1
2058 | Demand Method | Conf_Dmd_Method |  |  | uint16 | 12 | R/W | 1 | 1
2059 | Demand Window | Conf_Dmd_Window |  |  | uint16 | 12 | R/W | 1 | 1
2060 | Demand Sub Interval | Conf_Dmd_SubInterval |  |  | uint16 | 12 | R/W | 1 | 1
2061 | CT2 Value | Conf_CT2 |  |  | uint16 | 12 | R/W | 1 | 1
2097 | LCD Backlight Time | Conf_Backlight_Time |  |  | uint16 | 12 | R/W | 1 | 1
2101 | Reactive Power Calculation Method | Conf_CalcMethod_Q |  |  | uint16 | 12 | R/W | 1 | 1
2102 | VAR/PF Convention | Conf_CalcMethod_VarPF |  |  | uint16 | 12 | R/W | 1 | 1
2183 | Nominal Voltage | Conf_NominalVolt |  |  | uint16 | 12 | R/W | 1 | 1
2184 | Service Configuration | Conf_ServiceConfig |  |  | uint16 | 12 | R/W | 1 | 1
2185 | Input Channel 1 CT | Conf_001_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2186 | Input Channel 2 CT | Conf_002_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2187 | Input Channel 3 CT | Conf_003_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2188 | Input Channel 4 CT | Conf_004_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2189 | Input Channel 5 CT | Conf_005_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2190 | Input Channel 6 CT | Conf_006_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2191 | Input Channel 7 CT | Conf_007_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2192 | Input Channel 8 CT | Conf_008_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2193 | Input Channel 9 CT | Conf_009_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2194 | Input Channel 10 CT | Conf_010_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2195 | Input Channel 11 CT | Conf_011_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2196 | Input Channel 12 CT | Conf_012_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2197 | Input Channel 13 CT | Conf_013_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2198 | Input Channel 14 CT | Conf_014_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2199 | Input Channel 15 CT | Conf_015_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2200 | Input Channel 16 CT | Conf_016_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2201 | Input Channel 17 CT | Conf_017_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
2202 | Input Channel 18 CT | Conf_018_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
61723 | CT2 Type | Info_CT2_Type |  |  | uint16 | 12 | R | 1 | 1
61440 | Meter Model | Info_MeterModel |  |  | uint32 | 12 | R | 2 | 1
61442 | Hardware version | Info_HardwareVersion |  |  | uint32 | 12 | R | 2 | 1
61444 | Software version | Info_SoftwareVersion |  |  | uint32 | 12 | R | 2 | 1
61446 | Software date | Info_SoftwareDate |  |  | uint32 | 12 | R | 3 | 1
2221 | Restore Factory Setting | Conf_Restore_FactorySetting |  |  | uint16 | 12 | W | 1 | 1
2222 | Enable 10 Years TOU settings | Conf_TOU_Enable10Years |  |  | uint16 | 12 | R/W | 1 | 1
2223 | Non-Standard Content Seal Option | Conf_Seal_Option |  |  | uint16 | 12 | R/W | 1 | 1
2224 | Sealing Status | Info_Seal_Status |  |  | uint16 | 12 | R | 1 | 1
2111 | user01 User Name | Conf_NAME_s001 | [5 empty] | 3
2115 | user02 User Name | Conf_NAME_s002 | [5 empty] | 3
2119 | user03 User Name | Conf_NAME_s003 | [5 empty] | 3
2123 | user04 User Name | Conf_NAME_s004 | [5 empty] | 3
2127 | user05 User Name | Conf_NAME_s005 | [5 empty] | 3
2131 | user06 User Name | Conf_NAME_s006 | [5 empty] | 3
2135 | user07 User Name | Conf_NAME_s007 | [5 empty] | 3
2139 | user08 User Name | Conf_NAME_s008 | [5 empty] | 3
2143 | user09 User Name | Conf_NAME_s009 | [5 empty] | 3
2147 | user10 User Name | Conf_NAME_s010 | [5 empty] | 3
2151 | user11 User Name | Conf_NAME_s011 | [5 empty] | 3
2155 | user12 User Name | Conf_NAME_s012 | [5 empty] | 3
2159 | user13 User Name | Conf_NAME_s013 | [5 empty] | 3
2163 | user14 User Name | Conf_NAME_s014 | [5 empty] | 3
2167 | user15 User Name | Conf_NAME_s015 | [5 empty] | 3
2171 | user16 User Name | Conf_NAME_s016 | [5 empty] | 3
2175 | user17 User Name | Conf_NAME_s017 | [5 empty] | 3
2179 | user18 User Name | Conf_NAME_s018 | [5 empty] | 3