## Version history
Version | Changes | Author | Reviewer | Date | External Firmware Version
V1.0.0 | 初次定义 1.根据需求规格书定义basic setting、DIDORO、AIAO、Information、Calibration 项 | 侯保亮/杨月 |  | 2025-02-28
V1.0.1 | 修改 DI SOE功能 | 侯保亮/杨月 |  | 2025-03-03
V1.0.2 | Update modbus address according to software requirements. | 王少英 |  | 2025-04-24
V1.0.3 | (1) Delete RTU enable in [Basic Configuration] (2) Extract [DI Status] and [DO RO Status] as seperated sheet (3) SOE Log format is changed same as 4100 (4) Product Info format is changed same as 4100 (5) AiAo Setting: Add the interval between AI Setting and AO Setting (6) AI Original Data/AI physical measurement readings/AO output data/AO physical measurement readings: separate as AIAO Data page (7) Calibration: Add the interval between Calibration Commands and Calibration coefficients (8) Increase scalability by putting AI Gain and AI OffSet in one group, and AOGain and AI OffSet in another group (9) DI is changed to 14/28 ports. | 王少英/ 侯保亮 |  | 2025-06-18

## Overview
Block | Sheet | Start | End | Length (reg num) | Comments
DI Status | DI Status | 0x0000 | 0x001B | 28
DO Status | DO RO Status | 0x0000 | 0x0003 | 4
RO Status | DO RO Status | 0x0020 | 0x0021 | 2
Basic Meter Settings | Basic Configuration | 0x1000 | 0x101A | 27
Real-time clock | Basic Configuration | 0x1100 | 0x1106 | 7
Clear & Reset | Basic Configuration | 0x1200 | 0x1205 | 6
DI Settings | DI | 0x2000 | 0x2053 | 84
DI Pulse Count | DI | 0x2200 | 0x2237 | 56
DI Physical measurement readings | DI | 0x2300 | 0x2337 | 56
AI Setting | AIAO Setting | 0x3000 | 0x315F | 352
AO Setting | AIAO Setting | 0x3400 | 0x3457 | 88
AI Original Data | AIAO Data | 0x3500 | 0x351F | 32
AI physical measurement readings | AIAO Data | 0x3700 | 0x371F | 32
AO Output data | AIAO Data | 0x3900 | 0x3907 | 8
AO physical measurement readings | AIAO Data | 0x3950 | 0x3957 | 8
DO Settings | DO | 0x4000 | 0x4007 | 8
AI Calibration Commands | Calibration | 0x5000 | 0x5002 | 3
AO Calibration Commands | Calibration | 0x5100 | 0x5112 | 19
AI Gain OffSet Coef | Calibration | 0x5300 | 0x533F | 64
AO Gain OffSet Coef | Calibration | 0x5500 | 0x550F | 16
RO Settings | RO | 0x6000 | 0x6003 | 4
SOE Log Status | SOE Log | 0x6300 | 0x6301 | 2
SOE Log Read Window | SOE Log | 0x6302 | 0x637C | 123
Firmware Version Info | Information | 0xF000 | 0xF005 | 6
Reboot | Information | 0xF000 | 0xF001 | 2
Bootloader Info | Information | 0xF010 | 0xF017 | 8
Product Info | Information | 0xF040 | 0xF070 | 49

## Basic Configuration
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Basic Meter Settings | 0x1000 | 0x1000 | 4096 | 4096 | device password | word | R/W | 1 | 0－9999 | 0 | 0
| 0x1001 | 0x1001 | 4097 | 4097 | RS485 baud rate | word | R/W | 1 | 2400\4800\9600\14400\19200\38400\56000\57600\76800\115200(76800 need send 7680 115200need send 11520) | 19200 | 19200
| 0x1002 | 0x1002 | 4098 | 4098 | RS485 parity | word | R/W | 1 | 0：even 1：odd 2：Non2 3：Non1 | 3 | 3
| 0x1003 | 0x1003 | 4099 | 4099 | DHCP enable | word | R/W | 1 | 0: manual 1: DHCP | 0 | 0
| 0x1004 | 0x1004 | 4100 | 4100 | IP address 1st byte (high) IP address 2nd byte (low) | word | R/W | 1 | 0~255 | 192 168 1 254 | 192 168 1 254
| 0x1005 | 0x1005 | 4101 | 4101 | IP address 3rd byte (high) IP address 4th byte (low) | word | R/W | 1 | 0~255
| 0x1006 | 0x1006 | 4102 | 4102 | Subnet mask 1st byte (high) Subnet mask 2nd byte (low) | word | R/W | 1 | 0~255 | 255 255 255 0 | 255 255 255 0
| 0x1007 | 0x1007 | 4103 | 4103 | Subnet mask 3rd byte (high) Subnet mask 4th byte (low) | word | R/W | 1 | 0~255
| 0x1008 | 0x1008 | 4104 | 4104 | Gateway 1st byte (high) Gateway 2nd byte (low) | word | R/W | 1 | 0~255 | 192 168 1 1 | 192 168 1 1
| 0x1009 | 0x1009 | 4105 | 4105 | Gateway 3rd byte (high) Gateway 4th byte (low) | word | R/W | 1 | 0~255
| 0x100A | 0x100A | 4106 | 4106 | DNS primary server 1st byte (high) DNS primary server 2nd byte (low) | word | R/W | 1 | 0~255 | 8 8 8 8 | 8 8 8 8
| 0x100B | 0x100B | 4107 | 4107 | DNS primary server 3rd byte (high) DNS primary server 4th byte (low) | word | R/W | 1 | 0~255
| 0x100C | 0x100C | 4108 | 4108 | DNS secondary server 1st byte (high) DNS secondary server 2nd byte (low) | word | R/W | 1 | 0~255 | 8.8.4.4 | 8.8.4.4
| 0x100D | 0x100D | 4109 | 4109 | DNS secondary server 3rd byte (high) DNS secondary server 4th byte (low) | word | R/W | 1 | 0~255
| 0x100E | 0x100E | 4110 | 4110 | Modbus Slave ID | word | R/W | 1 | 1-247, used for both Modbus RTU and TCP | 1 | 1
| 0x100F | 0x100F | 4111 | 4111 | RS485 protocol | word | R/W | 1 | 0: disable 1: Modbus RTU 2: BACnet MS/TP | 1 | 1
| 0x1010 | 0x1010 | 4112 | 4112 | Modbus TCP Enable | word | R/W | 1 | 0: disable 1: enable | 1 | 1
| 0x1011 | 0x1011 | 4113 | 4113 | Modbus TCP port | word | R/W | 1 | 1-65534 | 502 | 502
| 0x1012 | 0x1012 | 4114 | 4114 | BACnet MS/TP Meter address | word | R/W | 1 | 0 - 127 | 1
| 0x1013 | 0x1013 | 4115 | 4115 | BACnet MS/TP Maximum number of message frames | word | R/W | 1 | 1 - 255 | 255 | 255
| 0x1014 | 0x1015 | 4116 | 4117 | BACnet MS/TP ID | uint32_t | R/W | 2 | 1 - 4194303(0x3FFFFF) | 0 | 0
| 0x1016 | 0x1016 | 4118 | 4118 | BACnet MS/TP Database Revision | word | R | 1 | 0 - 65535(0xFFFF) | 0 | 0
| 0x1017 | 0x1017 | 4119 | 4119 | Sealing Status | word | R | 1 | sealed: 0x0A unsealed: 0
| 0x1018 | 0x1019 | 4120 | 4121 | Device run time | uint32_t | RW | 2 | uint in second
Real-time clock
| 0x1100 | 0x1100 | 4352 | 4352 | Week | word | R/W | 1 | 1~7 | 3 | 3
| 0x1101 | 0x1101 | 4353 | 4353 | Year | word | R/W | 1 | 2000~2099 | 2025 | 2025
| 0x1102 | 0x1102 | 4354 | 4354 | Month | word | R/W | 1 | 1~12 | 1 | 1
| 0x1103 | 0x1103 | 4355 | 4355 | Day | word | R/W | 1 | 1~31 | 1 | 1
| 0x1104 | 0x1104 | 4356 | 4356 | Hour | word | R/W | 1 | 0~23 | 0 | 0
| 0x1105 | 0x1105 | 4357 | 4357 | Minute | word | R/W | 1 | 0~59 | 0 | 0
| 0x1106 | 0x1106 | 4358 | 4358 | Second | word | R/W | 1 | 0~59 | 0 | 0
Clear & Reset
| 0x1200 | 0x1200 | 4608 | 4608 | Clear device run time | word | W | 1 | 0: None 1: Clearing | 0 | 0
| 0x1201 | 0x1201 | 4609 | 4609 | Reboot | word | W | 1 | 0: None 1: Reboot | 0 | 0
| 0x1202 | 0x1202 | 4610 | 4610 | Factory reset and reboot | word | W | 1 | 0: None 1: Reset & Reboot | 0 | 0
| 0x1203 | 0x1203 | 4611 | 4611 | Network reset | word | W | 1 | 0: None 1: Resetting | 0 | 0
| 0x1204 | 0x1204 | 4612 | 4612 | Clear SOE Log | word | W | 1 | 0: None 1: Clearing | 0 | 0
| 0x1205 | 0x1205 | 4613 | 4613 | Clear DI Count | word | W | 1 | 0: None 1: Clearing | 0 | 0

## DI
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
DI Settings | 0x2000 | 0x2000 | 8192 | 8192 | DI1 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2001 | 0x2002 | 8193 | 8194 | DI1 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2003 | 0x2003 | 8195 | 8195 | DI2 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2004 | 0x2005 | 8196 | 8197 | DI2 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2006 | 0x2006 | 8198 | 8198 | DI3 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2007 | 0x2008 | 8199 | 8200 | DI3 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2009 | 0x2009 | 8201 | 8201 | DI4 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x200A | 0x200B | 8202 | 8203 | DI4 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x200C | 0x200C | 8204 | 8204 | DI5 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x200D | 0x200E | 8205 | 8206 | DI5 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x200F | 0x200F | 8207 | 8207 | DI6 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2010 | 0x2011 | 8208 | 8209 | DI6 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2012 | 0x2012 | 8210 | 8210 | DI7 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2013 | 0x2014 | 8211 | 8212 | DI7 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2015 | 0x2015 | 8213 | 8213 | DI8 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2016 | 0x2017 | 8214 | 8215 | DI8 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2018 | 0x2018 | 8216 | 8216 | DI9 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2019 | 0x201A | 8217 | 8218 | DI9 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x201B | 0x201B | 8219 | 8219 | DI10 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x201C | 0x201D | 8220 | 8221 | DI10 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x201E | 0x201E | 8222 | 8222 | DI11 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x201F | 0x2020 | 8223 | 8224 | DI11 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2021 | 0x2021 | 8225 | 8225 | DI12 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2022 | 0x2023 | 8226 | 8227 | DI12 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2024 | 0x2024 | 8228 | 8228 | DI13 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2025 | 0x2026 | 8229 | 8230 | DI13 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2027 | 0x2027 | 8231 | 8231 | DI14 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2028 | 0x2029 | 8232 | 8233 | DI14 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
Available for 28 x DI | 0x202A | 0x202A | 8234 | 8234 | DI15 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x202B | 0x202C | 8235 | 8236 | DI15 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x202D | 0x202D | 8237 | 8237 | DI16 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x202E | 0x202F | 8238 | 8239 | DI16 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2030 | 0x2030 | 8240 | 8240 | DI17 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2031 | 0x2032 | 8241 | 8242 | DI17 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2033 | 0x2033 | 8243 | 8243 | DI18 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2034 | 0x2035 | 8244 | 8245 | DI18 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2036 | 0x2036 | 8246 | 8246 | DI19 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2037 | 0x2038 | 8247 | 8248 | DI19 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2039 | 0x2039 | 8249 | 8249 | DI20 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x203A | 0x203B | 8250 | 8251 | DI20 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x203C | 0x203C | 8252 | 8252 | DI21 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x203D | 0x203E | 8253 | 8254 | DI21 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x203F | 0x203F | 8255 | 8255 | DI22 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2040 | 0x2041 | 8256 | 8257 | DI22 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2042 | 0x2042 | 8258 | 8258 | DI23 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2043 | 0x2044 | 8259 | 8260 | DI23 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2045 | 0x2045 | 8261 | 8261 | DI24 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2046 | 0x2047 | 8262 | 8263 | DI24 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2048 | 0x2048 | 8264 | 8264 | DI25 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2049 | 0x204A | 8265 | 8266 | DI25 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x204B | 0x204B | 8267 | 8267 | DI26 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x204C | 0x204D | 8268 | 8269 | DI26 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x204E | 0x204E | 8270 | 8270 | DI27 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x204F | 0x2050 | 8271 | 8272 | DI27 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
| 0x2051 | 0x2051 | 8273 | 8273 | DI28 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0
| 0x2052 | 0x2053 | 8274 | 8275 | DI28 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000
DI Pulse Count | 0x2200 | 0x2201 | 8704 | 8705 | DI1 pulse count | uint32_t | RW | 2
| 0x2202 | 0x2203 | 8706 | 8707 | DI2 pulse count | uint32_t | RW | 2
| 0x2204 | 0x2205 | 8708 | 8709 | DI3 pulse count | uint32_t | RW | 2
| 0x2206 | 0x2207 | 8710 | 8711 | DI4 pulse count | uint32_t | RW | 2
| 0x2208 | 0x2209 | 8712 | 8713 | DI5 pulse count | uint32_t | RW | 2
| 0x220A | 0x220B | 8714 | 8715 | DI6 pulse count | uint32_t | RW | 2
| 0x220C | 0x220D | 8716 | 8717 | DI7 pulse count | uint32_t | RW | 2
| 0x220E | 0x220F | 8718 | 8719 | DI8 pulse count | uint32_t | RW | 2
| 0x2210 | 0x2211 | 8720 | 8721 | DI9 pulse count | uint32_t | RW | 2
| 0x2212 | 0x2213 | 8722 | 8723 | DI10 pulse count | uint32_t | RW | 2
| 0x2214 | 0x2215 | 8724 | 8725 | DI11 pulse count | uint32_t | RW | 2
| 0x2216 | 0x2217 | 8726 | 8727 | DI12 pulse count | uint32_t | RW | 2
| 0x2218 | 0x2219 | 8728 | 8729 | DI13 pulse count | uint32_t | RW | 2
| 0x221A | 0x221B | 8730 | 8731 | DI14 pulse count | uint32_t | RW | 2
Available for 28 x DI | 0x221C | 0x221D | 8732 | 8733 | DI15 pulse count | uint32_t | RW | 2
| 0x221E | 0x221F | 8734 | 8735 | DI16 pulse count | uint32_t | RW | 2
| 0x2220 | 0x2221 | 8736 | 8737 | DI17 pulse count | uint32_t | RW | 2
| 0x2222 | 0x2223 | 8738 | 8739 | DI18 pulse count | uint32_t | RW | 2
| 0x2224 | 0x2225 | 8740 | 8741 | DI19 pulse count | uint32_t | RW | 2
| 0x2226 | 0x2227 | 8742 | 8743 | DI20 pulse count | uint32_t | RW | 2
| 0x2228 | 0x2229 | 8744 | 8745 | DI21 pulse count | uint32_t | RW | 2
| 0x222A | 0x222B | 8746 | 8747 | DI22 pulse count | uint32_t | RW | 2
| 0x222C | 0x222D | 8748 | 8749 | DI23 pulse count | uint32_t | RW | 2
| 0x222E | 0x222F | 8750 | 8751 | DI24 pulse count | uint32_t | RW | 2
| 0x2230 | 0x2231 | 8752 | 8753 | DI25 pulse count | uint32_t | RW | 2
| 0x2232 | 0x2233 | 8754 | 8755 | D216 pulse count | uint32_t | RW | 2
| 0x2234 | 0x2235 | 8756 | 8757 | DI27 pulse count | uint32_t | RW | 2
| 0x2236 | 0x2237 | 8758 | 8759 | DI28 pulse count | uint32_t | RW | 2
DI Physical measurement readings | 0x2300 | 0x2301 | 8960 | 8961 | DI1 pulse count physical measurement | float32_t | R | 2
| 0x2302 | 0x2303 | 8962 | 8963 | DI2 pulse count physical measurement | float32_t | R | 2
| 0x2304 | 0x2305 | 8964 | 8965 | DI3 pulse count physical measurement | float32_t | R | 2
| 0x2306 | 0x2307 | 8966 | 8967 | DI4 pulse count physical measurement | float32_t | R | 2
| 0x2308 | 0x2309 | 8968 | 8969 | DI5 pulse count physical measurement | float32_t | R | 2
| 0x230A | 0x230B | 8970 | 8971 | DI6 pulse count physical measurement | float32_t | R | 2
| 0x230C | 0x230D | 8972 | 8973 | DI7 pulse count physical measurement | float32_t | R | 2
| 0x230E | 0x230F | 8974 | 8975 | DI8 pulse count physical measurement | float32_t | R | 2
| 0x2310 | 0x2311 | 8976 | 8977 | DI9 pulse count physical measurement | float32_t | R | 2
| 0x2312 | 0x2313 | 8978 | 8979 | DI10 pulse count physical measurement | float32_t | R | 2
| 0x2314 | 0x2315 | 8980 | 8981 | DI11 pulse count physical measurement | float32_t | R | 2
| 0x2316 | 0x2317 | 8982 | 8983 | DI12 pulse count physical measurement | float32_t | R | 2
| 0x2318 | 0x2319 | 8984 | 8985 | DI13 pulse count physical measurement | float32_t | R | 2
| 0x231A | 0x231B | 8986 | 8987 | DI14 pulse count physical measurement | float32_t | R | 2
Available for 28 x DI | 0x231C | 0x231D | 8988 | 8989 | DI15 pulse count physical measurement | float32_t | R | 2
| 0x231E | 0x231F | 8990 | 8991 | DI16 pulse count physical measurement | float32_t | R | 2
| 0x2320 | 0x2321 | 8992 | 8993 | DI17 pulse count physical measurement | float32_t | R | 2
| 0x2322 | 0x2323 | 8994 | 8995 | DI18 pulse count physical measurement | float32_t | R | 2
| 0x2324 | 0x2325 | 8996 | 8997 | DI19 pulse count physical measurement | float32_t | R | 2
| 0x2326 | 0x2327 | 8998 | 8999 | DI20 pulse count physical measurement | float32_t | R | 2
| 0x2328 | 0x2329 | 9000 | 9001 | DI21 pulse count physical measurement | float32_t | R | 2
| 0x232A | 0x232B | 9002 | 9003 | DI22 pulse count physical measurement | float32_t | R | 2
| 0x232C | 0x232D | 9004 | 9005 | DI23 pulse count physical measurement | float32_t | R | 2
| 0x232E | 0x232F | 9006 | 9007 | DI24 pulse count physical measurement | float32_t | R | 2
| 0x2330 | 0x2331 | 9008 | 9009 | DI25 pulse count physical measurement | float32_t | R | 2
| 0x2332 | 0x2333 | 9010 | 9011 | D216 pulse count physical measurement | float32_t | R | 2
| 0x2334 | 0x2335 | 9012 | 9013 | DI27 pulse count physical measurement | float32_t | R | 2
| 0x2336 | 0x2337 | 9014 | 9015 | DI28 pulse count physical measurement | float32_t | R | 2

## DO
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
DO Settings | 0x4000 | 0x4000 | 16384 | 16384 | DO1 Type | uint16_t | R/W | 1 | 0: manual 1: pulse | 0 | 0
| 0x4001 | 0x4001 | 16385 | 16385 | DO1 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100
| 0x4002 | 0x4002 | 16386 | 16386 | DO2 Type | uint16_t | R/W | 1 | 0: manual 1: pulse | 0 | 0
| 0x4003 | 0x4003 | 16387 | 16387 | DO2 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100
| 0x4004 | 0x4004 | 16388 | 16388 | DO3 Type | uint16_t | R/W | 1 | 0: manual 1: pulse | 0 | 0
| 0x4005 | 0x4005 | 16389 | 16389 | DO3 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100
| 0x4006 | 0x4006 | 16390 | 16390 | DO4 Type | uint16_t | R/W | 1 | 0: manual 1: pulse | 0 | 0
| 0x4007 | 0x4007 | 16391 | 16391 | DO4 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100

## RO
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
RO Settings | 0x6000 | 0x6000 | 24576 | 24576 | RO1 Type | uint16_t | R/W | 1 | 0: manual 1: pulse | 0 | 0
| 0x6001 | 0x6001 | 24577 | 24577 | RO1 Pulse Width | uint16_t | R/W | 1 | 20~3000ms | 1000 | 1000
| 0x6002 | 0x6002 | 24578 | 24578 | RO2 Type | uint16_t | R/W | 1 | 0: manual 1: pulse | 0 | 0
| 0x6003 | 0x6003 | 24579 | 24579 | RO2 Pulse Width | uint16_t | R/W | 1 | 20~3000ms | 1000 | 1000

## DI Status
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
DI Status | 0x0000 | 0x0000 | 0 | 0 | DI 1 Status |  | R | 1 | 0: off 1: on
| 0x0001 | 0x0001 | 1 | 1 | DI 2 Status |  | R | 1 | 0: off 1: on
| 0x0002 | 0x0002 | 2 | 2 | DI 3 Status |  | R | 1 | 0: off 1: on
| 0x0003 | 0x0003 | 3 | 3 | DI 4 Status |  | R | 1 | 0: off 1: on
| 0x0004 | 0x0004 | 4 | 4 | DI 5 Status |  | R | 1 | 0: off 1: on
| 0x0005 | 0x0005 | 5 | 5 | DI 6 Status |  | R | 1 | 0: off 1: on
| 0x0006 | 0x0006 | 6 | 6 | DI 7 Status |  | R | 1 | 0: off 1: on
| 0x0007 | 0x0007 | 7 | 7 | DI 8 Status |  | R | 1 | 0: off 1: on
| 0x0008 | 0x0008 | 8 | 8 | DI 9 Status |  | R | 1 | 0: off 1: on
| 0x0009 | 0x0009 | 9 | 9 | DI 10 Status |  | R | 1 | 0: off 1: on
| 0x000A | 0x000A | 10 | 10 | DI 11 Status |  | R | 1 | 0: off 1: on
| 0x000B | 0x000B | 11 | 11 | DI 12 Status |  | R | 1 | 0: off 1: on
| 0x000C | 0x000C | 12 | 12 | DI 13 Status |  | R | 1 | 0: off 1: on
| 0x000D | 0x000D | 13 | 13 | DI 14 Status |  | R | 1 | 0: off 1: on
Available for 28 x DI | 0x000E | 0x000E | 14 | 14 | DI 15 Status |  | R | 1 | 0: off 1: on
| 0x000F | 0x000F | 15 | 15 | DI 16 Status |  | R | 1 | 0: off 1: on
| 0x0010 | 0x0010 | 16 | 16 | DI 17 Status |  | R | 1 | 0: off 1: on
| 0x0011 | 0x0011 | 17 | 17 | DI 18 Status |  | R | 1 | 0: off 1: on
| 0x0012 | 0x0012 | 18 | 18 | DI 19 Status |  | R | 1 | 0: off 1: on
| 0x0013 | 0x0013 | 19 | 19 | DI 20 Status |  | R | 1 | 0: off 1: on
| 0x0014 | 0x0014 | 20 | 20 | DI 21 Status |  | R | 1 | 0: off 1: on
| 0x0015 | 0x0015 | 21 | 21 | DI 22 Status |  | R | 1 | 0: off 1: on
| 0x0016 | 0x0016 | 22 | 22 | DI 23 Status |  | R | 1 | 0: off 1: on
| 0x0017 | 0x0017 | 23 | 23 | DI 24 Status |  | R | 1 | 0: off 1: on
| 0x0018 | 0x0018 | 24 | 24 | DI 25 Status |  | R | 1 | 0: off 1: on
| 0x0019 | 0x0019 | 25 | 25 | DI 26 Status |  | R | 1 | 0: off 1: on
| 0x001A | 0x001A | 26 | 26 | DI 27 Status |  | R | 1 | 0: off 1: on
| 0x001B | 0x001B | 27 | 27 | DI 28 Status |  | R | 1 | 0: off 1: on
(* Function Code 0x02 to Read.)

## DO RO Status
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
DO Status | 0x0000 | 0x0000 | 0 | 0 | DO1 Status |  | R/W | 1 | 0: off 1: on
| 0x0001 | 0x0001 | 1 | 1 | DO2 Status |  | R/W | 1 | 0: off 1: on
| 0x0002 | 0x0002 | 2 | 2 | DO3 Status |  | R/W | 1 | 0: off 1: on
| 0x0003 | 0x0003 | 3 | 3 | DO4 Status |  | R/W | 1 | 0: off 1: on
* Function Code 0x01 to Read.
* Function Code 0x05(Write Single Coil) or Function Code 0x0F（Write Multiple Coils）to Write.
RO Status | 0x0020 | 0x0020 | 32 | 32 | RO1 Status |  | R/W | 1 | 0:off 1: on
| 0x0021 | 0x0021 | 33 | 33 | RO2 Status |  | R/W | 1 | 0:off 1: on
* Function Code 0x01 to Read.
* Function Code 0x05(Write Single Coil) or Function Code 0x0F（Write Multiple Coils）to Write.

## SOE Log
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
SOE Log Status | 0x6300 | 0x6300 | 25344 | 25344 | the index of the SOE Log | uint16_t | R | 1 | 1-200
| 0x6301 | 0x6301 | 25345 | 25345 | Number of the SOE Log | uint16_t | R | 1 | SOE Log already occurred Count 0：Empty
SOE Log Read Window | 0x6302 | 0x6302 | 25346 | 25346 | The first index of the SOE Log will be read | uint16_t | R/W | 1 | 1-200
| 0x6303 | 0x6303 | 25347 | 25347 | Read the number of the SOE Log offset | uint16_t | R/W | 1 | 1--17
| 0x6304 | 0x6304 | 25348 | 25348 | Data state of SOE Log Window | uint16_t | R | 1 | 0x0B: window data effective; 0xFF: window data not effective;
| 0x6305 | 0x637C | 25349 | 25468 | SOE Log Reading Window | uint8_t | R | 120 | SOE Log Data
Soe Log Record Data Format |  |  |  |  | Soe Log ID | uint16_t |  | 1
[5 empty] | Time Stamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) | uint16_t |  | 4
[5 empty] | digtal Input Status | uint32_t |  | 2 | b27-b0->D28-DI1 Status:1:High 0：Low

## AIAO Setting
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
AI Setting
| 0x3000 | 0x3000 | 12288 | 12288 | AI1 Type | uint16_t | R/W | 1 | 0: voltage：0-10 V 1:current：0-20mA | 0 | 0
| 0x3001 | 0x3002 | 12289 | 12290 | AI1 Top Limit | float32 | R/W | 2 |  | 999 | 999
| 0x3003 | 0x3004 | 12291 | 12292 | AI1 Bot Limit | float32 | R/W | 2 |  | 0 | 0
| 0x3005 | 0x3005 | 12293 | 12293 | AI1 Line Num | uint16_t | R/W | 1 | 1~3 | 1 | 1
| 0x3006 | 0x300D | 12294 | 12301 | AI1 Line Point X | float32 | R/W | 8 | Non-negative floating point number within AI input range | 1 | 1
| 0x300E | 0x3015 | 12302 | 12309 | AI1 Line Point Y | float32 | R/W | 8 | floating point | 1 | 1 | 应该可以是负值；default值应考虑1：1
| 0x3016 | 0x3016 | 12310 | 12310 | AI2 Type | uint16_t | R/W | 1 | 0: voltage：0-10 V 1:current：0-20mA | 0 | 0
| 0x3017 | 0x3018 | 12311 | 12312 | AI2 Top Limit | float32 | R/W | 2 |  | 999 | 999
| 0x3019 | 0x301A | 12313 | 12314 | AI2 Bot Limit | float32 | R/W | 2 |  | 0 | 0
| 0x301B | 0x301B | 12315 | 12315 | AI2 Line Num | uint16_t | R/W | 1 | 1~3 | 1 | 1
| 0x301C | 0x3023 | 12316 | 12323 | AI2 Line Point X | float32 | R/W | 8 | Non-negative floating point number within AI input range | 1 | 1
| 0x3024 | 0x302B | 12324 | 12331 | AI2 Line Point Y | float32 | R/W | 8 | floating point | 1 | 1
| 0x302C | 0x302C | 12332 | 12332 | AI3 Type | uint16_t | R/W | 1 | 0: voltage：0-10 V 1:current：0-20mA | 0 | 0
| 0x302D | 0x302E | 12333 | 12334 | AI3 Top Limit | float32 | R/W | 2 |  | 999 | 999
| 0x302F | 0x3030 | 12335 | 12336 | AI3 Bot Limit | float32 | R/W | 2 |  | 0 | 0
| 0x3031 | 0x3031 | 12337 | 12337 | AI3 Line Num | uint16_t | R/W | 1 | 1~3 | 1 | 1
| 0x3032 | 0x3039 | 12338 | 12345 | AI3 Line Point X | float32 | R/W | 8 | Non-negative floating point number within AI input range | 1 | 1
| 0x303A | 0x3041 | 12346 | 12353 | AI3 Line Point Y | float32 | R/W | 8 | floating point | 1 | 1
| 0x3042 | 0x3042 | 12354 | 12354 | AI4 Type | uint16_t | R/W | 1 | 0: voltage：0-10 V 1:current：0-20mA | 0 | 0
| 0x3043 | 0x3044 | 12355 | 12356 | AI4 Top Limit | float32 | R/W | 2 |  | 999 | 999
| 0x3045 | 0x3046 | 12357 | 12358 | AI4 Bot Limit | float32 | R/W | 2 |  | 0 | 0
| 0x3047 | 0x3047 | 12359 | 12359 | AI4 Line Num | uint16_t | R/W | 1 | 1~3 | 1 | 1
| 0x3048 | 0x304F | 12360 | 12367 | AI4 Line Point X | float32 | R/W | 8 | Non-negative floating point number within AI input range | 1 | 1
| 0x3050 | 0x3057 | 12368 | 12375 | AI4 Line Point Y | float32 | R/W | 8 | floating point | 1 | 1
| 0x3058 | 0x3058 | 12376 | 12376 | AI5 Type | uint16_t | R/W | 1 | 0: voltage：0-10 V 1:current：0-20mA | 0 | 0
| 0x3059 | 0x305A | 12377 | 12378 | AI5 Top Limit | float32 | R/W | 2 |  | 999 | 999
| 0x305B | 0x305C | 12379 | 12380 | AI5 Bot Limit | float32 | R/W | 2 |  | 0 | 0
| 0x305D | 0x305D | 12381 | 12381 | AI5 Line Num | uint16_t | R/W | 1 | 1~3 | 1 | 1
| 0x305E | 0x3065 | 12382 | 12389 | AI5 Line Point X | float32 | R/W | 8 | Non-negative floating point number within AI input range | 1 | 1
| 0x3066 | 0x306D | 12390 | 12397 | AI5 Line Point Y | float32 | R/W | 8 | floating point | 1 | 1
| 0x306E | 0x306E | 12398 | 12398 | AI6 Type | uint16_t | R/W | 1 | 0: voltage：0-10 V 1:current：0-20mA | 0 | 0
| 0x306F | 0x3070 | 12399 | 12400 | AI6 Top Limit | float32 | R/W | 2 |  | 999 | 999
| 0x3071 | 0x3072 | 12401 | 12402 | AI6 Bot Limit | float32 | R/W | 2 |  | 0 | 0
| 0x3073 | 0x3073 | 12403 | 12403 | AI6 Line Num | uint16_t | R/W | 1 | 1~3 | 1 | 1
| 0x3074 | 0x307B | 12404 | 12411 | AI6 Line Point X | float32 | R/W | 8 | Non-negative floating point number within AI input range | 1 | 1
| 0x307C | 0x3083 | 12412 | 12419 | AI6 Line Point Y | float32 | R/W | 8 | floating point | 1 | 1
| …… | …… | …… | …… | …… | …… | …… | …… | …… | …… | ……
| 0x314A | 0x314A | 12618 | 12618 | AI16 Type | uint16_t | R/W | 1 | 0: voltage：0-10 V 1:current：0-20mA | 0 | 0
| 0x314B | 0x314C | 12619 | 12620 | AI16 Top Limit | float32 | R/W | 2 |  | 999 | 999
| 0x314D | 0x314E | 12621 | 12622 | AI16 Bot Limit | float32 | R/W | 2 |  | 0 | 0
| 0x314F | 0x314F | 12623 | 12623 | AI16 Line Num | uint16_t | R/W | 1 | 1~3 | 1 | 1
| 0x3150 | 0x3157 | 12624 | 12631 | AI16 Line Point X | float32 | R/W | 8 | Non-negative floating point number within AI input range | 1 | 1
| 0x3158 | 0x315F | 12632 | 12639 | AI16 Line Point Y | float32 | R/W | 8 | floating point | 1 | 1
352
AO Setting | 0x3400 | 0x3400 | 13312 | 13312 | AO1 Type | uint16_t | R/W | 1 | 0: voltage：0-10 V 1:current：0-20mA | 0 | 0
| 0x3401 | 0x3402 | 13313 | 13314 | AO1 Top Limit | float32 | R/W | 2 |  | 999 | 999
| 0x3403 | 0x3404 | 13315 | 13316 | AO1 Bot Limit | float32 | R/W | 2 |  | 0 | 0
| 0x3405 | 0x3405 | 13317 | 13317 | AO1 Line Num | uint16_t | R/W | 1 | 1~3 | 1 | 1
| 0x3406 | 0x340D | 13318 | 13325 | AO1 Line Point X | float32 | R/W | 8 | floating point | 1 | 1 | 应该可以是负值；default值应考虑1：1
| 0x340E | 0x3415 | 13326 | 13333 | AO1 Line Point Y | float32 | R/W | 8 | Non-negative floating point number within the AO output range | 1 | 1
| 0x3416 | 0x3416 | 13334 | 13334 | AO2 Type | uint16_t | R/W | 1 | 0: voltage：0-10 V 1:current：0-20mA | 0 | 0
| 0x3417 | 0x3418 | 13335 | 13336 | AO2 Top Limit | float32 | R/W | 2 |  | 999 | 999
| 0x3419 | 0x341A | 13337 | 13338 | AO2 Bot Limit | float32 | R/W | 2 |  | 0 | 0
| 0x341B | 0x341B | 13339 | 13339 | AO2 Line Num | uint16_t | R/W | 1 | 1~3 | 1 | 1
| 0x341C | 0x3423 | 13340 | 13347 | AO2 Line Point X | float32 | R/W | 8 | floating point | 1 | 1
| 0x3424 | 0x342B | 13348 | 13355 | AO2 Line Point Y | float32 | R/W | 8 | Non-negative floating point number within the AO output range | 1 | 1
| 0x342C | 0x342C | 13356 | 13356 | AO3 Type | uint16_t | R/W | 1 | 0: voltage：0-10 V 1:current：0-20mA | 0 | 0
| 0x342D | 0x342E | 13357 | 13358 | AO3 Top Limit | float32 | R/W | 2 |  | 999 | 999
| 0x342F | 0x3430 | 13359 | 13360 | AO3 Bot Limit | float32 | R/W | 2 |  | 0 | 0
| 0x3431 | 0x3431 | 13361 | 13361 | AO3 Line Num | uint16_t | R/W | 1 | 1~3 | 1 | 1
| 0x3432 | 0x3439 | 13362 | 13369 | AO3 Line Point X | float32 | R/W | 8 | floating point | 1 | 1
| 0x343A | 0x3441 | 13370 | 13377 | AO3 Line Point Y | float32 | R/W | 8 | Non-negative floating point number within the AO output range | 1 | 1
| 0x3442 | 0x3442 | 13378 | 13378 | AO4 Type | uint16_t | R/W | 1 | 0: voltage：0-10 V 1:current：0-20mA | 0 | 0
| 0x3443 | 0x3444 | 13379 | 13380 | AO4 Top Limit | float32 | R/W | 2 |  | 999 | 999
| 0x3445 | 0x3446 | 13381 | 13382 | AO4 Bot Limit | float32 | R/W | 2 |  | 0 | 0
| 0x3447 | 0x3447 | 13383 | 13383 | AO4 Line Num | uint16_t | R/W | 1 | 1~3 | 1 | 1
| 0x3448 | 0x344F | 13384 | 13391 | AO4 Line Point X | float32 | R/W | 8 | floating point | 1 | 1
| 0x3450 | 0x3457 | 13392 | 13399 | AO4 Line Point Y | float32 | R/W | 8 | Non-negative floating point number within the AO output range | 1 | 1
88

## AIAO Data
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
AI Original Data
| 0x3500 | 0x3501 | 13568 | 13569 | AI1 input original data | float32 | R | 2 |  | 0 | 0
| 0x3502 | 0x3503 | 13570 | 13571 | AI2 input original data | float32 | R | 2 |  | 0 | 0
| 0x3504 | 0x3505 | 13572 | 13573 | AI3 input original data | float32 | R | 2 |  | 0 | 0
| 0x3506 | 0x3507 | 13574 | 13575 | AI4 input original data | float32 | R | 2 |  | 0 | 0
| 0x3508 | 0x3509 | 13576 | 13577 | AI5 input original data | float32 | R | 2 |  | 0 | 0
| 0x350A | 0x350B | 13578 | 13579 | AI6 input original data | float32 | R | 2 |  | 0 | 0
| 0x350C | 0x350D | 13580 | 13581 | AI7 input original data | float32 | R | 2 |  | 0 | 0
| 0x350E | 0x350F | 13582 | 13583 | AI8 input original data | float32 | R | 2 |  | 0 | 0
| 0x3510 | 0x3511 | 13584 | 13585 | AI9 input original data | float32 | R | 2 |  | 0 | 0
| 0x3512 | 0x3513 | 13586 | 13587 | AI10 input original data | float32 | R | 2 |  | 0 | 0
| 0x3514 | 0x3515 | 13588 | 13589 | AI11 input original data | float32 | R | 2 |  | 0 | 0
| 0x3516 | 0x3517 | 13590 | 13591 | AI12 input original data | float32 | R | 2 |  | 0 | 0
| 0x3518 | 0x3519 | 13592 | 13593 | AI13 input original data | float32 | R | 2 |  | 0 | 0
| 0x351A | 0x351B | 13594 | 13595 | AI14 input original data | float32 | R | 2 |  | 0 | 0
| 0x351C | 0x351D | 13596 | 13597 | AI15 input original data | float32 | R | 2 |  | 0 | 0
| 0x351E | 0x351F | 13598 | 13599 | AI16 input original data | float32 | R | 2 |  | 0 | 0
32
AI physical measurement readings | 0x3700 | 0x3701 | 14080 | 14081 | AI1 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x3702 | 0x3703 | 14082 | 14083 | AI2 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x3704 | 0x3705 | 14084 | 14085 | AI3 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x3706 | 0x3707 | 14086 | 14087 | AI4 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x3708 | 0x3709 | 14088 | 14089 | AI5 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x370A | 0x370B | 14090 | 14091 | AI6 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x370C | 0x370D | 14092 | 14093 | AI7 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x370E | 0x370F | 14094 | 14095 | AI8 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x3710 | 0x3711 | 14096 | 14097 | AI9 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x3712 | 0x3713 | 14098 | 14099 | AI10 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x3714 | 0x3715 | 14100 | 14101 | AI11 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x3716 | 0x3717 | 14102 | 14103 | AI12 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x3718 | 0x3719 | 14104 | 14105 | AI13 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x371A | 0x371B | 14106 | 14107 | AI14 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x371C | 0x371D | 14108 | 14109 | AI15 physical measurement reading | float32 | R | 2 |  | 0 | 0
| 0x371E | 0x371F | 14110 | 14111 | AI16 physical measurement reading | float32 | R | 2 |  | 0 | 0
32
AO output data | 0x3900 | 0x3901 | 14592 | 14593 | AO1 output data | float32 | R | 2 |  | 0 | 0
| 0x3902 | 0x3903 | 14594 | 14595 | AO2 output data | float32 | R | 2 |  | 0 | 0
| 0x3904 | 0x3905 | 14596 | 14597 | AO3 output data | float32 | R | 2 |  | 0 | 0
| 0x3906 | 0x3907 | 14598 | 14599 | AO4 output data | float32 | R | 2 |  | 0 | 0
8
AO physical measurement Input | 0x3950 | 0x3951 | 14672 | 14673 | AO1 physical measurement Input | float32 | RW | 2 |  | 0 | 0
| 0x3952 | 0x3953 | 14674 | 14675 | AO2 physical measurement Input | float32 | RW | 2 |  | 0 | 0
| 0x3954 | 0x3955 | 14676 | 14677 | AO3 physical measurement Input | float32 | RW | 2 |  | 0 | 0
| 0x3956 | 0x3957 | 14678 | 14679 | AO4 physical measurement Input | float32 | RW | 2 |  | 0 | 0
8

## Information
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Firmware Version Info | 0xF000 | 0xF001 | 61440 | 61441 | Firmware version | uint8_t | R | 2 | In the format like x.yz (e.g., 1.01) | determined by firmware | determined by firmware
| 0xF002 | 0xF004 | 61442 | 61444 | Firmware release date | uint8_t | R | 3 | In the format like YYMMDD (221228) | determined by firmware | determined by firmware
| 0xF005 | 0xF005 | 61445 | 61445 | Firmware patch number | uint8_t | R | 1 | In the format like xy (01) | determined by firmware | determined by firmware
Reboot | 0xF000 | 0xF001 | 61440 | 61441 | Reset for update | uint8_t | W | 2 | 0xA1,0x58,0x58,0xA1 | 0
Bootloader Info | 0xF010 | 0xF011 | 61456 | 61457 | bootloader product string | uint8_t | R | 2 | IOM1 | determined by boot | determined by boot
| 0xF012 | 0xF013 | 61458 | 61459 | bootloader version | uint8_t | R | 2 | In the format like x.yz (e.g., 1.01) | determined by boot | determined by boot
| 0xF014 | 0xF016 | 61460 | 61462 | bootloader release date | uint8_t | R | 3 | ASCII, in format of YYMMDD (e.g. 241108) | determined by boot | determined by boot
| 0xF017 | 0xF017 | 61463 | 61463 | bootloader patch number | uint8_t | R | 1 | In the format like xy (01) | determined by boot | determined by boot
Product Info | 0xF040 | 0xF04F | 61504 | 61519 | Serial Number | uint8_t | R/W | 16 | In the format like ARFYYMMabcdef (e.g., AI2212000001)
| 0xF050 | 0xF051 | 61520 | 61521 | Hardware version | uint8_t | R/W | 2 | In the format like x.yz (e.g., 1.01)
| 0xF052 | 0xF052 | 61522 | 61522 | Function Model Type | uint16_t | R/W | 1 | 1：8 x AI, 2 x AO 2：16 x AI, 4 x AO 3：14 x DI, 2 x DO, 2 x RO 4：28 x DI, 4 x DO, 2 x RO
| 0xF053 | 0xF055 | 61523 | 61525 | Reserved 1 | uint16_t | R/W | 3
| 0xF056 | 0xF065 | 61526 | 61541 | MAC address | uint8_t | R/W | 16
| 0xF066 | 0xF066 | 61542 | 61542 | Certification Type | uint16_t | R/W | 1 | 0: None; 1: MID; 2: MC
| 0xF067 | 0xF068 | 61543 | 61544 | AIAO or DIDO flag | uint8_t | R/W | 2 | "IOM1" / "IOM2" / "IOM3" / "IOM4" |  | Need restart after setting
| 0xF069 | 0xF06F | 61545 | 61551 | Reserved 2 | uint16_t | R/W | 7
| 0xF070 | 0xF070 | 61552 | 61552 | Hardware Patch Number | uint8_t | R/W | 1 | In the format like xy (01)
* 0x6A to write

## Calibration
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
AI Calibration Commands | 0x5000 | 0x5000 | 20480 | 20480 | AI calibration stage | uint16_t | W/R | 1 | 0x00:normal 0xAA:enter calibration mode 0xBC: start calibration 0xEC exit calibration mode | 0 | 0
| 0x5001 | 0x5001 | 20481 | 20481 | H:calibStartChannelID L:caliboffsetID | uint16_t | W/R | 1 | 0-16 通道1编号1 0-16 | 0 | 0
| 0x5002 | 0x5002 | 20482 | 20482 | AI calibration result | uint16_t | R | 1 | 0x00:WAIT_START, 0x01:WAIT_SOURCE, 0x02:ONGOING, 0x03:CALIB_PASSED, 0x04:OVERTIME 0x05:FAILED
| 0x5003 | 0x5022 | 20483 | 20514 | AI calibRmsValue[16] | float32 | R | 32
AO Calibration Commands | 0x5100 | 0x5100 | 20736 | 20736 | H:AO calibration stage | uint16_t | W/R | 1 | 0x00:normal 0xAA:enter calibration mode 0xBC: start calibration 0xEC exit calibration mode | 0 | 0
| 0x5101 | 0x5101 | 20737 | 20737 | H:calibStartChannelID L:caliboffsetID | uint16_t | W/R | 1 | 0-4 通道1编号1 0-4 | 0 | 0
| 0x5102 | 0x5102 | 20738 | 20738 | return AO calibration result | uint16_t | R | 1 | 0x00:WAIT_START, 0x01:WAIT_SOURCE, 0x02:ONGOING, 0x03:CALIB_PASSED, 0x04:OVERTIME 0x05:FAILED
| 0x5103 | 0x5104 | 20739 | 20740 | AO1 calibValue1 | float32 | W/R | 2
| 0x5105 | 0x5106 | 20741 | 20742 | AO1 calibValue2 | float32 | W/R | 2
| 0x5107 | 0x5108 | 20743 | 20744 | AO2 calibValue1 | float32 | W/R | 2
| 0x5109 | 0x510A | 20745 | 20746 | AO2 calibValue2 | float32 | W/R | 2
| 0x510B | 0x510C | 20747 | 20748 | AO3 calibValue1 | float32 | W/R | 2
| 0x510D | 0x510E | 20749 | 20750 | AO3 calibValue2 | float32 | W/R | 2
| 0x510F | 0x5110 | 20751 | 20752 | AO4 calibValue1 | float32 | W/R | 2
| 0x5111 | 0x5112 | 20753 | 20754 | AO4 calibValue2 | float32 | W/R | 2
| 0x5113 | 0x511A | 20755 | 20762 | AO calibRmsValue[4] | float32 | R | 8
需要描述校准步骤；尽量把同一块板子的AI一起校准；AO一起校准。
AI Gain OffSet Coeff
| 0x5300 | 0x5301 | 21248 | 21249 | AI1GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x5302 | 0x5303 | 21250 | 21251 | AI1OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5304 | 0x5305 | 21252 | 21253 | AI2GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x5306 | 0x5307 | 21254 | 21255 | AI2OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5308 | 0x5309 | 21256 | 21257 | AI3GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x530A | 0x530B | 21258 | 21259 | AI3OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x530C | 0x530D | 21260 | 21261 | AI4GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x530E | 0x530F | 21262 | 21263 | AI4OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5310 | 0x5311 | 21264 | 21265 | AI5GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x5312 | 0x5313 | 21266 | 21267 | AI5OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5314 | 0x5315 | 21268 | 21269 | AI6GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x5316 | 0x5317 | 21270 | 21271 | AI6OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5318 | 0x5319 | 21272 | 21273 | AI7GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x531A | 0x531B | 21274 | 21275 | AI7OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x531C | 0x531D | 21276 | 21277 | AI8GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x531E | 0x531F | 21278 | 21279 | AI8OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5320 | 0x5321 | 21280 | 21281 | AI9GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x5322 | 0x5323 | 21282 | 21283 | AI9OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5324 | 0x5325 | 21284 | 21285 | AI10GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x5326 | 0x5327 | 21286 | 21287 | AI10OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5328 | 0x5329 | 21288 | 21289 | AI11GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x532A | 0x532B | 21290 | 21291 | AI11OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x532C | 0x532D | 21292 | 21293 | AI12GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x532E | 0x532F | 21294 | 21295 | AI12OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5330 | 0x5331 | 21296 | 21297 | AI13GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x5332 | 0x5333 | 21298 | 21299 | AI13OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5334 | 0x5335 | 21300 | 21301 | AI14GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x5336 | 0x5337 | 21302 | 21303 | AI14OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5338 | 0x5339 | 21304 | 21305 | AI15GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x533A | 0x533B | 21306 | 21307 | AI15OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x533C | 0x533D | 21308 | 21309 | AI16GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x533E | 0x533F | 21310 | 21311 | AI16OffsetCoef | float32 | R/W | 2 |  | 0 | 0
AO Gain Offset Coef | 0x5500 | 0x5501 | 21760 | 21761 | AO1GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x5502 | 0x5503 | 21762 | 21763 | AO1OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5504 | 0x5505 | 21764 | 21765 | AO2GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x5506 | 0x5507 | 21766 | 21767 | AO2OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x5508 | 0x5509 | 21768 | 21769 | AO3GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x550A | 0x550B | 21770 | 21771 | AI3OffsetCoef | float32 | R/W | 2 |  | 0 | 0
| 0x550C | 0x550D | 21772 | 21773 | AO4GainCoef | float32 | R/W | 2 |  | 1 | 1
| 0x550E | 0x550F | 21774 | 21775 | AI4OffsetCoef | float32 | R/W | 2 |  | 0 | 0