## block
blockId | type | start | count | isEnable | NAME
0 | VIRTUAL_BLOCK | 0 | 1 | TRUE | isOnline
1 | HOLDING_REGISTER | 8192 | 66 | TRUE | System Basic Reading
2 | HOLDING_REGISTER | 8448 | 120 | TRUE | Input Channal Basic Reading 1
3 | HOLDING_REGISTER | 8568 | 96 | TRUE | Input Channal Basic Reading 2
4 | HOLDING_REGISTER | 8664 | 90 | TRUE | User Channal Basic Reading 1
5 | HOLDING_REGISTER | 9472 | 62 | TRUE | Energy 1
6 | HOLDING_REGISTER | 11008 | 100 | TRUE | Energy 2
7 | HOLDING_REGISTER | 11108 | 24 | TRUE | Energy 3
8 | HOLDING_REGISTER | 11520 | 99 | TRUE | Demand 1
9 | HOLDING_REGISTER | 11619 | 36 | TRUE | Demand 2
10 | HOLDING_REGISTER | 11655 | 108 | TRUE | Demand 3
11 | HOLDING_REGISTER | 11763 | 108 | TRUE | Demand 4
12 | HOLDING_REGISTER | 11871 | 108 | TRUE | Demand 5
13 | HOLDING_REGISTER | 11979 | 108 | TRUE | Demand 6
14 | HOLDING_REGISTER | 12087 | 108 | TRUE | Demand 7
15 | HOLDING_REGISTER | 12195 | 108 | TRUE | Demand 8
16 | HOLDING_REGISTER | 12303 | 81 | TRUE | Demand 9
17 | HOLDING_REGISTER | 12384 | 81 | TRUE | Demand 10
18 | HOLDING_REGISTER | 12465 | 81 | TRUE | Demand 11
19 | HOLDING_REGISTER | 12800 | 108 | TRUE | Harmonics 1
20 | HOLDING_REGISTER | 12960 | 54 | TRUE | Harmonics 2
21 | HOLDING_REGISTER | 13056 | 93 | TRUE | Harmonics 3
22 | HOLDING_REGISTER | 13149 | 93 | TRUE | Harmonics 4
23 | HOLDING_REGISTER | 13242 | 93 | TRUE | Harmonics 5
24 | HOLDING_REGISTER | 13335 | 93 | TRUE | Harmonics 6
25 | HOLDING_REGISTER | 13428 | 93 | TRUE | Harmonics 7
26 | HOLDING_REGISTER | 13521 | 93 | TRUE | Harmonics 8
27 | HOLDING_REGISTER | 13614 | 9 | TRUE | Harmonics 9
28 | HOLDING_REGISTER | 13824 | 20 | TRUE | Phase Angle
29 | HOLDING_REGISTER | 2048 | 14 | TRUE | Settings 1
30 | HOLDING_REGISTER | 2097 | 6 | TRUE | Settings 2
31 | HOLDING_REGISTER | 2183 | 20 | TRUE | Settings 3
32 | HOLDING_REGISTER | 61723 | 1 | TRUE | Info 1
33 | HOLDING_REGISTER | 61440 | 9 | TRUE | Info 2
34 | HOLDING_REGISTER | 2221 | 4 | TRUE | Settings 4

## blockParams
ID | blockId | paramId | Start(Dec) | descrption | paramType | unit | dataType | byteOrder | RW | Reg | scale | analysisUnitId | datalog | trendreal | trendenergy | north | conf | range | readings | Alarm | DataLog | AcuCloud | MQTT | SNMP | BACnetIP |  | paramType_AcuCloud |  | AcuHMI中模板没有的，AcuCloud中有的字段
1 | 0 | 0-1 | 0 | IsOnline | IsOnline |  | isOnline | 1 | R | 1 | 1 | [6 empty] | 14 | 20-21 | realtime |  | realtime | realtime | realtime | realtime | realtime |  |  | DI14 | Digital Input Channel 14
2 | 1 | 1-1 | 8192 | System Frequency | FREQ_Hz | Hz | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime |  |  | DI12 | Digital Input Channel 12
3 | 1 | 1-2 | 8194 | Phase A Line-to-Neutral Voltage | VLN_a_V | V | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Va_V |  | DMD_I1_A | Phase A Current Demand
4 | 1 | 1-3 | 8196 | Phase B Line-to-Neutral Voltage | VLN_b_V | V | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Vb_V |  | DMD_I2_A | Phase B Current Demand
5 | 1 | 1-4 | 8198 | Phase C Line-to-Neutral Voltage | VLN_c_V | V | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Vc_V |  | DMD_I3_A | Phase C Current Demand
6 | 1 | 1-5 | 8200 | Average Line-to-Neutral Voltage | VLN_avg_V | V | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime |  |  | DI11 | Digital Input Channel 11
7 | 1 | 1-6 | 8202 | Phase A-B Line-to-Line Voltage | VLL_ab_V | V | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Vab_V |  | DI13 | Digital Input Channel 13
8 | 1 | 1-7 | 8204 | Phase B-C Line-to-Line Voltage | VLL_bc_V | V | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Vbc_V |  | DI15 | Digital Input Channel 15
9 | 1 | 1-8 | 8206 | Phase C-A Line-to-Line Voltage | VLL_ca_V | V | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Vca_V |  | DI16 | Digital Input Channel 16
10 | 1 | 1-9 | 8208 | Average Line-to-Line Voltage | VLL_avg_V | V | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Vlavg_V |  | DI4 | Digital Input Channel 4
11 | 1 | 1-10 | 8210 | Phase A Line Current | I_a_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ia_A |  | DI2 | Digital Input Channel 2
12 | 1 | 1-11 | 8212 | Phase B Line Current | I_b_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ib_A |  | DI1 | Digital Input Channel 1
13 | 1 | 1-12 | 8214 | Phase C Line Current | I_c_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ic_A |  | DI5 | Digital Input Channel 5
14 | 1 | 1-13 | 8216 | Average Line Current | I_avg_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Iavg_A |  | DI7 | Digital Input Channel 7
15 | 1 | 1-14 | 8218 | System Active Power | P_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P_kW |  | DI6 | Digital Input Channel 6
16 | 1 | 1-15 | 8220 | System Reactive Power | Q_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q_kvar |  | DI8 | Digital Input Channel 8
17 | 1 | 1-16 | 8222 | System Apparent Power | S_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S_kVA |  | KF_Ia | Phase A Current K Factor
18 | 1 | 1-17 | 8224 | System Power Factor | PF | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF |  | KF_Ib | Phase B Current K Factor
19 | 1 | 1-18 | 8226 | Average Load Nature | LC_avg |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime |  |  | KF_Ic | Phase C Current K Factor
20 | 1 | 1-19 | 8228 | Phase A Active Power | P_a_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Pa_kW |  | DI3 | Digital Input Channel 3
21 | 1 | 1-20 | 8230 | Phase B Active Power | P_b_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Pb_kW |  | DI17 | Digital Input Channel 17
22 | 1 | 1-21 | 8232 | Phase C Active Power | P_c_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Pc_kW |  | DI18 | Digital Input Channel 18
23 | 1 | 1-22 | 8234 | Phase A Reactive Power | Q_a_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qa_kvar |  | DI9 | Digital Input Channel 9
24 | 1 | 1-23 | 8236 | Phase B Reactive Power | Q_b_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qb_kvar
25 | 1 | 1-24 | 8238 | Phase C Reactive Power | Q_c_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qc_kvar
26 | 1 | 1-25 | 8240 | Phase A Apparent Power | S_a_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Sa_kVA
27 | 1 | 1-26 | 8242 | Phase B Apparent Power | S_b_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Sb_kVA
28 | 1 | 1-27 | 8244 | Phase C Apparent Power | S_c_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Sc_kVA
29 | 1 | 1-28 | 8246 | Phase A Power Factor | PF_a | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PFa
30 | 1 | 1-29 | 8248 | Phase B Power Factor | PF_b | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PFb
31 | 1 | 1-30 | 8250 | Phase C Power Factor | PF_c | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PFc
32 | 1 | 1-31 | 8252 | Phase A Load Nature | LC_a |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
33 | 1 | 1-32 | 8254 | Phase B Load Nature | LC_b |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
34 | 1 | 1-33 | 8256 | Phase C Load Nature | LC_c |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 6-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
35 | 2 | 2-1 | 8448 | Input Channel 1 current | I_001_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I001_A
36 | 2 | 2-2 | 8450 | Input Channel 1 Active Power | P_001_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P001_kW
37 | 2 | 2-3 | 8452 | Input Channel 1 Reactive Power | Q_001_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q001_kvar
38 | 2 | 2-4 | 8454 | Input Channel 1 Apparent Power | S_001_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S001_kVA
39 | 2 | 2-5 | 8456 | Input Channel 1 Power Factor | PF_001 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF001
40 | 2 | 2-6 | 8458 | Input Channel 1 Load Nature | LC_001 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
41 | 2 | 2-7 | 8460 | Input Channel 2 current | I_002_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I002_A
42 | 2 | 2-8 | 8462 | Input Channel 2 Active Power | P_002_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P002_kW
43 | 2 | 2-9 | 8464 | Input Channel 2 Reactive Power | Q_002_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q002_kvar
44 | 2 | 2-10 | 8466 | Input Channel 2 Apparent Power | S_002_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S002_kVA
45 | 2 | 2-11 | 8468 | Input Channel 2 Power Factor | PF_002 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF002
46 | 2 | 2-12 | 8470 | Input Channel 2 Load Nature | LC_002 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
47 | 2 | 2-13 | 8472 | Input Channel 3 current | I_003_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I003_A
48 | 2 | 2-14 | 8474 | Input Channel 3 Active Power | P_003_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P003_kW
49 | 2 | 2-15 | 8476 | Input Channel 3 Reactive Power | Q_003_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q003_kvar
50 | 2 | 2-16 | 8478 | Input Channel 3 Apparent Power | S_003_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S003_kVA
51 | 2 | 2-17 | 8480 | Input Channel 3 Power Factor | PF_003 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF003
52 | 2 | 2-18 | 8482 | Input Channel 3 Load Nature | LC_003 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
53 | 2 | 2-19 | 8484 | Input Channel 4 current | I_004_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I004_A
54 | 2 | 2-20 | 8486 | Input Channel 4 Active Power | P_004_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P004_kW
55 | 2 | 2-21 | 8488 | Input Channel 4 Reactive Power | Q_004_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q004_kvar
56 | 2 | 2-22 | 8490 | Input Channel 4 Apparent Power | S_004_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S004_kVA
57 | 2 | 2-23 | 8492 | Input Channel 4 Power Factor | PF_004 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF004
58 | 2 | 2-24 | 8494 | Input Channel 4 Load Nature | LC_004 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
59 | 2 | 2-25 | 8496 | Input Channel 5 current | I_005_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I005_A
60 | 2 | 2-26 | 8498 | Input Channel 5 Active Power | P_005_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P005_kW
61 | 2 | 2-27 | 8500 | Input Channel 5 Reactive Power | Q_005_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q005_kvar
62 | 2 | 2-28 | 8502 | Input Channel 5 Apparent Power | S_005_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S005_kVA
63 | 2 | 2-29 | 8504 | Input Channel 5 Power Factor | PF_005 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF005
64 | 2 | 2-30 | 8506 | Input Channel 5 Load Nature | LC_005 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
65 | 2 | 2-31 | 8508 | Input Channel 6 current | I_006_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I006_A
66 | 2 | 2-32 | 8510 | Input Channel 6 Active Power | P_006_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P006_kW
67 | 2 | 2-33 | 8512 | Input Channel 6 Reactive Power | Q_006_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q006_kvar
68 | 2 | 2-34 | 8514 | Input Channel 6 Apparent Power | S_006_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S006_kVA
69 | 2 | 2-35 | 8516 | Input Channel 6 Power Factor | PF_006 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF006
70 | 2 | 2-36 | 8518 | Input Channel 6 Load Nature | LC_006 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
71 | 2 | 2-37 | 8520 | Input Channel 7 current | I_007_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I007_A
72 | 2 | 2-38 | 8522 | Input Channel 7 Active Power | P_007_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P007_kW
73 | 2 | 2-39 | 8524 | Input Channel 7 Reactive Power | Q_007_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q007_kvar
74 | 2 | 2-40 | 8526 | Input Channel 7 Apparent Power | S_007_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S007_kVA
75 | 2 | 2-41 | 8528 | Input Channel 7 Power Factor | PF_007 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF007
76 | 2 | 2-42 | 8530 | Input Channel 7 Load Nature | LC_007 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
77 | 2 | 2-43 | 8532 | Input Channel 8 current | I_008_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I008_A
78 | 2 | 2-44 | 8534 | Input Channel 8 Active Power | P_008_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P008_kW
79 | 2 | 2-45 | 8536 | Input Channel 8 Reactive Power | Q_008_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q008_kvar
80 | 2 | 2-46 | 8538 | Input Channel 8 Apparent Power | S_008_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S008_kVA
81 | 2 | 2-47 | 8540 | Input Channel 8 Power Factor | PF_008 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF008
82 | 2 | 2-48 | 8542 | Input Channel 8 Load Nature | LC_008 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
83 | 2 | 2-49 | 8544 | Input Channel 9 current | I_009_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I009_A
84 | 2 | 2-50 | 8546 | Input Channel 9 Active Power | P_009_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P009_kW
85 | 2 | 2-51 | 8548 | Input Channel 9 Reactive Power | Q_009_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q009_kvar
86 | 2 | 2-52 | 8550 | Input Channel 9 Apparent Power | S_009_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S009_kVA
87 | 2 | 2-53 | 8552 | Input Channel 9 Power Factor | PF_009 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF009
88 | 2 | 2-54 | 8554 | Input Channel 9 Load Nature | LC_009 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
89 | 2 | 2-55 | 8556 | Input Channel 10 current | I_010_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I010_A
90 | 2 | 2-56 | 8558 | Input Channel 10 Active Power | P_010_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P010_kW
91 | 2 | 2-57 | 8560 | Input Channel 10 Reactive Power | Q_010_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q010_kvar
92 | 2 | 2-58 | 8562 | Input Channel 10 Apparent Power | S_010_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S010_kVA
93 | 2 | 2-59 | 8564 | Input Channel 10 Power Factor | PF_010 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF010
94 | 2 | 2-60 | 8566 | Input Channel 10 Load Nature | LC_010 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
95 | 3 | 3-1 | 8568 | Input Channel 11 current | I_011_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I011_A
96 | 3 | 3-2 | 8570 | Input Channel 11 Active Power | P_011_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P011_kW
97 | 3 | 3-3 | 8572 | Input Channel 11 Reactive Power | Q_011_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q011_kvar
98 | 3 | 3-4 | 8574 | Input Channel 11 Apparent Power | S_011_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S011_kVA
99 | 3 | 3-5 | 8576 | Input Channel 11 Power Factor | PF_011 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF011
100 | 3 | 3-6 | 8578 | Input Channel 11 Load Nature | LC_011 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
101 | 3 | 3-7 | 8580 | Input Channel 12 current | I_012_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I012_A
102 | 3 | 3-8 | 8582 | Input Channel 12 Active Power | P_012_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P012_kW
103 | 3 | 3-9 | 8584 | Input Channel 12 Reactive Power | Q_012_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q012_kvar
104 | 3 | 3-10 | 8586 | Input Channel 12 Apparent Power | S_012_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S012_kVA
105 | 3 | 3-11 | 8588 | Input Channel 12 Power Factor | PF_012 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF012
106 | 3 | 3-12 | 8590 | Input Channel 12 Load Nature | LC_012 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
107 | 3 | 3-13 | 8592 | Input Channel 13 current | I_013_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I013_A
108 | 3 | 3-14 | 8594 | Input Channel 13 Active Power | P_013_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P013_kW
109 | 3 | 3-15 | 8596 | Input Channel 13 Reactive Power | Q_013_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q013_kvar
110 | 3 | 3-16 | 8598 | Input Channel 13 Apparent Power | S_013_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S013_kVA
111 | 3 | 3-17 | 8600 | Input Channel 13 Power Factor | PF_013 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF013
112 | 3 | 3-18 | 8602 | Input Channel 13 Load Nature | LC_013 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
113 | 3 | 3-19 | 8604 | Input Channel 14 current | I_014_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I014_A
114 | 3 | 3-20 | 8606 | Input Channel 14 Active Power | P_014_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P014_kW
115 | 3 | 3-21 | 8608 | Input Channel 14 Reactive Power | Q_014_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q014_kvar
116 | 3 | 3-22 | 8610 | Input Channel 14 Apparent Power | S_014_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S014_kVA
117 | 3 | 3-23 | 8612 | Input Channel 14 Power Factor | PF_014 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF014
118 | 3 | 3-24 | 8614 | Input Channel 14 Load Nature | LC_014 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
119 | 3 | 3-25 | 8616 | Input Channel 15 current | I_015_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I015_A
120 | 3 | 3-26 | 8618 | Input Channel 15 Active Power | P_015_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P015_kW
121 | 3 | 3-27 | 8620 | Input Channel 15 Reactive Power | Q_015_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q015_kvar
122 | 3 | 3-28 | 8622 | Input Channel 15 Apparent Power | S_015_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S015_kVA
123 | 3 | 3-29 | 8624 | Input Channel 15 Power Factor | PF_015 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF015
124 | 3 | 3-30 | 8626 | Input Channel 15 Load Nature | LC_015 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
125 | 3 | 3-31 | 8628 | Input Channel 16 current | I_016_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I016_A
126 | 3 | 3-32 | 8630 | Input Channel 16 Active Power | P_016_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P016_kW
127 | 3 | 3-33 | 8632 | Input Channel 16 Reactive Power | Q_016_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q016_kvar
128 | 3 | 3-34 | 8634 | Input Channel 16 Apparent Power | S_016_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S016_kVA
129 | 3 | 3-35 | 8636 | Input Channel 16 Power Factor | PF_016 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF016
130 | 3 | 3-36 | 8638 | Input Channel 16 Load Nature | LC_016 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
131 | 3 | 3-37 | 8640 | Input Channel 17 current | I_017_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I017_A
132 | 3 | 3-38 | 8642 | Input Channel 17 Active Power | P_017_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P017_kW
133 | 3 | 3-39 | 8644 | Input Channel 17 Reactive Power | Q_017_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q017_kvar
134 | 3 | 3-40 | 8646 | Input Channel 17 Apparent Power | S_017_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S017_kVA
135 | 3 | 3-41 | 8648 | Input Channel 17 Power Factor | PF_017 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF017
136 | 3 | 3-42 | 8650 | Input Channel 17 Load Nature | LC_017 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
137 | 3 | 3-43 | 8652 | Input Channel 18 current | I_018_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | I018_A
138 | 3 | 3-44 | 8654 | Input Channel 18 Active Power | P_018_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P018_kW
139 | 3 | 3-45 | 8656 | Input Channel 18 Reactive Power | Q_018_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q018_kvar
140 | 3 | 3-46 | 8658 | Input Channel 18 Apparent Power | S_018_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S018_kVA
141 | 3 | 3-47 | 8660 | Input Channel 18 Power Factor | PF_018 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PF018
142 | 3 | 3-48 | 8662 | Input Channel 18 Load Nature | LC_018 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
143 | 4 | 4-1 | 8664 | User Channel 1 Active Power | P_s001_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ps1_kW
144 | 4 | 4-2 | 8666 | User Channel 1 Reactive Power | Q_s001_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qs1_kvar
145 | 4 | 4-3 | 8668 | User Channel 1 Apparent Power | S_s001_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ss1_kVA
146 | 4 | 4-4 | 8670 | User Channel 1 Power Factor | PF_s001 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PFs1
147 | 4 | 4-5 | 8672 | User Channel 1 Load Nature | LC_s001 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
148 | 4 | 4-6 | 8674 | User Channel 2 Active Power | P_s002_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ps2_kW
149 | 4 | 4-7 | 8676 | User Channel 2 Reactive Power | Q_s002_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qs2_kvar
150 | 4 | 4-8 | 8678 | User Channel 2 Apparent Power | S_s002_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ss2_kVA
151 | 4 | 4-9 | 8680 | User Channel 2 Power Factor | PF_s002 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PFs2
152 | 4 | 4-10 | 8682 | User Channel 2 Load Nature | LC_s002 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
153 | 4 | 4-11 | 8684 | User Channel 3 Active Power | P_s003_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ps3_kW
154 | 4 | 4-12 | 8686 | User Channel 3 Reactive Power | Q_s003_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qs3_kvar
155 | 4 | 4-13 | 8688 | User Channel 3 Apparent Power | S_s003_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ss3_kVA
156 | 4 | 4-14 | 8690 | User Channel 3 Power Factor | PF_s003 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PFs3
157 | 4 | 4-15 | 8692 | User Channel 3 Load Nature | LC_s003 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
158 | 4 | 4-16 | 8694 | User Channel 4 Active Power | P_s004_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ps4_kW
159 | 4 | 4-17 | 8696 | User Channel 4 Reactive Power | Q_s004_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qs4_kvar
160 | 4 | 4-18 | 8698 | User Channel 4 Apparent Power | S_s004_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ss4_kVA
161 | 4 | 4-19 | 8700 | User Channel 4 Power Factor | PF_s004 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PFs4
162 | 4 | 4-20 | 8702 | User Channel 4 Load Nature | LC_s004 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
163 | 4 | 4-21 | 8704 | User Channel 5 Active Power | P_s005_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ps5_kW
164 | 4 | 4-22 | 8706 | User Channel 5 Reactive Power | Q_s005_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qs5_kvar
165 | 4 | 4-23 | 8708 | User Channel 5 Apparent Power | S_s005_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ss5_kVA
166 | 4 | 4-24 | 8710 | User Channel 5 Power Factor | PF_s005 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PFs5
167 | 4 | 4-25 | 8712 | User Channel 5 Load Nature | LC_s005 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
168 | 4 | 4-26 | 8714 | User Channel 6 Active Power | P_s006_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ps6_kW
169 | 4 | 4-27 | 8716 | User Channel 6 Reactive Power | Q_s006_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qs6_kvar
170 | 4 | 4-28 | 8718 | User Channel 6 Apparent Power | S_s006_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ss6_kVA
171 | 4 | 4-29 | 8720 | User Channel 6 Power Factor | PF_s006 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PFs6
172 | 4 | 4-30 | 8722 | User Channel 6 Load Nature | LC_s006 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
173 | 4 | 4-31 | 8724 | User Channel 7 Active Power | P_s007_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
174 | 4 | 4-32 | 8726 | User Channel 7 Reactive Power | Q_s007_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
175 | 4 | 4-33 | 8728 | User Channel 7 Apparent Power | S_s007_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
176 | 4 | 4-34 | 8730 | User Channel 7 Power Factor | PF_s007 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
177 | 4 | 4-35 | 8732 | User Channel 7 Load Nature | LC_s007 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
178 | 4 | 4-36 | 8734 | User Channel 8 Active Power | P_s008_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
179 | 4 | 4-37 | 8736 | User Channel 8 Reactive Power | Q_s008_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
180 | 4 | 4-38 | 8738 | User Channel 8 Apparent Power | S_s008_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
181 | 4 | 4-39 | 8740 | User Channel 8 Power Factor | PF_s008 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
182 | 4 | 4-40 | 8742 | User Channel 8 Load Nature | LC_s008 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
183 | 4 | 4-41 | 8744 | User Channel 9 Active Power | P_s009_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
184 | 4 | 4-42 | 8746 | User Channel 9 Reactive Power | Q_s009_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
185 | 4 | 4-43 | 8748 | User Channel 9 Apparent Power | S_s009_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
186 | 4 | 4-44 | 8750 | User Channel 9 Power Factor | PF_s009 | % | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
187 | 4 | 4-45 | 8752 | User Channel 9 Load Nature | LC_s009 |  | float32 | 12 | R | 2 | 1 | [6 empty] | 14 | 7-20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
188 | 5 | 5-1 | 9472 | Phase A Import Active Energy | EP_IMP_a_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | EPa_IMP_kWh
189 | 5 | 5-2 | 9474 | Phase B Import Active Energy | EP_IMP_b_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | EPb_IMP_kWh
190 | 5 | 5-3 | 9476 | Phase C Import Active Energy | EP_IMP_c_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | EPc_IMP_kWh
191 | 5 | 5-4 | 9478 | System Import Active Energy | EP_IMP_kWh | kWh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | EP_IMP_kWh
192 | 5 | 5-5 | 9480 | Input Channel 1 Import Active Energy | EP_IMP_001_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP001_IMP_kWh
193 | 5 | 5-6 | 9482 | Input Channel 2 Import Active Energy | EP_IMP_002_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP002_IMP_kWh
194 | 5 | 5-7 | 9484 | Input Channel 3 Import Active Energy | EP_IMP_003_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP003_IMP_kWh
195 | 5 | 5-8 | 9486 | Input Channel 4 Import Active Energy | EP_IMP_004_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP004_IMP_kWh
196 | 5 | 5-9 | 9488 | Input Channel 5 Import Active Energy | EP_IMP_005_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP005_IMP_kWh
197 | 5 | 5-10 | 9490 | Input Channel 6 Import Active Energy | EP_IMP_006_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP006_IMP_kWh
198 | 5 | 5-11 | 9492 | Input Channel 7 Import Active Energy | EP_IMP_007_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP007_IMP_kWh
199 | 5 | 5-12 | 9494 | Input Channel 8 Import Active Energy | EP_IMP_008_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP008_IMP_kWh
200 | 5 | 5-13 | 9496 | Input Channel 9 Import Active Energy | EP_IMP_009_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP009_IMP_kWh
201 | 5 | 5-14 | 9498 | Input Channel 10 Import Active Energy | EP_IMP_010_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP010_IMP_kWh
202 | 5 | 5-15 | 9500 | Input Channel 11 Import Active Energy | EP_IMP_011_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP011_IMP_kWh
203 | 5 | 5-16 | 9502 | Input Channel 12 Import Active Energy | EP_IMP_012_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP012_IMP_kWh
204 | 5 | 5-17 | 9504 | Input Channel 13 Import Active Energy | EP_IMP_013_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP013_IMP_kWh
205 | 5 | 5-18 | 9506 | Input Channel 14 Import Active Energy | EP_IMP_014_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP014_IMP_kWh
206 | 5 | 5-19 | 9508 | Input Channel 15 Import Active Energy | EP_IMP_015_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP015_IMP_kWh
207 | 5 | 5-20 | 9510 | Input Channel 16 Import Active Energy | EP_IMP_016_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP016_IMP_kWh
208 | 5 | 5-21 | 9512 | Input Channel 17 Import Active Energy | EP_IMP_017_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP017_IMP_kWh
209 | 5 | 5-22 | 9514 | Input Channel 18 Import Active Energy | EP_IMP_018_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EP018_IMP_kWh
210 | 5 | 5-23 | 9516 | User Channel 1 Import Active Energy | EP_IMP_s001_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EPs1_IMP_kWh
211 | 5 | 5-24 | 9518 | User Channel 2 Import Active Energy | EP_IMP_s002_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EPs2_IMP_kWh
212 | 5 | 5-25 | 9520 | User Channel 3 Import Active Energy | EP_IMP_s003_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EPs3_IMP_kWh
213 | 5 | 5-26 | 9522 | User Channel 4 Import Active Energy | EP_IMP_s004_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EPs4_IMP_kWh
214 | 5 | 5-27 | 9524 | User Channel 5 Import Active Energy | EP_IMP_s005_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EPs5_IMP_kWh
215 | 5 | 5-28 | 9526 | User Channel 6 Import Active Energy | EP_IMP_s006_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EPs6_IMP_kWh
216 | 5 | 5-29 | 9528 | User Channel 7 Import Active Energy | EP_IMP_s007_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy
217 | 5 | 5-30 | 9530 | User Channel 8 Import Active Energy | EP_IMP_s008_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy
218 | 5 | 5-31 | 9532 | User Channel 9 Import Active Energy | EP_IMP_s009_kWh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy
219 | 6 | 6-1 | 11008 | Phase A Import Reactive Energy | EQ_IMP_a_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | EQa_IMP_kvarh
220 | 6 | 6-2 | 11010 | Phase B Import Reactive Energy | EQ_IMP_b_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | EQb_IMP_kvarh
221 | 6 | 6-3 | 11012 | Phase C Import Reactive Energy | EQ_IMP_c_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | EQc_IMP_kvarh
222 | 6 | 6-4 | 11014 | System Import Reactive Energy | EQ_IMP_kvarh | kvarh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | EQ_IMP_kvarh
223 | 6 | 6-5 | 11016 | Input Channel 1 Import Reactive Energy | EQ_IMP_001_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ001_IMP_kvarh
224 | 6 | 6-6 | 11018 | Input Channel 2 Import Reactive Energy | EQ_IMP_002_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ002_IMP_kvarh
225 | 6 | 6-7 | 11020 | Input Channel 3 Import Reactive Energy | EQ_IMP_003_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ003_IMP_kvarh
226 | 6 | 6-8 | 11022 | Input Channel 4 Import Reactive Energy | EQ_IMP_004_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ004_IMP_kvarh
227 | 6 | 6-9 | 11024 | Input Channel 5 Import Reactive Energy | EQ_IMP_005_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ005_IMP_kvarh
228 | 6 | 6-10 | 11026 | Input Channel 6 Import Reactive Energy | EQ_IMP_006_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ006_IMP_kvarh
229 | 6 | 6-11 | 11028 | Input Channel 7 Import Reactive Energy | EQ_IMP_007_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ007_IMP_kvarh
230 | 6 | 6-12 | 11030 | Input Channel 8 Import Reactive Energy | EQ_IMP_008_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ008_IMP_kvarh
231 | 6 | 6-13 | 11032 | Input Channel 9 Import Reactive Energy | EQ_IMP_009_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ009_IMP_kvarh
232 | 6 | 6-14 | 11034 | Input Channel 10 Import Reactive Energy | EQ_IMP_010_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ010_IMP_kvarh
233 | 6 | 6-15 | 11036 | Input Channel 11 Import Reactive Energy | EQ_IMP_011_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ011_IMP_kvarh
234 | 6 | 6-16 | 11038 | Input Channel 12 Import Reactive Energy | EQ_IMP_012_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ012_IMP_kvarh
235 | 6 | 6-17 | 11040 | Input Channel 13 Import Reactive Energy | EQ_IMP_013_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ013_IMP_kvarh
236 | 6 | 6-18 | 11042 | Input Channel 14 Import Reactive Energy | EQ_IMP_014_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ014_IMP_kvarh
237 | 6 | 6-19 | 11044 | Input Channel 15 Import Reactive Energy | EQ_IMP_015_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ015_IMP_kvarh
238 | 6 | 6-20 | 11046 | Input Channel 16 Import Reactive Energy | EQ_IMP_016_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ016_IMP_kvarh
239 | 6 | 6-21 | 11048 | Input Channel 17 Import Reactive Energy | EQ_IMP_017_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ017_IMP_kvarh
240 | 6 | 6-22 | 11050 | Input Channel 18 Import Reactive Energy | EQ_IMP_018_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQ018_IMP_kvarh
241 | 6 | 6-23 | 11052 | User Channel 1 Import Reactive Energy | EQ_IMP_s001_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQs1_IMP_kvarh
242 | 6 | 6-24 | 11054 | User Channel 2 Import Reactive Energy | EQ_IMP_s002_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQs2_IMP_kvarh
243 | 6 | 6-25 | 11056 | User Channel 3 Import Reactive Energy | EQ_IMP_s003_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQs3_IMP_kvarh
244 | 6 | 6-26 | 11058 | User Channel 4 Import Reactive Energy | EQ_IMP_s004_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQs4_IMP_kvarh
245 | 6 | 6-27 | 11060 | User Channel 5 Import Reactive Energy | EQ_IMP_s005_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQs5_IMP_kvarh
246 | 6 | 6-28 | 11062 | User Channel 6 Import Reactive Energy | EQ_IMP_s006_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | EQs6_IMP_kvarh
247 | 6 | 6-29 | 11064 | Phase A Apparent Energy | ES_a_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | ESa_kVAh
248 | 6 | 6-30 | 11066 | Phase B Apparent Energy | ES_b_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | ESb_kVAh
249 | 6 | 6-31 | 11068 | Phase C Apparent Energy | ES_c_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | ESc_kVAh
250 | 6 | 6-32 | 11070 | System Apparent Energy | ES_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 8-20 | energy | energy | energy | energy | energy | energy | energy | ES_kVAh
251 | 6 | 6-33 | 11072 | Input Channel 1 Apparent Energy | ES_001_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES001_kVAh
252 | 6 | 6-34 | 11074 | Input Channel 2 Apparent Energy | ES_002_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES002_kVAh
253 | 6 | 6-35 | 11076 | Input Channel 3 Apparent Energy | ES_003_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES003_kVAh
254 | 6 | 6-36 | 11078 | Input Channel 4 Apparent Energy | ES_004_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES004_kVAh
255 | 6 | 6-37 | 11080 | Input Channel 5 Apparent Energy | ES_005_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES005_kVAh
256 | 6 | 6-38 | 11082 | Input Channel 6 Apparent Energy | ES_006_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES006_kVAh
257 | 6 | 6-39 | 11084 | Input Channel 7 Apparent Energy | ES_007_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES007_kVAh
258 | 6 | 6-40 | 11086 | Input Channel 8 Apparent Energy | ES_008_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES008_kVAh
259 | 6 | 6-41 | 11088 | Input Channel 9 Apparent Energy | ES_009_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES009_kVAh
260 | 6 | 6-42 | 11090 | Input Channel 10 Apparent Energy | ES_010_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES010_kVAh
261 | 6 | 6-43 | 11092 | Input Channel 11 Apparent Energy | ES_011_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES011_kVAh
262 | 6 | 6-44 | 11094 | Input Channel 12 Apparent Energy | ES_012_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES012_kVAh
263 | 6 | 6-45 | 11096 | Input Channel 13 Apparent Energy | ES_013_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES013_kVAh
264 | 6 | 6-46 | 11098 | Input Channel 14 Apparent Energy | ES_014_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES014_kVAh
265 | 6 | 6-47 | 11100 | Input Channel 15 Apparent Energy | ES_015_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES015_kVAh
266 | 6 | 6-48 | 11102 | Input Channel 16 Apparent Energy | ES_016_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES016_kVAh
267 | 6 | 6-49 | 11104 | Input Channel 17 Apparent Energy | ES_017_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES017_kVAh
268 | 6 | 6-50 | 11106 | Input Channel 18 Apparent Energy | ES_018_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ES018_kVAh
269 | 7 | 7-1 | 11108 | User Channel 1 Apparent Energy | ES_s001_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ESs1_kVAh
270 | 7 | 7-2 | 11110 | User Channel 2 Apparent Energy | ES_s002_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ESs2_kVAh
271 | 7 | 7-3 | 11112 | User Channel 3 Apparent Energy | ES_s003_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ESs3_kVAh
272 | 7 | 7-4 | 11114 | User Channel 4 Apparent Energy | ES_s004_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ESs4_kVAh
273 | 7 | 7-5 | 11116 | User Channel 5 Apparent Energy | ES_s005_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ESs5_kVAh
274 | 7 | 7-6 | 11118 | User Channel 6 Apparent Energy | ES_s006_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy | ESs6_kVAh
275 | 7 | 7-7 | 11120 | User Channel 7 Import Reactive Energy | EQ_IMP_s007_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy
276 | 7 | 7-8 | 11122 | User Channel 8 Import Reactive Energy | EQ_IMP_s008_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy
277 | 7 | 7-9 | 11124 | User Channel 9 Import Reactive Energy | EQ_IMP_s009_kvarh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy
278 | 7 | 7-10 | 11126 | User Channel 7 Apparent Energy | ES_s007_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy
279 | 7 | 7-11 | 11128 | User Channel 8 Apparent Energy | ES_s008_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy
280 | 7 | 7-12 | 11130 | User Channel 9 Apparent Energy | ES_s009_kVAh | kVAh | uint32 | 12 | R/W | 2 | 0.1 |  | 1 |  | 3 | 4 |  | 16 | 9-20 | energy | energy | energy | energy | energy | energy | energy
281 | 8 | 8-1 | 11520 | System Active Power Demand | DMD_P_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P_kW
282 | 8 | 8-2 | 11522 | System Active Power Demand Predict | PRED_DMD_P_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
283 | 8 | 8-3 | 11524 | System Max Active Power Demand | MAX_DMD_P_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 12
284 | 8 | 8-4 | 11526 | System Max Active Power Demand Timestamp | MAX_DMDTS_P |  | word | 12 | R | 3 | 1
285 | 8 | 8-5 | 11529 | System Reactive Power Demand | DMD_Q_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q_kvar
286 | 8 | 8-6 | 11531 | System Reactive Power Demand Predict | PRED_DMD_Q_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
287 | 8 | 8-7 | 11533 | System Max Reactive Power Demand | MAX_DMD_Q_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 12
288 | 8 | 8-8 | 11535 | System Max Reactive Power Demand Timestamp | MAX_DMDTS_Q |  | word | 12 | R | 3 | 1
289 | 8 | 8-9 | 11538 | System Apparent Power Demand | DMD_S_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S_kVA
290 | 8 | 8-10 | 11540 | System Apparent Power Demand Predict | PRED_DMD_S_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
291 | 8 | 8-11 | 11542 | System Max Apparent Power Demand | MAX_DMD_S_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 12
292 | 8 | 8-12 | 11544 | System Max Apparent Power Demand Timestamp | MAX_DMDTS_S |  | word | 12 | R | 3 | 1
293 | 8 | 8-13 | 11547 | Phase A Current Demand | DMD_I_a_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ia_A | DMD_I1_A
294 | 8 | 8-14 | 11549 | Phase A Current Demand Predict | PRED_DMD_I_a_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
295 | 8 | 8-15 | 11551 | Phase A Max Current Demand | MAX_DMD_I_a_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 12
296 | 8 | 8-16 | 11553 | Phase A Max Current Demand Timestamp | MAX_DMDTS_I_a |  | word | 12 | R | 3 | 1
297 | 8 | 8-17 | 11556 | Phase A Active Power Demand | DMD_P_a_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Pa_kW
298 | 8 | 8-18 | 11558 | Phase A Active Power Demand Predict | PRED_DMD_P_a_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
299 | 8 | 8-19 | 11560 | Phase A Max Active Power Demand | MAX_DMD_P_a_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 12
300 | 8 | 8-20 | 11562 | Phase A Max Active Power Demand Timestamp | MAX_DMDTS_P_a |  | word | 12 | R | 3 | 1
301 | 8 | 8-21 | 11565 | Phase A Reactive Power Demand | DMD_Q_a_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Qa_kvar
302 | 8 | 8-22 | 11567 | Phase A Reactive Power Demand Predict | PRED_DMD_Q_a_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
303 | 8 | 8-23 | 11569 | Phase A Max Reactive Power Demand | MAX_DMD_Q_a_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 12
304 | 8 | 8-24 | 11571 | Phase A Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_a |  | word | 12 | R | 3 | 1
305 | 8 | 8-25 | 11574 | Phase A Apparent Power Demand | DMD_S_a_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Sa_kVA
306 | 8 | 8-26 | 11576 | Phase A Apparent Power Demand Predict | PRED_DMD_S_a_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
307 | 8 | 8-27 | 11578 | Phase A Max Apparent Power Demand | MAX_DMD_S_a_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 12
308 | 8 | 8-28 | 11580 | Phase A Max Apparent Power Demand Timestamp | MAX_DMDTS_S_a |  | word | 12 | R | 3 | 1
309 | 8 | 8-29 | 11583 | Phase B Current Demand | DMD_I_b_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ib_A | DMD_I2_A
310 | 8 | 8-30 | 11585 | Phase B Current Demand Predict | PRED_DMD_I_b_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
311 | 8 | 8-31 | 11587 | Phase B Max Current Demand | MAX_DMD_I_b_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 12
312 | 8 | 8-32 | 11589 | Phase B Max Current Demand Timestamp | MAX_DMDTS_I_b |  | word | 12 | R | 3 | 1
313 | 8 | 8-33 | 11592 | Phase B Active Power Demand | DMD_P_b_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Pb_kW
314 | 8 | 8-34 | 11594 | Phase A Active Power Demand Predict | PRED_DMD_P_b_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
315 | 8 | 8-35 | 11596 | Phase B Max Active Power Demand | MAX_DMD_P_b_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 12
316 | 8 | 8-36 | 11598 | Phase B Max Active Power Demand Timestamp | MAX_DMDTS_P_b |  | word | 12 | R | 3 | 1
317 | 8 | 8-37 | 11601 | Phase B Reactive Power Demand | DMD_Q_b_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Qb_kvar
318 | 8 | 8-38 | 11603 | Phase B Reactive Power Demand Predict | PRED_DMD_Q_b_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
319 | 8 | 8-39 | 11605 | Phase B Max Reactive Power Demand | MAX_DMD_Q_b_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 12
320 | 8 | 8-40 | 11607 | Phase B Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_b |  | word | 12 | R | 3 | 1
321 | 8 | 8-41 | 11610 | Phase B Apparent Power Demand | DMD_S_b_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Sb_kVA
322 | 8 | 8-42 | 11612 | Phase B Apparent Power Demand Predict | PRED_DMD_S_b_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
323 | 8 | 8-43 | 11614 | Phase B Max Apparent Power Demand | MAX_DMD_S_b_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 12
324 | 8 | 8-44 | 11616 | Phase B Max Apparent Power Demand Timestamp | MAX_DMDTS_S_b |  | word | 12 | R | 3 | 1
325 | 9 | 9-1 | 11619 | Phase C Current Demand | DMD_I_c_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ic_A | DMD_I3_A
326 | 9 | 9-2 | 11621 | Phase C Current Demand Predict | PRED_DMD_I_c_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
327 | 9 | 9-3 | 11623 | Phase C Max Current Demand | MAX_DMD_I_c_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 12
328 | 9 | 9-4 | 11625 | Phase C Max Current Demand Timestamp | MAX_DMDTS_I_c |  | word | 12 | R | 3 | 1
329 | 9 | 9-5 | 11628 | Phase C Active Power Demand | DMD_P_c_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Pc_kW
330 | 9 | 9-6 | 11630 | Phase C Active Power Demand Predict | PRED_DMD_P_c_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
331 | 9 | 9-7 | 11632 | Phase C Max Active Power Demand | MAX_DMD_P_c_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 12
332 | 9 | 9-8 | 11634 | Phase C Max Active Power Demand Timestamp | MAX_DMDTS_P_c |  | word | 12 | R | 3 | 1
333 | 9 | 9-9 | 11637 | Phase C Reactive Power Demand | DMD_Q_c_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Qc_kvar
334 | 9 | 9-10 | 11639 | Phase C Reactive Power Demand Predict | PRED_DMD_Q_c_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
335 | 9 | 9-11 | 11641 | Phase C Max Reactive Power Demand | MAX_DMD_Q_c_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 12
336 | 9 | 9-12 | 11643 | Phase C Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_c |  | word | 12 | R | 3 | 1
337 | 9 | 9-13 | 11646 | Phase C Apparent Power Demand | DMD_S_c_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Sc_kVA
338 | 9 | 9-14 | 11648 | Phase C Apparent Power Demand Predict | PRED_DMD_S_c_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 12-20-21 | demand | demand | demand | demand | demand | demand | demand
339 | 9 | 9-15 | 11650 | Phase C Max Apparent Power Demand | MAX_DMD_S_c_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 12
340 | 9 | 9-16 | 11652 | Phase C Max Apparent Power Demand Timestamp | MAX_DMDTS_S_c |  | word | 12 | R | 3 | 1
341 | 10 | 10-1 | 11655 | Input Channel 1 Current Demand | DMD_I_001_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I001_A
342 | 10 | 10-2 | 11657 | Input Channel 1 Current Demand Predict | PRED_DMD_I_001_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
343 | 10 | 10-3 | 11659 | Input Channel 1 Max Current Demand | MAX_DMD_I_001_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
344 | 10 | 10-4 | 11661 | Input Channel 1 Max Current Demand Timestamp | MAX_DMDTS_I_001 |  | word | 12 | R | 3 | 1
345 | 10 | 10-5 | 11664 | Input Channel 1 Active Power Demand | DMD_P_001_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P001_kW
346 | 10 | 10-6 | 11666 | Input Channel 1 Active Power Demand Predict | PRED_DMD_P_001_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
347 | 10 | 10-7 | 11668 | Input Channel 1 Max Active Power Demand | MAX_DMD_P_001_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
348 | 10 | 10-8 | 11670 | Input Channel 1 Max Active Power Demand Timestamp | MAX_DMDTS_P_001 |  | word | 12 | R | 3 | 1
349 | 10 | 10-9 | 11673 | Input Channel 1 Reactive Power Demand | DMD_Q_001_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q001_kvar
350 | 10 | 10-10 | 11675 | Input Channel 1 Reactive Power Demand Predict | PRED_DMD_Q_001_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
351 | 10 | 10-11 | 11677 | Input Channel 1 Max Reactive Power Demand | MAX_DMD_Q_001_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
352 | 10 | 10-12 | 11679 | Input Channel 1 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_001 |  | word | 12 | R | 3 | 1
353 | 10 | 10-13 | 11682 | Input Channel 1 Apparent Power Demand | DMD_S_001_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S001_kVA
354 | 10 | 10-14 | 11684 | Input Channel 1 Apparent Power Demand Predict | PRED_DMD_S_001_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
355 | 10 | 10-15 | 11686 | Input Channel 1 Max Apparent Power Demand | MAX_DMD_S_001_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
356 | 10 | 10-16 | 11688 | Input Channel 1 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_001 |  | word | 12 | R | 3 | 1
357 | 10 | 10-17 | 11691 | Input Channel 2 Current Demand | DMD_I_002_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I002_A
358 | 10 | 10-18 | 11693 | Input Channel 2 Current Demand Predict | PRED_DMD_I_002_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
359 | 10 | 10-19 | 11695 | Input Channel 2 Max Current Demand | MAX_DMD_I_002_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
360 | 10 | 10-20 | 11697 | Input Channel 2 Max Current Demand Timestamp | MAX_DMDTS_I_002 |  | word | 12 | R | 3 | 1
361 | 10 | 10-21 | 11700 | Input Channel 2 Active Power Demand | DMD_P_002_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P002_kW
362 | 10 | 10-22 | 11702 | Input Channel 2 Active Power Demand Predict | PRED_DMD_P_002_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
363 | 10 | 10-23 | 11704 | Input Channel 2 Max Active Power Demand | MAX_DMD_P_002_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
364 | 10 | 10-24 | 11706 | Input Channel 2 Max Active Power Demand Timestamp | MAX_DMDTS_P_002 |  | word | 12 | R | 3 | 1
365 | 10 | 10-25 | 11709 | Input Channel 2 Reactive Power Demand | DMD_Q_002_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q002_kvar
366 | 10 | 10-26 | 11711 | Input Channel 2 Reactive Power Demand Predict | PRED_DMD_Q_002_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
367 | 10 | 10-27 | 11713 | Input Channel 2 Max Reactive Power Demand | MAX_DMD_Q_002_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
368 | 10 | 10-28 | 11715 | Input Channel 2 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_002 |  | word | 12 | R | 3 | 1
369 | 10 | 10-29 | 11718 | Input Channel 2 Apparent Power Demand | DMD_S_002_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S002_kVA
370 | 10 | 10-30 | 11720 | Input Channel 2 Apparent Power Demand Predict | PRED_DMD_S_002_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
371 | 10 | 10-31 | 11722 | Input Channel 2 Max Apparent Power Demand | MAX_DMD_S_002_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
372 | 10 | 10-32 | 11724 | Input Channel 2 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_002 |  | word | 12 | R | 3 | 1
373 | 10 | 10-33 | 11727 | Input Channel 3 Current Demand | DMD_I_003_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I003_A
374 | 10 | 10-34 | 11729 | Input Channel 3 Current Demand Predict | PRED_DMD_I_003_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
375 | 10 | 10-35 | 11731 | Input Channel 3 Max Current Demand | MAX_DMD_I_003_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
376 | 10 | 10-36 | 11733 | Input Channel 3 Max Current Demand Timestamp | MAX_DMDTS_I_003 |  | word | 12 | R | 3 | 1
377 | 10 | 10-37 | 11736 | Input Channel 3 Active Power Demand | DMD_P_003_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P003_kW
378 | 10 | 10-38 | 11738 | Input Channel 3 Active Power Demand Predict | PRED_DMD_P_003_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
379 | 10 | 10-39 | 11740 | Input Channel 3 Max Active Power Demand | MAX_DMD_P_003_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
380 | 10 | 10-40 | 11742 | Input Channel 3 Max Active Power Demand Timestamp | MAX_DMDTS_P_003 |  | word | 12 | R | 3 | 1
381 | 10 | 10-41 | 11745 | Input Channel 3 Reactive Power Demand | DMD_Q_003_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q003_kvar
382 | 10 | 10-42 | 11747 | Input Channel 3 Reactive Power Demand Predict | PRED_DMD_Q_003_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
383 | 10 | 10-43 | 11749 | Input Channel 3 Max Reactive Power Demand | MAX_DMD_Q_003_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
384 | 10 | 10-44 | 11751 | Input Channel 3 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_003 |  | word | 12 | R | 3 | 1
385 | 10 | 10-45 | 11754 | Input Channel 3 Apparent Power Demand | DMD_S_003_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S003_kVA
386 | 10 | 10-46 | 11756 | Input Channel 3 Apparent Power Demand Predict | PRED_DMD_S_003_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
387 | 10 | 10-47 | 11758 | Input Channel 3 Max Apparent Power Demand | MAX_DMD_S_003_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
388 | 10 | 10-48 | 11760 | Input Channel 3 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_003 |  | word | 12 | R | 3 | 1
389 | 11 | 11-1 | 11763 | Input Channel 4 Current Demand | DMD_I_004_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I004_A
390 | 11 | 11-2 | 11765 | Input Channel 4 Current Demand Predict | PRED_DMD_I_004_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
391 | 11 | 11-3 | 11767 | Input Channel 4 Max Current Demand | MAX_DMD_I_004_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
392 | 11 | 11-4 | 11769 | Input Channel 4 Max Current Demand Timestamp | MAX_DMDTS_I_004 |  | word | 12 | R | 3 | 1
393 | 11 | 11-5 | 11772 | Input Channel 4 Active Power Demand | DMD_P_004_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P004_kW
394 | 11 | 11-6 | 11774 | Input Channel 4 Active Power Demand Predict | PRED_DMD_P_004_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
395 | 11 | 11-7 | 11776 | Input Channel 4 Max Active Power Demand | MAX_DMD_P_004_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
396 | 11 | 11-8 | 11778 | Input Channel 4 Max Active Power Demand Timestamp | MAX_DMDTS_P_004 |  | word | 12 | R | 3 | 1
397 | 11 | 11-9 | 11781 | Input Channel 4 Reactive Power Demand | DMD_Q_004_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q004_kvar
398 | 11 | 11-10 | 11783 | Input Channel 4 Reactive Power Demand Predict | PRED_DMD_Q_004_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
399 | 11 | 11-11 | 11785 | Input Channel 4 Max Reactive Power Demand | MAX_DMD_Q_004_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
400 | 11 | 11-12 | 11787 | Input Channel 4 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_004 |  | word | 12 | R | 3 | 1
401 | 11 | 11-13 | 11790 | Input Channel 4 Apparent Power Demand | DMD_S_004_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S004_kVA
402 | 11 | 11-14 | 11792 | Input Channel 4 Apparent Power Demand Predict | PRED_DMD_S_004_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
403 | 11 | 11-15 | 11794 | Input Channel 4 Max Apparent Power Demand | MAX_DMD_S_004_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
404 | 11 | 11-16 | 11796 | Input Channel 4 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_004 |  | word | 12 | R | 3 | 1
405 | 11 | 11-17 | 11799 | Input Channel 5 Current Demand | DMD_I_005_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I005_A
406 | 11 | 11-18 | 11801 | Input Channel 5 Current Demand Predict | PRED_DMD_I_005_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
407 | 11 | 11-19 | 11803 | Input Channel 5 Max Current Demand | MAX_DMD_I_005_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
408 | 11 | 11-20 | 11805 | Input Channel 5 Max Current Demand Timestamp | MAX_DMDTS_I_005 |  | word | 12 | R | 3 | 1
409 | 11 | 11-21 | 11808 | Input Channel 5 Active Power Demand | DMD_P_005_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P005_kW
410 | 11 | 11-22 | 11810 | Input Channel 5 Active Power Demand Predict | PRED_DMD_P_005_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
411 | 11 | 11-23 | 11812 | Input Channel 5 Max Active Power Demand | MAX_DMD_P_005_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
412 | 11 | 11-24 | 11814 | Input Channel 5 Max Active Power Demand Timestamp | MAX_DMDTS_P_005 |  | word | 12 | R | 3 | 1
413 | 11 | 11-25 | 11817 | Input Channel 5 Reactive Power Demand | DMD_Q_005_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q005_kvar
414 | 11 | 11-26 | 11819 | Input Channel 5 Reactive Power Demand Predict | PRED_DMD_Q_005_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
415 | 11 | 11-27 | 11821 | Input Channel 5 Max Reactive Power Demand | MAX_DMD_Q_005_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
416 | 11 | 11-28 | 11823 | Input Channel 5 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_005 |  | word | 12 | R | 3 | 1
417 | 11 | 11-29 | 11826 | Input Channel 5 Apparent Power Demand | DMD_S_005_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S005_kVA
418 | 11 | 11-30 | 11828 | Input Channel 5 Apparent Power Demand Predict | PRED_DMD_S_005_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
419 | 11 | 11-31 | 11830 | Input Channel 5 Max Apparent Power Demand | MAX_DMD_S_005_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
420 | 11 | 11-32 | 11832 | Input Channel 5 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_005 |  | word | 12 | R | 3 | 1
421 | 11 | 11-33 | 11835 | Input Channel 6 Current Demand | DMD_I_006_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I006_A
422 | 11 | 11-34 | 11837 | Input Channel 6 Current Demand Predict | PRED_DMD_I_006_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
423 | 11 | 11-35 | 11839 | Input Channel 6 Max Current Demand | MAX_DMD_I_006_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
424 | 11 | 11-36 | 11841 | Input Channel 6 Max Current Demand Timestamp | MAX_DMDTS_I_006 |  | word | 12 | R | 3 | 1
425 | 11 | 11-37 | 11844 | Input Channel 6 Active Power Demand | DMD_P_006_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P006_kW
426 | 11 | 11-38 | 11846 | Input Channel 6 Active Power Demand Predict | PRED_DMD_P_006_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
427 | 11 | 11-39 | 11848 | Input Channel 6 Max Active Power Demand | MAX_DMD_P_006_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
428 | 11 | 11-40 | 11850 | Input Channel 6 Max Active Power Demand Timestamp | MAX_DMDTS_P_006 |  | word | 12 | R | 3 | 1
429 | 11 | 11-41 | 11853 | Input Channel 6 Reactive Power Demand | DMD_Q_006_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q006_kvar
430 | 11 | 11-42 | 11855 | Input Channel 6 Reactive Power Demand Predict | PRED_DMD_Q_006_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
431 | 11 | 11-43 | 11857 | Input Channel 6 Max Reactive Power Demand | MAX_DMD_Q_006_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
432 | 11 | 11-44 | 11859 | Input Channel 6 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_006 |  | word | 12 | R | 3 | 1
433 | 11 | 11-45 | 11862 | Input Channel 6 Apparent Power Demand | DMD_S_006_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S006_kVA
434 | 11 | 11-46 | 11864 | Input Channel 6 Apparent Power Demand Predict | PRED_DMD_S_006_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
435 | 11 | 11-47 | 11866 | Input Channel 6 Max Apparent Power Demand | MAX_DMD_S_006_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
436 | 11 | 11-48 | 11868 | Input Channel 6 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_006 |  | word | 12 | R | 3 | 1
437 | 12 | 12-1 | 11871 | Input Channel 7 Current Demand | DMD_I_007_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I007_A
438 | 12 | 12-2 | 11873 | Input Channel 7 Current Demand Predict | PRED_DMD_I_007_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
439 | 12 | 12-3 | 11875 | Input Channel 7 Max Current Demand | MAX_DMD_I_007_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
440 | 12 | 12-4 | 11877 | Input Channel 7 Max Current Demand Timestamp | MAX_DMDTS_I_007 |  | word | 12 | R | 3 | 1
441 | 12 | 12-5 | 11880 | Input Channel 7 Active Power Demand | DMD_P_007_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P007_kW
442 | 12 | 12-6 | 11882 | Input Channel 7 Active Power Demand Predict | PRED_DMD_P_007_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
443 | 12 | 12-7 | 11884 | Input Channel 7 Max Active Power Demand | MAX_DMD_P_007_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
444 | 12 | 12-8 | 11886 | Input Channel 7 Max Active Power Demand Timestamp | MAX_DMDTS_P_007 |  | word | 12 | R | 3 | 1
445 | 12 | 12-9 | 11889 | Input Channel 7 Reactive Power Demand | DMD_Q_007_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q007_kvar
446 | 12 | 12-10 | 11891 | Input Channel 7 Reactive Power Demand Predict | PRED_DMD_Q_007_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
447 | 12 | 12-11 | 11893 | Input Channel 7 Max Reactive Power Demand | MAX_DMD_Q_007_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
448 | 12 | 12-12 | 11895 | Input Channel 7 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_007 |  | word | 12 | R | 3 | 1
449 | 12 | 12-13 | 11898 | Input Channel 7 Apparent Power Demand | DMD_S_007_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S007_kVA
450 | 12 | 12-14 | 11900 | Input Channel 7 Apparent Power Demand Predict | PRED_DMD_S_007_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
451 | 12 | 12-15 | 11902 | Input Channel 7 Max Apparent Power Demand | MAX_DMD_S_007_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
452 | 12 | 12-16 | 11904 | Input Channel 7 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_007 |  | word | 12 | R | 3 | 1
453 | 12 | 12-17 | 11907 | Input Channel 8 Current Demand | DMD_I_008_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I008_A
454 | 12 | 12-18 | 11909 | Input Channel 8 Current Demand Predict | PRED_DMD_I_008_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
455 | 12 | 12-19 | 11911 | Input Channel 8 Max Current Demand | MAX_DMD_I_008_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
456 | 12 | 12-20 | 11913 | Input Channel 8 Max Current Demand Timestamp | MAX_DMDTS_I_008 |  | word | 12 | R | 3 | 1
457 | 12 | 12-21 | 11916 | Input Channel 8 Active Power Demand | DMD_P_008_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P008_kW
458 | 12 | 12-22 | 11918 | Input Channel 8 Active Power Demand Predict | PRED_DMD_P_008_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
459 | 12 | 12-23 | 11920 | Input Channel 8 Max Active Power Demand | MAX_DMD_P_008_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
460 | 12 | 12-24 | 11922 | Input Channel 8 Max Active Power Demand Timestamp | MAX_DMDTS_P_008 |  | word | 12 | R | 3 | 1
461 | 12 | 12-25 | 11925 | Input Channel 8 Reactive Power Demand | DMD_Q_008_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q008_kvar
462 | 12 | 12-26 | 11927 | Input Channel 8 Reactive Power Demand Predict | PRED_DMD_Q_008_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
463 | 12 | 12-27 | 11929 | Input Channel 8 Max Reactive Power Demand | MAX_DMD_Q_008_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
464 | 12 | 12-28 | 11931 | Input Channel 8 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_008 |  | word | 12 | R | 3 | 1
465 | 12 | 12-29 | 11934 | Input Channel 8 Apparent Power Demand | DMD_S_008_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S008_kVA
466 | 12 | 12-30 | 11936 | Input Channel 8 Apparent Power Demand Predict | PRED_DMD_S_008_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
467 | 12 | 12-31 | 11938 | Input Channel 8 Max Apparent Power Demand | MAX_DMD_S_008_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
468 | 12 | 12-32 | 11940 | Input Channel 8 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_008 |  | word | 12 | R | 3 | 1
469 | 12 | 12-33 | 11943 | Input Channel 9 Current Demand | DMD_I_009_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I009_A
470 | 12 | 12-34 | 11945 | Input Channel 9 Current Demand Predict | PRED_DMD_I_009_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
471 | 12 | 12-35 | 11947 | Input Channel 9 Max Current Demand | MAX_DMD_I_009_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
472 | 12 | 12-36 | 11949 | Input Channel 9 Max Current Demand Timestamp | MAX_DMDTS_I_009 |  | word | 12 | R | 3 | 1
473 | 12 | 12-37 | 11952 | Input Channel 9 Active Power Demand | DMD_P_009_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P009_kW
474 | 12 | 12-38 | 11954 | Input Channel 9 Active Power Demand Predict | PRED_DMD_P_009_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
475 | 12 | 12-39 | 11956 | Input Channel 9 Max Active Power Demand | MAX_DMD_P_009_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
476 | 12 | 12-40 | 11958 | Input Channel 9 Max Active Power Demand Timestamp | MAX_DMDTS_P_009 |  | word | 12 | R | 3 | 1
477 | 12 | 12-41 | 11961 | Input Channel 9 Reactive Power Demand | DMD_Q_009_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q009_kvar
478 | 12 | 12-42 | 11963 | Input Channel 9 Reactive Power Demand Predict | PRED_DMD_Q_009_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
479 | 12 | 12-43 | 11965 | Input Channel 9 Max Reactive Power Demand | MAX_DMD_Q_009_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
480 | 12 | 12-44 | 11967 | Input Channel 9 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_009 |  | word | 12 | R | 3 | 1
481 | 12 | 12-45 | 11970 | Input Channel 9 Apparent Power Demand | DMD_S_009_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S009_kVA
482 | 12 | 12-46 | 11972 | Input Channel 9 Apparent Power Demand Predict | PRED_DMD_S_009_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
483 | 12 | 12-47 | 11974 | Input Channel 9 Max Apparent Power Demand | MAX_DMD_S_009_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
484 | 12 | 12-48 | 11976 | Input Channel 9 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_009 |  | word | 12 | R | 3 | 1
485 | 13 | 13-1 | 11979 | Input Channel 10 Current Demand | DMD_I_010_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I010_A
486 | 13 | 13-2 | 11981 | Input Channel 10 Current Demand Predict | PRED_DMD_I_010_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
487 | 13 | 13-3 | 11983 | Input Channel 10 Max Current Demand | MAX_DMD_I_010_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
488 | 13 | 13-4 | 11985 | Input Channel 10 Max Current Demand Timestamp | MAX_DMDTS_I_010 |  | word | 12 | R | 3 | 1
489 | 13 | 13-5 | 11988 | Input Channel 10 Active Power Demand | DMD_P_010_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P010_kW
490 | 13 | 13-6 | 11990 | Input Channel 10 Active Power Demand Predict | PRED_DMD_P_010_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
491 | 13 | 13-7 | 11992 | Input Channel 10 Max Active Power Demand | MAX_DMD_P_010_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
492 | 13 | 13-8 | 11994 | Input Channel 10 Max Active Power Demand Timestamp | MAX_DMDTS_P_010 |  | word | 12 | R | 3 | 1
493 | 13 | 13-9 | 11997 | Input Channel 10 Reactive Power Demand | DMD_Q_010_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q010_kvar
494 | 13 | 13-10 | 11999 | Input Channel 10 Reactive Power Demand Predict | PRED_DMD_Q_010_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
495 | 13 | 13-11 | 12001 | Input Channel 10 Max Reactive Power Demand | MAX_DMD_Q_010_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
496 | 13 | 13-12 | 12003 | Input Channel 10 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_010 |  | word | 12 | R | 3 | 1
497 | 13 | 13-13 | 12006 | Input Channel 10 Apparent Power Demand | DMD_S_010_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S010_kVA
498 | 13 | 13-14 | 12008 | Input Channel 10 Apparent Power Demand Predict | PRED_DMD_S_010_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
499 | 13 | 13-15 | 12010 | Input Channel 10 Max Apparent Power Demand | MAX_DMD_S_010_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
500 | 13 | 13-16 | 12012 | Input Channel 10 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_010 |  | word | 12 | R | 3 | 1
501 | 13 | 13-17 | 12015 | Input Channel 11 Current Demand | DMD_I_011_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I011_A
502 | 13 | 13-18 | 12017 | Input Channel 11 Current Demand Predict | PRED_DMD_I_011_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
503 | 13 | 13-19 | 12019 | Input Channel 11 Max Current Demand | MAX_DMD_I_011_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
504 | 13 | 13-20 | 12021 | Input Channel 11 Max Current Demand Timestamp | MAX_DMDTS_I_011 |  | word | 12 | R | 3 | 1
505 | 13 | 13-21 | 12024 | Input Channel 11 Active Power Demand | DMD_P_011_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P011_kW
506 | 13 | 13-22 | 12026 | Input Channel 11 Active Power Demand Predict | PRED_DMD_P_011_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
507 | 13 | 13-23 | 12028 | Input Channel 11 Max Active Power Demand | MAX_DMD_P_011_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
508 | 13 | 13-24 | 12030 | Input Channel 11 Max Active Power Demand Timestamp | MAX_DMDTS_P_011 |  | word | 12 | R | 3 | 1
509 | 13 | 13-25 | 12033 | Input Channel 11 Reactive Power Demand | DMD_Q_011_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q011_kvar
510 | 13 | 13-26 | 12035 | Input Channel 11 Reactive Power Demand Predict | PRED_DMD_Q_011_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
511 | 13 | 13-27 | 12037 | Input Channel 11 Max Reactive Power Demand | MAX_DMD_Q_011_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
512 | 13 | 13-28 | 12039 | Input Channel 11 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_011 |  | word | 12 | R | 3 | 1
513 | 13 | 13-29 | 12042 | Input Channel 11 Apparent Power Demand | DMD_S_011_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S011_kVA
514 | 13 | 13-30 | 12044 | Input Channel 11 Apparent Power Demand Predict | PRED_DMD_S_011_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
515 | 13 | 13-31 | 12046 | Input Channel 11 Max Apparent Power Demand | MAX_DMD_S_011_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
516 | 13 | 13-32 | 12048 | Input Channel 11 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_011 |  | word | 12 | R | 3 | 1
517 | 13 | 13-33 | 12051 | Input Channel 12 Current Demand | DMD_I_012_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I012_A
518 | 13 | 13-34 | 12053 | Input Channel 12 Current Demand Predict | PRED_DMD_I_012_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
519 | 13 | 13-35 | 12055 | Input Channel 12 Max Current Demand | MAX_DMD_I_012_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
520 | 13 | 13-36 | 12057 | Input Channel 12 Max Current Demand Timestamp | MAX_DMDTS_I_012 |  | word | 12 | R | 3 | 1
521 | 13 | 13-37 | 12060 | Input Channel 12 Active Power Demand | DMD_P_012_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P012_kW
522 | 13 | 13-38 | 12062 | Input Channel 12 Active Power Demand Predict | PRED_DMD_P_012_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
523 | 13 | 13-39 | 12064 | Input Channel 12 Max Active Power Demand | MAX_DMD_P_012_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
524 | 13 | 13-40 | 12066 | Input Channel 12 Max Active Power Demand Timestamp | MAX_DMDTS_P_012 |  | word | 12 | R | 3 | 1
525 | 13 | 13-41 | 12069 | Input Channel 12 Reactive Power Demand | DMD_Q_012_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q012_kvar
526 | 13 | 13-42 | 12071 | Input Channel 12 Reactive Power Demand Predict | PRED_DMD_Q_012_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
527 | 13 | 13-43 | 12073 | Input Channel 12 Max Reactive Power Demand | MAX_DMD_Q_012_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
528 | 13 | 13-44 | 12075 | Input Channel 12 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_012 |  | word | 12 | R | 3 | 1
529 | 13 | 13-45 | 12078 | Input Channel 12 Apparent Power Demand | DMD_S_012_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S012_kVA
530 | 13 | 13-46 | 12080 | Input Channel 12 Apparent Power Demand Predict | PRED_DMD_S_012_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
531 | 13 | 13-47 | 12082 | Input Channel 12 Max Apparent Power Demand | MAX_DMD_S_012_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
532 | 13 | 13-48 | 12084 | Input Channel 12 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_012 |  | word | 12 | R | 3 | 1
533 | 14 | 14-1 | 12087 | Input Channel 13 Current Demand | DMD_I_013_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I013_A
534 | 14 | 14-2 | 12089 | Input Channel 13 Current Demand Predict | PRED_DMD_I_013_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
535 | 14 | 14-3 | 12091 | Input Channel 13 Max Current Demand | MAX_DMD_I_013_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
536 | 14 | 14-4 | 12093 | Input Channel 13 Max Current Demand Timestamp | MAX_DMDTS_I_013 |  | word | 12 | R | 3 | 1
537 | 14 | 14-5 | 12096 | Input Channel 13 Active Power Demand | DMD_P_013_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P013_kW
538 | 14 | 14-6 | 12098 | Input Channel 13 Active Power Demand Predict | PRED_DMD_P_013_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
539 | 14 | 14-7 | 12100 | Input Channel 13 Max Active Power Demand | MAX_DMD_P_013_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
540 | 14 | 14-8 | 12102 | Input Channel 13 Max Active Power Demand Timestamp | MAX_DMDTS_P_013 |  | word | 12 | R | 3 | 1
541 | 14 | 14-9 | 12105 | Input Channel 13 Reactive Power Demand | DMD_Q_013_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q013_kvar
542 | 14 | 14-10 | 12107 | Input Channel 13 Reactive Power Demand Predict | PRED_DMD_Q_013_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
543 | 14 | 14-11 | 12109 | Input Channel 13 Max Reactive Power Demand | MAX_DMD_Q_013_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
544 | 14 | 14-12 | 12111 | Input Channel 13 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_013 |  | word | 12 | R | 3 | 1
545 | 14 | 14-13 | 12114 | Input Channel 13 Apparent Power Demand | DMD_S_013_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S013_kVA
546 | 14 | 14-14 | 12116 | Input Channel 13 Apparent Power Demand Predict | PRED_DMD_S_013_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
547 | 14 | 14-15 | 12118 | Input Channel 13 Max Apparent Power Demand | MAX_DMD_S_013_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
548 | 14 | 14-16 | 12120 | Input Channel 13 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_013 |  | word | 12 | R | 3 | 1
549 | 14 | 14-17 | 12123 | Input Channel 14 Current Demand | DMD_I_014_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I014_A
550 | 14 | 14-18 | 12125 | Input Channel 14 Current Demand Predict | PRED_DMD_I_014_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
551 | 14 | 14-19 | 12127 | Input Channel 14 Max Current Demand | MAX_DMD_I_014_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
552 | 14 | 14-20 | 12129 | Input Channel 14 Max Current Demand Timestamp | MAX_DMDTS_I_014 |  | word | 12 | R | 3 | 1
553 | 14 | 14-21 | 12132 | Input Channel 14 Active Power Demand | DMD_P_014_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P014_kW
554 | 14 | 14-22 | 12134 | Input Channel 14 Active Power Demand Predict | PRED_DMD_P_014_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
555 | 14 | 14-23 | 12136 | Input Channel 14 Max Active Power Demand | MAX_DMD_P_014_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
556 | 14 | 14-24 | 12138 | Input Channel 14 Max Active Power Demand Timestamp | MAX_DMDTS_P_014 |  | word | 12 | R | 3 | 1
557 | 14 | 14-25 | 12141 | Input Channel 14 Reactive Power Demand | DMD_Q_014_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q014_kvar
558 | 14 | 14-26 | 12143 | Input Channel 14 Reactive Power Demand Predict | PRED_DMD_Q_014_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
559 | 14 | 14-27 | 12145 | Input Channel 14 Max Reactive Power Demand | MAX_DMD_Q_014_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
560 | 14 | 14-28 | 12147 | Input Channel 14 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_014 |  | word | 12 | R | 3 | 1
561 | 14 | 14-29 | 12150 | Input Channel 14 Apparent Power Demand | DMD_S_014_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S014_kVA
562 | 14 | 14-30 | 12152 | Input Channel 14 Apparent Power Demand Predict | PRED_DMD_S_014_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
563 | 14 | 14-31 | 12154 | Input Channel 14 Max Apparent Power Demand | MAX_DMD_S_014_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
564 | 14 | 14-32 | 12156 | Input Channel 14 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_014 |  | word | 12 | R | 3 | 1
565 | 14 | 14-33 | 12159 | Input Channel 15 Current Demand | DMD_I_015_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I015_A
566 | 14 | 14-34 | 12161 | Input Channel 15 Current Demand Predict | PRED_DMD_I_015_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
567 | 14 | 14-35 | 12163 | Input Channel 15 Max Current Demand | MAX_DMD_I_015_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
568 | 14 | 14-36 | 12165 | Input Channel 15 Max Current Demand Timestamp | MAX_DMDTS_I_015 |  | word | 12 | R | 3 | 1
569 | 14 | 14-37 | 12168 | Input Channel 15 Active Power Demand | DMD_P_015_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P015_kW
570 | 14 | 14-38 | 12170 | Input Channel 15 Active Power Demand Predict | PRED_DMD_P_015_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
571 | 14 | 14-39 | 12172 | Input Channel 15 Max Active Power Demand | MAX_DMD_P_015_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
572 | 14 | 14-40 | 12174 | Input Channel 15 Max Active Power Demand Timestamp | MAX_DMDTS_P_015 |  | word | 12 | R | 3 | 1
573 | 14 | 14-41 | 12177 | Input Channel 15 Reactive Power Demand | DMD_Q_015_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q015_kvar
574 | 14 | 14-42 | 12179 | Input Channel 15 Reactive Power Demand Predict | PRED_DMD_Q_015_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
575 | 14 | 14-43 | 12181 | Input Channel 15 Max Reactive Power Demand | MAX_DMD_Q_015_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
576 | 14 | 14-44 | 12183 | Input Channel 15 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_015 |  | word | 12 | R | 3 | 1
577 | 14 | 14-45 | 12186 | Input Channel 15 Apparent Power Demand | DMD_S_015_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S015_kVA
578 | 14 | 14-46 | 12188 | Input Channel 15 Apparent Power Demand Predict | PRED_DMD_S_015_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
579 | 14 | 14-47 | 12190 | Input Channel 15 Max Apparent Power Demand | MAX_DMD_S_015_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
580 | 14 | 14-48 | 12192 | Input Channel 15 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_015 |  | word | 12 | R | 3 | 1
581 | 15 | 15-1 | 12195 | Input Channel 16 Current Demand | DMD_I_016_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I016_A
582 | 15 | 15-2 | 12197 | Input Channel 16 Current Demand Predict | PRED_DMD_I_016_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
583 | 15 | 15-3 | 12199 | Input Channel 16 Max Current Demand | MAX_DMD_I_016_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
584 | 15 | 15-4 | 12201 | Input Channel 16 Max Current Demand Timestamp | MAX_DMDTS_I_016 |  | word | 12 | R | 3 | 1
585 | 15 | 15-5 | 12204 | Input Channel 16 Active Power Demand | DMD_P_016_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P016_kW
586 | 15 | 15-6 | 12206 | Input Channel 16 Active Power Demand Predict | PRED_DMD_P_016_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
587 | 15 | 15-7 | 12208 | Input Channel 16 Max Active Power Demand | MAX_DMD_P_016_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
588 | 15 | 15-8 | 12210 | Input Channel 16 Max Active Power Demand Timestamp | MAX_DMDTS_P_016 |  | word | 12 | R | 3 | 1
589 | 15 | 15-9 | 12213 | Input Channel 16 Reactive Power Demand | DMD_Q_016_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q016_kvar
590 | 15 | 15-10 | 12215 | Input Channel 16 Reactive Power Demand Predict | PRED_DMD_Q_016_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
591 | 15 | 15-11 | 12217 | Input Channel 16 Max Reactive Power Demand | MAX_DMD_Q_016_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
592 | 15 | 15-12 | 12219 | Input Channel 16 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_016 |  | word | 12 | R | 3 | 1
593 | 15 | 15-13 | 12222 | Input Channel 16 Apparent Power Demand | DMD_S_016_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S016_kVA
594 | 15 | 15-14 | 12224 | Input Channel 16 Apparent Power Demand Predict | PRED_DMD_S_016_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
595 | 15 | 15-15 | 12226 | Input Channel 16 Max Apparent Power Demand | MAX_DMD_S_016_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
596 | 15 | 15-16 | 12228 | Input Channel 16 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_016 |  | word | 12 | R | 3 | 1
597 | 15 | 15-17 | 12231 | Input Channel 17 Current Demand | DMD_I_017_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I017_A
598 | 15 | 15-18 | 12233 | Input Channel 17 Current Demand Predict | PRED_DMD_I_017_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
599 | 15 | 15-19 | 12235 | Input Channel 17 Max Current Demand | MAX_DMD_I_017_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
600 | 15 | 15-20 | 12237 | Input Channel 17 Max Current Demand Timestamp | MAX_DMDTS_I_017 |  | word | 12 | R | 3 | 1
601 | 15 | 15-21 | 12240 | Input Channel 17 Active Power Demand | DMD_P_017_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P017_kW
602 | 15 | 15-22 | 12242 | Input Channel 17 Active Power Demand Predict | PRED_DMD_P_017_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
603 | 15 | 15-23 | 12244 | Input Channel 17 Max Active Power Demand | MAX_DMD_P_017_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
604 | 15 | 15-24 | 12246 | Input Channel 17 Max Active Power Demand Timestamp | MAX_DMDTS_P_017 |  | word | 12 | R | 3 | 1
605 | 15 | 15-25 | 12249 | Input Channel 17 Reactive Power Demand | DMD_Q_017_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q017_kvar
606 | 15 | 15-26 | 12251 | Input Channel 17 Reactive Power Demand Predict | PRED_DMD_Q_017_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
607 | 15 | 15-27 | 12253 | Input Channel 17 Max Reactive Power Demand | MAX_DMD_Q_017_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
608 | 15 | 15-28 | 12255 | Input Channel 17 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_017 |  | word | 12 | R | 3 | 1
609 | 15 | 15-29 | 12258 | Input Channel 17 Apparent Power Demand | DMD_S_017_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S017_kVA
610 | 15 | 15-30 | 12260 | Input Channel 17 Apparent Power Demand Predict | PRED_DMD_S_017_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
611 | 15 | 15-31 | 12262 | Input Channel 17 Max Apparent Power Demand | MAX_DMD_S_017_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
612 | 15 | 15-32 | 12264 | Input Channel 17 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_017 |  | word | 12 | R | 3 | 1
613 | 15 | 15-33 | 12267 | Input Channel 18 Current Demand | DMD_I_018_A | A | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_I018_A
614 | 15 | 15-34 | 12269 | Input Channel 18 Current Demand Predict | PRED_DMD_I_018_A | A | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
615 | 15 | 15-35 | 12271 | Input Channel 18 Max Current Demand | MAX_DMD_I_018_A | A | float32 | 12 | R | 2 | 1 | [7 empty] | 13
616 | 15 | 15-36 | 12273 | Input Channel 18 Max Current Demand Timestamp | MAX_DMDTS_I_018 |  | word | 12 | R | 3 | 1
617 | 15 | 15-37 | 12276 | Input Channel 18 Active Power Demand | DMD_P_018_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_P018_kW
618 | 15 | 15-38 | 12278 | Input Channel 18 Active Power Demand Predict | PRED_DMD_P_018_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
619 | 15 | 15-39 | 12280 | Input Channel 18 Max Active Power Demand | MAX_DMD_P_018_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
620 | 15 | 15-40 | 12282 | Input Channel 18 Max Active Power Demand Timestamp | MAX_DMDTS_P_018 |  | word | 12 | R | 3 | 1
621 | 15 | 15-41 | 12285 | Input Channel 18 Reactive Power Demand | DMD_Q_018_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Q018_kvar
622 | 15 | 15-42 | 12287 | Input Channel 18 Reactive Power Demand Predict | PRED_DMD_Q_018_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
623 | 15 | 15-43 | 12289 | Input Channel 18 Max Reactive Power Demand | MAX_DMD_Q_018_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
624 | 15 | 15-44 | 12291 | Input Channel 18 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_018 |  | word | 12 | R | 3 | 1
625 | 15 | 15-45 | 12294 | Input Channel 18 Apparent Power Demand | DMD_S_018_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_S018_kVA
626 | 15 | 15-46 | 12296 | Input Channel 18 Apparent Power Demand Predict | PRED_DMD_S_018_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
627 | 15 | 15-47 | 12298 | Input Channel 18 Max Apparent Power Demand | MAX_DMD_S_018_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
628 | 15 | 15-48 | 12300 | Input Channel 18 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_018 |  | word | 12 | R | 3 | 1
629 | 16 | 16-1 | 12303 | User Channel 1 Active Power Demand | DMD_P_s001_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ps1_kW
630 | 16 | 16-2 | 12305 | User Channel 1 Active Power Demand Predict | PRED_DMD_P_s001_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
631 | 16 | 16-3 | 12307 | User Channel 1 Max Active Power Demand | MAX_DMD_P_s001_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
632 | 16 | 16-4 | 12309 | User Channel 1 Max Active Power Demand Timestamp | MAX_DMDTS_P_001 |  | word | 12 | R | 3 | 1
633 | 16 | 16-5 | 12312 | User Channel 1 Reactive Power Demand | DMD_Q_s001_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Qs1_kvar
634 | 16 | 16-6 | 12314 | User Channel 1 Reactive Power Demand Predict | PRED_DMD_Q_s001_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
635 | 16 | 16-7 | 12316 | User Channel 1 Max Reactive Power Demand | MAX_DMD_Q_s001_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
636 | 16 | 16-8 | 12318 | User Channel 1 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_001 |  | word | 12 | R | 3 | 1
637 | 16 | 16-9 | 12321 | User Channel 1 Apparent Power Demand | DMD_S_s001_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ss1_kVA
638 | 16 | 16-10 | 12323 | User Channel 1 Apparent Power Demand Predict | PRED_DMD_S_s001_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
639 | 16 | 16-11 | 12325 | User Channel 1 Max Apparent Power Demand | MAX_DMD_S_s001_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
640 | 16 | 16-12 | 12327 | User Channel 1 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_001 |  | word | 12 | R | 3 | 1
641 | 16 | 16-13 | 12330 | User Channel 2 Active Power Demand | DMD_P_s002_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ps2_kW
642 | 16 | 16-14 | 12332 | User Channel 2 Active Power Demand Predict | PRED_DMD_P_s002_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
643 | 16 | 16-15 | 12334 | User Channel 2 Max Active Power Demand | MAX_DMD_P_s002_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
644 | 16 | 16-16 | 12336 | User Channel 2 Max Active Power Demand Timestamp | MAX_DMDTS_P_002 |  | word | 12 | R | 3 | 1
645 | 16 | 16-17 | 12339 | User Channel 2 Reactive Power Demand | DMD_Q_s002_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Qs2_kvar
646 | 16 | 16-18 | 12341 | User Channel 2 Reactive Power Demand Predict | PRED_DMD_Q_s002_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
647 | 16 | 16-19 | 12343 | User Channel 2 Max Reactive Power Demand | MAX_DMD_Q_s002_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
648 | 16 | 16-20 | 12345 | User Channel 2 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_002 |  | word | 12 | R | 3 | 1
649 | 16 | 16-21 | 12348 | User Channel 2 Apparent Power Demand | DMD_S_s002_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ss2_kVA
650 | 16 | 16-22 | 12350 | User Channel 2 Apparent Power Demand Predict | PRED_DMD_S_s002_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
651 | 16 | 16-23 | 12352 | User Channel 2 Max Apparent Power Demand | MAX_DMD_S_s002_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
652 | 16 | 16-24 | 12354 | User Channel 2 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_002 |  | word | 12 | R | 3 | 1
653 | 16 | 16-25 | 12357 | User Channel 3 Active Power Demand | DMD_P_s003_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ps3_kW
654 | 16 | 16-26 | 12359 | User Channel 3 Active Power Demand Predict | PRED_DMD_P_s003_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
655 | 16 | 16-27 | 12361 | User Channel 3 Max Active Power Demand | MAX_DMD_P_s003_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
656 | 16 | 16-28 | 12363 | User Channel 3 Max Active Power Demand Timestamp | MAX_DMDTS_P_003 |  | word | 12 | R | 3 | 1
657 | 16 | 16-29 | 12366 | User Channel 3 Reactive Power Demand | DMD_Q_s003_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Qs3_kvar
658 | 16 | 16-30 | 12368 | User Channel 3 Reactive Power Demand Predict | PRED_DMD_Q_s003_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
659 | 16 | 16-31 | 12370 | User Channel 3 Max Reactive Power Demand | MAX_DMD_Q_s003_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
660 | 16 | 16-32 | 12372 | User Channel 3 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_003 |  | word | 12 | R | 3 | 1
661 | 16 | 16-33 | 12375 | User Channel 3 Apparent Power Demand | DMD_S_s003_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ss3_kVA
662 | 16 | 16-34 | 12377 | User Channel 3 Apparent Power Demand Predict | PRED_DMD_S_s003_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
663 | 16 | 16-35 | 12379 | User Channel 3 Max Apparent Power Demand | MAX_DMD_S_s003_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
664 | 16 | 16-36 | 12381 | User Channel 3 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_003 |  | word | 12 | R | 3 | 1
665 | 17 | 17-1 | 12384 | User Channel 4 Active Power Demand | DMD_P_s004_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ps4_kW
666 | 17 | 17-2 | 12386 | User Channel 4 Active Power Demand Predict | PRED_DMD_P_s004_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
667 | 17 | 17-3 | 12388 | User Channel 4 Max Active Power Demand | MAX_DMD_P_s004_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
668 | 17 | 17-4 | 12390 | User Channel 4 Max Active Power Demand Timestamp | MAX_DMDTS_P_004 |  | word | 12 | R | 3 | 1
669 | 17 | 17-5 | 12393 | User Channel 4 Reactive Power Demand | DMD_Q_s004_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Qs4_kvar
670 | 17 | 17-6 | 12395 | User Channel 4 Reactive Power Demand Predict | PRED_DMD_Q_s004_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
671 | 17 | 17-7 | 12397 | User Channel 4 Max Reactive Power Demand | MAX_DMD_Q_s004_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
672 | 17 | 17-8 | 12399 | User Channel 4 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_004 |  | word | 12 | R | 3 | 1
673 | 17 | 17-9 | 12402 | User Channel 4 Apparent Power Demand | DMD_S_s004_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ss4_kVA
674 | 17 | 17-10 | 12404 | User Channel 4 Apparent Power Demand Predict | PRED_DMD_S_s004_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
675 | 17 | 17-11 | 12406 | User Channel 4 Max Apparent Power Demand | MAX_DMD_S_s004_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
676 | 17 | 17-12 | 12408 | User Channel 4 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_004 |  | word | 12 | R | 3 | 1
677 | 17 | 17-13 | 12411 | User Channel 5 Active Power Demand | DMD_P_s005_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ps5_kW
678 | 17 | 17-14 | 12413 | User Channel 5 Active Power Demand Predict | PRED_DMD_P_s005_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
679 | 17 | 17-15 | 12415 | User Channel 5 Max Active Power Demand | MAX_DMD_P_s005_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
680 | 17 | 17-16 | 12417 | User Channel 5 Max Active Power Demand Timestamp | MAX_DMDTS_P_005 |  | word | 12 | R | 3 | 1
681 | 17 | 17-17 | 12420 | User Channel 5 Reactive Power Demand | DMD_Q_s005_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Qs5_kvar
682 | 17 | 17-18 | 12422 | User Channel 5 Reactive Power Demand Predict | PRED_DMD_Q_s005_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
683 | 17 | 17-19 | 12424 | User Channel 5 Max Reactive Power Demand | MAX_DMD_Q_s005_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
684 | 17 | 17-20 | 12426 | User Channel 5 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_005 |  | word | 12 | R | 3 | 1
685 | 17 | 17-21 | 12429 | User Channel 5 Apparent Power Demand | DMD_S_s005_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ss5_kVA
686 | 17 | 17-22 | 12431 | User Channel 5 Apparent Power Demand Predict | PRED_DMD_S_s005_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
687 | 17 | 17-23 | 12433 | User Channel 5 Max Apparent Power Demand | MAX_DMD_S_s005_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
688 | 17 | 17-24 | 12435 | User Channel 5 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_005 |  | word | 12 | R | 3 | 1
689 | 17 | 17-25 | 12438 | User Channel 6 Active Power Demand | DMD_P_s006_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ps6_kW
690 | 17 | 17-26 | 12440 | User Channel 6 Active Power Demand Predict | PRED_DMD_P_s006_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
691 | 17 | 17-27 | 12442 | User Channel 6 Max Active Power Demand | MAX_DMD_P_s006_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
692 | 17 | 17-28 | 12444 | User Channel 6 Max Active Power Demand Timestamp | MAX_DMDTS_P_006 |  | word | 12 | R | 3 | 1
693 | 17 | 17-29 | 12447 | User Channel 6 Reactive Power Demand | DMD_Q_s006_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Qs6_kvar
694 | 17 | 17-30 | 12449 | User Channel 6 Reactive Power Demand Predict | PRED_DMD_Q_s006_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
695 | 17 | 17-31 | 12451 | User Channel 6 Max Reactive Power Demand | MAX_DMD_Q_s006_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
696 | 17 | 17-32 | 12453 | User Channel 6 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_006 |  | word | 12 | R | 3 | 1
697 | 17 | 17-33 | 12456 | User Channel 6 Apparent Power Demand | DMD_S_s006_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand | DMD_Ss6_kVA
698 | 17 | 17-34 | 12458 | User Channel 6 Apparent Power Demand Predict | PRED_DMD_S_s006_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
699 | 17 | 17-35 | 12460 | User Channel 6 Max Apparent Power Demand | MAX_DMD_S_s006_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
700 | 17 | 17-36 | 12462 | User Channel 6 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_006 |  | word | 12 | R | 3 | 1
701 | 18 | 18-1 | 12465 | User Channel 7 Active Power Demand | DMD_P_s007_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
702 | 18 | 18-2 | 12467 | User Channel 7 Active Power Demand Predict | PRED_DMD_P_s007_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
703 | 18 | 18-3 | 12469 | User Channel 7 Max Active Power Demand | MAX_DMD_P_s007_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
704 | 18 | 18-4 | 12471 | User Channel 7 Max Active Power Demand Timestamp | MAX_DMDTS_P_007 |  | word | 12 | R | 3 | 1
705 | 18 | 18-5 | 12474 | User Channel 7 Reactive Power Demand | DMD_Q_s007_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
706 | 18 | 18-6 | 12476 | User Channel 7 Reactive Power Demand Predict | PRED_DMD_Q_s007_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
707 | 18 | 18-7 | 12478 | User Channel 7 Max Reactive Power Demand | MAX_DMD_Q_s007_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
708 | 18 | 18-8 | 12480 | User Channel 7 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_007 |  | word | 12 | R | 3 | 1
709 | 18 | 18-9 | 12483 | User Channel 7 Apparent Power Demand | DMD_S_s007_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
710 | 18 | 18-10 | 12485 | User Channel 7 Apparent Power Demand Predict | PRED_DMD_S_s007_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
711 | 18 | 18-11 | 12487 | User Channel 7 Max Apparent Power Demand | MAX_DMD_S_s007_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
712 | 18 | 18-12 | 12489 | User Channel 7 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_007 |  | word | 12 | R | 3 | 1
713 | 18 | 18-13 | 12492 | User Channel 8 Active Power Demand | DMD_P_s008_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
714 | 18 | 18-14 | 12494 | User Channel 8 Active Power Demand Predict | PRED_DMD_P_s008_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
715 | 18 | 18-15 | 12496 | User Channel 8 Max Active Power Demand | MAX_DMD_P_s008_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
716 | 18 | 18-16 | 12498 | User Channel 8 Max Active Power Demand Timestamp | MAX_DMDTS_P_008 |  | word | 12 | R | 3 | 1
717 | 18 | 18-17 | 12501 | User Channel 8 Reactive Power Demand | DMD_Q_s008_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
718 | 18 | 18-18 | 12503 | User Channel 8 Reactive Power Demand Predict | PRED_DMD_Q_s008_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
719 | 18 | 18-19 | 12505 | User Channel 8 Max Reactive Power Demand | MAX_DMD_Q_s008_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
720 | 18 | 18-20 | 12507 | User Channel 8 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_008 |  | word | 12 | R | 3 | 1
721 | 18 | 18-21 | 12510 | User Channel 8 Apparent Power Demand | DMD_S_s008_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
722 | 18 | 18-22 | 12512 | User Channel 8 Apparent Power Demand Predict | PRED_DMD_S_s008_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
723 | 18 | 18-23 | 12514 | User Channel 8 Max Apparent Power Demand | MAX_DMD_S_s008_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
724 | 18 | 18-24 | 12516 | User Channel 8 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_008 |  | word | 12 | R | 3 | 1
725 | 18 | 18-25 | 12519 | User Channel 9 Active Power Demand | DMD_P_s009_kW | kW | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
726 | 18 | 18-26 | 12521 | User Channel 9 Active Power Demand Predict | PRED_DMD_P_s009_kW | kW | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
727 | 18 | 18-27 | 12523 | User Channel 9 Max Active Power Demand | MAX_DMD_P_s009_kW | kW | float32 | 12 | R | 2 | 1 | [7 empty] | 13
728 | 18 | 18-28 | 12525 | User Channel 9 Max Active Power Demand Timestamp | MAX_DMDTS_P_009 |  | word | 12 | R | 3 | 1
729 | 18 | 18-29 | 12528 | User Channel 9 Reactive Power Demand | DMD_Q_s009_kvar | kvar | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
730 | 18 | 18-30 | 12530 | User Channel 9 Reactive Power Demand Predict | PRED_DMD_Q_s009_kvar | kvar | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
731 | 18 | 18-31 | 12532 | User Channel 9 Max Reactive Power Demand | MAX_DMD_Q_s009_kvar | kvar | float32 | 12 | R | 2 | 1 | [7 empty] | 13
732 | 18 | 18-32 | 12534 | User Channel 9 Max Reactive Power Demand Timestamp | MAX_DMDTS_Q_009 |  | word | 12 | R | 3 | 1
733 | 18 | 18-33 | 12537 | User Channel 9 Apparent Power Demand | DMD_S_s009_kVA | kVA | float32 | 12 | R | 2 | 1 |  | 1 | 2 |  | 4 |  | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
734 | 18 | 18-34 | 12539 | User Channel 9 Apparent Power Demand Predict | PRED_DMD_S_s009_kVA | kVA | float32 | 12 | R | 2 | 1 | [6 empty] | 15 | 13-20-21 | demand | demand | demand | demand | demand | demand | demand
735 | 18 | 18-35 | 12541 | User Channel 9 Max Apparent Power Demand | MAX_DMD_S_s009_kVA | kVA | float32 | 12 | R | 2 | 1 | [7 empty] | 13
736 | 18 | 18-36 | 12543 | User Channel 9 Max Apparent Power Demand Timestamp | MAX_DMDTS_S_009 |  | word | 12 | R | 3 | 1
737 | 19 | 19-1 | 12800 | Voltage Unbalance Factor | UNBL_V_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 19 | 10-20-21 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | Unbl_V
738 | 19 | 19-2 | 12801 | Phase A Voltage THD | THD_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD | THD_Va
739 | 19 | 19-3 | 12802 | Phase B Voltage THD | THD_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD | THD_Vb
740 | 19 | 19-4 | 12803 | Phase C Voltage THD | THD_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD | THD_Vc
741 | 19 | 19-5 | 12804 | Average Voltage THD | THD_V_avg_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD
742 | 19 | 19-6 | 12805 | Phase A Voltage 2-th Harmonic | HAR2_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
743 | 19 | 19-7 | 12806 | Phase A Voltage 3-th Harmonic | HAR3_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
744 | 19 | 19-8 | 12807 | Phase A Voltage 4-th Harmonic | HAR4_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
745 | 19 | 19-9 | 12808 | Phase A Voltage 5-th Harmonic | HAR5_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
746 | 19 | 19-10 | 12809 | Phase A Voltage 6-th Harmonic | HAR6_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
747 | 19 | 19-11 | 12810 | Phase A Voltage 7-th Harmonic | HAR7_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
748 | 19 | 19-12 | 12811 | Phase A Voltage 8-th Harmonic | HAR8_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
749 | 19 | 19-13 | 12812 | Phase A Voltage 9-th Harmonic | HAR9_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
750 | 19 | 19-14 | 12813 | Phase A Voltage 10-th Harmonic | HAR10_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
751 | 19 | 19-15 | 12814 | Phase A Voltage 11-th Harmonic | HAR11_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
752 | 19 | 19-16 | 12815 | Phase A Voltage 12-th Harmonic | HAR12_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
753 | 19 | 19-17 | 12816 | Phase A Voltage 13-th Harmonic | HAR13_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
754 | 19 | 19-18 | 12817 | Phase A Voltage 14-th Harmonic | HAR14_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
755 | 19 | 19-19 | 12818 | Phase A Voltage 15-th Harmonic | HAR15_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
756 | 19 | 19-20 | 12819 | Phase A Voltage 16-th Harmonic | HAR16_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
757 | 19 | 19-21 | 12820 | Phase A Voltage 17-th Harmonic | HAR17_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
758 | 19 | 19-22 | 12821 | Phase A Voltage 18-th Harmonic | HAR18_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
759 | 19 | 19-23 | 12822 | Phase A Voltage 19-th Harmonic | HAR19_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
760 | 19 | 19-24 | 12823 | Phase A Voltage 20-th Harmonic | HAR20_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
761 | 19 | 19-25 | 12824 | Phase A Voltage 21-th Harmonic | HAR21_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
762 | 19 | 19-26 | 12825 | Phase A Voltage 22-th Harmonic | HAR22_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
763 | 19 | 19-27 | 12826 | Phase A Voltage 23-th Harmonic | HAR23_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
764 | 19 | 19-28 | 12827 | Phase A Voltage 24-th Harmonic | HAR24_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
765 | 19 | 19-29 | 12828 | Phase A Voltage 25-th Harmonic | HAR25_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
766 | 19 | 19-30 | 12829 | Phase A Voltage 26-th Harmonic | HAR26_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
767 | 19 | 19-31 | 12830 | Phase A Voltage 27-th Harmonic | HAR27_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
768 | 19 | 19-32 | 12831 | Phase A Voltage 28-th Harmonic | HAR28_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
769 | 19 | 19-33 | 12832 | Phase A Voltage 29-th Harmonic | HAR29_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
770 | 19 | 19-34 | 12833 | Phase A Voltage 30-th Harmonic | HAR30_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
771 | 19 | 19-35 | 12834 | Phase A Voltage 31-th Harmonic | HAR31_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
772 | 19 | 19-36 | 12835 | Phase B Voltage 2-th Harmonic | HAR2_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
773 | 19 | 19-37 | 12836 | Phase B Voltage 3-th Harmonic | HAR3_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
774 | 19 | 19-38 | 12837 | Phase B Voltage 4-th Harmonic | HAR4_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
775 | 19 | 19-39 | 12838 | Phase B Voltage 5-th Harmonic | HAR5_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
776 | 19 | 19-40 | 12839 | Phase B Voltage 6-th Harmonic | HAR6_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
777 | 19 | 19-41 | 12840 | Phase B Voltage 7-th Harmonic | HAR7_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
778 | 19 | 19-42 | 12841 | Phase B Voltage 8-th Harmonic | HAR8_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
779 | 19 | 19-43 | 12842 | Phase B Voltage 9-th Harmonic | HAR9_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
780 | 19 | 19-44 | 12843 | Phase B Voltage 10-th Harmonic | HAR10_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
781 | 19 | 19-45 | 12844 | Phase B Voltage 11-th Harmonic | HAR11_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
782 | 19 | 19-46 | 12845 | Phase B Voltage 12-th Harmonic | HAR12_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
783 | 19 | 19-47 | 12846 | Phase B Voltage 13-th Harmonic | HAR13_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
784 | 19 | 19-48 | 12847 | Phase B Voltage 14-th Harmonic | HAR14_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
785 | 19 | 19-49 | 12848 | Phase B Voltage 15-th Harmonic | HAR15_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
786 | 19 | 19-50 | 12849 | Phase B Voltage 16-th Harmonic | HAR16_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
787 | 19 | 19-51 | 12850 | Phase B Voltage 17-th Harmonic | HAR17_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
788 | 19 | 19-52 | 12851 | Phase B Voltage 18-th Harmonic | HAR18_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
789 | 19 | 19-53 | 12852 | Phase B Voltage 19-th Harmonic | HAR19_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
790 | 19 | 19-54 | 12853 | Phase B Voltage 20-th Harmonic | HAR20_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
791 | 19 | 19-55 | 12854 | Phase B Voltage 21-th Harmonic | HAR21_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
792 | 19 | 19-56 | 12855 | Phase B Voltage 22-th Harmonic | HAR22_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
793 | 19 | 19-57 | 12856 | Phase B Voltage 23-th Harmonic | HAR23_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
794 | 19 | 19-58 | 12857 | Phase B Voltage 24-th Harmonic | HAR24_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
795 | 19 | 19-59 | 12858 | Phase B Voltage 25-th Harmonic | HAR25_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
796 | 19 | 19-60 | 12859 | Phase B Voltage 26-th Harmonic | HAR26_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
797 | 19 | 19-61 | 12860 | Phase B Voltage 27-th Harmonic | HAR27_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
798 | 19 | 19-62 | 12861 | Phase B Voltage 28-th Harmonic | HAR28_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
799 | 19 | 19-63 | 12862 | Phase B Voltage 29-th Harmonic | HAR29_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
800 | 19 | 19-64 | 12863 | Phase B Voltage 30-th Harmonic | HAR30_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
801 | 19 | 19-65 | 12864 | Phase B Voltage 31-th Harmonic | HAR31_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
802 | 19 | 19-66 | 12865 | Phase C Voltage 2-th Harmonic | HAR2_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
803 | 19 | 19-67 | 12866 | Phase C Voltage 3-th Harmonic | HAR3_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
804 | 19 | 19-68 | 12867 | Phase C Voltage 4-th Harmonic | HAR4_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
805 | 19 | 19-69 | 12868 | Phase C Voltage 5-th Harmonic | HAR5_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
806 | 19 | 19-70 | 12869 | Phase C Voltage 6-th Harmonic | HAR6_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
807 | 19 | 19-71 | 12870 | Phase C Voltage 7-th Harmonic | HAR7_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
808 | 19 | 19-72 | 12871 | Phase C Voltage 8-th Harmonic | HAR8_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
809 | 19 | 19-73 | 12872 | Phase C Voltage 9-th Harmonic | HAR9_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
810 | 19 | 19-74 | 12873 | Phase C Voltage 10-th Harmonic | HAR10_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
811 | 19 | 19-75 | 12874 | Phase C Voltage 11-th Harmonic | HAR11_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
812 | 19 | 19-76 | 12875 | Phase C Voltage 12-th Harmonic | HAR12_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
813 | 19 | 19-77 | 12876 | Phase C Voltage 13-th Harmonic | HAR13_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
814 | 19 | 19-78 | 12877 | Phase C Voltage 14-th Harmonic | HAR14_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
815 | 19 | 19-79 | 12878 | Phase C Voltage 15-th Harmonic | HAR15_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
816 | 19 | 19-80 | 12879 | Phase C Voltage 16-th Harmonic | HAR16_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
817 | 19 | 19-81 | 12880 | Phase C Voltage 17-th Harmonic | HAR17_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
818 | 19 | 19-82 | 12881 | Phase C Voltage 18-th Harmonic | HAR18_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
819 | 19 | 19-83 | 12882 | Phase C Voltage 19-th Harmonic | HAR19_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
820 | 19 | 19-84 | 12883 | Phase C Voltage 20-th Harmonic | HAR20_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
821 | 19 | 19-85 | 12884 | Phase C Voltage 21-th Harmonic | HAR21_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
822 | 19 | 19-86 | 12885 | Phase C Voltage 22-th Harmonic | HAR22_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
823 | 19 | 19-87 | 12886 | Phase C Voltage 23-th Harmonic | HAR23_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
824 | 19 | 19-88 | 12887 | Phase C Voltage 24-th Harmonic | HAR24_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
825 | 19 | 19-89 | 12888 | Phase C Voltage 25-th Harmonic | HAR25_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
826 | 19 | 19-90 | 12889 | Phase C Voltage 26-th Harmonic | HAR26_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
827 | 19 | 19-91 | 12890 | Phase C Voltage 27-th Harmonic | HAR27_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
828 | 19 | 19-92 | 12891 | Phase C Voltage 28-th Harmonic | HAR28_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
829 | 19 | 19-93 | 12892 | Phase C Voltage 29-th Harmonic | HAR29_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
830 | 19 | 19-94 | 12893 | Phase C Voltage 30-th Harmonic | HAR30_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
831 | 19 | 19-95 | 12894 | Phase C Voltage 31-th Harmonic | HAR31_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
832 | 19 | 19-96 | 12895 | Current Unbalance Factor | UNBL_I_% | % | int16 | 12 | R | 1 | 100 | [6 empty] | 19 | 10-20-21 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | Unbl_I
833 | 19 | 19-97 | 12896 | Phase A Voltage Odd THD | OTHD_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD | OTHD_Va
834 | 19 | 19-98 | 12897 | Phase A Voltage Even THD | ETHD_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD
835 | 19 | 19-99 | 12898 | Phase A Voltage Crest Factor | CF_V_a_% | % | int16 | 12 | R | 1 | 0.001 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD | CF_Va
836 | 19 | 19-100 | 12899 | Phase A Voltage Telephone Harmonic Form Factor | THFF_V_a_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD
837 | 19 | 19-101 | 12900 | Phase B Voltage Odd THD | OTHD_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD | OTHD_Vb
838 | 19 | 19-102 | 12901 | Phase B Voltage Even THD | ETHD_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD
839 | 19 | 19-103 | 12902 | Phase B Voltage Crest Factor | CF_V_b_% | % | int16 | 12 | R | 1 | 0.001 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD | CF_Vb
840 | 19 | 19-104 | 12903 | Phase B Voltage Telephone Harmonic Form Factor | THFF_V_b_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD
841 | 19 | 19-105 | 12904 | Phase C Voltage Odd THD | OTHD_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD | OTHD_Vc
842 | 19 | 19-106 | 12905 | Phase C Voltage Even THD | ETHD_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD
843 | 19 | 19-107 | 12906 | Phase C Voltage Crest Factor | CF_V_c_% | % | int16 | 12 | R | 1 | 0.001 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD | CF_Vc
844 | 19 | 19-108 | 12907 | Phase C Voltage Telephone Harmonic Form Factor | THFF_V_c_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 10-20-21 | THD | THD | THD | THD | THD | THD | THD
845 | 20 | 20-1 | 12960 | Input Channel 1 Current Odd THD | OTHD_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
846 | 20 | 20-2 | 12961 | Input Channel 1 Current Even THD | ETHD_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
847 | 20 | 20-3 | 12962 | Input Channel 1 Current K Factor | KF_I_001_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
848 | 20 | 20-4 | 12963 | Input Channel 2 Current Odd THD | OTHD_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
849 | 20 | 20-5 | 12964 | Input Channel 2 Current Even THD | ETHD_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
850 | 20 | 20-6 | 12965 | Input Channel 2 Current K Factor | KF_I_002_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
851 | 20 | 20-7 | 12966 | Input Channel 3 Current Odd THD | OTHD_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
852 | 20 | 20-8 | 12967 | Input Channel 3 Current Even THD | ETHD_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
853 | 20 | 20-9 | 12968 | Input Channel 3 Current K Factor | KF_I_003_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
854 | 20 | 20-10 | 12969 | Input Channel 4 Current Odd THD | OTHD_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
855 | 20 | 20-11 | 12970 | Input Channel 4 Current Even THD | ETHD_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
856 | 20 | 20-12 | 12971 | Input Channel 4 Current K Factor | KF_I_004_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
857 | 20 | 20-13 | 12972 | Input Channel 5 Current Odd THD | OTHD_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
858 | 20 | 20-14 | 12973 | Input Channel 5 Current Even THD | ETHD_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
859 | 20 | 20-15 | 12974 | Input Channel 5 Current K Factor | KF_I_005_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
860 | 20 | 20-16 | 12975 | Input Channel 6 Current Odd THD | OTHD_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
861 | 20 | 20-17 | 12976 | Input Channel 6 Current Even THD | ETHD_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
862 | 20 | 20-18 | 12977 | Input Channel 6 Current K Factor | KF_I_006_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
863 | 20 | 20-19 | 12978 | Input Channel 7 Current Odd THD | OTHD_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
864 | 20 | 20-20 | 12979 | Input Channel 7 Current Even THD | ETHD_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
865 | 20 | 20-21 | 12980 | Input Channel 7 Current K Factor | KF_I_007_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
866 | 20 | 20-22 | 12981 | Input Channel 8 Current Odd THD | OTHD_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
867 | 20 | 20-23 | 12982 | Input Channel 8 Current Even THD | ETHD_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
868 | 20 | 20-24 | 12983 | Input Channel 8 Current K Factor | KF_I_008_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
869 | 20 | 20-25 | 12984 | Input Channel 9 Current Odd THD | OTHD_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
870 | 20 | 20-26 | 12985 | Input Channel 9 Current Even THD | ETHD_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
871 | 20 | 20-27 | 12986 | Input Channel 9 Current K Factor | KF_I_009_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
872 | 20 | 20-28 | 12987 | Input Channel 10 Current Odd THD | OTHD_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
873 | 20 | 20-29 | 12988 | Input Channel 10 Current Even THD | ETHD_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
874 | 20 | 20-30 | 12989 | Input Channel 10 Current K Factor | KF_I_010_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
875 | 20 | 20-31 | 12990 | Input Channel 11 Current Odd THD | OTHD_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
876 | 20 | 20-32 | 12991 | Input Channel 11 Current Even THD | ETHD_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
877 | 20 | 20-33 | 12992 | Input Channel 11 Current K Factor | KF_I_011_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
878 | 20 | 20-34 | 12993 | Input Channel 12 Current Odd THD | OTHD_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
879 | 20 | 20-35 | 12994 | Input Channel 12 Current Even THD | ETHD_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
880 | 20 | 20-36 | 12995 | Input Channel 12 Current K Factor | KF_I_012_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
881 | 20 | 20-37 | 12996 | Input Channel 13 Current Odd THD | OTHD_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
882 | 20 | 20-38 | 12997 | Input Channel 13 Current Even THD | ETHD_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
883 | 20 | 20-39 | 12998 | Input Channel 13 Current K Factor | KF_I_013_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
884 | 20 | 20-40 | 12999 | Input Channel 14 Current Odd THD | OTHD_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
885 | 20 | 20-41 | 13000 | Input Channel 14 Current Even THD | ETHD_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
886 | 20 | 20-42 | 13001 | Input Channel 14 Current K Factor | KF_I_014_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
887 | 20 | 20-43 | 13002 | Input Channel 15 Current Odd THD | OTHD_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
888 | 20 | 20-44 | 13003 | Input Channel 15 Current Even THD | ETHD_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
889 | 20 | 20-45 | 13004 | Input Channel 15 Current K Factor | KF_I_015_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
890 | 20 | 20-46 | 13005 | Input Channel 16 Current Odd THD | OTHD_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
891 | 20 | 20-47 | 13006 | Input Channel 16 Current Even THD | ETHD_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
892 | 20 | 20-48 | 13007 | Input Channel 16 Current K Factor | KF_I_016_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
893 | 20 | 20-49 | 13008 | Input Channel 17 Current Odd THD | OTHD_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
894 | 20 | 20-50 | 13009 | Input Channel 17 Current Even THD | ETHD_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
895 | 20 | 20-51 | 13010 | Input Channel 17 Current K Factor | KF_I_017_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
896 | 20 | 20-52 | 13011 | Input Channel 18 Current Odd THD | OTHD_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
897 | 20 | 20-53 | 13012 | Input Channel 18 Current Even THD | ETHD_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
898 | 20 | 20-54 | 13013 | Input Channel 18 Current K Factor | KF_I_018_% | % | int16 | 12 | R | 1 | 0.1 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
899 | 21 | 21-1 | 13056 | Input Channel 1 Current THD | THD_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
900 | 21 | 21-2 | 13057 | Input Channel 1 Current 2-th Harmonic | HAR2_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
901 | 21 | 21-3 | 13058 | Input Channel 1 Current 3-th Harmonic | HAR3_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
902 | 21 | 21-4 | 13059 | Input Channel 1 Current 4-th Harmonic | HAR4_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
903 | 21 | 21-5 | 13060 | Input Channel 1 Current 5-th Harmonic | HAR5_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
904 | 21 | 21-6 | 13061 | Input Channel 1 Current 6-th Harmonic | HAR6_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
905 | 21 | 21-7 | 13062 | Input Channel 1 Current 7-th Harmonic | HAR7_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
906 | 21 | 21-8 | 13063 | Input Channel 1 Current 8-th Harmonic | HAR8_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
907 | 21 | 21-9 | 13064 | Input Channel 1 Current 9-th Harmonic | HAR9_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
908 | 21 | 21-10 | 13065 | Input Channel 1 Current 10-th Harmonic | HAR10_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
909 | 21 | 21-11 | 13066 | Input Channel 1 Current 11-th Harmonic | HAR11_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
910 | 21 | 21-12 | 13067 | Input Channel 1 Current 12-th Harmonic | HAR12_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
911 | 21 | 21-13 | 13068 | Input Channel 1 Current 13-th Harmonic | HAR13_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
912 | 21 | 21-14 | 13069 | Input Channel 1 Current 14-th Harmonic | HAR14_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
913 | 21 | 21-15 | 13070 | Input Channel 1 Current 15-th Harmonic | HAR15_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
914 | 21 | 21-16 | 13071 | Input Channel 1 Current 16-th Harmonic | HAR16_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
915 | 21 | 21-17 | 13072 | Input Channel 1 Current 17-th Harmonic | HAR17_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
916 | 21 | 21-18 | 13073 | Input Channel 1 Current 18-th Harmonic | HAR18_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
917 | 21 | 21-19 | 13074 | Input Channel 1 Current 19-th Harmonic | HAR19_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
918 | 21 | 21-20 | 13075 | Input Channel 1 Current 20-th Harmonic | HAR20_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
919 | 21 | 21-21 | 13076 | Input Channel 1 Current 21-th Harmonic | HAR21_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
920 | 21 | 21-22 | 13077 | Input Channel 1 Current 22-th Harmonic | HAR22_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
921 | 21 | 21-23 | 13078 | Input Channel 1 Current 23-th Harmonic | HAR23_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
922 | 21 | 21-24 | 13079 | Input Channel 1 Current 24-th Harmonic | HAR24_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
923 | 21 | 21-25 | 13080 | Input Channel 1 Current 25-th Harmonic | HAR25_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
924 | 21 | 21-26 | 13081 | Input Channel 1 Current 26-th Harmonic | HAR26_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
925 | 21 | 21-27 | 13082 | Input Channel 1 Current 27-th Harmonic | HAR27_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
926 | 21 | 21-28 | 13083 | Input Channel 1 Current 28-th Harmonic | HAR28_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
927 | 21 | 21-29 | 13084 | Input Channel 1 Current 29-th Harmonic | HAR29_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
928 | 21 | 21-30 | 13085 | Input Channel 1 Current 30-th Harmonic | HAR30_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
929 | 21 | 21-31 | 13086 | Input Channel 1 Current 31-th Harmonic | HAR31_I_001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
930 | 21 | 21-32 | 13087 | Input Channel 2 Current THD | THD_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
931 | 21 | 21-33 | 13088 | Input Channel 2 Current 2-th Harmonic | HAR2_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
932 | 21 | 21-34 | 13089 | Input Channel 2 Current 3-th Harmonic | HAR3_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
933 | 21 | 21-35 | 13090 | Input Channel 2 Current 4-th Harmonic | HAR4_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
934 | 21 | 21-36 | 13091 | Input Channel 2 Current 5-th Harmonic | HAR5_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
935 | 21 | 21-37 | 13092 | Input Channel 2 Current 6-th Harmonic | HAR6_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
936 | 21 | 21-38 | 13093 | Input Channel 2 Current 7-th Harmonic | HAR7_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
937 | 21 | 21-39 | 13094 | Input Channel 2 Current 8-th Harmonic | HAR8_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
938 | 21 | 21-40 | 13095 | Input Channel 2 Current 9-th Harmonic | HAR9_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
939 | 21 | 21-41 | 13096 | Input Channel 2 Current 10-th Harmonic | HAR10_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
940 | 21 | 21-42 | 13097 | Input Channel 2 Current 11-th Harmonic | HAR11_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
941 | 21 | 21-43 | 13098 | Input Channel 2 Current 12-th Harmonic | HAR12_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
942 | 21 | 21-44 | 13099 | Input Channel 2 Current 13-th Harmonic | HAR13_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
943 | 21 | 21-45 | 13100 | Input Channel 2 Current 14-th Harmonic | HAR14_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
944 | 21 | 21-46 | 13101 | Input Channel 2 Current 15-th Harmonic | HAR15_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
945 | 21 | 21-47 | 13102 | Input Channel 2 Current 16-th Harmonic | HAR16_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
946 | 21 | 21-48 | 13103 | Input Channel 2 Current 17-th Harmonic | HAR17_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
947 | 21 | 21-49 | 13104 | Input Channel 2 Current 18-th Harmonic | HAR18_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
948 | 21 | 21-50 | 13105 | Input Channel 2 Current 19-th Harmonic | HAR19_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
949 | 21 | 21-51 | 13106 | Input Channel 2 Current 20-th Harmonic | HAR20_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
950 | 21 | 21-52 | 13107 | Input Channel 2 Current 21-th Harmonic | HAR21_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
951 | 21 | 21-53 | 13108 | Input Channel 2 Current 22-th Harmonic | HAR22_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
952 | 21 | 21-54 | 13109 | Input Channel 2 Current 23-th Harmonic | HAR23_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
953 | 21 | 21-55 | 13110 | Input Channel 2 Current 24-th Harmonic | HAR24_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
954 | 21 | 21-56 | 13111 | Input Channel 2 Current 25-th Harmonic | HAR25_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
955 | 21 | 21-57 | 13112 | Input Channel 2 Current 26-th Harmonic | HAR26_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
956 | 21 | 21-58 | 13113 | Input Channel 2 Current 27-th Harmonic | HAR27_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
957 | 21 | 21-59 | 13114 | Input Channel 2 Current 28-th Harmonic | HAR28_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
958 | 21 | 21-60 | 13115 | Input Channel 2 Current 29-th Harmonic | HAR29_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
959 | 21 | 21-61 | 13116 | Input Channel 2 Current 30-th Harmonic | HAR30_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
960 | 21 | 21-62 | 13117 | Input Channel 2 Current 31-th Harmonic | HAR31_I_002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
961 | 21 | 21-63 | 13118 | Input Channel 3 Current THD | THD_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
962 | 21 | 21-64 | 13119 | Input Channel 3 Current 2-th Harmonic | HAR2_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
963 | 21 | 21-65 | 13120 | Input Channel 3 Current 3-th Harmonic | HAR3_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
964 | 21 | 21-66 | 13121 | Input Channel 3 Current 4-th Harmonic | HAR4_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
965 | 21 | 21-67 | 13122 | Input Channel 3 Current 5-th Harmonic | HAR5_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
966 | 21 | 21-68 | 13123 | Input Channel 3 Current 6-th Harmonic | HAR6_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
967 | 21 | 21-69 | 13124 | Input Channel 3 Current 7-th Harmonic | HAR7_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
968 | 21 | 21-70 | 13125 | Input Channel 3 Current 8-th Harmonic | HAR8_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
969 | 21 | 21-71 | 13126 | Input Channel 3 Current 9-th Harmonic | HAR9_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
970 | 21 | 21-72 | 13127 | Input Channel 3 Current 10-th Harmonic | HAR10_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
971 | 21 | 21-73 | 13128 | Input Channel 3 Current 11-th Harmonic | HAR11_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
972 | 21 | 21-74 | 13129 | Input Channel 3 Current 12-th Harmonic | HAR12_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
973 | 21 | 21-75 | 13130 | Input Channel 3 Current 13-th Harmonic | HAR13_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
974 | 21 | 21-76 | 13131 | Input Channel 3 Current 14-th Harmonic | HAR14_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
975 | 21 | 21-77 | 13132 | Input Channel 3 Current 15-th Harmonic | HAR15_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
976 | 21 | 21-78 | 13133 | Input Channel 3 Current 16-th Harmonic | HAR16_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
977 | 21 | 21-79 | 13134 | Input Channel 3 Current 17-th Harmonic | HAR17_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
978 | 21 | 21-80 | 13135 | Input Channel 3 Current 18-th Harmonic | HAR18_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
979 | 21 | 21-81 | 13136 | Input Channel 3 Current 19-th Harmonic | HAR19_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
980 | 21 | 21-82 | 13137 | Input Channel 3 Current 20-th Harmonic | HAR20_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
981 | 21 | 21-83 | 13138 | Input Channel 3 Current 21-th Harmonic | HAR21_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
982 | 21 | 21-84 | 13139 | Input Channel 3 Current 22-th Harmonic | HAR22_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
983 | 21 | 21-85 | 13140 | Input Channel 3 Current 23-th Harmonic | HAR23_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
984 | 21 | 21-86 | 13141 | Input Channel 3 Current 24-th Harmonic | HAR24_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
985 | 21 | 21-87 | 13142 | Input Channel 3 Current 25-th Harmonic | HAR25_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
986 | 21 | 21-88 | 13143 | Input Channel 3 Current 26-th Harmonic | HAR26_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
987 | 21 | 21-89 | 13144 | Input Channel 3 Current 27-th Harmonic | HAR27_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
988 | 21 | 21-90 | 13145 | Input Channel 3 Current 28-th Harmonic | HAR28_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
989 | 21 | 21-91 | 13146 | Input Channel 3 Current 29-th Harmonic | HAR29_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
990 | 21 | 21-92 | 13147 | Input Channel 3 Current 30-th Harmonic | HAR30_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
991 | 21 | 21-93 | 13148 | Input Channel 3 Current 31-th Harmonic | HAR31_I_003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
992 | 22 | 22-1 | 13149 | Input Channel 4 Current THD | THD_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
993 | 22 | 22-2 | 13150 | Input Channel 4 Current 2-th Harmonic | HAR2_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
994 | 22 | 22-3 | 13151 | Input Channel 4 Current 3-th Harmonic | HAR3_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
995 | 22 | 22-4 | 13152 | Input Channel 4 Current 4-th Harmonic | HAR4_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
996 | 22 | 22-5 | 13153 | Input Channel 4 Current 5-th Harmonic | HAR5_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
997 | 22 | 22-6 | 13154 | Input Channel 4 Current 6-th Harmonic | HAR6_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
998 | 22 | 22-7 | 13155 | Input Channel 4 Current 7-th Harmonic | HAR7_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
999 | 22 | 22-8 | 13156 | Input Channel 4 Current 8-th Harmonic | HAR8_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1000 | 22 | 22-9 | 13157 | Input Channel 4 Current 9-th Harmonic | HAR9_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1001 | 22 | 22-10 | 13158 | Input Channel 4 Current 10-th Harmonic | HAR10_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1002 | 22 | 22-11 | 13159 | Input Channel 4 Current 11-th Harmonic | HAR11_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1003 | 22 | 22-12 | 13160 | Input Channel 4 Current 12-th Harmonic | HAR12_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1004 | 22 | 22-13 | 13161 | Input Channel 4 Current 13-th Harmonic | HAR13_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1005 | 22 | 22-14 | 13162 | Input Channel 4 Current 14-th Harmonic | HAR14_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1006 | 22 | 22-15 | 13163 | Input Channel 4 Current 15-th Harmonic | HAR15_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1007 | 22 | 22-16 | 13164 | Input Channel 4 Current 16-th Harmonic | HAR16_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1008 | 22 | 22-17 | 13165 | Input Channel 4 Current 17-th Harmonic | HAR17_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1009 | 22 | 22-18 | 13166 | Input Channel 4 Current 18-th Harmonic | HAR18_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1010 | 22 | 22-19 | 13167 | Input Channel 4 Current 19-th Harmonic | HAR19_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1011 | 22 | 22-20 | 13168 | Input Channel 4 Current 20-th Harmonic | HAR20_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1012 | 22 | 22-21 | 13169 | Input Channel 4 Current 21-th Harmonic | HAR21_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1013 | 22 | 22-22 | 13170 | Input Channel 4 Current 22-th Harmonic | HAR22_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1014 | 22 | 22-23 | 13171 | Input Channel 4 Current 23-th Harmonic | HAR23_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1015 | 22 | 22-24 | 13172 | Input Channel 4 Current 24-th Harmonic | HAR24_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1016 | 22 | 22-25 | 13173 | Input Channel 4 Current 25-th Harmonic | HAR25_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1017 | 22 | 22-26 | 13174 | Input Channel 4 Current 26-th Harmonic | HAR26_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1018 | 22 | 22-27 | 13175 | Input Channel 4 Current 27-th Harmonic | HAR27_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1019 | 22 | 22-28 | 13176 | Input Channel 4 Current 28-th Harmonic | HAR28_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1020 | 22 | 22-29 | 13177 | Input Channel 4 Current 29-th Harmonic | HAR29_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1021 | 22 | 22-30 | 13178 | Input Channel 4 Current 30-th Harmonic | HAR30_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1022 | 22 | 22-31 | 13179 | Input Channel 4 Current 31-th Harmonic | HAR31_I_004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1023 | 22 | 22-32 | 13180 | Input Channel 5 Current THD | THD_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1024 | 22 | 22-33 | 13181 | Input Channel 5 Current 2-th Harmonic | HAR2_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1025 | 22 | 22-34 | 13182 | Input Channel 5 Current 3-th Harmonic | HAR3_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1026 | 22 | 22-35 | 13183 | Input Channel 5 Current 4-th Harmonic | HAR4_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1027 | 22 | 22-36 | 13184 | Input Channel 5 Current 5-th Harmonic | HAR5_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1028 | 22 | 22-37 | 13185 | Input Channel 5 Current 6-th Harmonic | HAR6_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1029 | 22 | 22-38 | 13186 | Input Channel 5 Current 7-th Harmonic | HAR7_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1030 | 22 | 22-39 | 13187 | Input Channel 5 Current 8-th Harmonic | HAR8_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1031 | 22 | 22-40 | 13188 | Input Channel 5 Current 9-th Harmonic | HAR9_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1032 | 22 | 22-41 | 13189 | Input Channel 5 Current 10-th Harmonic | HAR10_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1033 | 22 | 22-42 | 13190 | Input Channel 5 Current 11-th Harmonic | HAR11_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1034 | 22 | 22-43 | 13191 | Input Channel 5 Current 12-th Harmonic | HAR12_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1035 | 22 | 22-44 | 13192 | Input Channel 5 Current 13-th Harmonic | HAR13_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1036 | 22 | 22-45 | 13193 | Input Channel 5 Current 14-th Harmonic | HAR14_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1037 | 22 | 22-46 | 13194 | Input Channel 5 Current 15-th Harmonic | HAR15_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1038 | 22 | 22-47 | 13195 | Input Channel 5 Current 16-th Harmonic | HAR16_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1039 | 22 | 22-48 | 13196 | Input Channel 5 Current 17-th Harmonic | HAR17_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1040 | 22 | 22-49 | 13197 | Input Channel 5 Current 18-th Harmonic | HAR18_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1041 | 22 | 22-50 | 13198 | Input Channel 5 Current 19-th Harmonic | HAR19_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1042 | 22 | 22-51 | 13199 | Input Channel 5 Current 20-th Harmonic | HAR20_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1043 | 22 | 22-52 | 13200 | Input Channel 5 Current 21-th Harmonic | HAR21_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1044 | 22 | 22-53 | 13201 | Input Channel 5 Current 22-th Harmonic | HAR22_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1045 | 22 | 22-54 | 13202 | Input Channel 5 Current 23-th Harmonic | HAR23_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1046 | 22 | 22-55 | 13203 | Input Channel 5 Current 24-th Harmonic | HAR24_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1047 | 22 | 22-56 | 13204 | Input Channel 5 Current 25-th Harmonic | HAR25_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1048 | 22 | 22-57 | 13205 | Input Channel 5 Current 26-th Harmonic | HAR26_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1049 | 22 | 22-58 | 13206 | Input Channel 5 Current 27-th Harmonic | HAR27_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1050 | 22 | 22-59 | 13207 | Input Channel 5 Current 28-th Harmonic | HAR28_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1051 | 22 | 22-60 | 13208 | Input Channel 5 Current 29-th Harmonic | HAR29_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1052 | 22 | 22-61 | 13209 | Input Channel 5 Current 30-th Harmonic | HAR30_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1053 | 22 | 22-62 | 13210 | Input Channel 5 Current 31-th Harmonic | HAR31_I_005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1054 | 22 | 22-63 | 13211 | Input Channel 6 Current THD | THD_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1055 | 22 | 22-64 | 13212 | Input Channel 6 Current 2-th Harmonic | HAR2_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1056 | 22 | 22-65 | 13213 | Input Channel 6 Current 3-th Harmonic | HAR3_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1057 | 22 | 22-66 | 13214 | Input Channel 6 Current 4-th Harmonic | HAR4_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1058 | 22 | 22-67 | 13215 | Input Channel 6 Current 5-th Harmonic | HAR5_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1059 | 22 | 22-68 | 13216 | Input Channel 6 Current 6-th Harmonic | HAR6_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1060 | 22 | 22-69 | 13217 | Input Channel 6 Current 7-th Harmonic | HAR7_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1061 | 22 | 22-70 | 13218 | Input Channel 6 Current 8-th Harmonic | HAR8_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1062 | 22 | 22-71 | 13219 | Input Channel 6 Current 9-th Harmonic | HAR9_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1063 | 22 | 22-72 | 13220 | Input Channel 6 Current 10-th Harmonic | HAR10_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1064 | 22 | 22-73 | 13221 | Input Channel 6 Current 11-th Harmonic | HAR11_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1065 | 22 | 22-74 | 13222 | Input Channel 6 Current 12-th Harmonic | HAR12_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1066 | 22 | 22-75 | 13223 | Input Channel 6 Current 13-th Harmonic | HAR13_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1067 | 22 | 22-76 | 13224 | Input Channel 6 Current 14-th Harmonic | HAR14_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1068 | 22 | 22-77 | 13225 | Input Channel 6 Current 15-th Harmonic | HAR15_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1069 | 22 | 22-78 | 13226 | Input Channel 6 Current 16-th Harmonic | HAR16_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1070 | 22 | 22-79 | 13227 | Input Channel 6 Current 17-th Harmonic | HAR17_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1071 | 22 | 22-80 | 13228 | Input Channel 6 Current 18-th Harmonic | HAR18_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1072 | 22 | 22-81 | 13229 | Input Channel 6 Current 19-th Harmonic | HAR19_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1073 | 22 | 22-82 | 13230 | Input Channel 6 Current 20-th Harmonic | HAR20_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1074 | 22 | 22-83 | 13231 | Input Channel 6 Current 21-th Harmonic | HAR21_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1075 | 22 | 22-84 | 13232 | Input Channel 6 Current 22-th Harmonic | HAR22_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1076 | 22 | 22-85 | 13233 | Input Channel 6 Current 23-th Harmonic | HAR23_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1077 | 22 | 22-86 | 13234 | Input Channel 6 Current 24-th Harmonic | HAR24_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1078 | 22 | 22-87 | 13235 | Input Channel 6 Current 25-th Harmonic | HAR25_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1079 | 22 | 22-88 | 13236 | Input Channel 6 Current 26-th Harmonic | HAR26_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1080 | 22 | 22-89 | 13237 | Input Channel 6 Current 27-th Harmonic | HAR27_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1081 | 22 | 22-90 | 13238 | Input Channel 6 Current 28-th Harmonic | HAR28_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1082 | 22 | 22-91 | 13239 | Input Channel 6 Current 29-th Harmonic | HAR29_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1083 | 22 | 22-92 | 13240 | Input Channel 6 Current 30-th Harmonic | HAR30_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1084 | 22 | 22-93 | 13241 | Input Channel 6 Current 31-th Harmonic | HAR31_I_006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1085 | 23 | 23-1 | 13242 | Input Channel 7 Current THD | THD_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1086 | 23 | 23-2 | 13243 | Input Channel 7 Current 2-th Harmonic | HAR2_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1087 | 23 | 23-3 | 13244 | Input Channel 7 Current 3-th Harmonic | HAR3_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1088 | 23 | 23-4 | 13245 | Input Channel 7 Current 4-th Harmonic | HAR4_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1089 | 23 | 23-5 | 13246 | Input Channel 7 Current 5-th Harmonic | HAR5_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1090 | 23 | 23-6 | 13247 | Input Channel 7 Current 6-th Harmonic | HAR6_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1091 | 23 | 23-7 | 13248 | Input Channel 7 Current 7-th Harmonic | HAR7_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1092 | 23 | 23-8 | 13249 | Input Channel 7 Current 8-th Harmonic | HAR8_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1093 | 23 | 23-9 | 13250 | Input Channel 7 Current 9-th Harmonic | HAR9_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1094 | 23 | 23-10 | 13251 | Input Channel 7 Current 10-th Harmonic | HAR10_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1095 | 23 | 23-11 | 13252 | Input Channel 7 Current 11-th Harmonic | HAR11_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1096 | 23 | 23-12 | 13253 | Input Channel 7 Current 12-th Harmonic | HAR12_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1097 | 23 | 23-13 | 13254 | Input Channel 7 Current 13-th Harmonic | HAR13_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1098 | 23 | 23-14 | 13255 | Input Channel 7 Current 14-th Harmonic | HAR14_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1099 | 23 | 23-15 | 13256 | Input Channel 7 Current 15-th Harmonic | HAR15_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1100 | 23 | 23-16 | 13257 | Input Channel 7 Current 16-th Harmonic | HAR16_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1101 | 23 | 23-17 | 13258 | Input Channel 7 Current 17-th Harmonic | HAR17_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1102 | 23 | 23-18 | 13259 | Input Channel 7 Current 18-th Harmonic | HAR18_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1103 | 23 | 23-19 | 13260 | Input Channel 7 Current 19-th Harmonic | HAR19_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1104 | 23 | 23-20 | 13261 | Input Channel 7 Current 20-th Harmonic | HAR20_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1105 | 23 | 23-21 | 13262 | Input Channel 7 Current 21-th Harmonic | HAR21_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1106 | 23 | 23-22 | 13263 | Input Channel 7 Current 22-th Harmonic | HAR22_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1107 | 23 | 23-23 | 13264 | Input Channel 7 Current 23-th Harmonic | HAR23_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1108 | 23 | 23-24 | 13265 | Input Channel 7 Current 24-th Harmonic | HAR24_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1109 | 23 | 23-25 | 13266 | Input Channel 7 Current 25-th Harmonic | HAR25_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1110 | 23 | 23-26 | 13267 | Input Channel 7 Current 26-th Harmonic | HAR26_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1111 | 23 | 23-27 | 13268 | Input Channel 7 Current 27-th Harmonic | HAR27_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1112 | 23 | 23-28 | 13269 | Input Channel 7 Current 28-th Harmonic | HAR28_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1113 | 23 | 23-29 | 13270 | Input Channel 7 Current 29-th Harmonic | HAR29_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1114 | 23 | 23-30 | 13271 | Input Channel 7 Current 30-th Harmonic | HAR30_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1115 | 23 | 23-31 | 13272 | Input Channel 7 Current 31-th Harmonic | HAR31_I_007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1116 | 23 | 23-32 | 13273 | Input Channel 8 Current THD | THD_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1117 | 23 | 23-33 | 13274 | Input Channel 8 Current 2-th Harmonic | HAR2_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1118 | 23 | 23-34 | 13275 | Input Channel 8 Current 3-th Harmonic | HAR3_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1119 | 23 | 23-35 | 13276 | Input Channel 8 Current 4-th Harmonic | HAR4_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1120 | 23 | 23-36 | 13277 | Input Channel 8 Current 5-th Harmonic | HAR5_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1121 | 23 | 23-37 | 13278 | Input Channel 8 Current 6-th Harmonic | HAR6_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1122 | 23 | 23-38 | 13279 | Input Channel 8 Current 7-th Harmonic | HAR7_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1123 | 23 | 23-39 | 13280 | Input Channel 8 Current 8-th Harmonic | HAR8_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1124 | 23 | 23-40 | 13281 | Input Channel 8 Current 9-th Harmonic | HAR9_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1125 | 23 | 23-41 | 13282 | Input Channel 8 Current 10-th Harmonic | HAR10_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1126 | 23 | 23-42 | 13283 | Input Channel 8 Current 11-th Harmonic | HAR11_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1127 | 23 | 23-43 | 13284 | Input Channel 8 Current 12-th Harmonic | HAR12_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1128 | 23 | 23-44 | 13285 | Input Channel 8 Current 13-th Harmonic | HAR13_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1129 | 23 | 23-45 | 13286 | Input Channel 8 Current 14-th Harmonic | HAR14_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1130 | 23 | 23-46 | 13287 | Input Channel 8 Current 15-th Harmonic | HAR15_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1131 | 23 | 23-47 | 13288 | Input Channel 8 Current 16-th Harmonic | HAR16_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1132 | 23 | 23-48 | 13289 | Input Channel 8 Current 17-th Harmonic | HAR17_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1133 | 23 | 23-49 | 13290 | Input Channel 8 Current 18-th Harmonic | HAR18_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1134 | 23 | 23-50 | 13291 | Input Channel 8 Current 19-th Harmonic | HAR19_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1135 | 23 | 23-51 | 13292 | Input Channel 8 Current 20-th Harmonic | HAR20_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1136 | 23 | 23-52 | 13293 | Input Channel 8 Current 21-th Harmonic | HAR21_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1137 | 23 | 23-53 | 13294 | Input Channel 8 Current 22-th Harmonic | HAR22_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1138 | 23 | 23-54 | 13295 | Input Channel 8 Current 23-th Harmonic | HAR23_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1139 | 23 | 23-55 | 13296 | Input Channel 8 Current 24-th Harmonic | HAR24_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1140 | 23 | 23-56 | 13297 | Input Channel 8 Current 25-th Harmonic | HAR25_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1141 | 23 | 23-57 | 13298 | Input Channel 8 Current 26-th Harmonic | HAR26_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1142 | 23 | 23-58 | 13299 | Input Channel 8 Current 27-th Harmonic | HAR27_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1143 | 23 | 23-59 | 13300 | Input Channel 8 Current 28-th Harmonic | HAR28_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1144 | 23 | 23-60 | 13301 | Input Channel 8 Current 29-th Harmonic | HAR29_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1145 | 23 | 23-61 | 13302 | Input Channel 8 Current 30-th Harmonic | HAR30_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1146 | 23 | 23-62 | 13303 | Input Channel 8 Current 31-th Harmonic | HAR31_I_008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1147 | 23 | 23-63 | 13304 | Input Channel 9 Current THD | THD_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1148 | 23 | 23-64 | 13305 | Input Channel 9 Current 2-th Harmonic | HAR2_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1149 | 23 | 23-65 | 13306 | Input Channel 9 Current 3-th Harmonic | HAR3_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1150 | 23 | 23-66 | 13307 | Input Channel 9 Current 4-th Harmonic | HAR4_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1151 | 23 | 23-67 | 13308 | Input Channel 9 Current 5-th Harmonic | HAR5_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1152 | 23 | 23-68 | 13309 | Input Channel 9 Current 6-th Harmonic | HAR6_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1153 | 23 | 23-69 | 13310 | Input Channel 9 Current 7-th Harmonic | HAR7_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1154 | 23 | 23-70 | 13311 | Input Channel 9 Current 8-th Harmonic | HAR8_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1155 | 23 | 23-71 | 13312 | Input Channel 9 Current 9-th Harmonic | HAR9_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1156 | 23 | 23-72 | 13313 | Input Channel 9 Current 10-th Harmonic | HAR10_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1157 | 23 | 23-73 | 13314 | Input Channel 9 Current 11-th Harmonic | HAR11_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1158 | 23 | 23-74 | 13315 | Input Channel 9 Current 12-th Harmonic | HAR12_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1159 | 23 | 23-75 | 13316 | Input Channel 9 Current 13-th Harmonic | HAR13_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1160 | 23 | 23-76 | 13317 | Input Channel 9 Current 14-th Harmonic | HAR14_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1161 | 23 | 23-77 | 13318 | Input Channel 9 Current 15-th Harmonic | HAR15_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1162 | 23 | 23-78 | 13319 | Input Channel 9 Current 16-th Harmonic | HAR16_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1163 | 23 | 23-79 | 13320 | Input Channel 9 Current 17-th Harmonic | HAR17_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1164 | 23 | 23-80 | 13321 | Input Channel 9 Current 18-th Harmonic | HAR18_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1165 | 23 | 23-81 | 13322 | Input Channel 9 Current 19-th Harmonic | HAR19_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1166 | 23 | 23-82 | 13323 | Input Channel 9 Current 20-th Harmonic | HAR20_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1167 | 23 | 23-83 | 13324 | Input Channel 9 Current 21-th Harmonic | HAR21_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1168 | 23 | 23-84 | 13325 | Input Channel 9 Current 22-th Harmonic | HAR22_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1169 | 23 | 23-85 | 13326 | Input Channel 9 Current 23-th Harmonic | HAR23_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1170 | 23 | 23-86 | 13327 | Input Channel 9 Current 24-th Harmonic | HAR24_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1171 | 23 | 23-87 | 13328 | Input Channel 9 Current 25-th Harmonic | HAR25_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1172 | 23 | 23-88 | 13329 | Input Channel 9 Current 26-th Harmonic | HAR26_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1173 | 23 | 23-89 | 13330 | Input Channel 9 Current 27-th Harmonic | HAR27_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1174 | 23 | 23-90 | 13331 | Input Channel 9 Current 28-th Harmonic | HAR28_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1175 | 23 | 23-91 | 13332 | Input Channel 9 Current 29-th Harmonic | HAR29_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1176 | 23 | 23-92 | 13333 | Input Channel 9 Current 30-th Harmonic | HAR30_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1177 | 23 | 23-93 | 13334 | Input Channel 9 Current 31-th Harmonic | HAR31_I_009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1178 | 24 | 24-1 | 13335 | Input Channel 10 Current THD | THD_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1179 | 24 | 24-2 | 13336 | Input Channel 10 Current 2-th Harmonic | HAR2_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1180 | 24 | 24-3 | 13337 | Input Channel 10 Current 3-th Harmonic | HAR3_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1181 | 24 | 24-4 | 13338 | Input Channel 10 Current 4-th Harmonic | HAR4_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1182 | 24 | 24-5 | 13339 | Input Channel 10 Current 5-th Harmonic | HAR5_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1183 | 24 | 24-6 | 13340 | Input Channel 10 Current 6-th Harmonic | HAR6_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1184 | 24 | 24-7 | 13341 | Input Channel 10 Current 7-th Harmonic | HAR7_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1185 | 24 | 24-8 | 13342 | Input Channel 10 Current 8-th Harmonic | HAR8_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1186 | 24 | 24-9 | 13343 | Input Channel 10 Current 9-th Harmonic | HAR9_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1187 | 24 | 24-10 | 13344 | Input Channel 10 Current 10-th Harmonic | HAR10_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1188 | 24 | 24-11 | 13345 | Input Channel 10 Current 11-th Harmonic | HAR11_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1189 | 24 | 24-12 | 13346 | Input Channel 10 Current 12-th Harmonic | HAR12_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1190 | 24 | 24-13 | 13347 | Input Channel 10 Current 13-th Harmonic | HAR13_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1191 | 24 | 24-14 | 13348 | Input Channel 10 Current 14-th Harmonic | HAR14_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1192 | 24 | 24-15 | 13349 | Input Channel 10 Current 15-th Harmonic | HAR15_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1193 | 24 | 24-16 | 13350 | Input Channel 10 Current 16-th Harmonic | HAR16_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1194 | 24 | 24-17 | 13351 | Input Channel 10 Current 17-th Harmonic | HAR17_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1195 | 24 | 24-18 | 13352 | Input Channel 10 Current 18-th Harmonic | HAR18_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1196 | 24 | 24-19 | 13353 | Input Channel 10 Current 19-th Harmonic | HAR19_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1197 | 24 | 24-20 | 13354 | Input Channel 10 Current 20-th Harmonic | HAR20_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1198 | 24 | 24-21 | 13355 | Input Channel 10 Current 21-th Harmonic | HAR21_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1199 | 24 | 24-22 | 13356 | Input Channel 10 Current 22-th Harmonic | HAR22_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1200 | 24 | 24-23 | 13357 | Input Channel 10 Current 23-th Harmonic | HAR23_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1201 | 24 | 24-24 | 13358 | Input Channel 10 Current 24-th Harmonic | HAR24_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1202 | 24 | 24-25 | 13359 | Input Channel 10 Current 25-th Harmonic | HAR25_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1203 | 24 | 24-26 | 13360 | Input Channel 10 Current 26-th Harmonic | HAR26_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1204 | 24 | 24-27 | 13361 | Input Channel 10 Current 27-th Harmonic | HAR27_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1205 | 24 | 24-28 | 13362 | Input Channel 10 Current 28-th Harmonic | HAR28_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1206 | 24 | 24-29 | 13363 | Input Channel 10 Current 29-th Harmonic | HAR29_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1207 | 24 | 24-30 | 13364 | Input Channel 10 Current 30-th Harmonic | HAR30_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1208 | 24 | 24-31 | 13365 | Input Channel 10 Current 31-th Harmonic | HAR31_I_010_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1209 | 24 | 24-32 | 13366 | Input Channel 11 Current THD | THD_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1210 | 24 | 24-33 | 13367 | Input Channel 11 Current 2-th Harmonic | HAR2_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1211 | 24 | 24-34 | 13368 | Input Channel 11 Current 3-th Harmonic | HAR3_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1212 | 24 | 24-35 | 13369 | Input Channel 11 Current 4-th Harmonic | HAR4_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1213 | 24 | 24-36 | 13370 | Input Channel 11 Current 5-th Harmonic | HAR5_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1214 | 24 | 24-37 | 13371 | Input Channel 11 Current 6-th Harmonic | HAR6_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1215 | 24 | 24-38 | 13372 | Input Channel 11 Current 7-th Harmonic | HAR7_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1216 | 24 | 24-39 | 13373 | Input Channel 11 Current 8-th Harmonic | HAR8_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1217 | 24 | 24-40 | 13374 | Input Channel 11 Current 9-th Harmonic | HAR9_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1218 | 24 | 24-41 | 13375 | Input Channel 11 Current 10-th Harmonic | HAR10_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1219 | 24 | 24-42 | 13376 | Input Channel 11 Current 11-th Harmonic | HAR11_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1220 | 24 | 24-43 | 13377 | Input Channel 11 Current 12-th Harmonic | HAR12_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1221 | 24 | 24-44 | 13378 | Input Channel 11 Current 13-th Harmonic | HAR13_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1222 | 24 | 24-45 | 13379 | Input Channel 11 Current 14-th Harmonic | HAR14_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1223 | 24 | 24-46 | 13380 | Input Channel 11 Current 15-th Harmonic | HAR15_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1224 | 24 | 24-47 | 13381 | Input Channel 11 Current 16-th Harmonic | HAR16_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1225 | 24 | 24-48 | 13382 | Input Channel 11 Current 17-th Harmonic | HAR17_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1226 | 24 | 24-49 | 13383 | Input Channel 11 Current 18-th Harmonic | HAR18_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1227 | 24 | 24-50 | 13384 | Input Channel 11 Current 19-th Harmonic | HAR19_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1228 | 24 | 24-51 | 13385 | Input Channel 11 Current 20-th Harmonic | HAR20_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1229 | 24 | 24-52 | 13386 | Input Channel 11 Current 21-th Harmonic | HAR21_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1230 | 24 | 24-53 | 13387 | Input Channel 11 Current 22-th Harmonic | HAR22_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1231 | 24 | 24-54 | 13388 | Input Channel 11 Current 23-th Harmonic | HAR23_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1232 | 24 | 24-55 | 13389 | Input Channel 11 Current 24-th Harmonic | HAR24_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1233 | 24 | 24-56 | 13390 | Input Channel 11 Current 25-th Harmonic | HAR25_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1234 | 24 | 24-57 | 13391 | Input Channel 11 Current 26-th Harmonic | HAR26_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1235 | 24 | 24-58 | 13392 | Input Channel 11 Current 27-th Harmonic | HAR27_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1236 | 24 | 24-59 | 13393 | Input Channel 11 Current 28-th Harmonic | HAR28_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1237 | 24 | 24-60 | 13394 | Input Channel 11 Current 29-th Harmonic | HAR29_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1238 | 24 | 24-61 | 13395 | Input Channel 11 Current 30-th Harmonic | HAR30_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1239 | 24 | 24-62 | 13396 | Input Channel 11 Current 31-th Harmonic | HAR31_I_011_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1240 | 24 | 24-63 | 13397 | Input Channel 12 Current THD | THD_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1241 | 24 | 24-64 | 13398 | Input Channel 12 Current 2-th Harmonic | HAR2_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1242 | 24 | 24-65 | 13399 | Input Channel 12 Current 3-th Harmonic | HAR3_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1243 | 24 | 24-66 | 13400 | Input Channel 12 Current 4-th Harmonic | HAR4_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1244 | 24 | 24-67 | 13401 | Input Channel 12 Current 5-th Harmonic | HAR5_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1245 | 24 | 24-68 | 13402 | Input Channel 12 Current 6-th Harmonic | HAR6_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1246 | 24 | 24-69 | 13403 | Input Channel 12 Current 7-th Harmonic | HAR7_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1247 | 24 | 24-70 | 13404 | Input Channel 12 Current 8-th Harmonic | HAR8_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1248 | 24 | 24-71 | 13405 | Input Channel 12 Current 9-th Harmonic | HAR9_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1249 | 24 | 24-72 | 13406 | Input Channel 12 Current 10-th Harmonic | HAR10_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1250 | 24 | 24-73 | 13407 | Input Channel 12 Current 11-th Harmonic | HAR11_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1251 | 24 | 24-74 | 13408 | Input Channel 12 Current 12-th Harmonic | HAR12_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1252 | 24 | 24-75 | 13409 | Input Channel 12 Current 13-th Harmonic | HAR13_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1253 | 24 | 24-76 | 13410 | Input Channel 12 Current 14-th Harmonic | HAR14_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1254 | 24 | 24-77 | 13411 | Input Channel 12 Current 15-th Harmonic | HAR15_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1255 | 24 | 24-78 | 13412 | Input Channel 12 Current 16-th Harmonic | HAR16_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1256 | 24 | 24-79 | 13413 | Input Channel 12 Current 17-th Harmonic | HAR17_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1257 | 24 | 24-80 | 13414 | Input Channel 12 Current 18-th Harmonic | HAR18_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1258 | 24 | 24-81 | 13415 | Input Channel 12 Current 19-th Harmonic | HAR19_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1259 | 24 | 24-82 | 13416 | Input Channel 12 Current 20-th Harmonic | HAR20_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1260 | 24 | 24-83 | 13417 | Input Channel 12 Current 21-th Harmonic | HAR21_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1261 | 24 | 24-84 | 13418 | Input Channel 12 Current 22-th Harmonic | HAR22_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1262 | 24 | 24-85 | 13419 | Input Channel 12 Current 23-th Harmonic | HAR23_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1263 | 24 | 24-86 | 13420 | Input Channel 12 Current 24-th Harmonic | HAR24_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1264 | 24 | 24-87 | 13421 | Input Channel 12 Current 25-th Harmonic | HAR25_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1265 | 24 | 24-88 | 13422 | Input Channel 12 Current 26-th Harmonic | HAR26_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1266 | 24 | 24-89 | 13423 | Input Channel 12 Current 27-th Harmonic | HAR27_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1267 | 24 | 24-90 | 13424 | Input Channel 12 Current 28-th Harmonic | HAR28_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1268 | 24 | 24-91 | 13425 | Input Channel 12 Current 29-th Harmonic | HAR29_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1269 | 24 | 24-92 | 13426 | Input Channel 12 Current 30-th Harmonic | HAR30_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1270 | 24 | 24-93 | 13427 | Input Channel 12 Current 31-th Harmonic | HAR31_I_012_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1271 | 25 | 25-1 | 13428 | Input Channel 13 Current THD | THD_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1272 | 25 | 25-2 | 13429 | Input Channel 13 Current 2-th Harmonic | HAR2_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1273 | 25 | 25-3 | 13430 | Input Channel 13 Current 3-th Harmonic | HAR3_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1274 | 25 | 25-4 | 13431 | Input Channel 13 Current 4-th Harmonic | HAR4_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1275 | 25 | 25-5 | 13432 | Input Channel 13 Current 5-th Harmonic | HAR5_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1276 | 25 | 25-6 | 13433 | Input Channel 13 Current 6-th Harmonic | HAR6_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1277 | 25 | 25-7 | 13434 | Input Channel 13 Current 7-th Harmonic | HAR7_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1278 | 25 | 25-8 | 13435 | Input Channel 13 Current 8-th Harmonic | HAR8_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1279 | 25 | 25-9 | 13436 | Input Channel 13 Current 9-th Harmonic | HAR9_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1280 | 25 | 25-10 | 13437 | Input Channel 13 Current 10-th Harmonic | HAR10_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1281 | 25 | 25-11 | 13438 | Input Channel 13 Current 11-th Harmonic | HAR11_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1282 | 25 | 25-12 | 13439 | Input Channel 13 Current 12-th Harmonic | HAR12_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1283 | 25 | 25-13 | 13440 | Input Channel 13 Current 13-th Harmonic | HAR13_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1284 | 25 | 25-14 | 13441 | Input Channel 13 Current 14-th Harmonic | HAR14_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1285 | 25 | 25-15 | 13442 | Input Channel 13 Current 15-th Harmonic | HAR15_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1286 | 25 | 25-16 | 13443 | Input Channel 13 Current 16-th Harmonic | HAR16_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1287 | 25 | 25-17 | 13444 | Input Channel 13 Current 17-th Harmonic | HAR17_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1288 | 25 | 25-18 | 13445 | Input Channel 13 Current 18-th Harmonic | HAR18_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1289 | 25 | 25-19 | 13446 | Input Channel 13 Current 19-th Harmonic | HAR19_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1290 | 25 | 25-20 | 13447 | Input Channel 13 Current 20-th Harmonic | HAR20_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1291 | 25 | 25-21 | 13448 | Input Channel 13 Current 21-th Harmonic | HAR21_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1292 | 25 | 25-22 | 13449 | Input Channel 13 Current 22-th Harmonic | HAR22_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1293 | 25 | 25-23 | 13450 | Input Channel 13 Current 23-th Harmonic | HAR23_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1294 | 25 | 25-24 | 13451 | Input Channel 13 Current 24-th Harmonic | HAR24_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1295 | 25 | 25-25 | 13452 | Input Channel 13 Current 25-th Harmonic | HAR25_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1296 | 25 | 25-26 | 13453 | Input Channel 13 Current 26-th Harmonic | HAR26_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1297 | 25 | 25-27 | 13454 | Input Channel 13 Current 27-th Harmonic | HAR27_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1298 | 25 | 25-28 | 13455 | Input Channel 13 Current 28-th Harmonic | HAR28_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1299 | 25 | 25-29 | 13456 | Input Channel 13 Current 29-th Harmonic | HAR29_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1300 | 25 | 25-30 | 13457 | Input Channel 13 Current 30-th Harmonic | HAR30_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1301 | 25 | 25-31 | 13458 | Input Channel 13 Current 31-th Harmonic | HAR31_I_013_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1302 | 25 | 25-32 | 13459 | Input Channel 14 Current THD | THD_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1303 | 25 | 25-33 | 13460 | Input Channel 14 Current 2-th Harmonic | HAR2_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1304 | 25 | 25-34 | 13461 | Input Channel 14 Current 3-th Harmonic | HAR3_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1305 | 25 | 25-35 | 13462 | Input Channel 14 Current 4-th Harmonic | HAR4_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1306 | 25 | 25-36 | 13463 | Input Channel 14 Current 5-th Harmonic | HAR5_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1307 | 25 | 25-37 | 13464 | Input Channel 14 Current 6-th Harmonic | HAR6_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1308 | 25 | 25-38 | 13465 | Input Channel 14 Current 7-th Harmonic | HAR7_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1309 | 25 | 25-39 | 13466 | Input Channel 14 Current 8-th Harmonic | HAR8_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1310 | 25 | 25-40 | 13467 | Input Channel 14 Current 9-th Harmonic | HAR9_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1311 | 25 | 25-41 | 13468 | Input Channel 14 Current 10-th Harmonic | HAR10_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1312 | 25 | 25-42 | 13469 | Input Channel 14 Current 11-th Harmonic | HAR11_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1313 | 25 | 25-43 | 13470 | Input Channel 14 Current 12-th Harmonic | HAR12_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1314 | 25 | 25-44 | 13471 | Input Channel 14 Current 13-th Harmonic | HAR13_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1315 | 25 | 25-45 | 13472 | Input Channel 14 Current 14-th Harmonic | HAR14_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1316 | 25 | 25-46 | 13473 | Input Channel 14 Current 15-th Harmonic | HAR15_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1317 | 25 | 25-47 | 13474 | Input Channel 14 Current 16-th Harmonic | HAR16_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1318 | 25 | 25-48 | 13475 | Input Channel 14 Current 17-th Harmonic | HAR17_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1319 | 25 | 25-49 | 13476 | Input Channel 14 Current 18-th Harmonic | HAR18_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1320 | 25 | 25-50 | 13477 | Input Channel 14 Current 19-th Harmonic | HAR19_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1321 | 25 | 25-51 | 13478 | Input Channel 14 Current 20-th Harmonic | HAR20_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1322 | 25 | 25-52 | 13479 | Input Channel 14 Current 21-th Harmonic | HAR21_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1323 | 25 | 25-53 | 13480 | Input Channel 14 Current 22-th Harmonic | HAR22_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1324 | 25 | 25-54 | 13481 | Input Channel 14 Current 23-th Harmonic | HAR23_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1325 | 25 | 25-55 | 13482 | Input Channel 14 Current 24-th Harmonic | HAR24_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1326 | 25 | 25-56 | 13483 | Input Channel 14 Current 25-th Harmonic | HAR25_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1327 | 25 | 25-57 | 13484 | Input Channel 14 Current 26-th Harmonic | HAR26_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1328 | 25 | 25-58 | 13485 | Input Channel 14 Current 27-th Harmonic | HAR27_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1329 | 25 | 25-59 | 13486 | Input Channel 14 Current 28-th Harmonic | HAR28_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1330 | 25 | 25-60 | 13487 | Input Channel 14 Current 29-th Harmonic | HAR29_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1331 | 25 | 25-61 | 13488 | Input Channel 14 Current 30-th Harmonic | HAR30_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1332 | 25 | 25-62 | 13489 | Input Channel 14 Current 31-th Harmonic | HAR31_I_014_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1333 | 25 | 25-63 | 13490 | Input Channel 15 Current THD | THD_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1334 | 25 | 25-64 | 13491 | Input Channel 15 Current 2-th Harmonic | HAR2_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1335 | 25 | 25-65 | 13492 | Input Channel 15 Current 3-th Harmonic | HAR3_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1336 | 25 | 25-66 | 13493 | Input Channel 15 Current 4-th Harmonic | HAR4_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1337 | 25 | 25-67 | 13494 | Input Channel 15 Current 5-th Harmonic | HAR5_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1338 | 25 | 25-68 | 13495 | Input Channel 15 Current 6-th Harmonic | HAR6_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1339 | 25 | 25-69 | 13496 | Input Channel 15 Current 7-th Harmonic | HAR7_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1340 | 25 | 25-70 | 13497 | Input Channel 15 Current 8-th Harmonic | HAR8_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1341 | 25 | 25-71 | 13498 | Input Channel 15 Current 9-th Harmonic | HAR9_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1342 | 25 | 25-72 | 13499 | Input Channel 15 Current 10-th Harmonic | HAR10_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1343 | 25 | 25-73 | 13500 | Input Channel 15 Current 11-th Harmonic | HAR11_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1344 | 25 | 25-74 | 13501 | Input Channel 15 Current 12-th Harmonic | HAR12_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1345 | 25 | 25-75 | 13502 | Input Channel 15 Current 13-th Harmonic | HAR13_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1346 | 25 | 25-76 | 13503 | Input Channel 15 Current 14-th Harmonic | HAR14_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1347 | 25 | 25-77 | 13504 | Input Channel 15 Current 15-th Harmonic | HAR15_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1348 | 25 | 25-78 | 13505 | Input Channel 15 Current 16-th Harmonic | HAR16_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1349 | 25 | 25-79 | 13506 | Input Channel 15 Current 17-th Harmonic | HAR17_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1350 | 25 | 25-80 | 13507 | Input Channel 15 Current 18-th Harmonic | HAR18_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1351 | 25 | 25-81 | 13508 | Input Channel 15 Current 19-th Harmonic | HAR19_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1352 | 25 | 25-82 | 13509 | Input Channel 15 Current 20-th Harmonic | HAR20_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1353 | 25 | 25-83 | 13510 | Input Channel 15 Current 21-th Harmonic | HAR21_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1354 | 25 | 25-84 | 13511 | Input Channel 15 Current 22-th Harmonic | HAR22_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1355 | 25 | 25-85 | 13512 | Input Channel 15 Current 23-th Harmonic | HAR23_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1356 | 25 | 25-86 | 13513 | Input Channel 15 Current 24-th Harmonic | HAR24_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1357 | 25 | 25-87 | 13514 | Input Channel 15 Current 25-th Harmonic | HAR25_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1358 | 25 | 25-88 | 13515 | Input Channel 15 Current 26-th Harmonic | HAR26_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1359 | 25 | 25-89 | 13516 | Input Channel 15 Current 27-th Harmonic | HAR27_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1360 | 25 | 25-90 | 13517 | Input Channel 15 Current 28-th Harmonic | HAR28_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1361 | 25 | 25-91 | 13518 | Input Channel 15 Current 29-th Harmonic | HAR29_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1362 | 25 | 25-92 | 13519 | Input Channel 15 Current 30-th Harmonic | HAR30_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1363 | 25 | 25-93 | 13520 | Input Channel 15 Current 31-th Harmonic | HAR31_I_015_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1364 | 26 | 26-1 | 13521 | Input Channel 16 Current THD | THD_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1365 | 26 | 26-2 | 13522 | Input Channel 16 Current 2-th Harmonic | HAR2_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1366 | 26 | 26-3 | 13523 | Input Channel 16 Current 3-th Harmonic | HAR3_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1367 | 26 | 26-4 | 13524 | Input Channel 16 Current 4-th Harmonic | HAR4_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1368 | 26 | 26-5 | 13525 | Input Channel 16 Current 5-th Harmonic | HAR5_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1369 | 26 | 26-6 | 13526 | Input Channel 16 Current 6-th Harmonic | HAR6_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1370 | 26 | 26-7 | 13527 | Input Channel 16 Current 7-th Harmonic | HAR7_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1371 | 26 | 26-8 | 13528 | Input Channel 16 Current 8-th Harmonic | HAR8_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1372 | 26 | 26-9 | 13529 | Input Channel 16 Current 9-th Harmonic | HAR9_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1373 | 26 | 26-10 | 13530 | Input Channel 16 Current 10-th Harmonic | HAR10_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1374 | 26 | 26-11 | 13531 | Input Channel 16 Current 11-th Harmonic | HAR11_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1375 | 26 | 26-12 | 13532 | Input Channel 16 Current 12-th Harmonic | HAR12_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1376 | 26 | 26-13 | 13533 | Input Channel 16 Current 13-th Harmonic | HAR13_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1377 | 26 | 26-14 | 13534 | Input Channel 16 Current 14-th Harmonic | HAR14_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1378 | 26 | 26-15 | 13535 | Input Channel 16 Current 15-th Harmonic | HAR15_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1379 | 26 | 26-16 | 13536 | Input Channel 16 Current 16-th Harmonic | HAR16_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1380 | 26 | 26-17 | 13537 | Input Channel 16 Current 17-th Harmonic | HAR17_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1381 | 26 | 26-18 | 13538 | Input Channel 16 Current 18-th Harmonic | HAR18_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1382 | 26 | 26-19 | 13539 | Input Channel 16 Current 19-th Harmonic | HAR19_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1383 | 26 | 26-20 | 13540 | Input Channel 16 Current 20-th Harmonic | HAR20_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1384 | 26 | 26-21 | 13541 | Input Channel 16 Current 21-th Harmonic | HAR21_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1385 | 26 | 26-22 | 13542 | Input Channel 16 Current 22-th Harmonic | HAR22_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1386 | 26 | 26-23 | 13543 | Input Channel 16 Current 23-th Harmonic | HAR23_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1387 | 26 | 26-24 | 13544 | Input Channel 16 Current 24-th Harmonic | HAR24_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1388 | 26 | 26-25 | 13545 | Input Channel 16 Current 25-th Harmonic | HAR25_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1389 | 26 | 26-26 | 13546 | Input Channel 16 Current 26-th Harmonic | HAR26_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1390 | 26 | 26-27 | 13547 | Input Channel 16 Current 27-th Harmonic | HAR27_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1391 | 26 | 26-28 | 13548 | Input Channel 16 Current 28-th Harmonic | HAR28_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1392 | 26 | 26-29 | 13549 | Input Channel 16 Current 29-th Harmonic | HAR29_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1393 | 26 | 26-30 | 13550 | Input Channel 16 Current 30-th Harmonic | HAR30_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1394 | 26 | 26-31 | 13551 | Input Channel 16 Current 31-th Harmonic | HAR31_I_016_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1395 | 26 | 26-32 | 13552 | Input Channel 17 Current THD | THD_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1396 | 26 | 26-33 | 13553 | Input Channel 17 Current 2-th Harmonic | HAR2_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1397 | 26 | 26-34 | 13554 | Input Channel 17 Current 3-th Harmonic | HAR3_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1398 | 26 | 26-35 | 13555 | Input Channel 17 Current 4-th Harmonic | HAR4_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1399 | 26 | 26-36 | 13556 | Input Channel 17 Current 5-th Harmonic | HAR5_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1400 | 26 | 26-37 | 13557 | Input Channel 17 Current 6-th Harmonic | HAR6_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1401 | 26 | 26-38 | 13558 | Input Channel 17 Current 7-th Harmonic | HAR7_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1402 | 26 | 26-39 | 13559 | Input Channel 17 Current 8-th Harmonic | HAR8_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1403 | 26 | 26-40 | 13560 | Input Channel 17 Current 9-th Harmonic | HAR9_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1404 | 26 | 26-41 | 13561 | Input Channel 17 Current 10-th Harmonic | HAR10_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1405 | 26 | 26-42 | 13562 | Input Channel 17 Current 11-th Harmonic | HAR11_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1406 | 26 | 26-43 | 13563 | Input Channel 17 Current 12-th Harmonic | HAR12_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1407 | 26 | 26-44 | 13564 | Input Channel 17 Current 13-th Harmonic | HAR13_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1408 | 26 | 26-45 | 13565 | Input Channel 17 Current 14-th Harmonic | HAR14_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1409 | 26 | 26-46 | 13566 | Input Channel 17 Current 15-th Harmonic | HAR15_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1410 | 26 | 26-47 | 13567 | Input Channel 17 Current 16-th Harmonic | HAR16_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1411 | 26 | 26-48 | 13568 | Input Channel 17 Current 17-th Harmonic | HAR17_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1412 | 26 | 26-49 | 13569 | Input Channel 17 Current 18-th Harmonic | HAR18_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1413 | 26 | 26-50 | 13570 | Input Channel 17 Current 19-th Harmonic | HAR19_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1414 | 26 | 26-51 | 13571 | Input Channel 17 Current 20-th Harmonic | HAR20_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1415 | 26 | 26-52 | 13572 | Input Channel 17 Current 21-th Harmonic | HAR21_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1416 | 26 | 26-53 | 13573 | Input Channel 17 Current 22-th Harmonic | HAR22_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1417 | 26 | 26-54 | 13574 | Input Channel 17 Current 23-th Harmonic | HAR23_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1418 | 26 | 26-55 | 13575 | Input Channel 17 Current 24-th Harmonic | HAR24_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1419 | 26 | 26-56 | 13576 | Input Channel 17 Current 25-th Harmonic | HAR25_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1420 | 26 | 26-57 | 13577 | Input Channel 17 Current 26-th Harmonic | HAR26_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1421 | 26 | 26-58 | 13578 | Input Channel 17 Current 27-th Harmonic | HAR27_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1422 | 26 | 26-59 | 13579 | Input Channel 17 Current 28-th Harmonic | HAR28_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1423 | 26 | 26-60 | 13580 | Input Channel 17 Current 29-th Harmonic | HAR29_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1424 | 26 | 26-61 | 13581 | Input Channel 17 Current 30-th Harmonic | HAR30_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1425 | 26 | 26-62 | 13582 | Input Channel 17 Current 31-th Harmonic | HAR31_I_017_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1426 | 26 | 26-63 | 13583 | Input Channel 18 Current THD | THD_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 17 | 11-20-21 | THD | THD | THD | THD | THD | THD | THD
1427 | 26 | 26-64 | 13584 | Input Channel 18 Current 2-th Harmonic | HAR2_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1428 | 26 | 26-65 | 13585 | Input Channel 18 Current 3-th Harmonic | HAR3_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1429 | 26 | 26-66 | 13586 | Input Channel 18 Current 4-th Harmonic | HAR4_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1430 | 26 | 26-67 | 13587 | Input Channel 18 Current 5-th Harmonic | HAR5_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1431 | 26 | 26-68 | 13588 | Input Channel 18 Current 6-th Harmonic | HAR6_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1432 | 26 | 26-69 | 13589 | Input Channel 18 Current 7-th Harmonic | HAR7_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1433 | 26 | 26-70 | 13590 | Input Channel 18 Current 8-th Harmonic | HAR8_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1434 | 26 | 26-71 | 13591 | Input Channel 18 Current 9-th Harmonic | HAR9_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1435 | 26 | 26-72 | 13592 | Input Channel 18 Current 10-th Harmonic | HAR10_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1436 | 26 | 26-73 | 13593 | Input Channel 18 Current 11-th Harmonic | HAR11_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1437 | 26 | 26-74 | 13594 | Input Channel 18 Current 12-th Harmonic | HAR12_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1438 | 26 | 26-75 | 13595 | Input Channel 18 Current 13-th Harmonic | HAR13_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1439 | 26 | 26-76 | 13596 | Input Channel 18 Current 14-th Harmonic | HAR14_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1440 | 26 | 26-77 | 13597 | Input Channel 18 Current 15-th Harmonic | HAR15_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1441 | 26 | 26-78 | 13598 | Input Channel 18 Current 16-th Harmonic | HAR16_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1442 | 26 | 26-79 | 13599 | Input Channel 18 Current 17-th Harmonic | HAR17_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1443 | 26 | 26-80 | 13600 | Input Channel 18 Current 18-th Harmonic | HAR18_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1444 | 26 | 26-81 | 13601 | Input Channel 18 Current 19-th Harmonic | HAR19_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1445 | 26 | 26-82 | 13602 | Input Channel 18 Current 20-th Harmonic | HAR20_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1446 | 26 | 26-83 | 13603 | Input Channel 18 Current 21-th Harmonic | HAR21_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1447 | 26 | 26-84 | 13604 | Input Channel 18 Current 22-th Harmonic | HAR22_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1448 | 26 | 26-85 | 13605 | Input Channel 18 Current 23-th Harmonic | HAR23_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1449 | 26 | 26-86 | 13606 | Input Channel 18 Current 24-th Harmonic | HAR24_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1450 | 26 | 26-87 | 13607 | Input Channel 18 Current 25-th Harmonic | HAR25_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1451 | 26 | 26-88 | 13608 | Input Channel 18 Current 26-th Harmonic | HAR26_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1452 | 26 | 26-89 | 13609 | Input Channel 18 Current 27-th Harmonic | HAR27_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1453 | 26 | 26-90 | 13610 | Input Channel 18 Current 28-th Harmonic | HAR28_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1454 | 26 | 26-91 | 13611 | Input Channel 18 Current 29-th Harmonic | HAR29_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1455 | 26 | 26-92 | 13612 | Input Channel 18 Current 30-th Harmonic | HAR30_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1456 | 26 | 26-93 | 13613 | Input Channel 18 Current 31-th Harmonic | HAR31_I_018_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 18 | 20-21 | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics | harmonics
1457 | 27 | 27-1 | 13614 | User Channel 1 Current Unbalance Factor | UNBL_I_s001_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 19 | 11-20-21 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
1458 | 27 | 27-2 | 13615 | User Channel 2 Current Unbalance Factor | UNBL_I_s002_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 19 | 11-20-21 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
1459 | 27 | 27-3 | 13616 | User Channel 3 Current Unbalance Factor | UNBL_I_s003_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 19 | 11-20-21 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
1460 | 27 | 27-4 | 13617 | User Channel 4 Current Unbalance Factor | UNBL_I_s004_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 19 | 11-20-21 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
1461 | 27 | 27-5 | 13618 | User Channel 5 Current Unbalance Factor | UNBL_I_s005_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 19 | 11-20-21 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
1462 | 27 | 27-6 | 13619 | User Channel 6 Current Unbalance Factor | UNBL_I_s006_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 19 | 11-20-21 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
1463 | 27 | 27-7 | 13620 | User Channel 7 Current Unbalance Factor | UNBL_I_s007_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 19 | 11-20-21 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
1464 | 27 | 27-8 | 13621 | User Channel 8 Current Unbalance Factor | UNBL_I_s008_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 19 | 11-20-21 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
1465 | 27 | 27-9 | 13622 | User Channel 9 Current Unbalance Factor | UNBL_I_s009_% | % | int16 | 12 | R | 1 | 0.01 | [6 empty] | 19 | 11-20-21 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
1463 | 28 | 28-1 | 13824 | Phase Angle of V2 to V1 | ANG_VLN_b | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1464 | 28 | 28-2 | 13825 | Phase Angle of V3 to V1 | ANG_VLN_c | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1465 | 28 | 28-3 | 13826 | Phase Angle of Load 1 Current to V1 | ANG_I_001 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1466 | 28 | 28-4 | 13827 | Phase Angle of Load 2 Current to V2 | ANG_I_002 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1467 | 28 | 28-5 | 13828 | Phase Angle of Load 3 Current to V3 | ANG_I_003 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1468 | 28 | 28-6 | 13829 | Phase Angle of Load 4 Current to V4 | ANG_I_004 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1469 | 28 | 28-7 | 13830 | Phase Angle of Load 5 Current to V5 | ANG_I_005 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1470 | 28 | 28-8 | 13831 | Phase Angle of Load 6 Current to V6 | ANG_I_006 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1471 | 28 | 28-9 | 13832 | Phase Angle of Load 7 Current to V7 | ANG_I_007 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1472 | 28 | 28-10 | 13833 | Phase Angle of Load 8 Current to V8 | ANG_I_008 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1473 | 28 | 28-11 | 13834 | Phase Angle of Load 9 Current to V9 | ANG_I_009 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1474 | 28 | 28-12 | 13835 | Phase Angle of Load 10 Current to V10 | ANG_I_010 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1475 | 28 | 28-13 | 13836 | Phase Angle of Load 11 Current to V11 | ANG_I_011 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1476 | 28 | 28-14 | 13837 | Phase Angle of Load 12 Current to V12 | ANG_I_012 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1477 | 28 | 28-15 | 13838 | Phase Angle of Load 13 Current to V13 | ANG_I_013 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1478 | 28 | 28-16 | 13839 | Phase Angle of Load 14 Current to V14 | ANG_I_014 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1479 | 28 | 28-17 | 13840 | Phase Angle of Load 15 Current to V15 | ANG_I_015 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1480 | 28 | 28-18 | 13841 | Phase Angle of Load 16 Current to V16 | ANG_I_016 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1481 | 28 | 28-19 | 13842 | Phase Angle of Load 17 Current to V17 | ANG_I_017 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1482 | 28 | 28-20 | 13843 | Phase Angle of Load 18 Current to V18 | ANG_I_018 | ° | int16 | 12 | R | 1 | 0.1 | [6 empty] | 14 | 20-21 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
1483 | 29 | 29-1 | 2048 | Channel 1 Address | Conf_Ch1_Addr |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1484 | 29 | 29-2 | 2049 | Channel 1 Parity | Conf_Ch1_Parity |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1485 | 29 | 29-3 | 2050 | Channel 2 Parity | Conf_Ch2_Parity |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1486 | 29 | 29-4 | 2051 | Channel 1 Baud Rate | Conf_Ch1_Baud |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1487 | 29 | 29-5 | 2052 | Channel 2 Baud Rate | Conf_Ch2_Baud |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1488 | 29 | 29-6 | 2053 | Password | Conf_Password |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1489 | 29 | 29-7 | 2054 | Pulse Constant | Conf_PulseConst |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1490 | 29 | 29-8 | 2055 | Pulse Width | Conf_PulseWidth |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1491 | 29 | 29-9 | 2056 | Channel 2 Address | Conf_Ch2_Addr |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1492 | 29 | 29-10 | 2058 | Demand Method | Conf_Dmd_Method |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1493 | 29 | 29-11 | 2059 | Demand Window | Conf_Dmd_Window |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1494 | 29 | 29-12 | 2060 | Demand Sub Interval | Conf_Dmd_SubInterval |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1495 | 29 | 29-13 | 2061 | CT2 Value | Conf_CT2 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1496 | 30 | 30-1 | 2097 | LCD Backlight Time | Conf_Backlight_Time |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1497 | 30 | 30-2 | 2101 | Reactive Power Calculation Method | Conf_CalcMethod_Q |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1498 | 30 | 30-3 | 2102 | VAR/PF Convention | Conf_CalcMethod_VarPF |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1499 | 31 | 31-1 | 2183 | Nominal Voltage | Conf_NominalVolt |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1500 | 31 | 31-2 | 2184 | Service Configuration | Conf_ServiceConfig |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5 |  | 6-8-10-12
1501 | 31 | 31-3 | 2185 | Input Channel 1 CT | Conf_001_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1502 | 31 | 31-4 | 2186 | Input Channel 2 CT | Conf_002_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1503 | 31 | 31-5 | 2187 | Input Channel 3 CT | Conf_003_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1504 | 31 | 31-6 | 2188 | Input Channel 4 CT | Conf_004_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1505 | 31 | 31-7 | 2189 | Input Channel 5 CT | Conf_005_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1506 | 31 | 31-8 | 2190 | Input Channel 6 CT | Conf_006_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1507 | 31 | 31-9 | 2191 | Input Channel 7 CT | Conf_007_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1508 | 31 | 31-10 | 2192 | Input Channel 8 CT | Conf_008_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1509 | 31 | 31-11 | 2193 | Input Channel 9 CT | Conf_009_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1510 | 31 | 31-12 | 2194 | Input Channel 10 CT | Conf_010_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1511 | 31 | 31-13 | 2195 | Input Channel 11 CT | Conf_011_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1512 | 31 | 31-14 | 2196 | Input Channel 12 CT | Conf_012_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1513 | 31 | 31-15 | 2197 | Input Channel 13 CT | Conf_013_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1514 | 31 | 31-16 | 2198 | Input Channel 14 CT | Conf_014_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1515 | 31 | 31-17 | 2199 | Input Channel 15 CT | Conf_015_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1516 | 31 | 31-18 | 2200 | Input Channel 16 CT | Conf_016_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1517 | 31 | 31-19 | 2201 | Input Channel 17 CT | Conf_017_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1518 | 31 | 31-20 | 2202 | Input Channel 18 CT | Conf_018_CT1 |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1519 | 32 | 32-1 | 61723 | CT2 Type | Info_CT2_Type |  | uint16 | 12 | R | 1 | 1 | [5 empty] | 5
1520 | 33 | 33-1 | 61440 | Meter Model | Info_MeterModel |  | uint32 | 12 | R | 2 | 1 | [5 empty] | 5 |  | 6-8-10-12
1521 | 33 | 33-2 | 61442 | Hardware version | Info_HardwareVersion |  | uint32 | 12 | R | 2 | 1
1522 | 33 | 33-3 | 61444 | Software version | Info_SoftwareVersion |  | uint32 | 12 | R | 2 | 1
1523 | 33 | 33-4 | 61446 | Software date | Info_SoftwareDate |  | uint32 | 12 | R | 3 | 1
1524 | 34 | 34-1 | 2221 | Restore Factory Setting | Conf_Restore_FactorySetting |  | uint16 | 12 | W | 1 | 1 | [5 empty] | 5
1525 | 34 | 34-2 | 2222 | Enable 10 Years TOU settings | Conf_TOU_Enable10Years |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1526 | 34 | 34-3 | 2223 | Non-Standard Content Seal Option | Conf_Seal_Option |  | uint16 | 12 | R/W | 1 | 1 | [5 empty] | 5
1527 | 34 | 34-4 | 2224 | Sealing Status | Info_Seal_Status |  | uint16 | 12 | R | 1 | 1 | [5 empty] | 5

## analysisUnits
analysisUnitId | analysisUnitTypeName

## analysisParams
threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis
three_phase_realtime | three_phase_energy_demand | three_phase_thd | three_phase_harmonics | three_phase_sequence
VLN_a_V | EP_IMP_a_kWh | THD_V_a_% | HAR2_V_a_% | SEQ_POS_REAL_I
ANG_VLN_a | EQ_IMP_a_kvarh | OTHD_V_a_% | HAR3_V_a_% | SEQ_NEG_REAL_I
VLL_ab_V | EP_EXP_a_kWh | ETHD_V_a_% | HAR4_V_a_% | SEQ_ZERO_REAL_I
ANG_VLL_ab | EQ_EXP_a_kvarh | CF_V_a_% | HAR5_V_a_% | SEQ_POS_IMG_I
I_a_A | EP_NET_a_kWh | THD_I_a_% | HAR6_V_a_% | SEQ_NEG_IMG_I
ANG_I_a | EQ_NET_a_kvarh | OTHD_I_a_% | HAR7_V_a_% | SEQ_ZERO_IMG_I
P_a_kW | EP_TOTAL_a_kWh | ETHD_I_a_% | HAR8_V_a_% | SEQ_POS_REAL_V
Q_a_kvar | EQ_TOTAL_a_kvarh | TDD_I_a_% | HAR9_V_a_% | SEQ_NEG_REAL_V
S_a_kVA | ES_a_kVAh | CF_I_a_% | HAR10_V_a_% | SEQ_ZERO_REAL_V
LC_a | EP_IMP_b_kWh | KF_I_a_% | HAR11_V_a_% | SEQ_POS_IMG_V
PF_a | EQ_IMP_b_kvarh | THD_V_b_% | HAR12_V_a_% | SEQ_NEG_IMG_V
LEAD_PF_a | EP_EXP_b_kWh | OTHD_V_b_% | HAR13_V_a_% | SEQ_ZERO_IMG_V
LAG_PF_a | EQ_EXP_b_kvarh | ETHD_V_b_% | HAR14_V_a_% | UNBL_V_%
VLN_b_V | EP_NET_b_kWh | CF_V_b_% | HAR15_V_a_% | UNBL_I_%
ANG_VLN_b | EQ_NET_b_kvarh | THD_I_b_% | HAR16_V_a_% | SEQ_ZERO_RATIO_V_%
VLL_bc_V | EP_TOTAL_b_kWh | OTHD_I_b_% | HAR17_V_a_% | SEQ_ZERO_RATIO_I_%
ANG_VLL_bb | EQ_TOTAL_b_kvarh | ETHD_I_b_% | HAR18_V_a_%
I_b_A | ES_b_kVAh | TDD_I_b_% | HAR19_V_a_%
ANG_I_b | EP_IMP_c_kWh | CF_I_b_% | HAR20_V_a_%
P_b_kW | EQ_IMP_c_kvarh | KF_I_b_% | HAR21_V_a_%
Q_b_kvar | EP_EXP_c_kWh | THD_V_c_% | HAR22_V_a_%
S_b_kVA | EQ_EXP_c_kvarh | OTHD_V_c_% | HAR23_V_a_%
LC_b | EP_NET_c_kWh | ETHD_V_c_% | HAR24_V_a_%
PF_b | EQ_NET_c_kvarh | CF_V_c_% | HAR25_V_a_%
LEAD_PF_b | EP_TOTAL_c_kWh | THD_I_c_% | HAR26_V_a_%
LAG_PF_b | EQ_TOTAL_c_kvarh | OTHD_I_c_% | HAR27_V_a_%
VLN_c_V | ES_c_kVAh | ETHD_I_c_% | HAR28_V_a_%
ANG_VLN_c | EP_IMP_kWh | TDD_I_c_% | HAR29_V_a_%
VLL_ca_V | EQ_IMP_kvarh | CF_I_c_% | HAR30_V_a_%
ANG_VLL_cb | EP_EXP_kWh | KF_I_c_% | HAR31_V_a_%
I_c_A | EQ_EXP_kvarh | THD_V_avg_% | HAR32_V_a_%
ANG_I_c | EP_NET_kWh | OTHD_V_avg_% | HAR33_V_a_%
P_c_kW | EQ_NET_kvarh | ETHD_V_avg_% | HAR34_V_a_%
Q_c_kvar | EP_TOTAL_kWh | CF_V_avg_% | HAR35_V_a_%
S_c_kVA | EQ_TOTAL_kvarh | THD_I_avg_% | HAR36_V_a_%
LC_c | ES_kVAh | OTHD_I_avg_% | HAR37_V_a_%
PF_c | DMD_P_a_kW | ETHD_I_avg_% | HAR38_V_a_%
LEAD_PF_c | DMD_Q_a_kvar | TDD_I_avg_% | HAR39_V_a_%
LAG_PF_c | DMD_S_a_kVA | CF_I_avg_% | HAR40_V_a_%
VLN_avg_V | DMD_P_b_kW | KF_I_avg_% | HAR41_V_a_%
VLL_avg_V | DMD_Q_b_kvar |  | HAR42_V_a_%
I_avg_A | DMD_S_b_kVA |  | HAR43_V_a_%
LC_avg | DMD_P_c_kW |  | HAR44_V_a_%
I_n_A | DMD_Q_c_kvar |  | HAR45_V_a_%
P_kW | DMD_S_c_kVA |  | HAR46_V_a_%
Q_kvar | DMD_P_kW |  | HAR47_V_a_%
S_kVA | DMD_Q_kvar |  | HAR48_V_a_%
PF | DMD_S_kVA |  | HAR49_V_a_%
LEAD_PF |  |  | HAR50_V_a_%
LAG_PF |  |  | HAR51_V_a_%
FREQ_Hz |  |  | HAR52_V_a_%
HAR53_V_a_%
HAR54_V_a_%
HAR55_V_a_%
HAR56_V_a_%
HAR57_V_a_%
HAR58_V_a_%
HAR59_V_a_%
HAR60_V_a_%
HAR61_V_a_%
HAR62_V_a_%
HAR63_V_a_%
HAR64_V_a_%
HAR65_V_a_%
HAR66_V_a_%
HAR67_V_a_%
HAR68_V_a_%
HAR69_V_a_%
HAR70_V_a_%
HAR71_V_a_%
HAR72_V_a_%
HAR73_V_a_%
HAR74_V_a_%
HAR75_V_a_%
HAR76_V_a_%
HAR77_V_a_%
HAR78_V_a_%
HAR79_V_a_%
HAR80_V_a_%
HAR81_V_a_%
HAR82_V_a_%
HAR83_V_a_%
HAR84_V_a_%
HAR85_V_a_%
HAR86_V_a_%
HAR87_V_a_%
HAR88_V_a_%
HAR89_V_a_%
HAR90_V_a_%
HAR91_V_a_%
HAR92_V_a_%
HAR93_V_a_%
HAR94_V_a_%
HAR95_V_a_%
HAR96_V_a_%
HAR97_V_a_%
HAR98_V_a_%
HAR99_V_a_%
HAR100_V_a_%
HAR101_V_a_%
HAR102_V_a_%
HAR103_V_a_%
HAR104_V_a_%
HAR105_V_a_%
HAR106_V_a_%
HAR107_V_a_%
HAR108_V_a_%
HAR109_V_a_%
HAR110_V_a_%
HAR111_V_a_%
HAR112_V_a_%
HAR113_V_a_%
HAR114_V_a_%
HAR115_V_a_%
HAR116_V_a_%
HAR117_V_a_%
HAR118_V_a_%
HAR119_V_a_%
HAR120_V_a_%
HAR121_V_a_%
HAR122_V_a_%
HAR123_V_a_%
HAR124_V_a_%
HAR125_V_a_%
HAR126_V_a_%
HAR127_V_a_%
ANG_HAR2_V_a
ANG_HAR3_V_a
ANG_HAR4_V_a
ANG_HAR5_V_a
ANG_HAR6_V_a
ANG_HAR7_V_a
ANG_HAR8_V_a
ANG_HAR9_V_a
ANG_HAR10_V_a
ANG_HAR11_V_a
ANG_HAR12_V_a
ANG_HAR13_V_a
ANG_HAR14_V_a
ANG_HAR15_V_a
ANG_HAR16_V_a
ANG_HAR17_V_a
ANG_HAR18_V_a
ANG_HAR19_V_a
ANG_HAR20_V_a
ANG_HAR21_V_a
ANG_HAR22_V_a
ANG_HAR23_V_a
ANG_HAR24_V_a
ANG_HAR25_V_a
ANG_HAR26_V_a
ANG_HAR27_V_a
ANG_HAR28_V_a
ANG_HAR29_V_a
ANG_HAR30_V_a
ANG_HAR31_V_a
ANG_HAR32_V_a
ANG_HAR33_V_a
ANG_HAR34_V_a
ANG_HAR35_V_a
ANG_HAR36_V_a
ANG_HAR37_V_a
ANG_HAR38_V_a
ANG_HAR39_V_a
ANG_HAR40_V_a
ANG_HAR41_V_a
ANG_HAR42_V_a
ANG_HAR43_V_a
ANG_HAR44_V_a
ANG_HAR45_V_a
ANG_HAR46_V_a
ANG_HAR47_V_a
ANG_HAR48_V_a
ANG_HAR49_V_a
ANG_HAR50_V_a
ANG_HAR51_V_a
ANG_HAR52_V_a
ANG_HAR53_V_a
ANG_HAR54_V_a
ANG_HAR55_V_a
ANG_HAR56_V_a
ANG_HAR57_V_a
ANG_HAR58_V_a
ANG_HAR59_V_a
ANG_HAR60_V_a
ANG_HAR61_V_a
ANG_HAR62_V_a
ANG_HAR63_V_a
ANG_HAR64_V_a
ANG_HAR65_V_a
ANG_HAR66_V_a
ANG_HAR67_V_a
ANG_HAR68_V_a
ANG_HAR69_V_a
ANG_HAR70_V_a
ANG_HAR71_V_a
ANG_HAR72_V_a
ANG_HAR73_V_a
ANG_HAR74_V_a
ANG_HAR75_V_a
ANG_HAR76_V_a
ANG_HAR77_V_a
ANG_HAR78_V_a
ANG_HAR79_V_a
ANG_HAR80_V_a
ANG_HAR81_V_a
ANG_HAR82_V_a
ANG_HAR83_V_a
ANG_HAR84_V_a
ANG_HAR85_V_a
ANG_HAR86_V_a
ANG_HAR87_V_a
ANG_HAR88_V_a
ANG_HAR89_V_a
ANG_HAR90_V_a
ANG_HAR91_V_a
ANG_HAR92_V_a
ANG_HAR93_V_a
ANG_HAR94_V_a
ANG_HAR95_V_a
ANG_HAR96_V_a
ANG_HAR97_V_a
ANG_HAR98_V_a
ANG_HAR99_V_a
ANG_HAR100_V_a
ANG_HAR101_V_a
ANG_HAR102_V_a
ANG_HAR103_V_a
ANG_HAR104_V_a
ANG_HAR105_V_a
ANG_HAR106_V_a
ANG_HAR107_V_a
ANG_HAR108_V_a
ANG_HAR109_V_a
ANG_HAR110_V_a
ANG_HAR111_V_a
ANG_HAR112_V_a
ANG_HAR113_V_a
ANG_HAR114_V_a
ANG_HAR115_V_a
ANG_HAR116_V_a
ANG_HAR117_V_a
ANG_HAR118_V_a
ANG_HAR119_V_a
ANG_HAR120_V_a
ANG_HAR121_V_a
ANG_HAR122_V_a
ANG_HAR123_V_a
ANG_HAR124_V_a
ANG_HAR125_V_a
ANG_HAR126_V_a
ANG_HAR127_V_a
HAR2_V_b_%
HAR3_V_b_%
HAR4_V_b_%
HAR5_V_b_%
HAR6_V_b_%
HAR7_V_b_%
HAR8_V_b_%
HAR9_V_b_%
HAR10_V_b_%
HAR11_V_b_%
HAR12_V_b_%
HAR13_V_b_%
HAR14_V_b_%
HAR15_V_b_%
HAR16_V_b_%
HAR17_V_b_%
HAR18_V_b_%
HAR19_V_b_%
HAR20_V_b_%
HAR21_V_b_%
HAR22_V_b_%
HAR23_V_b_%
HAR24_V_b_%
HAR25_V_b_%
HAR26_V_b_%
HAR27_V_b_%
HAR28_V_b_%
HAR29_V_b_%
HAR30_V_b_%
HAR31_V_b_%
HAR32_V_b_%
HAR33_V_b_%
HAR34_V_b_%
HAR35_V_b_%
HAR36_V_b_%
HAR37_V_b_%
HAR38_V_b_%
HAR39_V_b_%
HAR40_V_b_%
HAR41_V_b_%
HAR42_V_b_%
HAR43_V_b_%
HAR44_V_b_%
HAR45_V_b_%
HAR46_V_b_%
HAR47_V_b_%
HAR48_V_b_%
HAR49_V_b_%
HAR50_V_b_%
HAR51_V_b_%
HAR52_V_b_%
HAR53_V_b_%
HAR54_V_b_%
HAR55_V_b_%
HAR56_V_b_%
HAR57_V_b_%
HAR58_V_b_%
HAR59_V_b_%
HAR60_V_b_%
HAR61_V_b_%
HAR62_V_b_%
HAR63_V_b_%
HAR64_V_b_%
HAR65_V_b_%
HAR66_V_b_%
HAR67_V_b_%
HAR68_V_b_%
HAR69_V_b_%
HAR70_V_b_%
HAR71_V_b_%
HAR72_V_b_%
HAR73_V_b_%
HAR74_V_b_%
HAR75_V_b_%
HAR76_V_b_%
HAR77_V_b_%
HAR78_V_b_%
HAR79_V_b_%
HAR80_V_b_%
HAR81_V_b_%
HAR82_V_b_%
HAR83_V_b_%
HAR84_V_b_%
HAR85_V_b_%
HAR86_V_b_%
HAR87_V_b_%
HAR88_V_b_%
HAR89_V_b_%
HAR90_V_b_%
HAR91_V_b_%
HAR92_V_b_%
HAR93_V_b_%
HAR94_V_b_%
HAR95_V_b_%
HAR96_V_b_%
HAR97_V_b_%
HAR98_V_b_%
HAR99_V_b_%
HAR100_V_b_%
HAR101_V_b_%
HAR102_V_b_%
HAR103_V_b_%
HAR104_V_b_%
HAR105_V_b_%
HAR106_V_b_%
HAR107_V_b_%
HAR108_V_b_%
HAR109_V_b_%
HAR110_V_b_%
HAR111_V_b_%
HAR112_V_b_%
HAR113_V_b_%
HAR114_V_b_%
HAR115_V_b_%
HAR116_V_b_%
HAR117_V_b_%
HAR118_V_b_%
HAR119_V_b_%
HAR120_V_b_%
HAR121_V_b_%
HAR122_V_b_%
HAR123_V_b_%
HAR124_V_b_%
HAR125_V_b_%
HAR126_V_b_%
HAR127_V_b_%
ANG_HAR2_V_b
ANG_HAR3_V_b
ANG_HAR4_V_b
ANG_HAR5_V_b
ANG_HAR6_V_b
ANG_HAR7_V_b
ANG_HAR8_V_b
ANG_HAR9_V_b
ANG_HAR10_V_b
ANG_HAR11_V_b
ANG_HAR12_V_b
ANG_HAR13_V_b
ANG_HAR14_V_b
ANG_HAR15_V_b
ANG_HAR16_V_b
ANG_HAR17_V_b
ANG_HAR18_V_b
ANG_HAR19_V_b
ANG_HAR20_V_b
ANG_HAR21_V_b
ANG_HAR22_V_b
ANG_HAR23_V_b
ANG_HAR24_V_b
ANG_HAR25_V_b
ANG_HAR26_V_b
ANG_HAR27_V_b
ANG_HAR28_V_b
ANG_HAR29_V_b
ANG_HAR30_V_b
ANG_HAR31_V_b
ANG_HAR32_V_b
ANG_HAR33_V_b
ANG_HAR34_V_b
ANG_HAR35_V_b
ANG_HAR36_V_b
ANG_HAR37_V_b
ANG_HAR38_V_b
ANG_HAR39_V_b
ANG_HAR40_V_b
ANG_HAR41_V_b
ANG_HAR42_V_b
ANG_HAR43_V_b
ANG_HAR44_V_b
ANG_HAR45_V_b
ANG_HAR46_V_b
ANG_HAR47_V_b
ANG_HAR48_V_b
ANG_HAR49_V_b
ANG_HAR50_V_b
ANG_HAR51_V_b
ANG_HAR52_V_b
ANG_HAR53_V_b
ANG_HAR54_V_b
ANG_HAR55_V_b
ANG_HAR56_V_b
ANG_HAR57_V_b
ANG_HAR58_V_b
ANG_HAR59_V_b
ANG_HAR60_V_b
ANG_HAR61_V_b
ANG_HAR62_V_b
ANG_HAR63_V_b
ANG_HAR64_V_b
ANG_HAR65_V_b
ANG_HAR66_V_b
ANG_HAR67_V_b
ANG_HAR68_V_b
ANG_HAR69_V_b
ANG_HAR70_V_b
ANG_HAR71_V_b
ANG_HAR72_V_b
ANG_HAR73_V_b
ANG_HAR74_V_b
ANG_HAR75_V_b
ANG_HAR76_V_b
ANG_HAR77_V_b
ANG_HAR78_V_b
ANG_HAR79_V_b
ANG_HAR80_V_b
ANG_HAR81_V_b
ANG_HAR82_V_b
ANG_HAR83_V_b
ANG_HAR84_V_b
ANG_HAR85_V_b
ANG_HAR86_V_b
ANG_HAR87_V_b
ANG_HAR88_V_b
ANG_HAR89_V_b
ANG_HAR90_V_b
ANG_HAR91_V_b
ANG_HAR92_V_b
ANG_HAR93_V_b
ANG_HAR94_V_b
ANG_HAR95_V_b
ANG_HAR96_V_b
ANG_HAR97_V_b
ANG_HAR98_V_b
ANG_HAR99_V_b
ANG_HAR100_V_b
ANG_HAR101_V_b
ANG_HAR102_V_b
ANG_HAR103_V_b
ANG_HAR104_V_b
ANG_HAR105_V_b
ANG_HAR106_V_b
ANG_HAR107_V_b
ANG_HAR108_V_b
ANG_HAR109_V_b
ANG_HAR110_V_b
ANG_HAR111_V_b
ANG_HAR112_V_b
ANG_HAR113_V_b
ANG_HAR114_V_b
ANG_HAR115_V_b
ANG_HAR116_V_b
ANG_HAR117_V_b
ANG_HAR118_V_b
ANG_HAR119_V_b
ANG_HAR120_V_b
ANG_HAR121_V_b
ANG_HAR122_V_b
ANG_HAR123_V_b
ANG_HAR124_V_b
ANG_HAR125_V_b
ANG_HAR126_V_b
ANG_HAR127_V_b
HAR2_V_c_%
HAR3_V_c_%
HAR4_V_c_%
HAR5_V_c_%
HAR6_V_c_%
HAR7_V_c_%
HAR8_V_c_%
HAR9_V_c_%
HAR10_V_c_%
HAR11_V_c_%
HAR12_V_c_%
HAR13_V_c_%
HAR14_V_c_%
HAR15_V_c_%
HAR16_V_c_%
HAR17_V_c_%
HAR18_V_c_%
HAR19_V_c_%
HAR20_V_c_%
HAR21_V_c_%
HAR22_V_c_%
HAR23_V_c_%
HAR24_V_c_%
HAR25_V_c_%
HAR26_V_c_%
HAR27_V_c_%
HAR28_V_c_%
HAR29_V_c_%
HAR30_V_c_%
HAR31_V_c_%
HAR32_V_c_%
HAR33_V_c_%
HAR34_V_c_%
HAR35_V_c_%
HAR36_V_c_%
HAR37_V_c_%
HAR38_V_c_%
HAR39_V_c_%
HAR40_V_c_%
HAR41_V_c_%
HAR42_V_c_%
HAR43_V_c_%
HAR44_V_c_%
HAR45_V_c_%
HAR46_V_c_%
HAR47_V_c_%
HAR48_V_c_%
HAR49_V_c_%
HAR50_V_c_%
HAR51_V_c_%
HAR52_V_c_%
HAR53_V_c_%
HAR54_V_c_%
HAR55_V_c_%
HAR56_V_c_%
HAR57_V_c_%
HAR58_V_c_%
HAR59_V_c_%
HAR60_V_c_%
HAR61_V_c_%
HAR62_V_c_%
HAR63_V_c_%
HAR64_V_c_%
HAR65_V_c_%
HAR66_V_c_%
HAR67_V_c_%
HAR68_V_c_%
HAR69_V_c_%
HAR70_V_c_%
HAR71_V_c_%
HAR72_V_c_%
HAR73_V_c_%
HAR74_V_c_%
HAR75_V_c_%
HAR76_V_c_%
HAR77_V_c_%
HAR78_V_c_%
HAR79_V_c_%
HAR80_V_c_%
HAR81_V_c_%
HAR82_V_c_%
HAR83_V_c_%
HAR84_V_c_%
HAR85_V_c_%
HAR86_V_c_%
HAR87_V_c_%
HAR88_V_c_%
HAR89_V_c_%
HAR90_V_c_%
HAR91_V_c_%
HAR92_V_c_%
HAR93_V_c_%
HAR94_V_c_%
HAR95_V_c_%
HAR96_V_c_%
HAR97_V_c_%
HAR98_V_c_%
HAR99_V_c_%
HAR100_V_c_%
HAR101_V_c_%
HAR102_V_c_%
HAR103_V_c_%
HAR104_V_c_%
HAR105_V_c_%
HAR106_V_c_%
HAR107_V_c_%
HAR108_V_c_%
HAR109_V_c_%
HAR110_V_c_%
HAR111_V_c_%
HAR112_V_c_%
HAR113_V_c_%
HAR114_V_c_%
HAR115_V_c_%
HAR116_V_c_%
HAR117_V_c_%
HAR118_V_c_%
HAR119_V_c_%
HAR120_V_c_%
HAR121_V_c_%
HAR122_V_c_%
HAR123_V_c_%
HAR124_V_c_%
HAR125_V_c_%
HAR126_V_c_%
HAR127_V_c_%
ANG_HAR2_V_c
ANG_HAR3_V_c
ANG_HAR4_V_c
ANG_HAR5_V_c
ANG_HAR6_V_c
ANG_HAR7_V_c
ANG_HAR8_V_c
ANG_HAR9_V_c
ANG_HAR10_V_c
ANG_HAR11_V_c
ANG_HAR12_V_c
ANG_HAR13_V_c
ANG_HAR14_V_c
ANG_HAR15_V_c
ANG_HAR16_V_c
ANG_HAR17_V_c
ANG_HAR18_V_c
ANG_HAR19_V_c
ANG_HAR20_V_c
ANG_HAR21_V_c
ANG_HAR22_V_c
ANG_HAR23_V_c
ANG_HAR24_V_c
ANG_HAR25_V_c
ANG_HAR26_V_c
ANG_HAR27_V_c
ANG_HAR28_V_c
ANG_HAR29_V_c
ANG_HAR30_V_c
ANG_HAR31_V_c
ANG_HAR32_V_c
ANG_HAR33_V_c
ANG_HAR34_V_c
ANG_HAR35_V_c
ANG_HAR36_V_c
ANG_HAR37_V_c
ANG_HAR38_V_c
ANG_HAR39_V_c
ANG_HAR40_V_c
ANG_HAR41_V_c
ANG_HAR42_V_c
ANG_HAR43_V_c
ANG_HAR44_V_c
ANG_HAR45_V_c
ANG_HAR46_V_c
ANG_HAR47_V_c
ANG_HAR48_V_c
ANG_HAR49_V_c
ANG_HAR50_V_c
ANG_HAR51_V_c
ANG_HAR52_V_c
ANG_HAR53_V_c
ANG_HAR54_V_c
ANG_HAR55_V_c
ANG_HAR56_V_c
ANG_HAR57_V_c
ANG_HAR58_V_c
ANG_HAR59_V_c
ANG_HAR60_V_c
ANG_HAR61_V_c
ANG_HAR62_V_c
ANG_HAR63_V_c
ANG_HAR64_V_c
ANG_HAR65_V_c
ANG_HAR66_V_c
ANG_HAR67_V_c
ANG_HAR68_V_c
ANG_HAR69_V_c
ANG_HAR70_V_c
ANG_HAR71_V_c
ANG_HAR72_V_c
ANG_HAR73_V_c
ANG_HAR74_V_c
ANG_HAR75_V_c
ANG_HAR76_V_c
ANG_HAR77_V_c
ANG_HAR78_V_c
ANG_HAR79_V_c
ANG_HAR80_V_c
ANG_HAR81_V_c
ANG_HAR82_V_c
ANG_HAR83_V_c
ANG_HAR84_V_c
ANG_HAR85_V_c
ANG_HAR86_V_c
ANG_HAR87_V_c
ANG_HAR88_V_c
ANG_HAR89_V_c
ANG_HAR90_V_c
ANG_HAR91_V_c
ANG_HAR92_V_c
ANG_HAR93_V_c
ANG_HAR94_V_c
ANG_HAR95_V_c
ANG_HAR96_V_c
ANG_HAR97_V_c
ANG_HAR98_V_c
ANG_HAR99_V_c
ANG_HAR100_V_c
ANG_HAR101_V_c
ANG_HAR102_V_c
ANG_HAR103_V_c
ANG_HAR104_V_c
ANG_HAR105_V_c
ANG_HAR106_V_c
ANG_HAR107_V_c
ANG_HAR108_V_c
ANG_HAR109_V_c
ANG_HAR110_V_c
ANG_HAR111_V_c
ANG_HAR112_V_c
ANG_HAR113_V_c
ANG_HAR114_V_c
ANG_HAR115_V_c
ANG_HAR116_V_c
ANG_HAR117_V_c
ANG_HAR118_V_c
ANG_HAR119_V_c
ANG_HAR120_V_c
ANG_HAR121_V_c
ANG_HAR122_V_c
ANG_HAR123_V_c
ANG_HAR124_V_c
ANG_HAR125_V_c
ANG_HAR126_V_c
ANG_HAR127_V_c
HAR2_I_a_%
HAR3_I_a_%
HAR4_I_a_%
HAR5_I_a_%
HAR6_I_a_%
HAR7_I_a_%
HAR8_I_a_%
HAR9_I_a_%
HAR10_I_a_%
HAR11_I_a_%
HAR12_I_a_%
HAR13_I_a_%
HAR14_I_a_%
HAR15_I_a_%
HAR16_I_a_%
HAR17_I_a_%
HAR18_I_a_%
HAR19_I_a_%
HAR20_I_a_%
HAR21_I_a_%
HAR22_I_a_%
HAR23_I_a_%
HAR24_I_a_%
HAR25_I_a_%
HAR26_I_a_%
HAR27_I_a_%
HAR28_I_a_%
HAR29_I_a_%
HAR30_I_a_%
HAR31_I_a_%
HAR32_I_a_%
HAR33_I_a_%
HAR34_I_a_%
HAR35_I_a_%
HAR36_I_a_%
HAR37_I_a_%
HAR38_I_a_%
HAR39_I_a_%
HAR40_I_a_%
HAR41_I_a_%
HAR42_I_a_%
HAR43_I_a_%
HAR44_I_a_%
HAR45_I_a_%
HAR46_I_a_%
HAR47_I_a_%
HAR48_I_a_%
HAR49_I_a_%
HAR50_I_a_%
HAR51_I_a_%
HAR52_I_a_%
HAR53_I_a_%
HAR54_I_a_%
HAR55_I_a_%
HAR56_I_a_%
HAR57_I_a_%
HAR58_I_a_%
HAR59_I_a_%
HAR60_I_a_%
HAR61_I_a_%
HAR62_I_a_%
HAR63_I_a_%
HAR64_I_a_%
HAR65_I_a_%
HAR66_I_a_%
HAR67_I_a_%
HAR68_I_a_%
HAR69_I_a_%
HAR70_I_a_%
HAR71_I_a_%
HAR72_I_a_%
HAR73_I_a_%
HAR74_I_a_%
HAR75_I_a_%
HAR76_I_a_%
HAR77_I_a_%
HAR78_I_a_%
HAR79_I_a_%
HAR80_I_a_%
HAR81_I_a_%
HAR82_I_a_%
HAR83_I_a_%
HAR84_I_a_%
HAR85_I_a_%
HAR86_I_a_%
HAR87_I_a_%
HAR88_I_a_%
HAR89_I_a_%
HAR90_I_a_%
HAR91_I_a_%
HAR92_I_a_%
HAR93_I_a_%
HAR94_I_a_%
HAR95_I_a_%
HAR96_I_a_%
HAR97_I_a_%
HAR98_I_a_%
HAR99_I_a_%
HAR100_I_a_%
HAR101_I_a_%
HAR102_I_a_%
HAR103_I_a_%
HAR104_I_a_%
HAR105_I_a_%
HAR106_I_a_%
HAR107_I_a_%
HAR108_I_a_%
HAR109_I_a_%
HAR110_I_a_%
HAR111_I_a_%
HAR112_I_a_%
HAR113_I_a_%
HAR114_I_a_%
HAR115_I_a_%
HAR116_I_a_%
HAR117_I_a_%
HAR118_I_a_%
HAR119_I_a_%
HAR120_I_a_%
HAR121_I_a_%
HAR122_I_a_%
HAR123_I_a_%
HAR124_I_a_%
HAR125_I_a_%
HAR126_I_a_%
HAR127_I_a_%
ANG_HAR2_I_a
ANG_HAR3_I_a
ANG_HAR4_I_a
ANG_HAR5_I_a
ANG_HAR6_I_a
ANG_HAR7_I_a
ANG_HAR8_I_a
ANG_HAR9_I_a
ANG_HAR10_I_a
ANG_HAR11_I_a
ANG_HAR12_I_a
ANG_HAR13_I_a
ANG_HAR14_I_a
ANG_HAR15_I_a
ANG_HAR16_I_a
ANG_HAR17_I_a
ANG_HAR18_I_a
ANG_HAR19_I_a
ANG_HAR20_I_a
ANG_HAR21_I_a
ANG_HAR22_I_a
ANG_HAR23_I_a
ANG_HAR24_I_a
ANG_HAR25_I_a
ANG_HAR26_I_a
ANG_HAR27_I_a
ANG_HAR28_I_a
ANG_HAR29_I_a
ANG_HAR30_I_a
ANG_HAR31_I_a
ANG_HAR32_I_a
ANG_HAR33_I_a
ANG_HAR34_I_a
ANG_HAR35_I_a
ANG_HAR36_I_a
ANG_HAR37_I_a
ANG_HAR38_I_a
ANG_HAR39_I_a
ANG_HAR40_I_a
ANG_HAR41_I_a
ANG_HAR42_I_a
ANG_HAR43_I_a
ANG_HAR44_I_a
ANG_HAR45_I_a
ANG_HAR46_I_a
ANG_HAR47_I_a
ANG_HAR48_I_a
ANG_HAR49_I_a
ANG_HAR50_I_a
ANG_HAR51_I_a
ANG_HAR52_I_a
ANG_HAR53_I_a
ANG_HAR54_I_a
ANG_HAR55_I_a
ANG_HAR56_I_a
ANG_HAR57_I_a
ANG_HAR58_I_a
ANG_HAR59_I_a
ANG_HAR60_I_a
ANG_HAR61_I_a
ANG_HAR62_I_a
ANG_HAR63_I_a
ANG_HAR64_I_a
ANG_HAR65_I_a
ANG_HAR66_I_a
ANG_HAR67_I_a
ANG_HAR68_I_a
ANG_HAR69_I_a
ANG_HAR70_I_a
ANG_HAR71_I_a
ANG_HAR72_I_a
ANG_HAR73_I_a
ANG_HAR74_I_a
ANG_HAR75_I_a
ANG_HAR76_I_a
ANG_HAR77_I_a
ANG_HAR78_I_a
ANG_HAR79_I_a
ANG_HAR80_I_a
ANG_HAR81_I_a
ANG_HAR82_I_a
ANG_HAR83_I_a
ANG_HAR84_I_a
ANG_HAR85_I_a
ANG_HAR86_I_a
ANG_HAR87_I_a
ANG_HAR88_I_a
ANG_HAR89_I_a
ANG_HAR90_I_a
ANG_HAR91_I_a
ANG_HAR92_I_a
ANG_HAR93_I_a
ANG_HAR94_I_a
ANG_HAR95_I_a
ANG_HAR96_I_a
ANG_HAR97_I_a
ANG_HAR98_I_a
ANG_HAR99_I_a
ANG_HAR100_I_a
ANG_HAR101_I_a
ANG_HAR102_I_a
ANG_HAR103_I_a
ANG_HAR104_I_a
ANG_HAR105_I_a
ANG_HAR106_I_a
ANG_HAR107_I_a
ANG_HAR108_I_a
ANG_HAR109_I_a
ANG_HAR110_I_a
ANG_HAR111_I_a
ANG_HAR112_I_a
ANG_HAR113_I_a
ANG_HAR114_I_a
ANG_HAR115_I_a
ANG_HAR116_I_a
ANG_HAR117_I_a
ANG_HAR118_I_a
ANG_HAR119_I_a
ANG_HAR120_I_a
ANG_HAR121_I_a
ANG_HAR122_I_a
ANG_HAR123_I_a
ANG_HAR124_I_a
ANG_HAR125_I_a
ANG_HAR126_I_a
ANG_HAR127_I_a
ANG_HAR128_I_a
HAR2_I_b_%
HAR3_I_b_%
HAR4_I_b_%
HAR5_I_b_%
HAR6_I_b_%
HAR7_I_b_%
HAR8_I_b_%
HAR9_I_b_%
HAR10_I_b_%
HAR11_I_b_%
HAR12_I_b_%
HAR13_I_b_%
HAR14_I_b_%
HAR15_I_b_%
HAR16_I_b_%
HAR17_I_b_%
HAR18_I_b_%
HAR19_I_b_%
HAR20_I_b_%
HAR21_I_b_%
HAR22_I_b_%
HAR23_I_b_%
HAR24_I_b_%
HAR25_I_b_%
HAR26_I_b_%
HAR27_I_b_%
HAR28_I_b_%
HAR29_I_b_%
HAR30_I_b_%
HAR31_I_b_%
HAR32_I_b_%
HAR33_I_b_%
HAR34_I_b_%
HAR35_I_b_%
HAR36_I_b_%
HAR37_I_b_%
HAR38_I_b_%
HAR39_I_b_%
HAR40_I_b_%
HAR41_I_b_%
HAR42_I_b_%
HAR43_I_b_%
HAR44_I_b_%
HAR45_I_b_%
HAR46_I_b_%
HAR47_I_b_%
HAR48_I_b_%
HAR49_I_b_%
HAR50_I_b_%
HAR51_I_b_%
HAR52_I_b_%
HAR53_I_b_%
HAR54_I_b_%
HAR55_I_b_%
HAR56_I_b_%
HAR57_I_b_%
HAR58_I_b_%
HAR59_I_b_%
HAR60_I_b_%
HAR61_I_b_%
HAR62_I_b_%
HAR63_I_b_%
HAR64_I_b_%
HAR65_I_b_%
HAR66_I_b_%
HAR67_I_b_%
HAR68_I_b_%
HAR69_I_b_%
HAR70_I_b_%
HAR71_I_b_%
HAR72_I_b_%
HAR73_I_b_%
HAR74_I_b_%
HAR75_I_b_%
HAR76_I_b_%
HAR77_I_b_%
HAR78_I_b_%
HAR79_I_b_%
HAR80_I_b_%
HAR81_I_b_%
HAR82_I_b_%
HAR83_I_b_%
HAR84_I_b_%
HAR85_I_b_%
HAR86_I_b_%
HAR87_I_b_%
HAR88_I_b_%
HAR89_I_b_%
HAR90_I_b_%
HAR91_I_b_%
HAR92_I_b_%
HAR93_I_b_%
HAR94_I_b_%
HAR95_I_b_%
HAR96_I_b_%
HAR97_I_b_%
HAR98_I_b_%
HAR99_I_b_%
HAR100_I_b_%
HAR101_I_b_%
HAR102_I_b_%
HAR103_I_b_%
HAR104_I_b_%
HAR105_I_b_%
HAR106_I_b_%
HAR107_I_b_%
HAR108_I_b_%
HAR109_I_b_%
HAR110_I_b_%
HAR111_I_b_%
HAR112_I_b_%
HAR113_I_b_%
HAR114_I_b_%
HAR115_I_b_%
HAR116_I_b_%
HAR117_I_b_%
HAR118_I_b_%
HAR119_I_b_%
HAR120_I_b_%
HAR121_I_b_%
HAR122_I_b_%
HAR123_I_b_%
HAR124_I_b_%
HAR125_I_b_%
HAR126_I_b_%
HAR127_I_b_%
ANG_HAR2_I_b
ANG_HAR3_I_b
ANG_HAR4_I_b
ANG_HAR5_I_b
ANG_HAR6_I_b
ANG_HAR7_I_b
ANG_HAR8_I_b
ANG_HAR9_I_b
ANG_HAR10_I_b
ANG_HAR11_I_b
ANG_HAR12_I_b
ANG_HAR13_I_b
ANG_HAR14_I_b
ANG_HAR15_I_b
ANG_HAR16_I_b
ANG_HAR17_I_b
ANG_HAR18_I_b
ANG_HAR19_I_b
ANG_HAR20_I_b
ANG_HAR21_I_b
ANG_HAR22_I_b
ANG_HAR23_I_b
ANG_HAR24_I_b
ANG_HAR25_I_b
ANG_HAR26_I_b
ANG_HAR27_I_b
ANG_HAR28_I_b
ANG_HAR29_I_b
ANG_HAR30_I_b
ANG_HAR31_I_b
ANG_HAR32_I_b
ANG_HAR33_I_b
ANG_HAR34_I_b
ANG_HAR35_I_b
ANG_HAR36_I_b
ANG_HAR37_I_b
ANG_HAR38_I_b
ANG_HAR39_I_b
ANG_HAR40_I_b
ANG_HAR41_I_b
ANG_HAR42_I_b
ANG_HAR43_I_b
ANG_HAR44_I_b
ANG_HAR45_I_b
ANG_HAR46_I_b
ANG_HAR47_I_b
ANG_HAR48_I_b
ANG_HAR49_I_b
ANG_HAR50_I_b
ANG_HAR51_I_b
ANG_HAR52_I_b
ANG_HAR53_I_b
ANG_HAR54_I_b
ANG_HAR55_I_b
ANG_HAR56_I_b
ANG_HAR57_I_b
ANG_HAR58_I_b
ANG_HAR59_I_b
ANG_HAR60_I_b
ANG_HAR61_I_b
ANG_HAR62_I_b
ANG_HAR63_I_b
ANG_HAR64_I_b
ANG_HAR65_I_b
ANG_HAR66_I_b
ANG_HAR67_I_b
ANG_HAR68_I_b
ANG_HAR69_I_b
ANG_HAR70_I_b
ANG_HAR71_I_b
ANG_HAR72_I_b
ANG_HAR73_I_b
ANG_HAR74_I_b
ANG_HAR75_I_b
ANG_HAR76_I_b
ANG_HAR77_I_b
ANG_HAR78_I_b
ANG_HAR79_I_b
ANG_HAR80_I_b
ANG_HAR81_I_b
ANG_HAR82_I_b
ANG_HAR83_I_b
ANG_HAR84_I_b
ANG_HAR85_I_b
ANG_HAR86_I_b
ANG_HAR87_I_b
ANG_HAR88_I_b
ANG_HAR89_I_b
ANG_HAR90_I_b
ANG_HAR91_I_b
ANG_HAR92_I_b
ANG_HAR93_I_b
ANG_HAR94_I_b
ANG_HAR95_I_b
ANG_HAR96_I_b
ANG_HAR97_I_b
ANG_HAR98_I_b
ANG_HAR99_I_b
ANG_HAR100_I_b
ANG_HAR101_I_b
ANG_HAR102_I_b
ANG_HAR103_I_b
ANG_HAR104_I_b
ANG_HAR105_I_b
ANG_HAR106_I_b
ANG_HAR107_I_b
ANG_HAR108_I_b
ANG_HAR109_I_b
ANG_HAR110_I_b
ANG_HAR111_I_b
ANG_HAR112_I_b
ANG_HAR113_I_b
ANG_HAR114_I_b
ANG_HAR115_I_b
ANG_HAR116_I_b
ANG_HAR117_I_b
ANG_HAR118_I_b
ANG_HAR119_I_b
ANG_HAR120_I_b
ANG_HAR121_I_b
ANG_HAR122_I_b
ANG_HAR123_I_b
ANG_HAR124_I_b
ANG_HAR125_I_b
ANG_HAR126_I_b
ANG_HAR127_I_b
HAR2_I_c_%
HAR3_I_c_%
HAR4_I_c_%
HAR5_I_c_%
HAR6_I_c_%
HAR7_I_c_%
HAR8_I_c_%
HAR9_I_c_%
HAR10_I_c_%
HAR11_I_c_%
HAR12_I_c_%
HAR13_I_c_%
HAR14_I_c_%
HAR15_I_c_%
HAR16_I_c_%
HAR17_I_c_%
HAR18_I_c_%
HAR19_I_c_%
HAR20_I_c_%
HAR21_I_c_%
HAR22_I_c_%
HAR23_I_c_%
HAR24_I_c_%
HAR25_I_c_%
HAR26_I_c_%
HAR27_I_c_%
HAR28_I_c_%
HAR29_I_c_%
HAR30_I_c_%
HAR31_I_c_%
HAR32_I_c_%
HAR33_I_c_%
HAR34_I_c_%
HAR35_I_c_%
HAR36_I_c_%
HAR37_I_c_%
HAR38_I_c_%
HAR39_I_c_%
HAR40_I_c_%
HAR41_I_c_%
HAR42_I_c_%
HAR43_I_c_%
HAR44_I_c_%
HAR45_I_c_%
HAR46_I_c_%
HAR47_I_c_%
HAR48_I_c_%
HAR49_I_c_%
HAR50_I_c_%
HAR51_I_c_%
HAR52_I_c_%
HAR53_I_c_%
HAR54_I_c_%
HAR55_I_c_%
HAR56_I_c_%
HAR57_I_c_%
HAR58_I_c_%
HAR59_I_c_%
HAR60_I_c_%
HAR61_I_c_%
HAR62_I_c_%
HAR63_I_c_%
HAR64_I_c_%
HAR65_I_c_%
HAR66_I_c_%
HAR67_I_c_%
HAR68_I_c_%
HAR69_I_c_%
HAR70_I_c_%
HAR71_I_c_%
HAR72_I_c_%
HAR73_I_c_%
HAR74_I_c_%
HAR75_I_c_%
HAR76_I_c_%
HAR77_I_c_%
HAR78_I_c_%
HAR79_I_c_%
HAR80_I_c_%
HAR81_I_c_%
HAR82_I_c_%
HAR83_I_c_%
HAR84_I_c_%
HAR85_I_c_%
HAR86_I_c_%
HAR87_I_c_%
HAR88_I_c_%
HAR89_I_c_%
HAR90_I_c_%
HAR91_I_c_%
HAR92_I_c_%
HAR93_I_c_%
HAR94_I_c_%
HAR95_I_c_%
HAR96_I_c_%
HAR97_I_c_%
HAR98_I_c_%
HAR99_I_c_%
HAR100_I_c_%
HAR101_I_c_%
HAR102_I_c_%
HAR103_I_c_%
HAR104_I_c_%
HAR105_I_c_%
HAR106_I_c_%
HAR107_I_c_%
HAR108_I_c_%
HAR109_I_c_%
HAR110_I_c_%
HAR111_I_c_%
HAR112_I_c_%
HAR113_I_c_%
HAR114_I_c_%
HAR115_I_c_%
HAR116_I_c_%
HAR117_I_c_%
HAR118_I_c_%
HAR119_I_c_%
HAR120_I_c_%
HAR121_I_c_%
HAR122_I_c_%
HAR123_I_c_%
HAR124_I_c_%
HAR125_I_c_%
HAR126_I_c_%
HAR127_I_c_%
ANG_HAR2_I_c
ANG_HAR3_I_c
ANG_HAR4_I_c
ANG_HAR5_I_c
ANG_HAR6_I_c
ANG_HAR7_I_c
ANG_HAR8_I_c
ANG_HAR9_I_c
ANG_HAR10_I_c
ANG_HAR11_I_c
ANG_HAR12_I_c
ANG_HAR13_I_c
ANG_HAR14_I_c
ANG_HAR15_I_c
ANG_HAR16_I_c
ANG_HAR17_I_c
ANG_HAR18_I_c
ANG_HAR19_I_c
ANG_HAR20_I_c
ANG_HAR21_I_c
ANG_HAR22_I_c
ANG_HAR23_I_c
ANG_HAR24_I_c
ANG_HAR25_I_c
ANG_HAR26_I_c
ANG_HAR27_I_c
ANG_HAR28_I_c
ANG_HAR29_I_c
ANG_HAR30_I_c
ANG_HAR31_I_c
ANG_HAR32_I_c
ANG_HAR33_I_c
ANG_HAR34_I_c
ANG_HAR35_I_c
ANG_HAR36_I_c
ANG_HAR37_I_c
ANG_HAR38_I_c
ANG_HAR39_I_c
ANG_HAR40_I_c
ANG_HAR41_I_c
ANG_HAR42_I_c
ANG_HAR43_I_c
ANG_HAR44_I_c
ANG_HAR45_I_c
ANG_HAR46_I_c
ANG_HAR47_I_c
ANG_HAR48_I_c
ANG_HAR49_I_c
ANG_HAR50_I_c
ANG_HAR51_I_c
ANG_HAR52_I_c
ANG_HAR53_I_c
ANG_HAR54_I_c
ANG_HAR55_I_c
ANG_HAR56_I_c
ANG_HAR57_I_c
ANG_HAR58_I_c
ANG_HAR59_I_c
ANG_HAR60_I_c
ANG_HAR61_I_c
ANG_HAR62_I_c
ANG_HAR63_I_c
ANG_HAR64_I_c
ANG_HAR65_I_c
ANG_HAR66_I_c
ANG_HAR67_I_c
ANG_HAR68_I_c
ANG_HAR69_I_c
ANG_HAR70_I_c
ANG_HAR71_I_c
ANG_HAR72_I_c
ANG_HAR73_I_c
ANG_HAR74_I_c
ANG_HAR75_I_c
ANG_HAR76_I_c
ANG_HAR77_I_c
ANG_HAR78_I_c
ANG_HAR79_I_c
ANG_HAR80_I_c
ANG_HAR81_I_c
ANG_HAR82_I_c
ANG_HAR83_I_c
ANG_HAR84_I_c
ANG_HAR85_I_c
ANG_HAR86_I_c
ANG_HAR87_I_c
ANG_HAR88_I_c
ANG_HAR89_I_c
ANG_HAR90_I_c
ANG_HAR91_I_c
ANG_HAR92_I_c
ANG_HAR93_I_c
ANG_HAR94_I_c
ANG_HAR95_I_c
ANG_HAR96_I_c
ANG_HAR97_I_c
ANG_HAR98_I_c
ANG_HAR99_I_c
ANG_HAR100_I_c
ANG_HAR101_I_c
ANG_HAR102_I_c
ANG_HAR103_I_c
ANG_HAR104_I_c
ANG_HAR105_I_c
ANG_HAR106_I_c
ANG_HAR107_I_c
ANG_HAR108_I_c
ANG_HAR109_I_c
ANG_HAR110_I_c
ANG_HAR111_I_c
ANG_HAR112_I_c
ANG_HAR113_I_c
ANG_HAR114_I_c
ANG_HAR115_I_c
ANG_HAR116_I_c
ANG_HAR117_I_c
ANG_HAR118_I_c
ANG_HAR119_I_c
ANG_HAR120_I_c
ANG_HAR121_I_c
ANG_HAR122_I_c
ANG_HAR123_I_c
ANG_HAR124_I_c
ANG_HAR125_I_c
ANG_HAR126_I_c
ANG_HAR127_I_c

## analysisNames
analysisId | analysisUnitId | analysisName
1 | 1 | three_phase_realtime
2 | 1 | three_phase_energy_demand
3 | 1 | three_phase_thd
4 | 1 | three_phase_harmonics
5 | 1 | three_phase_sequence

## applications
appId | appName | isTimer | groupId | interval | isEnable | jsonConfig | appType
1 | north | FALSE | 4 | 0 | TRUE | "" | 2
2 | alarm | FALSE | 0 | 0 | TRUE | "" | 2
3 | datalog1 | TRUE | 1 | 3000 | TRUE | "" | 1
4 | datalog2 | TRUE | 1 | 3000 | TRUE | "" | 1
5 | datalog3 | TRUE | 1 | 3000 | TRUE | "" | 1
6 | datalog4 | TRUE | 1 | 3000 | TRUE | "" | 1
7 | trendlogreal | TRUE | 2 | 5000 | TRUE | "" | 1
8 | trendlogenergy | TRUE | 3 | 5000 | TRUE | "" | 1
9 | GeneralSetting | FALSE | 5 | 0 | TRUE | "" | 2
10 | realtime_system | FALSE | 6 | 0 | TRUE | "" | 2
11 | realtime_channel | FALSE | 7 | 0 | TRUE | "" | 2
12 | energy_system | FALSE | 8 | 0 | TRUE | "" | 2
13 | energy_channel | FALSE | 9 | 0 | TRUE | "" | 2
14 | thd_system | FALSE | 10 | 0 | TRUE | "" | 2
15 | thd_channel | FALSE | 11 | 0 | TRUE | "" | 2
16 | demand_system | FALSE | 12 | 0 | TRUE | "" | 2
17 | demand_channel | FALSE | 13 | 0 | TRUE | "" | 2
18 | acucloud | TRUE | 20 | 5000 | TRUE | "" | 1
19 | mqtt | TRUE | 25 | 5000 | TRUE | "" | 1
20 | snmp | TRUE | 21 | 5000 | TRUE | "" | 1
21 | bacnet | TRUE | 21 | 5000 | TRUE | "" | 1

## groups
groupId | groupType | paramCount
1 | datalog
2 | trendreal
3 | trendenergy
4 | north
5 | deviceSetting_General
6 | realtime_system
7 | realtime_channel
8 | energy_system
9 | energy_channel
10 | thd_system
11 | thd_channel
12 | demand_system
13 | demand_channel
14 | realtimeRange
15 | demandRange
16 | energyRange
17 | thdRange
18 | harmonicsRange
19 | sequenceRange
20 | haveEnergy |  | datalog_range,acucloud_range,mqtt_range,bacnet_range
21 | haveNoEnergy |  | alarm_range,snmp_range
22 | datalogRange
23 | mqttRange
24 | alarm_range
25 | mqtt
26 | alarm

## deviceTemplateInfo
label | description | version | firmwareVersion | deviceType | protocol
AcuRev-2100 | AcuRev-2100 three-phase AC meter | v1.00p01 | v6.27 | threePhaseACMeter | { "type": "Modbus", "transports": ["modbus-tcp", "modbus-rtu"] }