## Alarm setting
Alarm Enable | Alarm Channel | Parameter 1 index | Parameter 1 Logic | Parameter 1 Pickup Value | Parameter 1 Pickup Delay | Parameter 1 Dropout Value | Parameter 1 Dropout Delay | Channel Logic | Parameter 2 index | Parameter 2 Logic | Parameter 2 Pickup Value | Parameter 2 Pickup Delay | Parameter 2 Dropout Value | Parameter 2 Dropout Delay | DO selection | Parameter 1 Start(Dec) | Parameter 2 Start(Dec)
Enable | 1 | Input Channel 1 Current | > | 4 | 5000 | 3 | 5000 | && | Input Channel 2 Current | > | 4 | 5000 | 3 | 5000 | 1
Enable | 2 | Phase A Current | < | 8 | 5000 | 16 | 5000 | ¦¦ | Phase B Current | < | 8 | 5000 | 16 | 5000 | 0
Enable | 3 | Phase A Line-to-Neutral Voltage | > | 120 | 5000 | 110 | 5000 | && | Phase B Line-to-Neutral Voltage | > | 120 | 5000 | 110 | 5000 | 0
Enable | 4 | Phase B Line-to-Neutral Voltage | < | 80 | 2000 | 100 | 2000 | Disable | Phase C Line-to-Neutral Voltage | < | 80 | 2000 | 100 | 2000 | 0
Disable | 5 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 6 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 7 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 8 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 9 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 10 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 11 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 12 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 13 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 14 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 15 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 16 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 17 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 18 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 19 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0
Disable | 20 | DI1 | Disable | 0 | 0 | 0 | 0 | Disable | DI1 | Disable | 0 | 0 | 0 | 0 | 0

## Alarm Logic check
check_Alarm_channel | target_status | Phase_A_Voltage | Phase_B_Voltage | Phase_C_Voltage | Phase_A_Current | Phase_B_Current | Phase_C_Current | Va_angle | Vb_angle | Vc_angle | Ia_angle | Ib_angle | Ic_angle | frequency | keep_time(s) | check_result
1 | start | 100 | 100 | 100 | 5 | 5 | 5 | 0 | 240 | 120 | 0 | 240 | 120 | 50 | 10
1 | end | 100 | 100 | 100 | 2 | 2 | 2 | 0 | 240 | 120 | 0 | 240 | 120 | 50 | 10
2 | start | 100 | 100 | 100 | 0.5 | 3 | 3 | 0 | 240 | 120 | 0 | 240 | 120 | 50 | 10
2 | end | 100 | 100 | 100 | 3 | 3 | 3 | 0 | 240 | 120 | 0 | 240 | 120 | 50 | 10
3 | start | 150 | 150 | 150 | 2 | 2 | 2 | 0 | 240 | 120 | 0 | 240 | 120 | 50 | 10
3 | end | 105 | 105 | 105 | 2 | 2 | 2 | 0 | 240 | 120 | 0 | 240 | 120 | 50 | 10
4 | start | 105 | 105 | 60 | 2 | 2 | 2 | 0 | 240 | 120 | 0 | 240 | 120 | 50 | 10
4 | end | 105 | 105 | 105 | 2 | 2 | 2 | 0 | 240 | 120 | 0 | 240 | 120 | 50 | 10

## Alarm Setting Modbus Address
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range
Alarm settings code function : 03H Read, 10H Write
| 0x6000 | 0x6001 | 24576 | 24577 | Enable all alarm | uint32_t | R/W | 2 | Bit 0~19 for alarm channel 1~20 (0: disabled; 1：enabled
| 0x6002 | 0x6002 | 24578 | 24578 | Alarm Channel 1 Logic | uint16_t | R/W | 1 | bit2-0= 000：parameter 1 is not involved in the alert logic calculation bit2-0= 001：parameter 1 is used as the "=" condition in the alert logic calculation bit2-0= 010：parameter 1 is used for the ">" condition in the alert logic calculation bit2-0= 011：parameter 1 is used for the "<" condition in the alert logic calculation bit 5-3 = 000：parameter 2 is not involved in the alert logic calculation bit5-3= 001： parameter 2 is used as the "=" condition in the alert logic calculation bit 5-3 = 010：parameter 2 is used for the ">" condition in the alert logic calculation bit 5-3 =0 11：parameter 2 is used for the "<" condition in the alert logic calculation bit7-6=01：Parameters 1 and 2 have an "&&" relationship in the alert logic calculation bit7-6=10：Parameters 1 and 2 have an "¦¦" relationship in the alert logic calculation
| 0x6003 | 0x6003 | 24579 | 24579 | Alarm channel 1 RO selection | uint16_t | R/W | 1 | 0: no output 1-2: output relay ID
| 0x6004 | 0x6004 | 24580 | 24580 | Alarm channel 1 DO selection | uint16_t | R/W | 1 | 0: no output 1-8: output DO ID
| 0x6005 | 0x6005 | 24581 | 24581 | Alarm channel 1 parameter1 index | uint16_t | R/W | 1 | modbus addr (DI :1-4)、Basic Parameters 、Demand、Power Quality
| 0x6006 | 0x6007 | 24582 | 24583 | Alarm channel 1 parameter1 Pickup Value | float32 | R/W | 2
| 0x6008 | 0x6008 | 24584 | 24584 | Alarm channel 1 parameter1 Pickup Delay | uint16_t | R/W | 1 | 1-65535
| 0x6009 | 0x600A | 24585 | 24586 | Alarm channel 1 parameter1 Dropout Value | float32 | R/W | 2
| 0x600B | 0x600B | 24587 | 24587 | Alarm channel 1 parameter1 Dropout Delay | uint16_t | R/W | 1 | 1-65535
| 0x600C | 0x600C | 24588 | 24588 | Alarm channel 1 parameter2 index | uint16_t | R/W | 1 | modbus addr (DI :1-4)、Basic Parameters 、Demand、Power Quality
| 0x600D | 0x600E | 24589 | 24590 | Alarm channel 1 parameter2 Pickup Value | float32 | R/W | 2
| 0x600F | 0x600F | 24591 | 24591 | Alarm channel 1 parameter2 Pickup Delay | uint16_t | R/W | 1
| 0x6010 | 0x6011 | 24592 | 24593 | Alarm channel 1 parameter2 Dropout Value | float32 | R/W | 2
| 0x6012 | 0x6012 | 24594 | 24594 | Alarm channel 1 parameter2 Dropout Delay | uint16_t | R/W | 1
|  | 0x6013 | 24595 | 24595 | Alarm Channel 2 Logic |  |  | 1 | Start(Dec) = 相同参数channel1 Start(Dec) + Alarm configure 长度

## Alarm Reading Modbus Address
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range
Alarm Log Read Window
Data Format | 0x6200 | 0x6201 | 25088 | 25089 | The alarm status of each alarm channel | uint32_t | R | 2 | bit0-bit019：0->Alarm release 1:Alarm activation
| 0x6202 | 0x6202 | 25090 | 25090 | the index of the Alarm Log | uint16_t | R | 1 | 1-200
| 0x6203 | 0x6203 | 25091 | 25091 | Number of the Alarm Log | uint16_t | R | 1 | Alarm Log already occurred Count 0：Empty
| 0x6204 | 0x6204 | 25092 | 25092 | The first index of the alarm Log will be read | uint16_t | R/W | 1 | 1-200
| 0x6205 | 0x6205 | 25093 | 25093 | Read the number of the Alarm Log offset | uint16_t | R/W | 1 | 1--8
| 0x6206 | 0x6206 | 25094 | 25094 | Data state of Alarm Log Window | uint16_t | R | 1 | 0x00: window get data failed; 0x0B: window data effective; 0xFF: window data Busy;
| 0x6207 | 0x627E | 25095 | 25214 | Alarm Log Reading Window | uint16_t | R | 120 | Alarm Log Data
Alarm Log Record Data Format
[5 empty] | Alarm Log ID | uint16_t |  | 1
[5 empty] | Alarm Log Time Stamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) | uint16_t |  | 4
[5 empty] | Alarm Log Monitor ID | uint16_t |  | 1
[5 empty] | Alarm Status | uint16_t |  | 1 | 1:start 0:end 2：configuration change
[5 empty] | Alarm Log Extreme Value 1 | float32 |  | 2
[5 empty] | Alarm Log Extreme Value 2 | float32 |  | 2
[5 empty] | Alarm Log Duration | uint32_t |  | 2
Operations
| 0x1139 | 0x1139 | 4409 | 4409 | Clear alarm Log | uint16_t | W | 1 | 0: None | 0 | 0
1: Clearing