## Real time
Real Time | ID | Name | Description | Object Type | Data type | RW | Unit | Data type | Reg | Start(Dec) | End(Dec)
| 1 | Freq_rms | Frequency | Object Analog Input | float32 | R | Hertz | float32 | 2 | 8192 | 8193
| 2 | Ua_rms | Phase A Voltage | Object Analog Input | float32 | R | Volts | float32 | 2 | 8194 | 8195
| 3 | Ub_rms | Phase B Voltage | Object Analog Input | float32 | R | Volts | float32 | 2 | 8196 | 8197
| 4 | Uc_rms | Phase C Voltage | Object Analog Input | float32 | R | Volts | float32 | 2 | 8198 | 8199
| 5 | Uavg_rms | Phase Average Voltage | Object Analog Input | float32 | R | Volts | float32 | 2 | 8200 | 8201
| 6 | Uab_rms | Line Voltage AB | Object Analog Input | float32 | R | Volts | float32 | 2 | 8202 | 8203
| 7 | Ubc_rms | Line Voltage BC | Object Analog Input | float32 | R | Volts | float32 | 2 | 8204 | 8205
| 8 | Uca_rms | Line Voltage CA | Object Analog Input | float32 | R | Volts | float32 | 2 | 8206 | 8207
| 9 | Ulavg_rms | Average Line Voltage | Object Analog Input | float32 | R | Volts | float32 | 2 | 8208 | 8209
| 10 | UaAng_rms | Phase A Voltage Angle | Object Analog Input | float32 | R | Degrees Phase | float32 | 2 | 8210 | 8211
| 11 | UbAng_rms | Phase B Voltage Angle | Object Analog Input | float32 | R | Degrees Phase | float32 | 2 | 8212 | 8213
| 12 | UcAng_rms | Phase C Voltage Angle | Object Analog Input | float32 | R | Degrees Phase | float32 | 2 | 8214 | 8215
| 13 | Ia_rms | Phase A Current | Object Analog Input | float32 | R | Amperes | float32 | 2 | 8216 | 8217
| 14 | Pa_rms | Phase A Active Power | Object Analog Input | float32 | R | Kilowatts | float32 | 2 | 8218 | 8219
| 15 | Qa_rms | Phase A Reactive Power | Object Analog Input | float32 | R | Kilovolt Amperes Reactive | float32 | 2 | 8220 | 8221
| 16 | Sa_rms | Phase A Apparent Power | Object Analog Input | float32 | R | Kilovolt Amperes | float32 | 2 | 8222 | 8223
| 17 | LNa_rms | Phase A Load Nature(0:Resistive load 1:Capacitive load 2:Inductive load) | Object Analog Input | uint32_t | R | No Units | uint32_t | 2 | 8224 | 8225
| 18 | PFa_rms | Phase A Power Factor | Object Analog Input | float32 | R | Power Factor | float32 | 2 | 8226 | 8227
| 19 | Ib_rms | Phase B Current | Object Analog Input | float32 | R | Amperes | float32 | 2 | 8228 | 8229
| 20 | Pb_rms | Phase B Active Power | Object Analog Input | float32 | R | Kilowatts | float32 | 2 | 8230 | 8231
| 21 | Qb_rms | Phase B Reactive Power | Object Analog Input | float32 | R | Kilovolt Amperes Reactive | float32 | 2 | 8232 | 8233
| 22 | Sb_rms | Phase B Apparent Power | Object Analog Input | float32 | R | Kilovolt Amperes | float32 | 2 | 8234 | 8235
| 23 | LNb_rms | Phase B Load Nature(0:Resistive load 1:Capacitive load 2:Inductive load) | Object Analog Input | uint32_t | R | No Units | uint32_t | 2 | 8236 | 8237
| 24 | PFb_rms | Phase B Power Factor | Object Analog Input | float32 | R | Power Factor | float32 | 2 | 8238 | 8239
| 25 | Ic_rms | Phase C Current | Object Analog Input | float32 | R | Amperes | float32 | 2 | 8240 | 8241
| 26 | Pc_rms | Phase C Active Power | Object Analog Input | float32 | R | Kilowatts | float32 | 2 | 8242 | 8243
| 27 | Qc_rms | Phase C Reactive Power | Object Analog Input | float32 | R | Kilovolt Amperes Reactive | float32 | 2 | 8244 | 8245
| 28 | Sc_rms | Phase C Apparent Power | Object Analog Input | float32 | R | Kilovolt Amperes | float32 | 2 | 8246 | 8247
| 29 | LNc_rms | Phase C Load Nature (0:Resistive load 1:Capacitive load 2:Inductive load) | Object Analog Input | uint32_t | R | No Units | uint32_t | 2 | 8248 | 8249
| 30 | PFc_rms | Phase C Power Factor | Object Analog Input | float32 | R | Power Factor | float32 | 2 | 8250 | 8251
| 31 | Isys_rms | System Average Current | Object Analog Input | float32 | R | Amperes | float32 | 2 | 8252 | 8253
| 32 | Psys_rms | System Active Power | Object Analog Input | float32 | R | Kilowatts | float32 | 2 | 8254 | 8255
| 33 | Qsys_rms | System Reactive Power | Object Analog Input | float32 | R | Kilovolt Amperes Reactive | float32 | 2 | 8256 | 8257
| 34 | Ssys_rms | System Apparent Power | Object Analog Input | float32 | R | Kilovolt Amperes | float32 | 2 | 8258 | 8259
| 35 | LNsys_rms | System Load Nature(0:Resistive load 1:Capacitive load 2:Inductive load) | Object Analog Input | uint32_t | R | No Units | uint32_t | 2 | 8260 | 8261
| 36 | PFsys_rms | System Power Factor | Object Analog Input | float32 | R | Power Factor | float32 | 2 | 8262 | 8263
| 37 | Ichn1_rms | Input Channel 1 Current | Object Analog Input | float32 | R | Amperes | float32 | 2 | 8264 | 8265
| 38 | Pchn1_rms | Input Channel 1 Active Power | Object Analog Input | float32 | R | Kilowatts | float32 | 2 | 8266 | 8267
| 39 | Qchn1_rms | Input Channel 1 Reactive Power | Object Analog Input | float32 | R | Kilovolt Amperes Reactive | float32 | 2 | 8268 | 8269
| 40 | Schn1_rms | Input Channel 1 Apparent Power | Object Analog Input | float32 | R | Kilovolt Amperes | float32 | 2 | 8270 | 8271
| 41 | LNchn1_rms | Input Channel 1 Load Nature (0:Resistive load 1:Capacitive load 2:Inductive load) | Object Analog Input | uint32_t | R | No Units | uint32_t | 2 | 8272 | 8273
| 42 | PFchn1_rms | Input Channel 1 Power Factor | Object Analog Input | float32 | R | Power Factor | float32 | 2 | 8274 | 8275
| 43 | Angchn1_rms | Input Channel 1 Current Phase Angle | Object Analog Input | float32 | R | Degrees Phase | float32 | 2 | 8276 | 8277
.

## Energy
Energy | ID | Name | Description | Object Type | Data type | RW | Unit | Data type | Reg | Start(Dec) | End(Dec)
System Energy | 1 | PaImp_eng | Phase A active energy import | Object Large Analog Value | double | R | Kilowatt Hours | double | 4 | 12288 | 12287
| 2 | PaExp_eng | Phase A active energy export | Object Large Analog Value | double | R | Kilowatt Hours | double | 4 | 12292 | 12291
| 3 | PaNet_eng | Phase A active energy net | Object Large Analog Value | double | R | Kilowatt Hours | double | 4 | 12296 | 12295
| 4 | PaTotal_eng | Phase A active energy total | Object Large Analog Value | double | R | Kilowatt Hours | double | 4 | 12300 | 12299
| 5 | QaImp_eng | Phase A reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive | double | 4 | 12304 | 12303
| 6 | QaExp_eng | Phase A reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive | double | 4 | 12308 | 12307
| 7 | QaNet_eng | Phase A reactive energy net | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive | double | 4 | 12312 | 12311
| 8 | QaTotal_eng | Phase A reactive energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive | double | 4 | 12316 | 12315
| 9 | Sa_eng | Phase A apparent energy | Object Large Analog Value | double | R | Kilovolt Ampere Hours | double | 4 | 12320 | 12319
| 10 | PbImp_eng | Phase B active energy import | Object Large Analog Value | double | R | Kilowatt Hours | double | 4 | 12324 | 12323
| 11 | PbExp_eng | Phase B active energy export | Object Large Analog Value | double | R | Kilowatt Hours | double | 4 | 12328 | 12327
| 12 | PbNet_eng | Phase B active energy net | Object Large Analog Value | double | R | Kilowatt Hours | double | 4 | 12332 | 12331
| 13 | PbTotal_eng | Phase B active energy total | Object Large Analog Value | double | R | Kilowatt Hours | double | 4 | 12336 | 12335
| 14 | QbImp_eng | Phase B reactive energy import | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive | double | 4 | 12340 | 12339
| 15 | QbExp_eng | Phase B reactive energy export | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive | double | 4 | 12344 | 12343
| 16 | QbNet_eng | Phase B reactive energy net | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive | double | 4 | 12348 | 12347
| 17 | QbTotal_eng | Phase B reactive energy total | Object Large Analog Value | double | R | Kilovolt Ampere Hours Reactive | double | 4 | 12352 | 12351
| 18 | Sb_eng | Phase B apparent energy | Object Large Analog Value | double | R | Kilovolt Ampere Hours | double | 4 | 12356 | 12355