## Version history
Version | Changes | Author | Date | Internal Firmware Version | External Firmware Version
v1.01 | 初次定义 1.根据需求规格书定义basic setting、real time、energy、TOU default、TOU setting、TOU reading项内容 | 崔少航/李永 | 2024-09-23 | /
| 增加 Max Demand block | 李永 | 2024-09-25 | /
| 增加alarm、record、waveform | 刘宏波 | 2024-10-08 | /
| 1.修改User Channel Power Quality地址长度 2.修改energy页中net energy的数据类型 | 李永 | 2024-10-09 | /
| 1.修改DIpulse constant数据类型为float; 2.增加DI 脉冲计数 3.增加IO状态读写 4.增加SOE Log、Alarm log 清除功能 | 刘宏波 | 2024-10-12 | /
| 增加information | 李永 | 2024-10-15 | /
| 1、修复basic setting部分地址不连续的问题； 2、在basic setting部分加入device run time和device loadtime地址 | 杨月 | 2024-11-02 | /
| 增加校准系数读写 | 李子鑫 | 2024-11-06 | /
| information中添加Boot version | 唐辉 | 2024-11-12 | /
| 增加DSPphase补偿 | 李子鑫 | 2024-11-12 | /
| 更改information段的定义 | 杨月 | 2024-11-18 | /
| 重新整理 | 唐辉 | 2024-12-12 | /
| 1、Power Quality修改数据类型为Float; 2、Energy修改数据类型为Double; 3、（Power Quality、Energy、Max Demand寄存器地址有变动） | 唐辉 | 2025-02-07 | /
| 1.sheet(Data log And Trend log)中“Data log Reading Window”中： a.增加Read record offset项； b.增加Read record number项; c.增加Read record package offset项; d.增加Read record package number项； 2.sheet(Data log And Trend log)中“Data log Reading Window”中： a.增加 Data log1 record package counter项； b.增加 Data log1 record first package size 项； c.增加 Data log1 record last package size 项； | 王培功 | 2025-02-12 | /
| 1.sheet(Data log And Trend log)中“Data log Reading Window”中： a.增加 Data Log1 current record index 项。 | 王培功 | 2025-02-13 | /
| 1.sheet(Waveform¦PQ Event)中“Waveform Reading Window”中： a.修改读waveform协议。 | 杨月 | 2025-02-14 | /
| 1.sheet(Data log And Trend log)中 “Data log Setting“ 中 a. 增加 Data Log1 Mode3 Start Hour and Min 项 | 王培功 | 2025-02-17 | /
| 1.Sheet "Data log And Trend log" 中 增加 “Datalog Sector” | 王培功 | 2025-03-18 | /
| 在Calibration sheet页添加factory phase、gain、offset calibration result项 | 李永 | 2025-04-15 | v1.01p12
| 1.Sheet "Data log And Trend log" 中 修改 "0x6801 :Data Log1 number of blocks"描述 | 王培功 | 2025-05-20 | v1.01p13
| 修改Serial Number格式 | 唐辉 | 2025-05-26 | /
| PQEvent 、SOE、Alarm 读取LOG添加窗口状态 | 唐辉 | 2025-05-27 | v1.01p14
| Hardware Patch Number寄存器位置调整 | 唐辉 | 2025-06-03 | /
| 修改默认密码为0000，修改默认频率为60HZ | 唐辉 | 2025-06-03 | v1.01p15
| 1、Voltage Sag、Voltage Swell、Voltage Interruption、Current Swell添加Enable寄存器 2、Waveform record parameter setting寄存器起始地址调整 3、Voltage Rated Value取值范围修改 | 唐辉 | 2025-06-13 | v1.01p16
| 1、屏蔽原先接线配置中PT1和PT2，改为Reserve | 唐辉 | 2025-06-17 | v1.01p17
| 修改runtime和loadtime为可读可写 | 唐辉 | 2025-06-19 | /
| 删除ELEMENT_3_WIRE_3_DELTA接线方式 | 唐辉 | 2025-06-23 | /
| 屏蔽原先接线配置中Basic Reading Display format，改为Reserve | 唐辉 | 2025-07-01 | /
| Associate with waveform ID为0表示未产生Waveform | 唐辉 | 2025-07-03 | v1.01p18
| PQEvent 、SOE、Alarm Waveform读取窗口状态修改 | 唐辉 | 2025-07-09 | v1.01p19
| Waveform读取窗口增加frequency字段 | 杨月 | 2025-07-21 | v1.01p20
| Basic Setting添加临时密码寄存器 | 唐辉 | 2025-08-05 | v1.01p22
| Realtime中添加Product ID寄存器 | 唐辉 | 2025-10-31 | /
| Information中重新定义"Customer Type"和"Function Model Type" | 杨月 | 2025-10-31 | v1.01p33_PXB
| 取消"Customer Type"寄存器定义；将0xF052寄存器地址名称改成"Function Model Type" | 杨月 | 2025-11-11 | v1.01p34_PXB
| Basic Setting添加Ethernet Communication Mode | 唐辉 | 2025-11-20 | v1.01p35
| 重新定义Function Model Type的功能，更新此寄存器的配置方法 | 杨月 | 2026-01-06 | v1.01p39_PXB
| 在Waveform Reading Window Data Format中，将reasonMode的高16位用作上传user channel信息 | 杨月 | 2026-01-14 | v1.01p40
v1.02 | 添加Web2 Sheet | 唐辉 | 2026-01-12 | /
| Basic Setting添加device description寄存器 | 唐辉 | 2026-01-12 | v1.02p01
| Do Type添加Manual 模式 | 唐辉 | 2026-01-14 | v1.02p05
| 修改Web 2 Mode Set默认值 | 唐辉 | 2026-01-28 | v1.02p06
| 重新定义“Certification Type”寄存器，Default:0，1：MC认证 | 杨月 | 2026-02-02 | v1.02p07
| 添加PT1 PT2寄存器，实现PT变比可配置功能 | 杨月 | 2026-02-02
v1.03 | 添加User Channel Description | 唐辉 | 2026-04-10 | v1.03p01
| 添加Wrie Check寄存器 | 唐辉 | 2026-04-15 | v1.03p01
| realtime中添加Voltage Phase Order寄存器 | 唐辉 | 2026-04-28 | v1.03p02
| wiring check中添加Voltage 、Voltage Angle 、Current、Current Angle寄存器 | 唐辉 | 2026-04-28 | v1.03p02

## Overview
Block | Sector | Sheet | Start | End | Length(reg num) | Comments
Basic Settings | System、Communication、Time Settings | Basic Settings | 0x1000 | 0x102A | 43
| Metrology Settings | Basic Settings | 0x1040 | 0x10E2 | 163
| Io Settings | Basic Settings | 0x1100 | 0x1129 | 42
| Operations | Basic Settings | 0x1130 | 0x1144 | 21
| User Input Channel Description | Basic Settings | 0x1200 | 0x1277 | 120
Wring Check | Wiring Check | Wiring Check | 0x1300 | 0x13AC | 173
Real Time | System、Input Channel、User Channel Basic Parameters | Real time | 0x2000 | 0x2227 | 552
| Voltage Phase Order | Real time | 0x2228 | 0x2229 | 2
| System、Input Channel、User Channel Demand | Real time | 0x2300 | 0x24DF | 480
| System、Input Channel、User Channel Power Quality | Real time | 0x2600 | 0x2DED | 2030
Energy | System、Input Channel、User Channel Energy | Energy | 0x3000 | 0x359F | 1440
Max Demand | System、Input Channel、User Channel Max Demand | Max Demand | 0x3700 | 0x3BAF | 1200
TOU Default Settings | TOU factory basic default settings | TOU Default Settings | 0x4000 | 0x4010 | 17
| TOU schedule & season & holiday setting | TOU Default Settings | 0x4011 | 0x42DD | 717
| 10years holidy factory default settings | TOU Default Settings | 0x42DE | 0x4373 | 150
TOU Readings | A&B&C&system、Input Channel 、User Channel Current Month Accumulative TOU Energy | TOU Readings | 0x43A0 | 0x452F | 400
| A&B&C&system、Input Channel 、User Channel Previous Month Accumulative TOU Energy | TOU Readings | 0x4530 | 0x46BF | 400
| A&B&C&system、Input Channel 、User Channel Current Month Incremental TOU Energy | TOU Readings | 0x46C0 | 0x484F | 400
| A&B&C&system、Input Channel 、User Channel Previous Month Incremental TOU Energy | TOU Readings | 0x4850 | 0x49DF | 400
| TOU OverFlow flag | TOU Readings | 0x49E0 | 0x49E1 | 2
TOU Settings | Daylight Savings Time Settings | TOU setting | 0x4A00 | 0x4A01 | 2
| Format 1: Fixed Date | TOU setting | 0x4A02 | 0x4A0B | 10
| Format 2: Non Fixed Date | TOU setting | 0x4A0C | 0x4A17 | 12
| TOU basic Setting | TOU setting | 0x4A18 | 0x4A25 | 14
| Season Settings | TOU setting | 0x4A26 | 0x4A49 | 36
| Schedule Settings | TOU setting | 0x4A4A | 0x4C95 | 588
| Holiday Settings | TOU setting | 0x4C96 | 0x4CF2 | 93
| 10 Years Holiday Settings | TOU setting | 0x4CF3 | 0x508A | 920
| Special Weekday Schedule Settings | TOU setting | 0x508B | 0x50EB | 97
MaxMin | Max Value Record | MaxMin | 0x5200 | 0x5763 | 1380
| Min Value Record | MaxMin | 0x5800 | 0x5D63 | 1380
Alarm Record ¦DI¦SOE | Alarm Setting | Alarm Record ¦DI¦SOE | 0x6000 | 0x6155 | 342
| Alarm Log Read | Alarm Record ¦DI¦SOE | 0x6200 | 0x627E | 127
| SOE Log Read | Alarm Record ¦DI¦SOE | 0x6300 | 0x637C | 125
| DI | Alarm Record ¦DI¦SOE | 0x6400 | 0x6407 | 8
Waveform | Power Quality Event setting | Waveform¦PQ Event | 0x6500 | 0x6519 | 26
| Waveform record parameter setting | Waveform¦PQ Event | 0x6570 | 0x6577 | 8
| Waveform Reading Window | Waveform¦PQ Event | 0x6600 | 0x667D | 126
| PQ Event Record Reading Window | Waveform¦PQ Event | 0x6700 | 0x677D | 126
Data log And Trend log | Data log Setting | Data log And Trend log | 0x6800 | 0x6CDB | 1244
| Data log Reading Window | Data log And Trend log | 0x6E00 | 0x6E7E | 127
| Data log Status Reading | Data log And Trend log | 0x6F00 | 0x6F43 | 68
| DataLog Sector | Data log And Trend log | 0x6F4A | 0x6F5D | 20
Information | Firmware Version Info | Information | 0xF000 | 0xF005 | 6
| Bootloader Info | Information | 0xF010 | 0xF017 | 8
| Product Info | Information | 0xF040 | 0xF070 | 49
Calibration | Calibration Commands | Calibration | 0xF204 | 0xF241 | 62
| Calibration OffSet Coef | Calibration | 0xF250 | 0xF285 | 40
| GainCoef(V A/B/C) | Calibration | 0xF286 | 0xF28B | 6
| GainCoef(mA、 mV CT、RCT) | Calibration | 0xF28C | 0xF2BB | 48
| PhaseCoef(50Hz、60Hz) | Calibration | 0xF2BC | 0xF2F1 | 54
DI Status | DI Status | DI Status | 0x0000 | 0x0003 | 4
DO¦RO Status | DO Status | DO Status | 0x0000 | 0x0007 | 8
| RO Status | RO Status | 0x0020 | 0x0021 | 2
Web2 | Eth1 Setting | WEB2 | 0x0100 | 0x010C | 13
| Eth2 Setting | WEB2 | 0x010D | 0x010E | 2
| WIFI Module Setting | WEB2 | 0x010F | 0x0110 | 2
| Operation | WEB2 | 0x0111 | 0x0115 | 6
| Information | WEB2 | 0x0116 | 0x015D | 72

## Basic Setting
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
System Setting
Communication | 0x1000 | 0x1000 | 4096 | 4096 | Password | uint16_t | R/W | 1 | 0-9999 | 0
| 0x1001 | 0x1001 | 4097 | 4097 | Baud Rate | uint16_t | R/W | 1 | 2400\4800\9600\19200\38400\57600\76800\115200(76800 need send 7680 115200need send 11520) | 19200
| 0x1002 | 0x1002 | 4098 | 4098 | Parity | uint16_t | R/W | 1 | 0: even 1: odd 2: None2 3: None1 | 3: None1
| 0x1003 | 0x1003 | 4099 | 4099 | DHCP enable | uint16_t | R/W | 1 | 0: manual 1: DHCP | 0
| 0x1004 | 0x1004 | 4100 | 4100 | IP address 1st byte IP address 2nd byte | uint8_t | R/W | 1 | 0~255 | 192 168 1 254
| 0x1005 | 0x1005 | 4101 | 4101 | IP address 3rd byte IP address 4th byte | uint8_t | R/W | 1 | 0~255
| 0x1006 | 0x1006 | 4102 | 4102 | Subnet mask 1st byte Subnet mask 2nd byte | uint8_t | R/W | 1 | 0~255 | 255 255 255 0
| 0x1007 | 0x1007 | 4103 | 4103 | Subnet mask 3rd byte Subnet mask 4th byte | uint8_t | R/W | 1 | 0~255
| 0x1008 | 0x1008 | 4104 | 4104 | Gateway 1st byte Gateway 2nd byte | uint8_t | R/W | 1 | 0~255 | 192 168 1 1
| 0x1009 | 0x1009 | 4105 | 4105 | Gateway 3rd byte Gateway 4th byte | uint8_t | R/W | 1 | 0~255
| 0x100A | 0x100A | 4106 | 4106 | DNS primary server 1st byte DNS primary server 2nd byte | uint8_t | R/W | 1 | 0~255 | 8 8 8 8
| 0x100B | 0x100B | 4107 | 4107 | DNS primary server 3rd byte DNS primary server 4th byte | uint8_t | R/W | 1 | 0~255
| 0x100C | 0x100C | 4108 | 4108 | DNS secondary server 1st byte DNS secondary server 2nd byte | uint8_t | R/W | 1 | 0~255 | 8.8.4.4
| 0x100D | 0x100D | 4109 | 4109 | DNS secondary server 3rd byte DNS secondary server 4th byte | uint8_t | R/W | 1 | 0~255
| 0x100E | 0x100E | 4110 | 4110 | Modbus Slave ID | uint16_t | R/W | 1 | 1-247, used for both Modbus RTU and TCP | 1
| 0x100F | 0x100F | 4111 | 4111 | RS485 protocol | uint16_t | R/W | 1 | 0: disable 1: Modbus RTU 2: BACnet MS/TP | 1
| 0x1010 | 0x1010 | 4112 | 4112 | Modbus TCP Enable | uint16_t | R/W | 1 | 0: disable 1: enable | 1
| 0x1011 | 0x1011 | 4113 | 4113 | Modbus TCP port | uint16_t | R/W | 1 | 1-65534 | 502
| 0x1012 | 0x1012 | 4114 | 4114 | BACnet MS/TP Meter address | uint16_t | R/W | 1 | 1 - 127 | 1
| 0x1013 | 0x1013 | 4115 | 4115 | BACnet MS/TP Maximum number of message frames | uint16_t | R/W | 1 | 1 - 255 | 255
| 0x1014 | 0x1015 | 4116 | 4117 | BACnet MS/TP ID | uint32_t | R/W | 2 | 1 - 4194303(0x3FFFFF) | 1
| 0x1016 | 0x1016 | 4118 | 4118 | BACnet MS/TP Database Revision | uint16_t | R | 1 | 0 - 65535(0xFFFF) | 0
| 0x1017 | 0x1017 | 4119 | 4119 | LCD Backlight Time | uint16_t | R/W | 1 | 0-120 minute | 1
| 0x1018 | 0x1019 | 4120 | 4121 | Device run time | uint32_t | R/W | 2 | uint in second | 0
| 0x101A | 0x101B | 4122 | 4123 | Device load time | uint32_t | R/W | 2 | uint in second | 0
| 0x101C | 0x101C | 4124 | 4124 | MaxDemand Clear Mode | uint16_t | R/W | 1 | 0：Manual Mode 1：Automatic Mode 2：Disable | 0
| 0x101D | 0x101E | 4125 | 4126 | MaxDemand Clear Date Setting | uint8_t | R/W | 2 | ( day:uint8_t , hour:uint8_t, min:uint8_t , sec: uint8_t) | day: 1 hour: 0 min: 0 sec: 0
| 0x101F | 0x101F | 4127 | 4127 | MaxDemand Clear Total Count | uint16_t | R | 1 | 0-65535 | 0
| 0x1020 | 0x1022 | 4128 | 4130 | Timestamp of the most recent MaxDemand Clear | uint8_t | R | 3 | (year：uint8_t、month：uint8_t、day:uint8_t、hour:uint8_t、min:uint8_t、sec：uint8_t) | 0
| 0x1023 | 0x1023 | 4131 | 4131 | Non-standard Seal Parameter Select | uint16_t | R/W | 1 | bit0-4 (0 :NON bit0:RS485 Setting bit1:Ethernet Setting bit2: protocol Setting bit3:Clear Loadtime bit4: Clear Runtime) | 0
| 0x1024 | 0x1024 | 4132 | 4132 | Week | uint16_t | R/W | 1 | 1~7 | 1
| 0x1025 | 0x1025 | 4133 | 4133 | Year | uint16_t | R/W | 1 | 2000~2099 | 2024
| 0x1026 | 0x1026 | 4134 | 4134 | Month | uint16_t | R/W | 1 | 1~12 | 1
| 0x1027 | 0x1027 | 4135 | 4135 | Day | uint16_t | R/W | 1 | 1~31 | 1
| 0x1028 | 0x1028 | 4136 | 4136 | Hour | uint16_t | R/W | 1 | 0~23 | 0
| 0x1029 | 0x1029 | 4137 | 4137 | Minute | uint16_t | R/W | 1 | 0~59 | 0
| 0x102A | 0x102A | 4138 | 4138 | Second | uint16_t | R/W | 1 | 0~59 | 0
| 0x102B | 0x102B | 4139 | 4139 | TempPassword | uint16_t | R | 1 | 0-9999
| 0x102C | 0x102C | 4140 | 4140 | Ethernet Communication Mode | uint16_t | R/W | 1 | 0:RSTP Enable 1:Dual ETH (No RSTP) /*RSTP Disable ,ETH1 Enable,ETH2 Enable*/ 2:Single ETH (No RSTP) /*RSTP Disable ,ETH1 Enable,ETH2 Disable*/ | 0
| 0x102D | 0x103B | 4141 | 4155 | Device Description | uint8_t | R/W | 15 | ASCII string, 30 bytes (15 registers)
60
Metrology Settings
| 0x1040 | 0x1040 | 4160 | 4160 | Sealing Status | uint16_t | R | 1 | sealed: 0x0A unsealed: 0
| 0x1041 | 0x1041 | 4161 | 4161 | Frequency Selection | uint16_t | R/W | 1 | 0: 50Hz 1: 60Hz | 1
| 0x1042 | 0x1042 | 4162 | 4162 | Service Configuration | uint16_t | R/W | 1 | 0: ELEMENT_1_WIRE_2 1: ELEMENT_2_WIRE_3_PHASE_1 2: ELEMENT_2_WIRE_3_DELTA 3: ELEMENT_2_WIRE_3_NETWORK 4: ELEMENT_3_WIRE_4_Y | 4
| 0x1043 | 0x1044 | 4163 | 4164 | PT1 | uint32_t |  | 2 | 50 - 1000000 | 480
| 0x1045 | 0x1045 | 4165 | 4165 | PT2 | uint16_t |  | 1 | 50 - 830 | 480
| 0x1046 | 0x1046 | 4166 | 4166 | channel 1 input wiring ID | uint16_t | R/W | 1 | 1~24 | 1
| 0x1047 | 0x1047 | 4167 | 4167 | channel 1 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1048 | 0x1048 | 4168 | 4168 | channel 1 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1049 | 0x1049 | 4169 | 4169 | channel 1 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x104A | 0x104A | 4170 | 4170 | channle 1 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0
| 0x104B | 0x104B | 4171 | 4171 | channel 2 input wiring | uint16_t | R/W | 1 | 1~24 | 2
| 0x104C | 0x104C | 4172 | 4172 | channel 2 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x104D | 0x104D | 4173 | 4173 | channel 2 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x104E | 0x104E | 4174 | 4174 | channel 2 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x104F | 0x104F | 4175 | 4175 | channel 2 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1
| 0x1050 | 0x1050 | 4176 | 4176 | channel 3 input wiring | uint16_t | R/W | 1 | 1~24 | 3
| 0x1051 | 0x1051 | 4177 | 4177 | channel 3 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1052 | 0x1052 | 4178 | 4178 | channel 3 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1053 | 0x1053 | 4179 | 4179 | channel 3 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1054 | 0x1054 | 4180 | 4180 | channel 3 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2
| 0x1055 | 0x1055 | 4181 | 4181 | channel 4 input wiring | uint16_t | R/W | 1 | 1~24 | 4
| 0x1056 | 0x1056 | 4182 | 4182 | channel 4 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1057 | 0x1057 | 4183 | 4183 | channel 4 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1058 | 0x1058 | 4184 | 4184 | channel 4 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1059 | 0x1059 | 4185 | 4185 | channel 4 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0
| 0x105A | 0x105A | 4186 | 4186 | channel 5 input wiring | uint16_t | R/W | 1 | 1~24 | 5
| 0x105B | 0x105B | 4187 | 4187 | channel 5 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x105C | 0x105C | 4188 | 4188 | channel 5 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x105D | 0x105D | 4189 | 4189 | channel 5 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x105E | 0x105E | 4190 | 4190 | channel 5 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1
| 0x105F | 0x105F | 4191 | 4191 | channel 6 input wiring | uint16_t | R/W | 1 | 1~24 | 6
| 0x1060 | 0x1060 | 4192 | 4192 | channel 6 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1061 | 0x1061 | 4193 | 4193 | channel 6 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1062 | 0x1062 | 4194 | 4194 | channel 6 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1063 | 0x1063 | 4195 | 4195 | channel 6 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2
| 0x1064 | 0x1064 | 4196 | 4196 | channel 7 input wiring | uint16_t | R/W | 1 | 1~24 | 7
| 0x1065 | 0x1065 | 4197 | 4197 | channel 7 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1066 | 0x1066 | 4198 | 4198 | channel 7 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1067 | 0x1067 | 4199 | 4199 | channel 7 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1068 | 0x1068 | 4200 | 4200 | channel 7 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0
| 0x1069 | 0x1069 | 4201 | 4201 | channel 8 input wiring | uint16_t | R/W | 1 | 1~24 | 8
| 0x106A | 0x106A | 4202 | 4202 | channel 8 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x106B | 0x106B | 4203 | 4203 | channel 8 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x106C | 0x106C | 4204 | 4204 | channel 8 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x106D | 0x106D | 4205 | 4205 | channel 8 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1
| 0x106E | 0x106E | 4206 | 4206 | channel 9 input wiring | uint16_t | R/W | 1 | 1~24 | 9
| 0x106F | 0x106F | 4207 | 4207 | channel 9 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1070 | 0x1070 | 4208 | 4208 | channel 9 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1071 | 0x1071 | 4209 | 4209 | channel 9 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1072 | 0x1072 | 4210 | 4210 | channel 9 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2
| 0x1073 | 0x1073 | 4211 | 4211 | channel 10 input wiring | uint16_t | R/W | 1 | 1~24 | 10
| 0x1074 | 0x1074 | 4212 | 4212 | channel 10 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1075 | 0x1075 | 4213 | 4213 | channel 10 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1076 | 0x1076 | 4214 | 4214 | channel 10 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1077 | 0x1077 | 4215 | 4215 | channel 10 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0
| 0x1078 | 0x1078 | 4216 | 4216 | channel 11 input wiring | uint16_t | R/W | 1 | 1~24 | 11
| 0x1079 | 0x1079 | 4217 | 4217 | channel 11 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x107A | 0x107A | 4218 | 4218 | channel 11 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x107B | 0x107B | 4219 | 4219 | channel 11 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x107C | 0x107C | 4220 | 4220 | channel 11 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1
| 0x107D | 0x107D | 4221 | 4221 | channel 12 input wiring | uint16_t | R/W | 1 | 1~24 | 12
| 0x107E | 0x107E | 4222 | 4222 | channel 12 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x107F | 0x107F | 4223 | 4223 | channel 12 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1080 | 0x1080 | 4224 | 4224 | channel 12 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1081 | 0x1081 | 4225 | 4225 | channel 12 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2
| 0x1082 | 0x1082 | 4226 | 4226 | channel 13 input wiring | uint16_t | R/W | 1 | 1~24 | 13
| 0x1083 | 0x1083 | 4227 | 4227 | channel 13 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1084 | 0x1084 | 4228 | 4228 | channel 13 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1085 | 0x1085 | 4229 | 4229 | channel 13 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1086 | 0x1086 | 4230 | 4230 | channel 13 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0
| 0x1087 | 0x1087 | 4231 | 4231 | channel 14 input wiring | uint16_t | R/W | 1 | 1~24 | 14
| 0x1088 | 0x1088 | 4232 | 4232 | channel 14 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1089 | 0x1089 | 4233 | 4233 | channel 14 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x108A | 0x108A | 4234 | 4234 | channel 14 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x108B | 0x108B | 4235 | 4235 | channel 14 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1
| 0x108C | 0x108C | 4236 | 4236 | channel 15 input wiring | uint16_t | R/W | 1 | 1~24 | 15
| 0x108D | 0x108D | 4237 | 4237 | channel 15 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x108E | 0x108E | 4238 | 4238 | channel 15 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x108F | 0x108F | 4239 | 4239 | channel 15 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1090 | 0x1090 | 4240 | 4240 | channel 15 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2
| 0x1091 | 0x1091 | 4241 | 4241 | channel 16 input wiring | uint16_t | R/W | 1 | 1~24 | 16
| 0x1092 | 0x1092 | 4242 | 4242 | channel 16 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1093 | 0x1093 | 4243 | 4243 | channel 16 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1094 | 0x1094 | 4244 | 4244 | channel 16 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x1095 | 0x1095 | 4245 | 4245 | channel 16 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0
| 0x1096 | 0x1096 | 4246 | 4246 | channel 17 input wiring | uint16_t | R/W | 1 | 1~24 | 17
| 0x1097 | 0x1097 | 4247 | 4247 | channel 17 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x1098 | 0x1098 | 4248 | 4248 | channel 17 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x1099 | 0x1099 | 4249 | 4249 | channel 17 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x109A | 0x109A | 4250 | 4250 | channel 17 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1
| 0x109B | 0x109B | 4251 | 4251 | channel 18 input wiring | uint16_t | R/W | 1 | 1~24 | 18
| 0x109C | 0x109C | 4252 | 4252 | channel 18 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x109D | 0x109D | 4253 | 4253 | channel 18 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x109E | 0x109E | 4254 | 4254 | channel 18 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x109F | 0x109F | 4255 | 4255 | channel 18voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2
| 0x10A0 | 0x10A0 | 4256 | 4256 | channel 19 input wiring | uint16_t | R/W | 1 | 1~24 | 19
| 0x10A1 | 0x10A1 | 4257 | 4257 | channel 19 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x10A2 | 0x10A2 | 4258 | 4258 | channel 19 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x10A3 | 0x10A3 | 4259 | 4259 | channel 19 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x10A4 | 0x10A4 | 4260 | 4260 | channel 19 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0
| 0x10A5 | 0x10A5 | 4261 | 4261 | channel 20 input wiring | uint16_t | R/W | 1 | 1~24 | 20
| 0x10A6 | 0x10A6 | 4262 | 4262 | channel 20 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x10A7 | 0x10A7 | 4263 | 4263 | channel 20 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x10A8 | 0x10A8 | 4264 | 4264 | channel 20 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x10A9 | 0x10A9 | 4265 | 4265 | channel 20 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1
| 0x10AA | 0x10AA | 4266 | 4266 | channel 21 input wiring | uint16_t | R/W | 1 | 1~24 | 21
| 0x10AB | 0x10AB | 4267 | 4267 | channel 21 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x10AC | 0x10AC | 4268 | 4268 | channel 21 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x10AD | 0x10AD | 4269 | 4269 | channel 21 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x10AE | 0x10AE | 4270 | 4270 | channel 21 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2
| 0x10AF | 0x10AF | 4271 | 4271 | channel 22 input wiring | uint16_t | R/W | 1 | 1~24 | 22
| 0x10B0 | 0x10B0 | 4272 | 4272 | channel 22 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x10B1 | 0x10B1 | 4273 | 4273 | channel 22 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x10B2 | 0x10B2 | 4274 | 4274 | channel 22 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x10B3 | 0x10B3 | 4275 | 4275 | channel 22 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0
| 0x10B4 | 0x10B4 | 4276 | 4276 | channel 23 input wiring | uint16_t | R/W | 1 | 1~24 | 23
| 0x10B5 | 0x10B5 | 4277 | 4277 | channel 23 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x10B6 | 0x10B6 | 4278 | 4278 | channel 23 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x10B7 | 0x10B7 | 4279 | 4279 | channel 23 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x10B8 | 0x10B8 | 4280 | 4280 | channel 23 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1
| 0x10B9 | 0x10B9 | 4281 | 4281 | channel 24 input wiring | uint16_t | R/W | 1 | 1~24 | 24
| 0x10BA | 0x10BA | 4282 | 4282 | channel 24 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type
| 0x10BB | 0x10BB | 4283 | 4283 | channel 24 primary | uint16_t | R/W | 1 | 1-50000 A | 1000
| 0x10BC | 0x10BC | 4284 | 4284 | channel 24 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0
| 0x10BD | 0x10BD | 4285 | 4285 | channel 24 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2
| 0x10BE | 0x10BF | 4286 | 4287 | user 1 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 1/2/3, 7 0x07
| 0x10C0 | 0x10C1 | 4288 | 4289 | user 2 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 4/5/6, 56 0x38
| 0x10C2 | 0x10C3 | 4290 | 4291 | user 3 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 7/8/9, 448 0x1C0
| 0x10C4 | 0x10C5 | 4292 | 4293 | user 4 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 10/11/12, 3584 0xE00
| 0x10C6 | 0x10C7 | 4294 | 4295 | user 5 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 13/14/15, 28672 0x7000
| 0x10C8 | 0x10C9 | 4296 | 4297 | user 6 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 16/17/18, 229376 0x38000
| 0x10CA | 0x10CB | 4298 | 4299 | user 7 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 19/20/21, 1835008 0x1C0000
| 0x10CC | 0x10CD | 4300 | 4301 | user 8 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 22/23/24, 14680064 0xE00000
| 0x10CE | 0x10CF | 4302 | 4303 | user 9 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | not in use, 0
| 0x10D0 | 0x10D1 | 4304 | 4305 | user 10 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | not in use, 0
| 0x10D2 | 0x10D3 | 4306 | 4307 | user 11 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | not in use, 0
| 0x10D4 | 0x10D5 | 4308 | 4309 | user 12 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | not in use, 0
| 0x10D6 | 0x10D6 | 4310 | 4310 | Demand Method | uint16_t | R/W | 1 | 0: Fixed block, 1: Sliding block | 1
| 0x10D7 | 0x10D7 | 4311 | 4311 | Demand Interval | uint16_t | R/W | 1 | 1~30 minute | 15
| 0x10D8 | 0x10D8 | 4312 | 4312 | Demand update rate | uint16_t | R/W | 1 | 1~30 minute | 1
| 0x10D9 | 0x10D9 | 4313 | 4313 | VAR/PF Convention | uint16_t | R/W | 1 | 0: IEC; 1: IEEE | 0
| 0x10DA | 0x10DA | 4314 | 4314 | Energy Calculation Method | uint16_t | R/W | 1 | fixed to 1: Fundament+Harmonics | 1
| 0x10DB | 0x10DB | 4315 | 4315 | Reactive Power Calculation Method | uint16_t | R/W | 1 | 0: Generic Reactive Power 1: True Reactive Power | 0
| 0x10DC | 0x10DC | 4316 | 4316 | Phase Order | uint16_t | R/W | 1 | 0: ABC 1: ACB | 0
| 0x10DD | 0x10DD | 4317 | 4317 | Energy Reading Display format | uint16_t | R/W | 1 | 0: Primary in 0.1 kWh;1:0.01kWh; 2: Primary in 0.001kWh | 0
| 0x10DE | 0x10DE | 4318 | 4318 | Reserve3 | uint16_t | R/W | 1 |  | 0
| 0x10DF | 0x10E0 | 4319 | 4320 | Energy pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000
| 0x10E1 | 0x10E1 | 4321 | 4321 | Pulse LED width | uint16_t | R/W | 1 | 20~100ms | 100
| 0x10E2 | 0x10E2 | 4322 | 4322 | Pulse LED parameter selection | uint16_t | R/W | 1 | Energy parameter IDs(1-360) | 0 not in use
163
IO Settings
| 0x1100 | 0x1100 | 4352 | 4352 | DO 1 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication 2:Manual | 0
| 0x1101 | 0x1101 | 4353 | 4353 | DO 1 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100
| 0x1102 | 0x1102 | 4354 | 4354 | DO 1 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use
| 0x1103 | 0x1103 | 4355 | 4355 | DO 2 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication 2:Manual | 0
| 0x1104 | 0x1104 | 4356 | 4356 | DO 2 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100
| 0x1105 | 0x1105 | 4357 | 4357 | DO 2 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use
| 0x1106 | 0x1106 | 4358 | 4358 | DO 3 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication 2:Manual | 0
| 0x1107 | 0x1107 | 4359 | 4359 | DO 3 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100
| 0x1108 | 0x1108 | 4360 | 4360 | DO 3 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use
| 0x1109 | 0x1109 | 4361 | 4361 | DO 4 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication 2:Manual | 0
| 0x110A | 0x110A | 4362 | 4362 | DO 4 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100
| 0x110B | 0x110B | 4363 | 4363 | DO 4 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use
| 0x110C | 0x110C | 4364 | 4364 | DO 5 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication 2:Manual | 0
| 0x110D | 0x110D | 4365 | 4365 | DO 5 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100
| 0x110E | 0x110E | 4366 | 4366 | DO 5 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use
| 0x110F | 0x110F | 4367 | 4367 | DO 6 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication 2:Manual | 0
| 0x1110 | 0x1110 | 4368 | 4368 | DO 6 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100
| 0x1111 | 0x1111 | 4369 | 4369 | DO 6 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use
| 0x1112 | 0x1112 | 4370 | 4370 | DO 7 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication 2:Manual | 0
| 0x1113 | 0x1113 | 4371 | 4371 | DO 7 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100
| 0x1114 | 0x1114 | 4372 | 4372 | DO 7 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use
| 0x1115 | 0x1115 | 4373 | 4373 | DO 8 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication 2:Manual | 0
| 0x1116 | 0x1116 | 4374 | 4374 | DO 8 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100
| 0x1117 | 0x1117 | 4375 | 4375 | DO 8 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use
| 0x1118 | 0x1118 | 4376 | 4376 | DI 1 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0
| 0x1119 | 0x111A | 4377 | 4378 | DI 1 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000
| 0x111B | 0x111B | 4379 | 4379 | DI 2 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0
| 0x111C | 0x111D | 4380 | 4381 | DI 2 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000
| 0x111E | 0x111E | 4382 | 4382 | DI 3 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0
| 0x111F | 0x1120 | 4383 | 4384 | DI 3 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000
| 0x1121 | 0x1121 | 4385 | 4385 | DI 4 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0
| 0x1122 | 0x1123 | 4386 | 4387 | DI 4 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000
| 0x1124 | 0x1124 | 4388 | 4388 | RO 1 Type | uint16_t | R/W | 1 | 0: Relay Output 1: Alarm Indication | 0
| 0x1125 | 0x1125 | 4389 | 4389 | RO 1 Control Mode | uint16_t | R/W | 1 | Alarm Indication： 0: Latch 2: Manual Relay Output： 0: Latch 1: Momentary | 0
| 0x1126 | 0x1126 | 4390 | 4390 | RO 1 Pulse Width | uint16_t | R/W | 1 | 20 - 3000 ms | 100
| 0x1127 | 0x1127 | 4391 | 4391 | RO 2 Type | uint16_t | R/W | 1 | 0: Relay 1: Alarm | 0
| 0x1128 | 0x1128 | 4392 | 4392 | RO 2 Control Mode | uint16_t | R/W | 1 | Alarm Indication： 0: Latch 2: Manual Relay Output： 0: Latch 1: Momentary | 0
| 0x1129 | 0x1129 | 4393 | 4393 | RO 2 Pulse Width | uint16_t | R/W | 1 | 20 - 3000 ms | 100
42
Operations | 0x1130 | 0x1130 | 4400 | 4400 | Clear energy | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x1131 | 0x1131 | 4401 | 4401 | Clear Max demand | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x1132 | 0x1132 | 4402 | 4402 | Clear MaxDemand ClearCount and Timestamp | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x1133 | 0x1133 | 4403 | 4403 | Clear max/min | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x1134 | 0x1134 | 4404 | 4404 | Clear device run time | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x1135 | 0x1135 | 4405 | 4405 | Clear load time | uint16_t | W | 1 | 0: None 1: Reset | 0
| 0x1136 | 0x1136 | 4406 | 4406 | Factory reset | uint16_t | W | 1 | 0: None 1: Resetting | 0
| 0x1137 | 0x1137 | 4407 | 4407 | Network reset | uint16_t | W | 1 | 0: None 1: Resetting | 0
| 0x1138 | 0x1138 | 4408 | 4408 | Clear SOE Log | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x1139 | 0x1139 | 4409 | 4409 | Clear alarm Log | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x113A | 0x113A | 4410 | 4410 | Clear PQ event Log | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x113B | 0x113B | 4411 | 4411 | Clear Waveform | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x113C | 0x113C | 4412 | 4412 | Clear Data Log1 | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x113D | 0x113D | 4413 | 4413 | Clear Data Log2 | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x113E | 0x113E | 4414 | 4414 | Clear Data Log3 | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x113F | 0x113F | 4415 | 4415 | Clear Trend Log | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x1140 | 0x1140 | 4416 | 4416 | Clear DI Count | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x1141 | 0x1141 | 4417 | 4417 | Clear Year 10 Holiday Number Setting | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x1142 | 0x1142 | 4418 | 4418 | Restore TOU factory setting | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x1143 | 0x1143 | 4419 | 4419 | Clear TOU Energy | uint16_t | W | 1 | 0: None 1: Clearing | 0
| 0x1144 | 0x1144 | 4420 | 4420 | Device Reboot | uint16_t | W | 1 | 0: None 1: Reset | 0
21
User Input Channel Description
| 0x1200 | 0x1209 | 4608 | 4617 | User Channel 1 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)
| 0x120A | 0x1213 | 4618 | 4627 | User Channel 2 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)
| 0x1214 | 0x121D | 4628 | 4637 | User Channel 3 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)
| 0x121E | 0x1227 | 4638 | 4647 | User Channel 4 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)
| 0x1228 | 0x1231 | 4648 | 4657 | User Channel 5 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)
| 0x1232 | 0x123B | 4658 | 4667 | User Channel 6 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)
| 0x123C | 0x1245 | 4668 | 4677 | User Channel 7 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)
| 0x1246 | 0x124F | 4678 | 4687 | User Channel 8 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)
| 0x1250 | 0x1259 | 4688 | 4697 | User Channel 9 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)
| 0x125A | 0x1263 | 4698 | 4707 | User Channel 10 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)
| 0x1264 | 0x126D | 4708 | 4717 | User Channel 11 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)
| 0x126E | 0x1277 | 4718 | 4727 | User Channel 12 Description | string | R/W | 10 | ASCII string, 20 bytes (10 registers)

## Wiring Check
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Wiring Check | 0x1300 | 0x1300 | 4864 | 4864 | Wire Check Start | uint16_t | R/W | 1 | 0:Idle 1:Start | 0
| 0x1301 | 0x1301 | 4865 | 4865 | Wire Check Status | uint16_t | R | 1 | 0: Not Started 1: In Progress 2: Completed
| 0x1302 | 0x1302 | 4866 | 4866 | Phase Voltage Error Code | uint16_t | R | 1 | Bit0:Voltage terminals Va wiring is missing Bit1:Voltage terminals Vb wiring is missing Bit2:Voltage terminals Vc wiring is missing Bit3:The voltage terminals Va and Vn are reversed. Bit4: The voltage terminals Vb and Vn are reversed. Bit5: The voltage terminals Vc and Vn are reversed. Bit6: Phase error of voltage terminals Vb Bit7: Phase error of voltage terminals Vc Bit8: ABC/ACB sequence is configured incorrectly
| 0x1303 | 0x1303 | 4867 | 4867 | User1 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic (1E2W)： bit0: Current terminals Input Channal 1 wiring is missing Bit1: Current terminals Input Channal 1 positive and negative are reversed Bit2: Current terminals Input Channal 2 wiring is missing Bit3: Current terminals Input Channal 2 positive and negative are reversed Bit4: Current terminals Input Channal 3 wiring is missing Bit5: Current terminals Input Channal 3 positive and negative are reversed
| 0x1304 | 0x1304 | 4868 | 4868 | User2 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic (1E2W)： bit0: Current terminals Input Channal 4 wiring is missing Bit1: Current terminals Input Channal 4 positive and negative inversion Bit2: Current terminals Input Channal 5 wiring is missing Bit3: Current terminals Input Channal 5 positive and negative inversion Bit4: Current terminals Input Channal 6 wiring is missing Bit5: Current terminals Input Channal 6 positive and negative inversion
| 0x1305 | 0x1305 | 4869 | 4869 | User3 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic (1E2W)： bit0: Current terminals Input Channal 7 wiring is missing Bit1: Current terminals Input Channal 7 positive and negative inversion Bit2: Current terminals Input Channal 8 wiring is missing Bit3: Current terminals Input Channal 8 positive and negative inversion Bit4: Current terminals Input Channal 9 wiring is missing Bit5: Current terminals Input Channal 9 positive and negative inversion
| 0x1306 | 0x1306 | 4870 | 4870 | User4 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic (1E2W)： bit0: Current terminals Input Channal 10 wiring is missing Bit1: Current terminals Input Channal 10 positive and negative inversion Bit2: Current terminals Input Channal 11 wiring is missing Bit3: Current terminals Input Channal 11 positive and negative inversion Bit4: Current terminals Input Channal 12 wiring is missing Bit5: Current terminals Input Channal 12 positive and negative inversion
| 0x1307 | 0x1307 | 4871 | 4871 | User5 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic (1E2W)： bit0: Current terminals Input Channal 13 wiring is missing Bit1: Current terminals Input Channal 13 positive and negative inversion Bit2: Current terminals Input Channal 14 wiring is missing Bit3: Current terminals Input Channal 14 positive and negative inversion Bit4: Current terminals Input Channal 15 wiring is missing Bit5: Current terminals Input Channal 15 positive and negative inversion
| 0x1308 | 0x1308 | 4872 | 4872 | User6 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic (1E2W)： bit0: Current terminals Input Channal 16 wiring is missing Bit1: Current terminals Input Channal 16 positive and negative inversion Bit2: Current terminals Input Channal 17 wiring is missing Bit3: Current terminals Input Channal 17 positive and negative inversion Bit4: Current terminals Input Channal 18 wiring is missing Bit5: Current terminals Input Channal 18 positive and negative inversion
| 0x1309 | 0x1309 | 4873 | 4873 | User7 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic (1E2W)： bit0: Current terminals Input Channal 19 wiring is missing Bit1: Current terminals Input Channal 19 positive and negative inversion Bit2: Current terminals Input Channal 20 wiring is missing Bit3: Current terminals Input Channal 20 positive and negative inversion Bit4: Current terminals Input Channal 21 wiring is missing Bit5: Current terminals Input Channal 21 positive and negative inversion
| 0x130A | 0x130A | 4874 | 4874 | User8 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic (1E2W)： bit0: Current terminals Input Channal 22 wiring is missing Bit1: Current terminals Input Channal 22 positive and negative inversion Bit2: Current terminals Input Channal 23 wiring is missing Bit3: Current terminals Input Channal 23 positive and negative inversion Bit4: Current terminals Input Channal 24 wiring is missing Bit5: Current terminals Input Channal 24 positive and negative inversion
| 0x130B | 0x130B | 4875 | 4875 | User9 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic
| 0x130C | 0x130C | 4876 | 4876 | User10 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic
| 0x130D | 0x130D | 4877 | 4877 | User11 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic
| 0x130E | 0x130E | 4878 | 4878 | User12 Phase Current Error Code | uint16_t | R | 1 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic
| 0x130F | 0x1310 | 4879 | 4880 | Phase A Line-to-Neutral / Phase AB Line-to-Line Voltage | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase A Line-to-Neutral Voltage (2E3WDelta)： Phase AB Line-to-Line Voltage
| 0x1311 | 0x1312 | 4881 | 4882 | Phase A Line-to-Neutral / Phase AB Line-to-Line Voltage Phase Angle | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase A Line-to-Neutral Voltage Phase Angle (2E3WDelta)： Phase AB Line-to-Line Voltage Phase Angle
| 0x1313 | 0x1314 | 4883 | 4884 | Phase B Line-to-Neutral /Phase BC Line-to-Line Voltage | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase B Line-to-Neutral Voltage (2E3WDelta)： Phase BC Line-to-Line Voltage
| 0x1315 | 0x1316 | 4885 | 4886 | Phase B Line-to-Neutral / Phase BC Line-to-Line Voltage Phase Angle | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase B Line-to-Neutral Voltage Phase Angle (2E3WDelta)： Phase BC Line-to-Line Voltage Phase Angle
| 0x1317 | 0x1318 | 4887 | 4888 | Phase C Line-to-Neutral / Phase CA Line-to-Line Voltage | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase C Line-to-Neutral Voltage (2E3WDelta)： Phase CA Line-to-Line Voltage
| 0x1319 | 0x131A | 4889 | 4890 | Phase C Line-to-Neutral /Phase CA Line-to-Line Voltage Phase Angle | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase C Line-to-Neutral Voltage Phase Angle (2E3WDelta)： Phase CA Line-to-Line Voltage Phase Angle
| 0x131B | 0x131C | 4891 | 4892 | Voltage Phase Order | uint32_t | R | 2
| 0x131D | 0x131E | 4893 | 4894 | User1 Phase A Curent | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： User1 Phase A Curent (1E2W)： Input Channel 1 Curent
| 0x131F | 0x1320 | 4895 | 4896 | User1 Phase A Curent Angle | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： User1 Phase A Curent Angle (1E2W)： Input Channel 1 Curent Angle
| 0x1321 | 0x1322 | 4897 | 4898 | User1 Phase B Curent | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： User1 Phase B Curent (1E2W)： Input Channel 2 Curent
| 0x1323 | 0x1324 | 4899 | 4900 | User1 Phase B Curent Angle | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： User1 Phase B Curent Angle (1E2W)： Input Channel 2 Curent Angle
| 0x1325 | 0x1326 | 4901 | 4902 | User1 Phase C Curent | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： User1 Phase B Curent (1E2W)： Input Channel 3 Curent
| 0x1327 | 0x1328 | 4903 | 4904 | User1 Phase C Curent Angle | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： User1 Phase C Curent Angle (1E2W)： Input Channel 3 Curent Angle
| 0x1329 | 0x13AC | 4905 | 5036 | User2-User12 Phase Current and Curent Angle | float | R | 132
173

## WEB2
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Eth1 Setting | 0x0100 | 0x0101 | 256 | 257 | Meter Setting Status | uint32_t | R/W | 2 | Bit0:DHCP is setting Bit1:IP Address is setting Bit2:Subnet mask is setting Bit3:Gateway is setting Bit4:DNS1 is setting Bit5:DNS2 is setting Bit6:Device Reboot is setting Bit7:Factory Reset is setting Bit8:Network Reset is setting Bit9:Clock Update Enabe is setting Bit10:Web2 Mode is setting | 0
| 0x0102 | 0x0102 | 258 | 258 | DHCP enable | uint16_t | R/W | 1 | 0: Disable 1: Enable | 0
| 0x0103 | 0x0103 | 259 | 259 | IP address 1st byte IP address 2nd byte | uint8_t | R/W | 1 | 0~255 | 192.168.8.101
| 0x0104 | 0x0104 | 260 | 260 | IP address 3rd byte IP address 4th byte | uint8_t | R/W | 1 | 0~255
| 0x0105 | 0x0105 | 261 | 261 | Subnet mask 1st byte Subnet mask 2nd byte | uint8_t | R/W | 1 | 0~255 | 255 255 255 0
| 0x0106 | 0x0106 | 262 | 262 | Subnet mask 3rd byte Subnet mask 4th byte | uint8_t | R/W | 1 | 0~255
| 0x0107 | 0x0107 | 263 | 263 | Gateway 1st byte Gateway 2nd byte | uint8_t | R/W | 1 | 0~255 | 192.168.8.1
| 0x0108 | 0x0108 | 264 | 264 | Gateway 3rd byte Gateway 4th byte | uint8_t | R/W | 1 | 0~255
| 0x0109 | 0x0109 | 265 | 265 | DNS primary server 1st byte DNS primary server 2nd byte | uint8_t | R/W | 1 | 0~255 | 8.8.8.8
| 0x010A | 0x010A | 266 | 266 | DNS primary server 3rd byte DNS primary server 4th byte | uint8_t | R/W | 1 | 0~255
| 0x010B | 0x010B | 267 | 267 | DNS secondary server 1st byte DNS secondary server 2nd byte | uint8_t | R/W | 1 | 0~255 | 8.8.4.4
| 0x010C | 0x010C | 268 | 268 | DNS secondary server 3rd byte DNS secondary server 4th byte | uint8_t | R/W | 1 | 0~255
Eth2 Setting | 0x010D | 0x010D | 269 | 269 | IP address 1st byte IP address 2nd byte | uint8_t | R/W | 1 | 0~255 | 192 168 1 254
| 0x010E | 0x010E | 270 | 270 | IP address 3rd byte IP address 4th byte | uint8_t | R/W | 1 | 0~255
WIFI Module Setting | 0x010F | 0x010F | 271 | 271 | IP address 1st byte IP address 2nd byte | uint8_t | R/W | 1 | 0~255 | 192 168 1 254
| 0x0110 | 0x0110 | 272 | 272 | IP address 3rd byte IP address 4th byte | uint8_t | R/W | 1 | 0~255
Operation | 0x0111 | 0x0111 | 273 | 273 | Device Reboot | uint16_t | R/W | 1 | 0: None 1: Reboot | 0
| 0x0112 | 0x0112 | 274 | 274 | Factory reset | uint16_t | R/W | 1 | 0: None 1: Reset | 0
| 0x0113 | 0x0113 | 275 | 275 | Network reset | uint16_t | R/W | 1 | 0: None 1: Reset | 0
| 0x0114 | 0x0114 | 276 | 276 | Enable clock synchronization | uint16_t | R/W | 1 | 0: disabe 1: enable | 0
| 0x0115 | 0x0115 | 277 | 277 | System Mode Setting | uint16_t | R/W | 1 | 0：Web Module 1：Gateway | 0
Information | 0x0116 | 0x011D | 278 | 285 | Web2 Firmware version | uint8_t | R/W | 8
| 0x011E | 0x012D | 286 | 301 | Web2 Serial Number | uint8_t | R/W | 16
| 0x012E | 0x013D | 302 | 317 | MAC address(ETH1) | uint8_t | R/W | 16
| 0x013E | 0x014D | 318 | 333 | MAC address(ETH2) | uint8_t | R/W | 16
| 0x014E | 0x015D | 334 | 349 | MAC address(WIFI) | uint8_t | R/W | 16
94

## Real time
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Basic Parameters (code function : 03H Read)
System Basic Parameters | 0x1FFF | 0x1FFF | 8191 | 8191 | Product ID | uint16_t | R | 1 |  | 0x3C08（It is only Eaton that needs this）
| 0x2000 | 0x2001 | 8192 | 8193 | System Frequency | float | R | 2
| 0x2002 | 0x2003 | 8194 | 8195 | Phase A Line-to-Neutral Voltage | float | R | 2
| 0x2004 | 0x2005 | 8196 | 8197 | Phase B Line-to-Neutral Voltage | float | R | 2
| 0x2006 | 0x2007 | 8198 | 8199 | Phase C Line-to-Neutral Voltage | float | R | 2
| 0x2008 | 0x2009 | 8200 | 8201 | Average Line-to-Neutral Voltage | float | R | 2
| 0x200A | 0x200B | 8202 | 8203 | Phase AB Line-to-Line Voltage | float | R | 2
| 0x200C | 0x200D | 8204 | 8205 | Phase BC Line-to-Line Voltage | float | R | 2
| 0x200E | 0x200F | 8206 | 8207 | Phase CA Line-to-Line Voltage | float | R | 2
| 0x2010 | 0x2011 | 8208 | 8209 | Average Line-to-Line Voltage | float | R | 2
| 0x2012 | 0x2013 | 8210 | 8211 | Phase A Line-to-Neutral Voltage Phase Angle(1E_2W、2E_3W_1P、3E_4W_Y、2E_3W_Network) / Phase AB Line-to-Linel Voltage Phase Angle (2E_3W_Delta、 3E_3W_Delta) | float | R | 2
| 0x2014 | 0x2015 | 8212 | 8213 | Phase B Line-to-Neutral Voltage Phase Angle(1E_2W、2E_3W_1P、3E_4W_Y、2E_3W_Network) / PhaseBC Line-to-Linel Voltage Phase Angle (2E_3W_Delta 、3E_3W_Delta) | float | R | 2
| 0x2016 | 0x2017 | 8214 | 8215 | Phase C Line-to-Neutral Voltage Phase Angle(1E_2W、2E_3W_1P、3E_4W_Y、2E_3W_Network) / PhaseCA Line-to-Linel Voltage Phase Angle (2E_3W_Delta 、3E_3W_Delta) | float | R | 2
| 0x2018 | 0x2019 | 8216 | 8217 | Phase A Current | float | R | 2
| 0x201A | 0x201B | 8218 | 8219 | Phase A Active Power | float | R | 2
| 0x201C | 0x201D | 8220 | 8221 | Phase A Reactive Power | float | R | 2
| 0x201E | 0x201F | 8222 | 8223 | Phase A Apparent Power | float | R | 2
| 0x2020 | 0x2021 | 8224 | 8225 | Phase A Load Nature | uint32_t | R | 2
| 0x2022 | 0x2023 | 8226 | 8227 | Phase A Power Factor | float | R | 2
| 0x2024 | 0x2025 | 8228 | 8229 | Phase B Current | float | R | 2
| 0x2026 | 0x2027 | 8230 | 8231 | Phase B Active Power | float | R | 2
| 0x2028 | 0x2029 | 8232 | 8233 | Phase B Reactive Power | float | R | 2
| 0x202A | 0x202B | 8234 | 8235 | Phase B Apparent Power | float | R | 2
| 0x202C | 0x202D | 8236 | 8237 | Phase B Load Nature | uint32_t | R | 2
| 0x202E | 0x202F | 8238 | 8239 | Phase B Power Factor | float | R | 2
| 0x2030 | 0x2031 | 8240 | 8241 | Phase C Current | float | R | 2
| 0x2032 | 0x2033 | 8242 | 8243 | Phase C Active Power | float | R | 2
| 0x2034 | 0x2035 | 8244 | 8245 | Phase C Reactive Power | float | R | 2
| 0x2036 | 0x2037 | 8246 | 8247 | Phase C Apparent Power | float | R | 2
| 0x2038 | 0x2039 | 8248 | 8249 | Phase C Load Nature | uint32_t | R | 2
| 0x203A | 0x203B | 8250 | 8251 | Phase C Power Factor | float | R | 2
| 0x203C | 0x203D | 8252 | 8253 | System Average Current | float | R | 2
| 0x203E | 0x203F | 8254 | 8255 | System Active Power | float | R | 2
| 0x2040 | 0x2041 | 8256 | 8257 | System Reactive Power | float | R | 2
| 0x2042 | 0x2043 | 8258 | 8259 | System Apparent Power | float | R | 2
| 0x2044 | 0x2045 | 8260 | 8261 | System Load Nature | uint32_t | R | 2
| 0x2046 | 0x2047 | 8262 | 8263 | System Power Factor | float | R | 2
input Channel basic parameters | 0x2048 | 0x2049 | 8264 | 8265 | Input Channel 1 Current | float | R | 2
| 0x204A | 0x204B | 8266 | 8267 | Input Channel 1 Active Power | float | R | 2
| 0x204C | 0x204D | 8268 | 8269 | Input Channel 1 Reactive Power | float | R | 2
| 0x204E | 0x204F | 8270 | 8271 | Input Channel 1 Apparent Power | float | R | 2
| 0x2050 | 0x2051 | 8272 | 8273 | Input Channel 1 Load Nature | uint32_t | R | 2
| 0x2052 | 0x2053 | 8274 | 8275 | Input Channel 1 Power Factor | float | R | 2
| 0x2054 | 0x2055 | 8276 | 8277 | Input Channel 1 Current Phase Angle | float | R | 2
| 0x2056 | 0x2197 | 8278 | 8599 | Input Channel 2-24 basic parameters |  | R | 322
User Channel basic parameters | 0x2198 | 0x2199 | 8600 | 8601 | User Channel 1 Current | float | R | 2
| 0x219A | 0x219B | 8602 | 8603 | User Channel 1 Active Power | float | R | 2
| 0x219C | 0x219D | 8604 | 8605 | User Channel 1 Reactive Power | float | R | 2
| 0x219E | 0x219F | 8606 | 8607 | User Channel 1 Apparent Power | float | R | 2
| 0x21A0 | 0x21A1 | 8608 | 8609 | User Channel 1 Load Nature | uint32_t | R | 2
| 0x21A2 | 0x21A3 | 8610 | 8611 | User Channel 1 Power Factor | float | R | 2
| 0x21A4 | 0x2227 | 8612 | 8743 | User Channel 2-12 basic parameters |  | R | 132
| 0x2228 | 0x2229 | 8744 | 8745 | Voltage Phase Order | uint32_t | R | 2 | 0:ABC 1:ACB 2:Error
Demand(code function : 03H Read)
System Demand | 0x2300 | 0x2301 | 8960 | 8961 | Phase A Current Demand | float | R | 2
| 0x2302 | 0x2303 | 8962 | 8963 | Phase A Import Active Power Demand | float | R | 2
| 0x2304 | 0x2305 | 8964 | 8965 | Phase A Export Active Power Demand | float | R | 2
| 0x2306 | 0x2307 | 8966 | 8967 | Phase A Import Reactive Power Demand | float | R | 2
| 0x2308 | 0x2309 | 8968 | 8969 | Phase A Export Reactive Power Demand | float | R | 2
| 0x230A | 0x230B | 8970 | 8971 | Phase A Apparent Power Demand | float | R | 2
| 0x230C | 0x230D | 8972 | 8973 | Phase B Current Demand | float | R | 2
| 0x230E | 0x230F | 8974 | 8975 | Phase B Import Active Power Demand | float | R | 2
| 0x2310 | 0x2311 | 8976 | 8977 | Phase B Export Active Power Demand | float | R | 2
| 0x2312 | 0x2313 | 8978 | 8979 | Phase B Import Reactive Power Demand | float | R | 2
| 0x2314 | 0x2315 | 8980 | 8981 | Phase B Export Reactive Power Demand | float | R | 2
| 0x2316 | 0x2317 | 8982 | 8983 | Phase B Apparent Power Demand | float | R | 2
| 0x2318 | 0x2319 | 8984 | 8985 | Phase C Current Demand | float | R | 2
| 0x231A | 0x231B | 8986 | 8987 | Phase C Import Active Power Demand | float | R | 2
| 0x231C | 0x231D | 8988 | 8989 | Phase C Export Active Power Demand | float | R | 2
| 0x231E | 0x231F | 8990 | 8991 | Phase C Import Reactive Power Demand | float | R | 2
| 0x2320 | 0x2321 | 8992 | 8993 | Phase C Export Reactive Power Demand | float | R | 2
| 0x2322 | 0x2323 | 8994 | 8995 | Phase C Apparent Power Demand | float | R | 2
| 0x2324 | 0x2325 | 8996 | 8997 | System Average Current Demand | float | R | 2
| 0x2326 | 0x2327 | 8998 | 8999 | System Import Active Power Demand | float | R | 2
| 0x2328 | 0x2329 | 9000 | 9001 | System Export Active Power Demand | float | R | 2
| 0x232A | 0x232B | 9002 | 9003 | System Import Reactive Power Demand | float | R | 2
| 0x232C | 0x232D | 9004 | 9005 | System Export Reactive Power Demand | float | R | 2
| 0x232E | 0x232F | 9006 | 9007 | System Apparent Power Demand | float | R | 2
Input Channel Demand | 0x2330 | 0x2331 | 9008 | 9009 | Input Channel 1 Current Demand | float | R | 2
| 0x2332 | 0x2333 | 9010 | 9011 | Input Channel 1 Import Active Power Demand | float | R | 2
| 0x2334 | 0x2335 | 9012 | 9013 | Input Channel 1 Export Active Power Demand | float | R | 2
| 0x2336 | 0x2337 | 9014 | 9015 | Input Channel 1 Import Reactive Power Demand | float | R | 2
| 0x2338 | 0x2339 | 9016 | 9017 | Input Channel 1 Export Reactive Power Demand | float | R | 2
| 0x233A | 0x233B | 9018 | 9019 | Input Channel 1 Apparent Power Demand | float | R | 2
| 0x233C | 0x244F | 9020 | 9295 | Input Channel 2-24 Demands | float | R | 276
User Channel Demand | 0x2450 | 0x2451 | 9296 | 9297 | User Channel 1 Current Demand | float | R | 2
| 0x2452 | 0x2453 | 9298 | 9299 | User Channel 1 Import Active Power Demand | float | R | 2
| 0x2454 | 0x2455 | 9300 | 9301 | User Channel 1 Export Active Power Demand | float | R | 2
| 0x2456 | 0x2457 | 9302 | 9303 | User Channel 1 Import Reactive Power Demand | float | R | 2
| 0x2458 | 0x2459 | 9304 | 9305 | User Channel 1 Export Reactive Power Demand | float | R | 2
| 0x245A | 0x245B | 9306 | 9307 | User Channel 1 Apparent Power Demand | float | R | 2
| 0x245C | 0x24DF | 9308 | 9439 | User Channel 2-12 Demands | float | R | 132
480
Power Quality(code function : 03H Read)
System Power Quality | 0x2600 | 0x2601 | 9728 | 9729 | Voltage Positive Sequence Magnitude | float | R | 2
| 0x2602 | 0x2603 | 9730 | 9731 | Voltage Zero Sequence Magnitude | float | R | 2
| 0x2604 | 0x2605 | 9732 | 9733 | Voltage Negative Sequence Magnitude | float | R | 2
| 0x2606 | 0x2607 | 9734 | 9735 | Voltage Positive Sequence Angle | float | R | 2
| 0x2608 | 0x2609 | 9736 | 9737 | Voltage Zero Sequence Angle | float | R | 2
| 0x260A | 0x260B | 9738 | 9739 | Voltage Negative Sequence Angle | float | R | 2
| 0x260C | 0x260D | 9740 | 9741 | Voltage Unbalance Factor Magnitude | float | R | 2
| 0x260E | 0x260F | 9742 | 9743 | Phase A Voltage THD | float | R | 2
| 0x2610 | 0x2611 | 9744 | 9745 | Phase A Voltage THD Odd | float | R | 2
| 0x2612 | 0x2613 | 9746 | 9747 | Phase A Voltage THD Even | float | R | 2
| 0x2614 | 0x2615 | 9748 | 9749 | Phase A Voltage Crest Factor | float | R | 2
| 0x2616 | 0x2617 | 9750 | 9751 | Phase A Voltage THFF Factor | float | R | 2
| 0x2618 | 0x2653 | 9752 | 9811 | Phase A Voltage individual Harmonics 2-31 percentage | float | R | 60
| 0x2654 | 0x2655 | 9812 | 9813 | Phase B Voltage THD | float | R | 2
| 0x2656 | 0x2657 | 9814 | 9815 | Phase B Voltage THD Odd | float | R | 2
| 0x2658 | 0x2659 | 9816 | 9817 | Phase B Voltage THD Even | float | R | 2
| 0x265A | 0x265B | 9818 | 9819 | Phase B Voltage Crest Factor | float | R | 2
| 0x265C | 0x265D | 9820 | 9821 | Phase B Voltage THFF Factor | float | R | 2
| 0x265E | 0x2699 | 9822 | 9881 | Phase B Voltage individual Harmonics 2-31 percentage | float | R | 60
| 0x269A | 0x269B | 9882 | 9883 | Phase C Voltage THD | float | R | 2
| 0x269C | 0x269D | 9884 | 9885 | Phase C Voltage THD Odd | float | R | 2
| 0x269E | 0x269F | 9886 | 9887 | Phase C Voltage THD Even | float | R | 2
| 0x26A0 | 0x26A1 | 9888 | 9889 | Phase C Voltage Crest Factor | float | R | 2
| 0x26A2 | 0x26A3 | 9890 | 9891 | Phase C Voltage THFF Factor | float | R | 2
| 0x26A4 | 0x26DF | 9892 | 9951 | Phase C Voltage individual Harmonics 2-31 percentage | float | R | 60
| 0x26E0 | 0x26E1 | 9952 | 9953 | Average Voltage THD | float | R | 2
| 0x26E2 | 0x26E3 | 9954 | 9955 | Average Voltage THD Odd | float | R | 2
| 0x26E4 | 0x26E5 | 9956 | 9957 | Average Voltage THD Even | float | R | 2
Input Channel Power Quality | 0x26E6 | 0x26E7 | 9958 | 9959 | Input Channel 1 Current THD | float | R | 2
| 0x26E8 | 0x26E9 | 9960 | 9961 | Input Channel 1 Current THD Odd | float | R | 2
| 0x26EA | 0x26EB | 9962 | 9963 | Input Channel 1 Current THD Even | float | R | 2
| 0x26EC | 0x26ED | 9964 | 9965 | Input Channel 1 Current K Factor | float | R | 2
| 0x26EE | 0x2729 | 9966 | 10025 | Input Channel 1 Current individual Harmonics 2-31 percentage | float | R | 60
| 0x272A | 0x2D45 | 10026 | 11589 | Input channel 2-24 power quality | float | R | 1564
User Channel Power Quality | 0x2D46 | 0x2D47 | 11590 | 11591 | User Channel 1 Current Positive Sequence Magnitude | float | R | 2
| 0x2D48 | 0x2D49 | 11592 | 11593 | User Channel 1 Current Zero Sequence Magnitude | float | R | 2
| 0x2D4A | 0x2D4B | 11594 | 11595 | User Channel 1 Current Negative Sequence Magnitude | float | R | 2
| 0x2D4C | 0x2D4D | 11596 | 11597 | User Channel 1 Current Positive Sequence Angle | float | R | 2
| 0x2D4E | 0x2D4F | 11598 | 11599 | User Channel 1 Current Zero Sequence Angle | float | R | 2
| 0x2D50 | 0x2D51 | 11600 | 11601 | User Channel 1 Current Negative Sequence Angle | float | R | 2
| 0x2D52 | 0x2D53 | 11602 | 11603 | User Channel 1 Current Unbalance Factor Magnitude | float | R | 2
| 0x2D54 | 0x2DED | 11604 | 11757 | User channel 2-12 power quality | float | R | 154
2030

## Energy
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Energy Parameter ID | Range | Default
Energy( function code:03H)
System Energy | 0x3000 | 0x3003 | 12288 | 12291 | Phase A active energy import | double | R | 4 | 1
| 0x3004 | 0x3007 | 12292 | 12295 | Phase A active energy export | double | R | 4 | 2
| 0x3008 | 0x300B | 12296 | 12299 | Phase A active energy net | double | R | 4 | 3
| 0x300C | 0x300F | 12300 | 12303 | Phase A active energy total | double | R | 4 | 4
| 0x3010 | 0x3013 | 12304 | 12307 | Phase A reactive energy import | double | R | 4 | 5
| 0x3014 | 0x3017 | 12308 | 12311 | Phase A reactive energy export | double | R | 4 | 6
| 0x3018 | 0x301B | 12312 | 12315 | Phase A reactive energy net | double | R | 4 | 7
| 0x301C | 0x301F | 12316 | 12319 | Phase A reactive energy total | double | R | 4 | 8
| 0x3020 | 0x3023 | 12320 | 12323 | Phase A apparent energy | double | R | 4 | 9
| 0x3024 | 0x3027 | 12324 | 12327 | Phase B active energy import | double | R | 4 | 10
| 0x3028 | 0x302B | 12328 | 12331 | Phase B active energy export | double | R | 4 | 11
| 0x302C | 0x302F | 12332 | 12335 | Phase B active energy net | double | R | 4 | 12
| 0x3030 | 0x3033 | 12336 | 12339 | Phase B active energy total | double | R | 4 | 13
| 0x3034 | 0x3037 | 12340 | 12343 | Phase B reactive energy import | double | R | 4 | 14
| 0x3038 | 0x303B | 12344 | 12347 | Phase B reactive energy export | double | R | 4 | 15
| 0x303C | 0x303F | 12348 | 12351 | Phase B reactive energy net | double | R | 4 | 16
| 0x3040 | 0x3043 | 12352 | 12355 | Phase B reactive energy total | double | R | 4 | 17
| 0x3044 | 0x3047 | 12356 | 12359 | Phase B apparent energy | double | R | 4 | 18
| 0x3048 | 0x304B | 12360 | 12363 | Phase C active energy import | double | R | 4 | 19
| 0x304C | 0x304F | 12364 | 12367 | Phase C active energy export | double | R | 4 | 20
| 0x3050 | 0x3053 | 12368 | 12371 | Phase C active energy net | double | R | 4 | 21
| 0x3054 | 0x3057 | 12372 | 12375 | Phase C active energy total | double | R | 4 | 22
| 0x3058 | 0x305B | 12376 | 12379 | Phase C reactive energy import | double | R | 4 | 23
| 0x305C | 0x305F | 12380 | 12383 | Phase C reactive energy export | double | R | 4 | 24
| 0x3060 | 0x3063 | 12384 | 12387 | Phase C reactive energy net | double | R | 4 | 25
| 0x3064 | 0x3067 | 12388 | 12391 | Phase C reactive energy total | double | R | 4 | 26
| 0x3068 | 0x306B | 12392 | 12395 | Phase C apparent energy | double | R | 4 | 27
| 0x306C | 0x306F | 12396 | 12399 | System active energy import | double | R | 4 | 28
| 0x3070 | 0x3073 | 12400 | 12403 | System active energy export | double | R | 4 | 29
| 0x3074 | 0x3077 | 12404 | 12407 | System active energy net | double | R | 4 | 30
| 0x3078 | 0x307B | 12408 | 12411 | System active energy total | double | R | 4 | 31
| 0x307C | 0x307F | 12412 | 12415 | System reactive energy import | double | R | 4 | 32
| 0x3080 | 0x3083 | 12416 | 12419 | System reactive energy export | double | R | 4 | 33
| 0x3084 | 0x3087 | 12420 | 12423 | System reactive energy net | double | R | 4 | 34
| 0x3088 | 0x308B | 12424 | 12427 | System reactive energy total | double | R | 4 | 35
| 0x308C | 0x308F | 12428 | 12431 | System apparent energy | double | R | 4 | 36
Input Channel Energy | 0x3090 | 0x3093 | 12432 | 12435 | Input Channel 1 active energy import | double | R | 4 | 37
| 0x3094 | 0x3097 | 12436 | 12439 | Input Channel 1 active energy export | double | R | 4 | 38
| 0x3098 | 0x309B | 12440 | 12443 | Input Channel 1 active energy net | double | R | 4 | 39
| 0x309C | 0x309F | 12444 | 12447 | Input Channel 1 active energy total | double | R | 4 | 40
| 0x30A0 | 0x30A3 | 12448 | 12451 | Input Channel 1 reactive energy import | double | R | 4 | 41
| 0x30A4 | 0x30A7 | 12452 | 12455 | Input Channel 1 reactive energy export | double | R | 4 | 42
| 0x30A8 | 0x30AB | 12456 | 12459 | Input Channel 1 reactive energy net | double | R | 4 | 43
| 0x30AC | 0x30AF | 12460 | 12463 | Input Channel 1 reactive energy total | double | R | 4 | 44
| 0x30B0 | 0x30B3 | 12464 | 12467 | Input Channel 1 apparent energy | double | R | 4 | 45
| 0x30B4 | 0x33EF | 12468 | 13295 | Input Channel 2-24 energy | double | R | 828 | 46-252
User Channel Energy | 0x33F0 | 0x33F3 | 13296 | 13299 | User Channel 1 active energy import | double | R | 4 | 253
| 0x33F4 | 0x33F7 | 13300 | 13303 | User Channel 1 active energy export | double | R | 4 | 254
| 0x33F8 | 0x33FB | 13304 | 13307 | User Channel 1 active energy net | double | R | 4 | 255
| 0x33FC | 0x33FF | 13308 | 13311 | User Channel 1 active energy total | double | R | 4 | 256
| 0x3400 | 0x3403 | 13312 | 13315 | User Channel 1 reactive energy import | double | R | 4 | 257
| 0x3404 | 0x3407 | 13316 | 13319 | User Channel 1 reactive energy export | double | R | 4 | 258
| 0x3408 | 0x340B | 13320 | 13323 | User Channel 1 reactive energy net | double | R | 4 | 259
| 0x340C | 0x340F | 13324 | 13327 | User Channel 1 reactive energy total | double | R | 4 | 260
| 0x3410 | 0x3413 | 13328 | 13331 | User Channel 1 apparent energy | double | R | 4 | 261
| 0x3414 | 0x359F | 13332 | 13727 | User Channel 2-12 energy | double | R | 396 | 262-360
1440

## Max Demand
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Max Demand(code function : 03H Read)
System Max Demand | 0x3700 | 0x3701 | 14080 | 14081 | Phase A Current Max Demand | float | R | 2
| 0x3702 | 0x3704 | 14082 | 14084 | Phase A Current Max Demand timestamp ( year:uint16_t; month,day : uint16_t ( High byte: month,Low byte: day); hour,min:uint16_t( High byte: hour,Low byte: minute) | timestamp | R | 3
| 0x3705 | 0x3706 | 14085 | 14086 | Phase A Import Active Power Max Demand | float | R | 2
| 0x3707 | 0x3709 | 14087 | 14089 | Phase A Import Active Power Max Demand timestamp | timestamp | R | 3
| 0x370A | 0x370B | 14090 | 14091 | Phase A Export Active Power Max Demand | float | R | 2
| 0x370C | 0x370E | 14092 | 14094 | Phase A Export Active Power Max Demand timestamp | timestamp | R | 3
| 0x370F | 0x3710 | 14095 | 14096 | Phase A Import Reactive Power Max Demand | float | R | 2
| 0x3711 | 0x3713 | 14097 | 14099 | Phase A Import Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x3714 | 0x3715 | 14100 | 14101 | Phase A Export Reactive Power Max Demand | float | R | 2
| 0x3716 | 0x3718 | 14102 | 14104 | Phase A Export Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x3719 | 0x371A | 14105 | 14106 | Phase A Apparent Power Max Demand | float | R | 2
| 0x371B | 0x371D | 14107 | 14109 | Phase A Apparent Power Max Demand timestamp | timestamp | R | 3
| 0x371E | 0x371F | 14110 | 14111 | Phase B Current Max Demand | float | R | 2
| 0x3720 | 0x3722 | 14112 | 14114 | Phase B Current Max Demand timestamp | timestamp | R | 3
| 0x3723 | 0x3724 | 14115 | 14116 | Phase B Import Active Power Max Demand | float | R | 2
| 0x3725 | 0x3727 | 14117 | 14119 | Phase B Import Active Power Max Demand timestamp | timestamp | R | 3
| 0x3728 | 0x3729 | 14120 | 14121 | Phase B Export Active Power Max Demand | float | R | 2
| 0x372A | 0x372C | 14122 | 14124 | Phase B Export Active Power Max Demand timestamp | timestamp | R | 3
| 0x372D | 0x372E | 14125 | 14126 | Phase B Import Reactive Power Max Demand | float | R | 2
| 0x372F | 0x3731 | 14127 | 14129 | Phase B Import Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x3732 | 0x3733 | 14130 | 14131 | Phase B Export Reactive Power Max Demand | float | R | 2
| 0x3734 | 0x3736 | 14132 | 14134 | Phase B Export Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x3737 | 0x3738 | 14135 | 14136 | Phase B Apparent Power Max Demand | float | R | 2
| 0x3739 | 0x373B | 14137 | 14139 | Phase B Apparent Power Max Demand timestamp | timestamp | R | 3
| 0x373C | 0x373D | 14140 | 14141 | Phase C Current Max Demand | float | R | 2
| 0x373E | 0x3740 | 14142 | 14144 | Phase C Current Max Demand timestamp | timestamp | R | 3
| 0x3741 | 0x3742 | 14145 | 14146 | Phase C Import Active Power Max Demand | float | R | 2
| 0x3743 | 0x3745 | 14147 | 14149 | Phase C Import Active Power Max Demand timestamp | timestamp | R | 3
| 0x3746 | 0x3747 | 14150 | 14151 | Phase C Export Active Power Max Demand | float | R | 2
| 0x3748 | 0x374A | 14152 | 14154 | Phase C Export Active Power Max Demand timestamp | timestamp | R | 3
| 0x374B | 0x374C | 14155 | 14156 | Phase C Import Reactive Power Max Demand | float | R | 2
| 0x374D | 0x374F | 14157 | 14159 | Phase C Import Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x3750 | 0x3751 | 14160 | 14161 | Phase C Export Reactive Power Max Demand | float | R | 2
| 0x3752 | 0x3754 | 14162 | 14164 | Phase C Export Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x3755 | 0x3756 | 14165 | 14166 | Phase C Apparent Power Max Demand | float | R | 2
| 0x3757 | 0x3759 | 14167 | 14169 | Phase C Apparent Power Max Demand timestamp | timestamp | R | 3
| 0x375A | 0x375B | 14170 | 14171 | System Average Current Max Demand | float | R | 2
| 0x375C | 0x375E | 14172 | 14174 | System Average Current Max Demand timestamp | timestamp | R | 3
| 0x375F | 0x3760 | 14175 | 14176 | System Import Active Power Max Demand | float | R | 2
| 0x3761 | 0x3763 | 14177 | 14179 | System Import Active Power Max Demand timestamp | timestamp | R | 3
| 0x3764 | 0x3765 | 14180 | 14181 | System Export Active Power Max Demand | float | R | 2
| 0x3766 | 0x3768 | 14182 | 14184 | System Export Active Power Max Demand timestamp | timestamp | R | 3
| 0x3769 | 0x376A | 14185 | 14186 | System Import Reactive Power Max Demand | float | R | 2
| 0x376B | 0x376D | 14187 | 14189 | System Import Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x376E | 0x376F | 14190 | 14191 | System Export Reactive Power Max Demand | float | R | 2
| 0x3770 | 0x3772 | 14192 | 14194 | System Export Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x3773 | 0x3774 | 14195 | 14196 | System Apparent Power Max Demand | float | R | 2
| 0x3775 | 0x3777 | 14197 | 14199 | System Apparent Power Max Demand timestamp | timestamp | R | 3
Input Channel Max Demand | 0x3778 | 0x3779 | 14200 | 14201 | Input Channel 1 Current Max Demand | float | R | 2
| 0x377A | 0x377C | 14202 | 14204 | Input Channel 1 Current Max Demand timestamp | timestamp | R | 3
| 0x377D | 0x377E | 14205 | 14206 | Input Channel 1 Import Active Power Max Demand | float | R | 2
| 0x377F | 0x3781 | 14207 | 14209 | Input Channel 1 Import Active Power Max Demand timestamp | timestamp | R | 3
| 0x3782 | 0x3783 | 14210 | 14211 | Input Channel 1 Export Active Power Max Demand | float | R | 2
| 0x3784 | 0x3786 | 14212 | 14214 | Input Channel 1 Export Active Power Max Demand timestamp | timestamp | R | 3
| 0x3787 | 0x3788 | 14215 | 14216 | Input Channel 1 Import Reactive Power Max Demand | float | R | 2
| 0x3789 | 0x378B | 14217 | 14219 | Input Channel 1 Import Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x378C | 0x378D | 14220 | 14221 | Input Channel 1 Export Reactive Power Max Demand | float | R | 2
| 0x378E | 0x3790 | 14222 | 14224 | Input Channel 1 Export Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x3791 | 0x3792 | 14225 | 14226 | Input Channel 1 Apparent Power Max Demand | float | R | 2
| 0x3793 | 0x3795 | 14227 | 14229 | Input Channel 1 Apparent Power Max Demand timestamp | timestamp | R | 3
| 0x3796 | 0x3A47 | 14230 | 14919 | Input Channel 2-24 Max Demand and timestamp |  | R | 690
User Channel Max Demand | 0x3A48 | 0x3A49 | 14920 | 14921 | User Channel 1 Current Max Demand | float | R | 2
| 0x3A4A | 0x3A4C | 14922 | 14924 | User Channel 1 Current Max Demand timestamp | timestamp | R | 3
| 0x3A4D | 0x3A4E | 14925 | 14926 | User Channel 1 Import Active Power Max Demand | float | R | 2
| 0x3A4F | 0x3A51 | 14927 | 14929 | User Channel 1 Import Active Power Max Demand timestamp | timestamp | R | 3
| 0x3A52 | 0x3A53 | 14930 | 14931 | User Channel 1 Export Active Power Max Demand | float | R | 2
| 0x3A54 | 0x3A56 | 14932 | 14934 | User Channel 1 Export Active Power Max Demand timestamp | timestamp | R | 3
| 0x3A57 | 0x3A58 | 14935 | 14936 | User Channel 1 Import Reactive Power Max Demand | float | R | 2
| 0x3A59 | 0x3A5B | 14937 | 14939 | User Channel 1 Import Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x3A5C | 0x3A5D | 14940 | 14941 | User Channel 1 Export Reactive Power Max Demand | float | R | 2
| 0x3A5E | 0x3A60 | 14942 | 14944 | User Channel 1 Export Reactive Power Max Demand timestamp | timestamp | R | 3
| 0x3A61 | 0x3A62 | 14945 | 14946 | User Channel 1 Apparent Power Max Demand | float | R | 2
| 0x3A63 | 0x3A65 | 14947 | 14949 | User Channel 1 Apparent Power Max Demand timestamp | timestamp | R | 3
| 0x3A66 | 0x3BAF | 14950 | 15279 | User Channel 2-12 Max Demands and timestamp |  | R | 330
1200

## TOU Default Setting
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW Num | Reg Num | Range | Default
TOU factory default setting code function : 03H Read, 10H Write
| 0x4000 | 0x4000 | 16384 | 16384 | Clear factory value of multiple rates time zone | uint16_t | R/W | 1 | Send 0xAA to clear
| 0x4001 | 0x4001 | 16385 | 16385 | Note: Before setting factory value of multiple rates time zone, this command is needed | uint16_t | R/W | 1
| 0x4002 | 0x4002 | 16386 | 16386 | Year time zone number | uint16_t | R/W | 1 | 0~12
| 0x4003 | 0x4003 | 16387 | 16387 | day time section record number | uint16_t | R/W | 1 | 0~14
| 0x4004 | 0x4004 | 16388 | 16388 | day time section number | uint16_t | R/W | 1 | 0~14
| 0x4005 | 0x4005 | 16389 | 16389 | Tarif number | uint16_t | R/W | 1 | 0~3
| 0x4006 | 0x4006 | 16390 | 16390 | Week off（0: no week off day;1: Sunday;2: Saturday;3: Sunday, Saturday） | uint16_t | R/W | 1 | 0~127
| 0x4007 | 0x4007 | 16391 | 16391 | Week off time section | uint16_t | R/W | 1 | 0~14
| 0x4008 | 0x4008 | 16392 | 16392 | Special day number | uint16_t | R/W | 1 | 0~30
| 0x4009 | 0x4009 | 16393 | 16393 | Enable TOU | uint16_t | R/W | 1 | 1: enable
| 0x400A | 0x400A | 16394 | 16394 | Enable TOU time setup restoring to factory value | uint16_t | R/W | 1 | 1: enable
| 0x400B | 0x400B | 16395 | 16395 | Tou month settlement model 0: nature weekend） | uint16_t | R/W | 1 | 0~1
| 0x400C | 0x400C | 16396 | 16396 | Tou month settlement time: day （default: 1） | uint16_t | R/W | 1 | 1~31
| 0x400D | 0x400D | 16397 | 16397 | Tou month settlement time: hour （default: 0） | uint16_t | R/W | 1 | 0~23
| 0x400E | 0x400E | 16398 | 16398 | Tou month settlement time: minute （default: 0） | uint16_t | R/W | 1 | 0~59
| 0x400F | 0x400F | 16399 | 16399 | Tou month settlement time: second （default: 0） | uint16_t | R/W | 1 | 0~59
| 0x4010 | 0x4010 | 16400 | 16400 | Fault state word（default） | uint16_t | R | 1 | 0: Settings correct
17
TOU schedule & season & holiday setting code function : 03H Read, 6AH Write
| 0x4011 | 0x4013 | 16401 | 16403 | 1st time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x4014 | 0x4016 | 16404 | 16406 | 2nd time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x4017 | 0x4019 | 16407 | 16409 | 3rd time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x401A | 0x401C | 16410 | 16412 | 4th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x401D | 0x401F | 16413 | 16415 | 5th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x4020 | 0x4022 | 16416 | 16418 | 6th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x4023 | 0x4025 | 16419 | 16421 | 7th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x4026 | 0x4028 | 16422 | 16424 | 8th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x4029 | 0x402B | 16425 | 16427 | 9th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x402C | 0x402E | 16428 | 16430 | 10th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x402F | 0x4031 | 16431 | 16433 | 11th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x4032 | 0x4034 | 16434 | 16436 | 12th time zone beginning date and day section record number(month, day, hour section number) | uint16_t | R/W | 3
| 0x4035 | 0x4037 | 16437 | 16439 | 1st day time section, 1st time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x4038 | 0x403A | 16440 | 16442 | 1st day time section, 2nd time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x403B | 0x403D | 16443 | 16445 | 1st day time section, 3rd time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x403E | 0x4040 | 16446 | 16448 | 1st day time section, 4th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x4041 | 0x4043 | 16449 | 16451 | 1st day time section, 5th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x4044 | 0x4046 | 16452 | 16454 | 1st day time section, 6th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x4047 | 0x4049 | 16455 | 16457 | 1st day time section, 7th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x404A | 0x404C | 16458 | 16460 | 1st day time section, 8th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x404D | 0x404F | 16461 | 16463 | 1st day time section, 9th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x4050 | 0x4052 | 16464 | 16466 | 1st day time section, 10th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x4053 | 0x4055 | 16467 | 16469 | 1st day time section, 11th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x4056 | 0x4058 | 16470 | 16472 | 1st day time section, 12th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x4059 | 0x405B | 16473 | 16475 | 1st day time section, 13th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x405C | 0x405E | 16476 | 16478 | 1st day time section, 14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 3
| 0x405F | 0x4088 | 16479 | 16520 | 2nd day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x4089 | 0x40B2 | 16521 | 16562 | 3rd day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x40B3 | 0x40DC | 16563 | 16604 | 4th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x40DD | 0x4106 | 16605 | 16646 | 5th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x4107 | 0x4130 | 16647 | 16688 | 6th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x4131 | 0x415A | 16689 | 16730 | 7th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x415B | 0x4184 | 16731 | 16772 | 8th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x4185 | 0x41AE | 16773 | 16814 | 9th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x41AF | 0x41D8 | 16815 | 16856 | 10th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x41D9 | 0x4202 | 16857 | 16898 | 11th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x4203 | 0x422C | 16899 | 16940 | 12th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x422D | 0x4256 | 16941 | 16982 | 13th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x4257 | 0x4280 | 16983 | 17024 | 14th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） | uint16_t | R/W | 42
| 0x4281 | 0x4283 | 17025 | 17027 | 1st special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x4284 | 0x4286 | 17028 | 17030 | 2nd special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x4287 | 0x4289 | 17031 | 17033 | 3rd special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x428A | 0x428C | 17034 | 17036 | 4th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x428D | 0x428F | 17037 | 17039 | 5th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x4290 | 0x4292 | 17040 | 17042 | 6th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x4293 | 0x4295 | 17043 | 17045 | 7th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x4296 | 0x4298 | 17046 | 17048 | 8th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x4299 | 0x429B | 17049 | 17051 | 9th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x429C | 0x429E | 17052 | 17054 | 10th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x429F | 0x42A1 | 17055 | 17057 | 11th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42A2 | 0x42A4 | 17058 | 17060 | 12th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42A5 | 0x42A7 | 17061 | 17063 | 13th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42A8 | 0x42AA | 17064 | 17066 | 14th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42AB | 0x42AD | 17067 | 17069 | 15th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42AE | 0x42B0 | 17070 | 17072 | 16th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42B1 | 0x42B3 | 17073 | 17075 | 17th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42B4 | 0x42B6 | 17076 | 17078 | 18th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42B7 | 0x42B9 | 17079 | 17081 | 19th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42BA | 0x42BC | 17082 | 17084 | 20th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42BD | 0x42BF | 17085 | 17087 | 21st special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42C0 | 0x42C2 | 17088 | 17090 | 22nd special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42C3 | 0x42C5 | 17091 | 17093 | 23rd special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42C6 | 0x42C8 | 17094 | 17096 | 24th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42C9 | 0x42CB | 17097 | 17099 | 25th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42CC | 0x42CE | 17100 | 17102 | 26th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42CF | 0x42D1 | 17103 | 17105 | 27th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42D2 | 0x42D4 | 17106 | 17108 | 28th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42D5 | 0x42D7 | 17109 | 17111 | 29th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42D8 | 0x42DA | 17112 | 17114 | 30th special date and its time section number(month, day, time section number） | uint16_t | R/W | 3
| 0x42DB | 0x42DB | 17115 | 17115 | Default enable/disable ”Holiday many year setup“ | uint16_t | R/W | 1 | 1: enable
| 0x42DC | 0x42DC | 17116 | 17116 | Default beginning year of ”Holiday many year setup“ | uint16_t | R/W | 1 | 2000~2099
| 0x42DD | 0x42DD | 17117 | 17117 | Default ending year of ”Holiday many year setup“ | uint16_t | R/W | 1 | 2000~2099
717
10years holidy factory default setting code function : 03H Read, 6AH Write
| 0x42DE | 0x4373 | 17118 | 17267 | Setup address for ten year holiday by PC | uint16_t | R/W | 150

## TOU Reading
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Current Month Accumulative TOU Energy A&B&C&system code function : 03H Read
| 0x43A0 | 0x43A1 | 17312 | 17313 | Phase A sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43A2 | 0x43A3 | 17314 | 17315 | Phase A peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43A4 | 0x43A5 | 17316 | 17317 | Phase A valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43A6 | 0x43A7 | 17318 | 17319 | Phase A normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43A8 | 0x43A9 | 17320 | 17321 | Phase A total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43AA | 0x43AB | 17322 | 17323 | Phase B sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43AC | 0x43AD | 17324 | 17325 | Phase B peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43AE | 0x43AF | 17326 | 17327 | Phase B valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43B0 | 0x43B1 | 17328 | 17329 | Phase B normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43B2 | 0x43B3 | 17330 | 17331 | Phase B total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43B4 | 0x43B5 | 17332 | 17333 | Phase C sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43B6 | 0x43B7 | 17334 | 17335 | Phase C peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43B8 | 0x43B9 | 17336 | 17337 | Phase C valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43BA | 0x43BB | 17338 | 17339 | Phase C normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43BC | 0x43BD | 17340 | 17341 | Phase C total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43BE | 0x43BF | 17342 | 17343 | System sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43C0 | 0x43C1 | 17344 | 17345 | System peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43C2 | 0x43C3 | 17346 | 17347 | System valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43C4 | 0x43C5 | 17348 | 17349 | System normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43C6 | 0x43C7 | 17350 | 17351 | System total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
Current Month Accumulative TOU Energy 24-channels input code function : 03H Read
| 0x43C8 | 0x43C9 | 17352 | 17353 | input channel 1 sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43CA | 0x43CB | 17354 | 17355 | input channel 1 peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43CC | 0x43CD | 17356 | 17357 | input channel 1 valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43CE | 0x43CF | 17358 | 17359 | input channel 1 normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43D0 | 0x43D1 | 17360 | 17361 | input channel 1 total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x43D2 | 0x44B7 | 17362 | 17591 | input channel 2-24 Import active energy | uint32_t | R | 230 | 0~999999999
Current Month Accumulative TOU Energy 12-users code function : 03H
| 0x44B8 | 0x44B9 | 17592 | 17593 | user 1 sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x44BA | 0x44BB | 17594 | 17595 | user 1 peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x44BC | 0x44BD | 17596 | 17597 | user 1 valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x44BE | 0x44BF | 17598 | 17599 | user 1 normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x44C0 | 0x44C1 | 17600 | 17601 | user 1 total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x44C2 | 0x452F | 17602 | 17711 | user 2-12 Ep_Imp Import active energy | uint32_t | R | 110 | 0~999999999
Previous Month A&B&C&system Accumulative TOU Energy: 03H Read
| 0x4530 | 0x4531 | 17712 | 17713 | Phase A sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4532 | 0x4533 | 17714 | 17715 | Phase A peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4534 | 0x4535 | 17716 | 17717 | Phase A valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4536 | 0x4537 | 17718 | 17719 | Phase A normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4538 | 0x4539 | 17720 | 17721 | Phase A total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x453A | 0x453B | 17722 | 17723 | Phase B sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x453C | 0x453D | 17724 | 17725 | Phase B peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x453E | 0x453F | 17726 | 17727 | Phase B valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4540 | 0x4541 | 17728 | 17729 | Phase B normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4542 | 0x4543 | 17730 | 17731 | Phase B total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4544 | 0x4545 | 17732 | 17733 | Phase C sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4546 | 0x4547 | 17734 | 17735 | Phase C peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4548 | 0x4549 | 17736 | 17737 | Phase C valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x454A | 0x454B | 17738 | 17739 | Phase C normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x454C | 0x454D | 17740 | 17741 | Phase C total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x454E | 0x454F | 17742 | 17743 | System sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4550 | 0x4551 | 17744 | 17745 | System peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4552 | 0x4553 | 17746 | 17747 | System valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4554 | 0x4555 | 17748 | 17749 | System normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4556 | 0x4557 | 17750 | 17751 | System total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
Previous Month Accumulative TOU Energy: 24-channels input function code : 03H
| 0x4558 | 0x4559 | 17752 | 17753 | input channel 1 sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x455A | 0x455B | 17754 | 17755 | input channel 1 peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x455C | 0x455D | 17756 | 17757 | input channel 1 valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x455E | 0x455F | 17758 | 17759 | input channel 1 normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4560 | 0x4561 | 17760 | 17761 | input channel 1 total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4562 | 0x4647 | 17762 | 17991 | input channel 2-24 Ep_Imp Import active energy | uint32_t | R | 230 | 0~999999999
Previous Month Accumulative 12-users TOU Energy code function : 03H read
| 0x4648 | 0x4649 | 17992 | 17993 | user 1 sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x464A | 0x464B | 17994 | 17995 | user 1 peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x464C | 0x464D | 17996 | 17997 | user 1 valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x464E | 0x464F | 17998 | 17999 | user 1 normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4650 | 0x4651 | 18000 | 18001 | user 1 total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4652 | 0x46BF | 18002 | 18111 | user 2-12 Ep_Imp Import active energy | uint32_t | R | 110 | 0~999999999
Current Month Incremental A&B&C&system TOU Energy: 03H Read
| 0x46C0 | 0x46C1 | 18112 | 18113 | Phase A sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46C2 | 0x46C3 | 18114 | 18115 | Phase A peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46C4 | 0x46C5 | 18116 | 18117 | Phase A valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46C6 | 0x46C7 | 18118 | 18119 | Phase A normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46C8 | 0x46C9 | 18120 | 18121 | Phase A total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46CA | 0x46CB | 18122 | 18123 | Phase B sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46CC | 0x46CD | 18124 | 18125 | Phase B peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46CE | 0x46CF | 18126 | 18127 | Phase B valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46D0 | 0x46D1 | 18128 | 18129 | Phase B normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46D2 | 0x46D3 | 18130 | 18131 | Phase B total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46D4 | 0x46D5 | 18132 | 18133 | Phase C sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46D6 | 0x46D7 | 18134 | 18135 | Phase C peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46D8 | 0x46D9 | 18136 | 18137 | Phase C valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46DA | 0x46DB | 18138 | 18139 | Phase C normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46DC | 0x46DD | 18140 | 18141 | Phase C total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46DE | 0x46DF | 18142 | 18143 | Sytem sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46E0 | 0x46E1 | 18144 | 18145 | Sytem peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46E2 | 0x46E3 | 18146 | 18147 | Sytem valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46E4 | 0x46E5 | 18148 | 18149 | Sytem normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46E6 | 0x46E7 | 18150 | 18151 | Sytem total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
Current Month Incremental 24-channels input TOU Energy : 03H read
| 0x46E8 | 0x46E9 | 18152 | 18153 | input channel 1 sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46EA | 0x46EB | 18154 | 18155 | input channel 1 peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46EC | 0x46ED | 18156 | 18157 | input channel 1 valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46EE | 0x46EF | 18158 | 18159 | input channel 1 normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46F0 | 0x46F1 | 18160 | 18161 | input channel 1 total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x46F2 | 0x47D7 | 18162 | 18391 | input channel 2-24 Ep_Imp Import active energy | uint32_t | R | 230 | 0~999999999
Current Month Incremental 12-users input TOU Energy : 03H read
| 0x47D8 | 0x47D9 | 18392 | 18393 | user 1 sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x47DA | 0x47DB | 18394 | 18395 | user 1 peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x47DC | 0x47DD | 18396 | 18397 | user 1 valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x47DE | 0x47DF | 18398 | 18399 | user 1 normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x47E0 | 0x47E1 | 18400 | 18401 | user 1 total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x47E2 | 0x484F | 18402 | 18511 | user 2 - 12 Ep_Imp Import active energy | uint32_t | R | 110 | 0~999999999
Previous Month Incremental A/B/C&system TOU Energy: 03H Read
| 0x4850 | 0x4851 | 18512 | 18513 | Phase A sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4852 | 0x4853 | 18514 | 18515 | Phase A peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4854 | 0x4855 | 18516 | 18517 | Phase A valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4856 | 0x4857 | 18518 | 18519 | Phase A normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4858 | 0x4859 | 18520 | 18521 | Phase A total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x485A | 0x485B | 18522 | 18523 | Phase B sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x485C | 0x485D | 18524 | 18525 | Phase B peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x485E | 0x485F | 18526 | 18527 | Phase B valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4860 | 0x4861 | 18528 | 18529 | Phase B normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4862 | 0x4863 | 18530 | 18531 | Phase B total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4864 | 0x4865 | 18532 | 18533 | Phase C sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4866 | 0x4867 | 18534 | 18535 | Phase C peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4868 | 0x4869 | 18536 | 18537 | Phase C valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x486A | 0x486B | 18538 | 18539 | Phase C normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x486C | 0x486D | 18540 | 18541 | Phase C total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x486E | 0x486F | 18542 | 18543 | System sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4870 | 0x4871 | 18544 | 18545 | System peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4872 | 0x4873 | 18546 | 18547 | System valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4874 | 0x4875 | 18548 | 18549 | System normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4876 | 0x4877 | 18550 | 18551 | System total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
Previous Month Incremental 24-channels input TOU Energy : 03H read
| 0x4878 | 0x4879 | 18552 | 18553 | input channel 1 sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x487A | 0x487B | 18554 | 18555 | input channel 1 peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x487C | 0x487D | 18556 | 18557 | input channel 1 valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x487E | 0x487F | 18558 | 18559 | input channel 1 normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4880 | 0x4881 | 18560 | 18561 | input channel 1 total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4882 | 0x4967 | 18562 | 18791 | input channel 2 -24 Ep_Imp Import active energy | uint32_t | R | 230 | 0~999999999
Previous Month Incremental 12-users input TOU Energy : 03H read
| 0x4968 | 0x4969 | 18792 | 18793 | user 1 sharp - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x496A | 0x496B | 18794 | 18795 | user 1 peak - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x496C | 0x496D | 18796 | 18797 | user 1 valley - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x496E | 0x496F | 18798 | 18799 | user 1 normal - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4970 | 0x4971 | 18800 | 18801 | user 1 total - Ep_Imp Import active energy | uint32_t | R | 2 | 0~999999999
| 0x4972 | 0x49DF | 18802 | 18911 | user 2 - 12 Ep_Imp Import active energy | uint32_t | R | 110 | 0~999999999
1600
TOU OverFlow flag | 0x49E0 | 0x49E1 | 18912 | 18913 | TOU OverFlow flag | uint32_t | R | 2 | 0

## TOU Setting
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Daylight Savings Time Settings code function : 03H Read, 10H Write
| 0x4A00 | 0x4A00 | 18944 | 18944 | DST enable | uint16_t | R/W | 1 | 0: disable 1: enable | 0
| 0x4A01 | 0x4A01 | 18945 | 18945 | DST format | uint16_t | R/W | 1 | 0: format 1(fixed date) 1: format 2 (non fixed date) | 0
Format 1: Fixed Date : 03H Read, 10H Write
| 0x4A02 | 0x4A02 | 18946 | 18946 | DST Start Month | uint16_t | R/W | 1 | 1~12 | 3
| 0x4A03 | 0x4A03 | 18947 | 18947 | DST Start Day | uint16_t | R/W | 1 | 1~31 | 1
| 0x4A04 | 0x4A04 | 18948 | 18948 | DST Start Hour | uint16_t | R/W | 1 | 0-23 | 0
| 0x4A05 | 0x4A05 | 18949 | 18949 | DST Start Min | uint16_t | R/W | 1 | 0-59 | 0
| 0x4A06 | 0x4A06 | 18950 | 18950 | DST Start Adjust time (Unit: Min) | uint16_t | R/W | 1 | 1-120 | 60
| 0x4A07 | 0x4A07 | 18951 | 18951 | DST End Month | uint16_t | R/W | 1 | 1~12 | 11
| 0x4A08 | 0x4A08 | 18952 | 18952 | DST End Day | uint16_t | R/W | 1 | 1~31 | 1
| 0x4A09 | 0x4A09 | 18953 | 18953 | DST End Hour | uint16_t | R/W | 1 | 0-23 | 0
| 0x4A0A | 0x4A0A | 18954 | 18954 | DST End Minute | uint16_t | R/W | 1 | 0-59 | 0
| 0x4A0B | 0x4A0B | 18955 | 18955 | DST End Adjust time (Unit: Minute) | uint16_t | R/W | 1 | 1-120 | 60
Format 2: Non Fixed Date : 03H Read, 10H Write
| 0x4A0C | 0x4A0C | 18956 | 18956 | DST Start Month | uint16_t | R/W | 1 | 1~12 | 3
| 0x4A0D | 0x4A0D | 18957 | 18957 | DST Start Day | uint16_t | R/W | 1 | 0-6 0: Sunday 1~6: Monday to Saturday | 0
| 0x4A0E | 0x4A0E | 18958 | 18958 | DST Start Week | uint16_t | R/W | 1 | 1~5 | 2
| 0x4A0F | 0x4A0F | 18959 | 18959 | DST Start Hour | uint16_t | R/W | 1 | 0-23 | 0
| 0x4A10 | 0x4A10 | 18960 | 18960 | DST Start Minute | uint16_t | R/W | 1 | 0-59 | 0
| 0x4A11 | 0x4A11 | 18961 | 18961 | DST Start Adjust time (Unit: Minute) | uint16_t | R/W | 1 | 1-120 | 60
| 0x4A12 | 0x4A12 | 18962 | 18962 | DST End Month | uint16_t | R/W | 1 | 1~12 | 11
| 0x4A13 | 0x4A13 | 18963 | 18963 | DST End Day | uint16_t | R/W | 1 | 0-6 0: Sunday 1~6 Monday to Saturday | 0
| 0x4A14 | 0x4A14 | 18964 | 18964 | DST End Week | uint16_t | R/W | 1 | 1~5 | 1
| 0x4A15 | 0x4A15 | 18965 | 18965 | DST End Hour | uint16_t | R/W | 1 | 0-23 | 0
| 0x4A16 | 0x4A16 | 18966 | 18966 | DST End Minute | uint16_t | R/W | 1 | 0-59 | 0
| 0x4A17 | 0x4A17 | 18967 | 18967 | DST End Adjust time (Unit: Minute) | uint16_t | R/W | 1 | 1-120 | 60
TOU Basic Setting : 03H Read, 10H Write
| 0x4A18 | 0x4A18 | 18968 | 18968 | Number of seasons | uint16_t | R/W | 1 | 0~12 | tou default
| 0x4A19 | 0x4A19 | 18969 | 18969 | Number of schedules | uint16_t | R/W | 1 | 0~14 | tou default
| 0x4A1A | 0x4A1A | 18970 | 18970 | Number of segments | uint16_t | R/W | 1 | 0~14 | tou default
| 0x4A1B | 0x4A1B | 18971 | 18971 | Number of tariffs | uint16_t | R/W | 1 | 0~3 | tou default
| 0x4A1C | 0x4A1C | 18972 | 18972 | Weekend setting (Bit0: Sunday; Bit1-Bit6: Mon-Sat) bit=0: not weekend bit=1: is weekend | uint16_t | R/W | 1 | 0~127 | tou default
| 0x4A1D | 0x4A1D | 18973 | 18973 | Weekend Schedule ID | uint16_t | R/W | 1 | 0~14 | tou default
| 0x4A1E | 0x4A1E | 18974 | 18974 | Number of holidays | uint16_t | R/W | 1 | 0~30 | tou default
| 0x4A1F | 0x4A1F | 18975 | 18975 | Enable TOU | uint16_t | R/W | 1 | 1: enable | tou default
| 0x4A20 |  | 18976 | [6 empty] | tou default
| 0x4A20 | 0x4A20 | 18976 | 18976 | Monthly Billing Mode | uint16_t | R/W | 1 | 0~1 | tou default
| 0x4A21 | 0x4A21 | 18977 | 18977 | Billing time: day | uint16_t | R/W | 1 | 1~31 | tou default
| 0x4A22 | 0x4A22 | 18978 | 18978 | Billing time : hour | uint16_t | R/W | 1 | 0~23 | tou default
| 0x4A23 | 0x4A23 | 18979 | 18979 | Billing time: minute | uint16_t | R/W | 1 | 0~59 | tou default
| 0x4A24 | 0x4A24 | 18980 | 18980 | Billing time: second | uint16_t | R/W | 1 | 0~59 | tou default
| 0x4A25 | 0x4A25 | 18981 | 18981 | Error Code | uint16_t | R | 1 | 0: Settings correct | tou default
Season setting : 03H Read, 10H Write
| 0x4A26 | 0x4A28 | 18982 | 18984 | TOU Season 1 | uint16_t | R/W | 3 | In format of month, day, schedule ID | tou default
| 0x4A29 | 0x4A2B | 18985 | 18987 | TOU Season 2 | uint16_t | R/W | 3 |  | tou default
| 0x4A2C | 0x4A2E | 18988 | 18990 | TOU Season 3 | uint16_t | R/W | 3 |  | tou default
| 0x4A2F | 0x4A31 | 18991 | 18993 | TOU Season 4 | uint16_t | R/W | 3 |  | tou default
| 0x4A32 | 0x4A34 | 18994 | 18996 | TOU Season 5 | uint16_t | R/W | 3 |  | tou default
| 0x4A35 | 0x4A37 | 18997 | 18999 | TOU Season 6 | uint16_t | R/W | 3 |  | tou default
| 0x4A38 | 0x4A3A | 19000 | 19002 | TOU Season 7 | uint16_t | R/W | 3 |  | tou default
| 0x4A3B | 0x4A3D | 19003 | 19005 | TOU Season 8 | uint16_t | R/W | 3 |  | tou default
| 0x4A3E | 0x4A40 | 19006 | 19008 | TOU Season 9 | uint16_t | R/W | 3 |  | tou default
| 0x4A41 | 0x4A43 | 19009 | 19011 | TOU Season 10 | uint16_t | R/W | 3 |  | tou default
| 0x4A44 | 0x4A46 | 19012 | 19014 | TOU Season 11 | uint16_t | R/W | 3 |  | tou default
| 0x4A47 | 0x4A49 | 19015 | 19017 | TOU Season 12 | uint16_t | R/W | 3 |  | tou default
Schedule setting : 03H Read, 10H Write
| 0x4A4A | 0x4A4C | 19018 | 19020 | Schedule 1 Segment 1 setting In format of hour, minutes, segment （tariffs）ID | uint16_t | R/W | 3 |  | tou default
| 0x4A4D | 0x4A4F | 19021 | 19023 | Schedule 1 Segment 2 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A50 | 0x4A52 | 19024 | 19026 | Schedule 1 Segment 3 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A53 | 0x4A55 | 19027 | 19029 | Schedule 1 Segment 4 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A56 | 0x4A58 | 19030 | 19032 | Schedule 1 Segment 5 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A59 | 0x4A5B | 19033 | 19035 | Schedule 1 Segment 6 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A5C | 0x4A5E | 19036 | 19038 | Schedule 1 Segment 7 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A5F | 0x4A61 | 19039 | 19041 | Schedule 1 Segment 8 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A62 | 0x4A64 | 19042 | 19044 | Schedule 1 Segment 9 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A65 | 0x4A67 | 19045 | 19047 | Schedule 1 Segment 10 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A68 | 0x4A6A | 19048 | 19050 | Schedule 1 Segment 11 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A6B | 0x4A6D | 19051 | 19053 | Schedule 1 Segment 12 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A6E | 0x4A70 | 19054 | 19056 | Schedule 1 Segment 13 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A71 | 0x4A73 | 19057 | 19059 | Schedule 1 Segment 14 setting | uint16_t | R/W | 3 |  | tou default
| 0x4A74 | 0x4A9D | 19060 | 19101 | Schedule 2 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4A9E | 0x4AC7 | 19102 | 19143 | Schedule 3 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4AC8 | 0x4AF1 | 19144 | 19185 | Schedule 4 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4AF2 | 0x4B1B | 19186 | 19227 | Schedule 5 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4B1C | 0x4B45 | 19228 | 19269 | Schedule 6 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4B46 | 0x4B6F | 19270 | 19311 | Schedule 7 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4B70 | 0x4B99 | 19312 | 19353 | Schedule 8 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4B9A | 0x4BC3 | 19354 | 19395 | Schedule 9 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4BC4 | 0x4BED | 19396 | 19437 | Schedule 10 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4BEE | 0x4C17 | 19438 | 19479 | Schedule 11 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4C18 | 0x4C41 | 19480 | 19521 | Schedule 12 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4C42 | 0x4C6B | 19522 | 19563 | Schedule 13 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
| 0x4C6C | 0x4C95 | 19564 | 19605 | Schedule 14 setting | uint16_t | R/W | 42 | Same as schedule 1 segment 1-14 setting | tou default
Holiday setting : 03H Read, 10H Write
| 0x4C96 | 0x4C98 | 19606 | 19608 | 1st Holiday setting In format of month, day, schedule ID | uint16_t | R/W | 3
| 0x4C99 | 0x4C9B | 19609 | 19611 | 2nd Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4C9C | 0x4C9E | 19612 | 19614 | 3rd Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4C9F | 0x4CA1 | 19615 | 19617 | 4th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CA2 | 0x4CA4 | 19618 | 19620 | 5th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CA5 | 0x4CA7 | 19621 | 19623 | 6th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CA8 | 0x4CAA | 19624 | 19626 | 7th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CAB | 0x4CAD | 19627 | 19629 | 8th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CAE | 0x4CB0 | 19630 | 19632 | 9th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CB1 | 0x4CB3 | 19633 | 19635 | 10th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CB4 | 0x4CB6 | 19636 | 19638 | 11th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CB7 | 0x4CB9 | 19639 | 19641 | 12th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CBA | 0x4CBC | 19642 | 19644 | 13th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CBD | 0x4CBF | 19645 | 19647 | 14th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CC0 | 0x4CC2 | 19648 | 19650 | 15th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CC3 | 0x4CC5 | 19651 | 19653 | 16th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CC6 | 0x4CC8 | 19654 | 19656 | 17th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CC9 | 0x4CCB | 19657 | 19659 | 18th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CCC | 0x4CCE | 19660 | 19662 | 19th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CCF | 0x4CD1 | 19663 | 19665 | 20th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CD2 | 0x4CD4 | 19666 | 19668 | 21st Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CD5 | 0x4CD7 | 19669 | 19671 | 22nd Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CD8 | 0x4CDA | 19672 | 19674 | 23rd Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CDB | 0x4CDD | 19675 | 19677 | 24th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CDE | 0x4CE0 | 19678 | 19680 | 25th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CE1 | 0x4CE3 | 19681 | 19683 | 26th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CE4 | 0x4CE6 | 19684 | 19686 | 27th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CE7 | 0x4CE9 | 19687 | 19689 | 28th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CEA | 0x4CEC | 19690 | 19692 | 29th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CED | 0x4CEF | 19693 | 19695 | 30th Holiday setting | uint16_t | R/W | 3 |  | tou default
| 0x4CF0 | 0x4CF0 | 19696 | 19696 | Holiday Setting enable | uint16_t | R/W | 1 |  | 0
| 0x4CF1 | 0x4CF1 | 19697 | 19697 | Start Year | uint16_t | R/W | 1 |  | 2024
| 0x4CF2 | 0x4CF2 | 19698 | 19698 | End Year | uint16_t | R/W | 1 |  | 2099
10 years holiday setting : 03H Read, 10H Write
| 0x4CF3 | 0x4CF5 | 19699 | 19701 | Year 1 holiday 1 setting In format of month, day, schedule ID | uint16_t | R/W | 3 |  | 0
| 0x4CF6 | 0x4CF8 | 19702 | 19704 | Year 1 holiday 2 setting | uint16_t | R/W | 3 |  | 0
| 0x4CF9 | 0x4CFB | 19705 | 19707 | Year 1 holiday 3 setting | uint16_t | R/W | 3 |  | 0
| 0x4CFC | 0x4CFE | 19708 | 19710 | Year 1 holiday 4 setting | uint16_t | R/W | 3 |  | 0
| 0x4CFF | 0x4D01 | 19711 | 19713 | Year 1 holiday 5 setting | uint16_t | R/W | 3 |  | 0
| 0x4D02 | 0x4D04 | 19714 | 19716 | Year 1 holiday 6 setting | uint16_t | R/W | 3 |  | 0
| 0x4D05 | 0x4D07 | 19717 | 19719 | Year 1 holiday 7 setting | uint16_t | R/W | 3 |  | 0
| 0x4D08 | 0x4D0A | 19720 | 19722 | Year 1 holiday 8 setting | uint16_t | R/W | 3 |  | 0
| 0x4D0B | 0x4D0D | 19723 | 19725 | Year 1 holiday 9 setting | uint16_t | R/W | 3 |  | 0
| 0x4D0E | 0x4D10 | 19726 | 19728 | Year 1 holiday 10 setting | uint16_t | R/W | 3 |  | 0
| 0x4D11 | 0x4D13 | 19729 | 19731 | Year 1 holiday 11 setting | uint16_t | R/W | 3 |  | 0
| 0x4D14 | 0x4D16 | 19732 | 19734 | Year 1 holiday 12 setting | uint16_t | R/W | 3 |  | 0
| 0x4D17 | 0x4D19 | 19735 | 19737 | Year 1 holiday 13 setting | uint16_t | R/W | 3 |  | 0
| 0x4D1A | 0x4D1C | 19738 | 19740 | Year 1 holiday 14 setting | uint16_t | R/W | 3 |  | 0
| 0x4D1D | 0x4D1F | 19741 | 19743 | Year 1 holiday 15 setting | uint16_t | R/W | 3 |  | 0
| 0x4D20 | 0x4D22 | 19744 | 19746 | Year 1 holiday 16 setting | uint16_t | R/W | 3 |  | 0
| 0x4D23 | 0x4D25 | 19747 | 19749 | Year 1 holiday 17 setting | uint16_t | R/W | 3 |  | 0
| 0x4D26 | 0x4D28 | 19750 | 19752 | Year 1 holiday 18 setting | uint16_t | R/W | 3 |  | 0
| 0x4D29 | 0x4D2B | 19753 | 19755 | Year 1 holiday 19 setting | uint16_t | R/W | 3 |  | 0
| 0x4D2C | 0x4D2E | 19756 | 19758 | Year 1 holiday 20 setting | uint16_t | R/W | 3 |  | 0
| 0x4D2F | 0x4D31 | 19759 | 19761 | Year 1 holiday 21 setting | uint16_t | R/W | 3 |  | 0
| 0x4D32 | 0x4D34 | 19762 | 19764 | Year 1 holiday 22 setting | uint16_t | R/W | 3 |  | 0
| 0x4D35 | 0x4D37 | 19765 | 19767 | Year 1 holiday 23 setting | uint16_t | R/W | 3 |  | 0
| 0x4D38 | 0x4D3A | 19768 | 19770 | Year 1 holiday 24 setting | uint16_t | R/W | 3 |  | 0
| 0x4D3B | 0x4D3D | 19771 | 19773 | Year 1 holiday 25 setting | uint16_t | R/W | 3 |  | 0
| 0x4D3E | 0x4D40 | 19774 | 19776 | Year 1 holiday 26 setting | uint16_t | R/W | 3 |  | 0
| 0x4D41 | 0x4D43 | 19777 | 19779 | Year 1 holiday 27 setting | uint16_t | R/W | 3 |  | 0
| 0x4D44 | 0x4D46 | 19780 | 19782 | Year 1 holiday 28 setting | uint16_t | R/W | 3 |  | 0
| 0x4D47 | 0x4D49 | 19783 | 19785 | Year 1 holiday 29 setting | uint16_t | R/W | 3 |  | 0
| 0x4D4A | 0x4D4C | 19786 | 19788 | Year 1 holiday 30 setting | uint16_t | R/W | 3 |  | 0
| 0x4D4D | 0x4D4D | 19789 | 19789 | Year 1 setting Year | uint16_t | R/W | 1 |  | 2024
| 0x4D4E | 0x4D4E | 19790 | 19790 | Year 1 Number of holidays | uint16_t | R/W | 1 |  | 0
| 0x4D4F | 0x4D51 | 19791 | 19793 | Year 2 holiday 1 setting | uint16_t | R/W | 3 |  | 0
| 0x4D52 | 0x4D54 | 19794 | 19796 | Year 2 holiday 2 setting | uint16_t | R/W | 3 |  | 0
| 0x4D55 | 0x4D57 | 19797 | 19799 | Year 2 holiday 3 setting | uint16_t | R/W | 3 |  | 0
| 0x4D58 | 0x4D5A | 19800 | 19802 | Year 2 holiday 4 setting | uint16_t | R/W | 3 |  | 0
| 0x4D5B | 0x4D5D | 19803 | 19805 | Year 2 holiday 5 setting | uint16_t | R/W | 3 |  | 0
| 0x4D5E | 0x4D60 | 19806 | 19808 | Year 2 holiday 6 setting | uint16_t | R/W | 3 |  | 0
| 0x4D61 | 0x4D63 | 19809 | 19811 | Year 2 holiday 7 setting | uint16_t | R/W | 3 |  | 0
| 0x4D64 | 0x4D66 | 19812 | 19814 | Year 2 holiday 8 setting | uint16_t | R/W | 3 |  | 0
| 0x4D67 | 0x4D69 | 19815 | 19817 | Year 2 holiday 9 setting | uint16_t | R/W | 3 |  | 0
| 0x4D6A | 0x4D6C | 19818 | 19820 | Year 2 holiday 10 setting | uint16_t | R/W | 3 |  | 0
| 0x4D6D | 0x4D6F | 19821 | 19823 | Year 2 holiday 11 setting | uint16_t | R/W | 3 |  | 0
| 0x4D70 | 0x4D72 | 19824 | 19826 | Year 2 holiday 12 setting | uint16_t | R/W | 3 |  | 0
| 0x4D73 | 0x4D75 | 19827 | 19829 | Year 2 holiday 13 setting | uint16_t | R/W | 3 |  | 0
| 0x4D76 | 0x4D78 | 19830 | 19832 | Year 2 holiday 14 setting | uint16_t | R/W | 3 |  | 0
| 0x4D79 | 0x4D7B | 19833 | 19835 | Year 2 holiday 15 setting | uint16_t | R/W | 3 |  | 0
| 0x4D7C | 0x4D7E | 19836 | 19838 | Year 2 holiday 16 setting | uint16_t | R/W | 3 |  | 0
| 0x4D7F | 0x4D81 | 19839 | 19841 | Year 2 holiday 17 setting | uint16_t | R/W | 3 |  | 0
| 0x4D82 | 0x4D84 | 19842 | 19844 | Year 2 holiday 18 setting | uint16_t | R/W | 3 |  | 0
| 0x4D85 | 0x4D87 | 19845 | 19847 | Year 2 holiday 19 setting | uint16_t | R/W | 3 |  | 0
| 0x4D88 | 0x4D8A | 19848 | 19850 | Year 2 holiday 20 setting | uint16_t | R/W | 3 |  | 0
| 0x4D8B | 0x4D8D | 19851 | 19853 | Year 2 holiday 21 setting | uint16_t | R/W | 3 |  | 0
| 0x4D8E | 0x4D90 | 19854 | 19856 | Year 2 holiday 22 setting | uint16_t | R/W | 3 |  | 0
| 0x4D91 | 0x4D93 | 19857 | 19859 | Year 2 holiday 23 setting | uint16_t | R/W | 3 |  | 0
| 0x4D94 | 0x4D96 | 19860 | 19862 | Year 2 holiday 24 setting | uint16_t | R/W | 3 |  | 0
| 0x4D97 | 0x4D99 | 19863 | 19865 | Year 2 holiday 25 setting | uint16_t | R/W | 3 |  | 0
| 0x4D9A | 0x4D9C | 19866 | 19868 | Year 2 holiday 26 setting | uint16_t | R/W | 3 |  | 0
| 0x4D9D | 0x4D9F | 19869 | 19871 | Year 2 holiday 27 setting | uint16_t | R/W | 3 |  | 0
| 0x4DA0 | 0x4DA2 | 19872 | 19874 | Year 2 holiday 28 setting | uint16_t | R/W | 3 |  | 0
| 0x4DA3 | 0x4DA5 | 19875 | 19877 | Year 2 holiday 29 setting | uint16_t | R/W | 3 |  | 0
| 0x4DA6 | 0x4DA8 | 19878 | 19880 | Year 2 holiday 30 setting | uint16_t | R/W | 3 |  | 0
| 0x4DA9 | 0x4DA9 | 19881 | 19881 | Year 2 Setting Year | uint16_t | R/W | 1 |  | 2025
| 0x4DAA | 0x4DAA | 19882 | 19882 | Year 2 Holiday Number setting | uint16_t | R/W | 1 |  | 0
| 0x4DAB | 0x4DAD | 19883 | 19885 | Year 3 holiday 1 setting | uint16_t | R/W | 3 |  | 0
| 0x4DAE | 0x4DB0 | 19886 | 19888 | Year 3 holiday 2 setting | uint16_t | R/W | 3 |  | 0
| 0x4DB1 | 0x4DB3 | 19889 | 19891 | Year 3 holiday 3 setting | uint16_t | R/W | 3 |  | 0
| 0x4DB4 | 0x4DB6 | 19892 | 19894 | Year 3 holiday 4 setting | uint16_t | R/W | 3 |  | 0
| 0x4DB7 | 0x4DB9 | 19895 | 19897 | Year 3 holiday 5 setting | uint16_t | R/W | 3 |  | 0
| 0x4DBA | 0x4DBC | 19898 | 19900 | Year 3 holiday 6 setting | uint16_t | R/W | 3 |  | 0
| 0x4DBD | 0x4DBF | 19901 | 19903 | Year 3 holiday 7 setting | uint16_t | R/W | 3 |  | 0
| 0x4DC0 | 0x4DC2 | 19904 | 19906 | Year 3 holiday 8 setting | uint16_t | R/W | 3 |  | 0
| 0x4DC3 | 0x4DC5 | 19907 | 19909 | Year 3 holiday 9 setting | uint16_t | R/W | 3 |  | 0
| 0x4DC6 | 0x4DC8 | 19910 | 19912 | Year 3 holiday 10 setting | uint16_t | R/W | 3 |  | 0
| 0x4DC9 | 0x4DCB | 19913 | 19915 | Year 3 holiday 11 setting | uint16_t | R/W | 3 |  | 0
| 0x4DCC | 0x4DCE | 19916 | 19918 | Year 3 holiday 12 setting | uint16_t | R/W | 3 |  | 0
| 0x4DCF | 0x4DD1 | 19919 | 19921 | Year 3 holiday 13 setting | uint16_t | R/W | 3 |  | 0
| 0x4DD2 | 0x4DD4 | 19922 | 19924 | Year 3 holiday 14 setting | uint16_t | R/W | 3 |  | 0
| 0x4DD5 | 0x4DD7 | 19925 | 19927 | Year 3 holiday 15 setting | uint16_t | R/W | 3 |  | 0
| 0x4DD8 | 0x4DDA | 19928 | 19930 | Year 3 holiday 16 setting | uint16_t | R/W | 3 |  | 0
| 0x4DDB | 0x4DDD | 19931 | 19933 | Year 3 holiday 17 setting | uint16_t | R/W | 3 |  | 0
| 0x4DDE | 0x4DE0 | 19934 | 19936 | Year 3 holiday 18 setting | uint16_t | R/W | 3 |  | 0
| 0x4DE1 | 0x4DE3 | 19937 | 19939 | Year 3 holiday 19 setting | uint16_t | R/W | 3 |  | 0
| 0x4DE4 | 0x4DE6 | 19940 | 19942 | Year 3 holiday 20 setting | uint16_t | R/W | 3 |  | 0
| 0x4DE7 | 0x4DE9 | 19943 | 19945 | Year 3 holiday 21 setting | uint16_t | R/W | 3 |  | 0
| 0x4DEA | 0x4DEC | 19946 | 19948 | Year 3 holiday 22 setting | uint16_t | R/W | 3 |  | 0
| 0x4DED | 0x4DEF | 19949 | 19951 | Year 3 holiday 23 setting | uint16_t | R/W | 3 |  | 0
| 0x4DF0 | 0x4DF2 | 19952 | 19954 | Year 3 holiday 24 setting | uint16_t | R/W | 3 |  | 0
| 0x4DF3 | 0x4DF5 | 19955 | 19957 | Year 3 holiday 25 setting | uint16_t | R/W | 3 |  | 0
| 0x4DF6 | 0x4DF8 | 19958 | 19960 | Year 3 holiday 26 setting | uint16_t | R/W | 3 |  | 0
| 0x4DF9 | 0x4DFB | 19961 | 19963 | Year 3 holiday 27 setting | uint16_t | R/W | 3 |  | 0
| 0x4DFC | 0x4DFE | 19964 | 19966 | Year 3 holiday 28 setting | uint16_t | R/W | 3 |  | 0
| 0x4DFF | 0x4E01 | 19967 | 19969 | Year 3 holiday 29 setting | uint16_t | R/W | 3 |  | 0
| 0x4E02 | 0x4E04 | 19970 | 19972 | Year 3 holiday 30 setting | uint16_t | R/W | 3 |  | 0
| 0x4E05 | 0x4E05 | 19973 | 19973 | Year 3 Setting Year | uint16_t | R/W | 1 |  | 2026
| 0x4E06 | 0x4E06 | 19974 | 19974 | Year 3 Holiday Number setting | uint16_t | R/W | 1 |  | 0
| 0x4E07 | 0x4E09 | 19975 | 19977 | Year 4 holiday 1 setting | uint16_t | R/W | 3 |  | 0
| 0x4E0A | 0x4E0C | 19978 | 19980 | Year 4 holiday 2 setting | uint16_t | R/W | 3 |  | 0
| 0x4E0D | 0x4E0F | 19981 | 19983 | Year 4 holiday 3 setting | uint16_t | R/W | 3 |  | 0
| 0x4E10 | 0x4E12 | 19984 | 19986 | Year 4 holiday 4 setting | uint16_t | R/W | 3 |  | 0
| 0x4E13 | 0x4E15 | 19987 | 19989 | Year 4 holiday 5 setting | uint16_t | R/W | 3 |  | 0
| 0x4E16 | 0x4E18 | 19990 | 19992 | Year 4 holiday 6 setting | uint16_t | R/W | 3 |  | 0
| 0x4E19 | 0x4E1B | 19993 | 19995 | Year 4 holiday 7 setting | uint16_t | R/W | 3 |  | 0
| 0x4E1C | 0x4E1E | 19996 | 19998 | Year 4 holiday 8 setting | uint16_t | R/W | 3 |  | 0
| 0x4E1F | 0x4E21 | 19999 | 20001 | Year 4 holiday 9 setting | uint16_t | R/W | 3 |  | 0
| 0x4E22 | 0x4E24 | 20002 | 20004 | Year 4 holiday 10 setting | uint16_t | R/W | 3 |  | 0
| 0x4E25 | 0x4E27 | 20005 | 20007 | Year 4 holiday 11 setting | uint16_t | R/W | 3 |  | 0
| 0x4E28 | 0x4E2A | 20008 | 20010 | Year 4 holiday 12 setting | uint16_t | R/W | 3 |  | 0
| 0x4E2B | 0x4E2D | 20011 | 20013 | Year 4 holiday 13 setting | uint16_t | R/W | 3 |  | 0
| 0x4E2E | 0x4E30 | 20014 | 20016 | Year 4 holiday 14 setting | uint16_t | R/W | 3 |  | 0
| 0x4E31 | 0x4E33 | 20017 | 20019 | Year 4 holiday 15 setting | uint16_t | R/W | 3 |  | 0
| 0x4E34 | 0x4E36 | 20020 | 20022 | Year 4 holiday 16 setting | uint16_t | R/W | 3 |  | 0
| 0x4E37 | 0x4E39 | 20023 | 20025 | Year 4 holiday 17 setting | uint16_t | R/W | 3 |  | 0
| 0x4E3A | 0x4E3C | 20026 | 20028 | Year 4 holiday 18 setting | uint16_t | R/W | 3 |  | 0
| 0x4E3D | 0x4E3F | 20029 | 20031 | Year 4 holiday 19 setting | uint16_t | R/W | 3 |  | 0
| 0x4E40 | 0x4E42 | 20032 | 20034 | Year 4 holiday 20 setting | uint16_t | R/W | 3 |  | 0
| 0x4E43 | 0x4E45 | 20035 | 20037 | Year 4 holiday 21 setting | uint16_t | R/W | 3 |  | 0
| 0x4E46 | 0x4E48 | 20038 | 20040 | Year 4 holiday 22 setting | uint16_t | R/W | 3 |  | 0
| 0x4E49 | 0x4E4B | 20041 | 20043 | Year 4 holiday 23 setting | uint16_t | R/W | 3 |  | 0
| 0x4E4C | 0x4E4E | 20044 | 20046 | Year 4 holiday 24 setting | uint16_t | R/W | 3 |  | 0
| 0x4E4F | 0x4E51 | 20047 | 20049 | Year 4 holiday 25 setting | uint16_t | R/W | 3 |  | 0
| 0x4E52 | 0x4E54 | 20050 | 20052 | Year 4 holiday 26 setting | uint16_t | R/W | 3 |  | 0
| 0x4E55 | 0x4E57 | 20053 | 20055 | Year 4 holiday 27 setting | uint16_t | R/W | 3 |  | 0
| 0x4E58 | 0x4E5A | 20056 | 20058 | Year 4 holiday 28 setting | uint16_t | R/W | 3 |  | 0
| 0x4E5B | 0x4E5D | 20059 | 20061 | Year 4 holiday 29 setting | uint16_t | R/W | 3 |  | 0
| 0x4E5E | 0x4E60 | 20062 | 20064 | Year 4 holiday 30 setting | uint16_t | R/W | 3 |  | 0
| 0x4E61 | 0x4E61 | 20065 | 20065 | Year 4 Setting Year | uint16_t | R/W | 1 |  | 2027
| 0x4E62 | 0x4E62 | 20066 | 20066 | Year 4 Holiday Number setting | uint16_t | R/W | 1 |  | 0
| 0x4E63 | 0x4E65 | 20067 | 20069 | Year 5 holiday 1 setting | uint16_t | R/W | 3 |  | 0
| 0x4E66 | 0x4E68 | 20070 | 20072 | Year 5 holiday 2 setting | uint16_t | R/W | 3 |  | 0
| 0x4E69 | 0x4E6B | 20073 | 20075 | Year 5 holiday 3 setting | uint16_t | R/W | 3 |  | 0
| 0x4E6C | 0x4E6E | 20076 | 20078 | Year 5 holiday 4 setting | uint16_t | R/W | 3 |  | 0
| 0x4E6F | 0x4E71 | 20079 | 20081 | Year 5 holiday 5 setting | uint16_t | R/W | 3 |  | 0
| 0x4E72 | 0x4E74 | 20082 | 20084 | Year 5 holiday 6 setting | uint16_t | R/W | 3 |  | 0
| 0x4E75 | 0x4E77 | 20085 | 20087 | Year 5 holiday 7 setting | uint16_t | R/W | 3 |  | 0
| 0x4E78 | 0x4E7A | 20088 | 20090 | Year 5 holiday 8 setting | uint16_t | R/W | 3 |  | 0
| 0x4E7B | 0x4E7D | 20091 | 20093 | Year 5 holiday 9 setting | uint16_t | R/W | 3 |  | 0
| 0x4E7E | 0x4E80 | 20094 | 20096 | Year 5 holiday 10 setting | uint16_t | R/W | 3 |  | 0
| 0x4E81 | 0x4E83 | 20097 | 20099 | Year 5 holiday 11 setting | uint16_t | R/W | 3 |  | 0
| 0x4E84 | 0x4E86 | 20100 | 20102 | Year 5 holiday 12 setting | uint16_t | R/W | 3 |  | 0
| 0x4E87 | 0x4E89 | 20103 | 20105 | Year 5 holiday 13 setting | uint16_t | R/W | 3 |  | 0
| 0x4E8A | 0x4E8C | 20106 | 20108 | Year 5 holiday 14 setting | uint16_t | R/W | 3 |  | 0
| 0x4E8D | 0x4E8F | 20109 | 20111 | Year 5 holiday 15 setting | uint16_t | R/W | 3 |  | 0
| 0x4E90 | 0x4E92 | 20112 | 20114 | Year 5 holiday 16 setting | uint16_t | R/W | 3 |  | 0
| 0x4E93 | 0x4E95 | 20115 | 20117 | Year 5 holiday 17 setting | uint16_t | R/W | 3 |  | 0
| 0x4E96 | 0x4E98 | 20118 | 20120 | Year 5 holiday 18 setting | uint16_t | R/W | 3 |  | 0
| 0x4E99 | 0x4E9B | 20121 | 20123 | Year 5 holiday 19 setting | uint16_t | R/W | 3 |  | 0
| 0x4E9C | 0x4E9E | 20124 | 20126 | Year 5 holiday 20 setting | uint16_t | R/W | 3 |  | 0
| 0x4E9F | 0x4EA1 | 20127 | 20129 | Year 5 holiday 21 setting | uint16_t | R/W | 3 |  | 0
| 0x4EA2 | 0x4EA4 | 20130 | 20132 | Year 5 holiday 22 setting | uint16_t | R/W | 3 |  | 0
| 0x4EA5 | 0x4EA7 | 20133 | 20135 | Year 5 holiday 23 setting | uint16_t | R/W | 3 |  | 0
| 0x4EA8 | 0x4EAA | 20136 | 20138 | Year 5 holiday 24 setting | uint16_t | R/W | 3 |  | 0
| 0x4EAB | 0x4EAD | 20139 | 20141 | Year 5 holiday 25 setting | uint16_t | R/W | 3 |  | 0
| 0x4EAE | 0x4EB0 | 20142 | 20144 | Year 5 holiday 26 setting | uint16_t | R/W | 3 |  | 0
| 0x4EB1 | 0x4EB3 | 20145 | 20147 | Year 5 holiday 27 setting | uint16_t | R/W | 3 |  | 0
| 0x4EB4 | 0x4EB6 | 20148 | 20150 | Year 5 holiday 28 setting | uint16_t | R/W | 3 |  | 0
| 0x4EB7 | 0x4EB9 | 20151 | 20153 | Year 5 holiday 29 setting | uint16_t | R/W | 3 |  | 0
| 0x4EBA | 0x4EBC | 20154 | 20156 | Year 5 holiday 30 setting | uint16_t | R/W | 3 |  | 0
| 0x4EBD | 0x4EBD | 20157 | 20157 | Year 5 Setting Year | uint16_t | R/W | 1 |  | 2028
| 0x4EBE | 0x4EBE | 20158 | 20158 | Year 5 Holiday Number setting | uint16_t | R/W | 1 |  | 0
| 0x4EBF | 0x4EC1 | 20159 | 20161 | Year 6 holiday 1 setting | uint16_t | R/W | 3 |  | 0
| 0x4EC2 | 0x4EC4 | 20162 | 20164 | Year 6 holiday 2 setting | uint16_t | R/W | 3 |  | 0
| 0x4EC5 | 0x4EC7 | 20165 | 20167 | Year 6 holiday 3 setting | uint16_t | R/W | 3 |  | 0
| 0x4EC8 | 0x4ECA | 20168 | 20170 | Year 6 holiday 4 setting | uint16_t | R/W | 3 |  | 0
| 0x4ECB | 0x4ECD | 20171 | 20173 | Year 6 holiday 5 setting | uint16_t | R/W | 3 |  | 0
| 0x4ECE | 0x4ED0 | 20174 | 20176 | Year 6 holiday 6 setting | uint16_t | R/W | 3 |  | 0
| 0x4ED1 | 0x4ED3 | 20177 | 20179 | Year 6 holiday 7 setting | uint16_t | R/W | 3 |  | 0
| 0x4ED4 | 0x4ED6 | 20180 | 20182 | Year 6 holiday 8 setting | uint16_t | R/W | 3 |  | 0
| 0x4ED7 | 0x4ED9 | 20183 | 20185 | Year 6 holiday 9 setting | uint16_t | R/W | 3 |  | 0
| 0x4EDA | 0x4EDC | 20186 | 20188 | Year 6 holiday 10 setting | uint16_t | R/W | 3 |  | 0
| 0x4EDD | 0x4EDF | 20189 | 20191 | Year 6 holiday 11 setting | uint16_t | R/W | 3 |  | 0
| 0x4EE0 | 0x4EE2 | 20192 | 20194 | Year 6 holiday 12 setting | uint16_t | R/W | 3 |  | 0
| 0x4EE3 | 0x4EE5 | 20195 | 20197 | Year 6 holiday 13 setting | uint16_t | R/W | 3 |  | 0
| 0x4EE6 | 0x4EE8 | 20198 | 20200 | Year 6 holiday 14 setting | uint16_t | R/W | 3 |  | 0
| 0x4EE9 | 0x4EEB | 20201 | 20203 | Year 6 holiday 15 setting | uint16_t | R/W | 3 |  | 0
| 0x4EEC | 0x4EEE | 20204 | 20206 | Year 6 holiday 16 setting | uint16_t | R/W | 3 |  | 0
| 0x4EEF | 0x4EF1 | 20207 | 20209 | Year 6 holiday 17 setting | uint16_t | R/W | 3 |  | 0
| 0x4EF2 | 0x4EF4 | 20210 | 20212 | Year 6 holiday 18 setting | uint16_t | R/W | 3 |  | 0
| 0x4EF5 | 0x4EF7 | 20213 | 20215 | Year 6 holiday 19 setting | uint16_t | R/W | 3 |  | 0
| 0x4EF8 | 0x4EFA | 20216 | 20218 | Year 6 holiday 20 setting | uint16_t | R/W | 3 |  | 0
| 0x4EFB | 0x4EFD | 20219 | 20221 | Year 6 holiday 21 setting | uint16_t | R/W | 3 |  | 0
| 0x4EFE | 0x4F00 | 20222 | 20224 | Year 6 holiday 22 setting | uint16_t | R/W | 3 |  | 0
| 0x4F01 | 0x4F03 | 20225 | 20227 | Year 6 holiday 23 setting | uint16_t | R/W | 3 |  | 0
| 0x4F04 | 0x4F06 | 20228 | 20230 | Year 6 holiday 24 setting | uint16_t | R/W | 3 |  | 0
| 0x4F07 | 0x4F09 | 20231 | 20233 | Year 6 holiday 25 setting | uint16_t | R/W | 3 |  | 0
| 0x4F0A | 0x4F0C | 20234 | 20236 | Year 6 holiday 26 setting | uint16_t | R/W | 3 |  | 0
| 0x4F0D | 0x4F0F | 20237 | 20239 | Year 6 holiday 27 setting | uint16_t | R/W | 3 |  | 0
| 0x4F10 | 0x4F12 | 20240 | 20242 | Year 6 holiday 28 setting | uint16_t | R/W | 3 |  | 0
| 0x4F13 | 0x4F15 | 20243 | 20245 | Year 6 holiday 29 setting | uint16_t | R/W | 3 |  | 0
| 0x4F16 | 0x4F18 | 20246 | 20248 | Year 6 holiday 30 setting | uint16_t | R/W | 3 |  | 0
| 0x4F19 | 0x4F19 | 20249 | 20249 | Year 6 setting Year | uint16_t | R/W | 1 |  | 2029
| 0x4F1A | 0x4F1A | 20250 | 20250 | Year 6 Number of holidays | uint16_t | R/W | 1 |  | 0
| 0x4F1B | 0x4F1D | 20251 | 20253 | Year 7 holiday 1 setting | uint16_t | R/W | 3 |  | 0
| 0x4F1E | 0x4F20 | 20254 | 20256 | Year 7 holiday 2 setting | uint16_t | R/W | 3 |  | 0
| 0x4F21 | 0x4F23 | 20257 | 20259 | Year 7 holiday 3 setting | uint16_t | R/W | 3 |  | 0
| 0x4F24 | 0x4F26 | 20260 | 20262 | Year 7 holiday 4 setting | uint16_t | R/W | 3 |  | 0
| 0x4F27 | 0x4F29 | 20263 | 20265 | Year 7 holiday 5 setting | uint16_t | R/W | 3 |  | 0
| 0x4F2A | 0x4F2C | 20266 | 20268 | Year 7 holiday 6 setting | uint16_t | R/W | 3 |  | 0
| 0x4F2D | 0x4F2F | 20269 | 20271 | Year 7 holiday 7 setting | uint16_t | R/W | 3 |  | 0
| 0x4F30 | 0x4F32 | 20272 | 20274 | Year 7 holiday 8 setting | uint16_t | R/W | 3 |  | 0
| 0x4F33 | 0x4F35 | 20275 | 20277 | Year 7 holiday 9 setting | uint16_t | R/W | 3 |  | 0
| 0x4F36 | 0x4F38 | 20278 | 20280 | Year 7 holiday 10 setting | uint16_t | R/W | 3 |  | 0
| 0x4F39 | 0x4F3B | 20281 | 20283 | Year 7 holiday 11 setting | uint16_t | R/W | 3 |  | 0
| 0x4F3C | 0x4F3E | 20284 | 20286 | Year 7 holiday 12 setting | uint16_t | R/W | 3 |  | 0
| 0x4F3F | 0x4F41 | 20287 | 20289 | Year 7 holiday 13 setting | uint16_t | R/W | 3 |  | 0
| 0x4F42 | 0x4F44 | 20290 | 20292 | Year 7 holiday 14 setting | uint16_t | R/W | 3 |  | 0
| 0x4F45 | 0x4F47 | 20293 | 20295 | Year 7 holiday 15 setting | uint16_t | R/W | 3 |  | 0
| 0x4F48 | 0x4F4A | 20296 | 20298 | Year 7 holiday 16 setting | uint16_t | R/W | 3 |  | 0
| 0x4F4B | 0x4F4D | 20299 | 20301 | Year 7 holiday 17 setting | uint16_t | R/W | 3 |  | 0
| 0x4F4E | 0x4F50 | 20302 | 20304 | Year 7 holiday 18 setting | uint16_t | R/W | 3 |  | 0
| 0x4F51 | 0x4F53 | 20305 | 20307 | Year 7 holiday 19 setting | uint16_t | R/W | 3 |  | 0
| 0x4F54 | 0x4F56 | 20308 | 20310 | Year 7 holiday 20 setting | uint16_t | R/W | 3 |  | 0
| 0x4F57 | 0x4F59 | 20311 | 20313 | Year 7 holiday 21 setting | uint16_t | R/W | 3 |  | 0
| 0x4F5A | 0x4F5C | 20314 | 20316 | Year 7 holiday 22 setting | uint16_t | R/W | 3 |  | 0
| 0x4F5D | 0x4F5F | 20317 | 20319 | Year 7 holiday 23 setting | uint16_t | R/W | 3 |  | 0
| 0x4F60 | 0x4F62 | 20320 | 20322 | Year 7 holiday 24 setting | uint16_t | R/W | 3 |  | 0
| 0x4F63 | 0x4F65 | 20323 | 20325 | Year 7 holiday 25 setting | uint16_t | R/W | 3 |  | 0
| 0x4F66 | 0x4F68 | 20326 | 20328 | Year 7 holiday 26 setting | uint16_t | R/W | 3 |  | 0
| 0x4F69 | 0x4F6B | 20329 | 20331 | Year 7 holiday 27 setting | uint16_t | R/W | 3 |  | 0
| 0x4F6C | 0x4F6E | 20332 | 20334 | Year 7 holiday 28 setting | uint16_t | R/W | 3 |  | 0
| 0x4F6F | 0x4F71 | 20335 | 20337 | Year 7 holiday 29 setting | uint16_t | R/W | 3 |  | 0
| 0x4F72 | 0x4F74 | 20338 | 20340 | Year 7 holiday 30 setting | uint16_t | R/W | 3 |  | 0
| 0x4F75 | 0x4F75 | 20341 | 20341 | Year 7 Setting Year | uint16_t | R/W | 1 |  | 2030
| 0x4F76 | 0x4F76 | 20342 | 20342 | Year 7 Holiday Number setting | uint16_t | R/W | 1 |  | 0
| 0x4F77 | 0x4F79 | 20343 | 20345 | Year 8 holiday 1 setting | uint16_t | R/W | 3 |  | 0
| 0x4F7A | 0x4F7C | 20346 | 20348 | Year 8 holiday 2 setting | uint16_t | R/W | 3 |  | 0
| 0x4F7D | 0x4F7F | 20349 | 20351 | Year 8 holiday 3 setting | uint16_t | R/W | 3 |  | 0
| 0x4F80 | 0x4F82 | 20352 | 20354 | Year 8 holiday 4 setting | uint16_t | R/W | 3 |  | 0
| 0x4F83 | 0x4F85 | 20355 | 20357 | Year 8 holiday 5 setting | uint16_t | R/W | 3 |  | 0
| 0x4F86 | 0x4F88 | 20358 | 20360 | Year 8 holiday 6 setting | uint16_t | R/W | 3 |  | 0
| 0x4F89 | 0x4F8B | 20361 | 20363 | Year 8 holiday 7 setting | uint16_t | R/W | 3 |  | 0
| 0x4F8C | 0x4F8E | 20364 | 20366 | Year 8 holiday 8 setting | uint16_t | R/W | 3 |  | 0
| 0x4F8F | 0x4F91 | 20367 | 20369 | Year 8 holiday 9 setting | uint16_t | R/W | 3 |  | 0
| 0x4F92 | 0x4F94 | 20370 | 20372 | Year 8 holiday 10 setting | uint16_t | R/W | 3 |  | 0
| 0x4F95 | 0x4F97 | 20373 | 20375 | Year 8 holiday 11 setting | uint16_t | R/W | 3 |  | 0
| 0x4F98 | 0x4F9A | 20376 | 20378 | Year 8 holiday 12 setting | uint16_t | R/W | 3 |  | 0
| 0x4F9B | 0x4F9D | 20379 | 20381 | Year 8 holiday 13 setting | uint16_t | R/W | 3 |  | 0
| 0x4F9E | 0x4FA0 | 20382 | 20384 | Year 8 holiday 14 setting | uint16_t | R/W | 3 |  | 0
| 0x4FA1 | 0x4FA3 | 20385 | 20387 | Year 8 holiday 15 setting | uint16_t | R/W | 3 |  | 0
| 0x4FA4 | 0x4FA6 | 20388 | 20390 | Year 8 holiday 16 setting | uint16_t | R/W | 3 |  | 0
| 0x4FA7 | 0x4FA9 | 20391 | 20393 | Year 8 holiday 17 setting | uint16_t | R/W | 3 |  | 0
| 0x4FAA | 0x4FAC | 20394 | 20396 | Year 8 holiday 18 setting | uint16_t | R/W | 3 |  | 0
| 0x4FAD | 0x4FAF | 20397 | 20399 | Year 8 holiday 19 setting | uint16_t | R/W | 3 |  | 0
| 0x4FB0 | 0x4FB2 | 20400 | 20402 | Year 8 holiday 20 setting | uint16_t | R/W | 3 |  | 0
| 0x4FB3 | 0x4FB5 | 20403 | 20405 | Year 8 holiday 21 setting | uint16_t | R/W | 3 |  | 0
| 0x4FB6 | 0x4FB8 | 20406 | 20408 | Year 8 holiday 22 setting | uint16_t | R/W | 3 |  | 0
| 0x4FB9 | 0x4FBB | 20409 | 20411 | Year 8 holiday 23 setting | uint16_t | R/W | 3 |  | 0
| 0x4FBC | 0x4FBE | 20412 | 20414 | Year 8 holiday 24 setting | uint16_t | R/W | 3 |  | 0
| 0x4FBF | 0x4FC1 | 20415 | 20417 | Year 8 holiday 25 setting | uint16_t | R/W | 3 |  | 0
| 0x4FC2 | 0x4FC4 | 20418 | 20420 | Year 8 holiday 26 setting | uint16_t | R/W | 3 |  | 0
| 0x4FC5 | 0x4FC7 | 20421 | 20423 | Year 8 holiday 27 setting | uint16_t | R/W | 3 |  | 0
| 0x4FC8 | 0x4FCA | 20424 | 20426 | Year 8 holiday 28 setting | uint16_t | R/W | 3 |  | 0
| 0x4FCB | 0x4FCD | 20427 | 20429 | Year 8 holiday 29 setting | uint16_t | R/W | 3 |  | 0
| 0x4FCE | 0x4FD0 | 20430 | 20432 | Year 8 holiday 30 setting | uint16_t | R/W | 3 |  | 0
| 0x4FD1 | 0x4FD1 | 20433 | 20433 | Year 8 Setting Year | uint16_t | R/W | 1 |  | 2031
| 0x4FD2 | 0x4FD2 | 20434 | 20434 | Year 8 Holiday Number setting | uint16_t | R/W | 1 |  | 0
| 0x4FD3 | 0x4FD5 | 20435 | 20437 | Year 9 holiday 1 setting | uint16_t | R/W | 3 |  | 0
| 0x4FD6 | 0x4FD8 | 20438 | 20440 | Year 9 holiday 2 setting | uint16_t | R/W | 3 |  | 0
| 0x4FD9 | 0x4FDB | 20441 | 20443 | Year 9 holiday 3 setting | uint16_t | R/W | 3 |  | 0
| 0x4FDC | 0x4FDE | 20444 | 20446 | Year 9 holiday 4 setting | uint16_t | R/W | 3 |  | 0
| 0x4FDF | 0x4FE1 | 20447 | 20449 | Year 9 holiday 5 setting | uint16_t | R/W | 3 |  | 0
| 0x4FE2 | 0x4FE4 | 20450 | 20452 | Year 9 holiday 6 setting | uint16_t | R/W | 3 |  | 0
| 0x4FE5 | 0x4FE7 | 20453 | 20455 | Year 9 holiday 7 setting | uint16_t | R/W | 3 |  | 0
| 0x4FE8 | 0x4FEA | 20456 | 20458 | Year 9 holiday 8 setting | uint16_t | R/W | 3 |  | 0
| 0x4FEB | 0x4FED | 20459 | 20461 | Year 9 holiday 9 setting | uint16_t | R/W | 3 |  | 0
| 0x4FEE | 0x4FF0 | 20462 | 20464 | Year 9 holiday 10 setting | uint16_t | R/W | 3 |  | 0
| 0x4FF1 | 0x4FF3 | 20465 | 20467 | Year 9 holiday 11 setting | uint16_t | R/W | 3 |  | 0
| 0x4FF4 | 0x4FF6 | 20468 | 20470 | Year 9 holiday 12 setting | uint16_t | R/W | 3 |  | 0
| 0x4FF7 | 0x4FF9 | 20471 | 20473 | Year 9 holiday 13 setting | uint16_t | R/W | 3 |  | 0
| 0x4FFA | 0x4FFC | 20474 | 20476 | Year 9 holiday 14 setting | uint16_t | R/W | 3 |  | 0
| 0x4FFD | 0x4FFF | 20477 | 20479 | Year 9 holiday 15 setting | uint16_t | R/W | 3 |  | 0
| 0x5000 | 0x5002 | 20480 | 20482 | Year 9 holiday 16 setting | uint16_t | R/W | 3 |  | 0
| 0x5003 | 0x5005 | 20483 | 20485 | Year 9 holiday 17 setting | uint16_t | R/W | 3 |  | 0
| 0x5006 | 0x5008 | 20486 | 20488 | Year 9 holiday 18 setting | uint16_t | R/W | 3 |  | 0
| 0x5009 | 0x500B | 20489 | 20491 | Year 9 holiday 19 setting | uint16_t | R/W | 3 |  | 0
| 0x500C | 0x500E | 20492 | 20494 | Year 9 holiday 20 setting | uint16_t | R/W | 3 |  | 0
| 0x500F | 0x5011 | 20495 | 20497 | Year 9 holiday 21 setting | uint16_t | R/W | 3 |  | 0
| 0x5012 | 0x5014 | 20498 | 20500 | Year 9 holiday 22 setting | uint16_t | R/W | 3 |  | 0
| 0x5015 | 0x5017 | 20501 | 20503 | Year 9 holiday 23 setting | uint16_t | R/W | 3 |  | 0
| 0x5018 | 0x501A | 20504 | 20506 | Year 9 holiday 24 setting | uint16_t | R/W | 3 |  | 0
| 0x501B | 0x501D | 20507 | 20509 | Year 9 holiday 25 setting | uint16_t | R/W | 3 |  | 0
| 0x501E | 0x5020 | 20510 | 20512 | Year 9 holiday 26 setting | uint16_t | R/W | 3 |  | 0
| 0x5021 | 0x5023 | 20513 | 20515 | Year 9 holiday 27 setting | uint16_t | R/W | 3 |  | 0
| 0x5024 | 0x5026 | 20516 | 20518 | Year 9 holiday 28 setting | uint16_t | R/W | 3 |  | 0
| 0x5027 | 0x5029 | 20519 | 20521 | Year 9 holiday 29 setting | uint16_t | R/W | 3 |  | 0
| 0x502A | 0x502C | 20522 | 20524 | Year 9 holiday 30 setting | uint16_t | R/W | 3 |  | 0
| 0x502D | 0x502D | 20525 | 20525 | Year 9 Setting Year | uint16_t | R/W | 1
| 0x502E | 0x502E | 20526 | 20526 | Year 9 Holiday Number setting | uint16_t | R/W | 1 |  | 0
| 0x502F | 0x5031 | 20527 | 20529 | Year 10 holiday 1 setting | uint16_t | R/W | 3 |  | 0
| 0x5032 | 0x5034 | 20530 | 20532 | Year 10 holiday 2 setting | uint16_t | R/W | 3 |  | 0
| 0x5035 | 0x5037 | 20533 | 20535 | Year 10 holiday 3 setting | uint16_t | R/W | 3 |  | 0
| 0x5038 | 0x503A | 20536 | 20538 | Year 10 holiday 4 setting | uint16_t | R/W | 3 |  | 0
| 0x503B | 0x503D | 20539 | 20541 | Year 10 holiday 5 setting | uint16_t | R/W | 3 |  | 0
| 0x503E | 0x5040 | 20542 | 20544 | Year 10 holiday 6 setting | uint16_t | R/W | 3 |  | 0
| 0x5041 | 0x5043 | 20545 | 20547 | Year 10 holiday 7 setting | uint16_t | R/W | 3 |  | 0
| 0x5044 | 0x5046 | 20548 | 20550 | Year 10 holiday 8 setting | uint16_t | R/W | 3 |  | 0
| 0x5047 | 0x5049 | 20551 | 20553 | Year 10 holiday 9 setting | uint16_t | R/W | 3 |  | 0
| 0x504A | 0x504C | 20554 | 20556 | Year 10 holiday 10 setting | uint16_t | R/W | 3 |  | 0
| 0x504D | 0x504F | 20557 | 20559 | Year 10 holiday 11 setting | uint16_t | R/W | 3 |  | 0
| 0x5050 | 0x5052 | 20560 | 20562 | Year 10 holiday 12 setting | uint16_t | R/W | 3 |  | 0
| 0x5053 | 0x5055 | 20563 | 20565 | Year 10 holiday 13 setting | uint16_t | R/W | 3 |  | 0
| 0x5056 | 0x5058 | 20566 | 20568 | Year 10 holiday 14 setting | uint16_t | R/W | 3 |  | 0
| 0x5059 | 0x505B | 20569 | 20571 | Year 10 holiday 15 setting | uint16_t | R/W | 3 |  | 0
| 0x505C | 0x505E | 20572 | 20574 | Year 10 holiday 16 setting | uint16_t | R/W | 3 |  | 0
| 0x505F | 0x5061 | 20575 | 20577 | Year 10 holiday 17 setting | uint16_t | R/W | 3 |  | 0
| 0x5062 | 0x5064 | 20578 | 20580 | Year 10 holiday 18 setting | uint16_t | R/W | 3 |  | 0
| 0x5065 | 0x5067 | 20581 | 20583 | Year 10 holiday 19 setting | uint16_t | R/W | 3 |  | 0
| 0x5068 | 0x506A | 20584 | 20586 | Year 10 holiday 20 setting | uint16_t | R/W | 3 |  | 0
| 0x506B | 0x506D | 20587 | 20589 | Year 10 holiday 21 setting | uint16_t | R/W | 3 |  | 0
| 0x506E | 0x5070 | 20590 | 20592 | Year 10 holiday 22 setting | uint16_t | R/W | 3 |  | 0
| 0x5071 | 0x5073 | 20593 | 20595 | Year 10 holiday 23 setting | uint16_t | R/W | 3 |  | 0
| 0x5074 | 0x5076 | 20596 | 20598 | Year 10 holiday 24 setting | uint16_t | R/W | 3 |  | 0
| 0x5077 | 0x5079 | 20599 | 20601 | Year 10 holiday 25 setting | uint16_t | R/W | 3 |  | 0
| 0x507A | 0x507C | 20602 | 20604 | Year 10 holiday 26 setting | uint16_t | R/W | 3 |  | 0
| 0x507D | 0x507F | 20605 | 20607 | Year 10 holiday 27 setting | uint16_t | R/W | 3 |  | 0
| 0x5080 | 0x5082 | 20608 | 20610 | Year 10 holiday 28 setting | uint16_t | R/W | 3 |  | 0
| 0x5083 | 0x5085 | 20611 | 20613 | Year 10 holiday 29 setting | uint16_t | R/W | 3 |  | 0
| 0x5086 | 0x5088 | 20614 | 20616 | Year 10 holiday 30 setting | uint16_t | R/W | 3 |  | 0
| 0x5089 | 0x5089 | 20617 | 20617 | Year 10 Setting Year | uint16_t | R/W | 1 | 2000-2099 | 2032
| 0x508A | 0x508A | 20618 | 20618 | Year 10 Holiday Number setting | uint16_t | R/W | 1 | 0-30 | 0
Special weekday schedule settings : 03H Read, 10H Write
| 0x508B | 0x508B | 20619 | 20619 | Enable special weekday schedule | uint16_t | R/W | 1 | 0: Disable 1: Enable If 0, Weekend schedule uses registers 0x7804H & 0x7805H | 0
| 0x508C | 0x508C | 20620 | 20620 | Season 1 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x508D | 0x508D | 20621 | 20621 | Season 1 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x508E | 0x508E | 20622 | 20622 | Season 1 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x508F | 0x508F | 20623 | 20623 | Season 1 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x5090 | 0x5090 | 20624 | 20624 | Season 1 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x5091 | 0x5091 | 20625 | 20625 | Season 1 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x5092 | 0x5092 | 20626 | 20626 | Season 1 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x5093 | 0x5093 | 20627 | 20627 | Season 1 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x5094 | 0x5094 | 20628 | 20628 | Season 2 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x5095 | 0x5095 | 20629 | 20629 | Season 2 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x5096 | 0x5096 | 20630 | 20630 | Season 2 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x5097 | 0x5097 | 20631 | 20631 | Season 2 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x5098 | 0x5098 | 20632 | 20632 | Season 2 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x5099 | 0x5099 | 20633 | 20633 | Season 2 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x509A | 0x509A | 20634 | 20634 | Season 2 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x509B | 0x509B | 20635 | 20635 | Season 2 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x509C | 0x509C | 20636 | 20636 | Season 3 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x509D | 0x509D | 20637 | 20637 | Season 3 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x509E | 0x509E | 20638 | 20638 | Season 3 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x509F | 0x509F | 20639 | 20639 | Season 3 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50A0 | 0x50A0 | 20640 | 20640 | Season 3 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50A1 | 0x50A1 | 20641 | 20641 | Season 3 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50A2 | 0x50A2 | 20642 | 20642 | Season 3 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50A3 | 0x50A3 | 20643 | 20643 | Season 3 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50A4 | 0x50A4 | 20644 | 20644 | Season 4 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x50A5 | 0x50A5 | 20645 | 20645 | Season 4 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50A6 | 0x50A6 | 20646 | 20646 | Season 4 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50A7 | 0x50A7 | 20647 | 20647 | Season 4 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50A8 | 0x50A8 | 20648 | 20648 | Season 4 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50A9 | 0x50A9 | 20649 | 20649 | Season 4 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50AA | 0x50AA | 20650 | 20650 | Season 4 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50AB | 0x50AB | 20651 | 20651 | Season 4 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50AC | 0x50AC | 20652 | 20652 | Season 5 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x50AD | 0x50AD | 20653 | 20653 | Season 5 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50AE | 0x50AE | 20654 | 20654 | Season 5 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50AF | 0x50AF | 20655 | 20655 | Season 5 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50B0 | 0x50B0 | 20656 | 20656 | Season 5 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50B1 | 0x50B1 | 20657 | 20657 | Season 5 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50B2 | 0x50B2 | 20658 | 20658 | Season 5 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50B3 | 0x50B3 | 20659 | 20659 | Season 5 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50B4 | 0x50B4 | 20660 | 20660 | Season 6 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x50B5 | 0x50B5 | 20661 | 20661 | Season 6 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50B6 | 0x50B6 | 20662 | 20662 | Season 6 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50B7 | 0x50B7 | 20663 | 20663 | Season 6 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50B8 | 0x50B8 | 20664 | 20664 | Season 6 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50B9 | 0x50B9 | 20665 | 20665 | Season 6 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50BA | 0x50BA | 20666 | 20666 | Season 6 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50BB | 0x50BB | 20667 | 20667 | Season 6 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50BC | 0x50BC | 20668 | 20668 | Season 7 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x50BD | 0x50BD | 20669 | 20669 | Season 7 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50BE | 0x50BE | 20670 | 20670 | Season 7 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50BF | 0x50BF | 20671 | 20671 | Season 7 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50C0 | 0x50C0 | 20672 | 20672 | Season 7 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50C1 | 0x50C1 | 20673 | 20673 | Season 7 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50C2 | 0x50C2 | 20674 | 20674 | Season 7 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50C3 | 0x50C3 | 20675 | 20675 | Season 7 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50C4 | 0x50C4 | 20676 | 20676 | Season 8 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x50C5 | 0x50C5 | 20677 | 20677 | Season 8 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50C6 | 0x50C6 | 20678 | 20678 | Season 8 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50C7 | 0x50C7 | 20679 | 20679 | Season 8 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50C8 | 0x50C8 | 20680 | 20680 | Season 8 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50C9 | 0x50C9 | 20681 | 20681 | Season 8 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50CA | 0x50CA | 20682 | 20682 | Season 8 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50CB | 0x50CB | 20683 | 20683 | Season 8 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50CC | 0x50CC | 20684 | 20684 | Season 9 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x50CD | 0x50CD | 20685 | 20685 | Season 9 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50CE | 0x50CE | 20686 | 20686 | Season 9 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50CF | 0x50CF | 20687 | 20687 | Season 9 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50D0 | 0x50D0 | 20688 | 20688 | Season 9 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50D1 | 0x50D1 | 20689 | 20689 | Season 9 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50D2 | 0x50D2 | 20690 | 20690 | Season 9 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50D3 | 0x50D3 | 20691 | 20691 | Season 9 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50D4 | 0x50D4 | 20692 | 20692 | Season 10 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x50D5 | 0x50D5 | 20693 | 20693 | Season 10 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50D6 | 0x50D6 | 20694 | 20694 | Season 10 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50D7 | 0x50D7 | 20695 | 20695 | Season 10 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50D8 | 0x50D8 | 20696 | 20696 | Season 10 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50D9 | 0x50D9 | 20697 | 20697 | Season 10 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50DA | 0x50DA | 20698 | 20698 | Season 10 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50DB | 0x50DB | 20699 | 20699 | Season 10 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50DC | 0x50DC | 20700 | 20700 | Season 11 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x50DD | 0x50DD | 20701 | 20701 | Season 11 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50DE | 0x50DE | 20702 | 20702 | Season 11 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50DF | 0x50DF | 20703 | 20703 | Season 11 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50E0 | 0x50E0 | 20704 | 20704 | Season 11 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50E1 | 0x50E1 | 20705 | 20705 | Season 11 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50E2 | 0x50E2 | 20706 | 20706 | Season 11 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50E3 | 0x50E3 | 20707 | 20707 | Season 11 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50E4 | 0x50E4 | 20708 | 20708 | Season 12 weekday schedule enable | uint16_t | R/W | 1 | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled | 0
| 0x50E5 | 0x50E5 | 20709 | 20709 | Season 12 Sunday schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50E6 | 0x50E6 | 20710 | 20710 | Season 12 Monday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50E7 | 0x50E7 | 20711 | 20711 | Season 12 Tuesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50E8 | 0x50E8 | 20712 | 20712 | Season 12 Wednesday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50E9 | 0x50E9 | 20713 | 20713 | Season 12 Thursday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50EA | 0x50EA | 20714 | 20714 | Season 12 Friday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
| 0x50EB | 0x50EB | 20715 | 20715 | Season 12 Saturday Schedule ID | uint16_t | R/W | 1 | 0~14 | 0
1772

## MaxMin
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Max value record code function : 03H Read
| 0x5200 | 0x5201 | 20992 | 20993 | System Frequency Max value | float | R | 2
| 0x5202 | 0x5205 | 20994 | 20997 | System Frequency Max value Timestamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) | uint16_t | R | 4
| 0x5206 | 0x5207 | 20998 | 20999 | Phase A Line-to-Neutral Voltage Max value | float | R | 2
| 0x5208 | 0x520B | 21000 | 21003 | Phase A Line-to-Neutral Voltage Max value Timestamp | uint16_t | R | 4
| 0x520C | 0x520D | 21004 | 21005 | Phase B Line-to-Neutral Voltage Max value | float | R | 2
| 0x520E | 0x5211 | 21006 | 21009 | Phase B Line-to-Neutral Voltage Max value Timestamp | uint16_t | R | 4
| 0x5212 | 0x5213 | 21010 | 21011 | Phase C Line-to-Neutral Voltage Max value | float | R | 2
| 0x5214 | 0x5217 | 21012 | 21015 | Phase C Line-to-Neutral Voltage Max value Timestamp | uint16_t | R | 4
| 0x5218 | 0x5219 | 21016 | 21017 | Phase AB Line-to-Line Voltage Max value | float | R | 2
| 0x521A | 0x521D | 21018 | 21021 | Phase AB Line-to-Line Voltage Max value Timestamp | uint16_t | R | 4
| 0x521E | 0x521F | 21022 | 21023 | Phase BC Line-to-Line Voltage Max value | float | R | 2
| 0x5220 | 0x5223 | 21024 | 21027 | Phase BC Line-to-Line Voltage Max value Timestamp | uint16_t | R | 4
| 0x5224 | 0x5225 | 21028 | 21029 | Phase CA Line-to-Line Voltage Max value | float | R | 2
| 0x5226 | 0x5229 | 21030 | 21033 | Phase CA Line-to-Line Voltage Max value Timestamp | uint16_t | R | 4
| 0x522A | 0x522B | 21034 | 21035 | Phase A Current Max value | float | R | 2
| 0x522C | 0x522F | 21036 | 21039 | Phase A Current Max value Timestamp | uint16_t | R | 4
| 0x5230 | 0x5231 | 21040 | 21041 | Phase A Active Power Max value | float | R | 2
| 0x5232 | 0x5235 | 21042 | 21045 | Phase A Active Power Max value Timestamp | uint16_t | R | 4
| 0x5236 | 0x5237 | 21046 | 21047 | Phase A Reactive Power Max value | float | R | 2
| 0x5238 | 0x523B | 21048 | 21051 | Phase A Reactive Power Max value Timestamp | uint16_t | R | 4
| 0x523C | 0x523D | 21052 | 21053 | Phase A Apparent Power Max value | float | R | 2
| 0x523E | 0x5241 | 21054 | 21057 | Phase A Apparent Power Max value Timestamp | uint16_t | R | 4
| 0x5242 | 0x5243 | 21058 | 21059 | Phase A Power Factor Max value | float | R | 2
| 0x5244 | 0x5247 | 21060 | 21063 | Phase A Power Factor Max value Timestamp | uint16_t | R | 4
| 0x5248 | 0x5249 | 21064 | 21065 | Phase A Voltage THD Max value | float | R | 2
| 0x524A | 0x524D | 21066 | 21069 | Phase A Voltage THD Max value Timestamp | uint16_t | R | 4
| 0x524E | 0x524F | 21070 | 21071 | Phase B Current Max value | float | R | 2
| 0x5250 | 0x5253 | 21072 | 21075 | Phase B Current Max value Timestamp | uint16_t | R | 4
| 0x5254 | 0x5255 | 21076 | 21077 | Phase B Active Power Max value | float | R | 2
| 0x5256 | 0x5259 | 21078 | 21081 | Phase B Active Power Max value Timestamp | uint16_t | R | 4
| 0x525A | 0x525B | 21082 | 21083 | Phase B Reactive Power Max value | float | R | 2
| 0x525C | 0x525F | 21084 | 21087 | Phase B Reactive Power Max value Timestamp | uint16_t | R | 4
| 0x5260 | 0x5261 | 21088 | 21089 | Phase B Apparent Power Max value | float | R | 2
| 0x5262 | 0x5265 | 21090 | 21093 | Phase B Apparent Power Max value Timestamp | uint16_t | R | 4
| 0x5266 | 0x5267 | 21094 | 21095 | Phase B Power Factor Max value | float | R | 2
| 0x5268 | 0x526B | 21096 | 21099 | Phase B Power Factor Max value Timestamp | uint16_t | R | 4
| 0x526C | 0x526D | 21100 | 21101 | Phase B Voltage THD Max value | float | R | 2
| 0x526E | 0x5271 | 21102 | 21105 | Phase B Voltage THD Max value Timestamp | uint16_t | R | 4
| 0x5272 | 0x5273 | 21106 | 21107 | Phase C Current Max value Timestamp | float | R | 2
| 0x5274 | 0x5277 | 21108 | 21111 | Phase C Current Max value Timestamp | uint16_t | R | 4
| 0x5278 | 0x5279 | 21112 | 21113 | Phase C Active Power Max value | float | R | 2
| 0x527A | 0x527D | 21114 | 21117 | Phase C Active Power Max value Timestamp | uint16_t | R | 4
| 0x527E | 0x527F | 21118 | 21119 | Phase C Reactive Power Max value | float | R | 2
| 0x5280 | 0x5283 | 21120 | 21123 | Phase C Reactive Power Max value Timestamp | uint16_t | R | 4
| 0x5284 | 0x5285 | 21124 | 21125 | Phase C Apparent Power Max value | float | R | 2
| 0x5286 | 0x5289 | 21126 | 21129 | Phase C Apparent Power Max value Timestamp | uint16_t | R | 4
| 0x528A | 0x528B | 21130 | 21131 | Phase C Power Factor Max value | float | R | 2
| 0x528C | 0x528F | 21132 | 21135 | Phase C Power Factor Max value Timestamp | uint16_t | R | 4
| 0x5290 | 0x5291 | 21136 | 21137 | Phase C Voltage THD Max value | float | R | 2
| 0x5292 | 0x5295 | 21138 | 21141 | Phase C Voltage THD Max value Timestamp | uint16_t | R | 4
| 0x5296 | 0x5297 | 21142 | 21143 | Voltage Unbalance Factor Magnitude Max value | float | R | 2
| 0x5298 | 0x529B | 21144 | 21147 | Voltage Unbalance Factor Magnitude Max value Timestamp | uint16_t | R | 4
| 0x529C | 0x529D | 21148 | 21149 | Input Channel 1 Current Max value | float | R | 2
| 0x529E | 0x52A1 | 21150 | 21153 | Input Channel 1 Current Max value Timestamp | uint16_t | R | 4
| 0x52A2 | 0x52A3 | 21154 | 21155 | Input Channel 1 Active Power Max value | float | R | 2
| 0x52A4 | 0x52A7 | 21156 | 21159 | Input Channel 1 Active Power Max value Timestamp | uint16_t | R | 4
| 0x52A8 | 0x52A9 | 21160 | 21161 | Input Channel 1 Reactive Power Max value | float | R | 2
| 0x52AA | 0x52AD | 21162 | 21165 | Input Channel 1 Reactive Power Max value Timestamp | uint16_t | R | 4
| 0x52AE | 0x52AF | 21166 | 21167 | Input Channel 1 Apparent Power Max value | float | R | 2
| 0x52B0 | 0x52B3 | 21168 | 21171 | Input Channel 1 Apparent Power Max value Timestamp | uint16_t | R | 4
| 0x52B4 | 0x52B5 | 21172 | 21173 | Input Channel 1 Power Factor Max value | float | R | 2
| 0x52B6 | 0x52B9 | 21174 | 21177 | Input Channel 1 Power Factor Max value Timestamp | uint16_t | R | 4
| 0x52BA | 0x52BB | 21178 | 21179 | Input Channel 1 Current THD Max value | float | R | 2
| 0x52BC | 0x52BF | 21180 | 21183 | Input Channel 1 Current THD Max value Timestamp | uint16_t | R | 4
| 0x52C0 | 0x55FB | 21184 | 22011 | Input channel 2-24 Max value |  | R | 828
| 0x55FC | 0x55FD | 22012 | 22013 | User Channel 1 Current Max value | float | R | 2
| 0x55FE | 0x5601 | 22014 | 22017 | User Channel 1 Current Max value Timestamp | uint16_t | R | 4
| 0x5602 | 0x5603 | 22018 | 22019 | User Channel 1 Active Power Max value | float | R | 2
| 0x5604 | 0x5607 | 22020 | 22023 | User Channel 1 Active Power Max value Timestamp | uint16_t | R | 4
| 0x5608 | 0x5609 | 22024 | 22025 | User Channel 1 Reactive Power Max value | float | R | 2
| 0x560A | 0x560D | 22026 | 22029 | User Channel 1 Reactive Power Max value Timestamp | uint16_t | R | 4
| 0x560E | 0x560F | 22030 | 22031 | User Channel 1 Apparent Power Max value | float | R | 2
| 0x5610 | 0x5613 | 22032 | 22035 | User Channel 1 Apparent Power Max value Timestamp | uint16_t | R | 4
| 0x5614 | 0x5615 | 22036 | 22037 | User Channel 1 Power Factor | float | R | 2
| 0x5616 | 0x5619 | 22038 | 22041 | User Channel 1 Power Factor Timestamp | uint16_t | R | 4
| 0x561A | 0x5763 | 22042 | 22371 | User channel 2-12 Max value |  | R | 330
1380
Min value record
| 0x5800 | 0x5801 | 22528 | 22529 | System Frequency Min value | float | R | 2
| 0x5802 | 0x5805 | 22530 | 22533 | System Frequency Min value Timestamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) | uint16_t | R | 4
| 0x5806 | 0x5807 | 22534 | 22535 | Phase A Line-to-Neutral Voltage Min value | float | R | 2
| 0x5808 | 0x580B | 22536 | 22539 | Phase A Line-to-Neutral Voltage Min value Timestamp | uint16_t | R | 4
| 0x580C | 0x580D | 22540 | 22541 | Phase B Line-to-Neutral Voltage Min value | float | R | 2
| 0x580E | 0x5811 | 22542 | 22545 | Phase B Line-to-Neutral Voltage Min value Timestamp | uint16_t | R | 4
| 0x5812 | 0x5813 | 22546 | 22547 | Phase C Line-to-Neutral Voltage Min value | float | R | 2
| 0x5814 | 0x5817 | 22548 | 22551 | Phase C Line-to-Neutral Voltage Min value Timestamp | uint16_t | R | 4
| 0x5818 | 0x5819 | 22552 | 22553 | Phase AB Line-to-Line Voltage Min value | float | R | 2
| 0x581A | 0x581D | 22554 | 22557 | Phase AB Line-to-Line Voltage Min value Timestamp | uint16_t | R | 4
| 0x581E | 0x581F | 22558 | 22559 | Phase BC Line-to-Line Voltage Min value | float | R | 2
| 0x5820 | 0x5823 | 22560 | 22563 | Phase BC Line-to-Line Voltage Min value Timestamp | uint16_t | R | 4
| 0x5824 | 0x5825 | 22564 | 22565 | Phase CA Line-to-Line Voltage Min value | float | R | 2
| 0x5826 | 0x5829 | 22566 | 22569 | Phase CA Line-to-Line Voltage Min value Timestamp | uint16_t | R | 4
| 0x582A | 0x582B | 22570 | 22571 | Phase A Current Min value | float | R | 2
| 0x582C | 0x582F | 22572 | 22575 | Phase A Current Min value Timestamp | uint16_t | R | 4
| 0x5830 | 0x5831 | 22576 | 22577 | Phase A Active Power Min value | float | R | 2
| 0x5832 | 0x5835 | 22578 | 22581 | Phase A Active Power Min value Timestamp | uint16_t | R | 4
| 0x5836 | 0x5837 | 22582 | 22583 | Phase A Reactive Power Min value | float | R | 2
| 0x5838 | 0x583B | 22584 | 22587 | Phase A Reactive Power Min value Timestamp | uint16_t | R | 4
| 0x583C | 0x583D | 22588 | 22589 | Phase A Apparent Power Min value | float | R | 2
| 0x583E | 0x5841 | 22590 | 22593 | Phase A Apparent Power Min value Timestamp | uint16_t | R | 4
| 0x5842 | 0x5843 | 22594 | 22595 | Phase A Power Factor Min value | float | R | 2
| 0x5844 | 0x5847 | 22596 | 22599 | Phase A Power Factor Min value Timestamp | uint16_t | R | 4
| 0x5848 | 0x5849 | 22600 | 22601 | Phase A Voltage THD Min value | float | R | 2
| 0x584A | 0x584D | 22602 | 22605 | Phase A Voltage THD Min value Timestamp | uint16_t | R | 4
| 0x584E | 0x584F | 22606 | 22607 | Phase B Current Min value | float | R | 2
| 0x5850 | 0x5853 | 22608 | 22611 | Phase B Current Min value Timestamp | uint16_t | R | 4
| 0x5854 | 0x5855 | 22612 | 22613 | Phase B Active Power Min value | float | R | 2
| 0x5856 | 0x5859 | 22614 | 22617 | Phase B Active Power Min value Timestamp | uint16_t | R | 4
| 0x585A | 0x585B | 22618 | 22619 | Phase B Reactive Power Min value | float | R | 2
| 0x585C | 0x585F | 22620 | 22623 | Phase B Reactive Power Min value Timestamp | uint16_t | R | 4
| 0x5860 | 0x5861 | 22624 | 22625 | Phase B Apparent Power Min value | float | R | 2
| 0x5862 | 0x5865 | 22626 | 22629 | Phase B Apparent Power Min value Timestamp | uint16_t | R | 4
| 0x5866 | 0x5867 | 22630 | 22631 | Phase B Power Factor Min value | float | R | 2
| 0x5868 | 0x586B | 22632 | 22635 | Phase B Power Factor Min value Timestamp | uint16_t | R | 4
| 0x586C | 0x586D | 22636 | 22637 | Phase B Voltage THD Min value | float | R | 2
| 0x586E | 0x5871 | 22638 | 22641 | Phase B Voltage THD Min value Timestamp | uint16_t | R | 4
| 0x5872 | 0x5873 | 22642 | 22643 | Phase C Current Min value | float | R | 2
| 0x5874 | 0x5877 | 22644 | 22647 | Phase C Current Min value Timestamp | uint16_t | R | 4
| 0x5878 | 0x5879 | 22648 | 22649 | Phase C Active Power Min value | float | R | 2
| 0x587A | 0x587D | 22650 | 22653 | Phase C Active Power Min value Timestamp | uint16_t | R | 4
| 0x587E | 0x587F | 22654 | 22655 | Phase C Reactive Power Min value | float | R | 2
| 0x5880 | 0x5883 | 22656 | 22659 | Phase C Reactive Power Min value Timestamp | uint16_t | R | 4
| 0x5884 | 0x5885 | 22660 | 22661 | Phase C Apparent Power Min value | float | R | 2
| 0x5886 | 0x5889 | 22662 | 22665 | Phase C Apparent Power Min value Timestamp | uint16_t | R | 4
| 0x588A | 0x588B | 22666 | 22667 | Phase C Power Factor Min value | float | R | 2
| 0x588C | 0x588F | 22668 | 22671 | Phase C Power Factor Min value Timestamp | uint16_t | R | 4
| 0x5890 | 0x5891 | 22672 | 22673 | Phase C Voltage THD Min value | float | R | 2
| 0x5892 | 0x5895 | 22674 | 22677 | Phase C Voltage THD Min value Timestamp | uint16_t | R | 4
| 0x5896 | 0x5897 | 22678 | 22679 | Voltage Unbalance Factor Magnitude Min value | float | R | 2
| 0x5898 | 0x589B | 22680 | 22683 | Voltage Unbalance Factor Magnitude Min value Timestamp | uint16_t | R | 4
| 0x589C | 0x589D | 22684 | 22685 | Input Channel 1 Current Min value | float | R | 2
| 0x589E | 0x58A1 | 22686 | 22689 | Input Channel 1 Current Min value Timestamp | uint16_t | R | 4
| 0x58A2 | 0x58A3 | 22690 | 22691 | Input Channel 1 Active Power Min value | float | R | 2
| 0x58A4 | 0x58A7 | 22692 | 22695 | Input Channel 1 Active Power Min value Timestamp | uint16_t | R | 4
| 0x58A8 | 0x58A9 | 22696 | 22697 | Input Channel 1 Reactive Power Min value | float | R | 2
| 0x58AA | 0x58AD | 22698 | 22701 | Input Channel 1 Reactive Power Min value Timestamp | uint16_t | R | 4
| 0x58AE | 0x58AF | 22702 | 22703 | Input Channel 1 Apparent Power Min value | float | R | 2
| 0x58B0 | 0x58B3 | 22704 | 22707 | Input Channel 1 Apparent Power Min value Timestamp | uint16_t | R | 4
| 0x58B4 | 0x58B5 | 22708 | 22709 | Input Channel 1 Power Factor Min value | float | R | 2
| 0x58B6 | 0x58B9 | 22710 | 22713 | Input Channel 1 Power Factor Min value Timestamp | uint16_t | R | 4
| 0x58BA | 0x58BB | 22714 | 22715 | Input Channel 1 Current THD Min value | float | R | 2
| 0x58BC | 0x58BF | 22716 | 22719 | Input Channel 1 Current THD Min value Timestamp | uint16_t | R | 4
| 0x58C0 | 0x5BFB | 22720 | 23547 | Input channel 2-24 Min value |  | R | 828
| 0x5BFC | 0x5BFD | 23548 | 23549 | User Channel 1 Current Min value | float | R | 2
| 0x5BFE | 0x5C01 | 23550 | 23553 | User Channel 1 Current Min value Timestamp | uint16_t | R | 4
| 0x5C02 | 0x5C03 | 23554 | 23555 | User Channel 1 Active Power Min value | float | R | 2
| 0x5C04 | 0x5C07 | 23556 | 23559 | User Channel 1 Active Power Min value Timestamp | uint16_t | R | 4
| 0x5C08 | 0x5C09 | 23560 | 23561 | User Channel 1 Reactive Power Min value | float | R | 2
| 0x5C0A | 0x5C0D | 23562 | 23565 | User Channel 1 Reactive Power Min value Timestamp | uint16_t | R | 4
| 0x5C0E | 0x5C0F | 23566 | 23567 | User Channel 1 Apparent Power Min value | float | R | 2
| 0x5C10 | 0x5C13 | 23568 | 23571 | User Channel 1 Apparent Power Min value Timestamp | uint16_t | R | 4
| 0x5C14 | 0x5C15 | 23572 | 23573 | User Channel 1 Power Factor | float | R | 2
| 0x5C16 | 0x5C19 | 23574 | 23577 | User Channel 1 Power Factor Timestamp | uint16_t | R | 4
| 0x5C1A | 0x5D63 | 23578 | 23907 | User channel 2-12 Min value |  |  | 330
1380

## Alarm Record ¦DI¦SOE
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Alarm settings code function : 03H Read, 10H Write
| 0x6000 | 0x6001 | 24576 | 24577 | Enable all alarm | uint32_t | R/W | 2 | Bit 0~19 for alarm channel 1~20 (0: disabled; 1：enabled | 0
| 0x6002 | 0x6002 | 24578 | 24578 | Alarm Channel 1 Logic | uint16_t | R/W | 1 | bit2-0= 000：parameter 1 is not involved in the alert logic calculation bit2-0= 001：parameter 1 is used as the "=" condition in the alert logic calculation bit2-0= 010：parameter 1 is used for the ">" condition in the alert logic calculation bit2-0= 011：parameter 1 is used for the "<" condition in the alert logic calculation bit 5-3 = 000：parameter 2 is not involved in the alert logic calculation bit5-3= 001： parameter 2 is used as the "=" condition in the alert logic calculation bit 5-3 = 010：parameter 2 is used for the ">" condition in the alert logic calculation bit 5-3 =0 11：parameter 2 is used for the "<" condition in the alert logic calculation bit7-6=01：Parameters 1 and 2 have an "&&" relationship in the alert logic calculation bit7-6=10：Parameters 1 and 2 have an "¦¦" relationship in the alert logic calculation | 0
| 0x6003 | 0x6003 | 24579 | 24579 | Alarm channel 1 RO selection | uint16_t | R/W | 1 | 0: no output 1-2: output relay ID | 0
| 0x6004 | 0x6004 | 24580 | 24580 | Alarm channel 1 DO selection | uint16_t | R/W | 1 | 0: no output 1-8: output DO ID | 0
| 0x6005 | 0x6005 | 24581 | 24581 | Alarm channel 1 parameter1 index | uint16_t | R/W | 1 | modbus addr (DI :1-4)、Basic Parameters 、Demand、Power Quality | 0
| 0x6006 | 0x6007 | 24582 | 24583 | Alarm channel 1 parameter1 Pickup Value | float32 | R/W | 2 |  | 0
| 0x6008 | 0x6008 | 24584 | 24584 | Alarm channel 1 parameter1 Pickup Delay | uint16_t | R/W | 1 | 1-65535 | 0
| 0x6009 | 0x600A | 24585 | 24586 | Alarm channel 1 parameter1 Dropout Value | float32 | R/W | 2 |  | 0
| 0x600B | 0x600B | 24587 | 24587 | Alarm channel 1 parameter1 Dropout Delay | uint16_t | R/W | 1 | 1-65535 | 0
| 0x600C | 0x600C | 24588 | 24588 | Alarm channel 1 parameter2 index | uint16_t | R/W | 1 | modbus addr (DI :1-4)、Basic Parameters 、Demand、Power Quality | 0
| 0x600D | 0x600E | 24589 | 24590 | Alarm channel 1 parameter2 Pickup Value | float32 | R/W | 2 |  | 0
| 0x600F | 0x600F | 24591 | 24591 | Alarm channel 1 parameter2 Pickup Delay | uint16_t | R/W | 1 |  | 0
| 0x6010 | 0x6011 | 24592 | 24593 | Alarm channel 1 parameter2 Dropout Value | float32 | R/W | 2 |  | 0
| 0x6012 | 0x6012 | 24594 | 24594 | Alarm channel 1 parameter2 Dropout Delay | uint16_t | R/W | 1 |  | 0
| 0x6013 | 0x6023 | 24595 | 24611 | Alarm channel 2 configuration |  | R/W | 17 |  | 0
| 0x6024 | 0x6034 | 24612 | 24628 | Alarm channel 3 configuration |  | R/W | 17 |  | 0
| 0x6035 | 0x6045 | 24629 | 24645 | Alarm channel 4 configuration |  | R/W | 17 |  | 0
| 0x6046 | 0x6056 | 24646 | 24662 | Alarm channel 5 configuration |  | R/W | 17 |  | 0
| 0x6057 | 0x6067 | 24663 | 24679 | Alarm channel 6 configuration |  | R/W | 17 |  | 0
| 0x6068 | 0x6078 | 24680 | 24696 | Alarm channel 7 configuration |  | R/W | 17 |  | 0
| 0x6079 | 0x6089 | 24697 | 24713 | Alarm channel 8 configuration |  | R/W | 17 |  | 0
| 0x608A | 0x609A | 24714 | 24730 | Alarm channel 9 configuration |  | R/W | 17 |  | 0
| 0x609B | 0x60AB | 24731 | 24747 | Alarm channel 10 configuration |  | R/W | 17 |  | 0
| 0x60AC | 0x60BC | 24748 | 24764 | Alarm channel 11 configuration |  | R/W | 17 |  | 0
| 0x60BD | 0x60CD | 24765 | 24781 | Alarm channel 12 configuration |  | R/W | 17 |  | 0
| 0x60CE | 0x60DE | 24782 | 24798 | Alarm channel 13 configuration |  | R/W | 17 |  | 0
| 0x60DF | 0x60EF | 24799 | 24815 | Alarm channel 14 configuration |  | R/W | 17 |  | 0
| 0x60F0 | 0x6100 | 24816 | 24832 | Alarm channel 15 configuration |  | R/W | 17 |  | 0
| 0x6101 | 0x6111 | 24833 | 24849 | Alarm channel 16 configuration |  | R/W | 17 |  | 0
| 0x6112 | 0x6122 | 24850 | 24866 | Alarm channel 17 configuration |  | R/W | 17 |  | 0
| 0x6123 | 0x6133 | 24867 | 24883 | Alarm channel 18 configuration |  | R/W | 17 |  | 0
| 0x6134 | 0x6144 | 24884 | 24900 | Alarm channel 19 configuration |  | R/W | 17 |  | 0
| 0x6145 | 0x6155 | 24901 | 24917 | Alarm channel 20 configuration |  | R/W | 17 |  | 0
342
Alarm Log Read Window
Data Format | 0x6200 | 0x6201 | 25088 | 25089 | The alarm status of each alarm channel | uint32_t | R | 2 | bit0-bit019：0->Alarm release 1:Alarm activation
| 0x6202 | 0x6202 | 25090 | 25090 | the index of the Alarm Log | uint16_t | R | 1 | 1-200
| 0x6203 | 0x6203 | 25091 | 25091 | Number of the Alarm Log | uint16_t | R | 1 | Alarm Log already occurred Count 0：Empty
| 0x6204 | 0x6204 | 25092 | 25092 | The first index of the alarm Log will be read | uint16_t | R/W | 1 | 1-200
| 0x6205 | 0x6205 | 25093 | 25093 | Read the number of the Alarm Log offset | uint16_t | R/W | 1 | 1--8
| 0x6206 | 0x6206 | 25094 | 25094 | Data state of Alarm Log Window | uint16_t | R | 1 | 0x00: window get data failed; 0x0B: window data effective; 0xFF: window data Busy;
| 0x6207 | 0x627E | 25095 | 25214 | Alarm Log Reading Window | uint16_t | R | 120 | Alarm Log Data
SOE Log Status | 0x6300 | 0x6300 | 25344 | 25344 | the index of the SOE Log | uint16_t | R | 1 | 1-200
| 0x6301 | 0x6301 | 25345 | 25345 | Number of the SOE Log | uint16_t | R | 1 | SOE Log already occurred Count 0：Empty
SOE Log Read Window | 0x6302 | 0x6302 | 25346 | 25346 | The first index of the SOE Log will be read | uint16_t | R/W | 1 | 1-200
| 0x6303 | 0x6303 | 25347 | 25347 | Read the number of the SOE Log offset | uint16_t | R/W | 1 | 1--20
| 0x6304 | 0x6304 | 25348 | 25348 | Data state of SOE Log Window | uint16_t | R | 1 | 0x00: window get data failed; 0x0B: window data effective; 0xFF: window data Busy;
| 0x6305 | 0x637C | 25349 | 25468 | SOE Log Reading Window |  | R | 120 | SOE Log Data
DI pulse Count
| 0x6400 | 0x6401 | 25600 | 25601 | DI1 pulse count | uint32_t | R/W | 2
| 0x6402 | 0x6403 | 25602 | 25603 | DI2 pulse count | uint32_t | R/W | 2
| 0x6404 | 0x6405 | 25604 | 25605 | DI3 pulse count | uint32_t | R/W | 2
| 0x6406 | 0x6407 | 25606 | 25607 | DI4 pulse count | uint32_t | R/W | 2
Alarm Log Record Data Format
[5 empty] | Alarm Log ID | uint16_t |  | 1
[5 empty] | Alarm Log Time Stamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) | uint16_t |  | 4
[5 empty] | Alarm Log Monitor ID | uint16_t |  | 1
[5 empty] | Alarm Status | uint16_t |  | 1 | 1:start 0:end 2：configuration change
[5 empty] | Alarm Log Extreme Value 1 | float |  | 2
[5 empty] | Alarm Log Extreme Value 2 | float |  | 2
[5 empty] | Alarm Log Duration | uint32_t |  | 2
Soe Log Record Data Format
[5 empty] | Soe Log ID | uint16_t |  | 1
[5 empty] | Time Stamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) | uint16_t |  | 4
[5 empty] | digtal Input Status | uint16_t |  | 1 | b3-b0->DI4-DI1 Status:1:High 0：Low

## Waveform¦PQ Event
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Power Quality Event setting
Rated Value | 0x6500 | 0x6500 | 25856 | 25856 | Norminal Current | uint16_t | R/W | 1 | 1-50000A | 1000
| 0x6501 | 0x6501 | 25857 | 25857 | Nominal Voltage Low Byte | uint16_t | R/W | 1 | 50-1000000V High Byte Reg:0x651A | 480
Voltage Sag | 0x6502 | 0x6502 | 25858 | 25858 | Voltage Sag Enable | uint16_t | R/W | 1 | 0：disable 1：enable | 0
| 0x6503 | 0x6503 | 25859 | 25859 | Voltage Sag Threshold | uint16_t | R/W | 1 | 10%-90% | 50
| 0x6504 | 0x6504 | 25860 | 25860 | Voltage Sag Jitter | uint16_t | R/W | 1 | 1-10% | 0
| 0x6505 | 0x6505 | 25861 | 25861 | Voltage Sag Triggers Waveform Recording | uint16_t | R/W | 1 | 0:disable 1:enable | 0
| 0x6506 | 0x6506 | 25862 | 25862 | Voltage Sag - switch to output DO | uint16_t | R/W | 1 | 0-8 0:No Digital Output;1-8:DO1-DO8 | 0
| 0x6507 | 0x6507 | 25863 | 25863 | Voltage Sag - switch to output RO | uint16_t | R/W | 1 | 0-2 0:No Relay Ouput;1-2:RO1-RO2 | 0
Voltage Swell | 0x6508 | 0x6508 | 25864 | 25864 | Voltage Swell Enable | uint16_t | R/W | 1 | 0：disable 1：enable | 0
| 0x6509 | 0x6509 | 25865 | 25865 | Voltage Swell Threshold | uint16_t | R/W | 1 | 110%-150% | 150
| 0x650A | 0x650A | 25866 | 25866 | Voltage Swell Jitter | uint16_t | R/W | 1 | 1-10% | 5
| 0x650B | 0x650B | 25867 | 25867 | Voltage Swell Triggers Waveform Recording | uint16_t | R/W | 1 | 0:disable 1:enable | 0
| 0x650C | 0x650C | 25868 | 25868 | Voltage Swell - switch to output DO | uint16_t | R/W | 1 | 0-8 0:No Digital Output;1-8:DO1-DO8 | 0
| 0x650D | 0x650D | 25869 | 25869 | Voltage Swell - switch to output RO | uint16_t | R/W | 1 | 0-2 0:No Relay Ouput;1-2:RO1-RO2 | 0
Voltage Interruption | 0x650E | 0x650E | 25870 | 25870 | Voltage Interruption Enable | uint16_t | R/W | 1 | 0:disable 1:enable | 0
| 0x650F | 0x650F | 25871 | 25871 | Voltage Interruption Threshold | uint16_t | R/W | 1 | 5%-20% | 10
| 0x6510 | 0x6510 | 25872 | 25872 | Voltage Interruption Jitter | uint16_t | R/W | 1 | 1-10% | 1
| 0x6511 | 0x6511 | 25873 | 25873 | Voltage Interruption Triggers Waveform Recording | uint16_t | R/W | 1 | 0:disable 1:enable | 0
| 0x6512 | 0x6512 | 25874 | 25874 | Voltage Interruption - switch to output DO | uint16_t | R/W | 1 | 0-8 0:No Digital Output;1-8:DO1-DO8 | 0
| 0x6513 | 0x6513 | 25875 | 25875 | Voltage Interruption - switch to output RO | uint16_t | R/W | 1 | 0-2 0:No Relay Ouput;1-2:RO1-RO2 | 0
Current Swell | 0x6514 | 0x6514 | 25876 | 25876 | Current Swell Enable | uint16_t | R/W | 1 | 0：disable 1：enable | 0
| 0x6515 | 0x6515 | 25877 | 25877 | Current Swell Threshold | uint16_t | R/W | 1 | 110%-150% | 150
| 0x6516 | 0x6516 | 25878 | 25878 | Current Swell Jitter | uint16_t | R/W | 1 | 1-10% | 5
| 0x6517 | 0x6517 | 25879 | 25879 | Current Triggers Waveform Recording | uint16_t | R/W | 1 | 0:disable 1:enable | 0
| 0x6518 | 0x6518 | 25880 | 25880 | Current Swell - switch to output DO | uint16_t | R/W | 1 | 0-8 0:No Digital Output;1-8:DO1-DO8 | 0
| 0x6519 | 0x6519 | 25881 | 25881 | Current Swell - switch to output RO | uint16_t | R/W | 1 | 0-2 0:No Relay Ouput;1-2:RO1-RO2 | 0
| 0x651A | 0x651A | 25882 | 25882 | Nominal Voltage Hing Byte | uint16_t | R/W | 1
Waveform record parameter setting | 0x6570 | 0x6570 | 25968 | 25968 | sampling rate | uint16_t | R/W | 1 | 0:16 points 1:32 points 2:64 points 3:128 points | 2
| 0x6571 | 0x6571 | 25969 | 25969 | Number of cycles before the event occurred | uint16_t | R/W | 1 | 1-159, Total numbers of recorded waves is 2560 float data points, If sampling rate is 16 points, the max recorded waves is 160, Number of recorded waves before the event occurred shoud be setted to 1-159. | 10
| 0x6572 | 0x6572 | 25970 | 25970 | Number of cycles after the event occurred | uint16_t | R/W | 1 | 1-159, The max recorded waves is (160 - Number of recorded waves before the event occurred) | 10
| 0x6573 | 0x6573 | 25971 | 25971 | DI1 Trigger | uint16_t | R/W | 1 | 0:disable, 1-24：user 1-12，input channel 1-24, 0xFF:only record voltage | 0
| 0x6574 | 0x6574 | 25972 | 25972 | DI2 Trigger | uint16_t | R/W | 1 | 0:disable, 1-24：user1-12，input channel 1-24, 0xFF:only record voltage | 0
| 0x6575 | 0x6575 | 25973 | 25973 | DI3 Trigger | uint16_t | R/W | 1 | 0:disable, 1-24：user1-12，input channel 1-24, 0xFF:only record voltage | 0
| 0x6576 | 0x6576 | 25974 | 25974 | DI4 Trigger | uint16_t | R/W | 1 | 0:disable, 1-24：user1-12，input channel 1-24, 0xFF:only record voltage | 0
| 0x6577 | 0x6577 | 25975 | 25975 | Manually Trigger | uint16_t | R/W | 1 | 0:disable, 1-24：user1-12，input channel 1-24, 0xFF:only record voltage | 0
Waveform Reading Window | [7 empty] | 8
Data Format
| 0x6600 | 0x6600 | 26112 | 26112 | Group ID of reading waveform | uint16_t | R/W | 1 | 1 - 200 | 0x6601:0 0x6602:0 read waveform information(ID,Mode,Timestamp)
| 0x6601 | 0x6601 | 26113 | 26113 | The nth waveform cycle | uint16_t | R/W | 1 | 0:read waveform information(ID,Mode,Timestamp), 1-160
| 0x6602 | 0x6602 | 26114 | 26114 | The nth register packet of one waveform cycle | uint16_t | R/W | 1 | 0:read waveform information(ID,Mode,Timestamp), 1-39(max), 39=((128*4*6)/240), Maximum data capacity of one cycle/240
| 0x6603 | 0x6603 | 26115 | 26115 | Total groups already recorded | uint16_t | R | 1 | 0 - 200
| 0x6604 | 0x6604 | 26116 | 26116 | Data state of waveform record window | uint16_t | R | 1 | 0x00: window get data failed; 0x0B: window data effective; 0xFF: window data Busy;
| 0x6605 | 0x6605 | 26117 | 26117 | Latest waveform record groupe ID | uint16_t | R | 1 | 1 - 200;0: no waveform record data。
| 0x6606 | 0x667D | 26118 | 26237 | Waveform record data reading window |  | R | 120
| In the case of 16-point recording: 0:waveform ID(uint32_t),4bytes; Frequency,4bytes(float),Read-only; waveform record reason mode(uint32_t),4bytes;Time of waveform recording,8bytes( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) The following data frame defines waveform data, which is read in the sequence of Ua, Ub, Uc, USER_CH1, USER_CH2, and USER_CH3. 1: The first 120 registers, one group is divided into multiple packets, each occupying 120 registers in size; 2: The second 120 registers; 3: The third 120 registers; . . . . . . n: The nth 120 registers; The host needs to calculate how many packets the waveform will be divided into, and send commands in sequence to read the data packets.When reading waveform data for a channel, the resulting data frame may contain fewer than 120 registers, The empty registers will not be filled with data from other channels. The waveform data for the next channel will be stored starting from the beginning of the next data frame. when record reason mode is 0b00001000 or 0b00010000 or 0b01000000,The host can only get Ua Ub and Uc records; when record reason mode is 0b10010000, The host can get Ua/Ub/Uc and user USER_CH1/CH2/CH3 records. |  |  |  | In the case of 32-point recording and broadcasting, 0: waveform ID,4bytes;Frequency,4bytes(float),Read-only;Read-only; waveform record reason mode，4bytes;Time of waveform recording,8bytes; 1: The first 120 registers, one group is divided into multiple packets, each occupying 120 registers in size; 2: The second 120 registers; 3: The third 120 registers; . . . . . . n: The nth 120 registers; The lower 8 bits： 0b00000001:DI1 trigger(voltage); 0b00000010:DI2 trigger(voltage); 0b00000011:DI3 trigger(voltage); 0b00000100:DI4 trigger(voltage); 0b00000101:DI1 trigger(voltage&current); 0b00000110:DI2 trigger(voltage&current); 0b00000111:DI3 trigger(voltage&current); 0b00001001:DI4 trigger(voltage&current); 0b00001010:manual trigger(voltage); 0b00001011:manual trigger(voltage&current); 0b00001000:voltage sag; 0b00010000:voltage swell; 0b01000000:voltage interrupt; 0b10010000:current swell ¦-----------------------------------------32bytes--------------------------------------¦ higher lower 4bites 5bites 5bites 5bites 5bites 8bites reserved Ic inputCh Ib inputCh Ia inputCh userCh reasonMode Ia inputCh:0-24,0:no current recorded Ib inputCh:0-24,0:no current recorded Ic inputCh:0-24,0:no current recorded userCh:1-24,0 or 0xFF:only record voltage |  |  |  | In the case of 64-point recording: 0::waveform ID,4bytes;Frequency,4bytes(float),Read-only;Read-only waveform record reason mode，4bytes;Time of waveform recording,8bytes; 1: The first 120 registers, one group is divided into multiple packets, each occupying 120 registers in size; 2: The second 120 registers; 3: The third 120 registers; . . . . . . n: The nth 120 registers; |  | In the case of 128-point recording and broadcasting, 0: :waveform ID,4bytes;Read-only waveform record reason mode，4bytes;Time of waveform recording,8bytes; 1: The first 120 registers, one group is divided into multiple packets, each occupying 120 registers in size; 2: The second 120 registers; 3: The third 120 registers; . . . . . . n: The nth 120 registers;
PQ Event Record Reading Window
Data Format | 0x6700 | 0x6700 | 26368 | 26368 | the Status of the PQEvent | uint16_t | R | 1 | bit0:0->Volt Sag Event Out ,1->Volt Sag Event In ; bit1:0->Volt Swell Event Out ,1->Volt Swell Event In ; bit2:0->Volt Interruption Event Out ,1->Volt Interruption Event In ; bit3:0->current swell Event Out ,1->current swell Event In ;
| 0x6701 | 0x6701 | 26369 | 26369 | the index of the PQEvent Log | uint16_t | R | 1 | 1-200
| 0x6702 | 0x6702 | 26370 | 26370 | Number of the PQEvent Log | uint16_t | R | 1 | PQEvent Logal already occurred Count 0：Empty
| 0x6703 | 0x6703 | 26371 | 26371 | The first index of the PQEvent Log will be read | uint16_t | R/W | 1 | 1-200
| 0x6704 | 0x6704 | 26372 | 26372 | Read the number of the PQEvent Log offset | uint16_t | R/W | 1 | 1--5
| 0x6705 | 0x6705 | 26373 | 26373 | Data state of PQEvent Log window | uint16_t | R | 1 | 0x00: window get data failed; 0x0B: window data effective; 0xFF: window data Busy;
| 0x6706 | 0x677D | 26374 | 26493 | PQEvent Log Reading window |  | R | 120 | PQ Event Log Data
PQ Event Log Record Data Format
[5 empty] | PQ Event Log ID | uint16_t |  | 1
[5 empty] | Time Stamp ( year： uint8_t month： uint8_t day： uint8_t hour： uint8_t min： uint8_t sec： uint8_t millisec：uint16_t) | uint16_t |  | 4
[5 empty] | Event Type | uint16_t |  | 1 | 0b00001000:voltage sag; 0b00010000:voltage swell; 0b01000000:voltage interrupt; 0b10010000:current swell；
[5 empty] | Event Status | uint16_t |  | 1 | 0:in 1:out
[5 empty] | User channel for power quality events that occur | uint16_t |  | 1
[5 empty] | Associate with waveform ID | uint32_t |  | 2 | 0:No Waveform Trigger
[5 empty] | Duration of power quality events | uint32_t |  | 2
[5 empty] | Max Value of Parameter #1 | float |  | 2
[5 empty] | Max Value of Parameter #2 | float |  | 2
[5 empty] | Max Value of Parameter #3 | float |  | 2
[5 empty] | Min Value of Parameter #1 | float |  | 2
[5 empty] | Min Value of Parameter #2 | float |  | 2
[5 empty] | Min Value of Parameter #3 | float |  | 2

## Data log And Trend log
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Data log Setting
| 0x6800 | 0x6800 | 26624 | 26624 | Data Log1 number of registers | uint16_t | R/W | 1 | 0-300 | 0
| 0x6801 | 0x6801 | 26625 | 26625 | Data Log1 number of blocks | uint16_t | R/W | 1 | 0-1377 Datalog1, Datalog2, and Datalog3 share 1377 blocks. Trendlog uses 459 blocks exclusively | 0
| 0x6802 | 0x6802 | 26626 | 26626 | Data Log1 Interval | uint16_t | R/W | 1 | 1 - 1440 | 1
| 0x6803 | 0x692E | 26627 | 26926 | Data Log1 parameter selections(up to 300 parameters) | uint16_t | R/W | 300 | (Modbus parameter statr address) | 0
| 0x692F | 0x692F | 26927 | 26927 | Data Log1 mode selection | uint16_t | R/W | 1 | 0 - 2 | 0
| 0x6930 | 0x6930 | 26928 | 26928 | Data Log1 Mode2 Start month, year | uint8_t | R/W | 1 | Low byte: month,high byte: year（keep consistence with Data Log123） | 0
| 0x6931 | 0x6931 | 26929 | 26929 | Data Log1 Mode2 Start day, hour | uint8_t | R/W | 1 | Low byte: hour,high byte: day | month: 1 year: 0
| 0x6932 | 0x6932 | 26930 | 26930 | Data Log1 Mode2 Start minute, second | uint8_t | R/W | 1 | Low byte: second,high byte: minute | day: 1 hour: 0
| 0x6933 | 0x6933 | 26931 | 26931 | Data Log1 Mode2 End month, year | uint8_t | R/W | 1 | Low byte: month,high byte: year | month: 1 year: 0
| 0x6934 | 0x6934 | 26932 | 26932 | Data Log1 Mode2 End day, hour | uint8_t | R/W | 1 | Low byte: hour,high byte: day | day: 1 hour: 0
| 0x6935 | 0x6935 | 26933 | 26933 | Data Log1 Mode2 End minute, second | uint8_t | R/W | 1 | Low byte: second,high byte: minute | 0
| 0x6936 | 0x6936 | 26934 | 26934 | Data Log1 Mode3 Start Hour and Min | uint16_t | R/W | 1 | Low byte: min,high byte: hour | 0
| 0x6937 | 0x6A6D | 26935 | 27245 | Log2 setting |  | R/W | 311
| 0x6A6E | 0x6BA4 | 27246 | 27556 | Log3 setting |  | R/W | 311
| 0x6BA5 | 0x6CDB | 27557 | 27867 | Trend Log setting |  | R/W | 311
1244
Data log Reading Window
| 0x6E00 | 0x6E00 | 28160 | 28160 | Data logger ID | uint16_t | R/W | 1 | 0 - 3
| 0x6E01 | 0x6E02 | 28161 | 28162 | Readr record offset | uint32_t | R/W | 2
| 0x6E03 | 0x6E03 | 28163 | 28163 | Read record number | uint16_t | R/W | 1
| 0x6E04 | 0x6E04 | 28164 | 28164 | Read record package offset | uint16_t | R/W | 1
| 0x6E05 | 0x6E05 | 28165 | 28165 | Read record package number | uint16_t | R/W | 1
| 0x6E06 | 0x6E06 | 28166 | 28166 | window state | uint16_t | R | 1 | window state（0x0B: data effective,0xFF: data not effective,0xAA: Data Log on clearing,0xBB: Data Log clearing end）
| 0x6E07 | 0x6E7E | 28167 | 28286 | record data reading Window | uint16_t | R | 120 | Data Log format: record number（4bytes ）+ time stamps（6bytes） + [data1~dataN]（12Nbytes） + CRC( 2bytes). Data format: parameter1 average value, parameter2 average value...parameter1 max value, parameter2 max value, parameter1 min value, parameter2 min value...
Data log Status Reading
| 0x6F00 | 0x6F01 | 28416 | 28417 | Data Log1 Max Records | uint32_t | R | 2
| 0x6F02 | 0x6F03 | 28418 | 28419 | Data Log1 Used Records | uint32_t | R | 2
| 0x6F04 | 0x6F04 | 28420 | 28420 | Data Log1 Record size | uint16_t | R | 1
| 0x6F05 | 0x6F06 | 28421 | 28422 | Data Log1 current record index | uint32_t | R | 2
| 0x6F07 | 0x6F07 | 28423 | 28423 | Data Log1 Log Availability（reserve） | uint16_t | R | 1
| 0x6F08 | 0x6F0A | 28424 | 28426 | Data Log1 First Record Time stamp | uint16_t | R | 3
| 0x6F0B | 0x6F0D | 28427 | 28429 | Data Log1 Last Record Time stamp | uint16_t | R | 3
| 0x6F0E | 0x6F0E | 28430 | 28430 | Data Log1 Record package counter | uint16_t | R | 1
| 0x6F0F | 0x6F0F | 28431 | 28431 | Data Log1 Record first package size | uint16_t | R | 1
| 0x6F10 | 0x6F10 | 28432 | 28432 | Data Log1 Record last package size | uint16_t | R | 1
| 0x6F11 | 0x6F21 | 28433 | 28449 | Data log 2 Status Reading | uint16_t | R | 17
| 0x6F22 | 0x6F32 | 28450 | 28466 | Data log 3 Status Reading | uint16_t | R | 17
| 0x6F33 | 0x6F43 | 28467 | 28483 | Trend log Status Reading | uint16_t | R | 17
DataLog Sector
Datalog 1 Sector | 0x6F4A | 0x6F4A | 28490 | 28490 | first block | uint16_t | R | 1
| 0x6F4B | 0x6F4B | 28491 | 28491 | current block | uint16_t | R | 1
| 0x6F4C | 0x6F4D | 28492 | 28493 | current address | uint32_t | R | 2
| 0x6F4E | 0x6F4E | 28494 | 28494 | full (low byte) | uint16_t | R | 1 | 0: not full 1: sector is full
5
Datalog 2 Sector | 0x6F4F | 0x6F4F | 28495 | 28495 | first block | uint16_t | R | 1
| 0x6F50 | 0x6F50 | 28496 | 28496 | current block | uint16_t | R | 1
| 0x6F51 | 0x6F52 | 28497 | 28498 | current address | uint32_t | R | 2
| 0x6F53 | 0x6F53 | 28499 | 28499 | full (low byte) | uint16_t | R | 1 | 0: not full 1: sector is full
5
Datalog 3 Sector | 0x6F54 | 0x6F54 | 28500 | 28500 | first block | uint16_t | R | 1
| 0x6F55 | 0x6F55 | 28501 | 28501 | current block | uint16_t | R | 1
| 0x6F56 | 0x6F57 | 28502 | 28503 | current address | uint32_t | R | 2
| 0x6F58 | 0x6F58 | 28504 | 28504 | full (low byte) | uint16_t | R | 1 | 0: not full 1: sector is full
5
Datalog 4 Sector | 0x6F59 | 0x6F59 | 28505 | 28505 | first block | uint16_t | R | 1
| 0x6F5A | 0x6F5A | 28506 | 28506 | current block | uint16_t | R | 1
| 0x6F5B | 0x6F5C | 28507 | 28508 | current address | uint32_t | R | 2
| 0x6F5D | 0x6F5D | 28509 | 28509 | full (low byte) | uint16_t | R | 1 | 0: not full 1: sector is full
5
DataLog Current Window Status
| 0x6F72 | 0x6F72 | 28530 | 28530 | DataLog 1 Current Window Status | uint16_t | R | 1 | 0x00FF: Invalid, 0x00AA: Erasing, 0x000B: Valid, 0x0000: Inactive
| 0x6F73 | 0x6F73 | 28531 | 28531 | DataLog 2 Current Window Status | uint16_t | R | 1 | 0x00FF: Invalid, 0x00AA: Erasing, 0x000B: Valid, 0x0000: Inactive
| 0x6F74 | 0x6F74 | 28532 | 28532 | DataLog 3 Current Window Status | uint16_t | R | 1 | 0x00FF: Invalid, 0x00AA: Erasing, 0x000B: Valid, 0x0000: Inactive
| 0x6F75 | 0x6F75 | 28533 | 28533 | TrendLog Current Window Status | uint16_t | R | 1 | 0x00FF: Invalid, 0x00AA: Erasing, 0x000B: Valid, 0x0000: Inactive

## Information
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Fireware & Product information:03H Read
Firmware Version Info
| 0xF000 | 0xF001 | 61440 | 61441 | Firmware version | uint8_t | R | 2 | In the format like x.yz (e.g., 1.01) | determined by firmware
| 0xF002 | 0xF004 | 61442 | 61444 | Firmware release date | uint8_t | R | 3 | In the format like YYMMDD (221228) | determined by firmware
| 0xF005 | 0xF005 | 61445 | 61445 | Firmware patch number | uint8_t | R | 1 | In the format like xy (01) | determined by firmware
Update (0x6A to write) | 0xF000 | 0xF001 | 61440 | 61441 | Device entry update | uint8_t | W | 2 | 0xA1,0x58,0x58,0xA1 | 0
Bootloader Info
| 0xF010 | 0xF011 | 61456 | 61457 | bootloader product string | uint8_t | R | 2 | MAA1 | determined by boot
| 0xF012 | 0xF013 | 61458 | 61459 | bootloader version | uint8_t | R | 2 | In the format like x.yz (e.g., 1.01) | determined by boot
| 0xF014 | 0xF016 | 61460 | 61462 | bootloader release date | uint8_t | R | 3 | ASCII, in format of YYMMDD (e.g. 241108) | determined by boot
| 0xF017 | 0xF017 | 61463 | 61463 | bootloader patch number | uint8_t | R | 1 | In the format like xy (01) | determined by boot
Product Info (0x6A to write in factory)
| 0xF040 | 0xF04F | 61504 | 61519 | Serial Number | uint8_t | R/W | 16 | In the format like MAAYYMMabcde(e.g., MAA250400001) AcuRev-4100 and Eaton use the same SN format.
| 0xF050 | 0xF051 | 61520 | 61521 | Hardware version | uint8_t | R/W | 2 | In the format like x.yz (e.g., 1.01) The main version and sub-version are released to the factory by the hardware engineers from the R&D department.
| 0xF052 | 0xF052 | 61522 | 61522 | Function Model Type | uint16_t | R/W | 1 | 0: default value 1: 4110
| 0xF053 | 0xF053 | 61523 | 61523 | Reserved | uint8_t | R/W | 1 | Default:0
| 0xF054 | 0xF054 | 61524 | 61524 | Current Input Type | uint16_t | R/W | 1 | 0 for mA 1 for mV
| 0xF055 | 0xF055 | 61525 | 61525 | Power Supply Type | uint16_t | R/W | 1 | Fixed as 0 for P1,Default:0
| 0xF056 | 0xF065 | 61526 | 61541 | MAC address(port3) | uint8_t | R/W | 16 | Configure according to the assigned MAC address，Note that port1, port2, and port3 must be configured with different MAC addresses.
| 0xF066 | 0xF066 | 61542 | 61542 | Certification Type | uint16_t | R/W | 1 | 0: None; 1: MC; Default:0 | 0
| 0xF067 | 0xF06F | 61543 | 61551 | Reserved | uint8_t | R/W | 9 | Set the register to 0
| 0xF070 | 0xF070 | 61552 | 61552 | Hardware Patch Number | uint8_t | R/W | 1 | In the format like xy (01) The hardware patch version. The content of this register is controlled and configured by the factory.
| 0xF071 | 0xF080 | 61553 | 61568 | MAC address(port1) | uint8_t | R/W | 16 | Configure according to the assigned MAC address，Note that port1, port2, and port3 must be configured with different MAC addresses.
| 0xF081 | 0xF090 | 61569 | 61584 | MAC address(port2) | uint8_t | R/W | 16 | Configure according to the assigned MAC address，Note that port1, port2, and port3 must be configured with different MAC addresses.

## Calibration
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Calibration Commands | 0xF204 | 0xF204 | 61956 | 61956 | calibration stage | uint16_t | R/W | 1 | 0:normal 1:offset reset 2:start offset 3:gain reset 4:start gain 1st 5:start gain 2nd 6:phase reset 7:start phase 8:offset write 9:gain write 10:phase write 11：factory mode offset 12: factory mode gain and pahse 13:exit 0xAA:power on ok
| 0xF205 | 0xF205 | 61957 | 61957 | H:calibStartChannelID | uint16_t | R/W | 1 | calibStartChannelID：0-26 caliboffsetID：1-27
L:caliboffsetID
| 0xF206 | 0xF23B | 61958 | 62011 | calibRmsValue[27] | uint32_t | R | 54
| 0xF23C | 0xF23D | 62012 | 62013 | factory offset calibration result | uint32_t | R | 2 | bit0：Ua，bit1:Ub,bit2:Uc,bit3:current1,....bit26:current24. 0 is fail,1 is success
| 0xF23E | 0xF23F | 62014 | 62015 | factory gain calibration result | uint32_t | R | 2
| 0xF240 | 0xF241 | 62016 | 62017 | factory phase calibration result | uint32_t | R | 2
Calibration OffSet Coef
| 0xF250 | 0xF251 | 62032 | 62033 | V1offSetCoef | int32_t | R/W | 2
| 0xF252 | 0xF253 | 62034 | 62035 | V2offSetCoef | int32_t | R/W | 2
| 0xF254 | 0xF255 | 62036 | 62037 | V3offSetCoef | int32_t | R/W | 2
| 0xF256 | 0xF257 | 62038 | 62039 | I1offSetCoef | int32_t | R/W | 2
| 0xF258 | 0xF259 | 62040 | 62041 | I2offSetCoef | int32_t | R/W | 2
| 0xF25A | 0xF25B | 62042 | 62043 | I3offSetCoef | int32_t | R/W | 2
| 0xF25C | 0xF25D | 62044 | 62045 | I4offSetCoef | int32_t | R/W | 2
| 0xF25E | 0xF25F | 62046 | 62047 | I5offSetCoef | int32_t | R/W | 2
| 0xF260 | 0xF261 | 62048 | 62049 | I6offSetCoef | int32_t | R/W | 2
| 0xF262 | 0xF263 | 62050 | 62051 | I7offSetCoef | int32_t | R/W | 2
| 0xF264 | 0xF265 | 62052 | 62053 | I8offSetCoef | int32_t | R/W | 2
| 0xF266 | 0xF267 | 62054 | 62055 | I9offSetCoef | int32_t | R/W | 2
| 0xF268 | 0xF269 | 62056 | 62057 | I10offSetCoef | int32_t | R/W | 2
| 0xF26A | 0xF26B | 62058 | 62059 | I11offSetCoef | int32_t | R/W | 2
| 0xF26C | 0xF26D | 62060 | 62061 | I12offSetCoef | int32_t | R/W | 2
| 0xF26E | 0xF26F | 62062 | 62063 | I13offSetCoef | int32_t | R/W | 2
| 0xF270 | 0xF271 | 62064 | 62065 | I14offSetCoef | int32_t | R/W | 2
| 0xF272 | 0xF273 | 62066 | 62067 | I15offSetCoef | int32_t | R/W | 2
| 0xF274 | 0xF275 | 62068 | 62069 | I16offSetCoef | int32_t | R/W | 2
| 0xF276 | 0xF277 | 62070 | 62071 | I17offSetCoef | int32_t | R/W | 2
| 0xF278 | 0xF279 | 62072 | 62073 | I18offSetCoef | int32_t | R/W | 2
| 0xF27A | 0xF27B | 62074 | 62075 | I19offSetCoef | int32_t | R/W | 2
| 0xF27C | 0xF27D | 62076 | 62077 | I20offSetCoef | int32_t | R/W | 2
| 0xF27E | 0xF27F | 62078 | 62079 | I21offSetCoef | int32_t | R/W | 2
| 0xF280 | 0xF281 | 62080 | 62081 | I22offSetCoef | int32_t | R/W | 2
| 0xF282 | 0xF283 | 62082 | 62083 | I23offSetCoef | int32_t | R/W | 2
| 0xF284 | 0xF285 | 62084 | 62085 | I24offSetCoef | int32_t | R/W | 2
GainCoef(V A/B/C)
| 0xF286 | 0xF287 | 62086 | 62087 | V1gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF288 | 0xF289 | 62088 | 62089 | V2gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF28A | 0xF28B | 62090 | 62091 | V3gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
GainCoef(mA、 mV CT、RCT)
| 0xF28C | 0xF28D | 62092 | 62093 | I1gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF28E | 0xF28F | 62094 | 62095 | I2gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF290 | 0xF291 | 62096 | 62097 | I3gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF292 | 0xF293 | 62098 | 62099 | I4gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF294 | 0xF295 | 62100 | 62101 | I5gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF296 | 0xF297 | 62102 | 62103 | I6gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF298 | 0xF299 | 62104 | 62105 | I7gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF29A | 0xF29B | 62106 | 62107 | I8gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF29C | 0xF29D | 62108 | 62109 | I9gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF29E | 0xF29F | 62110 | 62111 | I10gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2A0 | 0xF2A1 | 62112 | 62113 | I11gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2A2 | 0xF2A3 | 62114 | 62115 | I12gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2A4 | 0xF2A5 | 62116 | 62117 | I13gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2A6 | 0xF2A7 | 62118 | 62119 | I14gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2A8 | 0xF2A9 | 62120 | 62121 | I15gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2AA | 0xF2AB | 62122 | 62123 | I16gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2AC | 0xF2AD | 62124 | 62125 | I17gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2AE | 0xF2AF | 62126 | 62127 | I18gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2B0 | 0xF2B1 | 62128 | 62129 | I19gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2B2 | 0xF2B3 | 62130 | 62131 | I20gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2B4 | 0xF2B5 | 62132 | 62133 | I21gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2B6 | 0xF2B7 | 62134 | 62135 | I22gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2B8 | 0xF2B9 | 62136 | 62137 | I23gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
| 0xF2BA | 0xF2BB | 62138 | 62139 | I24gainCoef | uint32_t | R/W | 2 | 8,385,608-8,391,608
PhaseCoef(50Hz、60Hz)
| 0xF2BC | 0xF2BC | 62140 | 62140 | V1phaseCoef | int16_t | R/W | 1
| 0xF2BD | 0xF2BD | 62141 | 62141 | V2phaseCoef | int16_t | R/W | 1
| 0xF2BE | 0xF2BE | 62142 | 62142 | V3phaseCoef | int16_t | R/W | 1
| 0xF2BF | 0xF2BF | 62143 | 62143 | I1phaseCoef | int16_t | R/W | 1
| 0xF2C0 | 0xF2C0 | 62144 | 62144 | I2phaseCoef | int16_t | R/W | 1
| 0xF2C1 | 0xF2C1 | 62145 | 62145 | I3phaseCoef | int16_t | R/W | 1
| 0xF2C2 | 0xF2C2 | 62146 | 62146 | I4phaseCoef | int16_t | R/W | 1
| 0xF2C3 | 0xF2C3 | 62147 | 62147 | I5phaseCoef | int16_t | R/W | 1
| 0xF2C4 | 0xF2C4 | 62148 | 62148 | I6phaseCoef | int16_t | R/W | 1
| 0xF2C5 | 0xF2C5 | 62149 | 62149 | I7phaseCoef | int16_t | R/W | 1
| 0xF2C6 | 0xF2C6 | 62150 | 62150 | I8phaseCoef | int16_t | R/W | 1
| 0xF2C7 | 0xF2C7 | 62151 | 62151 | I9phaseCoef | int16_t | R/W | 1
| 0xF2C8 | 0xF2C8 | 62152 | 62152 | I10phaseCoef | int16_t | R/W | 1
| 0xF2C9 | 0xF2C9 | 62153 | 62153 | I11phaseCoef | int16_t | R/W | 1
| 0xF2CA | 0xF2CA | 62154 | 62154 | I12phaseCoef | int16_t | R/W | 1
| 0xF2CB | 0xF2CB | 62155 | 62155 | I13phaseCoef | int16_t | R/W | 1
| 0xF2CC | 0xF2CC | 62156 | 62156 | I14phaseCoef | int16_t | R/W | 1
| 0xF2CD | 0xF2CD | 62157 | 62157 | I15phaseCoef | int16_t | R/W | 1
| 0xF2CE | 0xF2CE | 62158 | 62158 | I16phaseCoef | int16_t | R/W | 1
| 0xF2CF | 0xF2CF | 62159 | 62159 | I17phaseCoef | int16_t | R/W | 1
| 0xF2D0 | 0xF2D0 | 62160 | 62160 | I18phaseCoef | int16_t | R/W | 1
| 0xF2D1 | 0xF2D1 | 62161 | 62161 | I19phaseCoef | int16_t | R/W | 1
| 0xF2D2 | 0xF2D2 | 62162 | 62162 | I20phaseCoef | int16_t | R/W | 1
| 0xF2D3 | 0xF2D3 | 62163 | 62163 | I21phaseCoef | int16_t | R/W | 1
| 0xF2D4 | 0xF2D4 | 62164 | 62164 | I22phaseCoef | int16_t | R/W | 1
| 0xF2D5 | 0xF2D5 | 62165 | 62165 | I23phaseCoef | int16_t | R/W | 1
| 0xF2D6 | 0xF2D6 | 62166 | 62166 | I24phaseCoef | int16_t | R/W | 1
| 0xF2D7 | 0xF2D7 | 62167 | 62167 | dspV1phaseCoef | int16_t | R/W | 1
| 0xF2D8 | 0xF2D8 | 62168 | 62168 | dspV2phaseCoef | int16_t | R/W | 1
| 0xF2D9 | 0xF2D9 | 62169 | 62169 | dspV3phaseCoef | int16_t | R/W | 1
| 0xF2DA | 0xF2DA | 62170 | 62170 | dspI1phaseCoef | int16_t | R/W | 1
| 0xF2DB | 0xF2DB | 62171 | 62171 | dspI2phaseCoef | int16_t | R/W | 1
| 0xF2DC | 0xF2DC | 62172 | 62172 | dspI3phaseCoef | int16_t | R/W | 1
| 0xF2DD | 0xF2DD | 62173 | 62173 | dspI4phaseCoef | int16_t | R/W | 1
| 0xF2DE | 0xF2DE | 62174 | 62174 | dspI5phaseCoef | int16_t | R/W | 1
| 0xF2DF | 0xF2DF | 62175 | 62175 | dspI6phaseCoef | int16_t | R/W | 1
| 0xF2E0 | 0xF2E0 | 62176 | 62176 | dspI7phaseCoef | int16_t | R/W | 1
| 0xF2E1 | 0xF2E1 | 62177 | 62177 | dspI8phaseCoef | int16_t | R/W | 1
| 0xF2E2 | 0xF2E2 | 62178 | 62178 | dspI9phaseCoef | int16_t | R/W | 1
| 0xF2E3 | 0xF2E3 | 62179 | 62179 | dspI10phaseCoef | int16_t | R/W | 1
| 0xF2E4 | 0xF2E4 | 62180 | 62180 | dspI11phaseCoef | int16_t | R/W | 1
| 0xF2E5 | 0xF2E5 | 62181 | 62181 | dspI12phaseCoef | int16_t | R/W | 1
| 0xF2E6 | 0xF2E6 | 62182 | 62182 | dspI13phaseCoef | int16_t | R/W | 1
| 0xF2E7 | 0xF2E7 | 62183 | 62183 | dspI14phaseCoef | int16_t | R/W | 1
| 0xF2E8 | 0xF2E8 | 62184 | 62184 | dspI15phaseCoef | int16_t | R/W | 1
| 0xF2E9 | 0xF2E9 | 62185 | 62185 | dspI16phaseCoef | int16_t | R/W | 1
| 0xF2EA | 0xF2EA | 62186 | 62186 | dspI17phaseCoef | int16_t | R/W | 1
| 0xF2EB | 0xF2EB | 62187 | 62187 | dspI18phaseCoef | int16_t | R/W | 1
| 0xF2EC | 0xF2EC | 62188 | 62188 | dspI19phaseCoef | int16_t | R/W | 1
| 0xF2ED | 0xF2ED | 62189 | 62189 | dspI20phaseCoef | int16_t | R/W | 1
| 0xF2EE | 0xF2EE | 62190 | 62190 | dspI21phaseCoef | int16_t | R/W | 1
| 0xF2EF | 0xF2EF | 62191 | 62191 | dspI22phaseCoef | int16_t | R/W | 1
| 0xF2F0 | 0xF2F0 | 62192 | 62192 | dspI23phaseCoef | int16_t | R/W | 1
| 0xF2F1 | 0xF2F1 | 62193 | 62193 | dspI24phaseCoef | int16_t | R/W | 1
54

## DI Status
Block code function : 02H Read | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
DI Status
| 0x0000 | 0x0000 | 0 | 0 | DI1 | bit | R | 1
| 0x0001 | 0x0001 | 1 | 1 | DI2 | bit | R | 1
| 0x0002 | 0x0002 | 2 | 2 | DI3 | bit | R | 1
| 0x0003 | 0x0003 | 3 | 3 | DI4 | bit | R | 1

## DO¦RO Status
Block code function : 01H Read, 05H ¦ 0FH Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
IO Status
DO | 0x0000 | 0x0000 | 0 | 0 | DO1 | bit | R/W | 1
| 0x0001 | 0x0001 | 1 | 1 | DO2 | bit | R/W | 1
| 0x0002 | 0x0002 | 2 | 2 | DO3 | bit | R/W | 1
| 0x0003 | 0x0003 | 3 | 3 | DO4 | bit | R/W | 1
| 0x0004 | 0x0004 | 4 | 4 | DO5 | bit | R/W | 1
| 0x0005 | 0x0005 | 5 | 5 | DO6 | bit | R/W | 1
| 0x0006 | 0x0006 | 6 | 6 | DO7 | bit | R/W | 1
| 0x0007 | 0x0007 | 7 | 7 | DO8 | bit | R/W | 1
RO | 0x0020 | 0x0020 | 32 | 32 | RO1 | bit | R/W | 1
| 0x0021 | 0x0021 | 33 | 33 | RO2 | bit | R/W | 1