## Version History
Version | Changes | Author | Reviewer | Date | External Firmware Version
v1.00 | 初次发布.相比Acuvim II V2有如下变化 1. 增加了地址总表 2. 更改校准方法 3. 增加了双向视在电能 0x4900-0x490E 4. 增加了四象线无功电能 0x4910-0x492E 5. 调整了双向电能模块 - 电能寄存器 0x4930-0x493A 6. 更新了产品型号 7. 0x0FFE协议选择不再支持DNP3 8. 不再支持Net模块语音,密码,邮件服务配置0x020F-0x02A9 9. 不再支持AXM_BACnet通讯模块0x0400-0x0413 10. 不再支持V2波形记录的读取地址0x8E00-0x8E43;使用V4波形记录读取地址0x8F00-0x8F43 11. 不支持测温模块相关校准,配置和读数 12. Modbus和BACnet 波特率均限制在2400bps-115200bps 13. 0x463E为科诺定制地址区 14. 第一路和第二路波特率统一为2400bps-115200bps 15. 更正PXM3000型号为CRD6 16. 增加0x45F0负载百分比 17. 增加0x0200-0x020E 设备描述 18. 增加0xF073, 3CT/4CT配置 19. 增加PXM3000导轨型号CXD6; 删除定制型号CPCx, CUCx 20. 0x1020 需量计算滑差时间 - 出厂默认值 改成1 | 崔少航 |  | 2022-10-14
v1.01 | 1. 支持电流通道相序配置 0x10F4-0x10F7 2. 修改F000中HW VERSIO内容的R属性为RW(0xFB01)属性 3. Sonnen registers (tab Sonnen) 4. 恢复出厂设置由0x1028改为1026 5. Add 0x2105 Database Revision 6. 0x1021清除报警记录-写入0x0A有效 7. 自定义读取区域 0x6A00-0x6A1F 出厂默认值为0 8. 更新TOU出厂默认值读写方式 9. 清除波形记录0x800E, 清除事件记录0x800F-写入0x55有效 | Haibo Song |  | 2022-12-14
v1.02 | 1.按客户实际使用更新SunSpec | Haibo Song |  | 2023-01-19
v1.03 | 1. Translated to English and reformated. Updated parameter descriptions etc. 2. In "System Information" sheet, added 0xF074 power supply type 3. In "Meter Calibration" sheet, added 0xF2B0-0xF2B7 for FFT angle coefficients 4. In "Basic Settings" sheet, added 0x142F-0x1439 for indepenent input channel configurations 5. Added "Acuvim-L Parameters" sheet and related parameters in 0x2000-0x2029, 0x2080-0x20D3, 0x2180-0x21D3 6. Added "Independent Input Channel" sheet and related parameters in 0x2400-0x241F, 0x2500-0x2545, 0x2600-0x263F, 0x5220-0x5261, 0x5262-0x52D0 7. Merged DST, TOU settings, TOU schedule settings and TOU holiday settings to "TOU Settings" sheet 8. In “Meter Model" sheet, added Acuvim-L V4 models | Shaohang Cui |  | 2023-04-20 | v6.14
v1.04 | Added new sheet "Max, Min(float)" for Max/Min values in float format | Haibo Song |  | 2023-06-02 | v6.15
| Added new sheet "Debug" for troubleshooting scenario | Haibo Song |  | 2023-07-17
v1.05 | Added 0x10F8-0x10F9 in Basic Setting for Frequency Filter | Haibo Song |  | 2023-08-30 | v6.17
| Added 0xF0B1 for clearing feram memory in "System Information" | Haibo Song |  | 2023-09-08
v1.06 | 1. Added 0x1028 for enabling/disabling Modbus Gateway; 2. Added 0x10FF for choosing phase order; 3. Added 0x10FA-0x10FE for new pulse constant parameters 4. Added 0x303C -0x3043 for reading AI real values 5. Added 0x143A- 0x143B for load run time in Basic Setting. 6. Added 0x7E98 in TOU setting to clear 10 year holiday setting 7. Correct a wrong address in "Max, Min(float)" for min current demand | Haibo Song |  | 2023-12-07 | v6.20
v1.07 | Add 0x21D4 - 0x21DD in "Acuvim-L Parameters" for Phase Angles | Haibo Song |  | 2024-05-29 | v6.24
v1.08 | Add 0xF081 for MC enable/disable in "Basic Settings" | Haibo Song |  | 2024-06-04 | v6.26
v1.09 | 1. Added 0x0600- 0x064B in sheet "Acuvim-L Parameters" 2. Added 0x143C for flashing LCD command in "Basic Setting" 3. Added 0x010F-0x0115 for ETH2 parameters in "Communication Module" 4. Added 0x443A-0x443F for IO module DI status in "Alarm Recored¦DI" 5. Extended user defined parameters to 120 in "Basic Setting" 6. Added sheet "4-30 Class S Reading" 7. Added sheet "4-30 PQ Event" 8. Added 0x493D-0x49FE in "Real Time Parameters" for Moving Average Parameter for 1 Cycle RMS 9. Add 0x9503-0x9504 in "debug" sheet for waveform counter | Haibo Song |  | 2024-08-01 | v6.27
v1.10 | Remove power parameters from sheet "4-30 Class S Reading" Add PXE model in sheet "Meter Model" | Haibo Song |  | 2024-10-15 | v6.28
v1.11 | 0x143D "Phase Rotation" in sheet "Basic Setting": add a second value | Haibo Song |  | 2025-01-26 | v6.29/v6.30
V1.12 | 1. Add demand maxmin reset config 2. System Setting - In current direction in sheet "Basic Setting": 0x145D 3. Add 0xF02A in "System" for display version 4. Add accumulated energy setting and reading 5. Add wire check error code 6. Add 0x412B-0x412E in "Real Time Parameters" for TDD. 7. Add 0xF082 in "Basic Setting" for DELTA meter number. 8. Add 0x3044-0x3049 in "Real Time Parameters" for Displacement PF | Danyang Kuang Haibo Song Danyang Kuang Danyang Kuang Haibo Song |  | 2024/1/20 2024/01/31 2024/02/28 2025/04/09 2025/05/01 | v6.31
V1.13 | 1. Add all RO read&write (Delta Require) 0xF083-0XF08A in sheet "RO" | Danyang Kuang Haibo Song Danyang Kuang Danyang Kuang |  | 2025/4/16 | DELTA/
V1.14 | 1. Add 0xF083 for VFD enable. 2. Add 0x304A-0x304F for predictive demand in "Real Time Parameters" | Haibo Song |  | 2025-05-01 | v6.31_VFD_250415 | MTE model
v1.15 | 1. Add Compensation Factor for CT in 0x1461 - 0x1468 in "Basic Setting". 2. Add Polynomial_Coef in 0x1469 - 0x147A in "Basic Setting" | Haibo Song |  | 2025-06-27 | v6.30 DELTA v6.31 PXE
v1.16 | 1.Add default value for DELTA in 0x6B2F-0x6B38 in sheet "Basic Setting" 2. Add Last Interval Real Max/Min/Mean in 0x3050-0x3057 in sheet "Real Time Parameters". 3. Add Uart0 Writing enable/disable in 0x143E in sheet "Basic Setting" | Haibo Song |  | 2025-08-29 | v6.32 DELTA v6.32_AWS_250829
v1.17 | 1. Add RO Normal Condition in 0x147C; 2. Add Alarm channels trigger off delay in 0x147D - 0x148C | Haibo Song |  | 2025-11-04 | v6.36_ASA_251105
| 1. Add 0x148D for Energy Pulse Led Parameter Selection | Haibo Song |  | 2025-11-19 | For Xian
v1.18 | 1. Add 0x495F-0x4960 in "Real Time Parameters" for residual current. 2. Add 0x3098-0x30D9 in "Real Time Parameters" for last interval parameters. 3. Add 0x148E for Last interval setup for max/min/mean parameters in "Basic Setting" | Haibo Song |  | 2025-11-25 | v6.33_PXE_251212
v1.19 | Add 0x412F-0x4132 for current crest factor in sheet "Real Time Parameters" | Haibo Song |  | 2026-02-04 | v6.37_260204
v1.20 | Add 0x2640-0x26F0 for Transmission Line loss in sheet "Transmission Line loss" | Haibo Song |  | 2026-02-05
V1.21 | Add sheet "minilog" to record 3 months energy measurements at the interval of 5 mins | Bing |  | 2026-02-06
v1.22 | Add sheet Transmission line Loss : include configureation, power and enegry loss | Bolin Qu |  | 2026-02-12
v1.23 | Add Phase Angle of V1 to V1 (0x42A5) | Simon Chen |  | 2026-02-25
v1.24 | Add system Displacement power factor (0x30DA） | Bolin Qu | Simon Chen | 2026-03-04
v1.25 | Add 3LL-LN (DELTA High-Leg)for Voltage Input Wiring Type | Haibo Song | Simon Chen | 2026-03-05 | 6.37_2603xx 6.38_260305
v1.26 | Add Ethernet Port2 Connection status 0x0116 in sheet "Communication Module" updated block name in both Overview and Communication module tab | Haibo Song | Simon Chen | 2026-03-18 | 6.38_260318
v1.27 | Add Alarm Channel Real-Time Status from 0x26F1-0x2710 in sheet "Alarm Record" Add sheet "Alarm ID" | Haibo Song | Simon Chen | 2026-03-23 | 6.34_PXE_260323/6.26_PXM_260323

## Overview
Block | Sheet | Start | End | Length | Comments
AXM-NET/WEB/WEB2 settings | Communication module | 0x0100 | 0x0116 | 23
Device Description | Communication module | 0x0200 | 0x020E | 15
module language choice,password,mail server setup | Communication module | 0x020F | 0x02A9 | 155 | Not support any more
32 Virtual Relays | Communication module | 0x0216 | 0x0235 | 32
32 Virtual Inputs | Communication module | 0x0240 | 0x025F | 32
WiFi IP | Communication module | 0x02B0 | 0x02B1 | 2
AXM-WEB2 ETH2 IP | Communication module | 0x02B2 | 0x02B3 | 2
Network module reset | Communication module | 0x0300 | 0x0303 | 4
AXM_BACnet | Communication module | 0x0400 | 0x0413 | 20 | Not support any more
MESH network address | Communication module | 0x04f00 | 0x4F14 | 21
Acuvim LV3 primary real-time reading | Acuvim-L Parameters | 0x0600 | 0x064B | 76
| Basic Settings | 0x0FFD | 0x103E | 66 | 201
Basic Basic Settings | Basic Settings | 0x103F | 0x1045 | 7
Real time clock | Basic Settings | 0x1046 | 0x104D | 8
Alarm general settings | Basic Settings | 0x104E | 0x109D | 80
Alarm group settings | Basic Settings | 0x109E | 0x10C1 | 36
IO module settings | Basic Settings | 0x10C2 | 0x10C5 | 4
AO follow-up setting | Basic Settings | 0x10C6 | 0x10C8 | 3 | V3: not support
Wire temperature module setting | Basic Settings | 0x10D0 | 0x10F3 | 36
AO slope setting
| Basic Settings | 0x10F4 | 0x10F7 | 4
Current channel selection | Basic Settings | 0x10F8 | 0x10F9 | 2
Average Filter for Frequency（Update rate/Window Size） | Basic Settings | 0x10FA | 0x10FE | 5
Pulse constant | Basic Settings | 0x10FF |  | 1
Phase Order
| Data Log 1,2,3 | 0x1100 | 0x133F | 576
Data Log setup
| Basic Settings | 0x142F | 0x1439 | 11
Indepandent mode settings | Load Run Time | 0x143A | 0x143B | 2
System Setting | Basic Settings | 0x143C |  | 1
Flashing LCD | Basic Settings | 0x143D |  | 1
Phase Rotation | Basic Settings | 0x143E |  | 1
Uart0 Writing enable/disable
| Basic Setting | 0x1450 |  | 13
Demand maxmin Reset config | Basic Setting | 0x145D |  | 1
System Setting - In current direction
| Basic Setting | 0x1461 |  | 8 | DELTA
Compensation Factor for CT
| Basic Setting | 0x1469 |  | 18 | EATON
Polynomial_Coef | Basic Setting | 0x147C |  | 1 | ASA
RO Normal Condition | Basic Setting | 0x147D | 0x148C | 16 | ASA
Alarm channels trigger off delay | Basic Setting | 0x148D |  | 1
Energy Pulse Led Parameter Selection | Basic Setting | 0x148E |  | 1
Last interval for max/min/mean parameters
| Data Log 4 | 0x1500 | 0x15B9 | 186
Data Log settings
| Dual Source Energy | 0x1680 | 0x1687 | 8
Dual source energy module - setting
| Real Time Parameters | 0x1FFE | 0x2040 | 67 | Overlapped with Acuvim-L parameters; but they belongs to different model, so it is not an issue
Eaton customized parameters
| Acuvim-L parameters | 0x2000 | 0x2029 | 42
Acuvim-L Basic Readings (word)
| Acuvim-L parameters | 0x2080 | 0x20DD | 94
Acuvim-L Energy
| Basic Settings | 0x2100 | 0x2105 | 6
BACnet MS/TP settings
| Acuvim-L parameters | 0x2180 | 0x21D3 | 84
Acuvim-L Basic Readings (float)
| Independent Input Channel | 0x2400 | 0x241F | 32
Basic Readings (word)
| Debug | 0x2420 | 0x2421 | 2
Debug
| Independent Input Channel | 0x2500 | 0x2545 | 70
Energy
| Independent Input Channel | 0x2600 | 0x263F | 64
Basic Readings (Float)
| Transmission Line loss | 0x2640 | 0x26F0 | 177
Alarm Channel Status | Alarm Records | 0x26F1 | 0x2710 | 16
| Real Time Parameters | 0x3000 | 0x30D9 | 218
Real Time Parameters（100ms)
| Real Time Parameters | 0x3200 | 0x3226 | 39
Real Time Parameters（Integer）
| Real Time Parameters | 0x3400 | 0x341D | 30
20ms AcuvimIIV4、Eaton
| Real Time Parameters | 0x3500 | 0x3517 | 24
20ms AcuvimIIV2
| Real Time Parameters | 0x4000 | 0x4047 | 72
Real Time Parameters（1S） | Real Time Parameters | 0x4048 | 0x4059 | 18
Energy （1S） | Real Time Parameters | 0x405A | 0x412A | 209
Harmonics data（3S） | Real Time Parameters（TDD) | 0x412B | 0x412E | 4
| Real Time Parameters | 0x412F | 0x4132 | 3
Current crest factor
| Max, Min | 0x4136 | 0x41E4 | 175
Max value record | Max, Min | 0x41E5 | 0x4293 | 175
Min value record | Sequence and Phase Angle | 0x4294 | 0x429F | 12
Sequence | Sequence and Phase Angle | 0x42A0 | 0x42A8 | 9
Phase Angle | Alarm Records | 0x42A9 | 0x4348 | 160
Alarm Records | Alarm Records | 0x4349 | 0x4380 | 56
IO module DI pulse count | Alarm Records | 0x4381 | 0x4388 | 8
AO、AI analogic value | Alarm Records | 0x4389 | 0x4398 | 16
AO、AI real value | Alarm Records | 0x4399 | 0x4439 | 161
SOE record | Alarm Records | 0x443A | 0x443F | 6
IO module DI status
| Real Time Parameters | 0x4500 | 0x45BF | 192
Harmonics data（3S）32-63 cycle
| Real Time Parameters | 0x45F0 | 0x45F1 | 2
Load percentage
| Real Time Parameters | 0x4600 | 0x4605 | 6
Current demand | Max, Min | 0x4606 | 0x461A | 21
Current demand max. value
| Real Time Parameters | 0x4620 | 0x463D | 30
Energy - continue（1S） | Real Time Parameters | 0x463E | 0x478D | 336 | Customized address
Kono address list
| Real Time Parameters | 0x4900 | 0x490F | 16
Apparent Energy extend | Real Time Parameters | 0x4910 | 0x492F | 32
Four-quadrant reactive energy | Real Time Parameters/ Dual Source Energy | 0x4930 | 0x493B | 12
Dual source energy module - energy register
| Real Time Parameters | 0x493D | 0x495E | 34
Moving Average Parameter for 1 Cycle RMS | Real Time Parameters | 0x495F | 0x4960 | 2
Residual Current
| Communication Module | 0x4F00 | 0x4F14 | 21
MESH network address
| Max. Min(float) | 0x5000 | 0x51A7 | 424
Max/Min in float(normal mode)
| Independent Input Channel | 0x5220 | 0x52DD | 190
In Harmonics data
| Max. Min(float) | 0x52E0 | 0x5547 | 268
Max/Min in float(Independent mode)
| Data Log 1,2,3 | 0x6000 | 0x607E | 127
Data Log reading
| Data Log 1,2,3 | 0x6100 | 0x630B | 524
Data Log state
| Data Log 4 | 0x6400 | 0x647E | 127
Data Log 4 reading
| Data Log 4 | 0x6500 | 0x650B | 12
Data Log 4 state
| Basic Settings | 0x6A00 | 0x6A77 | 120
User defined reading area
| Basic Settings | 0x6B00 | 0x6B78 | 121
User defined reading setting area
| Dual Source Energy | 0x6D00 | 0x6D57 | 88
Dual source energy module - switch record area
| Real Time Parameters | 0x6E00 | 0x70E7 | 744
Harmonics amplitude value and phase angle（Secondary ）
| TOU Readings | 0x7200 | 0x7231 | 50
Current Month Accumulation TOU Energy | TOU Readings | 0x7232 | 0x7263 | 50
Previous Month Accumulation TOU Energy
| TOU Readings | 0x7300 | 0x7331 | 50
Current Month Incremental TOU Energy | TOU Readings | 0x7332 | 0x7363 | 50
Previous Month Incremental TOU Energy
| TOU Readings | 0x7500 | 0x759F | 160
Current Month TOU Max Demand
| TOU Readings | 0x7600 | 0x769F | 160
Previous Month TOU Max Demand
| TOU Settings | 0x7700 | 0x7717 | 24
Daylight Savings Time Settings
| TOU Settings | 0x7800 | 0x780E | 15
TOU Basic Settings
| TOU Settings | 0x7820 | 0x7843 | 36
Season settings | TOU Settings | 0x7844 | 0x7A8F | 588
Schedule settings | TOU Settings | 0x7A90 | 0x7AEC | 93
Holiday settings
| TOU Settings | 0x7B00 | 0x7E98 | 921
10 years holiday settings
| TOU Settings | 0x7F00 | 0x7F60 | 97
Special weekday schedule settings
| Waveform | 0x8000 | 0x8010 | 17
Waveform Settings | Waveform | 0x8011 | 0x801F | 15 | Not implemented
Energy Event output to DO/RO | Minilog | 0x8100 | 0x817B | 124
Minilog | Waveform | 0x8CFD | 0x8D4F | 83
Event Record reading Area
| Waveform | 0x8E00 | 0x8E43 | 68 | Not used any more
Waveform Record Reading/Access（Hardware V2.0）
| Waveform | 0x8F00 | 0x8F43 | 68
Waveform Record Reading/Access（Hardware V4.0）
| Wired temperature module | 0x9000 | 0x90FF | 256 | V3 does not support
Temperature module - temperature value reading | Wireless temperature module | 0x9100 | 0x9106 | 7 | V3 does not support
System information of wireless temperature module |  |  |  | 1
| Wireless temperature module | 0x9200 | 0x9311 | 274 | V3 does not support
Sensor Parameters |  |  |  | 1
| Wireless temperature module | 0x9400 | 0x9406 | 7 | V3 does not support
Networking Parameters
| Debug | 0x9500 | 0x9504 | 5
Debug
| 4-30 Class S Reading | 0x95B0 | 0xA3E2 | 3635
4-30 Class S Reading
| 4-30 PQ Event | 0xAF65 |  | 1
4-30 PQ Event Enable | 4-30 PQ Event | 0xAF66 | 0xAF8C | 45
PQ Event Setup | 4-30 PQ Event | 0xAF96 | 0xB008 | 115
PQ Event Log
| Sunspec | 0xC350 | 0xC419 | 202
Sunspec
| System Information | 0xF000 | 0xF008 | 9
Main version information | System Information | 0xF009 | 0xF020 | 24
IO version information | System Information | 0xF021 | 0xF024 | 4
AXM_NET | System Information | 0xF025 | 0xF028 | 4
PROFIBUS | System Information | 0xF029 | 0xF02F | 7 | V3 does not support
Wired temperature | System Information | 0xF030 | 0xF036 | 7 | V3 does not support
Wireless temperature | System Information | 0xF040 | 0xF0B1 | 114
Product information
| Basic Settings | 0xF081 |  | 1
MC-type | Basic Settings | 0xF082 |  | 1
DELTA Meter number
| IO Calibration | 0xF112 | 0xF114 | 3
Interface to PC（reserve） | IO Calibration | 0xF132 | 0xF139 | 8
IO module AO calibration parameters | IO Calibration | 0xF13A | 0xF141 | 8
IO module AI calibration parameters
| System Information | 0xF1F0 | 0xF1F1 | 2
CT/PT type setting
| IO Calibration | 0xF200 | 0xF202 | 3
IO module type setting
| Meter Calibration | 0xF204 | 0xF209 | 6
Acuvim II V3 RCT calibration | Meter Calibration | 0xF210 | 0xF25F | 80
Acuvim II V3 calibration | Meter Calibration | 0xF260 | 0xF2AF | 80
Acuvim II V3 RCT calibration
| Meter Calibration | 0xF2B0 | 0xF2E7 | 72
FFT angle Calibration
| Meter Calibration | 0xF3D0 | 0xF3DD | 14 | V3 does not support
Temperature module calibration
| TOU Default Setting | 0xF3FE | 0xF3FF | 2
Command to restore TOU factory default values | TOU Default Setting | 0xF400 | 0xF40E | 15
TOU factory default values
| TOU Default Setting | 0xF420 | 0xF6EC | 717
TOU factory default values 2
| TOU Default Setting | 0xF700 | 0xF795 | 150
PC used
| System Information | 0xFB01 |  | 1
Hardware version information
| Communication module | 0xFF00 | 0xFF01 | 2
Profibus address
| N/A | 0xFFF0 | 0xFFF0 | 1
AO Test
Customization |  | 0x0000 | 0x0043 | 68
Yuanjing Energy Wind-Electric Real-time parameters
|  | 0x901 | 0x901 | 1
Yuanjing Energy Wind-Electric PT1/PT2
|  | 0x6A00 | 0x6A1F | 32
Shanghai Wind-Electric Real-time parameters

## System Information
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | Reg | RW | Range | Default Value | Factory Default
Version Info
| 0xF000 |  | 61440 |  | Meter Model string in format like "CP01" (ASCII chars) |  | 1 | R | See "Meter Model" sheet
| 0xF001 |  | 61441 |  |  |  | 1 | R
| 0xF002 |  | 61442 |  | Hardware version string in format like "1.01" (ASCII chars). Write by Testbench via command 0x6A on address 0xFB01 |  | 1 | R
| 0xF003 |  | 61443 |  |  |  | 1 | R
| 0xF004 |  | 61444 |  | Software version string in format like "1.01" (ASCII chars) |  | 1 | R
| 0xF005 |  | 61445 |  |  |  | 1 | R
| 0xF006 |  | 61446 |  | Software date string in format like "230403" (ASCII chars, YYMMDD) |  | 1 | R
| 0xF007 |  | 61447 |  |  |  | 1 | R
| 0xF008 |  | 61448 |  |  |  | 1 | R
IO module info
IO Module 1, address 0
| 0xF009 |  | 61449 |  | A |  | 1 | R
0
| 0xF00A |  | 61450 |  | 1 |  | 1 | R
0
| 0xF00B |  | 61451 |  | 1 |  | 1 | R
1
| 0xF00C |  | 61452 |  | 0 |  | 1 | R
1
IO Module 2, address 0
| 0xF00D |  | 61453 |  | B |  | 1 | R
0
| 0xF00E |  | 61454 |  | 1 |  | 1 | R
0
| 0xF00F |  | 61455 |  | 1 |  | 1 | R
1
| 0xF010 |  | 61456 |  | 0 |  | 1 | R
1
IO Module 3, address 0
| 0xF011 |  | 61457 |  | C |  | 1 | R
0
| 0xF012 |  | 61458 |  | 1 |  | 1 | R
0
| 0xF013 |  | 61459 |  | 1 |  | 1 | R
1
| 0xF014 |  | 61460 |  | 0 |  | 1 | R
IO Module 1, address 1
| 0xF015 |  | 61461 |  | D |  | 1 | R
0
| 0xF016 |  | 61462 |  | 1 |  | 1 | R
0
| 0xF017 |  | 61463 |  | 1 |  | 1 | R
1
| 0xF018 |  | 61464 |  | 0 |  | 1 | R
IO Module 2, address 1
| 0xF019 |  | 61465 |  | E |  | 1 | R
0
| 0xF01A |  | 61466 |  | 1 |  | 1 | R
0
| 0xF01B |  | 61467 |  | 1 |  | 1 | R
1
| 0xF01C |  | 61468 |  | 0 |  | 1 | R
IO Module 3, address 1
| 0xF01D |  | 61469 |  | F |  | 1 | R
0
| 0xF01E |  | 61470 |  | 1 |  | 1 | R
0
| 0xF01F |  | 61471 |  | 1 |  | 1 | R
1
| 0xF020 |  | 61472 |  | 0 |  | 1 | R
Communication Module Info
| 0xF021 |  | 61473 |  | E |  | 1 | R | E: WEB module |  |  | Web module
[5 empty] | 0 | [6 empty] | Hardware version
| 0xF022 |  | 61474 |  | 1 |  | 1 | R
0
| 0xF023 |  | 61475 |  | 1 |  | 1 | R
1
| 0xF024 |  | 61476 |  | 0 |  | 1 | R |  |  |  | Firmware version
| 0xF025 |  | 61477 |  | P |  | 1 | R | P: profibus module
0
| 0xF026 |  | 61478 |  | 3 |  | 1 | R | Hardware version: 3.01
0
| 0xF027 |  | 61479 |  | 1 |  | 1 | R
[5 empty] | 1 |  |  |  | Firmware version: 1.02
| 0xF028 |  | 61480 |  | 0 |  | 1 | R
2
Display version | 0xF02A |  | 61482 |  |  |  | 2 |  |  |  |  | 6.31_MC_250228
Production Info
| 0xF040 | 0xF04F | 61504 | 61519 | Serial Number |  | 16 | RW, write by Testbench via command 0x6A | Acuvim II V3: in format AHBYYMMabcd Acuvim-L V4: in format CLDYYMMabcd
| 0xF050 | 0xF05F | 61520 | 61535 | Meter Model |  | 16 | RW, write by Testbench via command 0x6A | Acuvim II Acuvim IIR Acuvim IIE Acuvim IIW Acuvim IIBN Acuvim IIX Acuvim-CL Acuvim-EL |  | For DELTA: 0xF058 is 0:Delta1; 0xF058 is "11": Delta2
| 0xF060 | 0xF06F | 61536 | 61551 | WEB Module MAC address; write by WEB module |  | 16 | RW, write by Testbench via command 0x6A
| 0xF070 |  | 61552 |  | Model selection |  | 1 | RW, write by Testbench via command 0x6A | READ: Acuvim II: 0; Acuvim IIR: （1）; Acuvim IIE: （2）; Acuvim IIW: （3）; Acuvim IIBN: (4) Acuvim IIX: (5) (PXE2) PXE1: (6) Acuvim-CL: 7 Acuvim-EL: 8 | WRITE: Acuvim II: 0; Acuvim IIR: 0xE746; Acuvim IIE: 0xD829; Acuvim IIW: 0xC947; Acuvim IIBN: 0xC836 Acuvim IIX/PXE2: 0xBA28 PXE1: 0xBA29 Acuvim-CL: 0xE93A Acuvim-EL: 0xBC46
| 0xF071 |  | 61553 |  | Mount type selection |  | 1 | RW, write by Testbench via command 0x6A | 0: panel mount 1: DIN rail
| 0xF072 |  | 61554 |  | testbench disable seal |  | 1 | RW, write by Testbench via command 0x6A
| 0xF073 |  | 61555 |  | 3CT/4CT |  | 1 | RW, write by Testbench via command 0x6A | 0: 4CT; 1: 3CT For Acuvim-L, it can only be 4CT | 0: 4CT | 0: 4CT
| 0xF074 |  | 61556 |  | Power Supply Type |  | 1 | RW, write by Testbench via command 0x6A | 1: P1; 2: P2
| 0xF075 | 0xF07F | 61557 | 61567 | reserved |  | 11
| 0xF080 | 0xF080 | 61568 | 61568 | Restore web module default settings |  | 1 | RW | Write 1 to restore web module default settings
| 0xF090 | 0xF0B0 | 61584 | 61616 | Boot version info |  | 33 | R
| 0xF0B1 |  | 61617 |  | Clear feram command |  | 1 | R/W | 0x6666
| 0xF1F0 |  | 61936 |  | CT2 type | word | 1 | RW, write by Testbench via command 0x6A | 5: 1A/5A 333: 333mV/RCT 200: 200mA For Acuvim-L, it can only be 5 or 333
| 0xF1F1 |  | 61937 |  | PT2 type (actually not used) | word | 1 | RW, write by Testbench via command 0x6A | 100: 100V 400: 400V
| 0xFB01 |  | 64257 |  | Hardware version |  | 1 | RW, write by Testbench via command 0x6A | ASCII "00" to "99"

## IO Calibration
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Interface with PC（reserve）
| 0xF112 |  | 61714 |  | Frequency Configuration | int16 |  | 1 | 0: 50Hz; 1: 60Hz 2: 400Hz; 3: 800Hz
| 0xF113 |  | 61715 |  | Display test | int16 |  | 1 | 1: LCD all light 0: LCD normal
| 0xF114 |  | 61716 |  | Selection of AO test point | int16 |  | 1 | 0: auto follow; 1: test point; 2: low end; 3: high end; 4: zero point; 5: any point
IO module AO calibration values
| 0xF132 |  | 61746 |  | AO1 calibration value 1
| 0xF133 |  | 61747 |  | AO1 calibration value 2
| 0xF134 |  | 61748 |  | AO2 calibration value 1
| 0xF135 |  | 61749 |  | AO2 calibration value 2
| 0xF136 |  | 61750 |  | AO3 calibration value 1
| 0xF137 |  | 61751 |  | AO3 calibration value 2
| 0xF138 |  | 61752 |  | AO4 calibration value 1
| 0xF139 |  | 61753 |  | AO4 calibration value 2
IO module AI calibration values
| 0xF13A |  | 61754 |  | AI1 calibration value 1
| 0xF13B |  | 61755 |  | AI1 calibration value 2
| 0xF13C |  | 61756 |  | AI2 calibration value 1
| 0xF13D |  | 61757 |  | AI2 calibration value 2
| 0xF13E |  | 61758 |  | AI3 calibration value 1
| 0xF13F |  | 61759 |  | AI3 calibration value 2
| 0xF140 |  | 61760 |  | AI4 calibration value 1
| 0xF141 |  | 61761 |  | AI4 calibration value 2
IO module type setting
| 0xF200 |  | 61952 |  | IO1 address 0: A IO1 address 1: D | byte | R/W | 1
[5 empty] | 0 | byte | R/W
| 0xF201 |  | 61953 |  | IO2 address 0: B IO2 address 1: E | byte | R/W | 1
[5 empty] | AO Type | byte | R/W |  | Voltage type: 0 Current type: 1
| 0xF202 |  | 61954 |  | IO3 address 0: C IO3 address 1: F | byte | R/W | 1
[5 empty] | AI Type | byte | R/W |  | Voltage type: 0 Current type: 1

## Meter Calibration
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Calibration command
| 0xF204 |  | 61956 |  | Calibration command 1 (0x6A for writing） | word | W | 1
| 0xF205 |  | 61957 |  | Calibration command 2 (0x6A for writing） | word | W | 1
| 0xF206 |  | 61958 |  | Calibration command 3 (0x6A for writing） | word | W | 1
| 0xF207 |  | 61959 |  | Calibration command 4 (0x6A for writing） | word | W | 1
| 0xF208 |  | 61960 |  | Calibration inquire command (0x03 reading） | word | R | 1
| 0xF209 |  | 61961 |  | Exit calibration command (0x6A writing） | word | W | 1
5A, mA, mV calibration values
| 0xF210 | 0xF211 | 61968 | 61969 | 50Hz Va Gain | int32 | R/W | 2
| 0xF212 | 0xF213 | 61970 | 61971 | 50Hz Vb Gain | int32 | R/W | 2
| 0xF214 | 0xF215 | 61972 | 61973 | 50Hz Vc Gain | int32 | R/W | 2
| 0xF216 | 0xF217 | 61974 | 61975 | 50Hz Ia Gain | int32 | R/W | 2
| 0xF218 | 0xF219 | 61976 | 61977 | 50Hz Ib Gain | int32 | R/W | 2
| 0xF21A | 0xF21B | 61978 | 61979 | 50Hz Ic Gain | int32 | R/W | 2
| 0xF21C | 0xF21D | 61980 | 61981 | 50Hz In Gain | int32 | R/W | 2
| 0xF21E | 0xF21F | 61982 | 61983 | 50Hz Ia Phase Coeff | int32 | R/W | 2
| 0xF220 | 0xF221 | 61984 | 61985 | 50Hz Ib Phase Coeff | int32 | R/W | 2
| 0xF222 | 0xF223 | 61986 | 61987 | 50Hz Ic Phase Coeff | int32 | R/W | 2
| 0xF224 | 0xF225 | 61988 | 61989 | 50Hz Watt A Gain | int32 | R/W | 2
| 0xF226 | 0xF227 | 61990 | 61991 | 50Hz Watt B Gain | int32 | R/W | 2
| 0xF228 | 0xF229 | 61992 | 61993 | 50Hz Watt C Gain | int32 | R/W | 2
| 0xF22A | 0xF22B | 61994 | 61995 | 50Hz Va FFT Gain | float32 | R/W | 2
| 0xF22C | 0xF22D | 61996 | 61997 | 50Hz Vb FFT Gain | float32 | R/W | 2
| 0xF22E | 0xF22F | 61998 | 61999 | 50Hz Vc FFT Gain | float32 | R/W | 2
| 0xF230 | 0xF231 | 62000 | 62001 | 50Hz Ia FFT Gain | float32 | R/W | 2
| 0xF232 | 0xF233 | 62002 | 62003 | 50Hz Ib FFT Gain | float32 | R/W | 2
| 0xF234 | 0xF235 | 62004 | 62005 | 50Hz Ic FFT Gain | float32 | R/W | 2
| 0xF236 | 0xF237 | 62006 | 62007 | 50Hz In FFT Gain | float32 | R/W | 2
| 0xF238 | 0xF239 | 62008 | 62009 | 60Hz Va Gain | int32 | R/W | 2
| 0xF23A | 0xF23B | 62010 | 62011 | 60Hz Vb Gain | int32 | R/W | 2
| 0xF23C | 0xF23D | 62012 | 62013 | 60Hz Vc Gain | int32 | R/W | 2
| 0xF23E | 0xF23F | 62014 | 62015 | 60Hz Ia Gain | int32 | R/W | 2
| 0xF240 | 0xF241 | 62016 | 62017 | 60Hz Ib Gain | int32 | R/W | 2
| 0xF242 | 0xF243 | 62018 | 62019 | 60Hz Ic Gain | int32 | R/W | 2
| 0xF244 | 0xF245 | 62020 | 62021 | 60Hz In Gain | int32 | R/W | 2
| 0xF246 | 0xF247 | 62022 | 62023 | 60Hz Ia Phase Coeff | int32 | R/W | 2
| 0xF248 | 0xF249 | 62024 | 62025 | 60Hz Ib Phase Coeff | int32 | R/W | 2
| 0xF24A | 0xF24B | 62026 | 62027 | 60Hz Ic Phase Coeff | int32 | R/W | 2
| 0xF24C | 0xF24D | 62028 | 62029 | 60Hz Watt A Gain | int32 | R/W | 2
| 0xF24E | 0xF24F | 62030 | 62031 | 60Hz Watt B Gain | int32 | R/W | 2
| 0xF250 | 0xF251 | 62032 | 62033 | 60Hz Watt C Gain | int32 | R/W | 2
| 0xF252 | 0xF253 | 62034 | 62035 | 60Hz Va FFT Gain | float32 | R/W | 2
| 0xF254 | 0xF255 | 62036 | 62037 | 60Hz Vb FFT Gain | float32 | R/W | 2
| 0xF256 | 0xF257 | 62038 | 62039 | 60Hz Vc FFT Gain | float32 | R/W | 2
| 0xF258 | 0xF259 | 62040 | 62041 | 60Hz Ia FFT Gain | float32 | R/W | 2
| 0xF25A | 0xF25B | 62042 | 62043 | 60Hz Ib FFT Gain | float32 | R/W | 2
| 0xF25C | 0xF25D | 62044 | 62045 | 60Hz Ic FFT Gain | float32 | R/W | 2
| 0xF25E | 0xF25F | 62046 | 62047 | 60Hz In FFT Gain | float32 | R/W | 2
RCT calibration values
| 0xF260 | 0xF261 | 62048 | 62049 | RCT 50Hz Va Gain | int32 | R/W | 2
| 0xF262 | 0xF263 | 62050 | 62051 | RCT 50Hz Vb Gain | int32 | R/W | 2
| 0xF264 | 0xF265 | 62052 | 62053 | RCT 50Hz Vc Gain | int32 | R/W | 2
| 0xF266 | 0xF267 | 62054 | 62055 | RCT 50Hz Ia Gain | int32 | R/W | 2
| 0xF268 | 0xF269 | 62056 | 62057 | RCT 50Hz Ib Gain | int32 | R/W | 2
| 0xF26A | 0xF26B | 62058 | 62059 | RCT 50Hz Ic Gain | int32 | R/W | 2
| 0xF26C | 0xF26D | 62060 | 62061 | RCT 50Hz In Gain | int32 | R/W | 2
| 0xF26E | 0xF26F | 62062 | 62063 | RCT 50Hz Ia Phase Coeff | int32 | R/W | 2
| 0xF270 | 0xF271 | 62064 | 62065 | RCT 50Hz Ib Phase Coeff | int32 | R/W | 2
| 0xF272 | 0xF273 | 62066 | 62067 | RCT 50Hz Ic Phase Coeff | int32 | R/W | 2
| 0xF274 | 0xF275 | 62068 | 62069 | RCT 50Hz Watt A Gain | int32 | R/W | 2
| 0xF276 | 0xF277 | 62070 | 62071 | RCT 50Hz Watt B Gain | int32 | R/W | 2
| 0xF278 | 0xF279 | 62072 | 62073 | RCT 50Hz Watt C Gain | int32 | R/W | 2
| 0xF27A | 0xF27B | 62074 | 62075 | RCT 50Hz Va FFT Gain | float32 | R/W | 2
| 0xF27C | 0xF27D | 62076 | 62077 | RCT 50Hz Vb FFT Gain | float32 | R/W | 2
| 0xF27E | 0xF27F | 62078 | 62079 | RCT 50Hz Vc FFT Gain | float32 | R/W | 2
| 0xF280 | 0xF281 | 62080 | 62081 | RCT 50Hz Ia FFT Gain | float32 | R/W | 2
| 0xF282 | 0xF283 | 62082 | 62083 | RCT 50Hz Ib FFT Gain | float32 | R/W | 2
| 0xF284 | 0xF285 | 62084 | 62085 | RCT 50Hz Ic FFT Gain | float32 | R/W | 2
| 0xF286 | 0xF287 | 62086 | 62087 | RCT 50Hz In FFT Gain | float32 | R/W | 2
| 0xF288 | 0xF289 | 62088 | 62089 | RCT 60Hz Va Gain | int32 | R/W | 2
| 0xF28A | 0xF28B | 62090 | 62091 | RCT 60Hz Vb Gain | int32 | R/W | 2
| 0xF28C | 0xF28D | 62092 | 62093 | RCT 60Hz Vc Gain | int32 | R/W | 2
| 0xF28E | 0xF28F | 62094 | 62095 | RCT 60Hz Ia Gain | int32 | R/W | 2
| 0xF290 | 0xF291 | 62096 | 62097 | RCT 60Hz Ib Gain | int32 | R/W | 2
| 0xF292 | 0xF293 | 62098 | 62099 | RCT 60Hz Ic Gain | int32 | R/W | 2
| 0xF294 | 0xF295 | 62100 | 62101 | RCT 60Hz In Gain | int32 | R/W | 2
| 0xF296 | 0xF297 | 62102 | 62103 | RCT 60Hz Ia Phase Coeff | int32 | R/W | 2
| 0xF298 | 0xF299 | 62104 | 62105 | RCT 60Hz Ib Phase Coeff | int32 | R/W | 2
| 0xF29A | 0xF29B | 62106 | 62107 | RCT 60Hz Ic Phase Coeff | int32 | R/W | 2
| 0xF29C | 0xF29D | 62108 | 62109 | RCT 60Hz Watt A Gain | int32 | R/W | 2
| 0xF29E | 0xF29F | 62110 | 62111 | RCT 60Hz Watt B Gain | int32 | R/W | 2
| 0xF2A0 | 0xF2A1 | 62112 | 62113 | RCT 60Hz Watt C Gain | int32 | R/W | 2
| 0xF2A2 | 0xF2A3 | 62114 | 62115 | RCT 60Hz Va FFT Gain | float32 | R/W | 2
| 0xF2A4 | 0xF2A5 | 62116 | 62117 | RCT 60Hz Vb FFT Gain | float32 | R/W | 2
| 0xF2A6 | 0xF2A7 | 62118 | 62119 | RCT 60Hz Vc FFT Gain | float32 | R/W | 2
| 0xF2A8 | 0xF2A9 | 62120 | 62121 | RCT 60Hz Ia FFT Gain | float32 | R/W | 2
| 0xF2AA | 0xF2AB | 62122 | 62123 | RCT 60Hz Ib FFT Gain | float32 | R/W | 2
| 0xF2AC | 0xF2AD | 62124 | 62125 | RCT 60Hz Ic FFT Gain | float32 | R/W | 2
| 0xF2AE | 0xF2AF | 62126 | 62127 | RCT 60Hz In FFT Gain | float32 | R/W | 2
FFT angle coefficients
| 0xF2B0 | 0xF2B1 | 62128 | 62129 | 50Hz Va FFT angle Coef | float32 | R/W | 2
| 0xF2B2 | 0xF2B3 | 62130 | 62131 | 50Hz Vb FFT angle Coef | float32 | R/W | 2
| 0xF2B4 | 0xF2B5 | 62132 | 62133 | 50Hz Vc FFT angle Coef | float32 | R/W | 2
| 0xF2B6 | 0xF2B7 | 62134 | 62135 | 50Hz Ia FFT angle Coef | float32 | R/W | 2
| 0xF2B8 | 0xF2B9 | 62136 | 62137 | 50Hz Ib FFT angle Coef | float32 | R/W | 2
| 0xF2BA | 0xF2BB | 62138 | 62139 | 50Hz Ic FFT angle Coef | float32 | R/W | 2
| 0xF2BC | 0xF2BD | 62140 | 62141 | 50Hz In FFT angle Coef | float32 | R/W | 2
| 0xF2BE | 0xF2BF | 62142 | 62143 | 60Hz Va FFT angle Coef | float32 | R/W | 2
| 0xF2C0 | 0xF2C1 | 62144 | 62145 | 60Hz Vb FFT angle Coef | float32 | R/W | 2
| 0xF2C2 | 0xF2C3 | 62146 | 62147 | 60Hz Vc FFT angle Coef | float32 | R/W | 2
| 0xF2C4 | 0xF2C5 | 62148 | 62149 | 60Hz Ia FFT angle Coef | float32 | R/W | 2
| 0xF2C6 | 0xF2C7 | 62150 | 62151 | 60Hz Ib FFT angle Coef | float32 | R/W | 2
| 0xF2C8 | 0xF2C9 | 62152 | 62153 | 60Hz Ic FFT angle Coef | float32 | R/W | 2
| 0xF2CA | 0xF2CB | 62154 | 62155 | 60Hz In FFT angle Coef | float32 | R/W | 2
| 0xF2CC | 0xF2CD | 62156 | 62157 | RCT 50Hz Va FFT angle Coef | float32 | R/W | 2
| 0xF2CE | 0xF2CF | 62158 | 62159 | RCT 50Hz Vb FFT angle Coef | float32 | R/W | 2
| 0xF2D0 | 0xF2D1 | 62160 | 62161 | RCT 50Hz Vc FFT angle Coef | float32 | R/W | 2
| 0xF2D2 | 0xF2D3 | 62162 | 62163 | RCT 50Hz Ia FFT angle Coef | float32 | R/W | 2
| 0xF2D4 | 0xF2D5 | 62164 | 62165 | RCT 50Hz Ib FFT angle Coef | float32 | R/W | 2
| 0xF2D6 | 0xF2D7 | 62166 | 62167 | RCT 50Hz Ic FFT angle Coef | float32 | R/W | 2
| 0xF2D8 | 0xF2D9 | 62168 | 62169 | RCT 50Hz In FFT angle Coef | float32 | R/W | 2
| 0xF2DA | 0xF2DB | 62170 | 62171 | RCT 60Hz Va FFT angle Coef | float32 | R/W | 2
| 0xF2DC | 0xF2DD | 62172 | 62173 | RCT 60Hz Vb FFT angle Coef | float32 | R/W | 2
| 0xF2DE | 0xF2DF | 62174 | 62175 | RCT 60Hz Vc FFT angle Coef | float32 | R/W | 2
| 0xF2E0 | 0xF2E1 | 62176 | 62177 | RCT 60Hz Ia FFT angle Coef | float32 | R/W | 2
| 0xF2E2 | 0xF2E3 | 62178 | 62179 | RCT 60Hz Ib FFT angle Coef | float32 | R/W | 2
| 0xF2E4 | 0xF2E5 | 62180 | 62181 | RCT 60Hz Ic FFT angle Coef | float32 | R/W | 2
| 0xF2E6 | 0xF2E7 | 62182 | 62183 | RCT 60Hz In FFT angle Coef | float32 | R/W | 2
Temperature module calibration
| 0xF3D0 | 0xF3D0 | 62416 | 62416 | Calibration state: Calibration coefficient legitimacy | uint16 | R | 1 | BIT0: Is the calibration coefficient of the first temperature measurement channel legal?（same in following）0: legal 1: not legal BIT1: second channel BIT2: third channel BIT3: fourth channel BIT4: fifth channel Other bits: reserve
| 0xF3D1 | 0xF3D1 | 62417 | 62417 | Calibration state: Is calibration finished | uint16 | R | 1 | BIT0: step0: finished? 0: not,1: yes（same in following） BIT1: step1 Other bits: reserve
| 0xF3D2 | 0xF3D2 | 62418 | 62418 | Calibration state: Is calibration running | uint16 | R | 1 | BIT0: step0: is it in calibration? 0: no,1: yes（same in following） BIT1: step1: ... Other bits: reserve
| 0xF3D3 | 0xF3D3 | 62419 | 62419 | Calibration Step | uint16 | R | 1 | 0: temperature calibration step1 （T1=T2=T3= 32780Ω,0℃） 1: temperature calibration step2 （T1=T2=T3= 419Ω,116℃）
| 0xF3D4 | 0xF3D4 | 62420 | 62420 | 1 channel calibration parameter U1 | uint16 | R/W | 1 | Calibration parameters
| 0xF3D5 | 0xF3D5 | 62421 | 62421 | 1 channel calibration parameter R1 | uint16 | R/W | 1
| 0xF3D6 | 0xF3D6 | 62422 | 62422 | 2 channel calibration parameter U2 | uint16 | R/W | 1
| 0xF3D7 | 0xF3D7 | 62423 | 62423 | 2 channel calibration parameter R2 | uint16 | R/W | 1
| 0xF3D8 | 0xF3D8 | 62424 | 62424 | 3 channel calibration parameter U3 | uint16 | R/W | 1
| 0xF3D9 | 0xF3D9 | 62425 | 62425 | 3 channel calibration parameter R3 | uint16 | R/W | 1
| 0xF3DA | 0xF3DA | 62426 | 62426 | 4 channel calibration parameter U4 | uint16 | R/W | 1
| 0xF3DB | 0xF3DB | 62427 | 62427 | 4 channel calibration parameter R4 | uint16 | R/W | 1
| 0xF3DC | 0xF3DC | 62428 | 62428 | 5 channel calibration parameter U5 | uint16 | R/W | 1
| 0xF3DD | 0xF3DD | 62429 | 62429 | 5 channel calibration parameter R5 | uint16 | R/W | 1
0xF3FE: TOU factory default values

## Basic Settings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value | Release version/Note
System Settings: 03H Read, 10H Write
| 0x0FFD |  | 4093 |  | Frequency selection | word | R/W | 1 | 0: 50Hz 1: 60Hz 2. 400Hz | 0
| 0x0FFE |  | 4094 |  | Channel 1 Communication Protocol | word | R/W | 1 | 0: MODBUS 2: BACnet MS/TP | 0
| 0x0FFF |  | 4095 |  | Channel 1 Parity | word | R/W | 1 | 0: even 1: odd 2: None2 3: None1 | 3
| 0x1000 |  | 4096 |  | Password | word | R/W | 1 | 0-9999 | 0
| 0x1001 |  | 4097 |  | Channel 1 address | word | R/W | 1 | 1-247（Modbus） | 1
| 0x1002 |  | 4098 |  | Channel 1 Baud Rate | word | R/W | 1 | 2400-115200 | 19200
| 0x1003 |  | 4099 |  | Voltage Input Wiring Type | word | R/W | 1 | 0: 3LN 1: 1LN 2: 2LL 3: 3LL 4: 1LL 5：3LN-2.5 6: 2LN 7: 3LL-LN (DELTA High-Leg) | 0
| 0x1004 |  | 4100 |  | Current Input Wiring Type | word | R/W | 1 | 0: 3CT 1: 1CT 2: 2CT | 0
| 0x1005 |  | 4101 |  | PT1(High 16 bit) | word | R/W | 1 | 50.0-1000000.0 | 0
| 0x1006 |  | 4102 |  | PT1(Low 16 bit) | word | R/W | 1 |  | 400
| 0x1007 |  | 4103 |  | PT2 | word | R/W | 1 | 50.0-400.0 | 400
| 0x1008 |  | 4104 |  | CT1 | word | R/W | 1 | 1-50000 | 5
| 0x1009 |  | 4105 |  | CT2 | word | R/W | 1 | Depending on meter CT type * CT Type 1A/5A: 5: 5A; 1: 1A * CT Type mV: 333: 333mV; 100: 100mV/50Hz * CT Type mA: 80: 80mA; 100: 100mA; 200: 200mA | 5
| 0x100A |  | 4106 |  | kWh Pulse Constant | word | R/W | 1 | 1-60000 | 5000
| 0x100B |  | 4107 |  | kvarh Pulse Constant | word | R/W | 1 | 1-60000 | 5000
| 0x100C |  | 4108 |  | LCD Backlight Time | word | R/W | 1 | 0-120 | 1
| 0x100D |  | 4109 |  | Demand Interval | word | R/W | 1 | 1~30 | 15
| 0x100E |  | 4110 |  | Demand Method | word | R/W | 1 | 0: Fixed block, 1: Sliding block, 2: thermal, 3: Rolling block | 1
| 0x100F |  | 4111 |  | Clear Demand | word | R/W | 1 | Write 1 to clear | 0
| 0x1010 |  | 4112 |  | Clear Max/Min | word | R/W | 1 | Write 10 to clear | 0x55
| 0x1011 |  | 4113 |  | Clear run hours | word | R/W | 1 | Write 1 to clear | 0
| 0x1012 |  | 4114 |  | Current I1 Direction | word | R/W | 1 | 0: Positive; 1: Negative | 0
| 0x1013 |  | 4115 |  | Current I2 Direction | word | R/W | 1 | 0: Positive; 1: Negative | 0
| 0x1014 |  | 4116 |  | Current I3 Direction | word | R/W | 1 | 0: Positive; 1: Negative | 0
| 0x1015 |  | 4117 |  | VAR/PF Convention | word | R/W | 1 | 0: IEC; 1: IEEE | 0
| 0x1016 |  | 4118 |  | Clear Energy | word | R/W | 1 | Write 1 to clear | 0
| 0x1017 |  | 4119 |  | Energy Calculation Method | word | R/W | 1 | 0: Fundamental 1: Fundament+Harmonics | 1
| 0x1018 |  | 4120 |  | Reactive Power Calculation Method | word | R/W | 1 | 0: True Reactive Power 1: Generic Reactive Power | 0
| 0x1019 |  | 4121 |  | Energy Reading Display Primary/Secondary | word | R/W | 1 | 0: Primary; 1: Secondary; 2: Primary in 0.001kWh | 0 | 0/PXM3000 default 0 not editable
| 0x101A |  | 4122 |  | Reset Ethernet Module | word | R/W | 1 | 0: None 1: Reset 2: Restore factory default | 0
| 0x101B |  | 4123 |  | Enable SOE | word | R/W | 1 | 0: None 1: AXM-IO11 2: AXM-IO21 3: AXM-IO31 4: AXM-IO12 5: AXM-IO22 6: AXM-IO32 | 0
| 0x101C |  | 4124 |  | Clear Pulse Counter | word | R/W | 1 | 0: None 1: AXM-IO11 2: AXM-IO21 3: AXM-IO31 4: AXM-IO12 5: AXM-IO22 6: AXM-IO32 | 0
| 0x101D |  | 4125 |  | Basic Reading Display Primary/Secondary | word | R/W | 1 | 0: Secondary 1: Primary | 0 | 0/PXM3000 default 1 not editable
| 0x101E |  | 4126 |  | Non-standard content seal option | word | R/W | 1 | 0x55: enable 0xAA: disable | 0
| 0x101F |  | 4127 |  | Sealing status | word | R | 1 | sealed: 0x0A unsealed: 0
| 0x1020 |  | 4128 |  | demand calculation slip time | word | R/W | 1 | 1~30 | 1
| 0x1021 |  | 4129 |  | Clear alarm records | word | R/W | 1 | Write 0x0A to clear | 0 |  | use writing 0x0A to clear
| 0x1022 |  |  |  | CT41 | word | R/W | 1 | 1-50000 | 5 | As CT1
| 0x1023 |  |  |  | CT42 | word | R/W | 1 | Depending on meter CT type * CT Type 1A/5A: 5: 5A; 1: 1A * CT Type mV: 333: 333mV; 100: 100mV/50Hz * CT Type mA: 80: 80mA; 100: 100mA; 200: 200mA | 5 | As CT2
| 0x1024 |  |  |  | JiGuan customized PT
| 0x1025 |  |  |  | JiGuan customized CT
| 0x1026 |  |  |  | Restore factory setting | word | R/W |  | Write 0x01 to clear | 0
| 0x1027 |  |  |  | Line N current method | uint16 | R/W | 1 | 0: calculated 1: measured | 1 | 0
| 0x1028 |  |  |  | Modbus Gateway Enable/Disable | uint16 | R/W | 1 | 0: disable; 1:enable | 0 | 0
| 0x1029 |  |  |  | reserve
| 0x102A |  |  |  | reserve
| 0x102B |  |  |  | reserve
| 0x102C |  |  |  | Nominal full load power |  |  | 1 | 1 - 14400W | 1
| 0x102D |  |  |  | Load characteristics |  |  | 1 | 0: current 1: power | 0
| 0x102E |  | 4142 |  | System status | word | R | 1 | Bit0: for new alarm Bit1: for new SOE event
| 0x102F |  | 4143 |  | Channel 2 baud rate | word | R/W | 1 | 2400-115200 | 38400 | PXM3000 default: 115200 not editable
| 0x1030 |  | 4144 |  | Channel 2 parity | word | R/W | 1 | 0: even 1: odd 2: None2 3: None1 | 3 | PXM3000 default: 3 not editable
| 0x1031 |  | 4145 |  | Channel 2 address | word | R/W | 1 | 1-247（Modbus） | 1 | PXM3000 default 2 not editable
| 0x1032 |  | 4146 |  | Alarm group number | word | R | 1 | 0: no alarm record; 1-16: latest alarm record group number
| 0x1033 |  | 4147 |  | SOE record group number | word | R | 1 | 0: no SOE record; 1-20: latest SOE record group number
| 0x1034 |  | 4148 |  | Run Hour high byte | word | R | 1
| 0x1035 |  | 4149 |  | Run Hour low byte | word | R | 1
| 0x1036 |  | 4150 |  | module connection status | word | R | 1 | Bit0 ~ Bit5: for IO11 ~ IO32, Bit6: for wired temperature module Bit7: for wireless temperature module (0: not connected,1: connected)
| 0x1037 |  | 4151 |  | Temperature（used by old Acuvim II） | word | R | 1
| 0x1038 |  | 4152 |  | Channel 2 communication protocol | word | R/W | 1 | 0: other 1: BACnet 2: MESH 3: WIFI 4: WEB2(EATON vesion: ETHM) 5: Profibus | 0 | 0/PXM3000 defualt: 0 not editable
| 0x1039 |  | 4153 |  | enable downloading TOU Ten year configs | word | R/W | 1 |  | 0
| 0x103A |  | 4154 |  | Clear max demand - sharp tariff | word | R/W | 1
| 0x103B |  | 4155 |  | Clear max demand - peak tariff | word | R/W | 1
| 0x103C |  | 4156 |  | Clear max demand - valley tariff | word | R/W | 1
| 0x103D |  | 4157 |  | Clear max demand - normal tariff | word | R/W | 1
| 0x103E |  | 4158 |  | Clear max demand - all tariffs | word | R/W | 1
Real time clock
| 0x103F |  | 4159 |  | Week | word | R/W | 1 |  | 0
| 0x1040 |  | 4160 |  | Year | word | R/W | 1 |  | 2000
| 0x1041 |  | 4161 |  | Month | word | R/W | 1 |  | 1
| 0x1042 |  | 4162 |  | Day | word | R/W | 1 |  | 1
| 0x1043 |  | 4163 |  | Hour | word | R/W | 1 |  | 0
| 0x1044 |  | 4164 |  | Minute | word | R/W | 1 |  | 0
| 0x1045 |  | 4165 |  | Second | word | R/W | 1 |  | 0
Alarm settings
| 0x1046 |  | 4166 |  | Enable all alarm function | word | R/W | 1 | 1 | 0
| 0x1047 |  | 4167 |  | Enable alarm LCD flashing | word | R/W | 1 | 1 | 0
| 0x1048 |  | 4168 |  | Enable alarm channels | word | R/W | 1 | Bit 0~15 for alarm channel 1~16 (0: disabled; enabled) | 0
| 0x1049 |  | 4169 |  | Enable "AND" logic for alarm channels | word | R/W | 1 | Bit 0 for alarm channel 1 and 2; Bit 1 for alarm channel 3 and 4; Bit 2 for alarm channel 5 and 6; Bit 3 for alarm channel 7 and 8; Bit 4 for alarm channel 9 and 10; Bit 5 for alarm channel 11 and 12; Bit 6 for alarm channel 13 and 14; Bit 7 for alarm channel 15 and 16; (0: disabled; enabled) | 0
| 0x104A |  | 4170 |  | Alarm channels to trigger DO1 | word | R/W | 1 | Bit 0~15 for alarm channel 1~16 (0: disabled; enabled) | 0
| 0x104B |  | 4171 |  | Alarm channels to trigger DO2 | word | R/W | 1 | Bit 0~15 for alarm channel 1~16 (0: disabled; enabled) | 0
| 0x104C |  | 4172 |  | Alarm channels to trigger DO3 | word | R/W | 1 | Bit 0~15 for alarm channel 1~16 (0: disabled; enabled) | 0
| 0x104D |  | 4173 |  | Alarm channels to trigger DO4 | word | R/W | 1 | Bit 0~15 for alarm channel 1~16 (0: disabled; enabled) | 0
| 0x104E |  | 4174 |  | Alarm channel 1 parameter selection | int16 | R/W | 1 | 0 ~ 79 | 0
| 0x104F |  | 4175 |  | Alarm channel 1 logic | int16 | R/W | 1 | 1: > 2: = 3: < | 1
| 0x1050 |  | 4176 |  | Alarm channel 1 threshold (setpoint) | int16 | R/W | 1 | If DI parameter is selected: * 0 for no alarm * 1 for ON to trigger alarm * 2 for OFF to trigger alarm * 3 for both ON/OFF to trigger alarm | 0
| 0x1051 |  | 4177 |  | Alarm channel 1 delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x1052 |  | 4178 |  | Alarm channel 1 relay output selection | int16 | R/W | 1 | 0: no output 1-8: output relay ID | 0
| 0x1053 | 0x1057 | 4179 | 4183 | Alarm channel 2 configuration |  | R/W | 5
| 0x1058 | 0x105C | 4184 | 4188 | Alarm channel 3 configuration |  | R/W | 5
| 0x105D | 0x1061 | 4189 | 4193 | Alarm channel 4 configuration |  | R/W | 5
| 0x1062 | 0x1066 | 4194 | 4198 | Alarm channel 5 configuration |  | R/W | 5
| 0x1067 | 0x106B | 4199 | 4203 | Alarm channel 6 configuration |  | R/W | 5
| 0x106C | 0x1070 | 4204 | 4208 | Alarm channel 7 configuration |  | R/W | 5
| 0x1071 | 0x1075 | 4209 | 4213 | Alarm channel 8 configuration |  | R/W | 5
| 0x1076 | 0x107A | 4214 | 4218 | Alarm channel 9 configuration |  | R/W | 5
| 0x107B | 0x107F | 4219 | 4223 | Alarm channel 10 configuration |  | R/W | 5
| 0x1080 | 0x1084 | 4224 | 4228 | Alarm channel 11 configuration |  | R/W | 5
| 0x1085 | 0x1089 | 4229 | 4233 | Alarm channel 12 configuration |  | R/W | 5
| 0x108A | 0x108E | 4234 | 4238 | Alarm channel 13 configuration |  | R/W | 5 |  |  |  |  | Table of Alarm variable order number
| 0x108F | 0x1093 | 4239 | 4243 | Alarm channel 14 configuration |  | R/W | 5
| 0x1094 | 0x1098 | 4244 | 4248 | Alarm channel 15 configuration |  | R/W | 5
| 0x1099 | 0x109D | 4249 | 4253 | Alarm channel 16 configuration |  | R/W | 5
88
IO module settings
IO module1,address 0
| 0x109E |  | 4254 |  | DI1-6 type | word | R/W | 1 | Bit 0-5 for DI 1-6 0: Status Monitor; 1: Pulse Counter
| 0x109F |  | 4255 |  | DI Pulse Constant | word | R/W | 1 | 1 - 65535
| 0x10A0 |  | 4256 |  | RO Type Mode | word | R/W | 1 | 0: Relay 1: Alarm 2: PQ event
| 0x10A1 |  | 4257 |  | RO Control Mode | word | R/W | 1 | 0: Latch 1: Momentary 2: Manual
| 0x10A2 |  | 4258 |  | RO Pulse Width | word | R/W | 1 | 50 - 3000(in relay mode);300 - 3000(in alarm mode)
IO module 2,address 0
| 0x10A3 |  | 4259 |  | DI7~10 Type | word | R/W |  | Bit0-3 for DI7-10 0: Status Monitor; 1: Pulse Counter
| 0x10A4 |  | 4260 |  | DI Pulse Constant | word | R/W |  | 1~65535
| 0x10A5 |  | 4261 |  | DO Mode | word | R/W |  | 0: Energy Pulse output 1: Alarm output, 2: PQ event
| 0x10A6 |  | 4262 |  | DO Pulse width | word | R/W |  | 20~100ms
| 0x10A7 |  | 4263 |  | DO1 Parameter selection | word | R/W |  | 0: None 1: EP_IMP 2: EP_EXP 3: EQ-IMP 4: EQ_EXP
| 0x10A8 |  | 4264 |  | DO2 Parameter selection | word | R/W |  | 0: None 1: EP_IMP 2: EP_EXP 3: EQ-IMP 4: EQ_EXP
| 0x10A9 |  | 4265 |  | AO Type | word | R/W |  | 0: 0~20mA 1: 4~20mA 2: 0~5V 3: 1~5V
IO module 3,address 0
| 0x10AA |  | 4266 |  | DI11~DI14 Type | word | R/W |  | Bit0-3 for DI11-14 0: Status Monitor; 1: Pulse Counter
| 0x10AB |  | 4267 |  | DI Pulse Constant | word | R/W |  | 1~65535
| 0x10AC |  | 4268 |  | RO Type Mode | word | R/W |  | 0: Relay 1: Alarm
| 0x10AD |  | 4269 |  | RO Control Mode | word | R/W |  | 0: Latch 1: Momentary 2: Manual
| 0x10AE |  | 4270 |  | RO Pulse Width | word | R/W |  | 50 - 3000(in relay mode);300 - 3000(in alarm mode)
| 0x10AF |  | 4271 |  | AI Type | word | R/W |  | 0: 0~20mA 1: 4~20mA 2: 0~5V 3: 1~5V
IO module 1,address 1 | [10 empty] | As IO module 1, address 0
| 0x10B0 |  | 4272 |  | DI15~20 Type | word | R/W | 1 | Bit0-5 for DI15-20 0: Status Monitor; 1: Pulse Counter
| 0x10B1 |  | 4273 |  | DI Pulse Constant | word | R/W | 1 | 1~65535
| 0x10B2 |  | 4274 |  | RO Type Mode | word | R/W | 1 | 0: Relay 1: Alarm 2: PQ event
| 0x10B3 |  | 4275 |  | RO Control Mode | word | R/W | 1 | 0: Latch 1: Momentary 2: Manual
| 0x10B4 |  | 4276 |  | Pulse Width | word | R/W | 1 | 50 - 3000(in relay mode);300 - 3000(in alarm mode)
IO module 2, address 1 | [10 empty] | As IO module 2, address 0
| 0x10B5 |  | 4277 |  | DI21~DI24 Type | word | R/W |  | Bit0-3 for DI21-24 0: Status Monitor; 1: Pulse Counter
| 0x10B6 |  | 4278 |  | DI Pulse Constant | word | R/W |  | 1~65535
| 0x10B7 |  | 4279 |  | DO Mode | word | R/W |  | 0: Energy Pulse output 1: Alarm output, 2: PQ event
| 0x10B8 |  | 4280 |  | DO Pulse width | word | R/W |  | 20~100ms
| 0x10B9 |  | 4281 |  | DO1 Output | word | R/W |  | 0: None 1: EP_IMP 2: EP_EXP 3: EQ-IMP 4: EQ_EXP
| 0x10BA |  | 4282 |  | DO2 Output | word | R/W |  | 0: None 1: EP_IMP 2: EP_EXP 3: EQ-IMP 4: EQ_EXP
| 0x10BB |  | 4283 |  | AO Type | word | R/W |  | 0: 0~24mA 1: 4~24mA 2: 0~6V 3: 1~6V
IO module 3, address 1 | [10 empty] | As IO module 3, address 0
| 0x10BC |  | 4284 |  | DI25~DI28 Type | word | R/W |  | Bit0-3 for DI25-28 0: Status Monitor; 1: Pulse Counter
| 0x10BD |  | 4285 |  | DI Pulse Constant | word | R/W |  | 1~65535
| 0x10BE |  | 4286 |  | RO Type Mode | word | R/W |  | 0: Relay 1: Alarm 2: PQ event
| 0x10BF |  | 4287 |  | RO Control Mode | word | R/W |  | 0: Latch 1: Momentary 2: Manual
| 0x10C0 |  | 4288 |  | Pulse Width | word | R/W |  | 50 - 3000(in relay mode);300 - 3000(in alarm mode)
| 0x10C1 |  | 4289 |  | AI Type | word | R/W |  | 0: 0~20mA 1: 4~20mA 2: 0~5V 3: 1~5V
AO settings
| 0x10C2 | 0x10C2 | 4290 | 4290 | AO1 Parameter Selection | uint16 | R/W | 1 | 0-29. 0: Frequency; 1: Va; 2: Vb; 3: Vc; 4: VLN Avg; 5: Vab; 6: Vbc; 7: Vca; 8: VLL Avg; 9: Ia; 10: Ib; 11: Ic; 12: Iavg; 13: In; 14: Pa; 15: Pa; 16: Pc; 17: P; 18: Qa; 19: Qb; 20: Qc; 21: Q; 22: Sa; 23: Sb; 24: Sc; 25: S; 26: Pfa; 27: PFb; 28: PFc; 29: PF | 0 | 0
| 0x10C3 | 0x10C3 | 4291 | 4291 | AO2 Parameter Selection | uint16 | R/W | 1 |  | 0 | 0
| 0x10C4 | 0x10C4 | 4292 | 4292 | AO3 Parameter Selection | uint16 | R/W | 1 |  | 0 | 0
| 0x10C5 | 0x10C5 | 4293 | 4293 | AO4 Parameter Selection | uint16 | R/W | 1 |  | 0 | 0
| 0x10C6 | 0x10C8 | 4294 | 4296 | Wired temperature module parameter setup |  |  | 3
| 0x10D0 |  | 4304 |  | AO1 conversion curve number of setpoints | int16 | R/W | 1 | 1~3
| 0x10D1 |  | 4305 |  | AO1 setpoint 1 parameter value | int16 | R/W | 1
| 0x10D2 |  | 4306 |  | AO1 setpoint 2 parameter value | int16 | R/W | 1
| 0x10D3 |  | 4307 |  | AO1 setpoint 3 parameter value | Int | R/W | 1
| 0x10D4 |  | 4308 |  | AO1 setpoint 4 parameter value | int16 | R/W | 1
| 0x10D5 |  | 4309 |  | AO1 setpoint 1 AO value | int16 | R/W | 1 | For AO type 0-24mA/0-6V: 0~4095 For AO type 4~24mA/1-6V: 819~4915
| 0x10D6 |  | 4310 |  | AO1 setpoint 2 AO value | int16 | R/W | 1
| 0x10D7 |  | 4311 |  | AO1 setpoint 3 AO value | int16 | R/W | 1
| 0x10D8 |  | 4312 |  | AO1 setpoint 4 AO value | int16 | R/W | 1
| 0x10D9 | 0x10E1 | 4313 | 4321 | AO2 setpoints settings | int16 | R/W | 9
| 0x10E2 | 0x10EA | 4322 | 4330 | AO3 setpoints settings | int16 | R/W | 9
| 0x10EB | 0x10F3 | 4331 | 4339 | AO4 setpoints settings | int16 | R/W | 9
| 0x10F4 |  | 4340 |  | Ia channel phase selection | int16 | R/W | 1 | 0: not in use 1: phase A current 2: phase B current 3: phase C current 4: phase N current | 0 | 0
| 0x10F5 |  | 4341 |  | Ib channel phase selection | int16 | R/W | 1 |  | 0 | 0
| 0x10F6 |  | 4342 |  | Ic channel phase selection | int16 | R/W | 1 |  | 0 | 0
| 0x10F7 |  | 4343 |  | In channel phase selection | int16 | R/W | 1 |  | 0 | 0
Average Filter for Frequency | 0x10F8 |  | 4344 |  | Update rate | int16 | R/W | 1 | 1-Window size | 1 | 1
| 0x10F9 |  | 4345 |  | Window Size | int16 | R/W | 1 | 1-50 cycles | 4 | 4
Pulse constant | 0x10FA |  | 4346 |  | Pulse constant type | int16 | R/W | 1 | 0：disable; 1: enable | 0
| 0x10FB | 0x10FC | 4347 | 4348 | Pulse constant for energy, advance setting, active power | float | R/W | 2 | 0.001 - 800 | 1
| 0x10FD | 0x10FE | 4349 | 4350 | Pulse constant for energy, advance setting, reactive power | float | R/W | 2 | 0.001 - 800 | 1
Phase Order | 0x10FF |  | 4351 |  | Phase Order | uint16 | R/W | 1 | 0: ABC; 1:ACB | 0 | 0
Independent Input Channel settings
| 0x142F |  | 5167 |  | Enable Independent Input Channel | uint16 | R/W | 1 | 0: disable; 1: enable | 0 | 0
| 0x1430 |  | 5168 |  | I1 CT1 | uint16 | R/W | 1 | 1 - 50000 | 5 | 5
| 0x1431 |  | 5169 |  | I2 CT1 | uint16 | R/W | 1 |  | 5 | 5
| 0x1432 |  | 5170 |  | I3 CT1 | uint16 | R/W | 1 |  | 5 | 5
| 0x1433 |  | 5171 |  | Voltage selection for I1 power calculation | uint16 | R/W | 1 | 0: disable 1: Va 2: Vb 3: Vc 4: Vab 5: Vbc 6: Vca | 0 | 0
| 0x1434 |  | 5172 |  | Voltage selection for I2 power calculation | uint16 | R/W | 1 |  | 0 | 0
| 0x1435 |  | 5173 |  | Voltage selection for I3 power calculation | uint16 | R/W | 1 |  | 0 | 0
| 0x1436 |  | 5174 |  | Voltage selection for I4 power calculation | uint16 | R/W | 1 |  | 0 | 0
| 0x1437 |  | 5175 |  | Summation 1 channel config | uint16 | R/W | 1 | Bit0-3 for current input channel 1-4 (I1-I4) | 7 | 7
| 0x1438 |  | 5176 |  | Summation 2 channel config | uint16 | R/W | 1 | Bit0-3 for current input channel 1-4 (I1-I4) | 0 | 0
| 0x1439 |  | 5177 |  | In angle calibration flag Only allow write with 0x6A | uint16 | R/W | 1 | 0: In angle not calibrated Bit0-3: In angle calibrated for 50Hz, 60Hz, 50Hz RCT, 60Hz RCT | 0 | 0
System Setting | 0x143A |  | 5178 |  | Load Run Time High Byte | uint16 | R | 1 | 0 - 65535(0xFFFF) | 0
| 0x143B |  | 5179 |  | Load Run Time Low Byte | uint16 | R | 1 | 0 - 65535(0xFFFF) | 0
| 0x143C |  | 5180 |  | Flashing LCD command | uint16 | W | 1 | 0: grey; 1: light | 0
| 0x143D |  | 5181 |  | Phase Rotation | uint16 | RW | 1 | 0: reverse; 1: normal | 0 (1 for PXM model)
| 0x143E |  | 5182 |  | Uart0 Writing enable/disable | uint16 | RW | 1 | 0: enable; 1: disable | 0 |  | v6.32_PXE_251027; v6.37_260123
Demand reset max/min seting | 0x1450 |  | 5200 |  | Demand MaxMin reset mode | uint16 | RW | 1 | 0:manuel ; 1:auto | 0 | 0 | v6.31_MC_250417; v6.32_250627; v6.30_PXE_250627
| 0x1451 |  | 5201 |  | Demand MaxMin auto reset time (day/hour/min) | uint16 | RW | 3 | day(1-30) hour(1-24) min(1-60)
| 0x1454 |  | 5204 |  | Demand MaxMin reset count | uint16 | R | 1 | 0 - INT_MAX | 0 | 0
| 0x1455 |  | 5205 |  | Demand MaxMin last reset time | uint16 | R | 6 |  | 0 | 0
| 0x145B |  | 5211 |  | Demand MaxMin reset flag | uint16 | RW | 1 | 0-1 | 0 | 0
| 0x145C |  | 5212 |  | Demand MaxMin reset Record | uint16 | RW | 1 | 0-1 | 0 | 0
System Setting | 0x145D |  | 5213 |  | Current In Direction | word | R/W | 1 | 0: Positive; 1: Negative | 0 |  | v6.31_MC_250417; v6.32_250627; v6.30_PXE_250627
Accumulated Energy Setting | 0x145E |  | 5214 |  | Time Internal for accumulated energy | uint16 | R/W | 1 | 0: 30min 1:1day 2:1week 3:1month | 0 | 0 | v6.31_MC_250417;v6.32_250627
| 0x145F |  | 5215 |  | Manuel reset accumulated energy | uint16 | R/W | 1 | 0-1 | 0 | 0
Wirecheck error code | 0x1460 |  | 5216 |  | Wirecheck Error Code | uint16 | R | 1 | 0 - 65535(0xFFFF) | 0 |  | v6.32_250627; v6.30_PXE_250627
Compensation Factor for CT | 0x1461 | 0x1462 | 5217 | 5218 | Compensation Factor for CT, phase A | float32 | R/W | 2 |  | 1
| 0x1463 | 0x1464 | 5219 | 5220 | Compensation Factor for CT, phase B | float32 | R/W | 2 |  | 1
| 0x1465 | 0x1466 | 5221 | 5222 | Compensation Factor for CT, phase C | float32 | R/W | 2 |  | 1
| 0x1467 | 0x1468 | 5223 | 5224 | Compensation Factor for CT, phase N | float32 | R/W | 2 |  | 1
Polynomial_Coef | 0x1469 | 0x146A | 5225 | 5226 | Polynomial_Coef, Va_1 | float32 | R/W | 2 |  | 1 |  | v6.31_PXE_250804; v6.26_PXM_251010
| 0x146B | 0x146C | 5227 | 5228 | Polynomial_Coef, Va_2 | float32 | R/W | 2 |  | 1
| 0x146D | 0x146E | 5229 | 5230 | Polynomial_Coef, Va_3 | float32 | R/W | 2 |  | 1
| 0x146F | 0x1470 | 5231 | 5232 | Polynomial_Coef, Vb_1 | float32 | R/W | 2 |  | 1
| 0x1471 | 0x1472 | 5233 | 5234 | Polynomial_Coef, Vb_2 | float32 | R/W | 2 |  | 1
| 0x1473 | 0x1474 | 5235 | 5236 | Polynomial_Coef, Vb_3 | float32 | R/W | 2 |  | 1
| 0x1475 | 0x1476 | 5237 | 5238 | Polynomial_Coef, Vc_1 | float32 | R/W | 2 |  | 1
| 0x1477 | 0x1478 | 5239 | 5240 | Polynomial_Coef, Vc_2 | float32 | R/W | 2 |  | 1
| 0x1479 | 0x147A | 5241 | 5242 | Polynomial_Coef, Vc_3 | float32 | R/W | 2 |  | 1
v6.35_DELTA_250917; v6.35_250908_bootloader
| 0x147B |  | 5243 |  | Firmware update enable | uint16 | R/W | 2 | 1: enable
| 0x147C |  | 5244 |  | RO Normal Condition |  |  | 1 | bit1: IO11_RO1 -- 0: NO, 1: NC bit2: IO11_RO2 bit3: IO31_RO1 bit4: IO31_RO2 bit5: IO12_RO1 bit6: IO12_RO2 bit7: IO32_RO1 bit8: IO32_RO2 |  |  | v6.36_ASA_251105
| 0x147D |  | 5245 |  | Alarm channel 1 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x147E |  | 5246 |  | Alarm channel 2 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x147F |  | 5247 |  | Alarm channel 3 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x1480 |  | 5248 |  | Alarm channel 4 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x1481 |  | 5249 |  | Alarm channel 5 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x1482 |  | 5250 |  | Alarm channel 6 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x1483 |  | 5251 |  | Alarm channel 7 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x1484 |  | 5252 |  | Alarm channel 8 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x1485 |  | 5253 |  | Alarm channel 9 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x1486 |  | 5254 |  | Alarm channel 10 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x1487 |  | 5255 |  | Alarm channel 11 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x1488 |  | 5256 |  | Alarm channel 12 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x1489 |  | 5257 |  | Alarm channel 13 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x148A |  | 5258 |  | Alarm channel 14 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x148B |  | 5259 |  | Alarm channel 15 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x148C |  | 5260 |  | Alarm channel 16 trigger off delay | int16 | R/W | 1 | 0 ~ 60000（× 10mS） | 0
| 0x148D |  | 5261 |  | Energy Pulse Led Parameter Selection | word | R/W | 1 | 0: None 1: EP_IMP 2: EP_EXP 3: EQ-IMP 4: EQ_EXP |  |  | Xian
| 0x148E |  | 5262 |  | Last interval for max/min/mean parameters | int16 | R/W | 1 | From 1 to 15 | 1 |  | v6.33_PXE_251212
| 0x148F |  | 5263 |  | Wideband 400Hz mode | int16 | R/W | 1 |  | 0 |  | 1.00p00
Channel1 BACnet MS/TP settings
| 0x2100 |  | 8448 |  | BACnet MS/TP Meter address | uint16 | R/W | 1 | 0 - 127 | 1
| 0x2101 |  | 8449 |  | BACnet MS/TP Baud rate | uint16 | R/W | 1 | 2400 - 115200 | 19200
| 0x2102 |  | 8450 |  | BACnet MS/TP Maximum number of message frames | uint16 | R/W | 1 | 1 - 255 | 10
| 0x2103 |  | 8451 |  | BACnet MS/TP ID high byte | uint16 | R/W | 1 | 0 - 63(0x3F) | 0
| 0x2104 |  | 8452 |  | BACnet MS/TP ID low byte | uint16 | R/W | 1 | 1 - 65535(0xFFFF) | 1
| 0x2105 |  | 8452 |  | BACnet MS/TP Database Revision | uint16 | R | 1 | 0 - 65535(0xFFFF) | 0
Custom read settings area
| 0x6B00 |  | 27392 |  | The number of bytes have beeen set |  | R | 1 |  | Delta1: 46; Delta: 2 | Delta1: 46; Delta: 2
| 0x6B01 |  | 27393 |  | Parameter 1 Selection | uint16 | R/W | 1 |  | Delta1:0x3200; Delta2: 0x320D | Delta1:0x3200; Delta2: 0x320D
| 0x6B02 |  | 27394 |  | Parameter 2 Selection | uint16 | R/W | 1 |  | Delta1:0x3201; Delta2: 0x443A | Delta1:0x3201; Delta2: 0x443A
| 0x6B03 |  | 27395 |  | Parameter 3 Selection | uint16 | R/W | 1 |  | Delta1:0x3202; Delta2: 0 | Delta1:0x3202; Delta2: 0
| 0x6B04 |  | 27396 |  | Parameter 4 Selection | uint16 | R/W | 1 |  | Delta1:0x3203; Delta2: 0 | Delta1:0x3203; Delta2: 0
| 0x6B05 |  | 27397 |  | Parameter 5 Selection | uint16 | R/W | 1 |  | Delta1:0x3204; Delta2: 0 | Delta1:0x3204; Delta2: 0
| 0x6B06 |  | 27398 |  | Parameter 6 Selection | uint16 | R/W | 1 |  | Delta1:0x3205; Delta2: 0 | Delta1:0x3205; Delta2: 0
| 0x6B07 |  | 27399 |  | Parameter 7 Selection | uint16 | R/W | 1 |  | Delta1:0x3206; Delta2: 0 | Delta1:0x3206; Delta2: 0
| 0x6B08 |  | 27400 |  | Parameter 8 Selection | uint16 | R/W | 1 |  | Delta1:0x3207; Delta2: 0 | Delta1:0x3207; Delta2: 0
| 0x6B09 |  | 27401 |  | Parameter 9 Selection | uint16 | R/W | 1 |  | Delta1:0x3208; Delta2: 0 | Delta1:0x3208; Delta2: 0
| 0x6B0A |  | 27402 |  | Parameter 10 Selection | uint16 | R/W | 1 |  | Delta1:0x3209; Delta2: 0 | Delta1:0x3209; Delta2: 0
| 0x6B0B |  | 27403 |  | Parameter 11 Selection | uint16 | R/W | 1 |  | Delta1:0x320A; Delta2: 0 | Delta1:0x320A; Delta2: 0
| 0x6B0C |  | 27404 |  | Parameter 12 Selection | uint16 | R/W | 1 |  | Delta1:0x320B; Delta2: 0 | Delta1:0x320B; Delta2: 0
| 0x6B0D |  | 27405 |  | Parameter 13 Selection | uint16 | R/W | 1 |  | Delta1:0x320C; Delta2: 0 | Delta1:0x320C; Delta2: 0
| 0x6B0E |  | 27406 |  | Parameter 14 Selection | uint16 | R/W | 1 |  | Delta1:0x320D; Delta2: 0 | Delta1:0x320D; Delta2: 0
| 0x6B0F |  | 27407 |  | Parameter 15 Selection | uint16 | R/W | 1 |  | Delta1:0x320E; Delta2: 0 | Delta1:0x320E; Delta2: 0
| 0x6B10 |  | 27408 |  | Parameter 16 Selection | uint16 | R/W | 1 |  | Delta1:0x320F; Delta2: 0 | Delta1:0x320F; Delta2: 0
| 0x6B11 |  | 27409 |  | Parameter 17 Selection | uint16 | R/W | 1 |  | Delta1:0x3210; Delta2: 0 | Delta1:0x3210; Delta2: 0
| 0x6B12 |  | 27410 |  | Parameter 18 Selection | uint16 | R/W | 1 |  | Delta1:0x3211; Delta2: 0 | Delta1:0x3211; Delta2: 0
| 0x6B13 |  | 27411 |  | Parameter 19 Selection | uint16 | R/W | 1 |  | Delta1:0x3212; Delta2: 0 | Delta1:0x3212; Delta2: 0
| 0x6B14 |  | 27412 |  | Parameter 20 Selection | uint16 | R/W | 1 |  | Delta1:0x3213; Delta2: 0 | Delta1:0x3213; Delta2: 0
| 0x6B15 |  | 27413 |  | Parameter 21 Selection | uint16 | R/W | 1 |  | Delta1:0x3214; Delta2: 0 | Delta1:0x3214; Delta2: 0
| 0x6B16 |  | 27414 |  | Parameter 22 Selection | uint16 | R/W | 1 |  | Delta1:0x3215; Delta2: 0 | Delta1:0x3215; Delta2: 0
| 0x6B17 |  | 27415 |  | Parameter 23 Selection | uint16 | R/W | 1 |  | Delta1:0x3216; Delta2: 0 | Delta1:0x3216; Delta2: 0
| 0x6B18 |  | 27416 |  | Parameter 24 Selection | uint16 | R/W | 1 |  | Delta1:0x3217; Delta2: 0 | Delta1:0x3217; Delta2: 0
| 0x6B19 |  | 27417 |  | Parameter 25 Selection | uint16 | R/W | 1 |  | Delta1:0x3218; Delta2: 0 | Delta1:0x3218; Delta2: 0
| 0x6B1A |  | 27418 |  | Parameter 26 Selection | uint16 | R/W | 1 |  | Delta1:0x3219; Delta2: 0 | Delta1:0x3219; Delta2: 0
| 0x6B1B |  | 27419 |  | Parameter 27 Selection | uint16 | R/W | 1 |  | Delta1:0x321A; Delta2: 0 | Delta1:0x321A; Delta2: 0
| 0x6B1C |  | 27420 |  | Parameter 28 Selection | uint16 | R/W | 1 |  | Delta1:0x321B; Delta2: 0 | Delta1:0x321B; Delta2: 0
| 0x6B1D |  | 27421 |  | Parameter 29 Selection | uint16 | R/W | 1 |  | Delta1:0x321C; Delta2: 0 | Delta1:0x321C; Delta2: 0
| 0x6B1E |  | 27422 |  | Parameter 30 Selection | uint16 | R/W | 1 |  | Delta1:0x321D; Delta2: 0 | Delta1:0x321D; Delta2: 0
| 0x6B1F |  | 27423 |  | Parameter 31 Selection | uint16 | R/W | 1 |  | Delta1:0x405A; Delta2: 0 | Delta1:0x405A; Delta2: 0
| 0x6B20 |  | 27424 |  | Parameter 32 Selection | uint16 | R/W | 1 |  | Delta1:0x405B; Delta2: 0 | Delta1:0x405B; Delta2: 0
| 0x6B21 |  | 27425 |  | Parameter 33 Selection | uint16 | R/W | 1 |  | Delta1:0x405C; Delta2: 0 | Delta1:0x405C; Delta2: 0
| 0x6B22 |  | 27426 |  | Parameter 34 Selection | uint16 | R/W | 1 |  | Delta1:0x405D; Delta2: 0 | Delta1:0x405D; Delta2: 0
| 0x6B23 |  | 27427 |  | Parameter 35 Selection | uint16 | R/W | 1 |  | Delta1:0x405E; Delta2: 0 | Delta1:0x405E; Delta2: 0
| 0x6B24 |  | 27428 |  | Parameter 36 Selection | uint16 | R/W | 1 |  | Delta1:0x405F; Delta2: 0 | Delta1:0x405F; Delta2: 0
| 0x6B25 |  | 27429 |  | Parameter 37 Selection | uint16 | R/W | 1 |  | Delta1:0x4060; Delta2: 0 | Delta1:0x4060; Delta2: 0
| 0x6B26 |  | 27430 |  | Parameter 38 Selection | uint16 | R/W | 1 |  | Delta1:0x4061; Delta2: 0 | Delta1:0x4061; Delta2: 0
| 0x6B27 |  | 27431 |  | Parameter 39 Selection | uint16 | R/W | 1 |  | Delta1:0x4620; Delta2: 0 | Delta1:0x4620; Delta2: 0
| 0x6B28 |  | 27432 |  | Parameter 40 Selection | uint16 | R/W | 1 |  | Delta1:0x4621; Delta2: 0 | Delta1:0x4621; Delta2: 0
| 0x6B29 |  | 27433 |  | Parameter 41 Selection | uint16 | R/W | 1 |  | Delta1:0x4624; Delta2: 0 | Delta1:0x4624; Delta2: 0
| 0x6B2A |  | 27434 |  | Parameter 42 Selection | uint16 | R/W | 1 |  | Delta1:0x4625; Delta2: 0 | Delta1:0x4625; Delta2: 0
| 0x6B2B |  | 27435 |  | Parameter 43 Selection | uint16 | R/W | 1 |  | Delta1:0x4628; Delta2: 0 | Delta1:0x4628; Delta2: 0
| 0x6B2C |  | 27436 |  | Parameter 44 Selection | uint16 | R/W | 1 |  | Delta1:0x4629; Delta2: 0 | Delta1:0x4629; Delta2: 0
| 0x6B2D |  | 27437 |  | Parameter 45 Selection | uint16 | R/W | 1 |  | Delta1:0x4048; Delta2: 0 | Delta1:0x4048; Delta2: 0
| 0x6B2E |  | 27438 |  | Parameter 46 Selection | uint16 | R/W | 1 |  | Delta1:0x4049; Delta2: 0 | Delta1:0x4049; Delta2: 0
| 0x6B2F |  | 27439 |  | Parameter 47 Selection | uint16 | R/W | 1 |  | Delat: 0xF004 | Delat: 0xF004 | meter firmware version
| 0x6B30 |  | 27440 |  | Parameter 48 Selection | uint16 | R/W | 1 |  | Delat: 0xF005 | Delat: 0xF005
| 0x6B31 |  | 27441 |  | Parameter 49 Selection | uint16 | R/W | 1 |  | Delat: 0xF006 | Delat: 0xF006
| 0x6B32 |  | 27442 |  | Parameter 50 Selection | uint16 | R/W | 1 |  | Delat: 0xF007 | Delat: 0xF007
| 0x6B33 |  | 27443 |  | Parameter 51 Selection | uint16 | R/W | 1 |  | Delat: 0xF008 | Delat: 0xF008
| 0x6B34 |  | 27444 |  | Parameter 52 Selection | uint16 | R/W | 1 |  | Delat: 0xF024 | Delat: 0xF024 | web2 firmware version
| 0x6B35 |  | 27445 |  | Parameter 53 Selection | uint16 | R/W | 1 |  | Delat: 0xF025 | Delat: 0xF025
| 0x6B36 |  | 27446 |  | Parameter 54 Selection | uint16 | R/W | 1 |  | Delat: 0xF026 | Delat: 0xF026
| 0x6B37 |  | 27447 |  | Parameter 55 Selection | uint16 | R/W | 1 |  | Delat: 0xF027 | Delat: 0xF027
| 0x6B38 |  | 27448 |  | Parameter 56 Selection | uint16 | R/W | 1 |  | Delat: 0xF028 | Delat: 0xF028
| 0x6B39 |  | 27449 |  | Parameter 57 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B3A |  | 27450 |  | Parameter 58 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B3B |  | 27451 |  | Parameter 59 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B3C |  | 27452 |  | Parameter 60 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B3D |  | 27453 |  | Parameter 61 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B3E |  | 27454 |  | Parameter 61 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B3F |  | 27455 |  | Parameter 63 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B40 |  | 27456 |  | Parameter 64 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B41 |  | 27457 |  | Parameter 65 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B42 |  | 27458 |  | Parameter 66 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B43 |  | 27459 |  | Parameter 67 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B44 |  | 27460 |  | Parameter 68 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B45 |  | 27461 |  | Parameter 69 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B46 |  | 27462 |  | Parameter 70 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B47 |  | 27463 |  | Parameter 71 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B48 |  | 27464 |  | Parameter 72 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B49 |  | 27465 |  | Parameter 73 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B4A |  | 27466 |  | Parameter 74 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B4B |  | 27467 |  | Parameter 75 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B4C |  | 27468 |  | Parameter 76 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B4D |  | 27469 |  | Parameter 77 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B4E |  | 27470 |  | Parameter 78 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B4F |  | 27471 |  | Parameter 79 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B50 |  | 27472 |  | Parameter 80 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B51 |  | 27473 |  | Parameter 81 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B52 |  | 27474 |  | Parameter 82 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B53 |  | 27475 |  | Parameter 83 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B54 |  | 27476 |  | Parameter 84 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B55 |  | 27477 |  | Parameter 85 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B56 |  | 27478 |  | Parameter 86 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B57 |  | 27479 |  | Parameter 87 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B58 |  | 27480 |  | Parameter 88 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B59 |  | 27481 |  | Parameter 89 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B5A |  | 27482 |  | Parameter 90 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B5B |  | 27483 |  | Parameter 91 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B5C |  | 27484 |  | Parameter 92 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B5D |  | 27485 |  | Parameter 93 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B5E |  | 27486 |  | Parameter 94 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B5F |  | 27487 |  | Parameter 95 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B60 |  | 27488 |  | Parameter 96 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B61 |  | 27489 |  | Parameter 97 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B62 |  | 27490 |  | Parameter 98 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B63 |  | 27491 |  | Parameter 99 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B64 |  | 27492 |  | Parameter 100 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B65 |  | 27493 |  | Parameter 101 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B66 |  | 27494 |  | Parameter 102 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B67 |  | 27495 |  | Parameter 103 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B68 |  | 27496 |  | Parameter 104 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B69 |  | 27497 |  | Parameter 105 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B6A |  | 27498 |  | Parameter 106 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B6B |  | 27499 |  | Parameter 107 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B6C |  | 27500 |  | Parameter 108 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B6D |  | 27501 |  | Parameter 109 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B6E |  | 27502 |  | Parameter 110 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B6F |  | 27503 |  | Parameter 111 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B70 |  | 27504 |  | Parameter 112 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B71 |  | 27505 |  | Parameter 113 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B72 |  | 27506 |  | Parameter 114 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B73 |  | 27507 |  | Parameter 115 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B74 |  | 27508 |  | Parameter 116 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B75 |  | 27509 |  | Parameter 117 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B76 |  | 27510 |  | Parameter 118 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B77 |  | 27511 |  | Parameter 119 Selection | uint16 | R/W | 1 |  |  | 0
| 0x6B78 |  | 27512 |  | Parameter 120 Selection | uint16 | R/W | 1 |  |  | 0
User defined reading area
| 0x6A00 |  | 27136 |  | Parameter 1 reading | uint16 | R | 1 |  |  | 0
| 0x6A01 |  | 27137 |  | Parameter 2 reading | uint16 | R | 1 |  |  | 0
| 0x6A02 |  | 27138 |  | Parameter 3 reading | uint16 | R | 1 |  |  | 0
| 0x6A03 |  | 27139 |  | Parameter 4 reading | uint16 | R | 1 |  |  | 0
| 0x6A04 |  | 27140 |  | Parameter 5 reading | uint16 | R | 1 |  |  | 0
| 0x6A05 |  | 27141 |  | Parameter 6 reading | uint16 | R | 1 |  |  | 0
| 0x6A06 |  | 27142 |  | Parameter 7 reading | uint16 | R | 1 |  |  | 0
| 0x6A07 |  | 27143 |  | Parameter 8 reading | uint16 | R | 1 |  |  | 0
| 0x6A08 |  | 27144 |  | Parameter 9 reading | uint16 | R | 1 |  |  | 0
| 0x6A09 |  | 27145 |  | Parameter 10 reading | uint16 | R | 1 |  |  | 0
| 0x6A0A |  | 27146 |  | Parameter 11 reading | uint16 | R | 1 |  |  | 0
| 0x6A0B |  | 27147 |  | Parameter 12 reading | uint16 | R | 1 |  |  | 0
| 0x6A0C |  | 27148 |  | Parameter 13 reading | uint16 | R | 1 |  |  | 0
| 0x6A0D |  | 27149 |  | Parameter 14 reading | uint16 | R | 1 |  |  | 0
| 0x6A0E |  | 27150 |  | Parameter 15 reading | uint16 | R | 1 |  |  | 0
| 0x6A0F |  | 27151 |  | Parameter 16 reading | uint16 | R | 1 |  |  | 0
| 0x6A10 |  | 27152 |  | Parameter 17 reading | uint16 | R | 1 |  |  | 0
| 0x6A11 |  | 27153 |  | Parameter 18 reading | uint16 | R | 1 |  |  | 0
| 0x6A12 |  | 27154 |  | Parameter 19 reading | uint16 | R | 1 |  |  | 0
| 0x6A13 |  | 27155 |  | Parameter 20 reading | uint16 | R | 1 |  |  | 0
| 0x6A14 |  | 27156 |  | Parameter 21 reading | uint16 | R | 1 |  |  | 0
| 0x6A15 |  | 27157 |  | Parameter 22 reading | uint16 | R | 1 |  |  | 0
| 0x6A16 |  | 27158 |  | Parameter 23 reading | uint16 | R | 1 |  |  | 0
| 0x6A17 |  | 27159 |  | Parameter 24 reading | uint16 | R | 1 |  |  | 0
| 0x6A18 |  | 27160 |  | Parameter 25 reading | uint16 | R | 1 |  |  | 0
| 0x6A19 |  | 27161 |  | Parameter 26 reading | uint16 | R | 1 |  |  | 0
| 0x6A1A |  | 27162 |  | Parameter 27 reading | uint16 | R | 1 |  |  | 0
| 0x6A1B |  | 27163 |  | Parameter 28 reading | uint16 | R | 1 |  |  | 0
| 0x6A1C |  | 27164 |  | Parameter 29 reading | uint16 | R | 1 |  |  | 0
| 0x6A1D |  | 27165 |  | Parameter 30 reading | uint16 | R | 1 |  |  | 0
| 0x6A1E |  | 27166 |  | Parameter 31 reading | uint16 | R | 1 |  |  | 0
| 0x6A1F |  | 27167 |  | Parameter 32 reading | uint16 | R | 1 |  |  | 0
| 0x6A20 |  | 27168 |  | Parameter 33 reading | uint16 | R | 1 |  |  | 0
| 0x6A21 |  | 27169 |  | Parameter 34 reading | uint16 | R | 1 |  |  | 0
| 0x6A22 |  | 27170 |  | Parameter 35 reading | uint16 | R | 1 |  |  | 0
| 0x6A23 |  | 27171 |  | Parameter 36 reading | uint16 | R | 1 |  |  | 0
| 0x6A24 |  | 27172 |  | Parameter 37 reading | uint16 | R | 1 |  |  | 0
| 0x6A25 |  | 27173 |  | Parameter 38 reading | uint16 | R | 1 |  |  | 0
| 0x6A26 |  | 27174 |  | Parameter 39 reading | uint16 | R | 1 |  |  | 0
| 0x6A27 |  | 27175 |  | Parameter 40 reading | uint16 | R | 1 |  |  | 0
| 0x6A28 |  | 27176 |  | Parameter 41 reading | uint16 | R | 1 |  |  | 0
| 0x6A29 |  | 27177 |  | Parameter 42 reading | uint16 | R | 1 |  |  | 0
| 0x6A2A |  | 27178 |  | Parameter 43 reading | uint16 | R | 1 |  |  | 0
| 0x6A2B |  | 27179 |  | Parameter 44 reading | uint16 | R | 1 |  |  | 0
| 0x6A2C |  | 27180 |  | Parameter 45 reading | uint16 | R | 1 |  |  | 0
| 0x6A2D |  | 27181 |  | Parameter 46 reading | uint16 | R | 1 |  |  | 0
| 0x6A2E |  | 27182 |  | Parameter 47 reading | uint16 | R | 1 |  |  | 0
| 0x6A2F |  | 27183 |  | Parameter 48 reading | uint16 | R | 1 |  |  | 0
| 0x6A30 |  | 27184 |  | Parameter 49 reading | uint16 | R | 1 |  |  | 0
| 0x6A31 |  | 27185 |  | Parameter 50 reading | uint16 | R | 1 |  |  | 0
| 0x6A32 |  | 27186 |  | Parameter 51 reading | uint16 | R | 1 |  |  | 0
| 0x6A33 |  | 27187 |  | Parameter 52 reading | uint16 | R | 1 |  |  | 0
| 0x6A34 |  | 27188 |  | Parameter 53 reading | uint16 | R | 1 |  |  | 0
| 0x6A35 |  | 27189 |  | Parameter 54 reading | uint16 | R | 1 |  |  | 0
| 0x6A36 |  | 27190 |  | Parameter 55 reading | uint16 | R | 1 |  |  | 0
| 0x6A37 |  | 27191 |  | Parameter 56 reading | uint16 | R | 1 |  |  | 0
| 0x6A38 |  | 27192 |  | Parameter 57 reading | uint16 | R | 1 |  |  | 0
| 0x6A39 |  | 27193 |  | Parameter 58 reading | uint16 | R | 1 |  |  | 0
| 0x6A3A |  | 27194 |  | Parameter 59 reading | uint16 | R | 1 |  |  | 0
| 0x6A3B |  | 27195 |  | Parameter 60 reading | uint16 | R | 1 |  |  | 0
| 0x6A3C |  | 27196 |  | Parameter 61 reading | uint16 | R | 1 |  |  | 0
| 0x6A3D |  | 27197 |  | Parameter 62 reading | uint16 | R | 1 |  |  | 0
| 0x6A3E |  | 27198 |  | Parameter 63 reading | uint16 | R | 1 |  |  | 0
| 0x6A3F |  | 27199 |  | Parameter 64 reading | uint16 | R | 1 |  |  | 0
| 0x6A40 |  | 27200 |  | Parameter 65 reading | uint16 | R | 1 |  |  | 0
| 0x6A41 |  | 27201 |  | Parameter 66 reading | uint16 | R | 1 |  |  | 0
| 0x6A42 |  | 27202 |  | Parameter 67 reading | uint16 | R | 1 |  |  | 0
| 0x6A43 |  | 27203 |  | Parameter 68 reading | uint16 | R | 1 |  |  | 0
| 0x6A44 |  | 27204 |  | Parameter 69 reading | uint16 | R | 1 |  |  | 0
| 0x6A45 |  | 27205 |  | Parameter 70 reading | uint16 | R | 1 |  |  | 0
| 0x6A46 |  | 27206 |  | Parameter 71 reading | uint16 | R | 1 |  |  | 0
| 0x6A47 |  | 27207 |  | Parameter 71 reading | uint16 | R | 1 |  |  | 0
| 0x6A48 |  | 27208 |  | Parameter 73 reading | uint16 | R | 1 |  |  | 0
| 0x6A49 |  | 27209 |  | Parameter 74 reading | uint16 | R | 1 |  |  | 0
| 0x6A4A |  | 27210 |  | Parameter 75 reading | uint16 | R | 1 |  |  | 0
| 0x6A4B |  | 27211 |  | Parameter 76 reading | uint16 | R | 1 |  |  | 0
| 0x6A4C |  | 27212 |  | Parameter 77 reading | uint16 | R | 1 |  |  | 0
| 0x6A4D |  | 27213 |  | Parameter 78 reading | uint16 | R | 1 |  |  | 0
| 0x6A4E |  | 27214 |  | Parameter 79 reading | uint16 | R | 1 |  |  | 0
| 0x6A4F |  | 27215 |  | Parameter 80 reading | uint16 | R | 1 |  |  | 0
| 0x6A50 |  | 27216 |  | Parameter 81 reading | uint16 | R | 1 |  |  | 0
| 0x6A51 |  | 27217 |  | Parameter 82 reading | uint16 | R | 1 |  |  | 0
| 0x6A52 |  | 27218 |  | Parameter 83 reading | uint16 | R | 1 |  |  | 0
| 0x6A53 |  | 27219 |  | Parameter 84 reading | uint16 | R | 1 |  |  | 0
| 0x6A54 |  | 27220 |  | Parameter 85 reading | uint16 | R | 1 |  |  | 0
| 0x6A55 |  | 27221 |  | Parameter 86 reading | uint16 | R | 1 |  |  | 0
| 0x6A56 |  | 27222 |  | Parameter 87 reading | uint16 | R | 1 |  |  | 0
| 0x6A57 |  | 27223 |  | Parameter 88 reading | uint16 | R | 1 |  |  | 0
| 0x6A58 |  | 27224 |  | Parameter 89 reading | uint16 | R | 1 |  |  | 0
| 0x6A59 |  | 27225 |  | Parameter 90 reading | uint16 | R | 1 |  |  | 0
| 0x6A5A |  | 27226 |  | Parameter 91 reading | uint16 | R | 1 |  |  | 0
| 0x6A5B |  | 27227 |  | Parameter 92 reading | uint16 | R | 1 |  |  | 0
| 0x6A5C |  | 27228 |  | Parameter 93 reading | uint16 | R | 1 |  |  | 0
| 0x6A5D |  | 27229 |  | Parameter 94 reading | uint16 | R | 1 |  |  | 0
| 0x6A5E |  | 27230 |  | Parameter 95 reading | uint16 | R | 1 |  |  | 0
| 0x6A5F |  | 27231 |  | Parameter 96 reading | uint16 | R | 1 |  |  | 0
| 0x6A60 |  | 27232 |  | Parameter 97 reading | uint16 | R | 1 |  |  | 0
| 0x6A61 |  | 27233 |  | Parameter 98 reading | uint16 | R | 1 |  |  | 0
| 0x6A62 |  | 27234 |  | Parameter 99 reading | uint16 | R | 1 |  |  | 0
| 0x6A63 |  | 27235 |  | Parameter 100 reading | uint16 | R | 1 |  |  | 0
| 0x6A64 |  | 27236 |  | Parameter 101 reading | uint16 | R | 1 |  |  | 0
| 0x6A65 |  | 27237 |  | Parameter 102 reading | uint16 | R | 1 |  |  | 0
| 0x6A66 |  | 27238 |  | Parameter 103 reading | uint16 | R | 1 |  |  | 0
| 0x6A67 |  | 27239 |  | Parameter 104 reading | uint16 | R | 1 |  |  | 0
| 0x6A68 |  | 27240 |  | Parameter 105 reading | uint16 | R | 1 |  |  | 0
| 0x6A69 |  | 27241 |  | Parameter 106 reading | uint16 | R | 1 |  |  | 0
| 0x6A6A |  | 27242 |  | Parameter 107 reading | uint16 | R | 1 |  |  | 0
| 0x6A6B |  | 27243 |  | Parameter 108 reading | uint16 | R | 1 |  |  | 0
| 0x6A6C |  | 27244 |  | Parameter 109 reading | uint16 | R | 1 |  |  | 0
| 0x6A6D |  | 27245 |  | Parameter 110 reading | uint16 | R | 1 |  |  | 0
| 0x6A6E |  | 27246 |  | Parameter 111 reading | uint16 | R | 1 |  |  | 0
| 0x6A6F |  | 27247 |  | Parameter 112 reading | uint16 | R | 1 |  |  | 0
| 0x6A70 |  | 27248 |  | Parameter 113 reading | uint16 | R | 1 |  |  | 0
| 0x6A71 |  | 27249 |  | Parameter 114 reading | uint16 | R | 1 |  |  | 0
| 0x6A72 |  | 27250 |  | Parameter 115 reading | uint16 | R | 1 |  |  | 0
| 0x6A73 |  | 27251 |  | Parameter 116 reading | uint16 | R | 1 |  |  | 0
| 0x6A74 |  | 27252 |  | Parameter 117 reading | uint16 | R | 1 |  |  | 0
| 0x6A75 |  | 27253 |  | Parameter 118 reading | uint16 | R | 1 |  |  | 0
| 0x6A76 |  | 27254 |  | Parameter 119 reading | uint16 | R | 1 |  |  | 0
| 0x6A77 |  | 27255 |  | Parameter 120 reading | uint16 | R | 1 |  |  | 0
| 0xF083 |  | 61571 |  | VFD enable | uint16 | RW |  | 0 |  |  | v6.31_VFD_250415 | Overlapped with DELTA RO parameters; but they belongs to different model, so it is not an issue
Additonal 6A command | 0xF003 |  | 61443 |  | Restart IO module | uint16 | W | 1 | 1：module11; 2: module12; 3: module21; 4: module22; 5: module31; 6: module32. |  |  | v6.26_240405
| 0xF081 |  | 61569 |  | MC type (measurement canada) | uint16 | RW |  | 0: disable; 1:enable; 2: S type; 3: xx |  |  | v6.26
| 0xF082 |  | 61570 |  | DELTA meter number | uint16 | RW |  | 0 |  |  | v6.30_DELTA_250404

## Communication Module
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
AXM-NET/WEB/WEB2 settings
| 0x0100 |  | 256 |  | Connection status; write by NET/WEB/WEB2 module | word | R/W | 1
| 0x0101 |  | 257 |  | state sigh | word | R/W | 1
| 0x0102 |  | 258 |  | enable DHCP | word | R/W | 1 | 0: Manual 1: Enable DHCP |  | 0: II 1: PXM3000
| 0x0103 |  | 259 |  | IP address Byte 1 (high) and Byte 2 (low) | word | R/W | 1
| 0x0104 |  | 260 |  | IP address Byte 3 (high) and Byte 4 (low) | word | R/W | 1
| 0x0105 |  | 261 |  | Subnet mask Byte 1 (high) and Byte 2 (low) | word | R/W | 1
| 0x0106 |  | 262 |  | Subnet mask Byte 3 (high) and Byte 4 (low) | word | R/W | 1
| 0x0107 |  | 263 |  | Gateway IP address Byte 1 (high) and Byte 2 (low) | word | R/W | 1
| 0x0108 |  | 264 |  | Gateway IP address Byte 3 (high) and Byte 4 (low) | word | R/W | 1
| 0x0109 |  | 265 |  | DNS Server 1 IP address Byte 1 (high) and Byte 2 (low) | word | R/W | 1
| 0x010A |  | 266 |  | DNS Server 1 IP address Byte 3 (high) and Byte 4 (low) | word | R/W | 1
| 0x010B |  | 267 |  | DNS Server 2 IP address Byte 1 (high) and Byte 2 (low) | word | R/W | 1
| 0x010C |  | 268 |  | DNS Server 2 IP address Byte 3 (high) and Byte 4 (low) | word | R/W | 1
| 0x010D |  | 269 |  | Modbus Tcp port | word | R/W | 1 | 2000-5999
| 0x010E |  | 270 |  | Https port | word | R/W | 1
| 0x010F |  | 271 |  | enable DHCP，eth2 | word | R/W | 1 | 0: Manual 1: Enable DHCP |  | 0: II 1: PXM3000
| 0x0110 |  | 272 |  | IP address Byte 1 (high) and Byte 2 (low)，eth2 | word | R/W | 1
| 0x0111 |  | 273 |  | IP address Byte 3 (high) and Byte 4 (low)，eth2 | word | R/W | 1
| 0x0112 |  | 274 |  | Subnet mask Byte 1 (high) and Byte 2 (low)，eth2 | word | R/W | 1
| 0x0113 |  | 275 |  | Subnet mask Byte 3 (high) and Byte 4 (low)，eth2 | word | R/W | 1
| 0x0114 |  | 276 |  | Gateway IP address Byte 1 (high) and Byte 2 (low)，eth2 | word | R/W | 1
| 0x0115 |  | 277 |  | Gateway IP address Byte 3 (high) and Byte 4 (low)，eth2 | word | R/W | 1
| 0x0116 |  | 278 |  | Ethernet Port2 Connection status; write by NET/WEB/WEB2 module | word | R/W | 1
Device Description | 0x0200 | 0x020E | 512 | 526 | device description | word | R/W | 15
32 Virtual Relays | 0x0216 | 0x0235 | 534 | 565 | DNP3 Virtual Relay | word | R/W | 32
32 Virtual Inputs | 0x0240 | 0x025F | 576 | 607 | DNP3 Virtual Input | word | R/W | 32
WiFi IP | 0x02B0 | 0x02B1 | 688 | 689 | WIFI module WIFI IP address | word | R/W | 2
AXM-WEB2 ETH2 IP | 0x02B2 | 0x02B3 | 690 | 691 | AXM-WEB2 Ethernet2 IP address | word | R/W | 2
Network module reset | 0x0300 | 0x0303 | 768 | 771 | Reset network module | word | R/W | 4
AXM_BACnet
| 0x0400 |  | 1024 |  | enable DHCP | word | R/W | 1
| 0x0401 |  | 1025 |  | IP address Byte 1 (high) and Byte 2 (low) | word | R/W | 1
| 0x0402 |  | 1026 |  | IP address Byte 3 (high) and Byte 4 (low) | word | R/W | 1
| 0x0403 |  | 1027 |  | Subnet mask Byte 1 (high) and Byte 2 (low) | word | R/W | 1
| 0x0404 |  | 1028 |  | Subnet mask Byte 3 (high) and Byte 4 (low) | word | R/W | 1
| 0x0405 |  | 1029 |  | Gateway IP address Byte 1 (high) and Byte 2 (low) | word | R/W | 1
| 0x0406 |  | 1030 |  | Gateway IP address Byte 3 (high) and Byte 4 (low) | word | R/W | 1
| 0x0407 |  | 1031 |  | DNS Server 1 IP address Byte 1 (high) and Byte 2 (low) | word | R/W | 1
| 0x0408 |  | 1032 |  | DNS Server 1 IP address Byte 3 (high) and Byte 4 (low) | word | R/W | 1
| 0x0409 |  | 1033 |  | DNS Server 2 IP address Byte 1 (high) and Byte 2 (low) | word | R/W | 1
| 0x040A |  | 1034 |  | DNS Server 2 IP address Byte 3 (high) and Byte 4 (low) | word | R/W | 1
| 0x040B |  | 1035 |  | BACnet/IP Port | word | R/W | 1
| 0x040C |  | 1036 |  | MS/TP node address（MS/TP） | word | R/W | 1 |  | MAC address
| 0x040D |  | 1037 |  | BACnet Baud rate （MS/TP） | word | R/W | 1
| 0x040E |  | 1038 |  | Max info frames（MS/TP） | word | R/W | 1
| 0x040F |  | 1039 |  | BACnet module reset | word | R/W | 1
| 0x0410 |  | 1040 |  | BACnet endian selection （Keep temporaryly address) | word | R/W | 1
| 0x0411 |  | 1041 |  | BACnet MAC address first byte BACnet MAC address second byte | word | R | 1
| 0x0412 |  | 1042 |  | BACnet MAC address third byte BACnet MAC address fourth byte | word | R | 1
| 0x0413 |  | 1043 |  | BACnet MAC address 5th byte BACnet MAC address 6th byte | word | R | 1
[5 empty] | Reserve |  |  | 12
MESH network address
| 0x4F00 |  | 20224 |  | Restore MESH module command | uint16 | R | 1 |  | 0: no restore; 0x0A: restore
| 0x4F01 |  | 20225 |  | Restore MESH factory default command | uint16 | R | 1 |  | 0: no restore; 0x0A: restore
| 0x4F02 |  | 20226 |  | MESH module status | uint16 | R | 1 |  | 0: abnormal or not continuous; 0xaa: normal and continuous
| 0x4F03 | 0x4F0A | 20227 | 20234 | MESH module MAC address | uint16 | R | 8 |  | 16 ASCII codes（from high byte to low byte）
| 0x4F0B | 0x4F14 | 20235 | 20244 | MESH module ID | uint16 | R | 10 |  | 20 ASCII codes（from high byte to low byte）

## Real Time Parameters
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value | Release version
Eaton customized area
| 0x1FFE | 0x1FFF | 8190 | 8191 | Eaton Product ID | uint32 | R | 2 |  | 0x200E
| 0x2000 | 0x2000 | 8192 | 8192 | Eaton Status | uint16 | R | 1
| 0x2001 | 0x2001 | 8193 | 8193 | Eaton Alarm Status | uint16 | R | 1
| 0x2002 | 0x2003 | 8194 | 8195 | I a RMS | float32 | R | 2
| 0x2004 | 0x2005 | 8196 | 8197 | I b RMS | float32 | R | 2
| 0x2006 | 0x2007 | 8198 | 8199 | I c RMS | float32 | R | 2
| 0x2008 | 0x2009 | 8200 | 8201 | I n RMS | float32 | R | 2
| 0x200A | 0x200B | 8202 | 8203 | I average RMS | float32 | R | 2
| 0x200C | 0x200D | 8204 | 8205 | Uab RMS | float32 | R | 2
| 0x200E | 0x200F | 8206 | 8207 | Ubc RMS | float32 | R | 2
| 0x2010 | 0x2011 | 8208 | 8209 | Uca RMS | float32 | R | 2
| 0x2012 | 0x2013 | 8210 | 8211 | U LL average RMS | float32 | R | 2
| 0x2014 | 0x2015 | 8212 | 8213 | Ua RMS | float32 | R | 2
| 0x2016 | 0x2017 | 8214 | 8215 | Ub RMS | float32 | R | 2
| 0x2018 | 0x2019 | 8216 | 8217 | Uc RMS | float32 | R | 2
| 0x201A | 0x201B | 8218 | 8219 | U LN average RMS | float32 | R | 2
| 0x201C | 0x201D | 8220 | 8221 | P | float32 | R | 2
| 0x201E | 0x201F | 8222 | 8223 | S | float32 | R | 2
| 0x2020 | 0x2021 | 8224 | 8225 | PF | float32 | R | 2
| 0x2022 | 0x2023 | 8226 | 8227 | Freq | float32 | R | 2
| 0x2024 | 0x2025 | 8228 | 8229 | Pa | float32 | R | 2
| 0x2026 | 0x2027 | 8230 | 8231 | Pb | float32 | R | 2
| 0x2028 | 0x2029 | 8232 | 8233 | Pc | float32 | R | 2
| 0x202A | 0x202B | 8234 | 8235 | Sa | float32 | R | 2
| 0x202C | 0x202D | 8236 | 8237 | Sb | float32 | R | 2
| 0x202E | 0x202F | 8238 | 8239 | Sc | float32 | R | 2
| 0x2030 | 0x2031 | 8240 | 8241 | PFa | float32 | R | 2
| 0x2032 | 0x2033 | 8242 | 8243 | PFb | float32 | R | 2
| 0x2034 | 0x2035 | 8244 | 8245 | PFc | float32 | R | 2
| 0x2036 | 0x2036 | 8246 | 8246 | Primary/Secondary | uint16 | R | 1 | Primary : 2 Secondary : 0
| 0x2037 | 0x2038 | 8247 | 8248 | Ep IMP | int32 | R | 2
| 0x2039 | 0x2039 | 8249 | 8249 | Primary/Secondary | uint16 | R | 1 | Primary : 2 Secondary : 0
| 0x203A | 0x203B | 8250 | 8251 | EP EXP | int32 | R | 2
| 0x203C | 0x203C | 8252 | 8252 | Primary/Secondary | uint16 | R | 1 | Primary : 2 Secondary : 0
| 0x203D | 0x203E | 8253 | 8254 | EP Total | int32 | R | 2
Real time basic parameters（100ms)
| 0x3000 | 0x3001 | 12288 | 12289 | Freq_rms | float32 | R | 2
| 0x3002 | 0x3003 | 12290 | 12291 | Ua_rms | float32 | R | 2
| 0x3004 | 0x3005 | 12292 | 12293 | Ub_rms | float32 | R | 2
| 0x3006 | 0x3007 | 12294 | 12295 | Uc_rms | float32 | R | 2
| 0x3008 | 0x3009 | 12296 | 12297 | Uvag_rms | float32 | R | 2
| 0x300A | 0x300B | 12298 | 12299 | Uab_rms | float32 | R | 2
| 0x300C | 0x300D | 12300 | 12301 | Ubc_rms | float32 | R | 2
| 0x300E | 0x300F | 12302 | 12303 | Uca_rms | float32 | R | 2
| 0x3010 | 0x3011 | 12304 | 12305 | Ulag_rms | float32 | R | 2
| 0x3012 | 0x3013 | 12306 | 12307 | Ia_rms | float32 | R | 2
| 0x3014 | 0x3015 | 12308 | 12309 | Ib_rms | float32 | R | 2
| 0x3016 | 0x3017 | 12310 | 12311 | Ic_rms | float32 | R | 2
| 0x3018 | 0x3019 | 12312 | 12313 | Ivag_rms | float32 | R | 2
| 0x301A | 0x301B | 12314 | 12315 | In_rms | float32 | R | 2
| 0x301C | 0x301D | 12316 | 12317 | Pa_rms | float32 | R | 2
| 0x301E | 0x301F | 12318 | 12319 | Pb_rms | float32 | R | 2
| 0x3020 | 0x3021 | 12320 | 12321 | Pc_rms | float32 | R | 2
| 0x3022 | 0x3023 | 12322 | 12323 | P_rms | float32 | R | 2
| 0x3024 | 0x3025 | 12324 | 12325 | Qa_rms | float32 | R | 2
| 0x3026 | 0x3027 | 12326 | 12327 | Qb_rms | float32 | R | 2
| 0x3028 | 0x3029 | 12328 | 12329 | Qc_rms | float32 | R | 2
| 0x302A | 0x302B | 12330 | 12331 | Q_rms | float32 | R | 2
| 0x302C | 0x302D | 12332 | 12333 | Sa_rms | float32 | R | 2
| 0x302E | 0x302F | 12334 | 12335 | Sb_rms | float32 | R | 2
| 0x3030 | 0x3031 | 12336 | 12337 | Sc_rms | float32 | R | 2
| 0x3032 | 0x3033 | 12338 | 12339 | S_rms | float32 | R | 2
| 0x3034 | 0x3035 | 12340 | 12341 | PFa_rms | float32 | R | 2
| 0x3036 | 0x3037 | 12342 | 12343 | PFb_rms | float32 | R | 2
| 0x3038 | 0x3039 | 12344 | 12345 | PFc_rms | float32 | R | 2
| 0x303A | 0x303B | 12346 | 12347 | PF_rms | float32 | R | 2
| 0x303C | 0x303D | 12348 | 12349 | AI1 value， fast read | float32 | R | 2
| 0x303E | 0x303F | 12350 | 12351 | AI2 value， fast read | float32 | R | 2
| 0x3040 | 0x3041 | 12352 | 12353 | AI3 value， fast read | float32 | R | 2
| 0x3042 | 0x3043 | 12354 | 12355 | AI4 value， fast read | float32 | R | 2
| 0x3044 | 0x3045 | 12356 | 12357 | Displacement Power factor, Phase A | float32 | R | 2 |  |  |  | v6.32_250627; v6.30_PXE_250627
| 0x3046 | 0x3047 | 12358 | 12359 | Displacement Power factor, Phase B | float32 | R | 2
| 0x3048 | 0x3049 | 12360 | 12361 | Displacement Power factor, Phase C | float32 | R | 2
| 0x304A | 0x304B | 12362 | 12363 | Predictive Demand P | float32 | R | 2 |  |  |  | v6.32_250627; v6.30_PXE_250627
| 0x304C | 0x304D | 12364 | 12365 | Predictive Demand Q | float32 | R | 2
| 0x304E | 0x304F | 12366 | 12367 | Predictive Demand S | float32 | R | 2
| 0x3050 | 0x3051 | 12368 | 12369 | P Max, Phase A - Last Interval | float32 | R | 2 |  |  |  | v6.33_PXE_251212
| 0x3052 | 0x3053 | 12370 | 12371 | P Max, Phase B - Last Interval | float32 | R | 2
| 0x3054 | 0x3055 | 12372 | 12373 | P Max, Phase C - Last Interval | float32 | R | 2
| 0x3056 | 0x3057 | 12374 | 12375 | P Max, Total - Last Interval | float32 | R | 2
| 0x3058 | 0x3059 | 12376 | 12377 | P Min, Phase A - Last Interval | float32 | R | 2
| 0x305A | 0x305B | 12378 | 12379 | P Min, Phase B - Last Interval | float32 | R | 2
| 0x305C | 0x305D | 12380 | 12381 | P Min, Phase C - Last Interval | float32 | R | 2
| 0x305E | 0x305F | 12382 | 12383 | P Min, Total - Last Interval | float32 | R | 2
| 0x3060 | 0x3061 | 12384 | 12385 | P Mean, Phase A - Last Interval | float32 | R | 2
| 0x3062 | 0x3063 | 12386 | 12387 | P Mean, Phase B - Last Interval | float32 | R | 2
| 0x3064 | 0x3065 | 12388 | 12389 | P Mean, Phase C - Last Interval | float32 | R | 2
| 0x3066 | 0x3067 | 12390 | 12391 | P Mean, Total - Last Interval | float32 | R | 2
| 0x3068 | 0x3069 | 12392 | 12393 | Q Max, Phase A - Last Interval | float32 | R | 2
| 0x306A | 0x306B | 12394 | 12395 | Q Max, Phase B - Last Interval | float32 | R | 2
| 0x306C | 0x306D | 12396 | 12397 | Q Max, Phase C - Last Interval | float32 | R | 2
| 0x306E | 0x306F | 12398 | 12399 | Q Max, Total - Last Interval | float32 | R | 2
| 0x3070 | 0x3071 | 12400 | 12401 | Q Min, Phase A - Last Interval | float32 | R | 2
| 0x3072 | 0x3073 | 12402 | 12403 | Q Min, Phase B - Last Interval | float32 | R | 2
| 0x3074 | 0x3075 | 12404 | 12405 | Q Min, Phase C - Last Interval | float32 | R | 2
| 0x3076 | 0x3077 | 12406 | 12407 | Q Min, Total - Last Interval | float32 | R | 2
| 0x3078 | 0x3079 | 12408 | 12409 | Q Mean, Phase A - Last Interval | float32 | R | 2
| 0x307A | 0x307B | 12410 | 12411 | Q Mean, Phase B - Last Interval | float32 | R | 2
| 0x307C | 0x307D | 12412 | 12413 | Q Mean, Phase C - Last Interval | float32 | R | 2
| 0x307E | 0x307F | 12414 | 12415 | Q Mean, Total - Last Interval | float32 | R | 2
| 0x3080 | 0x3081 | 12416 | 12417 | S Max, Phase A - Last Interval | float32 | R | 2
| 0x3082 | 0x3083 | 12418 | 12419 | S Max, Phase B - Last Interval | float32 | R | 2
| 0x3084 | 0x3085 | 12420 | 12421 | S Max, Phase C - Last Interval | float32 | R | 2
| 0x3086 | 0x3087 | 12422 | 12423 | S Max, Total - Last Interval | float32 | R | 2
| 0x3088 | 0x3089 | 12424 | 12425 | S Min, Phase A - Last Interval | float32 | R | 2
| 0x308A | 0x308B | 12426 | 12427 | S Min, Phase B - Last Interval | float32 | R | 2
| 0x308C | 0x308D | 12428 | 12429 | S Min, Phase C - Last Interval | float32 | R | 2
| 0x308E | 0x308F | 12430 | 12431 | S Min, Total - Last Interval | float32 | R | 2
| 0x3090 | 0x3091 | 12432 | 12433 | S Mean, Phase A - Last Interval | float32 | R | 2
| 0x3092 | 0x3093 | 12434 | 12435 | S Mean, Phase B - Last Interval | float32 | R | 2
| 0x3094 | 0x3095 | 12436 | 12437 | S Mean, Phase C - Last Interval | float32 | R | 2
| 0x3096 | 0x3097 | 12438 | 12439 | S Mean, Total - Last Interval | float32 | R | 2
| 0x3098 | 0x3099 | 12440 | 12441 | I Max, Phase A - Last Interval | float32 | R | 2
| 0x309A | 0x309B | 12442 | 12443 | I Max, Phase B - Last Interval | float32 | R | 2
| 0x309C | 0x309D | 12444 | 12445 | I Max, Phase C - Last Interval | float32 | R | 2
| 0x309E | 0x309F | 12446 | 12447 | I Max, Phase N - Last Interval | float32 | R | 2
| 0x30A0 | 0x30A1 | 12448 | 12449 | I Max, average - Last Interval | float32 | R | 2
| 0x30A2 | 0x30A3 | 12450 | 12451 | I Min, Phase A - Last Interval | float32 | R | 2
| 0x30A4 | 0x30A5 | 12452 | 12453 | I Min, Phase B - Last Interval | float32 | R | 2
| 0x30A6 | 0x30A7 | 12454 | 12455 | I Min, Phase C - Last Interval | float32 | R | 2
| 0x30A8 | 0x30A9 | 12456 | 12457 | I Min, Phase N - Last Interval | float32 | R | 2
| 0x30AA | 0x30AB | 12458 | 12459 | I Min, average - Last Interval | float32 | R | 2
| 0x30AC | 0x30AD | 12460 | 12461 | I Mean, Phase A - Last Interval | float32 | R | 2
| 0x30AE | 0x30AF | 12462 | 12463 | I Mean, Phase B - Last Interval | float32 | R | 2
| 0x30B0 | 0x30B1 | 12464 | 12465 | I Mean, Phase C - Last Interval | float32 | R | 2
| 0x30B2 | 0x30B3 | 12466 | 12467 | I Mean, Phase N - Last Interval | float32 | R | 2
| 0x30B4 | 0x30B5 | 12468 | 12469 | I Mean, average - Last Interval | float32 | R | 2
| 0x30B6 | 0x30B7 | 12470 | 12471 | V Max, Phase A - Last Interval | float32 | R | 2
| 0x30B8 | 0x30B9 | 12472 | 12473 | V Max, Phase B - Last Interval | float32 | R | 2
| 0x30BA | 0x30BB | 12474 | 12475 | V Max, Phase C - Last Interval | float32 | R | 2
| 0x30BC | 0x30BD | 12476 | 12477 | V Max, Phase AB - Last Interval | float32 | R | 2
| 0x30BE | 0x30BF | 12478 | 12479 | V Max, Phase BC - Last Interval | float32 | R | 2
| 0x30C0 | 0x30C1 | 12480 | 12481 | V Max, Phase CA - Last Interval | float32 | R | 2
| 0x30C2 | 0x30C3 | 12482 | 12483 | V Min, Phase A - Last Interval | float32 | R | 2
| 0x30C4 | 0x30C5 | 12484 | 12485 | V Min, Phase B - Last Interval | float32 | R | 2
| 0x30C6 | 0x30C7 | 12486 | 12487 | V Min, Phase C - Last Interval | float32 | R | 2
| 0x30C8 | 0x30C9 | 12488 | 12489 | V Min, Phase AB - Last Interval | float32 | R | 2
| 0x30CA | 0x30CB | 12490 | 12491 | V Min, Phase BC - Last Interval | float32 | R | 2
| 0x30CC | 0x30CD | 12492 | 12493 | V Min, Phase CA - Last Interval | float32 | R | 2
| 0x30CE | 0x30CF | 12494 | 12495 | V Mean, Phase A - Last Interval | float32 | R | 2
| 0x30D0 | 0x30D1 | 12496 | 12497 | V Mean, Phase B - Last Interval | float32 | R | 2
| 0x30D2 | 0x30D3 | 12498 | 12499 | V Mean, Phase C - Last Interval | float32 | R | 2
| 0x30D4 | 0x30D5 | 12500 | 12501 | V Mean, Phase AB - Last Interval | float32 | R | 2
| 0x30D6 | 0x30D7 | 12502 | 12503 | V Mean, Phase BC - Last Interval | float32 | R | 2
| 0x30D8 | 0x30D9 | 12504 | 12505 | V Mean, Phase CA - Last Interval | float32 | R | 2
| 0x30DA | 0x30DB | 12506 | 12507 | Displacement Power factor, System | float32 | R | 2
140
Real time basic parameters（Integer）
| 0x3200 | 0x3200 | 12800 | 12800 | Freq_rms | int16 | R | 1
| 0x3201 | 0x3201 | 12801 | 12801 | Ua_rms | int16 | R | 1
| 0x3202 | 0x3202 | 12802 | 12802 | Ub_rms | int16 | R | 1
| 0x3203 | 0x3203 | 12803 | 12803 | Uc_rms | int16 | R | 1
| 0x3204 | 0x3204 | 12804 | 12804 | Uvag_rms | int16 | R | 1
| 0x3205 | 0x3205 | 12805 | 12805 | Uab_rms | int16 | R | 1
| 0x3206 | 0x3206 | 12806 | 12806 | Ubc_rms | int16 | R | 1
| 0x3207 | 0x3207 | 12807 | 12807 | Uca_rms | int16 | R | 1
| 0x3208 | 0x3208 | 12808 | 12808 | Ulag_rms | int16 | R | 1
| 0x3209 | 0x3209 | 12809 | 12809 | Ia_rms | int16 | R | 1
| 0x320A | 0x320A | 12810 | 12810 | Ib_rms | int16 | R | 1
| 0x320B | 0x320B | 12811 | 12811 | Ic_rms | int16 | R | 1
| 0x320C | 0x320C | 12812 | 12812 | Ivag_rms | int16 | R | 1
| 0x320D | 0x320D | 12813 | 12813 | In_rms | int16 | R | 1
| 0x320E | 0x320E | 12814 | 12814 | Pa_rms | int16 | R | 1
| 0x320F | 0x320F | 12815 | 12815 | Pb_rms | int16 | R | 1
| 0x3210 | 0x3210 | 12816 | 12816 | Pc_rms | int16 | R | 1
| 0x3211 | 0x3211 | 12817 | 12817 | P_rms | int16 | R | 1
| 0x3212 | 0x3212 | 12818 | 12818 | Qa_rms | int16 | R | 1
| 0x3213 | 0x3213 | 12819 | 12819 | Qb_rms | int16 | R | 1
| 0x3214 | 0x3214 | 12820 | 12820 | Qc_rms | int16 | R | 1
| 0x3215 | 0x3215 | 12821 | 12821 | Q_rms | int16 | R | 1
| 0x3216 | 0x3216 | 12822 | 12822 | Sa_rms | int16 | R | 1
| 0x3217 | 0x3217 | 12823 | 12823 | Sb_rms | int16 | R | 1
| 0x3218 | 0x3218 | 12824 | 12824 | Sc_rms | int16 | R | 1
| 0x3219 | 0x3219 | 12825 | 12825 | S_rms | int16 | R | 1
| 0x321A | 0x321A | 12826 | 12826 | PFa_rms | int16 | R | 1
| 0x321B | 0x321B | 12827 | 12827 | PFb_rms | int16 | R | 1
| 0x321C | 0x321C | 12828 | 12828 | PFc_rms | int16 | R | 1
| 0x321D | 0x321D | 12829 | 12829 | PF_rms | int16 | R | 1
| 0x321E | 0x321E | 12830 | 12830 | Unbl_u2 | int16 | R | 1
| 0x321F | 0x321F | 12831 | 12831 | Unbl_i2 | int16 | R | 1
| 0x3220 | 0x3220 | 12832 | 12832 | Rlc_val | int16 | R | 1
| 0x3221 | 0x3221 | 12833 | 12833 | P_dema | int16 | R | 1
| 0x3222 | 0x3222 | 12834 | 12834 | Q_dema | int16 | R | 1
| 0x3223 | 0x3223 | 12835 | 12835 | S_dema | int16 | R | 1
| 0x3224 | 0x3224 | 12836 | 12836 | Ia demand | int16 | R | 1
| 0x3225 | 0x3225 | 12837 | 12837 | Ib demand | int16 | R | 1
| 0x3226 | 0x3226 | 12838 | 12838 | Ic demand | int16 | R | 1
Basic parameters（20ms）
Acuvim II V4/Eaton/Acuvim-L V4
| 0x3400 | 0x3401 | 13312 | 13313 | FAST_RMS_UA | float32 | R | 2
| 0x3402 | 0x3403 | 13314 | 13315 | FAST_RMS_UB | float32 | R | 2
| 0x3404 | 0x3405 | 13316 | 13317 | FAST_RMS_UC | float32 | R | 2
| 0x3406 | 0x3407 | 13318 | 13319 | FAST_RMS_UAB | float32 | R | 2
| 0x3408 | 0x3409 | 13320 | 13321 | FAST_RMS_UBC | float32 | R | 2
| 0x340A | 0x340B | 13322 | 13323 | FAST_RMS_UCA | float32 | R | 2
| 0x340C | 0x340D | 13324 | 13325 | FAST_RMS_IA | float32 | R | 2
| 0x340E | 0x340F | 13326 | 13327 | FAST_RMS_IB | float32 | R | 2
| 0x3410 | 0x3411 | 13328 | 13329 | FAST_RMS_IC | float32 | R | 2
| 0x3412 | 0x3413 | 13330 | 13331 | FAST_RMS_UAVG | float32 | R | 2
| 0x3414 | 0x3415 | 13332 | 13333 | FAST_RMS_VLLAVG | float32 | R | 2
| 0x3416 | 0x3417 | 13334 | 13335 | FAST_RMS_IAVG | float32 | R | 2
| 0x3418 | 0x3419 | 13336 | 13337 | FAST_RMS_PSUM | float32 | R | 2
| 0x341A | 0x341B | 13338 | 13339 | FAST_RMS_QSUM | float32 | R | 2
| 0x341C | 0x341D | 13340 | 13341 | FAST_RMS_FREQ | float32 | R | 2
| 0x341E | 0x341F | 13342 | 13343 | Counter | float32 | R | 2
Acuvim II V2
| 0x3500 | 0x3501 | 13568 | 13569 | FAST_RMS_UA | float32 | R | 2
| 0x3502 | 0x3503 | 13570 | 13571 | FAST_RMS_UB | float32 | R | 2
| 0x3504 | 0x3505 | 13572 | 13573 | FAST_RMS_UC | float32 | R | 2
| 0x3506 | 0x3507 | 13574 | 13575 | FAST_RMS_IA | float32 | R | 2
| 0x3508 | 0x3509 | 13576 | 13577 | FAST_RMS_IB | float32 | R | 2
| 0x350A | 0x350B | 13578 | 13579 | FAST_RMS_IC | float32 | R | 2
| 0x350C | 0x350D | 13580 | 13581 | FAST_RMS_FREQ | float32 | R | 2
| 0x350E | 0x350F | 13582 | 13583 | FAST_RMS_UAB | float32 | R | 2
| 0x3510 | 0x3511 | 13584 | 13585 | FAST_RMS_UBC | float32 | R | 2
| 0x3512 | 0x3513 | 13586 | 13587 | FAST_RMS_UCA | float32 | R | 2
| 0x3514 | 0x3515 | 13588 | 13589 | FAST_RMS_PSUM | float32 | R | 2
| 0x3516 | 0x3517 | 13590 | 13591 | FAST_RMS_QSUM | float32 | R | 2
Real time basic parameters（1S）
| 0x4000 | 0x4001 | 16384 | 16385 | Freq_rms | float32 | R | 2
| 0x4002 | 0x4003 | 16386 | 16387 | Ua_rms | float32 | R | 2
| 0x4004 | 0x4005 | 16388 | 16389 | Ub_rms | float32 | R | 2
| 0x4006 | 0x4007 | 16390 | 16391 | Uc_rms | float32 | R | 2
| 0x4008 | 0x4009 | 16392 | 16393 | Uvag_rms | float32 | R | 2
| 0x400A | 0x400B | 16394 | 16395 | Uab_rms | float32 | R | 2
| 0x400C | 0x400D | 16396 | 16397 | Ubc_rms | float32 | R | 2
| 0x400E | 0x400F | 16398 | 16399 | Uca_rms | float32 | R | 2
| 0x4010 | 0x4011 | 16400 | 16401 | Ulag_rms | float32 | R | 2
| 0x4012 | 0x4013 | 16402 | 16403 | Ia_rms | float32 | R | 2
| 0x4014 | 0x4015 | 16404 | 16405 | Ib_rms | float32 | R | 2
| 0x4016 | 0x4017 | 16406 | 16407 | Ic_rms | float32 | R | 2
| 0x4018 | 0x4019 | 16408 | 16409 | Ivag_rms | float32 | R | 2
| 0x401A | 0x401B | 16410 | 16411 | In_rms | float32 | R | 2
| 0x401C | 0x401D | 16412 | 16413 | Pa_rms | float32 | R | 2
| 0x401E | 0x401F | 16414 | 16415 | Pb_rms | float32 | R | 2
| 0x4020 | 0x4021 | 16416 | 16417 | Pc_rms | float32 | R | 2
| 0x4022 | 0x4023 | 16418 | 16419 | P_rms | float32 | R | 2
| 0x4024 | 0x4025 | 16420 | 16421 | Qa_rms | float32 | R | 2
| 0x4026 | 0x4027 | 16422 | 16423 | Qb_rms | float32 | R | 2
| 0x4028 | 0x4029 | 16424 | 16425 | Qc_rms | float32 | R | 2
| 0x402A | 0x402B | 16426 | 16427 | Q_rms | float32 | R | 2
| 0x402C | 0x402D | 16428 | 16429 | Sa_rms | float32 | R | 2
| 0x402E | 0x402F | 16430 | 16431 | Sb_rms | float32 | R | 2
| 0x4030 | 0x4031 | 16432 | 16433 | Sc_rms | float32 | R | 2
| 0x4032 | 0x4033 | 16434 | 16435 | S_rms | float32 | R | 2
| 0x4034 | 0x4035 | 16436 | 16437 | PFa_rms | float32 | R | 2
| 0x4036 | 0x4037 | 16438 | 16439 | PFb_rms | float32 | R | 2
| 0x4038 | 0x4039 | 16440 | 16441 | PFc_rms | float32 | R | 2
| 0x403A | 0x403B | 16442 | 16443 | PF_rms | float32 | R | 2
| 0x403C | 0x403D | 16444 | 16445 | Unbl_u2 | float32 | R | 2
| 0x403E | 0x403F | 16446 | 16447 | Unbl_i2 | float32 | R | 2
| 0x4040 | 0x4041 | 16448 | 16449 | Rlc_val | float32 | R | 2
| 0x4042 | 0x4043 | 16450 | 16451 | P_dema | float32 | R | 2
| 0x4044 | 0x4045 | 16452 | 16453 | Q_dema | float32 | R | 2
| 0x4046 | 0x4047 | 16454 | 16455 | S_dema | float32 | R | 2
Energy （1S）
| 0x4048 | 0x4049 | 16456 | 16457 | Ep_imp Import active energy | uint32 | R/W | 2
| 0x404A | 0x404B | 16458 | 16459 | Ep_exp Expot active energy | uint32 | R/W | 2
| 0x404C | 0x404D | 16460 | 16461 | Eq_imp Import reactive energy | uint32 | R/W | 2
| 0x404E | 0x404F | 16462 | 16463 | Eq_exp Expot reactive energy | uint32 | R/W | 2
| 0x4050 | 0x4051 | 16464 | 16465 | Ep_total Total active energy | uint32 | R/W | 2
| 0x4052 | 0x4053 | 16466 | 16467 | Ep_net Net active energy | int32 | R/W | 2
| 0x4054 | 0x4055 | 16468 | 16469 | Eq_total Total reactive energy | uint32 | R/W | 2
| 0x4056 | 0x4057 | 16470 | 16471 | Eq_net Net reactive energy | int32 | R/W | 2
| 0x4058 | 0x4059 | 16472 | 16473 | Es Apparent energy | uint32 | R/W | 2
Harmonics - THD（3S）
| 0x405A |  | 16474 |  | THD_V1(V12) | int16 | R | 1 |  | two decimal
| 0x405B |  | 16475 |  | THD_V2(V31) | int16 | R | 1
| 0x405C |  | 16476 |  | THD_V3(V23) | int16 | R | 1
| 0x405D |  | 16477 |  | THD_avg | int16 | R | 1
| 0x405E |  | 16478 |  | THD_I1 | int16 | R | 1
| 0x405F |  | 16479 |  | THD_I2 | int16 | R | 1
| 0x4060 |  | 16480 |  | THD_I3 | int16 | R | 1
| 0x4061 |  | 16481 |  | THD_Iavg | int16 | R | 1
| 0x4062 | 0x407F | 16482 | 16511 | V1(V12) 2-31st harmonic | int16 | R | 30
| 0x4080 |  | 16512 |  | Odd THD_V1(V12) | int16 | R | 1
| 0x4081 |  | 16513 |  | Even THD_V1(V12) | int16 | R | 1
| 0x4082 |  | 16514 |  | V1(V12) crest factor | int16 | R | 1
| 0x4083 |  | 16515 |  | V1(V12) Telephone Harmonic Form Factor | int16 | R | 1
| 0x4084 | 0x40A1 | 16516 | 16545 | V2(V31) 2-31st harmonic | int16 | R | 30
| 0x40A2 |  | 16546 |  | Odd THD_V2(V31) | int16 | R | 1
| 0x40A3 |  | 16547 |  | Even THD_V2(V31) | int16 | R | 1
| 0x40A4 |  | 16548 |  | V2(V31) crest factor | int16 | R | 1
| 0x40A5 |  | 16549 |  | V2(V31) Telephone Harmonic Form Factor | int16 | R | 1
| 0x40A6 | 0x40C3 | 16550 | 16579 | V3(V23) 2-31st harmonic | int16 | R | 30
| 0x40C4 |  | 16580 |  | Odd THD_V3(V23) | int16 | R | 1
| 0x40C5 |  | 16581 |  | Even THD_V3(V23) | int16 | R | 1
| 0x40C6 |  | 16582 |  | V3(V23) crest factor | int16 | R | 1
| 0x40C7 |  | 16583 |  | V3(V23) Telephone Harmonic Form Factor | int16 | R | 1
| 0x40C8 | 0x40E5 | 16584 | 16613 | I1 2nd-31st harmonic | int16 | R | 30
| 0x40E6 |  | 16614 |  | Odd THD_I1 | int16 | R | 1
| 0x40E7 |  | 16615 |  | Even THD_I1 | int16 | R | 1
| 0x40E8 |  | 16616 |  | I1 K factor | int16 | R | 1
| 0x40E9 | 0x4106 | 16617 | 16646 | I2 2nd-31st harmonic | int16 | R | 30
| 0x4107 |  | 16647 |  | Odd THD_I2 | int16 | R | 1
| 0x4108 |  | 16648 |  | Even THD_I2 | int16 | R | 1
| 0x4109 |  | 16649 |  | I2 K factor | int16 | R | 1
| 0x410A | 0x4127 | 16650 | 16679 | I3 2nd-31st harmonic | int16 | R | 30
| 0x4128 |  | 16680 |  | Odd THD_I3 | int16 | R | 1
| 0x4129 |  | 16681 |  | Even THD_I3 | int16 | R | 1
| 0x412A |  | 16682 |  | I3 K factor | int16 | R | 1
| 0x412B |  | 16683 |  | TDD_I1 | int16 | R | 1 |  |  |  | v6.32_250627; v6.30_PXE_250627
| 0x412C |  | 16684 |  | TDD_I2 | int16 | R | 1
| 0x412D |  | 16685 |  | TDD_I3 | int16 | R | 1
| 0x412E |  | 16686 |  | TDD_Iavg | int16 | R | 1
| 0x412F |  | 16687 |  | I1 crest factor | int16 | R | 1 |  |  |  | v6.37_0204; v6.34_PXE_260123
| 0x4130 |  | 16688 |  | I2 crest factor | int16 | R | 1
| 0x4131 |  | 16689 |  | I3 crest factor | int16 | R | 1
| 0x4132 |  | 16690 |  | In crest factor | int16 | R | 1
Sequence
| 0x4294 |  | 17044 |  | Real part of Voltage Positive Sequence | int16 | R | 1
| 0x4295 |  | 17045 |  | Imag part of Voltage Postive Sequence | int16 | R | 1
| 0x4296 |  | 17046 |  | Real part of Voltage Negative Sequence | int16 | R | 1
| 0x4297 |  | 17047 |  | Imag part of Voltage Negative Sequence | int16 | R | 1
| 0x4298 |  | 17048 |  | Real part of Voltage Zero Sequence | int16 | R | 1
| 0x4299 |  | 17049 |  | Imag part of Voltage Zero Sequence | int16 | R | 1
| 0x429A |  | 17050 |  | Real part of Current Positive Sequence | int16 | R | 1
| 0x429B |  | 17051 |  | Imag part of Current Postive Sequence | int16 | R | 1
| 0x429C |  | 17052 |  | Real part of Current Negative Sequence | int16 | R | 1
| 0x429D |  | 17053 |  | Imag part of Current Negative Sequence | int16 | R | 1
| 0x429E |  | 17054 |  | Real part of Current Zero Sequence | int16 | R | 1
| 0x429F |  | 17055 |  | Imag part of Current Zero Sequence | int16 | R | 1
Phase Angle
| 0x42A0 |  | 17056 |  | Phase Angle of V2 to V1 | word | R | 1
| 0x42A1 |  | 17057 |  | Phase Angle of V3 to V1 | word | R | 1
| 0x42A2 |  | 17058 |  | Phase Angle of I1 to V1 | word | R | 1
| 0x42A3 |  | 17059 |  | Phase Angle of I2 to V1 | word | R | 1
| 0x42A4 |  | 17060 |  | Phase Angle of I3 to V1 | word | R | 1
| 0x42A5 |  | 17061 |  | Phase Angle of V1 to V1 | word | R | 1
Harmonics - individual（3S）
| 0x4500 | 0x451F | 17664 | 17695 | V1(V12) 32nd - 63rd harmonic | word | R | 32
| 0x4520 | 0x453F | 17696 | 17727 | V2(V31) 32nd - 63rd harmonic | word | R | 32
| 0x4540 | 0x455F | 17728 | 17759 | V3(V23) 32nd - 63rd harmonic | word | R | 32
| 0x4560 | 0x457F | 17760 | 17791 | I1 32nd - 63rd harmonic | word | R | 32
| 0x4580 | 0x459F | 17792 | 17823 | I2 32nd - 63rd harmonic | word | R | 32
| 0x45A0 | 0x45BF | 17824 | 17855 | I3 32nd - 63rd harmonic | word | R | 32
Load percentage
| 0x45F0 | 0x45F1 | 17904 | 17905 | Load percentage | float32 | R | 2
Current demand
| 0x4600 | 0x4601 | 17920 | 17921 | Ia demand | float32 | R | 2
| 0x4602 | 0x4603 | 17922 | 17923 | Ib demand | float32 | R | 2
| 0x4604 | 0x4605 | 17924 | 17925 | Ic demand | float32 | R | 2
Energy - continue（1S）
| 0x4620 | 0x4621 | 17952 | 17953 | Epa_imp Phase A import active energy | uint32 | R/W | 2
| 0x4622 | 0x4623 | 17954 | 17955 | Epa_exp Phase A expot active energy | uint32 | R/W | 2
| 0x4624 | 0x4625 | 17956 | 17957 | Epb_imp Phase B import active energy | uint32 | R/W | 2
| 0x4626 | 0x4627 | 17958 | 17959 | Epb_exp Phase B expot active energy | uint32 | R/W | 2
| 0x4628 | 0x4629 | 17960 | 17961 | Epc_imp Phase C import active energy | uint32 | R/W | 2
| 0x462A | 0x462B | 17962 | 17963 | Epc_exp Phase C expot active energy | uint32 | R/W | 2
| 0x462C | 0x462D | 17964 | 17965 | Eqa_imp Phase A import reactive energy | uint32 | R/W | 2
| 0x462E | 0x462F | 17966 | 17967 | Eqa_exp Phase A expot reactive energy | uint32 | R/W | 2
| 0x4630 | 0x4631 | 17968 | 17969 | Eqb_imp Phase B import reactive energy | uint32 | R/W | 2
| 0x4632 | 0x4633 | 17970 | 17971 | Eqb_exp Phase B expot reactive energy | uint32 | R/W | 2
| 0x4634 | 0x4635 | 17972 | 17973 | Eqc_imp Phase C import reactive energy | uint32 | R/W | 2
| 0x4636 | 0x4637 | 17974 | 17975 | Eqc_exp Phase C expot reactive energy | uint32 | R/W | 2
| 0x4638 | 0x4639 | 17976 | 17977 | Esa Phase A Apparent energy | uint32 | R/W | 2
| 0x463A | 0x463B | 17978 | 17979 | Esb Phase B Apparent energy | uint32 | R/W | 2
| 0x463C | 0x463D | 17980 | 17981 | Esc Phase C Apparent energy | uint32 | R/W | 2
Kono Customized
| 0x463E | 0x466D | 17982 | 18029 | 1st previous day energy; parameters in the order of: Ep_imp Import active energy Ep_exp Expot active energy Eq_imp Import reactive energy Eq_exp Expot reactive energy Ep_total Total active energy Ep_net Net active energy Eq_total Total reactive energy Eq_net Net reactive energy Es Apparent energy Epa_imp Phase A import active energy Epa_exp Phase A expot active energy Epb_imp Phase B import active energy Epb_exp Phase B expot active energy Epc_imp Phase C import active energy Epc_exp Phase C expot active energy Eqa_imp Phase A import reactive energy Eqa_exp Phase A expot reactive energy Eqb_imp Phase B import reactive energy Eqb_exp Phase B expot reactive energy Eqc_imp Phase C import reactive energy Eqc_exp Phase C expot reactive energy Esa Phase A Apparent energy Esb Phase B Apparent energy Esc Phase C Apparent energy | uint32 | R/W | 48 |  | 0-999999999
| 0x466E | 0x469D | 18030 | 18077 | 2nd previous day energy | uint32 | R/W | 48 |  | 0-999999999
| 0x469E | 0x46CD | 18078 | 18125 | 3rd previous day energy | uint32 | R/W | 48 |  | 0-999999999
| 0x46CE | 0x46FD | 18126 | 18173 | 4th previous day energy | uint32 | R/W | 48 |  | 0-999999999
| 0x46FE | 0x472D | 18174 | 18221 | 5th previous day energy | uint32 | R/W | 48 |  | 0-999999999
| 0x472E | 0x475D | 18222 | 18269 | 6th previous day energy | uint32 | R/W | 48 |  | 0-999999999
| 0x475E | 0x478D | 18270 | 18317 | 7th previous day energy | uint32 | R/W | 48 |  | 0-999999999
| 0x4700 | 0x473F | 18176 | 18239 | V1(V12) 64th - 127th harmonic | word | R | 64
| 0x4740 | 0x477F | 18240 | 18303 | V2(V31) 64th - 127th harmonic | word | R | 64
| 0x4780 | 0x47BF | 18304 | 18367 | V3(V23) 64th - 127th harmonic | word | R | 64
| 0x47C0 | 0x47FF | 18368 | 18431 | I1 64th - 127th harmonic | word | R | 64
| 0x4800 | 0x483F | 18432 | 18495 | I2 64th - 127th harmonic | word | R | 64
| 0x4840 | 0x487F | 18496 | 18559 | I3 64th - 127th harmonic | word | R | 64
| 0x48F0 | 0x48F1 | 18672 | 18673 | Ua pst | float32 | R | 2
| 0x48F2 | 0x48F3 | 18674 | 18675 | Ub pst | float32 | R | 2
| 0x48F4 | 0x48F5 | 18676 | 18677 | Uc pst | float32 | R | 2
| 0x48F6 | 0x48F7 | 18678 | 18679 | Ua plt | float32 | R | 2
| 0x48F8 | 0x48F9 | 18680 | 18681 | Ub plt | float32 | R | 2
| 0x48FA | 0x48FB | 18682 | 18683 | Uc plt | float32 | R | 2
Import/Export Apparent Energy
| 0x4900 | 0x4901 | 18688 | 18689 | Es_imp Import apparent energy | uint32 | R/W | 2
| 0x4902 | 0x4903 | 18690 | 18691 | Esa_imp Phase A import apparent energy | uint32 | R/W | 2
| 0x4904 | 0x4905 | 18692 | 18693 | Esb_imp Phase B import apparent energy | uint32 | R/W | 2
| 0x4906 | 0x4907 | 18694 | 18695 | Esc_imp Phase C import apparent energy | uint32 | R/W | 2
| 0x4908 | 0x4909 | 18696 | 18697 | Es_exp Export apparent energy | uint32 | R/W | 2
| 0x490A | 0x490B | 18698 | 18699 | Esa_exp Phase A export apparent energy | uint32 | R/W | 2
| 0x490C | 0x490D | 18700 | 18701 | Esb_exp Phase B export apparent energy | uint32 | R/W | 2
| 0x490E | 0x490F | 18702 | 18703 | Esc_exp Phase C export apparent energy | uint32 | R/W | 2
Four-quadrant reactive energy
| 0x4910 | 0x4911 | 18704 | 18705 | Reactive energy-Q1 | uint32 | R/W | 2
| 0x4912 | 0x4913 | 18706 | 18707 | Phase A reactive energy-Q1 | uint32 | R/W | 2
| 0x4914 | 0x4915 | 18708 | 18709 | Phase B reactive energy-Q1 | uint32 | R/W | 2
| 0x4916 | 0x4917 | 18710 | 18711 | Phase C reactive energy-Q1 | uint32 | R/W | 2
| 0x4918 | 0x4919 | 18712 | 18713 | Reactive energy-Q2 | uint32 | R/W | 2
| 0x491A | 0x491B | 18714 | 18715 | Phase A reactive energy-Q2 | uint32 | R/W | 2
| 0x491C | 0x491D | 18716 | 18717 | B phase reactive energy-Q2 | uint32 | R/W | 2
| 0x491E | 0x491F | 18718 | 18719 | Phase B reactive energy-Q2 | uint32 | R/W | 2
| 0x4920 | 0x4921 | 18720 | 18721 | Reactive energy-Q3 | uint32 | R/W | 2
| 0x4922 | 0x4923 | 18722 | 18723 | Phase A reactive energy-Q3 | uint32 | R/W | 2
| 0x4924 | 0x4925 | 18724 | 18725 | Phase B reactive energy-Q3 | uint32 | R/W | 2
| 0x4926 | 0x4927 | 18726 | 18727 | Phase C reactive energy-Q3 | uint32 | R/W | 2
| 0x4928 | 0x4929 | 18728 | 18729 | Reactive energy-Q4 | uint32 | R/W | 2
| 0x492A | 0x492B | 18730 | 18731 | Phase A reactive energy-Q4 | uint32 | R/W | 2
| 0x492C | 0x492D | 18732 | 18733 | Phase B reactive energy-Q4 | uint32 | R/W | 2
| 0x492E | 0x492F | 18734 | 18735 | Phase C reactive energy-Q4 | uint32 | R/W | 2
Moving Average Parameters
for 1 Cycle RMS | 0x493D | 0x493E | 18749 | 18750 | V1 | float32 | R | 2
| 0x493F | 0x4940 | 18751 | 18752 | V2 | float32 | R | 2
| 0x4941 | 0x4942 | 18753 | 18754 | V3 | float32 | R | 2
| 0x4943 | 0x4944 | 18755 | 18756 | V12 | float32 | R | 2
| 0x4945 | 0x4946 | 18757 | 18758 | V23 | float32 | R | 2
| 0x4947 | 0x4948 | 18759 | 18760 | V31 | float32 | R | 2
| 0x4949 | 0x494A | 18761 | 18762 | I1 | float32 | R | 2
| 0x494B | 0x494C | 18763 | 18764 | I2 | float32 | R | 2
| 0x494D | 0x494E | 18765 | 18766 | I3 | float32 | R | 2
| 0x494F | 0x4950 | 18767 | 18768 | In | float32 | R | 2
| 0x4951 | 0x4952 | 18769 | 18770 | P, phase A | float32 | R | 2
| 0x4953 | 0x4954 | 18771 | 18772 | P, phase B | float32 | R | 2
| 0x4955 | 0x4956 | 18773 | 18774 | P, phase C | float32 | R | 2
| 0x4957 | 0x4958 | 18775 | 18776 | S, phase A | float32 | R | 2
| 0x4959 | 0x495A | 18777 | 18778 | S, phase B | float32 | R | 2
| 0x495B | 0x495C | 18779 | 18780 | S, phase C | float32 | R | 2
| 0x495D | 0x495E | 18781 | 18782 | P, system | float32 | R | 2
| 0x495F | 0x4960 | 18783 | 18784 | Residual Current | float32 | R | 2 |  | 0 |  | v6.33_PXE_251212; v6.37_260123
36
Accumulated Energy （1S）
| 0x4980 | 0x4985 | 18816 | 18821 | Energy accumulated start time | uint16 | R | 6 |  |  |  | v6.29_250204
| 0x4986 | 0x498B | 18822 | 18827 | Energy accumulated end time | uint16 | R | 6
| 0x498C | 0x498D | 18828 | 18829 | Ep_imp Import active energy | uint32 | R | 2
| 0x498E | 0x498F | 18830 | 18831 | Ep_exp Expot active energy | uint32 | R | 2
| 0x4990 | 0x4991 | 18832 | 18833 | Eq_imp Import reactive energy | uint32 | R | 2
| 0x4992 | 0x4993 | 18834 | 18835 | Eq_exp Expot reactive energy | uint32 | R | 2
| 0x4994 | 0x4995 | 18836 | 18837 | Ep_total Total active energy | uint32 | R | 2
| 0x4996 | 0x4997 | 18838 | 18839 | Ep_net Net active energy | int32 | R | 2
| 0x4998 | 0x4999 | 18840 | 18841 | Eq_total Total reactive energy | uint32 | R | 2
| 0x499A | 0x499B | 18842 | 18843 | Eq_net Net reactive energy | int32 | R | 2
| 0x499C | 0x499D | 18844 | 18845 | Es Apparent energy | uint32 | R | 2
30
Harmonic - amplitude and phase angle
Values in secondary side | 0x6E00 | 0x6E3D | 28160 | 28221 | V1 or V12 harmonic amplitude (2nd - 63rd order) | int16 | R | 62 | Actual voltage U = reading data / 10
| 0x6E3E | 0x6E7B | 28222 | 28283 | V2 or V23 harmonic amplitude (2nd - 63rd order) | int16 | R | 62
| 0x6E7C | 0x6EB9 | 28284 | 28345 | V3 or V31 harmonic amplitude (2nd - 63rd order) | int16 | R | 62 |  | 0 | 0
| 0x6EBA | 0x6EF7 | 28346 | 28407 | I1 harmonic amplitude (2nd - 63rd order) | int16 | R | 62 | Actual current I = reading data / 1000
| 0x6EF8 | 0x6F35 | 28408 | 28469 | I2 harmonic amplitude (2nd - 63rd order) | int16 | R | 62
| 0x6F36 | 0x6F73 | 28470 | 28531 | I3 harmonic amplitude (2nd - 63rd order) | int16 | R | 62
| 0x6F74 | 0x6FB1 | 28532 | 28593 | V1 or V12 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62 | Actual phase angle = reading data / 10
| 0x6FB2 | 0x6FEF | 28594 | 28655 | V2 or V23 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62
| 0x6FF0 | 0x702D | 28656 | 28717 | V3 or V31 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62
| 0x702E | 0x706B | 28718 | 28779 | I1 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62
| 0x706C | 0x70A9 | 28780 | 28841 | I2 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62
| 0x70AA | 0x70E7 | 28842 | 28903 | I3 Harmonic phase angle (2nd - 63rd order) | int16 | R | 62

## Acuvim-L Parameters
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default Value | Factory Default
Basic Readings (word)
| 0x2000 |  | 8192 |  | Freq | int16 | R | 1 | 4500～6500
| 0x2001 |  | 8193 |  | Va | int16 | R | 1 | 0～65535
| 0x2002 |  | 8194 |  | Vb | int16 | R | 1 | 0～65535
| 0x2003 |  | 8195 |  | Vc | int16 | R | 1 | 0～65535
| 0x2004 |  | 8196 |  | Vlnagv | int16 | R | 1 | 0～65535
| 0x2005 |  | 8197 |  | Vab | int16 | R | 1 | 0～65535
| 0x2006 |  | 8198 |  | Vbc | int16 | R | 1 | 0～65535
| 0x2007 |  | 8199 |  | Vca | int16 | R | 1 | 0～65535
| 0x2008 |  | 8200 |  | Vllavg | int16 | R | 1 | 0～65535
| 0x2009 |  | 8201 |  | Ia | int16 | R | 1 | 0～65535
| 0x200A |  | 8202 |  | Ib | int16 | R | 1 | 0～65535
| 0x200B |  | 8203 |  | Ic | int16 | R | 1 | 0～65535
| 0x200C |  | 8204 |  | In_calc | int16 | R | 1 | 0～65535
| 0x200D |  | 8205 |  | In_measure | int16 | R | 1 | 0～65535
| 0x200E |  | 8206 |  | Itotal | int16 | R | 1 | 0～65535
| 0x200F |  | 8207 |  | Iavg | int16 | R | 1 | 0～65535
| 0x2010 |  | 8208 |  | Pa | int16 | R | 1 | -32768～32767
| 0x2011 |  | 8209 |  | Pb | int16 | R | 1 | -32768～32767
| 0x2012 |  | 8210 |  | Pc | int16 | R | 1 | -32768～32767
| 0x2013 |  | 8211 |  | P | int16 | R | 1 | -32768～32767
| 0x2014 |  | 8212 |  | Qa | int16 | R | 1 | -32768～32767
| 0x2015 |  | 8213 |  | Qb | int16 | R | 1 | -32768～32767
| 0x2016 |  | 8214 |  | Qc | int16 | R | 1 | -32768～32767
| 0x2017 |  | 8215 |  | Q | int16 | R | 1 | -32768～32767
| 0x2018 |  | 8216 |  | Sa | int16 | R | 1 | 0～65535
| 0x2019 |  | 8217 |  | Sb | int16 | R | 1 | 0～65535
| 0x201A |  | 8218 |  | Sc | int16 | R | 1 | 0～65535
| 0x201B |  | 8219 |  | S | int16 | R | 1 | 0～65535
| 0x201C |  | 8220 |  | PFa | int16 | R | 1 | -1000～1000
| 0x201D |  | 8221 |  | PFb | int16 | R | 1 | -1000～1000
| 0x201E |  | 8222 |  | PFc | int16 | R | 1 | -1000～1000
| 0x201F |  | 8223 |  | PF | int16 | R | 1 | -1000～1000
| 0x2020 |  | 8224 |  | U_unbl | int16 | R | 1 | 0～1000
| 0x2021 |  | 8225 |  | I_unbl | int16 | R | 1 | 0～1000
| 0x2022 |  | 8226 |  | LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x2023 |  | 8227 |  | P demand | int16 | R | 1 | -32768～32767
| 0x2024 |  | 8228 |  | Q Demand | int16 | R | 1 | -32768～32767
| 0x2025 |  | 8229 |  | S Demand | int16 | R | 1 | 0～65535
| 0x2026 |  | 8230 |  | Ia Demand | int16 | R | 1 | 0～65535
| 0x2027 |  | 8231 |  | Ib Demand | int16 | R | 1 | 0～65535
| 0x2028 |  | 8232 |  | Ic Demand | int16 | R | 1 | 0～65535
| 0x2029 |  | 8233 |  | In Demand | int16 | R | 1 | 0～65535
Energy
| 0x2080 | 0x2081 | 8320 | 8321 | Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x2082 | 0x2083 | 8322 | 8323 | Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x2084 | 0x2085 | 8324 | 8325 | Ep_total | uint32 | R/W | 2 | 0～999999999
| 0x2086 | 0x2087 | 8326 | 8327 | Ep_net | int32 | R/W | 2 | -999999999～999999999
| 0x2088 | 0x2089 | 8328 | 8329 | Ep_q1 | uint32 | R/W | 2 | 0～999999999
| 0x208A | 0x208B | 8330 | 8331 | Ep_q2 | uint32 | R/W | 2 | 0～999999999
| 0x208C | 0x208D | 8332 | 8333 | Ep_q3 | uint32 | R/W | 2 | 0～999999999
| 0x208E | 0x208F | 8334 | 8335 | Ep_q4 | uint32 | R/W | 2 | 0～999999999
| 0x2090 | 0x2091 | 8336 | 8337 | Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x2092 | 0x2093 | 8338 | 8339 | Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x2094 | 0x2095 | 8340 | 8341 | Eq_total | uint32 | R/W | 2 | 0～999999999
| 0x2096 | 0x2097 | 8342 | 8343 | Eq_net | int32 | R/W | 2 | -999999999～999999999
| 0x2098 | 0x2099 | 8344 | 8345 | Eq_q1 | uint32 | R/W | 2 | 0～999999999
| 0x209A | 0x209B | 8346 | 8347 | Eq_q2 | uint32 | R/W | 2 | 0～999999999
| 0x209C | 0x209D | 8348 | 8349 | Eq_q3 | uint32 | R/W | 2 | 0～999999999
| 0x209E | 0x209F | 8350 | 8351 | Eq_q4 | uint32 | R/W | 2 | 0～999999999
| 0x20A0 | 0x20A1 | 8352 | 8353 | Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x20A2 | 0x20A3 | 8354 | 8355 | ES_exp | uint32 | R/W | 2 | 0～999999999
| 0x20A4 | 0x20A5 | 8356 | 8357 | Es_total | uint32 | R/W | 2 | 0～999999999
| 0x20A6 | 0x20A7 | 8358 | 8359 | Es_net | int32 | R/W | 2 | -999999999～999999999
| 0x20A8 | 0x20A9 | 8360 | 8361 | Es_q1 | uint32 | R/W | 2 | 0～999999999
| 0x20AA | 0x20AB | 8362 | 8363 | Es_q2 | uint32 | R/W | 2 | 0～999999999
| 0x20AC | 0x20AD | 8364 | 8365 | Es_q3 | uint32 | R/W | 2 | 0～999999999
| 0x20AE | 0x20AF | 8366 | 8367 | Es_q4 | uint32 | R/W | 2 | 0～999999999
| 0x20B0 | 0x20B1 | 8368 | 8369 | Phase A Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x20B2 | 0x20B3 | 8370 | 8371 | Phase A Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x20B4 | 0x20B5 | 8372 | 8373 | Phase B Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x20B6 | 0x20B7 | 8374 | 8375 | Phase B Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x20B8 | 0x20B9 | 8376 | 8377 | Phase C Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x20BA | 0x20BB | 8378 | 8379 | Phase C Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x20BC | 0x20BD | 8380 | 8381 | Phase A Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x20BE | 0x20BF | 8382 | 8383 | Phase A Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x20C0 | 0x20C1 | 8384 | 8385 | Phase B Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x20C2 | 0x20C3 | 8386 | 8387 | Phase B Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x20C4 | 0x20C5 | 8388 | 8389 | Phase C Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x20C6 | 0x20C7 | 8390 | 8391 | Phase C Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x20C8 | 0x20C9 | 8392 | 8393 | Phase A Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x20CA | 0x20CB | 8394 | 8395 | Phase A Es_exp | uint32 | R/W | 2 | 0～999999999
| 0x20CC | 0x20CD | 8396 | 8397 | Phase B Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x20CE | 0x20CF | 8398 | 8399 | Phase B Es_exp | uint32 | R/W | 2 | 0～999999999
| 0x20D0 | 0x20D1 | 8400 | 8401 | Phase C Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x20D2 | 0x20D3 | 8402 | 8403 | Phase C Es_exp | uint32 | R/W | 2 | 0～999999999
Basic Readings (Float)
| 0x2180 | 0x2181 | 8576 | 8577 | Freq | float32 | R | 2
| 0x2182 | 0x2183 | 8578 | 8579 | Va | float32 | R | 2
| 0x2184 | 0x2185 | 8580 | 8581 | Vb | float32 | R | 2
| 0x2186 | 0x2187 | 8582 | 8583 | Vc | float32 | R | 2
| 0x2188 | 0x2189 | 8584 | 8585 | Vlnagv | float32 | R | 2
| 0x218A | 0x218B | 8586 | 8587 | Vab | float32 | R | 2
| 0x218C | 0x218D | 8588 | 8589 | Vbc | float32 | R | 2
| 0x218E | 0x218F | 8590 | 8591 | Vca | float32 | R | 2
| 0x2190 | 0x2191 | 8592 | 8593 | Vllavg | float32 | R | 2
| 0x2192 | 0x2193 | 8594 | 8595 | Ia | float32 | R | 2
| 0x2194 | 0x2195 | 8596 | 8597 | Ib | float32 | R | 2
| 0x2196 | 0x2197 | 8598 | 8599 | Ic | float32 | R | 2
| 0x2198 | 0x2199 | 8600 | 8601 | In_calc | float32 | R | 2
| 0x219A | 0x219B | 8602 | 8603 | In_measure | float32 | R | 2
| 0x219C | 0x219D | 8604 | 8605 | Itotal | float32 | R | 2
| 0x219E | 0x219F | 8606 | 8607 | Iavg | float32 | R | 2
| 0x21A0 | 0x21A1 | 8608 | 8609 | Pa | float32 | R | 2
| 0x21A2 | 0x21A3 | 8610 | 8611 | Pb | float32 | R | 2
| 0x21A4 | 0x21A5 | 8612 | 8613 | Pc | float32 | R | 2
| 0x21A6 | 0x21A7 | 8614 | 8615 | P | float32 | R | 2
| 0x21A8 | 0x21A9 | 8616 | 8617 | Qa | float32 | R | 2
| 0x21AA | 0x21AB | 8618 | 8619 | Qb | float32 | R | 2
| 0x21AC | 0x21AD | 8620 | 8621 | Qc | float32 | R | 2
| 0x21AE | 0x21AF | 8622 | 8623 | Q | float32 | R | 2
| 0x21B0 | 0x21B1 | 8624 | 8625 | Sa | float32 | R | 2
| 0x21B2 | 0x21B3 | 8626 | 8627 | Sb | float32 | R | 2
| 0x21B4 | 0x21B5 | 8628 | 8629 | Sc | float32 | R | 2
| 0x21B6 | 0x21B7 | 8630 | 8631 | S | float32 | R | 2
| 0x21B8 | 0x21B9 | 8632 | 8633 | PFa | float32 | R | 2
| 0x21BA | 0x21BB | 8634 | 8635 | PFb | float32 | R | 2
| 0x21BC | 0x21BD | 8636 | 8637 | PFc | float32 | R | 2
| 0x21BE | 0x21BF | 8638 | 8639 | PF | float32 | R | 2
| 0x21C0 | 0x21C1 | 8640 | 8641 | U_unbl | float32 | R | 2
| 0x21C2 | 0x21C3 | 8642 | 8643 | I_unbl | float32 | R | 2
| 0x21C4 | 0x21C5 | 8644 | 8645 | LN (L/C/R) | float32 | R | 2
| 0x21C6 | 0x21C7 | 8646 | 8647 | P demand | float32 | R | 2
| 0x21C8 | 0x21C9 | 8648 | 8649 | Q Demand | float32 | R | 2
| 0x21CA | 0x21CB | 8650 | 8651 | S Demand | float32 | R | 2
| 0x21CC | 0x21CD | 8652 | 8653 | Ia Demand | float32 | R | 2
| 0x21CE | 0x21CF | 8654 | 8655 | Ib Demand | float32 | R | 2
| 0x21D0 | 0x21D1 | 8656 | 8657 | Ic Demand | float32 | R | 2
| 0x21D2 | 0x21D3 | 8658 | 8659 | In Demand | float32 | R | 2
Phase Angle | 0x21D4 | 0x21D5 | 8660 | 8661 | Phase Angle of V2 to V1 | float32 | R | 2
| 0x21D6 | 0x21D7 | 8662 | 8663 | Phase Angle of V3 to V1 | float32 | R | 2
| 0x21D8 | 0x21D9 | 8664 | 8665 | Phase Angle of I1 to V1 | float32 | R | 2
| 0x21DA | 0x21DB | 8666 | 8667 | Phase Angle of I2 to V1 | float32 | R | 2
| 0x21DC | 0x21DD | 8668 | 8669 | Phase Angle of I3 to V1 | float32 | R | 2
Acuvim-LV3 values in primary side | 0x0600 | 0x0601 | 1536 | 1537 | Freq_rms | Float | R | 2
| 0x0602 | 0x0603 | 1538 | 1539 | Ua_rms | Float | R | 2
| 0x0604 | 0x0605 | 1540 | 1541 | Ub_rms | Float | R | 2
| 0x0606 | 0x0607 | 1542 | 1543 | Uc_rms | Float | R | 2
| 0x0608 | 0x0609 | 1544 | 1545 | Uab_rms | Float | R | 2
| 0x060A | 0x060B | 1546 | 1547 | Ubc_rms | Float | R | 2
| 0x060C | 0x060D | 1548 | 1549 | Uca_rms | Float | R | 2
| 0x060E | 0x060F | 1550 | 1551 | I a RMS | Float | R | 2
| 0x0610 | 0x0611 | 1552 | 1553 | I b RMS | Float | R | 2
| 0x0612 | 0x0613 | 1554 | 1555 | I c RMS | Float | R | 2
| 0x0614 | 0x0615 | 1556 | 1557 | I n RMS (calculation) | Float | R | 2
| 0x0616 | 0x0617 | 1558 | 1559 | Pa_rms | Float | R | 2
| 0x0618 | 0x0619 | 1560 | 1561 | Pb_rms | Float | R | 2
| 0x061A | 0x061B | 1562 | 1563 | Pc_rms | Float | R | 2
| 0x061C | 0x061D | 1564 | 1565 | P_rms | Float | R | 2
| 0x061E | 0x061F | 1566 | 1567 | Qa_rms | Float | R | 2
| 0x0620 | 0x0621 | 1568 | 1569 | Qb_rms | Float | R | 2
| 0x0622 | 0x0623 | 1570 | 1571 | Qc_rms | Float | R | 2
| 0x0624 | 0x0625 | 1572 | 1573 | Q_rms | Float | R | 2
| 0x0626 | 0x0627 | 1574 | 1575 | S_rms | Float | R | 2
| 0x0628 | 0x0629 | 1576 | 1577 | PFa_rms | Float | R | 2
| 0x062A | 0x062B | 1578 | 1579 | PFb_rms | Float | R | 2
| 0x062C | 0x062D | 1580 | 1581 | PFc_rms | Float | R | 2
| 0x062E | 0x062F | 1582 | 1583 | PF_rms | Float | R | 2
| 0x0630 | 0x0631 | 1584 | 1585 | Unbl_u2 | Float | R | 2
| 0x0632 | 0x0633 | 1586 | 1587 | Unbl_i2 | Float | R | 2
| 0x0634 | 0x0635 | 1588 | 1589 | Spare | Float | R | 2
| 0x0636 | 0x0637 | 1590 | 1591 | Sa_rms | Float | R | 2
| 0x0638 | 0x0639 | 1592 | 1593 | Sb_rms | Float | R | 2
| 0x063A | 0x063B | 1594 | 1595 | Sc_rms | Float | R | 2
| 0x063C | 0x063D | 1596 | 1597 | Spare | Float | R | 2
| 0x063E | 0x063F | 1598 | 1599 | S_dema | Float | R | 2
| 0x0640 | 0x0641 | 1600 | 1601 | P_dema | Float | R | 2
| 0x0642 | 0x0643 | 1602 | 1603 | Q_dema | Float | R | 2
| 0x0644 | 0x0645 | 1604 | 1605 | Ia demand | Float | R | 2
| 0x0646 | 0x0647 | 1606 | 1607 | Ib demand | Float | R | 2
| 0x0648 | 0x0649 | 1608 | 1609 | Ic demand | Float | R | 2
| 0x064A | 0x064B | 1610 | 1611 | Spare | Float | R | 2

## Transmission Line loss
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default Value | Factory Default
Configuration
| 0x2640 | 0x2640 | 9792 | 9792 | Main enbale flag | uint16 | R/W | 1 | Disable:0 Enable:1 | 0 | 0
| 0x2641 | 0x2641 | 9793 | 9793 | Meter location | uint16 | R/W | 1 | 0:Source no transformer, 1:Source with transformer, 4:Load no transformer, 5:Load with transformer | 0 | 0
| 0x2642 | 0x2642 | 9794 | 9794 | Bill location | uint16 | R/W | 1 | 0:Source no transformer, 1:Source with transformer, 4:Load no transformer, 5:Load with transformer | 1 | 1
| 0x2643 | 0x2643 | 9795 | 9795 | Transmission enable | uint16 | R/W | 1 | Disable:0 Enable:1 | 1 | 1
| 0x2644 | 0x2644 | 9796 | 9796 | Line 1 method | uint16 | R/W | 1 | 0:RLC 1:PI Model | 0 | 0
| 0x2645 | 0x2645 | 9797 | 9797 | Line 2 method | uint16 | R/W | 1 | 0:RLC 1:PI Model | 0 | 0
| 0x2646 | 0x2646 | 9798 | 9798 | Transformer enable | uint16 | R/W | 1 | Disable:0 Enable:1 | 1 | 1
| 0x2647 | 0x2647 | 9799 | 9799 | Transformer method | uint16 | R/W | 1 | 0: Nameplate method, 1: lossConstant method | 1 | 1
| 0x2648 | 0x2649 | 9800 | 9801 | C1 unit capacitor nF/km | float32 | R/W | 2 | 0-10000 nF | 9 | 9
| 0x264A | 0x264B | 9802 | 9803 | C2 unit capacitor nF/km | float32 | R/W | 2 | 0-10000 nF | 9 | 9
| 0x264C | 0x264D | 9804 | 9805 | L1 unit inductor mH/km | float32 | R/W | 2 | 0-10000 mH | 1.2 | 1.2
| 0x264E | 0x264F | 9806 | 9807 | L2 unit inductor mH/km | float32 | R/W | 2 | 0-10000 mH | 1.2 | 1.2
| 0x2650 | 0x2651 | 9808 | 9809 | R1 unit resistor ohm/km | float32 | R/W | 2 | 0-10000 ohms | 0.056 | 0.056
| 0x2652 | 0x2653 | 9810 | 9811 | R2 unit resistor ohm/km | float32 | R/W | 2 | 0-10000 ohms | 0.056 | 0.056
| 0x2654 | 0x2655 | 9812 | 9813 | L1 length of line 1 km | float32 | R/W | 2 | 0-1000 km | 200km | 200km
| 0x2656 | 0x2657 | 9814 | 9815 | L2 length of line 1 km | float32 | R/W | 2 | 0-1000 km | 200km | 200km
| 0x2658 | 0x2659 | 9816 | 9817 | HighRatedVolt | float32 | R/W | 2 | 0-1e6 V | 230000 | 230000
| 0x265A | 0x265B | 9818 | 9819 | LowRatedVolt | float32 | R/W | 2 | 0-1e6 V | 115000 | 115000
| 0x265C | 0x265D | 9820 | 9821 | RatedApparentPower | float32 | R/W | 2 | 0-5000e6 VA | 50000000 | 50000000
| 0x265E | 0x265F | 9822 | 9823 | TapChanger | float32 | R/W | 2 | 0-100% | 10% | 10%
| 0x2660 | 0x2661 | 9824 | 9825 | RatedPFe | float32 | R/W | 2 | 0-5000e6 | 250000 | 250000
| 0x2662 | 0x2663 | 9826 | 9827 | RatedPCu | float32 | R/W | 2 | 0-5000e6 | 100000 | 100000
| 0x2664 | 0x2665 | 9828 | 9829 | ExciationRatio | float32 | R/W | 2 | 0-100% | 5% | 5%
| 0x2666 | 0x2667 | 9830 | 9831 | ImpedanceRatio | float32 | R/W | 2 | 0-100% | 6% | 6%
| 0x2668 | 0x2669 | 9832 | 9833 | PercentPFe | float32 | R/W | 2 | 0-100% | PercentPFe = 0.2% | 0.2%
| 0x266A | 0x266B | 9834 | 9835 | PercentPCu | float32 | R/W | 2 | 0-100% | PercentPCu = 0.5% | 0.5%
| 0x266C | 0x266D | 9836 | 9837 | PercentSFe | float32 | R/W | 2 | 0-100% | PercentSFe = 0.25% | 0.25%
| 0x266E | 0x266F | 9838 | 9839 | PercentSCu | float32 | R/W | 2 | 0-100% | PercentSCu = 0.55% | 0.55%
48
Transmission line loss output
| 0x2670 | 0x2671 | 9840 | 9841 | PhaseA Line 1 Active power | float32 | R | 2
| 0x2672 | 0x2673 | 9842 | 9843 | PhaseA Line 1 Reactive power | float32 | R | 2
| 0x2674 | 0x2675 | 9844 | 9845 | PhaseA Line 2 Active power | float32 | R | 2
| 0x2676 | 0x2677 | 9846 | 9847 | PhaseA Line 2 Reactive power | float32 | R | 2
| 0x2678 | 0x2679 | 9848 | 9849 | PhaseA Transformer Active power | float32 | R | 2
| 0x267A | 0x267B | 9850 | 9851 | PhaseA Transformer Reactive power | float32 | R | 2
| 0x267C | 0x267D | 9852 | 9853 | PhaseA Total Active power | float32 | R | 2
| 0x267E | 0x267F | 9854 | 9855 | PhaseA Total Reactive power | float32 | R | 2
| 0x2680 | 0x2681 | 9856 | 9857 | PhaseA Line 1 Active Energy | float32 | R | 2
| 0x2682 | 0x2683 | 9858 | 9859 | PhaseA Line 1 Reactive Energy | float32 | R | 2
| 0x2684 | 0x2685 | 9860 | 9861 | PhaseA Line 2 Active Energy | float32 | R | 2
| 0x2686 | 0x2687 | 9862 | 9863 | PhaseA Line 2 Reactive Energy | float32 | R | 2
| 0x2688 | 0x2689 | 9864 | 9865 | PhaseA Transformer Active Energy | float32 | R | 2
| 0x268A | 0x268B | 9866 | 9867 | PhaseA Transformer Reactive Energy | float32 | R | 2
| 0x268C | 0x268D | 9868 | 9869 | PhaseA Total Active Energy | float32 | R | 2
| 0x268E | 0x268F | 9870 | 9871 | PhaseA Total Reactive Energy | float32 | R | 2
| 0x2690 | 0x2691 | 9872 | 9873 | PhaseB Line 1 Active power | float32 | R | 2
| 0x2692 | 0x2693 | 9874 | 9875 | PhaseB Line 1 Reactive power | float32 | R | 2
| 0x2694 | 0x2695 | 9876 | 9877 | PhaseB Line 2 Active power | float32 | R | 2
| 0x2696 | 0x2697 | 9878 | 9879 | PhaseB Line 2 Reactive power | float32 | R | 2
| 0x2698 | 0x2699 | 9880 | 9881 | PhaseB Transformer Active power | float32 | R | 2
| 0x269A | 0x269B | 9882 | 9883 | PhaseB Transformer Reactive power | float32 | R | 2
| 0x269C | 0x269D | 9884 | 9885 | PhaseB Total Active power | float32 | R | 2
| 0x269E | 0x269F | 9886 | 9887 | PhaseB Total Reactive power | float32 | R | 2
| 0x26A0 | 0x26A1 | 9888 | 9889 | PhaseB Line 1 Active Energy | float32 | R | 2
| 0x26A2 | 0x26A3 | 9890 | 9891 | PhaseB Line 1 Reactive Energy | float32 | R | 2
| 0x26A4 | 0x26A5 | 9892 | 9893 | PhaseB Line 2 Active Energy | float32 | R | 2
| 0x26A6 | 0x26A7 | 9894 | 9895 | PhaseB Line 2 Reactive Energy | float32 | R | 2
| 0x26A8 | 0x26A9 | 9896 | 9897 | PhaseB Transformer Active Energy | float32 | R | 2
| 0x26AA | 0x26AB | 9898 | 9899 | PhaseB Transformer Reactive Energy | float32 | R | 2
| 0x26AC | 0x26AD | 9900 | 9901 | PhaseB Total Active Energy | float32 | R | 2
| 0x26AE | 0x26AF | 9902 | 9903 | PhaseB Total Reactive Energy | float32 | R | 2
| 0x26B0 | 0x26B1 | 9904 | 9905 | PhaseC Line 1 Active power | float32 | R | 2
| 0x26B2 | 0x26B3 | 9906 | 9907 | PhaseC Line 1 Reactive power | float32 | R | 2
| 0x26B4 | 0x26B5 | 9908 | 9909 | PhaseC Line 2 Active power | float32 | R | 2
| 0x26B6 | 0x26B7 | 9910 | 9911 | PhaseC Line 2 Reactive power | float32 | R | 2
| 0x26B8 | 0x26B9 | 9912 | 9913 | PhaseC Transformer Active power | float32 | R | 2
| 0x26BA | 0x26BB | 9914 | 9915 | PhaseC Transformer Reactive power | float32 | R | 2
| 0x26BC | 0x26BD | 9916 | 9917 | PhaseC Total Active power | float32 | R | 2
| 0x26BE | 0x26BF | 9918 | 9919 | PhaseC Total Reactive power | float32 | R | 2
| 0x26C0 | 0x26C1 | 9920 | 9921 | PhaseC Line 1 Active Energy | float32 | R | 2
| 0x26C2 | 0x26C3 | 9922 | 9923 | PhaseC Line 1 Reactive Energy | float32 | R | 2
| 0x26C4 | 0x26C5 | 9924 | 9925 | PhaseC Line 2 Active Energy | float32 | R | 2
| 0x26C6 | 0x26C7 | 9926 | 9927 | PhaseC Line 2 Reactive Energy | float32 | R | 2
| 0x26C8 | 0x26C9 | 9928 | 9929 | PhaseC Transformer Active Energy | float32 | R | 2
| 0x26CA | 0x26CB | 9930 | 9931 | PhaseC Transformer Reactive Energy | float32 | R | 2
| 0x26CC | 0x26CD | 9932 | 9933 | PhaseC Total Active Energy | float32 | R | 2
| 0x26CE | 0x26CF | 9934 | 9935 | PhaseC Total Reactive Energy | float32 | R | 2
| 0x26D0 | 0x26D1 | 9936 | 9937 | System Line 1 Active power | float32 | R | 2
| 0x26D2 | 0x26D3 | 9938 | 9939 | System Line 1 Reactive power | float32 | R | 2
| 0x26D4 | 0x26D5 | 9940 | 9941 | System Line 2 Active power | float32 | R | 2
| 0x26D6 | 0x26D7 | 9942 | 9943 | System Line 2 Reactive power | float32 | R | 2
| 0x26D8 | 0x26D9 | 9944 | 9945 | System Transformer Active power | float32 | R | 2
| 0x26DA | 0x26DB | 9946 | 9947 | System Transformer Reactive power | float32 | R | 2
| 0x26DC | 0x26DD | 9948 | 9949 | System Total Active power | float32 | R | 2
| 0x26DE | 0x26DF | 9950 | 9951 | System Total Reactive power | float32 | R | 2
| 0x26E0 | 0x26E1 | 9952 | 9953 | System Line 1 Active Energy | float32 | R | 2
| 0x26E2 | 0x26E3 | 9954 | 9955 | System Line 1 Reactive Energy | float32 | R | 2
| 0x26E4 | 0x26E5 | 9956 | 9957 | System Line 2 Active Energy | float32 | R | 2
| 0x26E6 | 0x26E7 | 9958 | 9959 | System Line 2 Reactive Energy | float32 | R | 2
| 0x26E8 | 0x26E9 | 9960 | 9961 | System Transformer Active Energy | float32 | R | 2
| 0x26EA | 0x26EB | 9962 | 9963 | System Transformer Reactive Energy | float32 | R | 2
| 0x26EC | 0x26ED | 9964 | 9965 | System Total Active Energy | float32 | R | 2
| 0x26EE | 0x26EF | 9966 | 9967 | System Total Reactive Energy | float32 | R | 2
128
Reset
| 0x26F0 | 0x26F0 | 9968 | 9968 | Reset energy | int16 | R | 1

## Independent Input Channel
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default Value | Factory Default
Basic Readings (word)
| 0x2400 |  | 9216 |  | Channel 4 Current | int16 | R | 1 | 0～65535
| 0x2401 |  | 9217 |  | Channel 4 Angle | int16 | R | 1 | -1800～1800
| 0x2402 |  | 9218 |  | Channel 4 Active Power | int16 | R | 1 | -32768～32767
| 0x2403 |  | 9219 |  | Channel 4 Reactive Power | int16 | R | 1 | -32768～32767
| 0x2404 |  | 9220 |  | Channel 4 Apparent Power | int16 | R | 1 | 0～65535
| 0x2405 |  | 9221 |  | Channel 4 PF | int16 | R | 1 | -1000～1000
| 0x2406 |  | 9222 |  | Channel 4 LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x2407 |  | 9223 |  | Channel 4 Current Demand | int16 | R | 1 | 0～65535
| 0x2408 |  | 9224 |  | Summation 2 Iavg | int16 | R | 1 | 0～65535
| 0x2409 |  | 9225 |  | Summation 2 P | int16 | R | 1 | -32768～32767
| 0x240A |  | 9226 |  | Summation 2 Q | int16 | R | 1 | -32768～32767
| 0x240B |  | 9227 |  | Summation 2 S | int16 | R | 1 | 0～65535
| 0x240C |  | 9228 |  | Summation 2 PF | int16 | R | 1 | -1000～1000
| 0x240D |  | 9229 |  | Summation 2 LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x240E |  | 9230 |  | Channel 1 LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x240F |  | 9231 |  | Channel 2 LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x2410 |  | 9232 |  | Channel 3 LN (L/C/R) | int16 | R | 1 | 76/67/82
| 0x2411 |  | 9233 |  | Channel 1 P demand | int16 | R | 1 | -32768～32767
| 0x2412 |  | 9234 |  | Channel 2 P Demand | int16 | R | 1 | -32768～32767
| 0x2413 |  | 9235 |  | Channel 3 P Demand | int16 | R | 1 | 0～65535
| 0x2414 |  | 9236 |  | Channel 4 P demand | int16 | R | 1 | -32768～32767
| 0x2415 |  | 9237 |  | Summation 2 P demand | int16 | R | 1 | -32768～32767
| 0x2416 |  | 9238 |  | Channel 1 Q Demand | int16 | R | 1 | -32768～32767
| 0x2417 |  | 9239 |  | Channel 2 Q Demand | int16 | R | 1 | 0～65535
| 0x2418 |  | 9240 |  | Channel 3 Q demand | int16 | R | 1 | -32768～32767
| 0x2419 |  | 9241 |  | Channel 4 Q Demand | int16 | R | 1 | -32768～32767
| 0x241A |  | 9242 |  | Summation 2 Q Demand | int16 | R | 1 | -32768～32767
| 0x241B |  | 9243 |  | Channel 1 S Demand | int16 | R | 1 | 0～65535
| 0x241C |  | 9244 |  | Channel 2 S demand | int16 | R | 1 | -32768～32767
| 0x241D |  | 9245 |  | Channel 3 S Demand | int16 | R | 1 | -32768～32767
| 0x241E |  | 9246 |  | Channel 4 S Demand | int16 | R | 1 | 0～65535
| 0x241F |  | 9247 |  | Summation 2 S Demand | int16 | R | 1 | 0～65535
Energy
| 0x2500 | 0x2501 | 9472 | 9473 | Channel 4 Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x2502 | 0x2503 | 9474 | 9475 | Channel 4 Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x2504 | 0x2505 | 9476 | 9477 | Channel 4 Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x2506 | 0x2507 | 9478 | 9479 | Channel 4 Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x2508 | 0x2509 | 9480 | 9481 | Channel 4 Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x250A | 0x250B | 9482 | 9483 | Channel 4 Es_exp | uint32 | R/W | 2 | 0～999999999
| 0x250C | 0x250D | 9484 | 9485 | Channel 4 Es_total | uint32 | R/W | 2 | 0～999999999
| 0x250E | 0x250F | 9486 | 9487 | Channel 4 Eq_q1 | uint32 | R/W | 2 | 0～999999999
| 0x2510 | 0x2511 | 9488 | 9489 | Channel 4 Eq_q2 | uint32 | R/W | 2 | 0～999999999
| 0x2512 | 0x2513 | 9490 | 9491 | Channel 4 Eq_q3 | uint32 | R/W | 2 | 0～999999999
| 0x2514 | 0x2515 | 9492 | 9493 | Channel 4 Eq_q4 | uint32 | R/W | 2 | 0～999999999
| 0x2516 | 0x2517 | 9494 | 9495 | Summation 2 Ep_imp | uint32 | R/W | 2 | 0～999999999
| 0x2518 | 0x2519 | 9496 | 9497 | Summation 2 Ep_exp | uint32 | R/W | 2 | 0～999999999
| 0x251A | 0x251B | 9498 | 9499 | Summation 2 Ep_total | uint32 | R/W | 2 | 0～999999999
| 0x251C | 0x251D | 9500 | 9501 | Summation 2 Ep_net | int32 | R/W | 2 | -999999999～999999999
| 0x251E | 0x251F | 9502 | 9503 | Summation 2 Eq_imp | uint32 | R/W | 2 | 0～999999999
| 0x2520 | 0x2521 | 9504 | 9505 | Summation 2 Eq_exp | uint32 | R/W | 2 | 0～999999999
| 0x2522 | 0x2523 | 9506 | 9507 | Summation 2 Eq_total | uint32 | R/W | 2 | 0～999999999
| 0x2524 | 0x2525 | 9508 | 9509 | Summation 2 Eq_net | int32 | R/W | 2 | -999999999～999999999
| 0x2526 | 0x2527 | 9510 | 9511 | Summation 2 Es_imp | uint32 | R/W | 2 | 0～999999999
| 0x2528 | 0x2529 | 9512 | 9513 | Summation 2 ES_exp | uint32 | R/W | 2 | 0～999999999
| 0x252A | 0x252B | 9514 | 9515 | Summation 2 Es_total | uint32 | R/W | 2 | 0～999999999
| 0x252C | 0x252D | 9516 | 9517 | Summation 2 Es_net | int32 | R/W | 2 | -999999999～999999999
| 0x252E | 0x252F | 9518 | 9519 | Summation 2 Ep_q1 | uint32 | R/W | 2 | 0～999999999
| 0x2530 | 0x2531 | 9520 | 9521 | Summation 2 Ep_q2 | uint32 | R/W | 2 | 0～999999999
| 0x2532 | 0x2533 | 9522 | 9523 | Summation 2 Ep_q3 | uint32 | R/W | 2 | 0～999999999
| 0x2534 | 0x2535 | 9524 | 9525 | Summation 2 Ep_q4 | uint32 | R/W | 2 | 0～999999999
| 0x2536 | 0x2537 | 9526 | 9527 | Summation 2 Eq_q1 | uint32 | R/W | 2 | 0～999999999
| 0x2538 | 0x2539 | 9528 | 9529 | Summation 2 Eq_q2 | uint32 | R/W | 2 | 0～999999999
| 0x253A | 0x253B | 9530 | 9531 | Summation 2 Eq_q3 | uint32 | R/W | 2 | 0～999999999
| 0x253C | 0x253D | 9532 | 9533 | Summation 2 Eq_q4 | uint32 | R/W | 2 | 0～999999999
| 0x253E | 0x253F | 9534 | 9535 | Summation 2 Es_q1 | uint32 | R/W | 2 | 0～999999999
| 0x2540 | 0x2541 | 9536 | 9537 | Summation 2 Es_q2 | uint32 | R/W | 2 | 0～999999999
| 0x2542 | 0x2543 | 9538 | 9539 | Summation 2 Es_q3 | uint32 | R/W | 2 | 0～999999999
| 0x2544 | 0x2545 | 9540 | 9541 | Summation 2 Es_q4 | uint32 | R/W | 2 | 0～999999999
Basic Readings (Float)
| 0x2600 | 0x2601 | 9728 | 9729 | Channel 4 Current | float32 | R | 2
| 0x2602 | 0x2603 | 9730 | 9731 | Channel 4 Angle | float32 | R | 2
| 0x2604 | 0x2605 | 9732 | 9733 | Channel 4 Active Power | float32 | R | 2
| 0x2606 | 0x2607 | 9734 | 9735 | Channel 4 Reactive Power | float32 | R | 2
| 0x2608 | 0x2609 | 9736 | 9737 | Channel 4 Apparent Power | float32 | R | 2
| 0x260A | 0x260B | 9738 | 9739 | Channel 4 PF | float32 | R | 2
| 0x260C | 0x260D | 9740 | 9741 | Channel 4 LN (L/C/R) | float32 | R | 2
| 0x260E | 0x260F | 9742 | 9743 | Channel 4 Current Demand | float32 | R | 2
| 0x2610 | 0x2611 | 9744 | 9745 | Summation 2 Iavg | float32 | R | 2
| 0x2612 | 0x2613 | 9746 | 9747 | Summation 2 P | float32 | R | 2
| 0x2614 | 0x2615 | 9748 | 9749 | Summation 2 Q | float32 | R | 2
| 0x2616 | 0x2617 | 9750 | 9751 | Summation 2 S | float32 | R | 2
| 0x2618 | 0x2619 | 9752 | 9753 | Summation 2 PF | float32 | R | 2
| 0x261A | 0x261B | 9754 | 9755 | Summation 2 LN (L/C/R) | float32 | R | 2
| 0x261C | 0x261D | 9756 | 9757 | Channel 1 LN (L/C/R) | float32 | R | 2
| 0x261E | 0x261F | 9758 | 9759 | Channel 2 LN (L/C/R) | float32 | R | 2
| 0x2620 | 0x2621 | 9760 | 9761 | Channel 3 LN (L/C/R) | float32 | R | 2
| 0x2622 | 0x2623 | 9762 | 9763 | Channel 1 P demand | float32 | R | 2
| 0x2624 | 0x2625 | 9764 | 9765 | Channel 2 P Demand | float32 | R | 2
| 0x2626 | 0x2627 | 9766 | 9767 | Channel 3 P Demand | float32 | R | 2
| 0x2628 | 0x2629 | 9768 | 9769 | Channel 4 P demand | float32 | R | 2
| 0x262A | 0x262B | 9770 | 9771 | Summation 2 P demand | float32 | R | 2
| 0x262C | 0x262D | 9772 | 9773 | Channel 1 Q Demand | float32 | R | 2
| 0x262E | 0x262F | 9774 | 9775 | Channel 2 Q Demand | float32 | R | 2
| 0x2630 | 0x2631 | 9776 | 9777 | Channel 3 Q demand | float32 | R | 2
| 0x2632 | 0x2633 | 9778 | 9779 | Channel 4 Q Demand | float32 | R | 2
| 0x2634 | 0x2635 | 9780 | 9781 | Summation 2 Q Demand | float32 | R | 2
| 0x2636 | 0x2637 | 9782 | 9783 | Channel 1 S Demand | float32 | R | 2
| 0x2638 | 0x2639 | 9784 | 9785 | Channel 2 S demand | float32 | R | 2
| 0x263A | 0x263B | 9786 | 9787 | Channel 3 S Demand | float32 | R | 2
| 0x263C | 0x263D | 9788 | 9789 | Channel 4 S Demand | float32 | R | 2
| 0x263E | 0x263F | 9790 | 9791 | Summation 2 S Demand | float32 | R | 2
Harmonics（3S）
| 0x5220 |  | 21024 |  | Channel 4 current THD | int16 | R | 1
| 0x5221 | 0x523E | 21025 | 21054 | Channel 4 current 2nd-31st harmonic | int16 | R | 30
| 0x523F |  | 21055 |  | Channel 4 current odd THD | int16 | R | 1
| 0x5240 |  | 21056 |  | Channel 4 current even THD | int16 | R | 1
| 0x5241 |  | 21057 |  | Channel 4 current K factor | int16 | R | 1
| 0x5242 | 0x5261 | 21058 | 21089 | Channel 4 current 32nd-63rd harmonic | int16 | R | 32
Harmonic amplitude and phase angle (secondary side)
| 0x5262 | 0x529F | 21090 | 21151 | Channel 4 current harmonic amplitude (2nd - 63st) | int16 | R | 62 | Actual current I = reading data / 1000
| 0x52A0 | 0x52DD | 21152 | 21213 | Channel 4 current Harmonic phase angle (2nd - 63rd） | int16 | R | 62 | Actual phase angle = reading data / 10

## Dual Source Energy
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Dual Source Energy Settings
| 0x1680 | 0x1680 | 5760 | 5760 | Dual source energy enable/disable | word | R/W | 1 | 0: Disabled; 1: Enabled | 0 | 0
| 0x1681 | 0x1681 | 5761 | 5761 | Energy 1 selection | word | R/W | 1 | 0: Not selected 1: Active energy 2: Phase A active energy 3: Phase B active energy 4: Phase C active energy 5: Reactive energy 6: Phase A reactive energy 7: Phase B reactive energy 8: Phase C reactive energy 9: Apparent energy 10: Phase A apparent energy 11: Phase B apparent energy 12: Phase C apparent energy | 0 | 0
| 0x1682 | 0x1682 | 5762 | 5762 | Energy 2 selection | word | R/W | 1 |  | 0 | 0
| 0x1683 | 0x1683 | 5763 | 5763 | Energy 3 selection | word | R/W | 1 |  | 0 | 0
| 0x1684 | 0x1684 | 5764 | 5764 | Control mode | word | R/W | 1 | 0: Controlled by communication 1 ~ 28: Controlled by DI1-DI28 | 0 | 0
| 0x1685 | 0x1685 | 5765 | 5765 | Direction flag | word | R/W | 1 | When control mode is controlled by commnication, the value is writeable via communication; when control mode is controlled by DI, the value is readonly. 0: grid direction; 1: generator direction. | 0 | 0
| 0x1686 | 0x1686 | 5766 | 5766 | clear Dual Source energy | word | R/W | 1 | write 1 to clear | 0 | 0
| 0x1687 | 0x1687 | 5767 | 5767 | clear Dual Source energy switching record | word | R/W | 1 | write 1 to clear | 0 | 0
Dual Source Energy Readings
| 0x4930 | 0x4931 | 18736 | 18737 | Energy 1 - Grid Direction | uint32 | R | 2
| 0x4932 | 0x4933 | 18738 | 18739 | Energy 1 - Generator Direction | uint32 | R | 2
| 0x4934 | 0x4935 | 18740 | 18741 | Energy 2 - Grid Direction | uint32 | R | 2
| 0x4936 | 0x4937 | 18742 | 18743 | Energy 2 - Generator Direction | uint32 | R | 2
| 0x4938 | 0x4939 | 18744 | 18745 | Energy 3 - Grid Direction | uint32 | R | 2
| 0x493A | 0x493B | 18746 | 18747 | Energy 3 - Generator Direction | uint32 | R | 2
Dual Source Energy switching records
| 0x6D00 | 0x6D00 | 27904 | 27904 | the number of records to read | word | R/W | 1 | 1 to 20 | 0 | 0
| 0x6D01 | 0x6D01 | 27905 | 27905 | The ID of current switching record | word | R | 1 | 0 to 20 | 0 | 0
| 0x6D02 | 0x6D02 | 27906 | 27906 | The length of bytes that can be read by the current window | word | R | 1 | 0 to 85; 0: the window data is invalid. | 0 | 0
| 0x6D03 | 0x6D03 | 27907 | 27907 | 1st switch record - timestamp year&month | word | R | 1 | High byte: year Low byte: month
| 0x6D04 | 0x6D04 | 27908 | 27908 | 1st switch record - timestamp date&hour | word | R | 1 | High byte: date Low byte: hour
| 0x6D05 | 0x6D05 | 27909 | 27909 | 1st switch record - timestamp minute&second | word | R | 1 | High byte: minute Low byte: second
| 0x6D06 | 0x6D06 | 27910 | 27910 | 1st switch record - switch command source | word | R | 1 | 0: Controlled by communication 1 ~ 28: Controlled by DI1-DI28
| 0x6D07 | 0x6D07 | 27911 | 27911 | 1st switch record - switch command | word | R | 1 | 0: grid direction, 1: generator direction
| 0x6D08 | 0x6D09 | 27912 | 27913 | 1st Switch Record - Energy 1 - Grid Direction | word | R | 2
| 0x6D0A | 0x6D0B | 27914 | 27915 | 1st Switch Record - Energy 1 - Generator Direction | word | R | 2
| 0x6D0C | 0x6D0D | 27916 | 27917 | 1st Switch Record - Energy 2 - Grid Direction | word | R | 2
| 0x6D0E | 0x6D0F | 27918 | 27919 | 1st Switch Record - Energy 2 - Generator Direction | word | R | 2
| 0x6D10 | 0x6D11 | 27920 | 27921 | 1st Switch Record - Energy 3 - Grid Direction | word | R | 2
| 0x6D12 | 0x6D13 | 27922 | 27923 | 1st Switch Record - Energy 3 - Generator Direction | word | R | 2
| 0x6D14 | 0x6D24 | 27924 | 27940 | 2nd switch record data | word | R | 17
| 0x6D25 | 0x6D35 | 27941 | 27957 | 3rd switch record data | word | R | 17
| 0x6D36 | 0x6D46 | 27958 | 27974 | 4th switch record data | word | R | 17
| 0x6D47 | 0x6D57 | 27975 | 27991 | 5th switch record data | word | R | 17

## Data Log 1,2,3
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Data log Setting
| 0x1100 |  | 4352 |  | Log1 number of registers and number of sectors |  | R/W | 1
| 0x1101 |  | 4353 |  | Log1 Interval |  | R/W | 1
| 0x1102 | 0x1176 | 4354 | 4470 | Log1 parameter selections (up to 117 parameters) |  | R/W | 117
| 0x1177 | 0x11B1 | 4471 | 4529 | Log1 register #1-#117 descriptors |  | R/W | 59 | Currently not in use
| 0x11B2 |  | 4530 |  | Data log mode selection |  | R/W | 1
| 0x11B3 |  | 4531 |  | Start month, year |  | R/W | 1
| 0x11B4 |  | 4532 |  | Start day, hour |  | R/W | 1
| 0x11B5 |  | 4533 |  | Start minute, second |  | R/W | 1
| 0x11B6 |  | 4534 |  | End month, year |  | R/W | 1
| 0x11B7 |  | 4535 |  | End day, hour |  | R/W | 1
| 0x11B8 |  | 4536 |  | End minute, second |  | R/W | 1
| 0x11B9 |  | 4537 |  | Clear Data Log 1 |  | R/W | 1 | write 1 to clear
| 0x11C0 | 0x1279 | 4544 | 4729 | Log2 setting |  | R/W | 186
| 0x1280 | 0x1339 | 4736 | 4921 | Log3 setting |  | R/W | 186
Data log Reading
| 0x6000 |  | 24576 |  | Record type, enable, state |  | R/W | 1
| 0x6001 |  | 24577 |  | Record number of each window+window state |  | R/W | 1
| 0x6002 | 0x6003 | 24578 | 24579 | OFFSET |  | R/W | 2
| 0x6004 | 0x607E | 24580 | 24702 | Window |  | R | 123
Data log Status
| 0x6100 | 0x6101 | 24832 | 24833 | Max Records | uint32 | R | 2
| 0x6102 | 0x6103 | 24834 | 24835 | Used Records | uint32 | R | 2
| 0x6104 |  | 24836 |  | Record size | uint16 | R | 1
| 0x6105 |  | 24837 |  | Log Availability（reserve） | word | R | 1
| 0x6106 | 0x6108 | 24838 | 24840 | First Record Time stamp | word | R | 3
| 0x6109 | 0x610B | 24841 | 24843 | Last Record Time stamp |  |  | 3
| 0x6200 | 0x6201 | 25088 | 25089 | Max Records | word | R | 2
| 0x6202 | 0x6203 | 25090 | 25091 | Used Records |  |  | 2
| 0x6204 | 0x0000 | 25092 |  | Recordsize | uint32 | R | 1
| 0x6205 | 0x0000 | 25093 |  | Log Availability | uint32 | R | 1
| 0x6206 | 0x6208 | 25094 | 25096 | FirstRecordTimestamp | uint16 | R | 3
| 0x6209 | 0x620B | 25097 | 25099 | LastRecordTimestamp | word | R | 3
| 0x6300 | 0x6301 | 25344 | 25345 | Max Records | word | R | 2
| 0x6302 | 0x6303 | 25346 | 25347 | Used Records | word | R | 2
| 0x6304 |  | 25348 |  | Record size | uint32 | R | 1
| 0x6305 |  | 25349 |  | Log Availability | uint32 | R | 1
| 0x6306 | 0x6308 | 25350 | 25352 | First Record Time stamp | uint16 | R | 3
| 0x6309 | 0x630B | 25353 | 25355 | Last Record Time stamp, | word | R | 3

## Data Log 4
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Data Log settings
| 0x1500 |  | 5376 |  | Log1 number of registers and number of sectors |  | R/W | 1 | 0 -39;50 | 0 | 0
| 0x1501 |  | 5377 |  | Log1 Interval |  | R/W | 1 | 1 - 1440 | 0 | 0
| 0x1502 | 0x1576 | 5378 | 5494 | Log1 parameter selections (up to 117 parameters) |  | R/W | 117 | Parameter selection address Range: 0x4000 - 0x4041 (not include demand) 0x405A - 0x412A 0x4294 - 0x42A8 0x4381 - 0x4398 0x4500 - 0x45BF | 0 | 0
| 0x1577 | 0x15B1 | 5495 | 5553 | register #1-#117 descriptors |  | R/W | 59 |  | 0 | 0
| 0x15B2 |  | 5554 |  | Data log mode selection |  | R/W | 1 | 0 - 2 | 0 | 0
| 0x15B3 |  | 5555 |  | Start month, year |  | R/W | 1 | Low byte: month,high byte: year（keep consistence with Data Log123）
| 0x15B4 |  | 5556 |  | Start day, hour |  | R/W | 1 | Low byte: houe,high byte: day
| 0x15B5 |  | 5557 |  | Start minute, second |  | R/W | 1 | Low byte: second,high byte: minute
| 0x15B6 |  | 5558 |  | End month, year |  | R/W | 1 | Low byte: month,high byte: year
| 0x15B7 |  | 5559 |  | End day, hour |  | R/W | 1 | Low byte: houe,high byte: day
| 0x15B8 |  | 5560 |  | End minute, second |  | R/W | 1 | Low byte: second,high byte: minute
| 0x15B9 |  | 5561 |  | Clear Data Log 4 |  | R/W | 1 | write 1 to clear | 0 | 0
Data Log reading
| 0x6400 |  | 25600 |  | Record type, enable, state |  | R/W | 1 | 0 - 3 （3 for Data Log4） | 0 | 0
| 0x6401 |  | 25601 |  | Record number of each window+window state |  | R/W | 1 | High byte: Record number of window（setting）。 Low byte: window state（0x0B: data effective,0xFF: data not effective,0xAA: Data Log on clearing,0xBB: Data Log clearing end）
| 0x6402 | 0x6403 | 25602 | 25603 | OFFSET |  | R/W | 2
| 0x6404 | 0x647E | 25604 | 25726 | Window |  | R | 123 | Data Log format: record number（4bytes ）+ time stamps（6bytes） + [data1~dataN]（6Nbytes） + CRC( 2bytes)。 Data format: parameter1 average value, parameter2 average value...parameter1 max value, parameter2 max value, parameter1 min value, parameter2 min value...
Data Log status
| 0x6500 | 0x6501 | 25856 | 25857 | Max Records | uint32 | R | 2 | 0 - 468104
| 0x6502 | 0x6503 | 25858 | 25859 | Used Records | uint32 | R | 2 | 1 - 468104
| 0x6504 |  | 25860 |  | Recordsize | uint16 | R | 1 | 18 - 714
| 0x6505 |  | 25861 |  | Log Availability（reserve） | word | R | 1
| 0x6506 | 0x6508 | 25862 | 25864 | First Record Time stamp | word | R | 3
| 0x6509 | 0x650B | 25865 | 25867 | Last Record Time stamp |  | R | 3
note: max records of Data Log4 = 65536 / (number of register * 6 + 12) * sector number (fixed to 50 at present)

## Max,Min
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Max value record
| 0x4136 |  | 16694 |  | Max of V1 | int16 | R | 1
| 0x4137 | 0x413C | 16695 | 16700 | Time Stamp | int16 | R | 6
| 0x413D |  | 16701 |  | Max of V2 | int16 | R | 1
| 0x413E | 0x4143 | 16702 | 16707 | Time Stamp | int16 | R | 6
| 0x4144 |  | 16708 |  | Max of V3 | int16 | R | 1
| 0x4145 | 0x414A | 16709 | 16714 | Time Stamp | int16 | R | 6
| 0x414B |  | 16715 |  | Max of V12 | int16 | R | 1
| 0x414C | 0x4151 | 16716 | 16721 | Time Stamp | int16 | R | 6
| 0x4152 |  | 16722 |  | Max of V23 | int16 | R | 1
| 0x4153 | 0x4158 | 16723 | 16728 | Time Stamp | int16 | R | 6
| 0x4159 |  | 16729 |  | Max of V31 | int16 | R | 1
| 0x415A | 0x415F | 16730 | 16735 | Time Stamp | int16 | R | 6
| 0x4160 |  | 16736 |  | Max of I1 | int16 | R | 1
| 0x4161 | 0x4166 | 16737 | 16742 | Time Stamp | int16 | R | 6
| 0x4167 |  | 16743 |  | Max of I2 | int16 | R | 1
| 0x4168 | 0x416D | 16744 | 16749 | Time Stamp | int16 | R | 6
| 0x416E |  | 16750 |  | Max of I3 | int16 | R | 1
| 0x416F | 0x4174 | 16751 | 16756 | Time Stamp | int16 | R | 6
| 0x4175 |  | 16757 |  | Max of System Power | int16 | R | 1
| 0x4176 | 0x417B | 16758 | 16763 | Time Stamp | int16 | R | 6
| 0x417C |  | 16764 |  | Max of Reactive Power | int16 | R | 1
| 0x417D | 0x4182 | 16765 | 16770 | Time Stamp | int16 | R | 6
| 0x4183 |  | 16771 |  | Max of Apparent Power | int16 | R | 1
| 0x4184 | 0x4189 | 16772 | 16777 | Time Stamp | int16 | R | 6
| 0x418A |  | 16778 |  | Max of Power Factor | int16 | R | 1
| 0x418B | 0x4190 | 16779 | 16784 | Time Stamp | int16 | R | 6
| 0x4191 |  | 16785 |  | Max of Frequency | int16 | R | 1
| 0x4192 | 0x4197 | 16786 | 16791 | Time Stamp | int16 | R | 6
| 0x4198 |  | 16792 |  | Max of Power Demand | int16 | R | 1
| 0x4199 | 0x419E | 16793 | 16798 | Time Stamp | int16 | R | 6
| 0x419F |  | 16799 |  | Max of Reactive power demand | int16 | R | 1
| 0x41A0 | 0x41A5 | 16800 | 16805 | Time Stamp | int16 | R | 6
| 0x41A6 |  | 16806 |  | Max of Apparent power demand | int16 | R | 1
| 0x41A7 | 0x41AC | 16807 | 16812 | Time Stamp | int16 | R | 6
| 0x41AD |  | 16813 |  | Max of Voltage unbalance | int16 | R | 1
| 0x41AE | 0x41B3 | 16814 | 16819 | Time Stamp | int16 | R | 6
| 0x41B4 |  | 16820 |  | Max of Current unbalance | int16 | R | 1
| 0x41B5 | 0x41BA | 16821 | 16826 | Time Stamp | int16 | R | 6
| 0x41BB |  | 16827 |  | Max of THD_V1(V12) | int16 | R | 1
| 0x41BC | 0x41C1 | 16828 | 16833 | Time Stamp | int16 | R | 6
| 0x41C2 |  | 16834 |  | Max of THD_V2(V31) | int16 | R | 1
| 0x41C3 | 0x41C8 | 16835 | 16840 | Time Stamp | int16 | R | 6
| 0x41C9 |  | 16841 |  | Max of THD_V3(V23) | int16 | R | 1
| 0x41CA | 0x41CF | 16842 | 16847 | Time Stamp | int16 | R | 6
| 0x41D0 |  | 16848 |  | Max of THD_I1 | int16 | R | 1
| 0x41D1 | 0x41D6 | 16849 | 16854 | Time Stamp | int16 | R | 6
| 0x41D7 |  | 16855 |  | Max of THD_I2 | int16 | R | 1
| 0x41D8 | 0x41DD | 16856 | 16861 | Time Stamp | int16 | R | 6
| 0x41DE |  | 16862 |  | Max of THD_I3 | int16 | R | 1
| 0x41DF | 0x41E4 | 16863 | 16868 | Time Stamp | int16 | R | 6
Min value record
| 0x41E5 |  | 16869 |  | Min of V1 | int16 | R | 1
| 0x41E6 | 0x41EB | 16870 | 16875 | Time Stamp | int16 | R | 6
| 0x41EC |  | 16876 |  | Min of V2 | int16 | R | 1
| 0x41ED | 0x41F2 | 16877 | 16882 | Time Stamp | int16 | R | 6
| 0x41F3 |  | 16883 |  | Min of V3 | int16 | R | 1
| 0x41F4 | 0x41F9 | 16884 | 16889 | Time Stamp | int16 | R | 6
| 0x41FA |  | 16890 |  | Min of V12 | int16 | R | 1
| 0x41FB | 0x4200 | 16891 | 16896 | Time Stamp | int16 | R | 6
| 0x4201 |  | 16897 |  | Min of V23 | int16 | R | 1
| 0x4202 | 0x4207 | 16898 | 16903 | Time Stamp | int16 | R | 6
| 0x4208 |  | 16904 |  | Min of V31 | int16 | R | 1
| 0x4209 | 0x420E | 16905 | 16910 | Time Stamp | int16 | R | 6
| 0x420F |  | 16911 |  | Min of I1 | int16 | R | 1
| 0x4210 | 0x4215 | 16912 | 16917 | Time Stamp | int16 | R | 6
| 0x4216 |  | 16918 |  | Min of I2 | int16 | R | 1
| 0x4217 | 0x421C | 16919 | 16924 | Time Stamp | int16 | R | 6
| 0x421D |  | 16925 |  | Min of I3 | int16 | R | 1
| 0x421E | 0x4223 | 16926 | 16931 | Time Stamp | int16 | R | 6
| 0x4224 |  | 16932 |  | Min of System Power | int16 | R | 1
| 0x4225 | 0x422A | 16933 | 16938 | Time Stamp | int16 | R | 6
| 0x422B |  | 16939 |  | Min of Reactive Power | int16 | R | 1
| 0x422C | 0x4231 | 16940 | 16945 | Time Stamp | int16 | R | 6
| 0x4232 |  | 16946 |  | Min of Apparent Power | int16 | R | 1
| 0x4233 | 0x4238 | 16947 | 16952 | Time Stamp | int16 | R | 6
| 0x4239 |  | 16953 |  | Min of Power Factor | int16 | R | 1
| 0x423A | 0x423F | 16954 | 16959 | Time Stamp | int16 | R | 6
| 0x4240 |  | 16960 |  | Min of Frequency | int16 | R | 1
| 0x4241 | 0x4246 | 16961 | 16966 | Time Stamp | int16 | R | 6
| 0x4247 |  | 16967 |  | Min of Power Demand | int16 | R | 1
| 0x4248 | 0x424D | 16968 | 16973 | Time Stamp | int16 | R | 6
| 0x424E |  | 16974 |  | Min of Reactive power demand | int16 | R | 1
| 0x424F | 0x4254 | 16975 | 16980 | Time Stamp | int16 | R | 6
| 0x4255 |  | 16981 |  | Min of Apparent power demand | int16 | R | 1
| 0x4256 | 0x425B | 16982 | 16987 | Time Stamp | int16 | R | 6
| 0x425C |  | 16988 |  | Min of Voltage unbalance | int16 | R | 1
| 0x425D | 0x4262 | 16989 | 16994 | Time Stamp | int16 | R | 6
| 0x4263 |  | 16995 |  | Min of Current unbalance | int16 | R | 1
| 0x4264 | 0x4269 | 16996 | 17001 | Time Stamp | int16 | R | 6
| 0x426A |  | 17002 |  | Min of THD_V1(V12) | int16 | R | 1
| 0x426B | 0x4270 | 17003 | 17008 | Time Stamp | int16 | R | 6
| 0x4271 |  | 17009 |  | Min of THD_V2(V31) | int16 | R | 1
| 0x4272 | 0x4277 | 17010 | 17015 | Time Stamp | int16 | R | 6
| 0x4278 |  | 17016 |  | Min of THD_V3(V23) | int16 | R | 1
| 0x4279 | 0x427E | 17017 | 17022 | Time Stamp | int16 | R | 6
| 0x427F |  | 17023 |  | Min of THD_I1 | int16 | R | 1
| 0x4280 | 0x4285 | 17024 | 17029 | Time Stamp | int16 | R | 6
| 0x4286 |  | 17030 |  | Min of THD_I2 | int16 | R | 1
| 0x4287 | 0x428C | 17031 | 17036 | Time Stamp | int16 | R | 6
| 0x428D |  | 17037 |  | Min of THD_I3 | int16 | R | 1
| 0x428E | 0x4293 | 17038 | 17043 | Time Stamp | int16 | R | 6
| 0x4606 |  | 17926 |  | Max of Phase A current demand | int16 | R | 1
| 0x4607 | 0x460C | 17927 | 17932 | Time Stamp | int16 | R | 6
| 0x460D |  | 17933 | 17933 | Max of Phase B current demand | int16 | R | 1
| 0x460E | 0x4613 | 17934 | 17939 | Time Stamp | int16 | R | 6
| 0x4614 |  | 17940 | 17940 | Max of Phase C current demand | int16 | R | 1
| 0x4615 | 0x461A | 17941 | 17946 | Time Stamp | int16 | R | 6

## Max,Min(float)
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Max value record
| 0x5000 |  | 20480 |  | Max of V1 | float32 | R | 2
| 0x5002 | 0x5007 | 20482 | 20487 | Time Stamp | int16 | R | 6
| 0x5008 |  | 20488 |  | Max of V2 | float32 | R | 2
| 0x500A | 0x500F | 20490 | 20495 | Time Stamp | int16 | R | 6
| 0x5010 |  | 20496 |  | Max of V3 | float32 | R | 2
| 0x5012 | 0x5017 | 20498 | 20503 | Time Stamp | int16 | R | 6
| 0x5018 |  | 20504 |  | Max of V12 | float32 | R | 2
| 0x501A | 0x501F | 20506 | 20511 | Time Stamp | int16 | R | 6
| 0x5020 |  | 20512 |  | Max of V23 | float32 | R | 2
| 0x5022 | 0x5027 | 20514 | 20519 | Time Stamp | int16 | R | 6
| 0x5028 |  | 20520 |  | Max of V31 | float32 | R | 2
| 0x502A | 0x502F | 20522 | 20527 | Time Stamp | int16 | R | 6
| 0x5030 |  | 20528 |  | Max of I1 | float32 | R | 2
| 0x5032 | 0x5037 | 20530 | 20535 | Time Stamp | int16 | R | 6
| 0x5038 |  | 20536 |  | Max of I2 | float32 | R | 2
| 0x503A | 0x503F | 20538 | 20543 | Time Stamp | int16 | R | 6
| 0x5040 |  | 20544 |  | Max of I3 | float32 | R | 2
| 0x5042 | 0x5047 | 20546 | 20551 | Time Stamp | int16 | R | 6
| 0x5048 |  | 20552 |  | Max of System Power | float32 | R | 2
| 0x504A | 0x504F | 20554 | 20559 | Time Stamp | int16 | R | 6
| 0x5050 |  | 20560 |  | Max of Reactive Power | float32 | R | 2
| 0x5052 | 0x5057 | 20562 | 20567 | Time Stamp | int16 | R | 6
| 0x5058 |  | 20568 |  | Max of Apparent Power | float32 | R | 2
| 0x505A | 0x505F | 20570 | 20575 | Time Stamp | int16 | R | 6
| 0x5060 |  | 20576 |  | Max of Power Factor | float32 | R | 2
| 0x5062 | 0x5067 | 20578 | 20583 | Time Stamp | int16 | R | 6
| 0x5068 |  | 20584 |  | Max of Frequency | float32 | R | 2
| 0x506A | 0x506F | 20586 | 20591 | Time Stamp | int16 | R | 6
| 0x5070 |  | 20592 |  | Max of Power Demand | float32 | R | 2
| 0x5072 | 0x5077 | 20594 | 20599 | Time Stamp | int16 | R | 6
| 0x5078 |  | 20600 |  | Max of Reactive power demand | float32 | R | 2
| 0x507A | 0x507F | 20602 | 20607 | Time Stamp | int16 | R | 6
| 0x5080 |  | 20608 |  | Max of Apparent power demand | float32 | R | 2
| 0x5082 | 0x5087 | 20610 | 20615 | Time Stamp | int16 | R | 6
| 0x5088 |  | 20616 |  | Max of Voltage unbalance | float32 | R | 2
| 0x508A | 0x508F | 20618 | 20623 | Time Stamp | int16 | R | 6
| 0x5090 |  | 20624 |  | Max of Current unbalance | float32 | R | 2
| 0x5092 | 0x5097 | 20626 | 20631 | Time Stamp | int16 | R | 6
| 0x5098 |  | 20632 |  | Max of THD_V1(V12) | float32 | R | 2
| 0x509A | 0x509F | 20634 | 20639 | Time Stamp | int16 | R | 6
| 0x50A0 |  | 20640 |  | Max of THD_V2(V31) | float32 | R | 2
| 0x50A2 | 0x50A7 | 20642 | 20647 | Time Stamp | int16 | R | 6
| 0x50A8 |  | 20648 |  | Max of THD_V3(V23) | float32 | R | 2
| 0x50AA | 0x50AF | 20650 | 20655 | Time Stamp | int16 | R | 6
| 0x50B0 |  | 20656 |  | Max of THD_I1 | float32 | R | 2
| 0x50B2 | 0x50B7 | 20658 | 20663 | Time Stamp | int16 | R | 6
| 0x50B8 |  | 20664 |  | Max of THD_I2 | float32 | R | 2
| 0x50BA | 0x50BF | 20666 | 20671 | Time Stamp | int16 | R | 6
| 0x50C0 |  | 20672 |  | Max of THD_I3 | float32 | R | 2
| 0x50C2 | 0x50C7 | 20674 | 20679 | Time Stamp | int16 | R | 6
| 0x50C8 |  | 20680 |  | Max of Phase A current demand | float32 | R | 2
| 0x50CA | 0x50CF | 20682 | 20687 | Time Stamp | int16 | R | 6
| 0x50D0 |  | 20688 | 20689 | Max of Phase B current demand | float32 | R | 2
| 0x50D2 | 0x50D7 | 20690 | 20695 | Time Stamp | int16 | R | 6
| 0x50D8 |  | 20696 | 20697 | Max of Phase C current demand | float32 | R | 2
| 0x50DA | 0x50DF | 20698 | 20703 | Time Stamp | int16 | R | 6
Min value record
| 0x50E0 |  | 20704 |  | Min of V1 | float32 | R | 2
| 0x50E2 | 0x50E7 | 20706 | 20711 | Time Stamp | int16 | R | 6
| 0x50E8 |  | 20712 |  | Min of V2 | float32 | R | 2
| 0x50EA | 0x50EF | 20714 | 20719 | Time Stamp | int16 | R | 6
| 0x50F0 |  | 20720 |  | Min of V3 | float32 | R | 2
| 0x50F2 | 0x50F7 | 20722 | 20727 | Time Stamp | int16 | R | 6
| 0x50F8 |  | 20728 |  | Min of V12 | float32 | R | 2
| 0x50FA | 0x50FF | 20730 | 20735 | Time Stamp | int16 | R | 6
| 0x5100 |  | 20736 |  | Min of V23 | float32 | R | 2
| 0x5102 | 0x5107 | 20738 | 20743 | Time Stamp | int16 | R | 6
| 0x5108 |  | 20744 |  | Min of V31 | float32 | R | 2
| 0x510A | 0x510F | 20746 | 20751 | Time Stamp | int16 | R | 6
| 0x5110 |  | 20752 |  | Min of I1 | float32 | R | 2
| 0x5112 | 0x5117 | 20754 | 20759 | Time Stamp | int16 | R | 6
| 0x5118 |  | 20760 |  | Min of I2 | float32 | R | 2
| 0x511A | 0x511F | 20762 | 20767 | Time Stamp | int16 | R | 6
| 0x5120 |  | 20768 |  | Min of I3 | float32 | R | 2
| 0x5122 | 0x5127 | 20770 | 20775 | Time Stamp | int16 | R | 6
| 0x5128 |  | 20776 |  | Min of System Power | float32 | R | 2
| 0x512A | 0x512F | 20778 | 20783 | Time Stamp | int16 | R | 6
| 0x5130 |  | 20784 |  | Min of Reactive Power | float32 | R | 2
| 0x5132 | 0x5137 | 20786 | 20791 | Time Stamp | int16 | R | 6
| 0x5138 |  | 20792 |  | Min of Apparent Power | float32 | R | 2
| 0x513A | 0x513F | 20794 | 20799 | Time Stamp | int16 | R | 6
| 0x5140 |  | 20800 |  | Min of Power Factor | float32 | R | 2
| 0x5142 | 0x5147 | 20802 | 20807 | Time Stamp | int16 | R | 6
| 0x5148 |  | 20808 |  | Min of Frequency | float32 | R | 2
| 0x514A | 0x514F | 20810 | 20815 | Time Stamp | int16 | R | 6
| 0x5150 |  | 20816 |  | Min of Power Demand | float32 | R | 2
| 0x5152 | 0x5157 | 20818 | 20823 | Time Stamp | int16 | R | 6
| 0x5158 |  | 20824 |  | Min of Reactive power demand | float32 | R | 2
| 0x515A | 0x515F | 20826 | 20831 | Time Stamp | int16 | R | 6
| 0x5160 |  | 20832 |  | Min of Apparent power demand | float32 | R | 2
| 0x5162 | 0x5167 | 20834 | 20839 | Time Stamp | int16 | R | 6
| 0x5168 |  | 20840 |  | Min of Voltage unbalance | float32 | R | 2
| 0x516A | 0x516F | 20842 | 20847 | Time Stamp | int16 | R | 6
| 0x5170 |  | 20848 |  | Min of Current unbalance | float32 | R | 2
| 0x5172 | 0x5177 | 20850 | 20855 | Time Stamp | int16 | R | 6
| 0x5178 |  | 20856 |  | Min of THD_V1(V12) | float32 | R | 2
| 0x517A | 0x517F | 20858 | 20863 | Time Stamp | int16 | R | 6
| 0x5180 |  | 20864 |  | Min of THD_V2(V31) | float32 | R | 2
| 0x5182 | 0x5187 | 20866 | 20871 | Time Stamp | int16 | R | 6
| 0x5188 |  | 20872 |  | Min of THD_V3(V23) | float32 | R | 2
| 0x518A | 0x518F | 20874 | 20879 | Time Stamp | int16 | R | 6
| 0x5190 |  | 20880 |  | Min of THD_I1 | float32 | R | 2
| 0x5192 | 0x5197 | 20882 | 20887 | Time Stamp | int16 | R | 6
| 0x5198 |  | 20888 |  | Min of THD_I2 | float32 | R | 2
| 0x519A | 0x519F | 20890 | 20895 | Time Stamp | int16 | R | 6
| 0x51A0 |  | 20896 |  | Min of THD_I3 | float32 | R | 2
| 0x51A2 | 0x51A7 | 20898 | 20903 | Time Stamp | int16 | R | 6
| 0x52E0 |  | 21216 |  | Max of Phase A P | float32 | R | 2
| 0x52E2 | 0x52E7 | 21218 | 21223 | Time Stamp | int16 | R | 6
| 0x52E8 |  | 21224 |  | Max of Phase B P | float32 | R | 2
| 0x52EA | 0x52EF | 21226 | 21231 | Time Stamp | int16 | R | 6
| 0x52F0 |  | 21232 |  | Max of Phase C P | float32 | R | 2
| 0x52F2 | 0x52F7 | 21234 | 21239 | Time Stamp | int16 | R | 6
| 0x52F8 |  | 21240 |  | Max of Phase N P | float32 | R | 2
| 0x52FA | 0x52FF | 21242 | 21247 | Time Stamp | int16 | R | 6
| 0x5300 |  | 21248 |  | Max of Phase A Q | float32 | R | 2
| 0x5302 | 0x5307 | 21250 | 21255 | Time Stamp | int16 | R | 6
| 0x5308 |  | 21256 |  | Max of Phase B Q | float32 | R | 2
| 0x530A | 0x530F | 21258 | 21263 | Time Stamp | int16 | R | 6
| 0x5310 |  | 21264 |  | Max of Phase C Q | float32 | R | 2
| 0x5312 | 0x5317 | 21266 | 21271 | Time Stamp | int16 | R | 6
| 0x5318 |  | 21272 |  | Max of Phase N Q | float32 | R | 2
| 0x531A | 0x531F | 21274 | 21279 | Time Stamp | int16 | R | 6
| 0x5320 |  | 21280 |  | Max of Phase A S | float32 | R | 2
| 0x5322 | 0x5327 | 21282 | 21287 | Time Stamp | int16 | R | 6
| 0x5328 |  | 21288 |  | Max of Phase B S | float32 | R | 2
| 0x532A | 0x532F | 21290 | 21295 | Time Stamp | int16 | R | 6
| 0x5330 |  | 21296 |  | Max of Phase C S | float32 | R | 2
| 0x5332 | 0x5337 | 21298 | 21303 | Time Stamp | int16 | R | 6
| 0x5338 |  | 21304 |  | Max of Phase N S | float32 | R | 2
| 0x533A | 0x533F | 21306 | 21311 | Time Stamp | int16 | R | 6
| 0x5340 |  | 21312 |  | Max of Phase A PF | float32 | R | 2
| 0x5342 | 0x5347 | 21314 | 21319 | Time Stamp | int16 | R | 6
| 0x5348 |  | 21320 |  | Max of Phase B PF | float32 | R | 2
| 0x534A | 0x534F | 21322 | 21327 | Time Stamp | int16 | R | 6
| 0x5350 |  | 21328 |  | Max of Phase C PF | float32 | R | 2
| 0x5352 | 0x5357 | 21330 | 21335 | Time Stamp | int16 | R | 6
| 0x5358 |  | 21336 |  | Max of Phase N PF | float32 | R | 2
| 0x535A | 0x535F | 21338 | 21343 | Time Stamp | int16 | R | 6
| 0x5360 |  | 21344 |  | Max of Phase A P demand | float32 | R | 2
| 0x5362 | 0x5367 | 21346 | 21351 | Time Stamp | int16 | R | 6
| 0x5368 |  | 21352 |  | Max of Phase B P Demand | float32 | R | 2
| 0x536A | 0x536F | 21354 | 21359 | Time Stamp | int16 | R | 6
| 0x5370 |  | 21360 |  | Max of Phase C P Demand | float32 | R | 2
| 0x5372 | 0x5377 | 21362 | 21367 | Time Stamp | int16 | R | 6
| 0x5378 |  | 21368 |  | Max of Phase N P Demand | float32 | R | 2
| 0x537A | 0x537F | 21370 | 21375 | Time Stamp | int16 | R | 6
| 0x5380 |  | 21376 |  | Max of Phase A Q demand | float32 | R | 2
| 0x5382 | 0x5387 | 21378 | 21383 | Time Stamp | int16 | R | 6
| 0x5388 |  | 21384 |  | Max of Phase B Q Demand | float32 | R | 2
| 0x538A | 0x538F | 21386 | 21391 | Time Stamp | int16 | R | 6
| 0x5390 |  | 21392 |  | Max of Phase C Q Demand | float32 | R | 2
| 0x5392 | 0x5397 | 21394 | 21399 | Time Stamp | int16 | R | 6
| 0x5398 |  | 21400 |  | Max of Phase N Q demand | float32 | R | 2
| 0x539A | 0x539F | 21402 | 21407 | Time Stamp | int16 | R | 6
| 0x53A0 |  | 21408 |  | Max of Phase A S Demand | float32 | R | 2
| 0x53A2 | 0x53A7 | 21410 | 21415 | Time Stamp | int16 | R | 6
| 0x53A8 |  | 21416 |  | Max of Phase B S Demand | float32 | R | 2
| 0x53AA | 0x53AF | 21418 | 21423 | Time Stamp | int16 | R | 6
| 0x53B0 |  | 21424 |  | Max of Phase C S demand | float32 | R | 2
| 0x53B2 | 0x53B7 | 21426 | 21431 | Time Stamp | int16 | R | 6
| 0x53B8 |  | 21432 |  | Max of Phase N S Demand | float32 | R | 2
| 0x53BA | 0x53BF | 21434 | 21439 | Time Stamp | int16 | R | 6
| 0x53C0 |  | 21440 |  | Max of Phase N I Demand | float32 | R | 2
| 0x53C2 | 0x53C7 | 21442 | 21447 | Time Stamp | int16 | R | 6
| 0x53C8 |  | 21448 |  | Max of Phase N I | float32 | R | 2
| 0x53CA | 0x53CF | 21450 | 21455 | Time Stamp | int16 | R | 6
| 0x53D0 |  | 21456 |  | Max of Summation 2 P | float32 | R | 2
| 0x53D2 | 0x53D7 | 21458 | 21463 | Time Stamp | int16 | R | 6
| 0x53D8 |  | 21464 |  | Max of Summation 2 Q | float32 | R | 2
| 0x53DA | 0x53DF | 21466 | 21471 | Time Stamp | int16 | R | 6
| 0x53E0 |  | 21472 |  | Max of Summation 2 S | float32 | R | 2
| 0x53E2 | 0x53E7 | 21474 | 21479 | Time Stamp | int16 | R | 6
| 0x53E8 |  | 21480 |  | Max of Summation 2 PF | float32 | R | 2
| 0x53EA | 0x53EF | 21482 | 21487 | Time Stamp | int16 | R | 6
| 0x53F0 |  | 21488 |  | Max of Summation 2 P demand | float32 | R | 2
| 0x53F2 | 0x53F7 | 21490 | 21495 | Time Stamp | int16 | R | 6
| 0x53F8 |  | 21496 |  | Max of Summation 2 Q Demand | float32 | R | 2
| 0x53FA | 0x53FF | 21498 | 21503 | Time Stamp | int16 | R | 6
| 0x5400 |  | 21504 |  | Max of Summation 2 S Demand | float32 | R | 2
| 0x5402 | 0x5407 | 21506 | 21511 | Time Stamp | int16 | R | 6
| 0x5408 |  | 21512 |  | Max of Summation 2 I | float32 | R | 2
| 0x540A | 0x540F | 21514 | 21519 | Time Stamp | int16 | R | 6
| 0x5410 |  | 21520 |  | Max of In THD | float32 | R | 2
| 0x5412 | 0x5417 | 21522 | 21527 | Time Stamp | int16 | R | 6
| 0x5418 |  | 21528 |  | Min of Phase A P | float32 | R | 2
| 0x541A | 0x541F | 21530 | 21535 | Time Stamp | int16 | R | 6
| 0x5420 |  | 21536 |  | Min of Phase B P | float32 | R | 2
| 0x5422 | 0x5427 | 21538 | 21543 | Time Stamp | int16 | R | 6
| 0x5428 |  | 21544 |  | Min of Phase C P | float32 | R | 2
| 0x542A | 0x542F | 21546 | 21551 | Time Stamp | int16 | R | 6
| 0x5430 |  | 21552 |  | Min of Phase N P | float32 | R | 2
| 0x5432 | 0x5437 | 21554 | 21559 | Time Stamp | int16 | R | 6
| 0x5438 |  | 21560 |  | Min of Phase A Q | float32 | R | 2
| 0x543A | 0x543F | 21562 | 21567 | Time Stamp | int16 | R | 6
| 0x5440 |  | 21568 |  | Min of Phase B Q | float32 | R | 2
| 0x5442 | 0x5447 | 21570 | 21575 | Time Stamp | int16 | R | 6
| 0x5448 |  | 21576 |  | Min of Phase C Q | float32 | R | 2
| 0x544A | 0x544F | 21578 | 21583 | Time Stamp | int16 | R | 6
| 0x5450 |  | 21584 |  | Min of Phase N Q | float32 | R | 2
| 0x5452 | 0x5457 | 21586 | 21591 | Time Stamp | int16 | R | 6
| 0x5458 |  | 21592 |  | Min of Phase A S | float32 | R | 2
| 0x545A | 0x545F | 21594 | 21599 | Time Stamp | int16 | R | 6
| 0x5460 |  | 21600 |  | Min of Phase B S | float32 | R | 2
| 0x5462 | 0x5467 | 21602 | 21607 | Time Stamp | int16 | R | 6
| 0x5468 |  | 21608 |  | Min of Phase C S | float32 | R | 2
| 0x546A | 0x546F | 21610 | 21615 | Time Stamp | int16 | R | 6
| 0x5470 |  | 21616 |  | Min of Phase N S | float32 | R | 2
| 0x5472 | 0x5477 | 21618 | 21623 | Time Stamp | int16 | R | 6
| 0x5478 |  | 21624 |  | Min of Phase A PF | float32 | R | 2
| 0x547A | 0x547F | 21626 | 21631 | Time Stamp | int16 | R | 6
| 0x5480 |  | 21632 |  | Min of Phase B PF | float32 | R | 2
| 0x5482 | 0x5487 | 21634 | 21639 | Time Stamp | int16 | R | 6
| 0x5488 |  | 21640 |  | Min of Phase C PF | float32 | R | 2
| 0x548A | 0x548F | 21642 | 21647 | Time Stamp | int16 | R | 6
| 0x5490 |  | 21648 |  | Min of Phase N PF | float32 | R | 2
| 0x5492 | 0x5497 | 21650 | 21655 | Time Stamp | int16 | R | 6
| 0x5498 |  | 21656 |  | Min of Phase A P demand | float32 | R | 2
| 0x549A | 0x549F | 21658 | 21663 | Time Stamp | int16 | R | 6
| 0x54A0 |  | 21664 |  | Min of Phase B P Demand | float32 | R | 2
| 0x54A2 | 0x54A7 | 21666 | 21671 | Time Stamp | int16 | R | 6
| 0x54A8 |  | 21672 |  | Min of Phase C P Demand | float32 | R | 2
| 0x54AA | 0x54AF | 21674 | 21679 | Time Stamp | int16 | R | 6
| 0x54B0 |  | 21680 |  | Min of Phase N P demand | float32 | R | 2
| 0x54B2 | 0x54B7 | 21682 | 21687 | Time Stamp | int16 | R | 6
| 0x54B8 |  | 21688 |  | Min of Phase A Q Demand | float32 | R | 2
| 0x54BA | 0x54BF | 21690 | 21695 | Time Stamp | int16 | R | 6
| 0x54C0 |  | 21696 |  | Min of Phase B Q Demand | float32 | R | 2
| 0x54C2 | 0x54C7 | 21698 | 21703 | Time Stamp | int16 | R | 6
| 0x54C8 |  | 21704 |  | Min of Phase C Q demand | float32 | R | 2
| 0x54CA | 0x54CF | 21706 | 21711 | Time Stamp | int16 | R | 6
| 0x54D0 |  | 21712 |  | Min of Phase N Q Demand | float32 | R | 2
| 0x54D2 | 0x54D7 | 21714 | 21719 | Time Stamp | int16 | R | 6
| 0x54D8 |  | 21720 |  | Min of Phase A S Demand | float32 | R | 2
| 0x54DA | 0x54DF | 21722 | 21727 | Time Stamp | int16 | R | 6
| 0x54E0 |  | 21728 |  | Min of Phase B S demand | float32 | R | 2
| 0x54E2 | 0x54E7 | 21730 | 21735 | Time Stamp | int16 | R | 6
| 0x54E8 |  | 21736 |  | Min of Phase C S Demand | float32 | R | 2
| 0x54EA | 0x54EF | 21738 | 21743 | Time Stamp | int16 | R | 6
| 0x54F0 |  | 21744 |  | Min of Phase N S Demand | float32 | R | 2
| 0x54F2 | 0x54F7 | 21746 | 21751 | Time Stamp | int16 | R | 6
| 0x54F8 |  | 21752 |  | Min of Phase N I | float32 | R | 2
| 0x54FA | 0x54FF | 21754 | 21759 | Time Stamp | int16 | R | 6
| 0x5500 |  | 21760 |  | Min of Summation 2 P | float32 | R | 2
| 0x5502 | 0x5507 | 21762 | 21767 | Time Stamp | int16 | R | 6
| 0x5508 |  | 21768 |  | Min of Summation 2 Q | float32 | R | 2
| 0x550A | 0x550F | 21770 | 21775 | Time Stamp | int16 | R | 6
| 0x5510 |  | 21776 |  | Min of Summation 2 S | float32 | R | 2
| 0x5512 | 0x5517 | 21778 | 21783 | Time Stamp | int16 | R | 6
| 0x5518 |  | 21784 |  | Min of Summation 2 PF | float32 | R | 2
| 0x551A | 0x551F | 21786 | 21791 | Time Stamp | int16 | R | 6
| 0x5520 |  | 21792 |  | Min of Summation 2 P demand | float32 | R | 2
| 0x5522 | 0x5527 | 21794 | 21799 | Time Stamp | int16 | R | 6
| 0x5528 |  | 21800 |  | Min of Summation 2 Q Demand | float32 | R | 2
| 0x552A | 0x552F | 21802 | 21807 | Time Stamp | int16 | R | 6
| 0x5530 |  | 21808 |  | Min of Summation 2 S Demand | float32 | R | 2
| 0x5532 | 0x5537 | 21810 | 21815 | Time Stamp | int16 | R | 6
| 0x5538 |  | 21816 |  | Min of Summation 2 I | float32 | R | 2
| 0x553A | 0x553F | 21818 | 21823 | Time Stamp | int16 | R | 6
| 0x5540 |  | 21824 |  | Min of In THD | float32 | R | 2
| 0x5542 | 0x5547 | 21826 | 21831 | Time Stamp | int16 | R | 6

## RO
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value | Release version
RO read: FC 01 write: FC 05
| 0x0000 | 0x0000 | 0 | 0 | RO11-1 |  | R/W | 1
| 0x0001 | 0x0001 | 1 | 1 | RO11-2 |  | R/W | 1
| 0x0002 | 0x0002 | 2 | 2 | RO31-1 |  | R/W | 1
| 0x0003 | 0x0003 | 3 | 3 | RO31-2 |  | R/W | 1
| 0x0004 | 0x0004 | 4 | 4 | RO12-1 |  | R/W | 1
| 0x0005 | 0x0005 | 5 | 5 | RO12-2 |  | R/W | 1
| 0x0006 | 0x0006 | 6 | 6 | RO32-1 |  | R/W | 1
| 0x0007 | 0x0007 | 7 | 7 | RO32-2 |  | R/W | 1
| 0x0008 | 0x0008 | 8 | 8 | RO_T-1 |  | R/W | 1
| 0x0009 | 0x0009 | 9 | 9 | RO_T-2 |  | R/W | 1
Delta Meter 11 read: FC 03 write: FC 16
| 0xF083 | 0xF083 | 61571 | 61571 | RO11-1 |  | R/W | 1 |  |  |  | v6.30_DELTA_250416
| 0xF084 | 0xF084 | 61572 | 61572 | RO11-2 |  | R/W | 1
| 0xF085 | 0xF085 | 61573 | 61573 | RO31-1 |  | R/W | 1
| 0xF086 | 0xF086 | 61574 | 61574 | RO31-2 |  | R/W | 1
| 0xF087 | 0xF087 | 61575 | 61575 | RO12-1 |  | R/W | 1
| 0xF088 | 0xF088 | 61576 | 61576 | RO12-2 |  | R/W | 1
| 0xF089 | 0xF089 | 61577 | 61577 | RO32-1 |  | R/W | 1
| 0xF08A | 0xF08A | 61578 | 61578 | RO32-2 |  | R/W | 1

## Alarm Records｜DI¦AO¦AI¦SOE
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Alarm Log
| 0x42A9 |  | 17065 |  | Alarm Log 1: Alarming Status | int16 | R | 1 | High Byte: Alarm ID Low Byte Bit0: Alarm Status; 1: On 0: Off Low Byte Bit1: if "AND" enabled
| 0x42AA |  | 17066 |  | Alarm Log 1: Alarming parameter code | int16 | R | 1 | 0~79
| 0x42AB |  | 17067 |  | Alarm Log 1: over/under limit value | int16 | R | 1 | Related to parameter chosen
| 0x42AC |  | 17068 |  | Alarm Log 1: timestamp: year | int16 | R | 1
| 0x42AD |  | 17069 |  | Alarm Log 1: timestamp: month | int16 | R | 1
| 0x42AE |  | 17070 |  | Alarm Log 1: timestamp: day | int16 | R | 1
| 0x42AF |  | 17071 |  | Alarm Log 1: timestamp: hour | int16 | R | 1
| 0x42B0 |  | 17072 |  | Alarm Log 1: timestamp: minute | int16 | R | 1
| 0x42B1 |  | 17073 |  | Alarm Log 1: timestamp: second | int16 | R | 1
| 0x42B2 |  | 17074 |  | Alarm Log 1: timestamp: ms | int16 | R | 1
| 0x42B3 | 0x42BC | 17075 | 17084 | Alarm Log 2 | int16 | R | 10
| 0x42BD | 0x42C6 | 17085 | 17094 | Alarm Log 3 | int16 | R | 10
| 0x42C7 | 0x42D0 | 17095 | 17104 | Alarm Log 4 | int16 | R | 10
| 0x42D1 | 0x42DA | 17105 | 17114 | Alarm Log 5 | int16 | R | 10
| 0x42DB | 0x42E4 | 17115 | 17124 | Alarm Log 6 | int16 | R | 10
| 0x42E5 | 0x42EE | 17125 | 17134 | Alarm Log 7 | int16 | R | 10
| 0x42EF | 0x42F8 | 17135 | 17144 | Alarm Log 8 | int16 | R | 10
| 0x42F9 | 0x4302 | 17145 | 17154 | Alarm Log 9 | int16 | R | 10
| 0x4303 | 0x430C | 17155 | 17164 | Alarm Log 10 | int16 | R | 10
| 0x430D | 0x4316 | 17165 | 17174 | Alarm Log 11 | int16 | R | 10
| 0x4317 | 0x4320 | 17175 | 17184 | Alarm Log 12 | int16 | R | 10
| 0x4321 | 0x432A | 17185 | 17194 | Alarm Log 13 | int16 | R | 10
| 0x432B | 0x4334 | 17195 | 17204 | Alarm Log 14 | int16 | R | 10
| 0x4335 | 0x433E | 17205 | 17214 | Alarm Log 15 | int16 | R | 10
| 0x433F | 0x4348 | 17215 | 17224 | Alarm Log 16 | int16 | R | 10
| 0x26F1 |  | 9969 |  | Alarm Channel1 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26F2 |  | 9970 |  | Alarm Channel2 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26F3 |  | 9971 |  | Alarm Channel3 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26F4 |  | 9972 |  | Alarm Channel4 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26F5 |  | 9973 |  | Alarm Channel5 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26F6 |  | 9974 |  | Alarm Channel6 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26F7 |  | 9975 |  | Alarm Channel7 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26F8 |  | 9976 |  | Alarm Channel8 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26F9 |  | 9977 |  | Alarm Channel9 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26FA |  | 9978 |  | Alarm Channel10 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26FB |  | 9979 |  | Alarm Channel11 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26FC |  | 9980 |  | Alarm Channel12 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26FD |  | 9981 |  | Alarm Channel13 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26FE |  | 9982 |  | Alarm Channel14 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x26FF |  | 9983 |  | Alarm Channel15 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
| 0x2700 |  | 9984 |  | Alarm Channel16 Status | int16 | R | 1 | 1 = ON， 0 = OFF | 0 = OFF
IO module DI pulse count
| 0x4349 | 0x434A | 17225 | 17226 | DI1 pulse count | uint32 | R | 2
| 0x434B | 0x434C | 17227 | 17228 | DI2 pulse count | uint32 | R | 2
| 0x434D | 0x434E | 17229 | 17230 | DI3 pulse count | uint32 | R | 2
| 0x434F | 0x4350 | 17231 | 17232 | DI4 pulse count | uint32 | R | 2
| 0x4351 | 0x4352 | 17233 | 17234 | DI5 pulse count | uint32 | R | 2
| 0x4353 | 0x4354 | 17235 | 17236 | DI6 pulse count | uint32 | R | 2
| 0x4355 | 0x4356 | 17237 | 17238 | DI7 pulse count | uint32 | R | 2
| 0x4357 | 0x4358 | 17239 | 17240 | DI8 pulse count | uint32 | R | 2
| 0x4359 | 0x435A | 17241 | 17242 | DI9 pulse count | uint32 | R | 2
| 0x435B | 0x435C | 17243 | 17244 | DI10 pulse count | uint32 | R | 2
| 0x435D | 0x435E | 17245 | 17246 | DI11 pulse count | uint32 | R | 2
| 0x435F | 0x4360 | 17247 | 17248 | DI12 pulse count | uint32 | R | 2
| 0x4361 | 0x4362 | 17249 | 17250 | DI13 pulse count | uint32 | R | 2
| 0x4363 | 0x4364 | 17251 | 17252 | DI14 pulse count | uint32 | R | 2
| 0x4365 | 0x4366 | 17253 | 17254 | DI15 pulse count | uint32 | R | 2
| 0x4367 | 0x4368 | 17255 | 17256 | DI16 pulse count | uint32 | R | 2
| 0x4369 | 0x436A | 17257 | 17258 | DI17 pulse count | uint32 | R | 2
| 0x436B | 0x436C | 17259 | 17260 | DI18 pulse count | uint32 | R | 2
| 0x436D | 0x436E | 17261 | 17262 | DI19 pulse count | uint32 | R | 2
| 0x436F | 0x4370 | 17263 | 17264 | DI20 pulse count | uint32 | R | 2
| 0x4371 | 0x4372 | 17265 | 17266 | DI21 pulse count | uint32 | R | 2
| 0x4373 | 0x4374 | 17267 | 17268 | DI22 pulse count | uint32 | R | 2
| 0x4375 | 0x4376 | 17269 | 17270 | DI23 pulse count | uint32 | R | 2
| 0x4377 | 0x4378 | 17271 | 17272 | DI24 pulse count | uint32 | R | 2
| 0x4379 | 0x437A | 17273 | 17274 | DI25 pulse count | uint32 | R | 2
| 0x437B | 0x437C | 17275 | 17276 | DI26 pulse count | uint32 | R | 2
| 0x437D | 0x437E | 17277 | 17278 | DI27 pulse count | uint32 | R | 2
| 0x437F | 0x4380 | 17279 | 17280 | DI28 pulse count | uint32 | R | 2
AO/AI analogic value
| 0x4381 |  | 17281 |  | AO1 output value | word | R | 1
| 0x4382 |  | 17282 |  | AO2 output value | word | R | 1
| 0x4383 |  | 17283 |  | AO3 output value | word | R | 1
| 0x4384 |  | 17284 |  | AO4 output value | word | R | 1
| 0x4385 |  | 17285 |  | AI1 sample value | word | R | 1
| 0x4386 |  | 17286 |  | AI2 sample value | word | R | 1
| 0x4387 |  | 17287 |  | AI3 sample value | word | R | 1
| 0x4388 |  | 17288 |  | AI4 sample value | word | R | 1
AO/AI real value
| 0x4389 | 0x438A | 17289 | 17290 | AO1 value | float32 | R | 2
| 0x438B | 0x438C | 17291 | 17292 | AO2 value | float32 | R | 2
| 0x438D | 0x438E | 17293 | 17294 | AO3 value | float32 | R | 2
| 0x438F | 0x4390 | 17295 | 17296 | AO4 value | float32 | R | 2
| 0x4391 | 0x4392 | 17297 | 17298 | AI1 value | float32 | R | 2
| 0x4393 | 0x4394 | 17299 | 17300 | AI2 value | float32 | R | 2
| 0x4395 | 0x4396 | 17301 | 17302 | AI3 value | float32 | R | 2
| 0x4397 | 0x4398 | 17303 | 17304 | AI4 value | float32 | R | 2
SOE Log
| 0x4399 |  | 17305 |  | SOE Log 1 timestamp - year | word | R | 1
| 0x439A |  | 17306 |  | SOE Log 1 timestamp - month | word | R | 1
| 0x439B |  | 17307 |  | SOE Log 1 timestamp - day | word | R | 1
| 0x439C |  | 17308 |  | SOE Log 1 timestamp - hour | word | R | 1
| 0x439D |  | 17309 |  | SOE Log 1 timestamp - minute | word | R | 1
| 0x439E |  | 17310 |  | SOE Log 1 timestamp - second | word | R | 1
| 0x439F |  | 17311 |  | SOE Log 1 timestamp - ms | word | R | 1
| 0x43A0 |  | 17312 |  | SOE Log 1 status | word | R | 1
| 0x43A1 | 0x43A8 | 17313 | 17320 | SOE Log 2 | word | R | 8
| 0x43A9 | 0x43B0 | 17321 | 17328 | SOE Log 3 | word | R | 8
| 0x43B1 | 0x43B8 | 17329 | 17336 | SOE Log 4 | word | R | 8
| 0x43B9 | 0x43C0 | 17337 | 17344 | SOE Log 5 | word | R | 8
| 0x43C1 | 0x43C8 | 17345 | 17352 | SOE Log 6 | word | R | 8
| 0x43C9 | 0x43D0 | 17353 | 17360 | SOE Log 7 | word | R | 8
| 0x43D1 | 0x43D8 | 17361 | 17368 | SOE Log 8 | word | R | 8
| 0x43D9 | 0x43E0 | 17369 | 17376 | SOE Log 9 | word | R | 8
| 0x43E1 | 0x43E8 | 17377 | 17384 | SOE Log 10 | word | R | 8
| 0x43E9 | 0x43F0 | 17385 | 17392 | SOE Log 11 | word | R | 8
| 0x43F1 | 0x43F8 | 17393 | 17400 | SOE Log 12 | word | R | 8
| 0x43F9 | 0x4400 | 17401 | 17408 | SOE Log 13 | word | R | 8
| 0x4401 | 0x4408 | 17409 | 17416 | SOE Log 14 | word | R | 8
| 0x4409 | 0x4410 | 17417 | 17424 | SOE Log 15 | word | R | 8
| 0x4411 | 0x4418 | 17425 | 17432 | SOE Log 16 | word | R | 8
| 0x4419 | 0x4420 | 17433 | 17440 | SOE Log 17 | word | R | 8
| 0x4421 | 0x4428 | 17441 | 17448 | SOE Log 18 | word | R | 8
| 0x4429 | 0x4430 | 17449 | 17456 | SOE Log 19 | word | R | 8
| 0x4431 | 0x4438 | 17457 | 17464 | SOE Log 20 | word | R | 8
| 0x4439 |  | 17465 | 17465 | SOE record from IO module number | word | R | 1
IO11- | 0x443A |  | 17466 | 17466 | bit0-bit6: DI1 -- DI6 | word | R | 1
IO21- | 0x443B |  | 17467 | 17467 | bit0-bit4: DI1 -- DI4 | word | R | 1
IO31- | 0x443C |  | 17468 | 17468 | bit0-bit4: DI1 -- DI4 | word | R | 1
IO12- | 0x443D |  | 17469 | 17469 | bit0-bit6: DI1 -- DI6 | word | R | 1
IO22- | 0x443E |  | 17470 | 17470 | bit0-bit4: DI1 -- DI4 | word | R | 1
IO32- | 0x443F |  | 17471 | 17471 | bit0-bit4: DI1 -- DI4 | word | R | 1
IO4 | 0x4440 |  | 17472 | 17472 | RCM channel 1 status | word | R | 1 | 0: normal
1: short circuit
2: open circuit
3: overflow
| 0x4441 |  | 17473 | 17473 | RCM channel 2 status | word | R | 1 | 0: normal
1: short circuit
2: open circuit
3: overflow
| 0x4442 |  | 17474 | 17474 | RTD channel 1 status | word | R | 1 | "0: normal
1: short circuit
2: open circuit
3: overflow"
| 0x4443 |  | 17475 | 17475 | RTD channel 2 status | word | R | 1 | "0: normal
1: short circuit
2: open circuit
3: overflow"
| 0x4444 |  | 17476 | 17476 | RTD channel 1 temperature resistance | word | R | 1 | PT 100: 60 to 280Ω
PT1000: 600 to 2800Ω
KTY83: 500 to 2600Ω
KTY84: 350 to 2600Ω
| 0x4445 |  | 17477 | 17477 | RTD channel 2 temperature resistance | word | R | 1 | PT 100: 60 to 280Ω
PT1000: 600 to 2800Ω
KTY83: 500 to 2600Ω
KTY84: 350 to 2600Ω
| 0x4446 | 0x4447 | 17478 | 17479 | RCM - Channel 1 passive CT residual current (I_rms) | float32 | R | 2 | 0-30mA
| 0x4448 | 0x4449 | 17480 | 17481 | RCM - Channel 1 Hall effect CT total residual current (I_total) | float32 | R | 2 | 0-20mA
| 0x444A | 0x444B | 17482 | 17483 | RCM - Channel 1 Hall effect CT AC residual current (I_AC) | float32 | R | 2 | 0-20mA
| 0x444C | 0x444D | 17484 | 17485 | RCM - Channel 1 Hall effect CT DC residual current (I_DC) | float32 | R | 2 | 0-20mA
| 0x444E | 0x444F | 17486 | 17487 | RCM - Channel 2 passive CT residual current (I_rms) | float32 | R | 2 | 0-30mA
| 0x4450 | 0x4451 | 17488 | 17489 | RCM - Channel 2 Hall effect CT total residual current (I_total) | float32 | R | 2 | 0-20mA
| 0x4452 | 0x4453 | 17490 | 17491 | RCM - Channel 2 Hall effect CT AC residual current (I_AC) | float32 | R | 2 | 0-20mA
| 0x4454 | 0x4455 | 17492 | 17493 | RCM - Channel 2 Hall effect CT DC residual current (I_DC) | float32 | R | 2 | 0-20mA
| 0x4456 | 0x4457 | 17494 | 17495 | RTD - Channel 1 Temperature | float32 | R | 2 | PT 100&1000: -99 to 500℃
KTY83: -55 to 175℃
KTY84: -40 to 300℃
| 0x4458 | 0x4459 | 17496 | 17497 | RTD - Channel 2 Temperature | float32 | R | 2 | PT 100&1000: -99 to 500℃
KTY83: -55 to 175℃
KTY84: -40 to 300℃
26

## Waveform
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Waveform record parameter setup
| 0x8000 |  | 32768 |  | Manually Trigger | word | R/W | 1 | Write 0x00AA to trigger
| 0x8001 |  | 32769 |  | DI Trigger-AXM-IO11 | word | R/W | 1
| 0x8002 |  | 32770 |  | DI Trigger-AXM-IO21 | word | R/W | 1
| 0x8003 |  | 32771 |  | DI Trigger-AXM-IO31 | word | R/W | 1
| 0x8004 |  | 32772 |  | Voltage Rated Value | word | R/W | 1
| 0x8005 |  | 32773 |  | Voltage Sag Trigger | word | R/W | 1
| 0x8006 |  | 32774 |  | Voltage Sag Threshold | word | R/W | 1
| 0x8007 |  | 32775 |  | Voltage Sag Half cycle | word | R/W | 1
| 0x8008 |  | 32776 |  | Voltage Swell Trigger | word | R/W | 1
| 0x8009 |  | 32777 |  | Voltage Swell Threshold | word | R/W | 1
| 0x800A |  | 32778 |  | Sample rate | word | R/W | 1 | 0: 16 points; 1: 32 points; 2: 64 points; 3: 128 points; 4: 256 points; 5: 512.
| 0x800B |  | 32779 |  | Current Rated Value | word | R/W | 1
| 0x800C |  | 32780 |  | Over-Current Trigger | word | R/W | 1
| 0x800D |  | 32781 |  | Over-Current Threshold | word | R/W | 1
| 0x800E |  | 32782 |  | Waveform Clear | word | R/W | 1
| 0x800F |  | 32783 |  | Power Quality Event clear | word | R/W | 1
| 0x8010 |  | 32784 |  | Energy quality event, waveform record event - switch to output D01 | word | R/W | 1 | 0: No alarm output Bit0: Energy quality event-Voltage Sag Bit1: Energy quality event-Voltage Swell Bit2: waveform record event-Voltage Sag Bit3waveform record event-Voltage Swell Bit4: waveform record event-Over Current
| 0x8011 |  | 32785 |  | Energy quality event, waveform record event - switch to output D02 | word | R/W | 1
| 0x8012 |  | 32786 |  | Energy quality event, waveform record event - switch to output D03 | word | R/W | 1
| 0x8013 |  | 32787 |  | Energy quality event, waveform record event - switch to output D04 | word | R/W | 1
| 0x8014 |  | 32788 |  | Energy quality event-Voltage Sag output to RO | word | R/W | 1 | 0: No output Bit0: Output to relay 1 . . Bit7: Output to relay 8
| 0x8015 |  | 32789 |  | Energy quality event-Voltage Swell output to RO | word | R/W | 1
| 0x8016 |  | 32790 |  | waveform record event-Voltage Sag output to RO | word | R/W | 1
| 0x8017 |  | 32791 |  | waveform record event-Voltage Swell output to RO | word | R/W | 1
| 0x8018 |  | 32792 |  | waveform record event-Over-current output to RO | word | R/W | 1
Event Record Reading Area
| 0x8CFD |  | 36093 |  | Latest event record group number | word | R | 1
| 0x8CFE |  | 36094 |  | Read event record first group number | word | R/W | 1
| 0x8CFF |  | 36095 |  | Item number of every reading | word | R/W | 1
| 0x8D00 |  | 36096 |  | Time stamp: high byte-year,low byte-month | word | R | 1
| 0x8D01 |  | 36097 |  | Time stamp: high byte-day,low byte-hour | word | R | 1
| 0x8D02 |  | 36098 |  | Time stamp: high byte-minute,low byte-second | word | R | 1
| 0x8D03 |  | 36099 |  | Time stamp: ms | word | R | 1
| 0x8D04 |  | 36100 |  | Voltage sag or voltage swell --- event record | word | R | 1
| 0x8D05 |  | 36101 |  | Rated value | word | R | 1
| 0x8D06 |  | 36102 |  | Set value | word | R | 1
| 0x8D07 |  | 36103 |  | Half cycle count | word | R | 1
| 0x8D08 | 0x8D0F | 36104 | 36111 | 2nd event record | word | R | 8
| 0x8D10 | 0x8D17 | 36112 | 36119 | 3rd event record | word | R | 8
| 0x8D18 | 0x8D1F | 36120 | 36127 | 4th event record | word | R | 8
| 0x8D20 | 0x8D27 | 36128 | 36135 | 5th event record | word | R | 8
| 0x8D28 | 0x8D2F | 36136 | 36143 | 6th event record | word | R | 8
| 0x8D30 | 0x8D37 | 36144 | 36151 | 7th event record | word | R | 8
| 0x8D38 | 0x8D3F | 36152 | 36159 | 8th event record | word | R | 8
| 0x8D40 | 0x8D47 | 36160 | 36167 | 9th event record | word | R | 8
| 0x8D48 | 0x8D4F | 36168 | 36175 | 10th event record | word | R | 8
Event Record Reading（Hardware V2.0）
| 0x8E00 |  | 36352 |  | Group number of reading waveform | word | R/W | 1
| 0x8E01 |  | 36353 |  | Data number of each record | word | R/W | 1
| 0x8E02 |  | 36354 |  | Data state of waveform record window | word | R | 1
| 0x8E03 |  | 36355 |  | Latest waveform record groupe number | word | R | 1
| 0x8E04 | 0x8E43 | 36356 | 36419 | Waveform record data reading window | int16 | R | 64
Event Record Reading（Hardware V4.0）
Data Format
| 0x8F00 | 0x8F00 | 36608 | 36608 | Group number of reading waveform | word | R/W | 1 | 1 - 100 or 1 - 200
| 0x8F01 | 0x8F01 | 36609 | 36609 | Data number of each record | word | R/W | 1 | For detail see function description
| 0x8F02 | 0x8F02 | 36610 | 36610 | Data state of waveform record window | word | R | 1 | 0xBH: window data effective; 0xFF: window data not effective; 0xAA: waveform record content under clearing。
| 0x8F03 | 0x8F03 | 36611 | 36611 | Latest waveform record groupe number | word | R | 1 | 1 - 100 or 1 - 200;0: no waveform record data。
| 0x8F04 | 0x8F43 | 36612 | 36675 | Waveform record data reading window | word | R | 64 | -32768 ~ 32767
| In the case of 64-point recording: 0: Read-only waveform record reason mode; 1: Time and reason of waveform recording; 2 - 11: The first ten cycles of UA waveform data; 12 - 21: The first ten cycles of UB waveform data; 22 - 31: The first ten cycles of UC waveform data; 32 - 41: The first ten cycles of IA waveform data; 42 - 51: The first ten cycles of IB waveform data; 52 - 61: The first ten cycles of IC waveform data; 62 - 71: ten cycles after the UA waveform data; 72 - 81: Ten cycles after UB waveform data; 82 - 91: ten cycles after UC waveform data; 92 - 101: ten cycles after the IA waveform data; 102 - 111: ten cycles after IB waveform data; 112 - 121: ten cycles after IC waveform data; |  |  |  | In the case of 128-point recording and broadcasting, 0: Read-only waveform record reason mode; 1: Time and reason of waveform recording; 2 - 21: The first ten cycles of UA waveform data; 22 - 41: The first ten cycles of UB waveform data; 42 - 61: The first ten cycles of UC waveform data; 62 - 81: The first ten cycles of IA waveform data; 82 - 101: The first ten cycles of IB waveform data; 102 - 121: The first ten cycles of IC waveform data; 122 - 141: ten cycles after UA waveform data; 142 - 161: Ten cycles after UB waveform data; 162 - 181: ten cycles after UC waveform data; 182 - 201: ten cycles after the IA waveform data; 202 - 221: ten cycles after IB waveform data; 222 - 241: ten cycles after IC waveform data;
Read window data arRangement when data number = 1
| 0x8F04 | 0x8F05 | 36612 | 36613 | Frequency (Accuracy) | float32 | R | 2
| 0x8F06 | 0x8F07 | 36614 | 36615 | Voltage/Bit | float32 | R | 2
| 0x8F08 | 0x8F09 | 36616 | 36617 | Current/Bit | float32 | R | 2
| 0x8F0A | 0x8F10 | 36618 | 36624 | Waveform time | word | R | 7 | In sequence as year, month, day, hour,minute, second, ms。
| 0x8F11 | 0x8F19 | 36625 | 36633 | Waveform cause | word | R | 9
| 0x8F1A | 0x8F43 | 36634 | 36675 | For future | word | R | 42
64

## 4-30 Class S Readings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
10/12 cycle
| 0x95B0 | 0x95B3 | 38320 | 38323 | Time Stamp， for RMS | Uint64 | R | 4
| 0x95B4 | 0x95B7 | 38324 | 38327 | Time Stamp, for FFT | Uint64 | R | 4
| 0x95B8 |  | 38328 |  | Valid flag | int16 | R | 1
| 0x95B9 |  | 38329 |  | Event flag | int16 | R | 1
| 0x95BA |  | 38330 |  | Block number | int16 | R | 1
| 0x95BB | 0x95BC | 38331 | 38332 | Frequency | int32 | R | 2
| 0x95BD | 0x95BE | 38333 | 38334 | V1 | float32 | R | 2
| 0x95BF | 0x95C0 | 38335 | 38336 | V2 | float32 | R | 2
| 0x95C1 | 0x95C2 | 38337 | 38338 | V3 | float32 | R | 2
| 0x95C3 | 0x95C4 | 38339 | 38340 | V12 | float32 | R | 2
| 0x95C5 | 0x95C6 | 38341 | 38342 | V23 | float32 | R | 2
| 0x95C7 | 0x95C8 | 38343 | 38344 | V31 | float32 | R | 2
| 0x95C9 | 0x95CA | 38345 | 38346 | VLN, average | float32 | R | 2
| 0x95CB | 0x95CC | 38347 | 38348 | VLL, average | float32 | R | 2
| 0x95CD | 0x95CE | 38349 | 38350 | I1 | float32 | R | 2
| 0x95CF | 0x95D0 | 38351 | 38352 | I2 | float32 | R | 2
| 0x95D1 | 0x95D2 | 38353 | 38354 | I3 | float32 | R | 2
| 0x95D3 | 0x95D4 | 38355 | 38356 | In | float32 | R | 2
| 0x95D5 | 0x95D6 | 38357 | 38358 | I, average | float32 | R | 2
| 0x95D7 | 0x95D8 | 38359 | 38360 | THD_V1(V12) | float32 | R | 2
| 0x95D9 | 0x95DA | 38361 | 38362 | THD_V1(V12), odd | float32 | R | 2
| 0x95DB | 0x95DC | 38363 | 38364 | THD_V1(V12), even | float32 | R | 2
| 0x95DD | 0x95DE | 38365 | 38366 | Crest Factor, V1(V12), | float32 | R | 2
| 0x95DF | 0x95E0 | 38367 | 38368 | THD_V2(V31) | float32 | R | 2
| 0x95E1 | 0x95E2 | 38369 | 38370 | THD_V2(V31), odd | float32 | R | 2
| 0x95E3 | 0x95E4 | 38371 | 38372 | THD_V2(V31), even | float32 | R | 2
| 0x95E5 | 0x95E6 | 38373 | 38374 | Crest Factor, V2(V31), | float32 | R | 2
| 0x95E7 | 0x95E8 | 38375 | 38376 | THD_V3(V23) | float32 | R | 2
| 0x95E9 | 0x95EA | 38377 | 38378 | THD_V3(V23), odd | float32 | R | 2
| 0x95EB | 0x95EC | 38379 | 38380 | THD_V3(V23), even | float32 | R | 2
| 0x95ED | 0x95EE | 38381 | 38382 | Crest Factor, V3(V23) | float32 | R | 2
| 0x95EF | 0x95F0 | 38383 | 38384 | THD_I1 | float32 | R | 2
| 0x95F1 | 0x95F2 | 38385 | 38386 | THD_I1, odd | float32 | R | 2
| 0x95F3 | 0x95F4 | 38387 | 38388 | THD_I1, even | float32 | R | 2
| 0x95F5 | 0x95F6 | 38389 | 38390 | Crest Factor, I1 | float32 | R | 2
| 0x95F7 | 0x95F8 | 38391 | 38392 | THD_I2 | float32 | R | 2
| 0x95F9 | 0x95FA | 38393 | 38394 | THD_I2, odd | float32 | R | 2
| 0x95FB | 0x95FC | 38395 | 38396 | THD_I2, even | float32 | R | 2
| 0x95FD | 0x95FE | 38397 | 38398 | Crest Factor, I2 | float32 | R | 2
| 0x95FF | 0x9600 | 38399 | 38400 | THD_I3 | float32 | R | 2
| 0x9601 | 0x9602 | 38401 | 38402 | THD_I3, odd | float32 | R | 2
| 0x9603 | 0x9604 | 38403 | 38404 | THD_I3, even | float32 | R | 2
| 0x9605 | 0x9606 | 38405 | 38406 | Crest Factor, I3 | float32 | R | 2
| 0x9607 | 0x9608 | 38407 | 38408 | Voltage Unbalance Factor | float32 | R | 2
| 0x9609 | 0x960A | 38409 | 38410 | Voltage Zero Unbalance Factor | float32 | R | 2
| 0x960B | 0x960C | 38411 | 38412 | Voltage Zero Sequence, real part | float32 | R | 2
| 0x960D | 0x960E | 38413 | 38414 | Voltage Zero Sequence, imaginary part | float32 | R | 2
| 0x960F | 0x9610 | 38415 | 38416 | Voltage Positive Sequence, real part | float32 | R | 2
| 0x9611 | 0x9612 | 38417 | 38418 | Voltage Positive Sequence, imaginary part | float32 | R | 2
| 0x9613 | 0x9614 | 38419 | 38420 | Voltage Negative Sequence, real part | float32 | R | 2
| 0x9615 | 0x9616 | 38421 | 38422 | Voltage Negative Sequence, imaginary part | float32 | R | 2
| 0x9617 | 0x9618 | 38423 | 38424 | Current Unbalance Factor | float32 | R | 2
| 0x9619 | 0x961A | 38425 | 38426 | Current Zero Unbalance Factor | float32 | R | 2
| 0x961B | 0x961C | 38427 | 38428 | Current Zero Sequence, real part | float32 | R | 2
| 0x961D | 0x961E | 38429 | 38430 | Current Zero Sequence, imaginary part | float32 | R | 2
| 0x961F | 0x9620 | 38431 | 38432 | Current Positive Sequence, real part | float32 | R | 2
| 0x9621 | 0x9622 | 38433 | 38434 | Current Positive Sequence, imaginary part | float32 | R | 2
| 0x9623 | 0x9624 | 38435 | 38436 | Current Negative Sequence, real part | float32 | R | 2
| 0x9625 | 0x9626 | 38437 | 38438 | Current Negative Sequence, imaginary part | float32 | R | 2
119
150/180 cycle
| 0x9647 | 0x964A | 38471 | 38474 | Time Stamp， for RMS | Uint64 | R | 4
| 0x964B | 0x964E | 38475 | 38478 | Time Stamp, for FFT | Uint64 | R | 4
| 0x964F |  | 38479 |  | Valid flag | int16 | R | 1
| 0x9650 |  | 38480 |  | Event flag | int16 | R | 1
| 0x9651 |  | 38481 |  | Block number | int16 | R | 1
| 0x9652 | 0x9653 | 38482 | 38483 | Frequency | int32 | R | 2
| 0x9654 | 0x9655 | 38484 | 38485 | V1 | float32 | R | 2
| 0x9656 | 0x9657 | 38486 | 38487 | V2 | float32 | R | 2
| 0x9658 | 0x9659 | 38488 | 38489 | V3 | float32 | R | 2
| 0x965A | 0x965B | 38490 | 38491 | V12 | float32 | R | 2
| 0x965C | 0x965D | 38492 | 38493 | V23 | float32 | R | 2
| 0x965E | 0x965F | 38494 | 38495 | V31 | float32 | R | 2
| 0x9660 | 0x9661 | 38496 | 38497 | VLN, average | float32 | R | 2
| 0x9662 | 0x9663 | 38498 | 38499 | VLL, average | float32 | R | 2
| 0x9664 | 0x9665 | 38500 | 38501 | I1 | float32 | R | 2
| 0x9666 | 0x9667 | 38502 | 38503 | I2 | float32 | R | 2
| 0x9668 | 0x9669 | 38504 | 38505 | I3 | float32 | R | 2
| 0x966A | 0x966B | 38506 | 38507 | In | float32 | R | 2
| 0x966C | 0x966D | 38508 | 38509 | I, average | float32 | R | 2
| 0x966E | 0x966F | 38510 | 38511 | THD_V1(V12) | float32 | R | 2
| 0x9670 | 0x9671 | 38512 | 38513 | THD_V1(V12), odd | float32 | R | 2
| 0x9672 | 0x9673 | 38514 | 38515 | THD_V1(V12), even | float32 | R | 2
| 0x9674 | 0x9675 | 38516 | 38517 | Crest Factor, V1(V12), | float32 | R | 2
| 0x9676 | 0x9677 | 38518 | 38519 | THD_V2(V31) | float32 | R | 2
| 0x9678 | 0x9679 | 38520 | 38521 | THD_V2(V31), odd | float32 | R | 2
| 0x967A | 0x967B | 38522 | 38523 | THD_V2(V31), even | float32 | R | 2
| 0x967C | 0x967D | 38524 | 38525 | Crest Factor, V2(V31), | float32 | R | 2
| 0x967E | 0x967F | 38526 | 38527 | THD_V3(V23) | float32 | R | 2
| 0x9680 | 0x9681 | 38528 | 38529 | THD_V3(V23), odd | float32 | R | 2
| 0x9682 | 0x9683 | 38530 | 38531 | THD_V3(V23), even | float32 | R | 2
| 0x9684 | 0x9685 | 38532 | 38533 | Crest Factor, V3(V23) | float32 | R | 2
| 0x9686 | 0x9687 | 38534 | 38535 | THD_I1 | float32 | R | 2
| 0x9688 | 0x9689 | 38536 | 38537 | THD_I1, odd | float32 | R | 2
| 0x968A | 0x968B | 38538 | 38539 | THD_I1, even | float32 | R | 2
| 0x968C | 0x968D | 38540 | 38541 | Crest Factor, I1 | float32 | R | 2
| 0x968E | 0x968F | 38542 | 38543 | THD_I2 | float32 | R | 2
| 0x9690 | 0x9691 | 38544 | 38545 | THD_I2, odd | float32 | R | 2
| 0x9692 | 0x9693 | 38546 | 38547 | THD_I2, even | float32 | R | 2
| 0x9694 | 0x9695 | 38548 | 38549 | Crest Factor, I2 | float32 | R | 2
| 0x9696 | 0x9697 | 38550 | 38551 | THD_I3 | float32 | R | 2
| 0x9698 | 0x9699 | 38552 | 38553 | THD_I3, odd | float32 | R | 2
| 0x969A | 0x969B | 38554 | 38555 | THD_I3, even | float32 | R | 2
| 0x969C | 0x969D | 38556 | 38557 | Crest Factor, I3 | float32 | R | 2
| 0x969E | 0x969F | 38558 | 38559 | Voltage Unbalance Factor | float32 | R | 2
| 0x96A0 | 0x96A1 | 38560 | 38561 | Voltage Zero Unbalance Factor | float32 | R | 2
| 0x96A2 | 0x96A3 | 38562 | 38563 | Voltage Zero Sequence, real part | float32 | R | 2
| 0x96A4 | 0x96A5 | 38564 | 38565 | Voltage Zero Sequence, imaginary part | float32 | R | 2
| 0x96A6 | 0x96A7 | 38566 | 38567 | Voltage Positive Sequence, real part | float32 | R | 2
| 0x96A8 | 0x96A9 | 38568 | 38569 | Voltage Positive Sequence, imaginary part | float32 | R | 2
| 0x96AA | 0x96AB | 38570 | 38571 | Voltage Negative Sequence, real part | float32 | R | 2
| 0x96AC | 0x96AD | 38572 | 38573 | Voltage Negative Sequence, imaginary part | float32 | R | 2
| 0x96AE | 0x96AF | 38574 | 38575 | Current Unbalance Factor | float32 | R | 2
| 0x96B0 | 0x96B1 | 38576 | 38577 | Current Zero Unbalance Factor | float32 | R | 2
| 0x96B2 | 0x96B3 | 38578 | 38579 | Current Zero Sequence, real part | float32 | R | 2
| 0x96B4 | 0x96B5 | 38580 | 38581 | Current Zero Sequence, imaginary part | float32 | R | 2
| 0x96B6 | 0x96B7 | 38582 | 38583 | Current Positive Sequence, real part | float32 | R | 2
| 0x96B8 | 0x96B9 | 38584 | 38585 | Current Positive Sequence, imaginary part | float32 | R | 2
| 0x96BA | 0x96BB | 38586 | 38587 | Current Negative Sequence, real part | float32 | R | 2
| 0x96BC | 0x96BD | 38588 | 38589 | Current Negative Sequence, imaginary part | float32 | R | 2
119
10 min
| 0x96DE | 0x96E1 | 38622 | 38625 | Time Stamp， for RMS | Uint64 | R | 4
| 0x96E2 | 0x96E5 | 38626 | 38629 | Time Stamp, for FFT | Uint64 | R | 4
| 0x96E6 |  | 38630 |  | Valid flag | int16 | R | 1
| 0x96E7 |  | 38631 |  | Event flag | int16 | R | 1
| 0x96E8 |  | 38632 |  | Not Use | int16 | R | 1
| 0x96E9 | 0x96EA | 38633 | 38634 | Frequency | int32 | R | 2
| 0x96EB | 0x96EC | 38635 | 38636 | V1 | float32 | R | 2
| 0x96ED | 0x96EE | 38637 | 38638 | V2 | float32 | R | 2
| 0x96EF | 0x96F0 | 38639 | 38640 | V3 | float32 | R | 2
| 0x96F1 | 0x96F2 | 38641 | 38642 | V12 | float32 | R | 2
| 0x96F3 | 0x96F4 | 38643 | 38644 | V23 | float32 | R | 2
| 0x96F5 | 0x96F6 | 38645 | 38646 | V31 | float32 | R | 2
| 0x96F7 | 0x96F8 | 38647 | 38648 | VLN, average | float32 | R | 2
| 0x96F9 | 0x96FA | 38649 | 38650 | VLL, average | float32 | R | 2
| 0x96FB | 0x96FC | 38651 | 38652 | I1 | float32 | R | 2
| 0x96FD | 0x96FE | 38653 | 38654 | I2 | float32 | R | 2
| 0x96FF | 0x9700 | 38655 | 38656 | I3 | float32 | R | 2
| 0x9701 | 0x9702 | 38657 | 38658 | In | float32 | R | 2
| 0x9703 | 0x9704 | 38659 | 38660 | I, average | float32 | R | 2
| 0x9705 | 0x9706 | 38661 | 38662 | THD_V1(V12) | float32 | R | 2
| 0x9707 | 0x9708 | 38663 | 38664 | THD_V1(V12), odd | float32 | R | 2
| 0x9709 | 0x970A | 38665 | 38666 | THD_V1(V12), even | float32 | R | 2
| 0x970B | 0x970C | 38667 | 38668 | Crest Factor, V1(V12), | float32 | R | 2
| 0x970D | 0x970E | 38669 | 38670 | THD_V2(V31) | float32 | R | 2
| 0x970F | 0x9710 | 38671 | 38672 | THD_V2(V31), odd | float32 | R | 2
| 0x9711 | 0x9712 | 38673 | 38674 | THD_V2(V31), even | float32 | R | 2
| 0x9713 | 0x9714 | 38675 | 38676 | Crest Factor, V2(V31), | float32 | R | 2
| 0x9715 | 0x9716 | 38677 | 38678 | THD_V3(V23) | float32 | R | 2
| 0x9717 | 0x9718 | 38679 | 38680 | THD_V3(V23), odd | float32 | R | 2
| 0x9719 | 0x971A | 38681 | 38682 | THD_V3(V23), even | float32 | R | 2
| 0x971B | 0x971C | 38683 | 38684 | Crest Factor, V3(V23) | float32 | R | 2
| 0x971D | 0x971E | 38685 | 38686 | THD_I1 | float32 | R | 2
| 0x971F | 0x9720 | 38687 | 38688 | THD_I1, odd | float32 | R | 2
| 0x9721 | 0x9722 | 38689 | 38690 | THD_I1, even | float32 | R | 2
| 0x9723 | 0x9724 | 38691 | 38692 | Crest Factor, I1 | float32 | R | 2
| 0x9725 | 0x9726 | 38693 | 38694 | THD_I2 | float32 | R | 2
| 0x9727 | 0x9728 | 38695 | 38696 | THD_I2, odd | float32 | R | 2
| 0x9729 | 0x972A | 38697 | 38698 | THD_I2, even | float32 | R | 2
| 0x972B | 0x972C | 38699 | 38700 | Crest Factor, I2 | float32 | R | 2
| 0x972D | 0x972E | 38701 | 38702 | THD_I3 | float32 | R | 2
| 0x972F | 0x9730 | 38703 | 38704 | THD_I3, odd | float32 | R | 2
| 0x9731 | 0x9732 | 38705 | 38706 | THD_I3, even | float32 | R | 2
| 0x9733 | 0x9734 | 38707 | 38708 | Crest Factor, I3 | float32 | R | 2
| 0x9735 | 0x9736 | 38709 | 38710 | Voltage Unbalance Factor | float32 | R | 2
| 0x9737 | 0x9738 | 38711 | 38712 | Voltage Zero Unbalance Factor | float32 | R | 2
| 0x9739 | 0x973A | 38713 | 38714 | Voltage Zero Sequence, real part | float32 | R | 2
| 0x973B | 0x973C | 38715 | 38716 | Voltage Zero Sequence, imaginary part | float32 | R | 2
| 0x973D | 0x973E | 38717 | 38718 | Voltage Positive Sequence, real part | float32 | R | 2
| 0x973F | 0x9740 | 38719 | 38720 | Voltage Positive Sequence, imaginary part | float32 | R | 2
| 0x9741 | 0x9742 | 38721 | 38722 | Voltage Negative Sequence, real part | float32 | R | 2
| 0x9743 | 0x9744 | 38723 | 38724 | Voltage Negative Sequence, imaginary part | float32 | R | 2
| 0x9745 | 0x9746 | 38725 | 38726 | Current Unbalance Factor | float32 | R | 2
| 0x9747 | 0x9748 | 38727 | 38728 | Current Zero Unbalance Factor | float32 | R | 2
| 0x9749 | 0x974A | 38729 | 38730 | Current Zero Sequence, real part | float32 | R | 2
| 0x974B | 0x974C | 38731 | 38732 | Current Zero Sequence, imaginary part | float32 | R | 2
| 0x974D | 0x974E | 38733 | 38734 | Current Positive Sequence, real part | float32 | R | 2
| 0x974F | 0x9750 | 38735 | 38736 | Current Positive Sequence, imaginary part | float32 | R | 2
| 0x9751 | 0x9752 | 38737 | 38738 | Current Negative Sequence, real part | float32 | R | 2
| 0x9753 | 0x9754 | 38739 | 38740 | Current Negative Sequence, imaginary part | float32 | R | 2
119
2 hours
| 0x9775 | 0x9778 | 38773 | 38776 | Time Stamp， for RMS | Uint64 | R | 4
| 0x9779 | 0x977C | 38777 | 38780 | Time Stamp, for FFT | Uint64 | R | 4
| 0x977D |  | 38781 |  | Valid flag | int16 | R | 1
| 0x977E |  | 38782 |  | Event flag | int16 | R | 1
| 0x977F |  | 38783 |  | Not Use | int16 | R | 1
| 0x9780 | 0x9781 | 38784 | 38785 | Frequency | int32 | R | 2
| 0x9782 | 0x9783 | 38786 | 38787 | V1 | float32 | R | 2
| 0x9784 | 0x9785 | 38788 | 38789 | V2 | float32 | R | 2
| 0x9786 | 0x9787 | 38790 | 38791 | V3 | float32 | R | 2
| 0x9788 | 0x9789 | 38792 | 38793 | V12 | float32 | R | 2
| 0x978A | 0x978B | 38794 | 38795 | V23 | float32 | R | 2
| 0x978C | 0x978D | 38796 | 38797 | V31 | float32 | R | 2
| 0x978E | 0x978F | 38798 | 38799 | VLN, average | float32 | R | 2
| 0x9790 | 0x9791 | 38800 | 38801 | VLL, average | float32 | R | 2
| 0x9792 | 0x9793 | 38802 | 38803 | I1 | float32 | R | 2
| 0x9794 | 0x9795 | 38804 | 38805 | I2 | float32 | R | 2
| 0x9796 | 0x9797 | 38806 | 38807 | I3 | float32 | R | 2
| 0x9798 | 0x9799 | 38808 | 38809 | In | float32 | R | 2
| 0x979A | 0x979B | 38810 | 38811 | I, average | float32 | R | 2
| 0x979C | 0x979D | 38812 | 38813 | THD_V1(V12) | float32 | R | 2
| 0x979E | 0x979F | 38814 | 38815 | THD_V1(V12), odd | float32 | R | 2
| 0x97A0 | 0x97A1 | 38816 | 38817 | THD_V1(V12), even | float32 | R | 2
| 0x97A2 | 0x97A3 | 38818 | 38819 | Crest Factor, V1(V12), | float32 | R | 2
| 0x97A4 | 0x97A5 | 38820 | 38821 | THD_V2(V31) | float32 | R | 2
| 0x97A6 | 0x97A7 | 38822 | 38823 | THD_V2(V31), odd | float32 | R | 2
| 0x97A8 | 0x97A9 | 38824 | 38825 | THD_V2(V31), even | float32 | R | 2
| 0x97AA | 0x97AB | 38826 | 38827 | Crest Factor, V2(V31), | float32 | R | 2
| 0x97AC | 0x97AD | 38828 | 38829 | THD_V3(V23) | float32 | R | 2
| 0x97AE | 0x97AF | 38830 | 38831 | THD_V3(V23), odd | float32 | R | 2
| 0x97B0 | 0x97B1 | 38832 | 38833 | THD_V3(V23), even | float32 | R | 2
| 0x97B2 | 0x97B3 | 38834 | 38835 | Crest Factor, V3(V23) | float32 | R | 2
| 0x97B4 | 0x97B5 | 38836 | 38837 | THD_I1 | float32 | R | 2
| 0x97B6 | 0x97B7 | 38838 | 38839 | THD_I1, odd | float32 | R | 2
| 0x97B8 | 0x97B9 | 38840 | 38841 | THD_I1, even | float32 | R | 2
| 0x97BA | 0x97BB | 38842 | 38843 | Crest Factor, I1 | float32 | R | 2
| 0x97BC | 0x97BD | 38844 | 38845 | THD_I2 | float32 | R | 2
| 0x97BE | 0x97BF | 38846 | 38847 | THD_I2, odd | float32 | R | 2
| 0x97C0 | 0x97C1 | 38848 | 38849 | THD_I2, even | float32 | R | 2
| 0x97C2 | 0x97C3 | 38850 | 38851 | Crest Factor, I2 | float32 | R | 2
| 0x97C4 | 0x97C5 | 38852 | 38853 | THD_I3 | float32 | R | 2
| 0x97C6 | 0x97C7 | 38854 | 38855 | THD_I3, odd | float32 | R | 2
| 0x97C8 | 0x97C9 | 38856 | 38857 | THD_I3, even | float32 | R | 2
| 0x97CA | 0x97CB | 38858 | 38859 | Crest Factor, I3 | float32 | R | 2
| 0x97CC | 0x97CD | 38860 | 38861 | Voltage Unbalance Factor | float32 | R | 2
| 0x97CE | 0x97CF | 38862 | 38863 | Voltage Zero Unbalance Factor | float32 | R | 2
| 0x97D0 | 0x97D1 | 38864 | 38865 | Voltage Zero Sequence, real part | float32 | R | 2
| 0x97D2 | 0x97D3 | 38866 | 38867 | Voltage Zero Sequence, imaginary part | float32 | R | 2
| 0x97D4 | 0x97D5 | 38868 | 38869 | Voltage Positive Sequence, real part | float32 | R | 2
| 0x97D6 | 0x97D7 | 38870 | 38871 | Voltage Positive Sequence, imaginary part | float32 | R | 2
| 0x97D8 | 0x97D9 | 38872 | 38873 | Voltage Negative Sequence, real part | float32 | R | 2
| 0x97DA | 0x97DB | 38874 | 38875 | Voltage Negative Sequence, imaginary part | float32 | R | 2
| 0x97DC | 0x97DD | 38876 | 38877 | Current Unbalance Factor | float32 | R | 2
| 0x97DE | 0x97DF | 38878 | 38879 | Current Zero Unbalance Factor | float32 | R | 2
| 0x97E0 | 0x97E1 | 38880 | 38881 | Current Zero Sequence, real part | float32 | R | 2
| 0x97E2 | 0x97E3 | 38882 | 38883 | Current Zero Sequence, imaginary part | float32 | R | 2
| 0x97E4 | 0x97E5 | 38884 | 38885 | Current Positive Sequence, real part | float32 | R | 2
| 0x97E6 | 0x97E7 | 38886 | 38887 | Current Positive Sequence, imaginary part | float32 | R | 2
| 0x97E8 | 0x97E9 | 38888 | 38889 | Current Negative Sequence, real part | float32 | R | 2
| 0x97EA | 0x97EB | 38890 | 38891 | Current Negative Sequence, imaginary part | float32 | R | 2
119
Harmonic - amplitude
10/12 cycle | 0x980C | 0x984B | 38924 | 38987 | V1 or V12 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0x984C | 0x98C9 | 38988 | 39113 | V1 or V12 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0x98CA | 0x9909 | 39114 | 39177 | V2 or V23 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64 |  | 0 | 0
| 0x990A | 0x9987 | 39178 | 39303 | V2 or V23 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0x9988 | 0x99C7 | 39304 | 39367 | V3 or V31 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0x99C8 | 0x9A45 | 39368 | 39493 | V3 or V31 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0x9A46 | 0x9A85 | 39494 | 39557 | I1 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64 | Actual amplitude percentage = reading data / 100
| 0x9A86 | 0x9B03 | 39558 | 39683 | I1 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0x9B04 | 0x9B43 | 39684 | 39747 | I2 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0x9B44 | 0x9BC1 | 39748 | 39873 | I2 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0x9BC2 | 0x9C01 | 39874 | 39937 | I3 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0x9C02 | 0x9C7F | 39938 | 40063 | I3 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
150/180 cycle | 0x9C80 | 0x9CBF | 40064 | 40127 | V1 or V12 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64 | Actual amplitude percentage = reading data / 100
| 0x9CC0 | 0x9D3D | 40128 | 40253 | V1 or V12 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0x9D3E | 0x9D7D | 40254 | 40317 | V2 or V23 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64 |  | 0 | 0
| 0x9D7E | 0x9DFB | 40318 | 40443 | V2 or V23 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0x9DFC | 0x9E3B | 40444 | 40507 | V3 or V31 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0x9E3C | 0x9EB9 | 40508 | 40633 | V3 or V31 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0x9EBA | 0x9EF9 | 40634 | 40697 | I1 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0x9EFA | 0x9F77 | 40698 | 40823 | I1 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0x9F78 | 0x9FB7 | 40824 | 40887 | I2 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0x9FB8 | 0xA035 | 40888 | 41013 | I2 Harmonic amplitude (1st - 63rd order) | float32 | R | 126 |  | 0 | 0
| 0xA036 | 0xA075 | 41014 | 41077 | I3 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0xA076 | 0xA0F3 | 41078 | 41203 | I3 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
10 minutes | 0xA0F4 | 0xA133 | 41204 | 41267 | V1 or V12 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0xA134 | 0xA1B1 | 41268 | 41393 | V1 or V12 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0xA1B2 | 0xA1F1 | 41394 | 41457 | V2 or V23 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0xA1F2 | 0xA26F | 41458 | 41583 | V2 or V23 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0xA270 | 0xA2AF | 41584 | 41647 | V3 or V31 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64 |  | 0 | 0
| 0xA2B0 | 0xA32D | 41648 | 41773 | V3 or V31 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0xA32E | 0xA36D | 41774 | 41837 | I1 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0xA36E | 0xA3EB | 41838 | 41963 | I1 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0xA3EC | 0xA42B | 41964 | 42027 | I2 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0xA42C | 0xA4A9 | 42028 | 42153 | I2 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0xA4AA | 0xA4E9 | 42154 | 42217 | I3 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64 | Actual amplitude percentage = reading data / 100
| 0xA4EA | 0xA567 | 42218 | 42343 | I3 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
2 hours | 0xA568 | 0xA5A7 | 42344 | 42407 | V1 or V12 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0xA5A8 | 0xA625 | 42408 | 42533 | V1 or V12 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0xA626 | 0xA665 | 42534 | 42597 | V2 or V23 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0xA666 | 0xA6E3 | 42598 | 42723 | V2 or V23 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0xA6E4 | 0xA723 | 42724 | 42787 | V3 or V31 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64 | Actual amplitude percentage = reading data / 100
| 0xA724 | 0xA7A1 | 42788 | 42913 | V3 or V31 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0xA7A2 | 0xA7E1 | 42914 | 42977 | I1 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0xA7E2 | 0xA85F | 42978 | 43103 | I1 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0xA860 | 0xA89F | 43104 | 43167 | I2 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0xA8A0 | 0xA91D | 43168 | 43293 | I2 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
| 0xA91E | 0xA95D | 43294 | 43357 | I3 harmonic amplitude percentage (1st - 63rd order) | uint16 | R | 64
| 0xA95E | 0xA9DB | 43358 | 43483 | I3 Harmonic amplitude (1st - 63rd order) | float32 | R | 126
10s | 0xA9DD | 0xA9E0 | 43485 | 43488 | Time Stamp， for RMS | Uint64 | R | 4
| 0xA9E1 |  | 43489 |  | Event flag | int16 | R | 1
| 0xA9E2 | 0xA9E3 | 43490 | 43491 | Frequency | int32 | R | 2
1 cycle RMS | 0xB00A | 0xB00D | 45066 | 45069 | Time Stamp， for RMS | Uint64 | R | 4
| 0xB00E | 0xB00F | 45070 | 45071 | Block number | int32 | R | 2
| 0xB010 | 0xB011 | 45072 | 45073 | V1 | float32 | R | 2
| 0xB012 | 0xB013 | 45074 | 45075 | V2 | float32 | R | 2
| 0xB014 | 0xB015 | 45076 | 45077 | V3 | float32 | R | 2
| 0xB016 | 0xB017 | 45078 | 45079 | V12 | float32 | R | 2
| 0xB018 | 0xB019 | 45080 | 45081 | V23 | float32 | R | 2
| 0xB01A | 0xB01B | 45082 | 45083 | V31 | float32 | R | 2
| 0xB01C | 0xB01D | 45084 | 45085 | I1 | float32 | R | 2
| 0xB01E | 0xB01F | 45086 | 45087 | I2 | float32 | R | 2
| 0xB020 | 0xB021 | 45088 | 45089 | I3 | float32 | R | 2
| 0xB022 | 0xB023 | 45090 | 45091 | I4 | float32 | R | 2
26

## 4-30 PQ Event
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Event record parameter setup
| 0xAF65 |  | 44901 |  | Class S PQ Event enable | word | R/W | 1 | 0: disable; 1: enable
| 0xAF66 |  | 44902 |  | Voltage Rated Value | word | R/W | 1 | 10 to 690(3LL）or 400 | 400
| 0xAF67 |  | 44903 |  | Current Rated Value | word | R/W | 1 | 500 to 5000(5A) or 100-1000 | 5000(5A meter) 1000(mV meter)
| 0xAF68 |  | 44904 |  | Sample rate | word | R/W | 1 | 0: 16 points; 1: 32 points; 2: 64 points; 3: 128 points; 4: 256 points; 5: 512.
| 0xAF69 |  | 44905 |  | Voltage Sag Enable/Disable | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF6A |  | 44906 |  | Voltage Sag Threshold | word | R/W | 1 | 10 to 90 | 90
|  |  | 44907 |  | Voltage Sag Hysteresis | word | R/W | 1 | 1 to 10 | 2
| 0xAF6C |  | 44908 |  | Voltage Sag Waveform Trigger | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF6D |  | 44909 |  | Voltage Sag Event - switch to digital output D0X | word | R/W | 1 | 0: No output; 1:D01; 2: D02; 3: D03; 4: D04
| 0xAF6E |  | 44910 |  | Energy quality event-Voltage Sag output to RO | word | R/W | 1 | 0: No output Bit0: Output to relay RO11-1 Bit1: RO11-2. Bit2: RO31-1 Bit3: RO31-2. Bit4: RO12-1 Bit5: RO12-2. Bit6: RO32-1 Bit7: RO32-2
| 0xAF6F |  | 44911 |  | Voltage Swell Enable/Disable | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF70 |  | 44912 |  | Voltage Swell Threshold | word | R/W | 1 | 110 to 150 | 120
|  |  | 44913 |  | Voltage Swell Hysteresis | word | R/W | 1 | 1 to 10 | 2
| 0xAF72 |  | 44914 |  | Voltage Swell Waveform Trigger | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF73 |  | 44915 |  | Voltage Swell Event - switch to digital output D0X | word | R/W | 1 | 0: No output; 1:D01; 2: D02; 3: D03; 4: D04
| 0xAF74 |  | 44916 |  | Energy quality event-Voltage Swell output to RO | word | R/W | 1 | 0: No output Bit0: Output to relay RO11-1 Bit1: RO11-2. Bit2: RO31-1 Bit3: RO31-2. Bit4: RO12-1 Bit5: RO12-2. Bit6: RO32-1 Bit7: RO32-2
| 0xAF75 |  | 44917 |  | Voltage Interrupt Enable/Disable | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF76 |  | 44918 |  | Voltage Interrupt Threshold | word | R/W | 1 | 5 to 10 | 10
| 0xAF77 |  | 44919 |  | Voltage Interrupt Hysteresis | word | R/W | 1 | 1 to 10 | 2
| 0xAF78 |  | 44920 |  | Voltage Interrupt Waveform Trigger | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF79 |  | 44921 |  | Voltage Interrupt Event - switch to digital output D0X | word | R/W | 1 | 0: No output; 1:D01; 2: D02; 3: D03; 4: D04
| 0xAF7A |  | 44922 |  | Energy quality event-Voltage Interrupt output to RO | word | R/W | 1 | 0: No output Bit0: Output to relay RO11-1 Bit1: RO11-2. Bit2: RO31-1 Bit3: RO31-2. Bit4: RO12-1 Bit5: RO12-2. Bit6: RO32-1 Bit7: RO32-2
| 0xAF7B |  | 44923 |  | Unbalance Voltage Enable/Disable | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF7C |  | 44924 |  | Unbalance Voltage Threshold | word | R/W | 1 | 5 to 50 | 5
| 0xAF7D |  | 44925 |  | Unbalance Voltage Hysteresis | word | R/W | 1 | 1 to 10 | 2
| 0xAF7E |  | 44926 |  | Unbalance Voltage Waveform Trigger | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF7F |  | 44927 |  | Unbalance Voltage Event - switch to digital output D0X | word | R/W | 1 | 0: No output; 1:D01; 2: D02; 3: D03; 4: D04
| 0xAF80 |  | 44928 |  | Energy quality event-Unbalance Voltage output to RO | word | R/W | 1 | 0: No output Bit0: Output to relay RO11-1 Bit1: RO11-2. Bit2: RO31-1 Bit3: RO31-2. Bit4: RO12-1 Bit5: RO12-2. Bit6: RO32-1 Bit7: RO32-2
| 0xAF81 |  | 44929 |  | Current Dip Enable/Disable | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF82 |  | 44930 |  | Current Dip Threshold | word | R/W | 1 | 10 to 90 | 90
| 0xAF83 |  | 44931 |  | Current Dip Hysteresis | word | R/W | 1 | 1 to 10 | 2
| 0xAF84 |  | 44932 |  | Current Dip Waveform Trigger | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF85 |  | 44933 |  | Current Dip Event - switch to digital output D0X | word | R/W | 1 | 0: No output; 1:D01; 2: D02; 3: D03; 4: D04
| 0xAF86 |  | 44934 |  | Energy quality event-Current Dip output to RO | word | R/W | 1 | 0: No output Bit0: Output to relay RO11-1 Bit1: RO11-2. Bit2: RO31-1 Bit3: RO31-2. Bit4: RO12-1 Bit5: RO12-2. Bit6: RO32-1 Bit7: RO32-2
| 0xAF87 |  | 44935 |  | Current Swell Enable/Disable | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF88 |  | 44936 |  | Current Swell Threshold | word | R/W | 1 | 110 to 150 | 110
| 0xAF89 |  | 44937 |  | Current Swell Hysteresis | word | R/W | 1 | 1 to 10 | 2
| 0xAF8A |  | 44938 |  | Current Swell Waveform Trigger | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF8B |  | 44939 |  | Current Swell Event - switch to digital output D0X | word | R/W | 1 | 0: No output; 1:D01; 2: D02; 3: D03; 4: D04
| 0xAF8C |  | 44940 |  | Energy quality event-Current Swell output to RO | word | R/W | 1 | 0: No output Bit0: Output to relay RO11-1 Bit1: RO11-2. Bit2: RO31-1 Bit3: RO31-2. Bit4: RO12-1 Bit5: RO12-2. Bit6: RO32-1 Bit7: RO32-2
| 0xAF8D |  | 44941 |  | Unbalance Current Enable/Disable | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF8E |  | 44942 |  | Unbalance Current Threshold | word | R/W | 1 | 5 to 50 | 5
| 0xAF8F |  | 44943 |  | Unbalance Current Hysteresis | word | R/W | 1 | 1 to 10 | 2
| 0xAF90 |  | 44944 |  | Unbalance Current Waveform Trigger | word | R/W | 1 | 0: disable; 1: enable | 0
| 0xAF91 |  | 44945 |  | Unbalance Current Event - switch to digital output D0X | word | R/W | 1 | 0: No output; 1:D01; 2: D02; 3: D03; 4: D04
| 0xAF92 |  | 44946 |  | Energy quality event-Unbalance Current output to RO | word | R/W | 1 | 0: No output Bit0: Output to relay RO11-1 Bit1: RO11-2. Bit2: RO31-1 Bit3: RO31-2. Bit4: RO12-1 Bit5: RO12-2. Bit6: RO32-1 Bit7: RO32-2
45
Event Record Reading Area(Log)
| 0xAF96 |  | 44950 |  | Latest event record group number | word | R | 1
| 0xAF97 |  | 44951 |  | Read event record first group number | word | R/W | 1
| 0xAF98 |  | 44952 |  | Item number of every reading | word | R/W | 1
| 0xAF99 |  | 44953 |  | Time Stamp, UTC | uint32 | R | 2
| 0xAF9B |  | 44955 |  | Time Stamp, Ms | uint16 | R | 1
| 0xAF9C |  | 44956 |  | Event Trigger Info | uint16 | R | 1 | Bit 0-2: Phase A,B,C Bit 3-6: Dip, Swell, Unbalance, Interrupt Bit 7: Voltage or Current, Voltage:0 , Current:1
| 0xAF9D | 0xAF9E | 44957 | 44958 | Exterm Value 1 | float | R | 2
| 0xAF9F | 0xAFA0 | 44959 | 44960 | Exterm Value 2 | float | R | 2
| 0xAFA1 | 0xAFA2 | 44961 | 44962 | Exterm Value 3 | float | R | 2
| 0xAFA3 | 0xAFA4 | 44963 | 44964 | Event Duration | uint32 | R | 2
| 0xAFA5 | 0xAFA6 | 44965 | 44966 | Pading 1 | uint32 | R | 2
| 0xAFA7 | 0xAFA8 | 44967 | 44968 | Pading 2 | uint32 | R | 2
19
| 0xAFA9 | 0xAFB8 | 44969 | 44984 | 2nd event record |  | R | 16
| 0xAFB9 | 0xAFC8 | 44985 | 45000 | 3rd event record |  | R | 16
| 0xAFC9 | 0xAFD8 | 45001 | 45016 | 4th event record |  | R | 16
| 0xAFD9 | 0xAFE8 | 45017 | 45032 | 5th event record |  | R | 16
| 0xAFE9 | 0xAFF8 | 45033 | 45048 | 6th event record |  | R | 16
| 0xAFF9 | 0xB008 | 45049 | 45064 | 7th event record |  | R | 16
96

## TOU Default Setting
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value | Note
TOU factory default settings
0x6A command for writing | 0xF3FE |  | 62462 |  | Clear factory value of multiple rates time zone | word | R/W | 1 |  |  |  | Send 0xAA to clear
| 0xF3FF |  | 62463 |  | Note: Before setting factory value of multiple rates time zone, this command is needed |  |  | 1 |  |  |  | Not effective
| 0xF400 |  | 62464 |  | Year time zone number | word | R/W | 1
| 0xF401 |  | 62465 |  | day time section record number | word | R/W | 1
| 0xF402 |  | 62466 |  | day time section number | word | R/W | 1
| 0xF403 |  | 62467 |  | Tarif number | word | R/W | 1
| 0xF404 |  | 62468 |  | Week off（0: no week off day;1: Sunday;2: Saturday;3: Sunday, Saturday） | word | R/W | 1
| 0xF405 |  | 62469 |  | Week off time section | word | R/W | 1
| 0xF406 |  | 62470 |  | Special day number | word | R/W | 1
| 0xF407 |  | 62471 |  | Enable TOU | word | R/W | 1
| 0xF408 |  | 62472 |  | Enable TOU time setup restoring to factory value | word | R/W | 1
| 0xF409 |  | 62473 |  | Tou month settlement model 0: nature weekend） | word | R/W | 1
| 0xF40A |  | 62474 |  | Tou month settlement time: day （default: 1） | word | R/W | 1
| 0xF40B |  | 62475 |  | Tou month settlement time: hour （default: 0） | word | R/W | 1
| 0xF40C |  | 62476 |  | Tou month settlement time: minute （default: 0） | word | R/W | 1
| 0xF40D |  | 62477 |  | Tou month settlement time: second （default: 0） | word | R/W | 1
| 0xF40E |  | 62478 |  | Fault state word（default） | word | R/W | 1
| 0xF420 | 0xF422 | 62496 | 62498 | 1st time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF423 | 0xF425 | 62499 | 62501 | 2nd time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF426 | 0xF428 | 62502 | 62504 | 3rd time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF429 | 0xF42B | 62505 | 62507 | 4th time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF42C | 0xF42E | 62508 | 62510 | 5th time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF42F | 0xF431 | 62511 | 62513 | 6th time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF432 | 0xF434 | 62514 | 62516 | 7th time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF435 | 0xF437 | 62517 | 62519 | 8th time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF438 | 0xF43A | 62520 | 62522 | 9th time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF43B | 0xF43D | 62523 | 62525 | 10th time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF43E | 0xF440 | 62526 | 62528 | 11th time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF441 | 0xF443 | 62529 | 62531 | 12th time zone beginning date and day section record number(month, day, hour section number) |  | R/W | 3
| 0xF444 | 0xF446 | 62532 | 62534 | 1st day time section, 1st time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF447 | 0xF449 | 62535 | 62537 | 1st day time section, 2nd time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF44A | 0xF44C | 62538 | 62540 | 1st day time section, 3rd time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF44D | 0xF44F | 62541 | 62543 | 1st day time section, 4th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF450 | 0xF452 | 62544 | 62546 | 1st day time section, 5th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF453 | 0xF455 | 62547 | 62549 | 1st day time section, 6th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF456 | 0xF458 | 62550 | 62552 | 1st day time section, 7th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF459 | 0xF45B | 62553 | 62555 | 1st day time section, 8th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF45C | 0xF45E | 62556 | 62558 | 1st day time section, 9th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF45F | 0xF461 | 62559 | 62561 | 1st day time section, 10th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF462 | 0xF464 | 62562 | 62564 | 1st day time section, 11th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF465 | 0xF467 | 62565 | 62567 | 1st day time section, 12th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF468 | 0xF46A | 62568 | 62570 | 1st day time section, 13th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF46B | 0xF46D | 62571 | 62573 | 1st day time section, 14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 3
| 0xF46E | 0xF497 | 62574 | 62615 | 2nd day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF498 | 0xF4C1 | 62616 | 62657 | 3rd day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF4C2 | 0xF4EB | 62658 | 62699 | 4th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF4EC | 0xF515 | 62700 | 62741 | 5th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF516 | 0xF53F | 62742 | 62783 | 6th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF540 | 0xF569 | 62784 | 62825 | 7th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF56A | 0xF593 | 62826 | 62867 | 8th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF594 | 0xF5BD | 62868 | 62909 | 9th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF5BE | 0xF5E7 | 62910 | 62951 | 10th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF5E8 | 0xF611 | 62952 | 62993 | 11th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF612 | 0xF63B | 62994 | 63035 | 12th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF63C | 0xF665 | 63036 | 63077 | 13th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF666 | 0xF68F | 63078 | 63119 | 14th day time section, 1st -14th time section begin time and tariff number(hour,minute,tariff） |  | R/W | 42
| 0xF690 | 0xF692 | 63120 | 63122 | 1st special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF693 | 0xF695 | 63123 | 63125 | 2nd special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF696 | 0xF698 | 63126 | 63128 | 3rd special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF699 | 0xF69B | 63129 | 63131 | 4th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF69C | 0xF69E | 63132 | 63134 | 5th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF69F | 0xF6A1 | 63135 | 63137 | 6th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6A2 | 0xF6A4 | 63138 | 63140 | 7th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6A5 | 0xF6A7 | 63141 | 63143 | 8th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6A8 | 0xF6AA | 63144 | 63146 | 9th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6AB | 0xF6AD | 63147 | 63149 | 10th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6AE | 0xF6B0 | 63150 | 63152 | 11th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6B1 | 0xF6B3 | 63153 | 63155 | 12th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6B4 | 0xF6B6 | 63156 | 63158 | 13th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6B7 | 0xF6B9 | 63159 | 63161 | 14th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6BA | 0xF6BC | 63162 | 63164 | 15th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6BD | 0xF6BF | 63165 | 63167 | 16th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6C0 | 0xF6C2 | 63168 | 63170 | 17th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6C3 | 0xF6C5 | 63171 | 63173 | 18th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6C6 | 0xF6C8 | 63174 | 63176 | 19th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6C9 | 0xF6CB | 63177 | 63179 | 20th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6CC | 0xF6CE | 63180 | 63182 | 21st special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6CF | 0xF6D1 | 63183 | 63185 | 22nd special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6D2 | 0xF6D4 | 63186 | 63188 | 23rd special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6D5 | 0xF6D7 | 63189 | 63191 | 24th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6D8 | 0xF6DA | 63192 | 63194 | 25th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6DB | 0xF6DD | 63195 | 63197 | 26th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6DE | 0xF6E0 | 63198 | 63200 | 27th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6E1 | 0xF6E3 | 63201 | 63203 | 28th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6E4 | 0xF6E6 | 63204 | 63206 | 29th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6E7 | 0xF6E9 | 63207 | 63209 | 30th special date and its time section number(month, day, time section number） |  | R/W | 3
| 0xF6EA |  | 63210 |  | Default enable/disable ”Holiday many year setup“ |  | R/W | 1
| 0xF6EB |  | 63211 |  | Default beginning year of ”Holiday many year setup“ |  | R/W | 1
| 0xF6EC |  | 63212 |  | Default ending year of ”Holiday many year setup“ |  | R/W | 1
10years holidy factory default settings
0x6A command for writing | 0xF700 | 0xF795 | 63232 | 63381 | Setup address for ten year holiday by PC | word | R/W | 150
PROFIBUS address
0x10 command for writing | 0xFF00 |  | 65280 |  | PROFIBUS address | word | R/W | 1

## TOU Readings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Current Month Accumulative TOU Energy: 03H Read
| 0x7200 | 0x7201 | 29184 | 29185 | sharp - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7202 | 0x7203 | 29186 | 29187 | sharp - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7204 | 0x7205 | 29188 | 29189 | sharp - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7206 | 0x7207 | 29190 | 29191 | sharp - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7208 | 0x7209 | 29192 | 29193 | sharp - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x720A | 0x720B | 29194 | 29195 | peak - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x720C | 0x720D | 29196 | 29197 | peak - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x720E | 0x720F | 29198 | 29199 | peak - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7210 | 0x7211 | 29200 | 29201 | peak - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7212 | 0x7213 | 29202 | 29203 | peak - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7214 | 0x7215 | 29204 | 29205 | valley - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7216 | 0x7217 | 29206 | 29207 | valley - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7218 | 0x7219 | 29208 | 29209 | valley - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x721A | 0x721B | 29210 | 29211 | valley - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x721C | 0x721D | 29212 | 29213 | valley - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x721E | 0x721F | 29214 | 29215 | normal - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7220 | 0x7221 | 29216 | 29217 | normal - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7222 | 0x7223 | 29218 | 29219 | normal - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7224 | 0x7225 | 29220 | 29221 | normal - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7226 | 0x7227 | 29222 | 29223 | normal - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7228 | 0x7229 | 29224 | 29225 | total - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x722A | 0x722B | 29226 | 29227 | total - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x722C | 0x722D | 29228 | 29229 | total - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x722E | 0x722F | 29230 | 29231 | total - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7230 | 0x7231 | 29232 | 29233 | total - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
Previous Month Accumulative TOU Energy: 03H Read
| 0x7232 | 0x7233 | 29234 | 29235 | sharp - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7234 | 0x7235 | 29236 | 29237 | sharp - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7236 | 0x7237 | 29238 | 29239 | sharp - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7238 | 0x7239 | 29240 | 29241 | sharp - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x723A | 0x723B | 29242 | 29243 | sharp - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x723C | 0x723D | 29244 | 29245 | peak - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x723E | 0x723F | 29246 | 29247 | peak - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7240 | 0x7241 | 29248 | 29249 | peak - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7242 | 0x7243 | 29250 | 29251 | peak - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7244 | 0x7245 | 29252 | 29253 | peak - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7246 | 0x7247 | 29254 | 29255 | valley - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7248 | 0x7249 | 29256 | 29257 | valley - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x724A | 0x724B | 29258 | 29259 | valley - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x724C | 0x724D | 29260 | 29261 | valley - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x724E | 0x724F | 29262 | 29263 | valley - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7250 | 0x7251 | 29264 | 29265 | normal - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7252 | 0x7253 | 29266 | 29267 | normal - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7254 | 0x7255 | 29268 | 29269 | normal - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7256 | 0x7257 | 29270 | 29271 | normal - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7258 | 0x7259 | 29272 | 29273 | normal - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x725A | 0x725B | 29274 | 29275 | total - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x725C | 0x725D | 29276 | 29277 | total - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x725E | 0x725F | 29278 | 29279 | total - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7260 | 0x7261 | 29280 | 29281 | total - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7262 | 0x7263 | 29282 | 29283 | total - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
Current Month Incremental TOU Energy: 03H Read
| 0x7300 | 0x7301 | 29440 | 29441 | sharp - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7302 | 0x7303 | 29442 | 29443 | sharp - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7304 | 0x7305 | 29444 | 29445 | sharp - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7306 | 0x7307 | 29446 | 29447 | sharp - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7308 | 0x7309 | 29448 | 29449 | sharp - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x730A | 0x730B | 29450 | 29451 | peak - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x730C | 0x730D | 29452 | 29453 | peak - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x730E | 0x730F | 29454 | 29455 | peak - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7310 | 0x7311 | 29456 | 29457 | peak - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7312 | 0x7313 | 29458 | 29459 | peak - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7314 | 0x7315 | 29460 | 29461 | valley - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7316 | 0x7317 | 29462 | 29463 | valley - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7318 | 0x7319 | 29464 | 29465 | valley - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x731A | 0x731B | 29466 | 29467 | valley - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x731C | 0x731D | 29468 | 29469 | valley - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x731E | 0x731F | 29470 | 29471 | normal - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7320 | 0x7321 | 29472 | 29473 | normal - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7322 | 0x7323 | 29474 | 29475 | normal - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7324 | 0x7325 | 29476 | 29477 | normal - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7326 | 0x7327 | 29478 | 29479 | normal - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7328 | 0x7329 | 29480 | 29481 | total - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x732A | 0x732B | 29482 | 29483 | total - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x732C | 0x732D | 29484 | 29485 | total - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x732E | 0x732F | 29486 | 29487 | total - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7330 | 0x7331 | 29488 | 29489 | total - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
Previous Month Incremental TOU Energy: 03H Read
| 0x7332 | 0x7333 | 29490 | 29491 | sharp - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7334 | 0x7335 | 29492 | 29493 | sharp - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7336 | 0x7337 | 29494 | 29495 | sharp - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7338 | 0x7339 | 29496 | 29497 | sharp - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x733A | 0x733B | 29498 | 29499 | sharp - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x733C | 0x733D | 29500 | 29501 | peak - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x733E | 0x733F | 29502 | 29503 | peak - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7340 | 0x7341 | 29504 | 29505 | peak - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7342 | 0x7343 | 29506 | 29507 | peak - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7344 | 0x7345 | 29508 | 29509 | peak - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7346 | 0x7347 | 29510 | 29511 | valley - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7348 | 0x7349 | 29512 | 29513 | valley - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x734A | 0x734B | 29514 | 29515 | valley - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x734C | 0x734D | 29516 | 29517 | valley - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x734E | 0x734F | 29518 | 29519 | valley - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x7350 | 0x7351 | 29520 | 29521 | normal - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x7352 | 0x7353 | 29522 | 29523 | normal - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x7354 | 0x7355 | 29524 | 29525 | normal - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7356 | 0x7357 | 29526 | 29527 | normal - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7358 | 0x7359 | 29528 | 29529 | normal - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
| 0x735A | 0x735B | 29530 | 29531 | total - Ep_Imp Import active energy | uint32 | R/W | 2 | 0~999999999
| 0x735C | 0x735D | 29532 | 29533 | total - Ep_Exp Export active energy | uint32 | R/W | 2 | 0~999999999
| 0x735E | 0x735F | 29534 | 29535 | total - Eq_Imp Import reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7360 | 0x7361 | 29536 | 29537 | total - Eq_Exp Export reactive energy | uint32 | R/W | 2 | 0~999999999
| 0x7362 | 0x7363 | 29538 | 29539 | total - Es Apparent energy | uint32 | R/W | 2 | 0~999999999
Current Month TOU Max Demand
| 0x7500 | 0x7503 | 29952 | 29955 | sharp - max import active power demand and timestamp (format: max value; year month; date hour; minute second) | int16 | R | 4
| 0x7504 | 0x7507 | 29956 | 29959 | sharp - max export active power demand and timestamp | int16 | R | 4
| 0x7508 | 0x750B | 29960 | 29963 | sharp - max import reactive power demand and timestamp | int16 | R | 4
| 0x750C | 0x750F | 29964 | 29967 | sharp - max export reactive power demand and timestamp | int16 | R | 4
| 0x7510 | 0x7513 | 29968 | 29971 | sharp - max apparent power demand and timestamp | int16 | R | 4
| 0x7514 | 0x7517 | 29972 | 29975 | sharp - max Ia demand and timestamp | int16 | R | 4
| 0x7518 | 0x751B | 29976 | 29979 | sharp - max Ib demand and timestamp | int16 | R | 4
| 0x751C | 0x751F | 29980 | 29983 | sharp - max Ic demand and timestamp | int16 | R | 4
| 0x7520 | 0x7523 | 29984 | 29987 | peak - max import active power demand and timestamp | int16 | R | 4
| 0x7524 | 0x7527 | 29988 | 29991 | peak - max export active power demand and timestamp | int16 | R | 4
| 0x7528 | 0x752B | 29992 | 29995 | peak - max import reactive power demand and timestamp | int16 | R | 4
| 0x752C | 0x752F | 29996 | 29999 | peak - max export reactive power demand and timestamp | int16 | R | 4
| 0x7530 | 0x7533 | 30000 | 30003 | peak - max apparent power demand and timestamp | int16 | R | 4
| 0x7534 | 0x7537 | 30004 | 30007 | peak - max Ia demand and timestamp | int16 | R | 4
| 0x7538 | 0x753B | 30008 | 30011 | peak - max Ib demand and timestamp | int16 | R | 4
| 0x753C | 0x753F | 30012 | 30015 | peak - max Ic demand and timestamp | int16 | R | 4
| 0x7540 | 0x7543 | 30016 | 30019 | valley - max import active power demand and timestamp | int16 | R | 4
| 0x7544 | 0x7547 | 30020 | 30023 | valley - max export active power demand and timestamp | int16 | R | 4
| 0x7548 | 0x754B | 30024 | 30027 | valley - max import reactive power demand and timestamp | int16 | R | 4
| 0x754C | 0x754F | 30028 | 30031 | valley - max export reactive power demand and timestamp | int16 | R | 4
| 0x7550 | 0x7553 | 30032 | 30035 | valley - max apparent power demand and timestamp | int16 | R | 4
| 0x7554 | 0x7557 | 30036 | 30039 | valley - max Ia demand and timestamp | int16 | R | 4
| 0x7558 | 0x755B | 30040 | 30043 | valley - max Ib demand and timestamp | int16 | R | 4
| 0x755C | 0x755F | 30044 | 30047 | valley - max Ic demand and timestamp | int16 | R | 4
| 0x7560 | 0x7563 | 30048 | 30051 | normal - max import active power demand and timestamp | int16 | R | 4
| 0x7564 | 0x7567 | 30052 | 30055 | normal - max export active power demand and timestamp | int16 | R | 4
| 0x7568 | 0x756B | 30056 | 30059 | normal - max import reactive power demand and timestamp | int16 | R | 4
| 0x756C | 0x756F | 30060 | 30063 | normal - max export reactive power demand and timestamp | int16 | R | 4
| 0x7570 | 0x7573 | 30064 | 30067 | normal - max apparent power demand and timestamp | int16 | R | 4
| 0x7574 | 0x7577 | 30068 | 30071 | normal - max Ia demand and timestamp | int16 | R | 4
| 0x7578 | 0x757B | 30072 | 30075 | normal - max Ib demand and timestamp | int16 | R | 4
| 0x757C | 0x757F | 30076 | 30079 | normal - max Ic demand and timestamp | int16 | R | 4
| 0x7580 | 0x7583 | 30080 | 30083 | total - max import active power demand and timestamp | int16 | R | 4
| 0x7584 | 0x7587 | 30084 | 30087 | total - max export active power demand and timestamp | int16 | R | 4
| 0x7588 | 0x758B | 30088 | 30091 | total - max import reactive power demand and timestamp | int16 | R | 4
| 0x758C | 0x758F | 30092 | 30095 | total - max export reactive power demand and timestamp | int16 | R | 4
| 0x7590 | 0x7593 | 30096 | 30099 | total - max apparent power demand and timestamp | int16 | R | 4
| 0x7594 | 0x7597 | 30100 | 30103 | total - max Ia demand and timestamp | int16 | R | 4
| 0x7598 | 0x759B | 30104 | 30107 | total - max Ib demand and timestamp | int16 | R | 4
| 0x759C | 0x759F | 30108 | 30111 | total - max Ic demand and timestamp | int16 | R | 4
Previous Month TOU Max Demand
| 0x7600 | 0x7603 | 30208 | 30211 | sharp - max import active power demand and timestamp (format: max value; year month; date hour; minute second) | int16 | R | 4
| 0x7604 | 0x7607 | 30212 | 30215 | sharp - max export active power demand and timestamp | int16 | R | 4
| 0x7608 | 0x760B | 30216 | 30219 | sharp - max import reactive power demand and timestamp | int16 | R | 4
| 0x760C | 0x760F | 30220 | 30223 | sharp - max export reactive power demand and timestamp | int16 | R | 4
| 0x7610 | 0x7613 | 30224 | 30227 | sharp - max apparent power demand and timestamp | int16 | R | 4
| 0x7614 | 0x7617 | 30228 | 30231 | sharp - max Ia demand and timestamp | int16 | R | 4
| 0x7618 | 0x761B | 30232 | 30235 | sharp - max Ib demand and timestamp | int16 | R | 4
| 0x761C | 0x761F | 30236 | 30239 | sharp - max Ic demand and timestamp | int16 | R | 4
| 0x7620 | 0x7623 | 30240 | 30243 | peak - max import active power demand and timestamp | int16 | R | 4
| 0x7624 | 0x7627 | 30244 | 30247 | peak - max export active power demand and timestamp | int16 | R | 4
| 0x7628 | 0x762B | 30248 | 30251 | peak - max import reactive power demand and timestamp | int16 | R | 4
| 0x762C | 0x762F | 30252 | 30255 | peak - max export reactive power demand and timestamp | int16 | R | 4
| 0x7630 | 0x7633 | 30256 | 30259 | peak - max apparent power demand and timestamp | int16 | R | 4
| 0x7634 | 0x7637 | 30260 | 30263 | peak - max Ia demand and timestamp | int16 | R | 4
| 0x7638 | 0x763B | 30264 | 30267 | peak - max Ib demand and timestamp | int16 | R | 4
| 0x763C | 0x763F | 30268 | 30271 | peak - max Ic demand and timestamp | int16 | R | 4
| 0x7640 | 0x7643 | 30272 | 30275 | valley - max import active power demand and timestamp | int16 | R | 4
| 0x7644 | 0x7647 | 30276 | 30279 | valley - max export active power demand and timestamp | int16 | R | 4
| 0x7648 | 0x764B | 30280 | 30283 | valley - max import reactive power demand and timestamp | int16 | R | 4
| 0x764C | 0x764F | 30284 | 30287 | valley - max export reactive power demand and timestamp | int16 | R | 4
| 0x7650 | 0x7653 | 30288 | 30291 | valley - max apparent power demand and timestamp | int16 | R | 4
| 0x7654 | 0x7657 | 30292 | 30295 | valley - max Ia demand and timestamp | int16 | R | 4
| 0x7658 | 0x765B | 30296 | 30299 | valley - max Ib demand and timestamp | int16 | R | 4
| 0x765C | 0x765F | 30300 | 30303 | valley - max Ic demand and timestamp | int16 | R | 4
| 0x7660 | 0x7663 | 30304 | 30307 | normal - max import active power demand and timestamp | int16 | R | 4
| 0x7664 | 0x7667 | 30308 | 30311 | normal - max export active power demand and timestamp | int16 | R | 4
| 0x7668 | 0x766B | 30312 | 30315 | normal - max import reactive power demand and timestamp | int16 | R | 4
| 0x766C | 0x766F | 30316 | 30319 | normal - max export reactive power demand and timestamp | int16 | R | 4
| 0x7670 | 0x7673 | 30320 | 30323 | normal - max apparent power demand and timestamp | int16 | R | 4
| 0x7674 | 0x7677 | 30324 | 30327 | normal - max Ia demand and timestamp | int16 | R | 4
| 0x7678 | 0x767B | 30328 | 30331 | normal - max Ib demand and timestamp | int16 | R | 4
| 0x767C | 0x767F | 30332 | 30335 | normal - max Ic demand and timestamp | int16 | R | 4
| 0x7680 | 0x7683 | 30336 | 30339 | total - max import active power demand and timestamp | int16 | R | 4
| 0x7684 | 0x7687 | 30340 | 30343 | total - max export active power demand and timestamp | int16 | R | 4
| 0x7688 | 0x768B | 30344 | 30347 | total - max import reactive power demand and timestamp | int16 | R | 4
| 0x768C | 0x768F | 30348 | 30351 | total - max export reactive power demand and timestamp | int16 | R | 4
| 0x7690 | 0x7693 | 30352 | 30355 | total - max apparent power demand and timestamp | int16 | R | 4
| 0x7694 | 0x7697 | 30356 | 30359 | total - max Ia demand and timestamp | int16 | R | 4
| 0x7698 | 0x769B | 30360 | 30363 | total - max Ib demand and timestamp | int16 | R | 4
| 0x769C | 0x769F | 30364 | 30367 | total - max Ic demand and timestamp | int16 | R | 4

## TOU Settings
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
Daylight Savings Time Settings: 03H Read, 10H Write
| 0x7700 |  | 30464 |  | DST enable | word | R/W | 1 | 0: disable 1: enable
| 0x7701 |  | 30465 |  | DST format | word | R/W | 1 | 0: format 1(fixed date) 1: format 2 (non fixed date)
Format 1: Fixed Date
| 0x7702 |  | 30466 |  | DST Start Month | word | R/W | 1 | 1~12
| 0x7703 |  | 30467 |  | DST Start Day | word | R/W | 1 | 1~31
| 0x7704 |  | 30468 |  | DST Start Hour | word | R/W | 1 | 0-23
| 0x7705 |  | 30469 |  | DST Start Min | word | R/W | 1 | 0-59
| 0x7706 |  | 30470 |  | DST Start Adjust time (Unit: Min) | word | R/W | 1 | 1-120
| 0x7707 |  | 30471 |  | DST End Month | word | R/W | 1 | 1~12
| 0x7708 |  | 30472 |  | DST End Day | word | R/W | 1 | 1~31
| 0x7709 |  | 30473 |  | DST End Hour | word | R/W | 1 | 0-23
| 0x770A |  | 30474 |  | DST End Minute | word | R/W | 1 | 0-59
| 0x770B |  | 30475 |  | DST End Adjust time (Unit: Minute) | word | R/W | 1 | 1-120
Format 2: Non Fixed Date
| 0x770C |  | 30476 |  | DST Start Month | word | R/W | 1 | 1~12
| 0x770D |  | 30477 |  | DST Start Day | word | R/W | 1 | 0-6 0: Sunday 1~6: Monday to Saturday
| 0x770E |  | 30478 |  | DST Start Week | word | R/W | 1 | 1~5
| 0x770F |  | 30479 |  | DST Start Hour | word | R/W | 1 | 0-23
| 0x7710 |  | 30480 |  | DST Start Minute | word | R/W | 1 | 0-59
| 0x7711 |  | 30481 |  | DST Start Adjust time (Unit: Minute) | word | R/W | 1 | 1-120
| 0x7712 |  | 30482 |  | DST End Month | word | R/W | 1 | 1~12
| 0x7713 |  | 30483 |  | DST End Day | word | R/W | 1 | 0-6 0: Sunday 1~6 Monday to Saturday
| 0x7714 |  | 30484 |  | DST End Week | word | R/W | 1 | 1~5
| 0x7715 |  | 30485 |  | DST End Hour | word | R/W | 1 | 0-23
| 0x7716 |  | 30486 |  | DST End Minute | word | R/W | 1 | 0-59
| 0x7717 |  | 30487 |  | DST End Adjust time (Unit: Minute) | word | R/W | 1 | 1-120
TOU Basic Settings
| 0x7800 |  | 30720 |  | Number of seasons |  | R/W | 1 | 0~12
| 0x7801 |  | 30721 |  | Number of schedules |  | R/W | 1 | 0~14
| 0x7802 |  | 30722 |  | Number of segments |  | R/W | 1 | 0~14
| 0x7803 |  | 30723 |  | Number of tariffs |  | R/W | 1 | 0~3
| 0x7804 |  | 30724 |  | Weekend setting (Bit0: Sunday; Bit1-Bit6: Mon-Sat) bit=0: not weekend bit=1: is weekend |  | R/W | 1 | 0~127
| 0x7805 |  | 30725 |  | Weekend Schedule ID |  | R/W | 1 | 0~14
| 0x7806 |  | 30726 |  | Number of holidays |  | R/W | 1 | 0~30
| 0x7807 |  | 30727 |  | Enable TOU |  | R/W | 1 | 1: enable
| 0x7808 |  | 30728 |  | Restore factory settings |  | R/W | 1
| 0x7809 |  | 30729 |  | Monthly Billing Mode |  | R/W | 1
| 0x780A |  | 30730 |  | Billing time: day |  | R/W | 1 | 1~31
| 0x780B |  | 30731 |  | Billing time : hour |  | R/W | 1 | 0~23
| 0x780C |  | 30732 |  | Billing time: minute |  | R/W | 1 | 0~59
| 0x780D |  | 30733 |  | Billing time: second |  | R/W | 1 | 0~59
| 0x780E |  | 30734 |  | Error Code |  | R/W | 1 | 0: Settings correct
Season settings
| 0x7820 | 0x7822 | 30752 | 30754 | TOU Season 1 |  | R/W | 3 | In format of month, day, schedule ID
| 0x7823 | 0x7825 | 30755 | 30757 | TOU Season 2 |  | R/W | 3
| 0x7826 | 0x7828 | 30758 | 30760 | TOU Season 3 |  | R/W | 3
| 0x7829 | 0x782B | 30761 | 30763 | TOU Season 4 |  | R/W | 3
| 0x782C | 0x782E | 30764 | 30766 | TOU Season 5 |  | R/W | 3
| 0x782F | 0x7831 | 30767 | 30769 | TOU Season 6 |  | R/W | 3
| 0x7832 | 0x7834 | 30770 | 30772 | TOU Season 7 |  | R/W | 3
| 0x7835 | 0x7837 | 30773 | 30775 | TOU Season 8 |  | R/W | 3
| 0x7838 | 0x783A | 30776 | 30778 | TOU Season 9 |  | R/W | 3
| 0x783B | 0x783D | 30779 | 30781 | TOU Season 10 |  | R/W | 3
| 0x783E | 0x7840 | 30782 | 30784 | TOU Season 11 |  | R/W | 3
| 0x7841 | 0x7843 | 30785 | 30787 | TOU Season 12 |  | R/W | 3
Schedule settings
| 0x7844 | 0x7846 | 30788 | 30790 | Schedule 1 Segment 1 settings In format of hour, minutes, segment ID |  | R/W | 3
| 0x7847 | 0x7849 | 30791 | 30793 | Schedule 1 Segment 2 settings |  | R/W | 3
| 0x784A | 0x784C | 30794 | 30796 | Schedule 1 Segment 3 settings |  | R/W | 3
| 0x784D | 0x784F | 30797 | 30799 | Schedule 1 Segment 4 settings |  | R/W | 3
| 0x7850 | 0x7852 | 30800 | 30802 | Schedule 1 Segment 5 settings |  | R/W | 3
| 0x7853 | 0x7855 | 30803 | 30805 | Schedule 1 Segment 6 settings |  | R/W | 3
| 0x7856 | 0x7858 | 30806 | 30808 | Schedule 1 Segment 7 settings |  | R/W | 3
| 0x7859 | 0x785B | 30809 | 30811 | Schedule 1 Segment 8 settings |  | R/W | 3
| 0x785C | 0x785E | 30812 | 30814 | Schedule 1 Segment 9 settings |  | R/W | 3
| 0x785F | 0x7861 | 30815 | 30817 | Schedule 1 Segment 10 settings |  | R/W | 3
| 0x7862 | 0x7864 | 30818 | 30820 | Schedule 1 Segment 11 settings |  | R/W | 3
| 0x7865 | 0x7867 | 30821 | 30823 | Schedule 1 Segment 12 settings |  | R/W | 3
| 0x7868 | 0x786A | 30824 | 30826 | Schedule 1 Segment 13 settings |  | R/W | 3
| 0x786B | 0x786D | 30827 | 30829 | Schedule 1 Segment 14 settings |  | R/W | 3
| 0x786E | 0x7897 | 30830 | 30871 | Schedule 2 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x7898 | 0x78C1 | 30872 | 30913 | Schedule 3 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x78C2 | 0x78EB | 30914 | 30955 | Schedule 4 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x78EC | 0x7915 | 30956 | 30997 | Schedule 5 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x7916 | 0x793F | 30998 | 31039 | Schedule 6 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x7940 | 0x7969 | 31040 | 31081 | Schedule 7 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x796A | 0x7993 | 31082 | 31123 | Schedule 8 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x7994 | 0x79BD | 31124 | 31165 | Schedule 9 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x79BE | 0x79E7 | 31166 | 31207 | Schedule 10 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x79E8 | 0x7A11 | 31208 | 31249 | Schedule 11 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x7A12 | 0x7A3B | 31250 | 31291 | Schedule 12 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x7A3C | 0x7A65 | 31292 | 31333 | Schedule 13 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
| 0x7A66 | 0x7A8F | 31334 | 31375 | Schedule 14 settings |  | R/W | 42 | Same as schedule 1 segment 1-14 settings
Holiday settings
| 0x7A90 | 0x7A92 | 31376 | 31378 | 1st Holiday settings In format of month, day, schedule ID |  | R/W | 3
| 0x7A93 | 0x7A95 | 31379 | 31381 | 2nd Holiday settings |  | R/W | 3
| 0x7A96 | 0x7A98 | 31382 | 31384 | 3rd Holiday settings |  | R/W | 3
| 0x7A99 | 0x7A9B | 31385 | 31387 | 4th Holiday settings |  | R/W | 3
| 0x7A9C | 0x7A9E | 31388 | 31390 | 5th Holiday settings |  | R/W | 3
| 0x7A9F | 0x7AA1 | 31391 | 31393 | 6th Holiday settings |  | R/W | 3
| 0x7AA2 | 0x7AA4 | 31394 | 31396 | 7th Holiday settings |  | R/W | 3
| 0x7AA5 | 0x7AA7 | 31397 | 31399 | 8th Holiday settings |  | R/W | 3
| 0x7AA8 | 0x7AAA | 31400 | 31402 | 9th Holiday settings |  | R/W | 3
| 0x7AAB | 0x7AAD | 31403 | 31405 | 10th Holiday settings |  | R/W | 3
| 0x7AAE | 0x7AB0 | 31406 | 31408 | 11th Holiday settings |  | R/W | 3
| 0x7AB1 | 0x7AB3 | 31409 | 31411 | 12th Holiday settings |  | R/W | 3
| 0x7AB4 | 0x7AB6 | 31412 | 31414 | 13th Holiday settings |  | R/W | 3
| 0x7AB7 | 0x7AB9 | 31415 | 31417 | 14th Holiday settings |  | R/W | 3
| 0x7ABA | 0x7ABC | 31418 | 31420 | 15th Holiday settings |  | R/W | 3
| 0x7ABD | 0x7ABF | 31421 | 31423 | 16th Holiday settings |  | R/W | 3
| 0x7AC0 | 0x7AC2 | 31424 | 31426 | 17th Holiday settings |  | R/W | 3
| 0x7AC3 | 0x7AC5 | 31427 | 31429 | 18th Holiday settings |  | R/W | 3
| 0x7AC6 | 0x7AC8 | 31430 | 31432 | 19th Holiday settings |  | R/W | 3
| 0x7AC9 | 0x7ACB | 31433 | 31435 | 20th Holiday settings |  | R/W | 3
| 0x7ACC | 0x7ACE | 31436 | 31438 | 21st Holiday settings |  | R/W | 3
| 0x7ACF | 0x7AD1 | 31439 | 31441 | 22nd Holiday settings |  | R/W | 3
| 0x7AD2 | 0x7AD4 | 31442 | 31444 | 23rd Holiday settings |  | R/W | 3
| 0x7AD5 | 0x7AD7 | 31445 | 31447 | 24th Holiday settings |  | R/W | 3
| 0x7AD8 | 0x7ADA | 31448 | 31450 | 25th Holiday settings |  | R/W | 3
| 0x7ADB | 0x7ADD | 31451 | 31453 | 26th Holiday settings |  | R/W | 3
| 0x7ADE | 0x7AE0 | 31454 | 31456 | 27th Holiday settings |  | R/W | 3
| 0x7AE1 | 0x7AE3 | 31457 | 31459 | 28th Holiday settings |  | R/W | 3
| 0x7AE4 | 0x7AE6 | 31460 | 31462 | 29th Holiday settings |  | R/W | 3
| 0x7AE7 | 0x7AE9 | 31463 | 31465 | 30th Holiday settings |  | R/W | 3
| 0x7AEA |  | 31466 |  | Holiday Setting enable |  | R/W
| 0x7AEB |  | 31467 |  | Start Year |  | R/W
| 0x7AEC |  | 31468 |  | End Year |  | R/W
10 years holiday settings
| 0x7B00 | 0x7B02 | 31488 | 31490 | Year 1 holiday 1 settings In format of month, day, schedule ID |  | R/W | 3
| 0x7B03 | 0x7B05 | 31491 | 31493 | Year 1 holiday 2 settings |  | R/W | 3
| 0x7B06 | 0x7B08 | 31494 | 31496 | Year 1 holiday 3 settings |  | R/W | 3
| 0x7B09 | 0x7B0B | 31497 | 31499 | Year 1 holiday 4 settings |  | R/W | 3
| 0x7B0C | 0x7B0E | 31500 | 31502 | Year 1 holiday 5 settings |  | R/W | 3
| 0x7B0F | 0x7B11 | 31503 | 31505 | Year 1 holiday 6 settings |  | R/W | 3
| 0x7B12 | 0x7B14 | 31506 | 31508 | Year 1 holiday 7 settings |  | R/W | 3
| 0x7B15 | 0x7B17 | 31509 | 31511 | Year 1 holiday 8 settings |  | R/W | 3
| 0x7B18 | 0x7B1A | 31512 | 31514 | Year 1 holiday 9 settings |  | R/W | 3
| 0x7B1B | 0x7B1D | 31515 | 31517 | Year 1 holiday 10 settings |  | R/W | 3
| 0x7B1E | 0x7B20 | 31518 | 31520 | Year 1 holiday 11 settings |  | R/W | 3
| 0x7B21 | 0x7B23 | 31521 | 31523 | Year 1 holiday 12 settings |  | R/W | 3
| 0x7B24 | 0x7B26 | 31524 | 31526 | Year 1 holiday 13 settings |  | R/W | 3
| 0x7B27 | 0x7B29 | 31527 | 31529 | Year 1 holiday 14 settings |  | R/W | 3
| 0x7B2A | 0x7B2C | 31530 | 31532 | Year 1 holiday 15 settings |  | R/W | 3
| 0x7B2D | 0x7B2F | 31533 | 31535 | Year 1 holiday 16 settings |  | R/W | 3
| 0x7B30 | 0x7B32 | 31536 | 31538 | Year 1 holiday 17 settings |  | R/W | 3
| 0x7B33 | 0x7B35 | 31539 | 31541 | Year 1 holiday 18 settings |  | R/W | 3
| 0x7B36 | 0x7B38 | 31542 | 31544 | Year 1 holiday 19 settings |  | R/W | 3
| 0x7B39 | 0x7B3B | 31545 | 31547 | Year 1 holiday 20 settings |  | R/W | 3
| 0x7B3C | 0x7B3E | 31548 | 31550 | Year 1 holiday 21 settings |  | R/W | 3
| 0x7B3F | 0x7B41 | 31551 | 31553 | Year 1 holiday 22 settings |  | R/W | 3
| 0x7B42 | 0x7B44 | 31554 | 31556 | Year 1 holiday 23 settings |  | R/W | 3
| 0x7B45 | 0x7B47 | 31557 | 31559 | Year 1 holiday 24 settings |  | R/W | 3
| 0x7B48 | 0x7B4A | 31560 | 31562 | Year 1 holiday 25 settings |  | R/W | 3
| 0x7B4B | 0x7B4D | 31563 | 31565 | Year 1 holiday 26 settings |  | R/W | 3
| 0x7B4E | 0x7B50 | 31566 | 31568 | Year 1 holiday 27 settings |  | R/W | 3
| 0x7B51 | 0x7B53 | 31569 | 31571 | Year 1 holiday 28 settings |  | R/W | 3
| 0x7B54 | 0x7B56 | 31572 | 31574 | Year 1 holiday 29 settings |  | R/W | 3
| 0x7B57 | 0x7B59 | 31575 | 31577 | Year 1 holiday 30 settings |  | R/W | 3
| 0x7B5A |  | 31578 |  | Year 1 Settings Year |  | R/W
| 0x7B5B |  | 31579 |  | Year 1 Number of holidays |  | R/W
| 0x7B5C | 0x7B5E | 31580 | 31582 | Year 2 holiday 1 settings |  | R/W | 3
| 0x7B5F | 0x7B61 | 31583 | 31585 | Year 2 holiday 2 settings |  | R/W | 3
| 0x7B62 | 0x7B64 | 31586 | 31588 | Year 2 holiday 3 settings |  | R/W | 3
| 0x7B65 | 0x7B67 | 31589 | 31591 | Year 2 holiday 4 settings |  | R/W | 3
| 0x7B68 | 0x7B6A | 31592 | 31594 | Year 2 holiday 5 settings |  | R/W | 3
| 0x7B6B | 0x7B6D | 31595 | 31597 | Year 2 holiday 6 settings |  | R/W | 3
| 0x7B6E | 0x7B70 | 31598 | 31600 | Year 2 holiday 7 settings |  | R/W | 3
| 0x7B71 | 0x7B73 | 31601 | 31603 | Year 2 holiday 8 settings |  | R/W | 3
| 0x7B74 | 0x7B76 | 31604 | 31606 | Year 2 holiday 9 settings |  | R/W | 3
| 0x7B77 | 0x7B79 | 31607 | 31609 | Year 2 holiday 10 settings |  | R/W | 3
| 0x7B7A | 0x7B7C | 31610 | 31612 | Year 2 holiday 11 settings |  | R/W | 3
| 0x7B7D | 0x7B7F | 31613 | 31615 | Year 2 holiday 12 settings |  | R/W | 3
| 0x7B80 | 0x7B82 | 31616 | 31618 | Year 2 holiday 13 settings |  | R/W | 3
| 0x7B83 | 0x7B85 | 31619 | 31621 | Year 2 holiday 14 settings |  | R/W | 3
| 0x7B86 | 0x7B88 | 31622 | 31624 | Year 2 holiday 15 settings |  | R/W | 3
| 0x7B89 | 0x7B8B | 31625 | 31627 | Year 2 holiday 16 settings |  | R/W | 3
| 0x7B8C | 0x7B8E | 31628 | 31630 | Year 2 holiday 17 settings |  | R/W | 3
| 0x7B8F | 0x7B91 | 31631 | 31633 | Year 2 holiday 18 settings |  | R/W | 3
| 0x7B92 | 0x7B94 | 31634 | 31636 | Year 2 holiday 19 settings |  | R/W | 3
| 0x7B95 | 0x7B97 | 31637 | 31639 | Year 2 holiday 20 settings |  | R/W | 3
| 0x7B98 | 0x7B9A | 31640 | 31642 | Year 2 holiday 21 settings |  | R/W | 3
| 0x7B9B | 0x7B9D | 31643 | 31645 | Year 2 holiday 22 settings |  | R/W | 3
| 0x7B9E | 0x7BA0 | 31646 | 31648 | Year 2 holiday 23 settings |  | R/W | 3
| 0x7BA1 | 0x7BA3 | 31649 | 31651 | Year 2 holiday 24 settings |  | R/W | 3
| 0x7BA4 | 0x7BA6 | 31652 | 31654 | Year 2 holiday 25 settings |  | R/W | 3
| 0x7BA7 | 0x7BA9 | 31655 | 31657 | Year 2 holiday 26 settings |  | R/W | 3
| 0x7BAA | 0x7BAC | 31658 | 31660 | Year 2 holiday 27 settings |  | R/W | 3
| 0x7BAD | 0x7BAF | 31661 | 31663 | Year 2 holiday 28 settings |  | R/W | 3
| 0x7BB0 | 0x7BB2 | 31664 | 31666 | Year 2 holiday 29 settings |  | R/W | 3
| 0x7BB3 | 0x7BB5 | 31667 | 31669 | Year 2 holiday 30 settings |  | R/W | 3
| 0x7BB6 |  | 31670 |  | Year 2 Setting Year |  | R/W
| 0x7BB7 |  | 31671 |  | Year 2 Holiday Number setting |  | R/W
| 0x7BB8 | 0x7BBA | 31672 | 31674 | Year 3 holiday 1 settings |  | R/W | 3
| 0x7BBB | 0x7BBD | 31675 | 31677 | Year 3 holiday 2 settings |  | R/W | 3
| 0x7BBE | 0x7BC0 | 31678 | 31680 | Year 3 holiday 3 settings |  | R/W | 3
| 0x7BC1 | 0x7BC3 | 31681 | 31683 | Year 3 holiday 4 settings |  | R/W | 3
| 0x7BC4 | 0x7BC6 | 31684 | 31686 | Year 3 holiday 5 settings |  | R/W | 3
| 0x7BC7 | 0x7BC9 | 31687 | 31689 | Year 3 holiday 6 settings |  | R/W | 3
| 0x7BCA | 0x7BCC | 31690 | 31692 | Year 3 holiday 7 settings |  | R/W | 3
| 0x7BCD | 0x7BCF | 31693 | 31695 | Year 3 holiday 8 settings |  | R/W | 3
| 0x7BD0 | 0x7BD2 | 31696 | 31698 | Year 3 holiday 9 settings |  | R/W | 3
| 0x7BD3 | 0x7BD5 | 31699 | 31701 | Year 3 holiday 10 settings |  | R/W | 3
| 0x7BD6 | 0x7BD8 | 31702 | 31704 | Year 3 holiday 11 settings |  | R/W | 3
| 0x7BD9 | 0x7BDB | 31705 | 31707 | Year 3 holiday 12 settings |  | R/W | 3
| 0x7BDC | 0x7BDE | 31708 | 31710 | Year 3 holiday 13 settings |  | R/W | 3
| 0x7BDF | 0x7BE1 | 31711 | 31713 | Year 3 holiday 14 settings |  | R/W | 3
| 0x7BE2 | 0x7BE4 | 31714 | 31716 | Year 3 holiday 15 settings |  | R/W | 3
| 0x7BE5 | 0x7BE7 | 31717 | 31719 | Year 3 holiday 16 settings |  | R/W | 3
| 0x7BE8 | 0x7BEA | 31720 | 31722 | Year 3 holiday 17 settings |  | R/W | 3
| 0x7BEB | 0x7BED | 31723 | 31725 | Year 3 holiday 18 settings |  | R/W | 3
| 0x7BEE | 0x7BF0 | 31726 | 31728 | Year 3 holiday 19 settings |  | R/W | 3
| 0x7BF1 | 0x7BF3 | 31729 | 31731 | Year 3 holiday 20 settings |  | R/W | 3
| 0x7BF4 | 0x7BF6 | 31732 | 31734 | Year 3 holiday 21 settings |  | R/W | 3
| 0x7BF7 | 0x7BF9 | 31735 | 31737 | Year 3 holiday 22 settings |  | R/W | 3
| 0x7BFA | 0x7BFC | 31738 | 31740 | Year 3 holiday 23 settings |  | R/W | 3
| 0x7BFD | 0x7BFF | 31741 | 31743 | Year 3 holiday 24 settings |  | R/W | 3
| 0x7C00 | 0x7C02 | 31744 | 31746 | Year 3 holiday 25 settings |  | R/W | 3
| 0x7C03 | 0x7C05 | 31747 | 31749 | Year 3 holiday 26 settings |  | R/W | 3
| 0x7C06 | 0x7C08 | 31750 | 31752 | Year 3 holiday 27 settings |  | R/W | 3
| 0x7C09 | 0x7C0B | 31753 | 31755 | Year 3 holiday 28 settings |  | R/W | 3
| 0x7C0C | 0x7C0E | 31756 | 31758 | Year 3 holiday 29 settings |  | R/W | 3
| 0x7C0F | 0x7C11 | 31759 | 31761 | Year 3 holiday 30 settings |  | R/W | 3
| 0x7C12 |  | 31762 |  | Year 3 Setting Year |  | R/W
| 0x7C13 |  | 31763 |  | Year 3 Holiday Number setting |  | R/W
| 0x7C14 | 0x7C16 | 31764 | 31766 | Year 4 holiday 1 settings |  | R/W | 3
| 0x7C17 | 0x7C19 | 31767 | 31769 | Year 4 holiday 2 settings |  | R/W | 3
| 0x7C1A | 0x7C1C | 31770 | 31772 | Year 4 holiday 3 settings |  | R/W | 3
| 0x7C1D | 0x7C1F | 31773 | 31775 | Year 4 holiday 4 settings |  | R/W | 3
| 0x7C20 | 0x7C22 | 31776 | 31778 | Year 4 holiday 5 settings |  | R/W | 3
| 0x7C23 | 0x7C25 | 31779 | 31781 | Year 4 holiday 6 settings |  | R/W | 3
| 0x7C26 | 0x7C28 | 31782 | 31784 | Year 4 holiday 7 settings |  | R/W | 3
| 0x7C29 | 0x7C2B | 31785 | 31787 | Year 4 holiday 8 settings |  | R/W | 3
| 0x7C2C | 0x7C2E | 31788 | 31790 | Year 4 holiday 9 settings |  | R/W | 3
| 0x7C2F | 0x7C31 | 31791 | 31793 | Year 4 holiday 10 settings |  | R/W | 3
| 0x7C32 | 0x7C34 | 31794 | 31796 | Year 4 holiday 11 settings |  | R/W | 3
| 0x7C35 | 0x7C37 | 31797 | 31799 | Year 4 holiday 12 settings |  | R/W | 3
| 0x7C38 | 0x7C3A | 31800 | 31802 | Year 4 holiday 13 settings |  | R/W | 3
| 0x7C3B | 0x7C3D | 31803 | 31805 | Year 4 holiday 14 settings |  | R/W | 3
| 0x7C3E | 0x7C40 | 31806 | 31808 | Year 4 holiday 15 settings |  | R/W | 3
| 0x7C41 | 0x7C43 | 31809 | 31811 | Year 4 holiday 16 settings |  | R/W | 3
| 0x7C44 | 0x7C46 | 31812 | 31814 | Year 4 holiday 17 settings |  | R/W | 3
| 0x7C47 | 0x7C49 | 31815 | 31817 | Year 4 holiday 18 settings |  | R/W | 3
| 0x7C4A | 0x7C4C | 31818 | 31820 | Year 4 holiday 19 settings |  | R/W | 3
| 0x7C4D | 0x7C4F | 31821 | 31823 | Year 4 holiday 20 settings |  | R/W | 3
| 0x7C50 | 0x7C52 | 31824 | 31826 | Year 4 holiday 21 settings |  | R/W | 3
| 0x7C53 | 0x7C55 | 31827 | 31829 | Year 4 holiday 22 settings |  | R/W | 3
| 0x7C56 | 0x7C58 | 31830 | 31832 | Year 4 holiday 23 settings |  | R/W | 3
| 0x7C59 | 0x7C5B | 31833 | 31835 | Year 4 holiday 24 settings |  | R/W | 3
| 0x7C5C | 0x7C5E | 31836 | 31838 | Year 4 holiday 25 settings |  | R/W | 3
| 0x7C5F | 0x7C61 | 31839 | 31841 | Year 4 holiday 26 settings |  | R/W | 3
| 0x7C62 | 0x7C64 | 31842 | 31844 | Year 4 holiday 27 settings |  | R/W | 3
| 0x7C65 | 0x7C67 | 31845 | 31847 | Year 4 holiday 28 settings |  | R/W | 3
| 0x7C68 | 0x7C6A | 31848 | 31850 | Year 4 holiday 29 settings |  | R/W | 3
| 0x7C6B | 0x7C6D | 31851 | 31853 | Year 4 holiday 30 settings |  | R/W | 3
| 0x7C6E |  | 31854 |  | Year 4 Setting Year |  | R/W
| 0x7C6F |  | 31855 |  | Year 4 Holiday Number setting |  | R/W
| 0x7C70 | 0x7C72 | 31856 | 31858 | Year 5 holiday 1 settings |  | R/W | 3
| 0x7C73 | 0x7C75 | 31859 | 31861 | Year 5 holiday 2 settings |  | R/W | 3
| 0x7C76 | 0x7C78 | 31862 | 31864 | Year 5 holiday 3 settings |  | R/W | 3
| 0x7C79 | 0x7C7B | 31865 | 31867 | Year 5 holiday 4 settings |  | R/W | 3
| 0x7C7C | 0x7C7E | 31868 | 31870 | Year 5 holiday 5 settings |  | R/W | 3
| 0x7C7F | 0x7C81 | 31871 | 31873 | Year 5 holiday 6 settings |  | R/W | 3
| 0x7C82 | 0x7C84 | 31874 | 31876 | Year 5 holiday 7 settings |  | R/W | 3
| 0x7C85 | 0x7C87 | 31877 | 31879 | Year 5 holiday 8 settings |  | R/W | 3
| 0x7C88 | 0x7C8A | 31880 | 31882 | Year 5 holiday 9 settings |  | R/W | 3
| 0x7C8B | 0x7C8D | 31883 | 31885 | Year 5 holiday 10 settings |  | R/W | 3
| 0x7C8E | 0x7C90 | 31886 | 31888 | Year 5 holiday 11 settings |  | R/W | 3
| 0x7C91 | 0x7C93 | 31889 | 31891 | Year 5 holiday 12 settings |  | R/W | 3
| 0x7C94 | 0x7C96 | 31892 | 31894 | Year 5 holiday 13 settings |  | R/W | 3
| 0x7C97 | 0x7C99 | 31895 | 31897 | Year 5 holiday 14 settings |  | R/W | 3
| 0x7C9A | 0x7C9C | 31898 | 31900 | Year 5 holiday 15 settings |  | R/W | 3
| 0x7C9D | 0x7C9F | 31901 | 31903 | Year 5 holiday 16 settings |  | R/W | 3
| 0x7CA0 | 0x7CA2 | 31904 | 31906 | Year 5 holiday 17 settings |  | R/W | 3
| 0x7CA3 | 0x7CA5 | 31907 | 31909 | Year 5 holiday 18 settings |  | R/W | 3
| 0x7CA6 | 0x7CA8 | 31910 | 31912 | Year 5 holiday 19 settings |  | R/W | 3
| 0x7CA9 | 0x7CAB | 31913 | 31915 | Year 5 holiday 20 settings |  | R/W | 3
| 0x7CAC | 0x7CAE | 31916 | 31918 | Year 5 holiday 21 settings |  | R/W | 3
| 0x7CAF | 0x7CB1 | 31919 | 31921 | Year 5 holiday 22 settings |  | R/W | 3
| 0x7CB2 | 0x7CB4 | 31922 | 31924 | Year 5 holiday 23 settings |  | R/W | 3
| 0x7CB5 | 0x7CB7 | 31925 | 31927 | Year 5 holiday 24 settings |  | R/W | 3
| 0x7CB8 | 0x7CBA | 31928 | 31930 | Year 5 holiday 25 settings |  | R/W | 3
| 0x7CBB | 0x7CBD | 31931 | 31933 | Year 5 holiday 26 settings |  | R/W | 3
| 0x7CBE | 0x7CC0 | 31934 | 31936 | Year 5 holiday 27 settings |  | R/W | 3
| 0x7CC1 | 0x7CC3 | 31937 | 31939 | Year 5 holiday 28 settings |  | R/W | 3
| 0x7CC4 | 0x7CC6 | 31940 | 31942 | Year 5 holiday 29 settings |  | R/W | 3
| 0x7CC7 | 0x7CC9 | 31943 | 31945 | Year 5 holiday 30 settings |  | R/W | 3
| 0x7CCA |  | 31946 |  | Year 5 Setting Year |  | R/W
| 0x7CCB |  | 31947 |  | Year 5 Holiday Number setting |  | R/W
| 0x7CCC | 0x7CCE | 31948 | 31950 | Year 6 holiday 1 settings |  | R/W | 3
| 0x7CCF | 0x7CD1 | 31951 | 31953 | Year 6 holiday 2 settings |  | R/W | 3
| 0x7CD2 | 0x7CD4 | 31954 | 31956 | Year 6 holiday 3 settings |  | R/W | 3
| 0x7CD5 | 0x7CD7 | 31957 | 31959 | Year 6 holiday 4 settings |  | R/W | 3
| 0x7CD8 | 0x7CDA | 31960 | 31962 | Year 6 holiday 5 settings |  | R/W | 3
| 0x7CDB | 0x7CDD | 31963 | 31965 | Year 6 holiday 6 settings |  | R/W | 3
| 0x7CDE | 0x7CE0 | 31966 | 31968 | Year 6 holiday 7 settings |  | R/W | 3
| 0x7CE1 | 0x7CE3 | 31969 | 31971 | Year 6 holiday 8 settings |  | R/W | 3
| 0x7CE4 | 0x7CE6 | 31972 | 31974 | Year 6 holiday 9 settings |  | R/W | 3
| 0x7CE7 | 0x7CE9 | 31975 | 31977 | Year 6 holiday 10 settings |  | R/W | 3
| 0x7CEA | 0x7CEC | 31978 | 31980 | Year 6 holiday 11 settings |  | R/W | 3
| 0x7CED | 0x7CEF | 31981 | 31983 | Year 6 holiday 12 settings |  | R/W | 3
| 0x7CF0 | 0x7CF2 | 31984 | 31986 | Year 6 holiday 13 settings |  | R/W | 3
| 0x7CF3 | 0x7CF5 | 31987 | 31989 | Year 6 holiday 14 settings |  | R/W | 3
| 0x7CF6 | 0x7CF8 | 31990 | 31992 | Year 6 holiday 15 settings |  | R/W | 3
| 0x7CF9 | 0x7CFB | 31993 | 31995 | Year 6 holiday 16 settings |  | R/W | 3
| 0x7CFC | 0x7CFE | 31996 | 31998 | Year 6 holiday 17 settings |  | R/W | 3
| 0x7CFF | 0x7D01 | 31999 | 32001 | Year 6 holiday 18 settings |  | R/W | 3
| 0x7D02 | 0x7D04 | 32002 | 32004 | Year 6 holiday 19 settings |  | R/W | 3
| 0x7D05 | 0x7D07 | 32005 | 32007 | Year 6 holiday 20 settings |  | R/W | 3
| 0x7D08 | 0x7D0A | 32008 | 32010 | Year 6 holiday 21 settings |  | R/W | 3
| 0x7D0B | 0x7D0D | 32011 | 32013 | Year 6 holiday 22 settings |  | R/W | 3
| 0x7D0E | 0x7D10 | 32014 | 32016 | Year 6 holiday 23 settings |  | R/W | 3
| 0x7D11 | 0x7D13 | 32017 | 32019 | Year 6 holiday 24 settings |  | R/W | 3
| 0x7D14 | 0x7D16 | 32020 | 32022 | Year 6 holiday 25 settings |  | R/W | 3
| 0x7D17 | 0x7D19 | 32023 | 32025 | Year 6 holiday 26 settings |  | R/W | 3
| 0x7D1A | 0x7D1C | 32026 | 32028 | Year 6 holiday 27 settings |  | R/W | 3
| 0x7D1D | 0x7D1F | 32029 | 32031 | Year 6 holiday 28 settings |  | R/W | 3
| 0x7D20 | 0x7D22 | 32032 | 32034 | Year 6 holiday 29 settings |  | R/W | 3
| 0x7D23 | 0x7D25 | 32035 | 32037 | Year 6 holiday 30 settings |  | R/W | 3
| 0x7D26 |  | 32038 |  | Year 6 Settings Year |  | R/W
| 0x7D27 |  | 32039 |  | Year 6 Number of holidays |  | R/W
| 0x7D28 | 0x7D2A | 32040 | 32042 | Year 7 holiday 1 settings |  | R/W | 3
| 0x7D2B | 0x7D2D | 32043 | 32045 | Year 7 holiday 2 settings |  | R/W | 3
| 0x7D2E | 0x7D30 | 32046 | 32048 | Year 7 holiday 3 settings |  | R/W | 3
| 0x7D31 | 0x7D33 | 32049 | 32051 | Year 7 holiday 4 settings |  | R/W | 3
| 0x7D34 | 0x7D36 | 32052 | 32054 | Year 7 holiday 5 settings |  | R/W | 3
| 0x7D37 | 0x7D39 | 32055 | 32057 | Year 7 holiday 6 settings |  | R/W | 3
| 0x7D3A | 0x7D3C | 32058 | 32060 | Year 7 holiday 7 settings |  | R/W | 3
| 0x7D3D | 0x7D3F | 32061 | 32063 | Year 7 holiday 8 settings |  | R/W | 3
| 0x7D40 | 0x7D42 | 32064 | 32066 | Year 7 holiday 9 settings |  | R/W | 3
| 0x7D43 | 0x7D45 | 32067 | 32069 | Year 7 holiday 10 settings |  | R/W | 3
| 0x7D46 | 0x7D48 | 32070 | 32072 | Year 7 holiday 11 settings |  | R/W | 3
| 0x7D49 | 0x7D4B | 32073 | 32075 | Year 7 holiday 12 settings |  | R/W | 3
| 0x7D4C | 0x7D4E | 32076 | 32078 | Year 7 holiday 13 settings |  | R/W | 3
| 0x7D4F | 0x7D51 | 32079 | 32081 | Year 7 holiday 14 settings |  | R/W | 3
| 0x7D52 | 0x7D54 | 32082 | 32084 | Year 7 holiday 15 settings |  | R/W | 3
| 0x7D55 | 0x7D57 | 32085 | 32087 | Year 7 holiday 16 settings |  | R/W | 3
| 0x7D58 | 0x7D5A | 32088 | 32090 | Year 7 holiday 17 settings |  | R/W | 3
| 0x7D5B | 0x7D5D | 32091 | 32093 | Year 7 holiday 18 settings |  | R/W | 3
| 0x7D5E | 0x7D60 | 32094 | 32096 | Year 7 holiday 19 settings |  | R/W | 3
| 0x7D61 | 0x7D63 | 32097 | 32099 | Year 7 holiday 20 settings |  | R/W | 3
| 0x7D64 | 0x7D66 | 32100 | 32102 | Year 7 holiday 21 settings |  | R/W | 3
| 0x7D67 | 0x7D69 | 32103 | 32105 | Year 7 holiday 22 settings |  | R/W | 3
| 0x7D6A | 0x7D6C | 32106 | 32108 | Year 7 holiday 23 settings |  | R/W | 3
| 0x7D6D | 0x7D6F | 32109 | 32111 | Year 7 holiday 24 settings |  | R/W | 3
| 0x7D70 | 0x7D72 | 32112 | 32114 | Year 7 holiday 25 settings |  | R/W | 3
| 0x7D73 | 0x7D75 | 32115 | 32117 | Year 7 holiday 26 settings |  | R/W | 3
| 0x7D76 | 0x7D78 | 32118 | 32120 | Year 7 holiday 27 settings |  | R/W | 3
| 0x7D79 | 0x7D7B | 32121 | 32123 | Year 7 holiday 28 settings |  | R/W | 3
| 0x7D7C | 0x7D7E | 32124 | 32126 | Year 7 holiday 29 settings |  | R/W | 3
| 0x7D7F | 0x7D81 | 32127 | 32129 | Year 7 holiday 30 settings |  | R/W | 3
| 0x7D82 |  | 32130 |  | Year 7 Setting Year |  | R/W
| 0x7D83 |  | 32131 |  | Year 7 Holiday Number setting |  | R/W
| 0x7D84 | 0x7D86 | 32132 | 32134 | Year 8 holiday 1 settings |  | R/W | 3
| 0x7D87 | 0x7D89 | 32135 | 32137 | Year 8 holiday 2 settings |  | R/W | 3
| 0x7D8A | 0x7D8C | 32138 | 32140 | Year 8 holiday 3 settings |  | R/W | 3
| 0x7D8D | 0x7D8F | 32141 | 32143 | Year 8 holiday 4 settings |  | R/W | 3
| 0x7D90 | 0x7D92 | 32144 | 32146 | Year 8 holiday 5 settings |  | R/W | 3
| 0x7D93 | 0x7D95 | 32147 | 32149 | Year 8 holiday 6 settings |  | R/W | 3
| 0x7D96 | 0x7D98 | 32150 | 32152 | Year 8 holiday 7 settings |  | R/W | 3
| 0x7D99 | 0x7D9B | 32153 | 32155 | Year 8 holiday 8 settings |  | R/W | 3
| 0x7D9C | 0x7D9E | 32156 | 32158 | Year 8 holiday 9 settings |  | R/W | 3
| 0x7D9F | 0x7DA1 | 32159 | 32161 | Year 8 holiday 10 settings |  | R/W | 3
| 0x7DA2 | 0x7DA4 | 32162 | 32164 | Year 8 holiday 11 settings |  | R/W | 3
| 0x7DA5 | 0x7DA7 | 32165 | 32167 | Year 8 holiday 12 settings |  | R/W | 3
| 0x7DA8 | 0x7DAA | 32168 | 32170 | Year 8 holiday 13 settings |  | R/W | 3
| 0x7DAB | 0x7DAD | 32171 | 32173 | Year 8 holiday 14 settings |  | R/W | 3
| 0x7DAE | 0x7DB0 | 32174 | 32176 | Year 8 holiday 15 settings |  | R/W | 3
| 0x7DB1 | 0x7DB3 | 32177 | 32179 | Year 8 holiday 16 settings |  | R/W | 3
| 0x7DB4 | 0x7DB6 | 32180 | 32182 | Year 8 holiday 17 settings |  | R/W | 3
| 0x7DB7 | 0x7DB9 | 32183 | 32185 | Year 8 holiday 18 settings |  | R/W | 3
| 0x7DBA | 0x7DBC | 32186 | 32188 | Year 8 holiday 19 settings |  | R/W | 3
| 0x7DBD | 0x7DBF | 32189 | 32191 | Year 8 holiday 20 settings |  | R/W | 3
| 0x7DC0 | 0x7DC2 | 32192 | 32194 | Year 8 holiday 21 settings |  | R/W | 3
| 0x7DC3 | 0x7DC5 | 32195 | 32197 | Year 8 holiday 22 settings |  | R/W | 3
| 0x7DC6 | 0x7DC8 | 32198 | 32200 | Year 8 holiday 23 settings |  | R/W | 3
| 0x7DC9 | 0x7DCB | 32201 | 32203 | Year 8 holiday 24 settings |  | R/W | 3
| 0x7DCC | 0x7DCE | 32204 | 32206 | Year 8 holiday 25 settings |  | R/W | 3
| 0x7DCF | 0x7DD1 | 32207 | 32209 | Year 8 holiday 26 settings |  | R/W | 3
| 0x7DD2 | 0x7DD4 | 32210 | 32212 | Year 8 holiday 27 settings |  | R/W | 3
| 0x7DD5 | 0x7DD7 | 32213 | 32215 | Year 8 holiday 28 settings |  | R/W | 3
| 0x7DD8 | 0x7DDA | 32216 | 32218 | Year 8 holiday 29 settings |  | R/W | 3
| 0x7DDB | 0x7DDD | 32219 | 32221 | Year 8 holiday 30 settings |  | R/W | 3
| 0x7DDE |  | 32222 |  | Year 8 Setting Year |  | R/W
| 0x7DDF |  | 32223 |  | Year 8 Holiday Number setting |  | R/W
| 0x7DE0 | 0x7DE2 | 32224 | 32226 | Year 9 holiday 1 settings |  | R/W | 3
| 0x7DE3 | 0x7DE5 | 32227 | 32229 | Year 9 holiday 2 settings |  | R/W | 3
| 0x7DE6 | 0x7DE8 | 32230 | 32232 | Year 9 holiday 3 settings |  | R/W | 3
| 0x7DE9 | 0x7DEB | 32233 | 32235 | Year 9 holiday 4 settings |  | R/W | 3
| 0x7DEC | 0x7DEE | 32236 | 32238 | Year 9 holiday 5 settings |  | R/W | 3
| 0x7DEF | 0x7DF1 | 32239 | 32241 | Year 9 holiday 6 settings |  | R/W | 3
| 0x7DF2 | 0x7DF4 | 32242 | 32244 | Year 9 holiday 7 settings |  | R/W | 3
| 0x7DF5 | 0x7DF7 | 32245 | 32247 | Year 9 holiday 8 settings |  | R/W | 3
| 0x7DF8 | 0x7DFA | 32248 | 32250 | Year 9 holiday 9 settings |  | R/W | 3
| 0x7DFB | 0x7DFD | 32251 | 32253 | Year 9 holiday 10 settings |  | R/W | 3
| 0x7DFE | 0x7E00 | 32254 | 32256 | Year 9 holiday 11 settings |  | R/W | 3
| 0x7E01 | 0x7E03 | 32257 | 32259 | Year 9 holiday 12 settings |  | R/W | 3
| 0x7E04 | 0x7E06 | 32260 | 32262 | Year 9 holiday 13 settings |  | R/W | 3
| 0x7E07 | 0x7E09 | 32263 | 32265 | Year 9 holiday 14 settings |  | R/W | 3
| 0x7E0A | 0x7E0C | 32266 | 32268 | Year 9 holiday 15 settings |  | R/W | 3
| 0x7E0D | 0x7E0F | 32269 | 32271 | Year 9 holiday 16 settings |  | R/W | 3
| 0x7E10 | 0x7E12 | 32272 | 32274 | Year 9 holiday 17 settings |  | R/W | 3
| 0x7E13 | 0x7E15 | 32275 | 32277 | Year 9 holiday 18 settings |  | R/W | 3
| 0x7E16 | 0x7E18 | 32278 | 32280 | Year 9 holiday 19 settings |  | R/W | 3
| 0x7E19 | 0x7E1B | 32281 | 32283 | Year 9 holiday 20 settings |  | R/W | 3
| 0x7E1C | 0x7E1E | 32284 | 32286 | Year 9 holiday 21 settings |  | R/W | 3
| 0x7E1F | 0x7E21 | 32287 | 32289 | Year 9 holiday 22 settings |  | R/W | 3
| 0x7E22 | 0x7E24 | 32290 | 32292 | Year 9 holiday 23 settings |  | R/W | 3
| 0x7E25 | 0x7E27 | 32293 | 32295 | Year 9 holiday 24 settings |  | R/W | 3
| 0x7E28 | 0x7E2A | 32296 | 32298 | Year 9 holiday 25 settings |  | R/W | 3
| 0x7E2B | 0x7E2D | 32299 | 32301 | Year 9 holiday 26 settings |  | R/W | 3
| 0x7E2E | 0x7E30 | 32302 | 32304 | Year 9 holiday 27 settings |  | R/W | 3
| 0x7E31 | 0x7E33 | 32305 | 32307 | Year 9 holiday 28 settings |  | R/W | 3
| 0x7E34 | 0x7E36 | 32308 | 32310 | Year 9 holiday 29 settings |  | R/W | 3
| 0x7E37 | 0x7E39 | 32311 | 32313 | Year 9 holiday 30 settings |  | R/W | 3
| 0x7E3A |  | 32314 |  | Year 9 Setting Year |  | R/W
| 0x7E3B |  | 32315 |  | Year 9 Holiday Number setting |  | R/W
| 0x7E3C | 0x7E3E | 32316 | 32318 | Year 10 holiday 1 settings |  | R/W | 3
| 0x7E3F | 0x7E41 | 32319 | 32321 | Year 10 holiday 2 settings |  | R/W | 3
| 0x7E42 | 0x7E44 | 32322 | 32324 | Year 10 holiday 3 settings |  | R/W | 3
| 0x7E45 | 0x7E47 | 32325 | 32327 | Year 10 holiday 4 settings |  | R/W | 3
| 0x7E48 | 0x7E4A | 32328 | 32330 | Year 10 holiday 5 settings |  | R/W | 3
| 0x7E4B | 0x7E4D | 32331 | 32333 | Year 10 holiday 6 settings |  | R/W | 3
| 0x7E4E | 0x7E50 | 32334 | 32336 | Year 10 holiday 7 settings |  | R/W | 3
| 0x7E51 | 0x7E53 | 32337 | 32339 | Year 10 holiday 8 settings |  | R/W | 3
| 0x7E54 | 0x7E56 | 32340 | 32342 | Year 10 holiday 9 settings |  | R/W | 3
| 0x7E57 | 0x7E59 | 32343 | 32345 | Year 10 holiday 10 settings |  | R/W | 3
| 0x7E5A | 0x7E5C | 32346 | 32348 | Year 10 holiday 11 settings |  | R/W | 3
| 0x7E5D | 0x7E5F | 32349 | 32351 | Year 10 holiday 12 settings |  | R/W | 3
| 0x7E60 | 0x7E62 | 32352 | 32354 | Year 10 holiday 13 settings |  | R/W | 3
| 0x7E63 | 0x7E65 | 32355 | 32357 | Year 10 holiday 14 settings |  | R/W | 3
| 0x7E66 | 0x7E68 | 32358 | 32360 | Year 10 holiday 15 settings |  | R/W | 3
| 0x7E69 | 0x7E6B | 32361 | 32363 | Year 10 holiday 16 settings |  | R/W | 3
| 0x7E6C | 0x7E6E | 32364 | 32366 | Year 10 holiday 17 settings |  | R/W | 3
| 0x7E6F | 0x7E71 | 32367 | 32369 | Year 10 holiday 18 settings |  | R/W | 3
| 0x7E72 | 0x7E74 | 32370 | 32372 | Year 10 holiday 19 settings |  | R/W | 3
| 0x7E75 | 0x7E77 | 32373 | 32375 | Year 10 holiday 20 settings |  | R/W | 3
| 0x7E78 | 0x7E7A | 32376 | 32378 | Year 10 holiday 21 settings |  | R/W | 3
| 0x7E7B | 0x7E7D | 32379 | 32381 | Year 10 holiday 22 settings |  | R/W | 3
| 0x7E7E | 0x7E80 | 32382 | 32384 | Year 10 holiday 23 settings |  | R/W | 3
| 0x7E81 | 0x7E83 | 32385 | 32387 | Year 10 holiday 24 settings |  | R/W | 3
| 0x7E84 | 0x7E86 | 32388 | 32390 | Year 10 holiday 25 settings |  | R/W | 3
| 0x7E87 | 0x7E89 | 32391 | 32393 | Year 10 holiday 26 settings |  | R/W | 3
| 0x7E8A | 0x7E8C | 32394 | 32396 | Year 10 holiday 27 settings |  | R/W | 3
| 0x7E8D | 0x7E8F | 32397 | 32399 | Year 10 holiday 28 settings |  | R/W | 3
| 0x7E90 | 0x7E92 | 32400 | 32402 | Year 10 holiday 29 settings |  | R/W | 3
| 0x7E93 | 0x7E95 | 32403 | 32405 | Year 10 holiday 30 settings |  | R/W | 3
| 0x7E96 |  | 32406 |  | Year 10 Setting Year |  | R/W
| 0x7E97 |  | 32407 |  | Year 10 Holiday Number setting |  | R/W
| 0x7E98 |  | 32408 |  | Clear -- Year 10 Holiday Number setting |  | W | 1 |  | 0xAA
Special weekday schedule settings
| 0x7F00 |  | 32512 |  | Enable special weekday schedule |  | R/W |  | 0: Disable 1: Enable If 0, Weekend schedule uses registers 0x7804H & 0x7805H
| 0x7F01 |  | 32513 |  | Season 1 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F02 |  | 32514 |  | Season 1 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F03 |  | 32515 |  | Season 1 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F04 |  | 32516 |  | Season 1 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F05 |  | 32517 |  | Season 1 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F06 |  | 32518 |  | Season 1 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F07 |  | 32519 |  | Season 1 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F08 |  | 32520 |  | Season 1 Saturday Schedule ID |  | R/W |  | 0~14
| 0x7F09 |  | 32521 |  | Season 2 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F0A |  | 32522 |  | Season 2 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F0B |  | 32523 |  | Season 2 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F0C |  | 32524 |  | Season 2 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F0D |  | 32525 |  | Season 2 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F0E |  | 32526 |  | Season 2 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F0F |  | 32527 |  | Season 2 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F10 |  | 32528 |  | Season 2 Saturday Schedule ID |  | R/W |  | 0~14
| 0x7F11 |  | 32529 |  | Season 3 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F12 |  | 32530 |  | Season 3 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F13 |  | 32531 |  | Season 3 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F14 |  | 32532 |  | Season 3 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F15 |  | 32533 |  | Season 3 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F16 |  | 32534 |  | Season 3 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F17 |  | 32535 |  | Season 3 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F18 |  | 32536 |  | Season 3 Saturday Schedule ID |  | R/W |  | 0~14
| 0x7F19 |  | 32537 |  | Season 4 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F1A |  | 32538 |  | Season 4 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F1B |  | 32539 |  | Season 4 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F1C |  | 32540 |  | Season 4 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F1D |  | 32541 |  | Season 4 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F1E |  | 32542 |  | Season 4 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F1F |  | 32543 |  | Season 4 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F20 |  | 32544 |  | Season 4 Saturday Schedule ID |  | R/W |  | 0~14
| 0x7F21 |  | 32545 |  | Season 5 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F22 |  | 32546 |  | Season 5 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F23 |  | 32547 |  | Season 5 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F24 |  | 32548 |  | Season 5 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F25 |  | 32549 |  | Season 5 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F26 |  | 32550 |  | Season 5 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F27 |  | 32551 |  | Season 5 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F28 |  | 32552 |  | Season 5 Saturday Schedule ID |  | R/W |  | 0~14
| 0x7F29 |  | 32553 |  | Season 6 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F2A |  | 32554 |  | Season 6 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F2B |  | 32555 |  | Season 6 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F2C |  | 32556 |  | Season 6 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F2D |  | 32557 |  | Season 6 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F2E |  | 32558 |  | Season 6 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F2F |  | 32559 |  | Season 6 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F30 |  | 32560 |  | Season 6 Saturday Schedule ID |  | R/W |  | 0~14
| 0x7F31 |  | 32561 |  | Season 7 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F32 |  | 32562 |  | Season 7 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F33 |  | 32563 |  | Season 7 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F34 |  | 32564 |  | Season 7 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F35 |  | 32565 |  | Season 7 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F36 |  | 32566 |  | Season 7 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F37 |  | 32567 |  | Season 7 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F38 |  | 32568 |  | Season 7 Saturday Schedule ID |  | R/W |  | 0~14
| 0x7F39 |  | 32569 |  | Season 8 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F3A |  | 32570 |  | Season 8 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F3B |  | 32571 |  | Season 8 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F3C |  | 32572 |  | Season 8 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F3D |  | 32573 |  | Season 8 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F3E |  | 32574 |  | Season 8 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F3F |  | 32575 |  | Season 8 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F40 |  | 32576 |  | Season 8 Saturday Schedule ID |  | R/W |  | 0~14
| 0x7F41 |  | 32577 |  | Season 9 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F42 |  | 32578 |  | Season 9 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F43 |  | 32579 |  | Season 9 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F44 |  | 32580 |  | Season 9 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F45 |  | 32581 |  | Season 9 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F46 |  | 32582 |  | Season 9 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F47 |  | 32583 |  | Season 9 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F48 |  | 32584 |  | Season 9 Saturday Schedule ID |  | R/W |  | 0~14
| 0x7F49 |  | 32585 |  | Season 10 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F4A |  | 32586 |  | Season 10 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F4B |  | 32587 |  | Season 10 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F4C |  | 32588 |  | Season 10 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F4D |  | 32589 |  | Season 10 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F4E |  | 32590 |  | Season 10 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F4F |  | 32591 |  | Season 10 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F50 |  | 32592 |  | Season 10 Saturday Schedule ID |  | R/W |  | 0~14
| 0x7F51 |  | 32593 |  | Season 11 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F52 |  | 32594 |  | Season 11 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F53 |  | 32595 |  | Season 11 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F54 |  | 32596 |  | Season 11 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F55 |  | 32597 |  | Season 11 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F56 |  | 32598 |  | Season 11 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F57 |  | 32599 |  | Season 11 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F58 |  | 32600 |  | Season 11 Saturday Schedule ID |  | R/W |  | 0~14
| 0x7F59 |  | 32601 |  | Season 12 weekday schedule enable |  | R/W |  | bit0: Sunday bit1-bit6: Monday-Saturday bit=1 means Enabled
| 0x7F5A |  | 32602 |  | Season 12 Sunday schedule ID |  | R/W |  | 0~14
| 0x7F5B |  | 32603 |  | Season 12 Monday Schedule ID |  | R/W |  | 0~14
| 0x7F5C |  | 32604 |  | Season 12 Tuesday Schedule ID |  | R/W |  | 0~14
| 0x7F5D |  | 32605 |  | Season 12 Wednesday Schedule ID |  | R/W |  | 0~14
| 0x7F5E |  | 32606 |  | Season 12 Thursday Schedule ID |  | R/W |  | 0~14
| 0x7F5F |  | 32607 |  | Season 12 Friday Schedule ID |  | R/W |  | 0~14
| 0x7F60 |  | 32608 |  | Season 12 Saturday Schedule ID |  | R/W |  | 0~14

## SunSpec
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
SunSpec System Information Address Table
| 0xC350 | 0xC351 | 50000 | 50001 | SunSpec_ID | Uint16 | R | 2 | 0x53756e53 |  | Y
| 0xC352 | 0xC352 | 50002 | 50002 | ID | Uint16 | R | 1 | 1 |  | Y
| 0xC353 | 0xC353 | 50003 | 50003 | Lenth | Uint16 | R | 1 | 65 |  | Y
| 0xC354 | 0xC363 | 50004 | 50019 | Manufacturer | string | R | 16 | Well known value registered with SunSpec for compliance | ACCUENERGY 41 43 43 55 45 4E 45 52 47 59 | Y
| 0xC364 | 0xC373 | 50020 | 50035 | Model | string | R | 16 | Manufacturer specific value (32 chars) | Acuvim II 41 63 75 76 69 6D 20 49 49 | Y
| 0xC374 | 0xC37B | 50036 | 50043 | Options | string | R | 8 | Manufacturer specific value (16 chars) | Acuvim IIX 41 63 75 76 69 6D 20 49 49 00（II）/52（IIR）/45(IIE)/57(IIW)/42 4E(IIBN) MK II(4D 4B 20 49 49) | Y | 0xF050 product model ID
| 0xC37C | 0xC383 | 50044 | 50051 | Version | string | R | 8 | Manufacturer specific value (16 chars) | H: 2.32 S: 3.91 48 3A 32 2E 33 32 20 53 3A 33 2E 39 31 20 20 20 | Y
| 0xC384 | 0xC393 | 50052 | 50067 | Serial Number | string | R | 16 | Manufacturer specific value (32 chars) |  | Y
| 0xC394 | 0xC394 | 50068 | 50068 | Device Address | uint16 | R | 1 | Modbus device address |  | Y
SunSpec Measured Data Address Table (Continued)
| 0xC395 | 0xC395 | 50069 | 50069 | ID | Uint16 | R | 1 | Meter (Single Phase)single phase (AN or AB) meter --201 split single phase (ABN) meter –202 wye-connect three phase (abcn) meter-203 delta-connect three phase (abc) meter --204 |  | Y
| 0xC396 | 0xC396 | 50070 | 50070 | Lenth | Uint16 | R | 1 | 105 |  | Y
| 0xC397 | 0xC397 | 50071 | 50071 | Amps(average): Sunspec; Amps(average): AcuvimII | int16 | R | 1 | 0~9999 A |  | Y
| 0xC398 | 0xC398 | 50072 | 50072 | Amps Phase A: Sunspec; Phase A Current: AcuvimII | int16 | R | 1 | 0~9999 A | Change to 0~32767 | Y
| 0xC399 | 0xC399 | 50073 | 50073 | Amps Phase B: Sunspec; Phase B Current: AcuvimII | int16 | R | 1 | 0~9999 A |  | Y
| 0xC39A | 0xC39A | 50074 | 50074 | Amps Phase C: Sunspec; Phase C Current: AcuvimII | int16 | R | 1 | 0~9999 A |  | Y
| 0xC39B | 0xC39B | 50075 | 50075 | Current scale factor: Sunspec; CT Ratio: Acuvim II | sunssf | R | 1 | - 3 ~ + 2(used as exponent of a power of 10) |  | Y
| 0xC39C | 0xC39C | 50076 | 50076 | Voltage LN (average): Sunspec; Phase Average Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC39D | 0xC39D | 50077 | 50077 | Phase Voltage AN: Sunspec; Phase A Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC39E | 0xC39E | 50078 | 50078 | Phase Voltage BN: Sunspec; Phase B Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC39F | 0xC39F | 50079 | 50079 | Phase Voltage CN: Sunspec; Phase C Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC3A0 | 0xC3A0 | 50080 | 50080 | Voltage LL (average): Sunspec; Line Average Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC3A1 | 0xC3A1 | 50081 | 50081 | Phase Voltage AB: Sunspec; Line AB Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC3A2 | 0xC3A2 | 50082 | 50082 | Phase Voltage BC: Sunspec; Line BC Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC3A3 | 0xC3A3 | 50083 | 50083 | Phase Voltage CA: Sunspec; Line CA Voltage: Acuvim II | int16 | R | 1 | 0~9999 V |  | Y
| 0xC3A4 | 0xC3A4 | 50084 | 50084 | Voltage scale factor: Sunspec | sunssf | R | 1 | - 2 ~ 4(used as exponent of a power of 10) |  | Y
| 0xC3A5 | 0xC3A5 | 50085 | 50085 | Frequency | int16 | R | 1 | 45Hz-65Hz |  | Y
| 0xC3A6 | 0xC3A6 | 50086 | 50086 | Frequency scale factor | sunssf | R | 1 | -2(used as exponent of a power of 10) |  | Y
| 0xC3A7 | 0xC3A7 | 50087 | 50087 | Total Real Power: Sunspec; Total Active Power: Acuvim II | int16 | R | 1 | 0~9999 W | 'Change to -32768~32767 | Y
| 0xC3A8 | 0xC3A8 | 50088 | 50088 | Watts phase A: Sunspec; Phase A Active Power: Acuvim II | int16 | R | 1 | 0~9999 W | P | Y
| 0xC3A9 | 0xC3A9 | 50089 | 50089 | Watts phase B: Sunspec; Phase B Active Power: Acuvim II | int16 | R | 1 | 0~9999 W |  | Y
| 0xC3AA | 0xC3AA | 50090 | 50090 | Watts phase C: Sunspec; Phase C Active Power: Acuvim II | int16 | R | 1 | 0~9999 W |  | Y
| 0xC3AB | 0xC3AB | 50091 | 50091 | Real Power scale factor: Sunspec | sunssf | R | 1 | -1~ 4(used as exponent of a power of 10) |  | Y
| 0xC3AC | 0xC3AC | 50092 | 50092 | Total Apparent Power VA: Sunspec; Total Apparent Power: Acuvim II | int16 | R | 1 | 0~9999 VA | S | Y
| 0xC3AD | 0xC3AD | 50093 | 50093 | VA phase A: Sunspec; Phase A Apparent Power: Acuvim II | int16 | R | 1 | 0~9999 VA |  | Y
| 0xC3AE | 0xC3AE | 50094 | 50094 | VA phase B: Sunspec; Phase B Apparent Power: Acuvim II | int16 | R | 1 | 0~9999 VA |  | Y
| 0xC3AF | 0xC3AF | 50095 | 50095 | VA phaseCA: Sunspec; Phase C Apparent Power: Acuvim II | int16 | R | 1 | 0~9999 VA |  | Y
| 0xC3B0 | 0xC3B0 | 50096 | 50096 | Apparent Power scale factor: Sunspec; | sunssf | R | 1 | - 1 ~ 4(used as exponent of a power of 10) | -1~8 | Y
| 0xC3B1 | 0xC3B1 | 50097 | 50097 | Reactive Power VAR: Sunspec; Total Reactive Power: Acuvim II | int16 | R | 1 | 0~9999 var |  | Y
| 0xC3B2 | 0xC3B2 | 50098 | 50098 | VAR phase A: Sunspec; Phase A Reactive Power: Acuvim II | int16 | R | 1 | 0~9999 var | -32768~32767 | Y
| 0xC3B3 | 0xC3B3 | 50099 | 50099 | VAR phase B: Sunspec; Phase B Reactive Power: Acuvim II | int16 | R | 1 | 0~9999 var | Q | Y
| 0xC3B4 | 0xC3B4 | 50100 | 50100 | VAR phase C: Sunspec; Phase C Reactive Power: Acuvim II | int16 | R | 1 | 0~9999 var |  | Y
| 0xC3B5 | 0xC3B5 | 50101 | 50101 | Reactive Power scale factor: Sunspec | sunssf | R | 1 | -1 ~ 4(used as exponent of a power of 10) | -1~8 | Y
| 0xC3B6 | 0xC3B6 | 50102 | 50102 | Power Factor | int16 | R | 1 | -1000 ~ 1000 |  | Y
| 0xC3B7 | 0xC3B7 | 50103 | 50103 | PF phase A | int16 | R | 1 | -1000 ~ 1000 |  | Y
| 0xC3B8 | 0xC3B8 | 50104 | 50104 | PF phase B | int16 | R | 1 | -1000 ~ 1000 |  | Y
| 0xC3B9 | 0xC3B9 | 50105 | 50105 | PF phase C | int16 | R | 1 | -1000 ~ 1000 |  | Y
| 0xC3BA | 0xC3BA | 50106 | 50106 | Power Factor scale factor: Sunspec | sunssf | R | 1 | -3(used as exponent of a power of 10) |  | Y
| 0xC3BB | 0xC3BC | 50107 | 50108 | Total Real Energy Exported: Sunspec Total Active Energy Exported: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh（unit: W） | EP Export/Output | Y
| 0xC3BD | 0xC3BE | 50109 | 50110 | Total Watt-hours Exported in phase A: Sunspec; Total Active Energy Exported in Phase A: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3BF | 0xC3C0 | 50111 | 50112 | Total Watt-hours Exported in phase B: Sunspec; Total Active Energy Exported in PhaseB: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3C1 | 0xC3C2 | 50113 | 50114 | Total Watt-hours Exported in phase C: Sunspec; Total Active Energy Exported in Phase C: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3C3 | 0xC3C4 | 50115 | 50116 | Total Real Energy Imported: Sunspec; Total Active Energy Imported: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh | EP Import/Input | Y
| 0xC3C5 | 0xC3C6 | 50117 | 50118 | Total Watt-hours Imported phase A: Sunspec; Total Active Energy Imported in Phase A: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3C7 | 0xC3C8 | 50119 | 50120 | Total Watt-hours Imported phase B: Sunspec; Total Active Energy Imported in Phase B: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3C9 | 0xC3CA | 50121 | 50122 | Total Watt-hours Imported phase C: Sunspec; Total Active Energy Imported in Phase C: Acuvim II | acc32 | R/W | 2 | 0-999999999 Wh |  | Y
| 0xC3CB | 0xC3CB | 50123 | 50123 | TotWh_SF: Sunspec | sunssf | R | 1 | Update to : Secondary Change to 0,Primary as 3(used as exponent of a power of 10) |  | Y
| 0xC3CC | 0xC3CD | 50124 | 50125 | Total VA-hours Exported: Sunspec; | acc32 | R/W | 2 | P < 0 | ES Export/Output
| 0xC3CE | 0xC3CF | 50126 | 50127 | Total VA-hours Exported in phase A: Sunspec; | acc32 | R/W | 2
| 0xC3D0 | 0xC3D1 | 50128 | 50129 | Total VA-hours Exported in phase B: Sunspec; | acc32 | R/W | 2
| 0xC3D2 | 0xC3D3 | 50130 | 50131 | Total VA-hours Exported in phase C: Sunspec; | acc32 | R/W | 2
| 0xC3D4 | 0xC3D5 | 50132 | 50133 | Total VA-hours Imported: Sunspec; | acc32 | R/W | 2 |  | ES Import/Input
| 0xC3D6 | 0xC3D7 | 50134 | 50135 | Total VA-hours Imported in phase A: Sunspec; | acc32 | R/W | 2
| 0xC3D8 | 0xC3D9 | 50136 | 50137 | Total VA-hours Imported in phase B: Sunspec; | acc32 | R/W | 2
| 0xC3DA | 0xC3DB | 50138 | 50139 | Total VA-hours Imported in phase C: Sunspec; | acc32 | R/W | 2
| 0xC3DC | 0xC3DC | 50140 | 50140 | TotVAh_SF: Sunspec | sunssf | R | 1 | Update to : Secondary Change to 0,Primary as 3(used as exponent of a power of 10) |  | Y
| 0xC3DD | 0xC3DE | 50141 | 50142 | Total VAr-hours Imported Q1: Sunspec | acc32 | R/W | 2 |  | EQ
| 0xC3DF | 0xC3E0 | 50143 | 50144 | Total VAr-hours Imported Q1 phase A: Sunspec | acc32 | R/W | 2
| 0xC3E1 | 0xC3E2 | 50145 | 50146 | Total VAr-hours Imported Q1 phase B: Sunspec | acc32 | R/W | 2
| 0xC3E3 | 0xC3E4 | 50147 | 50148 | Total VAr-hours Imported Q1 phase C: Sunspec | acc32 | R/W | 2
| 0xC3E5 | 0xC3E6 | 50149 | 50150 | Total VAr-hours Imported Q2: Sunspec | acc32 | R/W | 2
| 0xC3E7 | 0xC3E8 | 50151 | 50152 | Total VAr-hours Imported Q2 phase A: Sunspec | acc32 | R/W | 2
| 0xC3E9 | 0xC3EA | 50153 | 50154 | Total VAr-hours Imported Q2 phase B: Sunspec | acc32 | R/W | 2
| 0xC3EB | 0xC3EC | 50155 | 50156 | Total VAr-hours Imported Q2 phase C: Sunspec | acc32 | R/W | 2
| 0xC3ED | 0xC3EE | 50157 | 50158 | Total VAr-hours Exported Q3: Sunspec | acc32 | R/W | 2
| 0xC3EF | 0xC3F0 | 50159 | 50160 | Total VAr-hours Exported Q3 phase A: Sunspec | acc32 | R/W | 2
| 0xC3F1 | 0xC3F2 | 50161 | 50162 | Total VAr-hours Exported Q3 phase B: Sunspec | acc32 | R/W | 2
| 0xC3F3 | 0xC3F4 | 50163 | 50164 | Total VAr-hours Exported Q3 phase C: Sunspec | acc32 | R/W | 2
| 0xC3F5 | 0xC3F6 | 50165 | 50166 | Total VAr-hours Exported Q4: Sunspec | acc32 | R/W | 2
| 0xC3F7 | 0xC3F8 | 50167 | 50168 | Total VAr-hours Exported Q4 phase A: Sunspec | acc32 | R/W | 2
| 0xC3F9 | 0xC3FA | 50169 | 50170 | Total VAr-hours Exported Q4 phase B: Sunspec | acc32 | R/W | 2
| 0xC3FB | 0xC3FC | 50171 | 50172 | Total VAr-hours Exported Q4 phase C: Sunspec | acc32 | R/W | 2
| 0xC3FD | 0xC3FD | 50173 | 50173 | TotVArh_SF: Sunspec; | sunssf | R | 1 | Update to : Secondary Change to 0,Primary as 3(used as exponent of a power of 10)
| 0xC3FE | 0xC3FF | 50174 | 50175 | Meter Event Flags | bitfield32 | R | 2 | 0
| 0xC400 | 0xC400 | 50176 | 50176 | SunSpec_end_ID: Sunspec | Uint16 |  | 1 | 0xFFFF
| 0xC401 | 0xC401 | 50177 | 50177 | SunSpec_end_lenth: Sunspec | Uint16 |  | 1 | 0x0000

## Meter Model
Modbus address 0xF000-0xF0001
Acuvim II V3 | Panel Mount |  |  | DIN Rail
| 5A/1A | 333mV/RCT | mA | 5A/1A | 333mV/RCT | mA
Acuvim IIR | CP02 | CP22 | CP42 | CU02 | CU22 | CU42
Acuvim IIW | CP04 | CP24 | CP44 | CU04 | CU24 | CU44
Acuvim IIX | CS06 | CS26 | CS46
Acuvim IIR-400 | CF02 | CF22 | CF42 | CX02 | CX22 | CX42
Acuvim IIW-400 | CF04 | CF24 | CF44 | CX04 | CX24 | CX44
Acuvim II V3 Line Power | Panel Mount |  |  | DIN Rail
| 5A/1A | 333mV/RCT | mA | 5A/1A | 333mV/RCT | mA
BCON | CL02 | CL22 | CL42 | CV02 | CV22 | CV42 | Acuvim IIR
BCONWAV | CL04 | CL24 | CL44 | CV04 | CV24 | CV44 | Acuvim IIW
Acuvim II V3 Motor Power | Panel Mount |  |  | DIN Rail
| 5A/1A | 333mV/RCT | mA | 5A/1A | 333mV/RCT | mA
BCONMOT | CM02 | CM22 | CM42 | CW02 | CW22 | CW42 | Acuvim IIR
BCONWEBMOT | CM04 | CM24 | CM44 | CW04 | CW24 | CW44 | Acuvim IIW
Eaton customized models | Panel Mount |  |  | DIN Rail
| 5A/mV/mA |  |  | 5A/mV/mA
PXM1000 Ring terminal | CPD1 |  |  | CUD1
PXM1100 Ring terminal | CPD2 |  |  | CUD2
PXM1200 Ring terminal | CPD3 |  |  | CUD3
PXM1300 Ring terminal | CPD4 |  |  | CUD4
PXM1000 4CT | CPG1 |  |  | CUG1
PXM1100 4CT | CPG2 |  |  | CUG2
PXM1200 4CT | CPG3 |  |  | CUG3
PXM1300 4CT | CPG4 |  |  | CUG4
PXM3000 Ring terminal | CRD6 |  |  | CXD6
DEIF customized models | CPBx |  |  | CUBx
MIC-2 MKII | CPB2 | [5 empty] | Acuvim IIR-D-5A-P1V3
MIC-2 MKII DIN |  |  |  | CUB2 |  |  | Acuvim IIR-M-5A-P1V3
MIC-2 MKII FCT | CPB2 | [5 empty] | Acuvim IIR-D-RCT-P1V3
MIC-2 MKII FCT DIN |  |  |  | CUB2 |  |  | Acuvim IIR-M-RCT-P1V3
MIB 8000C | CPB7 | [5 empty] | Acuvim-CL-D-5A-P1V4
MIC-2 MKII LV | CPB2 | [5 empty] | Acuvim IIR-D-5A-P2V3
Acuvim-L V4 | Panel Mount |  | DIN Rail
| 5A/1A | 333mV/RCT | 5A/1A | 333mV/RCT
Acuvim-CL | CP07 | CP27 | CU07 | CU27
Acuvim-EL | CP08 | CP28 | CU08 | CU28
PXE | Panel Mount |  | DIN Rail
Ring terminal
| 5A/1A |  | 5A/1A
PXE1M(T)B1(4)A-3 | CPE1 |  | CUE1
PXE2M(T)B1(4)A-3 | CPE4 |  | CUE4
Ring terminal
| 333mV/RCT |  | 333mV/RCT
PXE1M(T)B1(4)V-3 | CPE1 |  | CUE1
PXE2M(T)B1(4)V-3 | CPE4 |  | CUE4
4CT
| 5A/1A |  | 5A/1A
PXE1M(T)B1(4)A-4 | CPH1 |  | CUH1
PXE2M(T)B1(4)A-4 | CPH4 |  | CUH4
4CT
| 333mV/RCT |  | 333mV/RCT
PXE1M(T)B1(4)V-4 | CPH1 |  | CUH1
PXE2M(T)B1(4)V-4 | CPH4 |  | CUH4
M: panel mount with display T: DIN rail without display

## MiniLog
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory Value
| 0x8100 | 0x8101 |  |  | Clear Minilog Status | uint16 | W | 1
| 0x8101 | 0x8102 |  |  | Get available record amount | uint16 | R | 1
| 0x8102 | 0x8103 |  |  | Set the reading start position | uint16 | W | 1
| 0x8103 | 0x817B |  |  | Minilog data |  | R | 121 |  |  |  | Minilog data APU strcuture [ 000 - 001 ], 2 byte: available record amount (range: 1-5) [ 002 - 049 ], 48 byte: minilog record，[0-7] unix utc time, [8-43] 9 energy measurements map to (modbus reg 0x4048) [44-47] reserved [ 050 - 097 ], 48 byte: minilog record，[0-7] unix utc time, [8-43] 9 energy measurements map to (modbus reg 0x4048) [44-47] reserved [ 098 - 145 ], 48 byte: minilog record，[0-7] unix utc time, [8-43] 9 energy measurements map to (modbus reg 0x4048) [44-47] reserved [ 146 - 193 ], 48 byte: minilog record，[0-7] unix utc time, [8-43] 9 energy measurements map to (modbus reg 0x4048) [44-47] reserved [ 194 - 241 ], 48 byte: minilog record，[0-7] unix utc time, [8-43] 9 energy measurements map to (modbus reg 0x4048) [44-47] reserved

## Debug
Block | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value
Debug | 0x2420 | 0x2421 | 9248 | 9249 | In rush reboot counter | uint16 | R/W
| 0x9500 |  | 38144 |  | Normal reboot counter | uint16 | R/W
| 0x9501 |  | 38145 |  | ADE9000 in idle state counter | uint16 | R/W
| 0x9502 |  | 38146 |  | Loop internal | uint16 | R
| 0x9503 | 0x9504 | 38147 | 38148 | Waveform counter | uint32 | R/W

## Alarm ID
General | Alarm Parameter | List Number
| Frequency | 0
| Volts AN | 1
| Volts BN | 2
| Volts CN | 3
| Volts LN Average | 4
| Volts AB | 5
| Volts BC | 6
| Volts CA | 7
| Volts LL Average | 8
| I A | 9
| I B | 10
| I C | 11
| I Average | 12
| I N | 13
| Watt A | 14
| Watt B | 15
| Watt C | 16
| Watt Total | 17
| VAR A | 18
| VAR B | 19
| VAR C | 20
| VAR Total | 21
| VA A | 22
| VA B | 23
| VA C | 24
| VA Total | 25
| Pwr Factor A | 26
| Pwr Factor B | 27
| Pwr Factor C | 28
| Pwr Factor Total | 29
| Unbalance V | 30
| Unbalance I | 31
| Load Type | 32
| THD Volts AN/AB | 33
| THD Volts BN/CA | 34
| THD Volts CN/BC | 35
| THD Volts Average | 36
| THD I A | 37
| THD I B | 38
| THD I C | 39
| THD I Average | 40
| AI 311 | 41
| AI 312 | 42
| AI 321 | 43
| AI 322 | 44
| Watt Demand | 45
| Var Demand | 46
| VA Demand | 47
| Dmd I A | 48
| Dmd I B | 49
| Dmd I C | 50
| Reverse Phase Sequence | 51
| DI 111 | 52
| DI 112 | 53
| DI 113 | 54
| DI 114 | 55
| DI 115 | 56
| DI 116 | 57
| DI 211 | 58
| DI 212 | 59
| DI 213 | 60
| DI 214 | 61
| DI 311 | 62
| DI 312 | 63
| DI 313 | 64
| DI 314 | 65
| DI 121 | 66
| DI 122 | 67
| DI 123 | 68
| DI 124 | 69
| DI 125 | 70
| DI 126 | 71
| DI 221 | 72
| DI 222 | 73
| DI 223 | 74
| DI 224 | 75
| DI 321 | 76
| DI 322 | 77
| DI 323 | 78
| DI 324 | 79
ABB IO4 | RCM Channel 1 Status | 85
| RCM Channel 2 Status | 86
| RTD Channel 1 Status | 87
| RTD Channel 2 Status | 88
| RCM Channel 1 passive CT residual current (I_rms) | 89
| RCM Channel 1 Hall effect CT total residual current (I_total) | 90
| RCM Channel 1 Hall effect CT AC residual current (I_AC) | 91
| RCM Channel 1 Hall effect CT DC residual current (I_DC) | 92
| RCM Channel 2 passive CT residual current (I_rms) | 93
| RCM Channel 2 Hall effect CT total residual current (I_total) | 94
| RCM Channel 2 Hall effect CT AC residual current (I_AC) | 95
| RCM Channel 2 Hall effect CT DC residual current (I_DC) | 96
| RTD Channel 1 Temperature | 97
| RTD Channel 2 Temperature | 98