## Version history
Version | Changes | Author | Date | Internal Firmware Version | External Firmware Version
v1.00 |  |  |  | /

## Overview
Block | Sector | Sheet | Start | End | Length(reg num) | Comments
System Setting | System、Communication、Time Settings | Basic Settings | 0x1000 | 0x1006 | 6
| Basic Settings | Basic Settings | 0x1040 | 0x10A0 | 97
| Metrology Settings | Basic Settings | 0x10AA | 0x17CC | 1827
| Operations | Basic Settings | 0x17D6 | 0x17DB | 6
Wring Check | Wiring Check | Wiring Check | 0x1300 | 0x13EC | 237
HS(Half Cycle) | RMS(Half Cycle) | RMS(Half Cycle) | 0x2000 | 0x2400 | 677
Energy | Energy | Energy | 0x2500 | 0x268E | 399
Demand | Demand | Demand | 0x2700 | 0x2842 | 323
10¦12 Cycle | RMS(10/12 Cycle) | RMS(10/12 Cycle) | 0x2900 | 0x2BB1 | 690
| Power(10/12 Cycle) | Power(10/12 Cycle) | 0x2BB2 | 0x2C22 | 113
| Power Quality(10/12 Cycle) | Power Quality(10/12 Cycle) | 0x2C23 | 0x3FF2 | 5072
150¦180 Cycle | RMS(150¦180 Cycle) | RMS(150¦180 Cycle) | 0x4000 | 0x42B1 | 690
| Power(150¦180 Cycle) | Power(150¦180 Cycle) | 0x42B2 | 0x4322 | 113
| Power Quality(150¦180 Cycle) | Power Quality(150¦180 Cycle) | 0x4323 | 0x56F2 | 5072
| Flicker | Flicker | 0x56F3 | 0x56FE | 12
10 Min | RMS(10 Min) | RMS(10 Min) | 0x5710 | 0x59C1 | 690
| Power(10 Min) | Power(10 Min) | 0x59C2 | 0x5A32 | 113
| Power Quality(10 Min) | Power Quality(10 Min) | 0x5A33 | 0x6E02 | 5072
| Flicker(10 Min) | Flicker(10 Min) | 0x6E03 | 0x6E0E | 12
2 Hr | RMS(2Hr) | RMS(2Hr) | 0x6E20 | 0x70D1 | 690
| Power(2Hr) | Power(2Hr) | 0x70D2 | 0x7142 | 113
| Power Quality(2Hr) | Power Quality(2Hr) | 0x7143 | 0x8512 | 5072
| Flicker(2Hr) | Flicker(2Hr) | 0x8513 | 0x851E | 12
10S Freq | 10S Freq | 10S Freq | 0x8530 | 0x853F | 16
MaxMin | Max Record Value | Max Record Value | 0x8550 | 0x8BCB | 1660
| Min Record Value | Min Record Value | 0x8BE0 | 0x925B | 1660
Max Demand | MaxDemand | MaxDemand | 0x9270 | 0x9632 | 963
Information | Device Info | Device Info | 0x9650 | 0x9700 | 177
| MH Info | MH Info | 0x9710 | 0x9714 | 5
DeviceStatus | Configure Device Running States | Configure Device Running States | 0x9720 | 0x9786 | 103
Waveform¦PQ Event | Power Quality Event setting | Power Quality Event setting | 0x9790 | 0x92B1 | 34
| Waveform Setting | Waveform Setting | 0x92B2 | 0x92B3 | 2
| PQ Event Log | PQ Event Log |  |  |  | reserved
| Waveform Log | Waveform Log |  |  |  | reserved
AlarmStatus | [5 empty] | reserved

## Basic Settings
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
System Setting
Communication | 0x1000 | 0x1000 | 4096 | 4096 | Modbus Slave ID | uint16_t | R/W | 1 | 1-247, used for both Modbus RTU and TCP
| 0x1001 | 0x1001 | 4097 | 4097 | Modbus TCP Enable | uint16_t | R/W | 1 | 0: disable 1: enable | 0
| 0x1002 | 0x1002 | 4098 | 4098 | Modbus TCP Port | uint16_t | R/W | 1 | 1-65534 | 502
| 0x1003 | 0x1003 | 4099 | 4099 | COM1 Interface | uint16_t | R/W | 1 | 0: Client 1: Server | 0: Client
| 0x1004 | 0x1004 | 4100 | 4100 | COM2 Interface | uint16_t | R/W | 1 | 0: Client 1: Server | 0: Client
| 0x1005 | 0x1005 | 4101 | 4101 | Baud Rate | uint16_t | R/W | 1 | 0: 9600 1: 19200 2: 38400 3: 57600 4: 115200 | 19200
| 0x1006 | 0x1006 | 4102 | 4102 | Parity | uint16_t | R/W | 1 | 0: None1 1: None2 2: Even 3: Odd | 0: None1
Basic Settings | 0x1040 | 0x104F | 4160 | 4175 | VMM1 Serial Number | uint8_t | R/W | 16 | ASCII string, 32 bytes (16 registers) | None
| 0x1050 | 0x105F | 4176 | 4191 | VMM2 Serial Number | uint8_t | R/W | 16 | ASCII string, 32 bytes (16 registers) | None
| 0x1060 | 0x106F | 4192 | 4207 | CMM1 Serial Number | uint8_t | R/W | 16 | ASCII string, 32 bytes (16 registers) | None
| 0x1070 | 0x107F | 4208 | 4223 | CMM2 Serial Number | uint8_t | R/W | 16 | ASCII string, 32 bytes (16 registers) | None
| 0x1080 | 0x108F | 4224 | 4239 | CMM3 Serial Number | uint8_t | R/W | 16 | ASCII string, 32 bytes (16 registers) | None
| 0x1090 | 0x109F | 4240 | 4255 | CMM4 Serial Number | uint8_t | R/W | 16 | ASCII string, 32 bytes (16 registers) | None
| 0x10A0 | 0x10A0 | 4256 | 4256 | VMM Operating Mode | uint16_t | R/W | 1 | 1: Dual VMM – Independent 2: Dual VMM – Mirrored | Dual VMM – Independent
Metrology Settings | 0x10AA | 0x10AA | 4266 | 4266 | VMM1 Service Configuration | uint16_t | R/W | 1 | 0: ELEMENT_1_WIRE_2 1: ELEMENT_2_WIRE_3_PHASE_1 2: ELEMENT_2_WIRE_3_DELTA 3: ELEMENT_2_WIRE_3_NETWORK 4: ELEMENT_3_WIRE_4_Y 5: ELEMENT_3_WIRE_4_DELTA
| 0x10AB | 0x10AC | 4267 | 4268 | VMM1 PT1 | uint32_t | R/W | 2 | 50-1000000
| 0x10AD | 0x10AD | 4269 | 4269 | VMM1 PT2 | uint16_t | R/W | 1 | 50-830
| 0x10AE | 0x10AE | 4270 | 4270 | VMM1 Phase Order | uint16_t | R/W | 1 | 0:ABC 1:ACB
| 0x10AF | 0x10AF | 4271 | 4271 | VMM1 Flicker Settings | uint16_t | R/W | 1 | 0: Disable 1: Automatic 2:120V-50Hz-60W Incandescent 3:230V-50Hz-60W Incandescent 4:120V-60Hz-60W Incandescent 5:230V-60Hz-60W Incandescent
| 0x10B0 | 0x10B5 | 4272 | 4277 | VMM2 Metrology Settings | uint16_t | R/W | 6
| 0x10B6 | 0x10B6 | 4278 | 4278 | CMM1 Channel 1 Input Wiring ID | uint16_t | R/W | 1 | 1~24
| 0x10B7 | 0x10B7 | 4279 | 4279 | CMM1 Channel 1 CT Type | uint16_t | R/W | 1 | 1: 333mV 2: RCT
| 0x10B8 | 0x10B8 | 4280 | 4280 | CMM1 Channel 1 Primary | uint16_t | R/W | 1 | 1-50000 A
| 0x10B9 | 0x10B9 | 4281 | 4281 | CMM1 Channel 1 Direction | uint16_t | R/W | 1 | 0:positive 1:negative
| 0x10BA | 0x1115 | 4282 | 4373 | CMM1 Channel 2-24 Metrology Settings | uint16_t | R/W | 92
| 0x1116 | 0x118E | 4374 | 4494 | CMM2 Channel 25-48 Metrology Settings | uint16_t | R/W | 121
| 0x118F | 0x1207 | 4495 | 4615 | CMM3 Channel 49-72 Metrology Settings | uint16_t | R/W | 121
| 0x1208 | 0x1280 | 4616 | 4736 | CMM4 Channel 73-96 Metrology Settings | uint16_t | R/W | 121
| 0x1281 | 0x1281 | 4737 | 4737 | MP1 VMM Select | uint16_t | R/W | 1 | 0:VMM1,1:VMM2
| 0x1282 | 0x1282 | 4738 | 4738 | MP1 Wiring Type | uint16_t | R/W | 1 | 0: ELEMENT_1_WIRE_2 1: ELEMENT_2_WIRE_3_PHASE_1 2: ELEMENT_2_WIRE_3_DELTA 3: ELEMENT_2_WIRE_3_NETWORK 4: ELEMENT_3_WIRE_4_Y 5: ELEMENT_3_WIRE_4_DELTA
| 0x1283 | 0x1285 | 4739 | 4741 | MP1 Phase Slot Assignment 1-3 | uint16_t | R/W | 3 | Three uint16_t arrays for the three slot settings(1-96); unused entries filled with 0.
| 0x1286 | 0x1286 | 4742 | 4742 | MP1 Neutral Source | uint16_t | R/W | 1 | 0:None 1:Calculated 2:Measured
| 0x1287 | 0x1287 | 4743 | 4743 | MP1 Neutral Measured Channel Ref | uint16_t | R/W | 1 | 1~96
| 0x1288 | 0x17C0 | 4744 | 6080 | MP2-MP192 Metrology Settings |  | R/W | 1337
| 0x17C1 | 0x17C1 | 6081 | 6081 | Frequency Selection | uint16_t | R/W | 1 | 0: 50Hz 1: 60Hz
| 0x17C2 | 0x17C2 | 6082 | 6082 | PF Convention | uint16_t | R/W | 1 | PF Format IEC: 0 PF Format IEEE: 1
| 0x17C3 | 0x17C3 | 6083 | 6083 | Demand Algorithm | uint16_t | R/W | 1 | Fixed Window: 0 Sliding Window: 1
| 0x17C4 | 0x17C4 | 6084 | 6084 | Demand Interval | uint16_t | R/W | 1 | 1~30 minute
| 0x17C5 | 0x17C5 | 6085 | 6085 | Demand Update Interval | uint16_t | R/W | 1 | 1~30 minute
| 0x17C6 | 0x17C6 | 6086 | 6086 | Energy Calculation Method | uint16_t | R/W | 1 | Generic: 0 Fundamental: 1
| 0x17C7 | 0x17C8 | 6087 | 6088 | Energy pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001)
| 0x17C9 | 0x17C9 | 6089 | 6089 | Pulse LED width | uint16_t | R/W | 1 | 20~100ms
| 0x17CA | 0x17CA | 6090 | 6090 | Pulse LED parameter selection | uint16_t | R/W | 1 | Energy parameter IDs(1-946)
| 0x17CB | 0x17CB | 6091 | 6091 | Harmonic Group Setting | uint16_t | R/W | 1 | 0: Harmonic group 1: Harmonic subgroup
| 0x17CC | 0x17CC | 6092 | 6092 | Harmonic/Inter-harmonic Setting | uint16_t | R/W | 1 | 0: Harmonic 1:Harmonic & Inter-harmonic
Operation | 0x17D6 | 0x17D6 | 6102 | 6102 | Reboot | uint16_t | R/W | 1
| 0x17D7 | 0x17D7 | 6103 | 6103 | Factory Reset | uint16_t | R/W | 1
| 0x17D8 | 0x17D8 | 6104 | 6104 | Clear Runtime | uint16_t | R/W | 1
| 0x17D9 | 0x17D9 | 6105 | 6105 | Clear LoadTime | uint16_t | R/W | 1
| 0x17DA | 0x17DA | 6106 | 6106 | Clear MaxMin | uint16_t | R/W | 1
| 0x17DB | 0x17DB | 6107 | 6107 | Clear MaxDemand | uint16_t | R/W | 1

## Wring Check
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Wiring Check | 0x1300 | 0x1300 | 4864 | 4864 | Wire Check Start | uint16_t | R/W | 1 | 0:Idle 1:Start
| 0x1301 | 0x1301 | 4865 | 4865 | Wire Check Status | uint16_t | R | 1 | 0: Not Started 1: In Progress 2: Completed
| 0x1302 | 0x1302 | 4866 | 4866 | VMM1 Phase Voltage Error Code | uint16_t | R | 1 | Bit0:Voltage terminals Va wiring is missing Bit1:Voltage terminals Vb wiring is missing Bit2:Voltage terminals Vc wiring is missing Bit3:The voltage terminals Va and Vn are reversed. Bit4: The voltage terminals Vb and Vn are reversed. Bit5: The voltage terminals Vc and Vn are reversed. Bit6: Phase error of voltage terminals Vb Bit7: Phase error of voltage terminals Vc Bit8: ABC/ACB sequence is configured incorrectly
| 0x1303 | 0x1303 | 4867 | 4867 | VMM2 Phase Voltage Error Code | uint16_t | R | 1
| 0x1304 | 0x13C3 | 4868 | 5059 | MP1-MP192 Phase Current Error Code | uint16_t | R | 192 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： Bit0:Current terminals Ia wiring is missing Bit1:Current terminals Ib wiring is missing Bit2:Current terminals Ic wiring is missing Bit3:Current terminals Ia positive and negative are reversed Bit4:Current terminals Ib positive and negative are reversed Bit5:Current terminals Ic positive and negative are reversed Bit6:Incorrect phase sequence of current Ia Bit7:Incorrect phase sequence of current Ib Bit8:Incorrect phase sequence of current Ic (1E2W)： bit0: Current terminals Input Channal 1 wiring is missing Bit1: Current terminals Input Channal 1 positive and negative are reversed Bit2: Current terminals Input Channal 2 wiring is missing Bit3: Current terminals Input Channal 2 positive and negative are reversed Bit4: Current terminals Input Channal 3 wiring is missing Bit5: Current terminals Input Channal 3 positive and negative are reversed
| 0x13C4 | 0x13C5 | 5060 | 5061 | VMM1 Phase A Line-to-Neutral / Phase AB Line-to-Line Voltage | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase A Line-to-Neutral Voltage (2E3WDelta)： Phase AB Line-to-Line Voltage
| 0x13C6 | 0x13C7 | 5062 | 5063 | VMM1 Phase A Line-to-Neutral / Phase AB Line-to-Line Voltage Phase Angle | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase A Line-to-Neutral Voltage (2E3WDelta)： Phase AB Line-to-Line Voltage
| 0x13C8 | 0x13C9 | 5064 | 5065 | VMM1 Phase B Line-to-Neutral / Phase BC Line-to-Line Voltage | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase A Line-to-Neutral Voltage (2E3WDelta)： Phase AB Line-to-Line Voltage
| 0x13CA | 0x13CB | 5066 | 5067 | VMM1 Phase B Line-to-Neutral / Phase BC Line-to-Line Voltage Phase Angle | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase A Line-to-Neutral Voltage (2E3WDelta)： Phase AB Line-to-Line Voltage
| 0x13CC | 0x13CD | 5068 | 5069 | VMM1 Phase C Line-to-Neutral / Phase CA Line-to-Line Voltage | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase A Line-to-Neutral Voltage (2E3WDelta)： Phase AB Line-to-Line Voltage
| 0x13CE | 0x13CF | 5070 | 5071 | VMM1 Phase C Line-to-Neutral / Phase CA Line-to-Line Voltage Phase Angle | float | R | 2 | (2E3W1P、1E2W、3E4WY、2E3WNetwork)： Phase A Line-to-Neutral Voltage (2E3WDelta)： Phase AB Line-to-Line Voltage
| 0x13D0 | 0x13D1 | 5072 | 5073 | VMM1 Voltage Phase Order | float | R | 2 | 8
| 0x13D2 | 0x13DF | 5074 | 5087 | VMM2 Wring Check Voltage Measured value | float | R | 14
| 0x13E0 | 0x13E0 | 5088 | 5088 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x13E1 | 0x13E2 | 5089 | 5090 | MPx Phase A Curent | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： MP1 Phase A Curent (1E2W)： MP1 Input Channel 1 Curent
| 0x13E3 | 0x13E4 | 5091 | 5092 | MPx Phase A Curent Angle | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： MP1 Phase A Curent (1E2W)： MP1 Input Channel 1 Curent Angle
| 0x13E5 | 0x13E6 | 5093 | 5094 | MPx Phase B Curent | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： MP1 Phase B Curent (1E2W)： MP1 Input Channel 2 Curent
| 0x13E7 | 0x13E8 | 5095 | 5096 | MPx Phase B Curent Angle | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： MP1 Phase B Curent (1E2W)： MP1 Input Channel 2 Curent Angle
| 0x13E9 | 0x13EA | 5097 | 5098 | MPx Phase C Curent | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： MP1 Phase C Curent (1E2W)： MP1 Input Channel 3 Curent
| 0x13EB | 0x13EC | 5099 | 5100 | MPx Phase C Curent Angle | float | R | 2 | (2E3W1P、2E3WDelta、3E4WY、2E3WNetwork)： MP1 Phase C Curent (1E2W)： MP1 Input Channel 3 Curent Angle

## HS(Half Cycle)
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
RMS(Half Cycle) |  |  |  |  | HS Param Update Time Stamp | uint64_t | R | 4
| 0x2000 | 0x2001 | 8192 | 8193 | VMM1 System Frequency | float | R | 2
| 0x2002 | 0x2003 | 8194 | 8195 | VMM1 Phase A Line-to-Neutral Voltage | float | R | 2
| 0x2004 | 0x2005 | 8196 | 8197 | VMM1 Phase B Line-to-Neutral Voltage | float | R | 2
| 0x2006 | 0x2007 | 8198 | 8199 | VMM1 Phase C Line-to-Neutral Voltage | float | R | 2
| 0x2008 | 0x2009 | 8200 | 8201 | VMM1 Phase A Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x200A | 0x200B | 8202 | 8203 | VMM1 Phase B Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x200C | 0x200D | 8204 | 8205 | VMM1 Phase C Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x200E | 0x200F | 8206 | 8207 | VMM1 Average Line-to-Neutral Voltage | float | R | 2
| 0x2010 | 0x2011 | 8208 | 8209 | VMM1 Phase AB Line-to-Line Voltage | float | R | 2
| 0x2012 | 0x2013 | 8210 | 8211 | VMM1 Phase BC Line-to-Line Voltage | float | R | 2
| 0x2014 | 0x2015 | 8212 | 8213 | VMM1 Phase CA Line-to-Line Voltage | float | R | 2
| 0x2016 | 0x2017 | 8214 | 8215 | VMM1 Phase AB Line-to-Line Voltage Phase Angle | float | R | 2
| 0x2018 | 0x2019 | 8216 | 8217 | VMM1 Phase BC Line-to-Line Voltage Phase Angle | float | R | 2
| 0x201A | 0x201B | 8218 | 8219 | VMM1 Phase CA Line-to-Line Voltage Phase Angle | float | R | 2
| 0x201C | 0x201D | 8220 | 8221 | VMM1 Average Line-to-Line Voltage | float | R | 2
| 0x201E | 0x201F | 8222 | 8223 | VMM1 Phase A Current | float | R | 2
| 0x2020 | 0x2021 | 8224 | 8225 | VMM1 Phase B Current | float | R | 2
| 0x2022 | 0x2023 | 8226 | 8227 | VMM1 Phase C Current | float | R | 2
| 0x2024 | 0x2025 | 8228 | 8229 | VMM1 Neutral Current | float | R | 2
| 0x2026 | 0x2027 | 8230 | 8231 | VMM1 Phase A Current Phase Angle | float | R | 2
| 0x2028 | 0x2029 | 8232 | 8233 | VMM1 Phase B Current Phase Angle | float | R | 2
| 0x202A | 0x202B | 8234 | 8235 | VMM1 Phase C Current Phase Angle | float | R | 2
| 0x202C | 0x202D | 8236 | 8237 | VMM1 Neutral Current Phase Angle | float | R | 2
| 0x202E | 0x205D | 8238 | 8285 | VMM1 CMM1 Input Channel 1-24 Current Angle | float | R | 48
| 0x205E | 0x208D | 8286 | 8333 | VMM1 CMM2 Input Channel 1-24 Current Angle | float | R | 48
| 0x208E | 0x20BD | 8334 | 8381 | VMM1 CMM3 Input Channel 1-24 Current Angle | float | R | 48
| 0x20BE | 0x20ED | 8382 | 8429 | VMM1 CMM4 Input Channel 1-24 Current Angle | float | R | 48
| 0x20EE | 0x21DB | 8430 | 8667 | VMM2 Realtime Parameter | float | R | 238
| 0x21DC | 0x220B | 8668 | 8715 | CMM1 Input Channel 1-24 Current | float | R | 48
| 0x220C | 0x223B | 8716 | 8763 | CMM2 Input Channel 25-48 Current | float | R | 48
| 0x223C | 0x226B | 8764 | 8811 | CMM3 Input Channel 49-72 Current | float | R | 48
| 0x226C | 0x229B | 8812 | 8859 | CMM4 Input Channel 73-96 Current | float | R | 48
| 0x229C | 0x229C | 8860 | 8860 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x229D | 0x229E | 8861 | 8862 | MP1 Neutral Current | float | R | 2
| 0x229F | 0x22A0 | 8863 | 8864 | MP1 Neutral Current Phase Angle | float | R | 2

## Energy（1s）
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Energy | 0x2500 | 0x2503 | 9472 | 9475 | VMM1 Phase A active energy import | double | R | 4
| 0x2504 | 0x2507 | 9476 | 9479 | VMM1 Phase A active energy export | double | R | 4
| 0x2508 | 0x250B | 9480 | 9483 | VMM1 Phase A active energy net | double | R | 4
| 0x250C | 0x250F | 9484 | 9487 | VMM1 Phase A active energy total | double | R | 4
| 0x2510 | 0x2513 | 9488 | 9491 | VMM1 Phase A reactive energy import | double | R | 4
| 0x2514 | 0x2517 | 9492 | 9495 | VMM1 Phase A reactive energy export | double | R | 4
| 0x2518 | 0x251B | 9496 | 9499 | VMM1 Phase A reactive energy net | double | R | 4
| 0x251C | 0x251F | 9500 | 9503 | VMM1 Phase A reactive energy total | double | R | 4
| 0x2520 | 0x2523 | 9504 | 9507 | VMM1 Phase A apparent energy | double | R | 4
| 0x2524 | 0x2527 | 9508 | 9511 | VMM1 Phase B active energy import | double | R | 4
| 0x2528 | 0x252B | 9512 | 9515 | VMM1 Phase B active energy export | double | R | 4
| 0x252C | 0x252F | 9516 | 9519 | VMM1 Phase B active energy net | double | R | 4
| 0x2530 | 0x2533 | 9520 | 9523 | VMM1 Phase B active energy total | double | R | 4
| 0x2534 | 0x2537 | 9524 | 9527 | VMM1 Phase B reactive energy import | double | R | 4
| 0x2538 | 0x253B | 9528 | 9531 | VMM1 Phase B reactive energy export | double | R | 4
| 0x253C | 0x253F | 9532 | 9535 | VMM1 Phase B reactive energy net | double | R | 4
| 0x2540 | 0x2543 | 9536 | 9539 | VMM1 Phase B reactive energy total | double | R | 4
| 0x2544 | 0x2547 | 9540 | 9543 | VMM1 Phase B apparent energy | double | R | 4
| 0x2548 | 0x254B | 9544 | 9547 | VMM1 Phase C active energy import | double | R | 4
| 0x254C | 0x254F | 9548 | 9551 | VMM1 Phase C active energy export | double | R | 4
| 0x2550 | 0x2553 | 9552 | 9555 | VMM1 Phase C active energy net | double | R | 4
| 0x2554 | 0x2557 | 9556 | 9559 | VMM1 Phase C active energy total | double | R | 4
| 0x2558 | 0x255B | 9560 | 9563 | VMM1 Phase C reactive energy import | double | R | 4
| 0x255C | 0x255F | 9564 | 9567 | VMM1 Phase C reactive energy export | double | R | 4
| 0x2560 | 0x2563 | 9568 | 9571 | VMM1 Phase C reactive energy net | double | R | 4
| 0x2564 | 0x2567 | 9572 | 9575 | VMM1 Phase C reactive energy total | double | R | 4
| 0x2568 | 0x256B | 9576 | 9579 | VMM1 Phase C apparent energy | double | R | 4
| 0x256C | 0x256F | 9580 | 9583 | VMM1 System active energy import | double | R | 4
| 0x2570 | 0x2573 | 9584 | 9587 | VMM1 System active energy export | double | R | 4
| 0x2574 | 0x2577 | 9588 | 9591 | VMM1 System active energy net | double | R | 4
| 0x2578 | 0x257B | 9592 | 9595 | VMM1 System active energy total | double | R | 4
| 0x257C | 0x257F | 9596 | 9599 | VMM1 System reactive energy import | double | R | 4
| 0x2580 | 0x2583 | 9600 | 9603 | VMM1 System reactive energy export | double | R | 4
| 0x2584 | 0x2587 | 9604 | 9607 | VMM1 System reactive energy net | double | R | 4
| 0x2588 | 0x258B | 9608 | 9611 | VMM1 System reactive energy total | double | R | 4
| 0x258C | 0x258F | 9612 | 9615 | VMM1 System apparent energy | double | R | 4
| 0x2590 | 0x2590 | 9616 | 9616 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x2591 | 0x2594 | 9617 | 9620 | VMM1 CMM1 Input Channel 1 active energy import | double | R | 4
| 0x2595 | 0x2598 | 9621 | 9624 | VMM1 CMM1 Input Channel 1 active energy export | double | R | 4
| 0x2599 | 0x259C | 9625 | 9628 | VMM1 CMM1 Input Channel 1 active energy net | double | R | 4
| 0x259D | 0x25A0 | 9629 | 9632 | VMM1 CMM1 Input Channel 1 active energy total | double | R | 4
| 0x25A1 | 0x25A4 | 9633 | 9636 | VMM1 CMM1 Input Channel 1 reactive energy import | double | R | 4
| 0x25A5 | 0x25A8 | 9637 | 9640 | VMM1 CMM1 Input Channel 1 reactive energy export | double | R | 4
| 0x25A9 | 0x25AC | 9641 | 9644 | VMM1 CMM1 Input Channel 1 reactive energy net | double | R | 4
| 0x25AD | 0x25B0 | 9645 | 9648 | VMM1 CMM1 Input Channel 1 reactive energy total | double | R | 4
| 0x25B1 | 0x25B4 | 9649 | 9652 | VMM1 CMM1 Input Channel 1 apparent energy | double | R | 4
| 0x25B5 | 0x2669 | 9653 | 9833 | VMM2 Energy Parameter |  | R | 181
| 0x266A | 0x266A | 9834 | 9834 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x266B | 0x266E | 9835 | 9838 | MP1 active energy import | double | R | 4
| 0x266F | 0x2672 | 9839 | 9842 | MP1 active energy export | double | R | 4
| 0x2673 | 0x2676 | 9843 | 9846 | MP1 active energy net | double | R | 4
| 0x2677 | 0x267A | 9847 | 9850 | MP1 active energy total | double | R | 4
| 0x267B | 0x267E | 9851 | 9854 | MP1 reactive energy import | double | R | 4
| 0x267F | 0x2682 | 9855 | 9858 | MP1 reactive energy export | double | R | 4
| 0x2683 | 0x2686 | 9859 | 9862 | MP1 reactive energy net | double | R | 4
| 0x2687 | 0x268A | 9863 | 9866 | MP1 reactive energy total | double | R | 4
| 0x268B | 0x268E | 9867 | 9870 | MP1 apparent energy | double | R | 4

## Demand
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Demand | 0x2700 | 0x2701 | 9984 | 9985 | VMM1 Phase A Current Demand | float | R | 2
| 0x2702 | 0x2703 | 9986 | 9987 | VMM1 Phase A Import Active Power Demand | float | R | 2
| 0x2704 | 0x2705 | 9988 | 9989 | VMM1 Phase A Export Active Power Demand | float | R | 2
| 0x2706 | 0x2707 | 9990 | 9991 | VMM1 Phase A Import Reactive Power Demand | float | R | 2
| 0x2708 | 0x2709 | 9992 | 9993 | VMM1 Phase A Export Reactive Power Demand | float | R | 2
| 0x270A | 0x270B | 9994 | 9995 | VMM1 Phase A Apparent Power Demand | float | R | 2
| 0x270C | 0x270D | 9996 | 9997 | VMM1 Phase B Current Demand | float | R | 2
| 0x270E | 0x270F | 9998 | 9999 | VMM1 Phase B Import Active Power Demand | float | R | 2
| 0x2710 | 0x2711 | 10000 | 10001 | VMM1 Phase B Export Active Power Demand | float | R | 2
| 0x2712 | 0x2713 | 10002 | 10003 | VMM1 Phase B Import Reactive Power Demand | float | R | 2
| 0x2714 | 0x2715 | 10004 | 10005 | VMM1 Phase B Export Reactive Power Demand | float | R | 2
| 0x2716 | 0x2717 | 10006 | 10007 | VMM1 Phase B Apparent Power Demand | float | R | 2
| 0x2718 | 0x2719 | 10008 | 10009 | VMM1 Phase C Current Demand | float | R | 2
| 0x271A | 0x271B | 10010 | 10011 | VMM1 Phase C Import Active Power Demand | float | R | 2
| 0x271C | 0x271D | 10012 | 10013 | VMM1 Phase C Export Active Power Demand | float | R | 2
| 0x271E | 0x271F | 10014 | 10015 | VMM1 Phase C Import Reactive Power Demand | float | R | 2
| 0x2720 | 0x2721 | 10016 | 10017 | VMM1 Phase C Export Reactive Power Demand | float | R | 2
| 0x2722 | 0x2723 | 10018 | 10019 | VMM1 Phase C Apparent Power Demand | float | R | 2
| 0x2724 | 0x2725 | 10020 | 10021 | VMM1 System Average Current Demand | float | R | 2
| 0x2726 | 0x2727 | 10022 | 10023 | VMM1 System Import Active Power Demand | float | R | 2
| 0x2728 | 0x2729 | 10024 | 10025 | VMM1 System Export Active Power Demand | float | R | 2
| 0x272A | 0x272B | 10026 | 10027 | VMM1 System Import Reactive Power Demand | float | R | 2
| 0x272C | 0x272D | 10028 | 10029 | VMM1 System Export Reactive Power Demand | float | R | 2
| 0x272E | 0x272F | 10030 | 10031 | VMM1 System Apparent Power Demand | float | R | 2
| 0x2730 | 0x275F | 10032 | 10079 | VMM2 Demand Parameter | float | R | 48
| 0x2760 | 0x278F | 10080 | 10127 | CMM1 Input Channel 1-24 Current Demand | float | R | 48
| 0x2790 | 0x27BF | 10128 | 10175 | CMM2 Input Channel 25-48 Current Demand | float | R | 48
| 0x27C0 | 0x27EF | 10176 | 10223 | CMM3 Input Channel 49-72 Current Demand | float | R | 48
| 0x27F0 | 0x281F | 10224 | 10271 | CMM4 Input Channel 73-96 Current Demand | float | R | 48
| 0x2820 | 0x2820 | 10272 | 10272 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x2821 | 0x2822 | 10273 | 10274 | VMM1 CMM1 Input Channel 1 Import Active Power Demand | float | R | 2
| 0x2823 | 0x2824 | 10275 | 10276 | VMM1 CMM1 Input Channel 1 Export Active Power Demand | float | R | 2
| 0x2825 | 0x2826 | 10277 | 10278 | VMM1 CMM1 Input Channel 1 Import Reactive Power Demand | float | R | 2
| 0x2827 | 0x2828 | 10279 | 10280 | VMM1 CMM1 Input Channel 1 Export Reactive Power Demand | float | R | 2
| 0x2829 | 0x282A | 10281 | 10282 | VMM1 CMM1 Input Channel 1 Apparent Power Demand | float | R | 2
| 0x282B | 0x282B | 10283 | 10283 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x282C | 0x282D | 10284 | 10285 | VMM2 CMM1 Input Channel 1 Import Active Power Demand | float | R | 2
| 0x282E | 0x282F | 10286 | 10287 | VMM2 CMM1 Input Channel 1 Export Active Power Demand | float | R | 2
| 0x2830 | 0x2831 | 10288 | 10289 | VMM2 CMM1 Input Channel 1 Import Reactive Power Demand | float | R | 2
| 0x2832 | 0x2833 | 10290 | 10291 | VMM2 CMM1 Input Channel 1 Export Reactive Power Demand | float | R | 2
| 0x2834 | 0x2835 | 10292 | 10293 | VMM2 CMM1 Input Channel 1 Apparent Power Demand | float | R | 2
| 0x2836 | 0x2836 | 10294 | 10294 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x2837 | 0x2838 | 10295 | 10296 | MP1 Average Current Demand | float | R | 2
| 0x2839 | 0x283A | 10297 | 10298 | MP1 Import Active Power Demand | float | R | 2
| 0x283B | 0x283C | 10299 | 10300 | MP1 Export Active Power Demand | float | R | 2
| 0x283D | 0x283E | 10301 | 10302 | MP1 Import Reactive Power Demand | float | R | 2
| 0x283F | 0x2840 | 10303 | 10304 | MP1 Export Reactive Power Demand | float | R | 2
| 0x2841 | 0x2842 | 10305 | 10306 | MP1 Apparent Power Demand | float | R | 2

## 10¦12 Cycle
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
RMS(10/12 Cycle) | 0x2900 | 0x2903 | 10496 | 10499 | 10/12 Cycle RMS Param Update Timestamp | uint64_t | R | 4
| 0x2904 | 0x2904 | 10500 | 10500 | 10/12 Cycle RMS Param Valid Flag(50160) | uint16_t | R | 1
| 0x2905 | 0x2905 | 10501 | 10501 | 10/12 Cycle RMS Param Event Flag | uint16_t | R | 1
| 0x2906 | 0x2906 | 10502 | 10502 | 10/12 Cycle RMS Param Block Number | uint16_t | R | 1
| 0x2907 | 0x2908 | 10503 | 10504 | VMM1 System Frequency | float | R | 2
| 0x2909 | 0x290A | 10505 | 10506 | VMM1 Phase A Line-to-Neutral Voltage | float | R | 2
| 0x290B | 0x290C | 10507 | 10508 | VMM1 Phase B Line-to-Neutral Voltage | float | R | 2
| 0x290D | 0x290E | 10509 | 10510 | VMM1 Phase C Line-to-Neutral Voltage | float | R | 2
| 0x290F | 0x2910 | 10511 | 10512 | VMM1 Phase A Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x2911 | 0x2912 | 10513 | 10514 | VMM1 Phase B Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x2913 | 0x2914 | 10515 | 10516 | VMM1 Phase C Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x2915 | 0x2916 | 10517 | 10518 | VMM1 Average Line-to-Neutral Voltage | float | R | 2
| 0x2917 | 0x2918 | 10519 | 10520 | VMM1 Phase AB Line-to-Line Voltage | float | R | 2
| 0x2919 | 0x291A | 10521 | 10522 | VMM1 Phase BC Line-to-Line Voltage | float | R | 2
| 0x291B | 0x291C | 10523 | 10524 | VMM1 Phase CA Line-to-Line Voltage | float | R | 2
| 0x291D | 0x291E | 10525 | 10526 | VMM1 Phase AB Line-to-Line Voltage Phase Angle | float | R | 2
| 0x291F | 0x2920 | 10527 | 10528 | VMM1 Phase BC Line-to-Line Voltage Phase Angle | float | R | 2
| 0x2921 | 0x2922 | 10529 | 10530 | VMM1 Phase CA Line-to-Line Voltage Phase Angle | float | R | 2
| 0x2923 | 0x2924 | 10531 | 10532 | VMM1 Average Line-to-Line Voltage | float | R | 2
| 0x2925 | 0x2926 | 10533 | 10534 | VMM1 Voltage Phase Order | float | R | 2
| 0x2927 | 0x2928 | 10535 | 10536 | VMM1 Phase A Current | float | R | 2
| 0x2929 | 0x292A | 10537 | 10538 | VMM1 Phase B Current | float | R | 2
| 0x292B | 0x292C | 10539 | 10540 | VMM1 Phase C Current | float | R | 2
| 0x292D | 0x292E | 10541 | 10542 | VMM1 Neutral Current | float | R | 2
| 0x292F | 0x2930 | 10543 | 10544 | VMM1 System Average Current | float | R | 2
| 0x2931 | 0x2932 | 10545 | 10546 | VMM1 Phase A Current Phase Angle | float | R | 2
| 0x2933 | 0x2934 | 10547 | 10548 | VMM1 Phase B Current Phase Angle | float | R | 2
| 0x2935 | 0x2936 | 10549 | 10550 | VMM1 Phase C Current Phase Angle | float | R | 2
| 0x2937 | 0x2938 | 10551 | 10552 | VMM1 Neutral Current Phase Angle | float | R | 2
| 0x2939 | 0x2968 | 10553 | 10600 | VMM1 CMM1 Input Channel 1-24 Current Angle | float | R | 48
| 0x2969 | 0x2998 | 10601 | 10648 | VMM1 CMM2 Input Channel 1-24 Current Angle | float | R | 48
| 0x2999 | 0x29C8 | 10649 | 10696 | VMM1 CMM3 Input Channel 1-24 Current Angle | float | R | 48
| 0x29C9 | 0x29F8 | 10697 | 10744 | VMM1 CMM4 Input Channel 1-24 Current Angle | float | R | 48
| 0x29F9 | 0x2AEA | 10745 | 10986 | VMM2 Realtime Parameter | float | R | 242
| 0x2AEB | 0x2B1A | 10987 | 11034 | CMM1 Input Channel 1-24 Current | float | R | 48
| 0x2B1B | 0x2B4A | 11035 | 11082 | CMM2 Input Channel 25-48 Current | float | R | 48
| 0x2B4B | 0x2B7A | 11083 | 11130 | CMM3 Input Channel 49-72 Current | float | R | 48
| 0x2B7B | 0x2BAA | 11131 | 11178 | CMM4 Input Channel 73-96 Current | float | R | 48
| 0x2BAB | 0x2BAB | 11179 | 11179 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x2BAC | 0x2BAD | 11180 | 11181 | MP1 Average Current | float | R | 2
| 0x2BAE | 0x2BAF | 11182 | 11183 | MP1 Neutral Current | float | R | 2
| 0x2BB0 | 0x2BB1 | 11184 | 11185 | MP1 Neutral Current Phase Angle | float | R | 2
Power(10/12 Cycle) | 0x2BB2 | 0x2BB3 | 11186 | 11187 | VMM1 Phase A Active Power | float | R | 2
| 0x2BB4 | 0x2BB5 | 11188 | 11189 | VMM1 Phase A Reactive Power | float | R | 2
| 0x2BB6 | 0x2BB7 | 11190 | 11191 | VMM1 Phase A Apparent Power | float | R | 2
| 0x2BB8 | 0x2BB9 | 11192 | 11193 | VMM1 Phase A Load Nature | uint32_t | R | 2
| 0x2BBA | 0x2BBB | 11194 | 11195 | VMM1 Phase A Power Factor | float | R | 2
| 0x2BBC | 0x2BBD | 11196 | 11197 | VMM1 Phase B Active Power | float | R | 2
| 0x2BBE | 0x2BBF | 11198 | 11199 | VMM1 Phase B Reactive Power | float | R | 2
| 0x2BC0 | 0x2BC1 | 11200 | 11201 | VMM1 Phase B Apparent Power | float | R | 2
| 0x2BC2 | 0x2BC3 | 11202 | 11203 | VMM1 Phase B Load Nature | uint32_t | R | 2
| 0x2BC4 | 0x2BC5 | 11204 | 11205 | VMM1 Phase B Power Factor | float | R | 2
| 0x2BC6 | 0x2BC7 | 11206 | 11207 | VMM1 Phase C Active Power | float | R | 2
| 0x2BC8 | 0x2BC9 | 11208 | 11209 | VMM1 Phase C Reactive Power | float | R | 2
| 0x2BCA | 0x2BCB | 11210 | 11211 | VMM1 Phase C Apparent Power | float | R | 2
| 0x2BCC | 0x2BCD | 11212 | 11213 | VMM1 Phase C Load Nature | uint32_t | R | 2
| 0x2BCE | 0x2BCF | 11214 | 11215 | VMM1 Phase C Power Factor | float | R | 2
| 0x2BD0 | 0x2BD1 | 11216 | 11217 | VMM1 System Active Power | float | R | 2
| 0x2BD2 | 0x2BD3 | 11218 | 11219 | VMM1 System Reactive Power | float | R | 2
| 0x2BD4 | 0x2BD5 | 11220 | 11221 | VMM1 System Apparent Power | float | R | 2
| 0x2BD6 | 0x2BD7 | 11222 | 11223 | VMM1 System Load Nature | uint32_t | R | 2
| 0x2BD8 | 0x2BD9 | 11224 | 11225 | VMM1 System Power Factor | float | R | 2
| 0x2BDA | 0x2BDA | 11226 | 11226 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x2BDB | 0x2BDC | 11227 | 11228 | VMM1 CMM1 Input Channel 1 Active Power | float | R | 2
| 0x2BDD | 0x2BDE | 11229 | 11230 | VMM1 CMM1 Input Channel 1 Reactive Powerr | float | R | 2
| 0x2BDF | 0x2BE0 | 11231 | 11232 | VMM1 CMM1 Input Channel 1 Apparent Power | float | R | 2
| 0x2BE1 | 0x2BE2 | 11233 | 11234 | VMM1 CMM1 Input Channel 1 Load Naturer | uint32_t | R | 2
| 0x2BE3 | 0x2BE4 | 11235 | 11236 | VMM1 CMM1 Input Channel 1 Power Factor | float | R | 2
| 0x2BE5 | 0x2C17 | 11237 | 11287 | VMM2 Power Parameter |  | R | 51
| 0x2C18 | 0x2C18 | 11288 | 11288 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x2C19 | 0x2C1A | 11289 | 11290 | MPl Active Power | float | R | 2
| 0x2C1B | 0x2C1C | 11291 | 11292 | MPl Reactive Powerr | float | R | 2
| 0x2C1D | 0x2C1E | 11293 | 11294 | MPl Apparent Power | float | R | 2
| 0x2C1F | 0x2C20 | 11295 | 11296 | MPl Load Naturer | uint32_t | R | 2
| 0x2C21 | 0x2C22 | 11297 | 11298 | MPl Power Factor | float | R | 2
Power Quality(10/12 Cycle) | 0x2C23 | 0x2C24 | 11299 | 11300 | VMM1 Voltage Positive Sequence Magnitude | float | R | 2
| 0x2C25 | 0x2C26 | 11301 | 11302 | VMM1 Voltage Zero Sequence Magnitude | float | R | 2
| 0x2C27 | 0x2C28 | 11303 | 11304 | VMM1 Voltage Negative Sequence Magnitude | float | R | 2
| 0x2C29 | 0x2C2A | 11305 | 11306 | VMM1 Voltage Positive Sequence Angle | float | R | 2
| 0x2C2B | 0x2C2C | 11307 | 11308 | VMM1 Voltage Zero Sequence Angle | float | R | 2
| 0x2C2D | 0x2C2E | 11309 | 11310 | VMM1 Voltage Negative Sequence Angle | float | R | 2
| 0x2C2F | 0x2C30 | 11311 | 11312 | VMM1 Voltage Unbalance Negative | float | R | 2
| 0x2C31 | 0x2C32 | 11313 | 11314 | VMM1 Voltage Unbalance Zero | float | R | 2
| 0x2C33 | 0x2C34 | 11315 | 11316 | VMM1 Phase A Voltage THD | float | R | 2
| 0x2C35 | 0x2C36 | 11317 | 11318 | VMM1 Phase A Voltage THD Odd | float | R | 2
| 0x2C37 | 0x2C38 | 11319 | 11320 | VMM1 Phase A Voltage THD Even | float | R | 2
| 0x2C39 | 0x2C3A | 11321 | 11322 | VMM1 Phase A Voltage Crest Factor | float | R | 2
| 0x2C3B | 0x2D38 | 11323 | 11576 | VMM1 Phase A 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x2D39 | 0x2E36 | 11577 | 11830 | VMM1 Phase A 1-127st Voltage Harmonics Group | float | R | 254
| 0x2E37 | 0x2F34 | 11831 | 12084 | VMM1 Phase A 1-127st Voltage Angle Harmonics | float | R | 254
| 0x2F35 | 0x2F36 | 12085 | 12086 | VMM1 Phase B Voltage THD | float | R | 2
| 0x2F37 | 0x2F38 | 12087 | 12088 | VMM1 Phase B Voltage THD Odd | float | R | 2
| 0x2F39 | 0x2F3A | 12089 | 12090 | VMM1 Phase B Voltage THD Even | float | R | 2
| 0x2F3B | 0x2F3C | 12091 | 12092 | VMM1 Phase B Voltage Crest Factor | float | R | 2
| 0x2F3D | 0x303A | 12093 | 12346 | VMM1 Phase B 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x303B | 0x3138 | 12347 | 12600 | VMM1 Phase B 1-127st Voltage Harmonics Group | float | R | 254
| 0x3139 | 0x3236 | 12601 | 12854 | VMM1 Phase B 1-127st Voltage Angle Harmonics | float | R | 254
| 0x3237 | 0x3238 | 12855 | 12856 | VMM1 Phase C Voltage THD | float | R | 2
| 0x3239 | 0x323A | 12857 | 12858 | VMM1 Phase C Voltage THD Odd | float | R | 2
| 0x323B | 0x323C | 12859 | 12860 | VMM1 Phase C Voltage THD Even | float | R | 2
| 0x323D | 0x323E | 12861 | 12862 | VMM1 Phase C Voltage Crest Factor | float | R | 2
| 0x323F | 0x333C | 12863 | 13116 | VMM1 Phase C 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x333D | 0x343A | 13117 | 13370 | VMM1 Phase C 1-127st Voltage Harmonics Group | float | R | 254
| 0x343B | 0x3538 | 13371 | 13624 | VMM1 Phase C 1-127st Voltage Angle Harmonics | float | R | 254
| 0x3539 | 0x353A | 13625 | 13626 | VMM1 Average Voltage THD | float | R | 2
| 0x353B | 0x353C | 13627 | 13628 | VMM1 Average Voltage THD Odd | float | R | 2
| 0x353D | 0x353E | 13629 | 13630 | VMM1 Average Voltage THD Even | float | R | 2
| 0x353F | 0x3E5A | 13631 | 15962 | VMM2 Voltage Power Quality | float | R | 2332
| 0x3E5B | 0x3E5B | 15963 | 15963 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x3E5C | 0x3E5D | 15964 | 15965 | CMM1 Input Channel 1 Current TDD | float | R | 2
| 0x3E5E | 0x3E5F | 15966 | 15967 | CMM1 Input Channel 1 Current THD | float | R | 2
| 0x3E60 | 0x3E61 | 15968 | 15969 | CMM1 Input Channel 1 Current THD Odd | float | R | 2
| 0x3E62 | 0x3E63 | 15970 | 15971 | CMM1 Input Channel 1 Current THD Even | float | R | 2
| 0x3E64 | 0x3E65 | 15972 | 15973 | CMM1 Input Channel 1 Current Crest Factor | float | R | 2
| 0x3E66 | 0x3E67 | 15974 | 15975 | CMM1 Input Channel 1 Current K Factor | float | R | 2
| 0x3E68 | 0x3EE5 | 15976 | 16101 | CMM1 Input Channel 1 1-63st Current Magnitude Harmonics | float | R | 126
| 0x3EE6 | 0x3F63 | 16102 | 16227 | CMM1 Input Channel 1 1-63st Current Harmonics Group | float | R | 126
| 0x3F64 | 0x3FE1 | 16228 | 16353 | CMM1 Input Channel 1 1-63st Current Angle Harmonics | float | R | 126
| 0x3FE2 | 0x3FE2 | 16354 | 16354 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x3FE3 | 0x3FE4 | 16355 | 16356 | MP1 Current Positive Sequence Magnitude | float | R | 2
| 0x3FE5 | 0x3FE6 | 16357 | 16358 | MP1 Current Zero Sequence Magnitude | float | R | 2
| 0x3FE7 | 0x3FE8 | 16359 | 16360 | MP1 Current Negative Sequence Magnitude | float | R | 2
| 0x3FE9 | 0x3FEA | 16361 | 16362 | MP1 Current Positive Sequence Angle | float | R | 2
| 0x3FEB | 0x3FEC | 16363 | 16364 | MP1 Current Zero Sequence Angle | float | R | 2
| 0x3FED | 0x3FEE | 16365 | 16366 | MP1 Current Negative Sequence Angle | float | R | 2
| 0x3FEF | 0x3FF0 | 16367 | 16368 | MP1 Current Unbalance Negative | float | R | 2
| 0x3FF1 | 0x3FF2 | 16369 | 16370 | MP1 Current Unbalance Zero | float | R | 2

## 150¦180 Cycle
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
RMS(150¦180 Cycle) | 0x4000 | 0x4003 | 16384 | 16387 | 150/180 Cycle RMS Param Update Timestamp | uint64_t | R | 4
| 0x4004 | 0x4004 | 16388 | 16388 | 150/180 Cycle RMS Param Valid Flag(50160) | uint16_t | R | 1
| 0x4005 | 0x4005 | 16389 | 16389 | 150/180 Cycle RMS Param Event Flag | uint16_t | R | 1
| 0x4006 | 0x4006 | 16390 | 16390 | 150/180 Cycle RMS Param Block Number | uint16_t | R | 1
| 0x4007 | 0x4008 | 16391 | 16392 | VMM1 System Frequency | float | R | 2
| 0x4009 | 0x400A | 16393 | 16394 | VMM1 Phase A Line-to-Neutral Voltage | float | R | 2
| 0x400B | 0x400C | 16395 | 16396 | VMM1 Phase B Line-to-Neutral Voltage | float | R | 2
| 0x400D | 0x400E | 16397 | 16398 | VMM1 Phase C Line-to-Neutral Voltage | float | R | 2
| 0x400F | 0x4010 | 16399 | 16400 | VMM1 Phase A Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x4011 | 0x4012 | 16401 | 16402 | VMM1 Phase B Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x4013 | 0x4014 | 16403 | 16404 | VMM1 Phase C Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x4015 | 0x4016 | 16405 | 16406 | VMM1 Average Line-to-Neutral Voltage | float | R | 2
| 0x4017 | 0x4018 | 16407 | 16408 | VMM1 Phase AB Line-to-Line Voltage | float | R | 2
| 0x4019 | 0x401A | 16409 | 16410 | VMM1 Phase BC Line-to-Line Voltage | float | R | 2
| 0x401B | 0x401C | 16411 | 16412 | VMM1 Phase CA Line-to-Line Voltage | float | R | 2
| 0x401D | 0x401E | 16413 | 16414 | VMM1 Phase AB Line-to-Line Voltage Phase Angle | float | R | 2
| 0x401F | 0x4020 | 16415 | 16416 | VMM1 Phase BC Line-to-Line Voltage Phase Angle | float | R | 2
| 0x4021 | 0x4022 | 16417 | 16418 | VMM1 Phase CA Line-to-Line Voltage Phase Angle | float | R | 2
| 0x4023 | 0x4024 | 16419 | 16420 | VMM1 Average Line-to-Line Voltage | float | R | 2
| 0x4025 | 0x4026 | 16421 | 16422 | VMM1 Voltage Phase Order | float | R | 2
| 0x4027 | 0x4028 | 16423 | 16424 | VMM1 Phase A Current | float | R | 2
| 0x4029 | 0x402A | 16425 | 16426 | VMM1 Phase B Current | float | R | 2
| 0x402B | 0x402C | 16427 | 16428 | VMM1 Phase C Current | float | R | 2
| 0x402D | 0x402E | 16429 | 16430 | VMM1 Neutral Current | float | R | 2
| 0x402F | 0x4030 | 16431 | 16432 | VMM1 System Average Current | float | R | 2
| 0x4031 | 0x4032 | 16433 | 16434 | VMM1 Phase A Current Phase Angle | float | R | 2
| 0x4033 | 0x4034 | 16435 | 16436 | VMM1 Phase B Current Phase Angle | float | R | 2
| 0x4035 | 0x4036 | 16437 | 16438 | VMM1 Phase C Current Phase Angle | float | R | 2
| 0x4037 | 0x4038 | 16439 | 16440 | VMM1 Neutral Current Phase Angle | float | R | 2
| 0x4039 | 0x4068 | 16441 | 16488 | VMM1 CMM1 Input Channel 1-24 Current Angle | float | R | 48
| 0x4069 | 0x4098 | 16489 | 16536 | VMM1 CMM2 Input Channel 1-24 Current Angle | float | R | 48
| 0x4099 | 0x40C8 | 16537 | 16584 | VMM1 CMM3 Input Channel 1-24 Current Angle | float | R | 48
| 0x40C9 | 0x40F8 | 16585 | 16632 | VMM1 CMM4 Input Channel 1-24 Current Angle | float | R | 48
| 0x40F9 | 0x41EA | 16633 | 16874 | VMM2 Realtime Parameter | float | R | 242
| 0x41EB | 0x421A | 16875 | 16922 | CMM1 Input Channel 1-24 Current | float | R | 48
| 0x421B | 0x424A | 16923 | 16970 | CMM2 Input Channel 25-48 Current | float | R | 48
| 0x424B | 0x427A | 16971 | 17018 | CMM3 Input Channel 49-72 Current | float | R | 48
| 0x427B | 0x42AA | 17019 | 17066 | CMM4 Input Channel 73-96 Current | float | R | 48
| 0x42AB | 0x42AB | 17067 | 17067 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x42AC | 0x42AD | 17068 | 17069 | MP1 Average Current | float | R | 2
| 0x42AE | 0x42AF | 17070 | 17071 | MP1 Neutral Current | float | R | 2
| 0x42B0 | 0x42B1 | 17072 | 17073 | MP1 Neutral Current Phase Angle | float | R | 2
Power(150¦180 Cycle) | 0x42B2 | 0x42B3 | 17074 | 17075 | VMM1 Phase A Active Power | float | R | 2
| 0x42B4 | 0x42B5 | 17076 | 17077 | VMM1 Phase A Reactive Power | float | R | 2
| 0x42B6 | 0x42B7 | 17078 | 17079 | VMM1 Phase A Apparent Power | float | R | 2
| 0x42B8 | 0x42B9 | 17080 | 17081 | VMM1 Phase A Load Nature | uint32_t | R | 2
| 0x42BA | 0x42BB | 17082 | 17083 | VMM1 Phase A Power Factor | float | R | 2
| 0x42BC | 0x42BD | 17084 | 17085 | VMM1 Phase B Active Power | float | R | 2
| 0x42BE | 0x42BF | 17086 | 17087 | VMM1 Phase B Reactive Power | float | R | 2
| 0x42C0 | 0x42C1 | 17088 | 17089 | VMM1 Phase B Apparent Power | float | R | 2
| 0x42C2 | 0x42C3 | 17090 | 17091 | VMM1 Phase B Load Nature | uint32_t | R | 2
| 0x42C4 | 0x42C5 | 17092 | 17093 | VMM1 Phase B Power Factor | float | R | 2
| 0x42C6 | 0x42C7 | 17094 | 17095 | VMM1 Phase C Active Power | float | R | 2
| 0x42C8 | 0x42C9 | 17096 | 17097 | VMM1 Phase C Reactive Power | float | R | 2
| 0x42CA | 0x42CB | 17098 | 17099 | VMM1 Phase C Apparent Power | float | R | 2
| 0x42CC | 0x42CD | 17100 | 17101 | VMM1 Phase C Load Nature | uint32_t | R | 2
| 0x42CE | 0x42CF | 17102 | 17103 | VMM1 Phase C Power Factor | float | R | 2
| 0x42D0 | 0x42D1 | 17104 | 17105 | VMM1 System Active Power | float | R | 2
| 0x42D2 | 0x42D3 | 17106 | 17107 | VMM1 System Reactive Power | float | R | 2
| 0x42D4 | 0x42D5 | 17108 | 17109 | VMM1 System Apparent Power | float | R | 2
| 0x42D6 | 0x42D7 | 17110 | 17111 | VMM1 System Load Nature | uint32_t | R | 2
| 0x42D8 | 0x42D9 | 17112 | 17113 | VMM1 System Power Factor | float | R | 2
| 0x42DA | 0x42DA | 17114 | 17114 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x42DB | 0x42DC | 17115 | 17116 | VMM1 CMM1 Input Channel 1 Active Power | float | R | 2
| 0x42DD | 0x42DE | 17117 | 17118 | VMM1 CMM1 Input Channel 1 Reactive Powerr | float | R | 2
| 0x42DF | 0x42E0 | 17119 | 17120 | VMM1 CMM1 Input Channel 1 Apparent Power | float | R | 2
| 0x42E1 | 0x42E2 | 17121 | 17122 | VMM1 CMM1 Input Channel 1 Load Naturer | uint32_t | R | 2
| 0x42E3 | 0x42E4 | 17123 | 17124 | VMM1 CMM1 Input Channel 1 Power Factor | float | R | 2
| 0x42E5 | 0x4317 | 17125 | 17175 | VMM2 Power Parameter |  | R | 51
| 0x4318 | 0x4318 | 17176 | 17176 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x4319 | 0x431A | 17177 | 17178 | MPl Active Power | float | R | 2
| 0x431B | 0x431C | 17179 | 17180 | MPl Reactive Powerr | float | R | 2
| 0x431D | 0x431E | 17181 | 17182 | MPl Apparent Power | float | R | 2
| 0x431F | 0x4320 | 17183 | 17184 | MPl Load Naturer | uint32_t | R | 2
| 0x4321 | 0x4322 | 17185 | 17186 | MPl Power Factor | float | R | 2
Power Quality(150¦180 Cycle) | 0x4323 | 0x4324 | 17187 | 17188 | VMM1 Voltage Positive Sequence Magnitude | float | R | 2
| 0x4325 | 0x4326 | 17189 | 17190 | VMM1 Voltage Zero Sequence Magnitude | float | R | 2
| 0x4327 | 0x4328 | 17191 | 17192 | VMM1 Voltage Negative Sequence Magnitude | float | R | 2
| 0x4329 | 0x432A | 17193 | 17194 | VMM1 Voltage Positive Sequence Angle | float | R | 2
| 0x432B | 0x432C | 17195 | 17196 | VMM1 Voltage Zero Sequence Angle | float | R | 2
| 0x432D | 0x432E | 17197 | 17198 | VMM1 Voltage Negative Sequence Angle | float | R | 2
| 0x432F | 0x4330 | 17199 | 17200 | VMM1 Voltage Unbalance Negative | float | R | 2
| 0x4331 | 0x4332 | 17201 | 17202 | VMM1 Voltage Unbalance Zero | float | R | 2
| 0x4333 | 0x4334 | 17203 | 17204 | VMM1 Phase A Voltage THD | float | R | 2
| 0x4335 | 0x4336 | 17205 | 17206 | VMM1 Phase A Voltage THD Odd | float | R | 2
| 0x4337 | 0x4338 | 17207 | 17208 | VMM1 Phase A Voltage THD Even | float | R | 2
| 0x4339 | 0x433A | 17209 | 17210 | VMM1 Phase A Voltage Crest Factor | float | R | 2
| 0x433B | 0x4438 | 17211 | 17464 | VMM1 Phase A 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x4439 | 0x4536 | 17465 | 17718 | VMM1 Phase A 1-127st Voltage Harmonics Group | float | R | 254
| 0x4537 | 0x4634 | 17719 | 17972 | VMM1 Phase A 1-127st Voltage Angle Harmonics | float | R | 254
| 0x4635 | 0x4636 | 17973 | 17974 | VMM1 Phase B Voltage THD | float | R | 2
| 0x4637 | 0x4638 | 17975 | 17976 | VMM1 Phase B Voltage THD Odd | float | R | 2
| 0x4639 | 0x463A | 17977 | 17978 | VMM1 Phase B Voltage THD Even | float | R | 2
| 0x463B | 0x463C | 17979 | 17980 | VMM1 Phase B Voltage Crest Factor | float | R | 2
| 0x463D | 0x473A | 17981 | 18234 | VMM1 Phase B 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x473B | 0x4838 | 18235 | 18488 | VMM1 Phase B 1-127st Voltage Harmonics Group | float | R | 254
| 0x4839 | 0x4936 | 18489 | 18742 | VMM1 Phase B 1-127st Voltage Angle Harmonics | float | R | 254
| 0x4937 | 0x4938 | 18743 | 18744 | VMM1 Phase C Voltage THD | float | R | 2
| 0x4939 | 0x493A | 18745 | 18746 | VMM1 Phase C Voltage THD Odd | float | R | 2
| 0x493B | 0x493C | 18747 | 18748 | VMM1 Phase C Voltage THD Even | float | R | 2
| 0x493D | 0x493E | 18749 | 18750 | VMM1 Phase C Voltage Crest Factor | float | R | 2
| 0x493F | 0x4A3C | 18751 | 19004 | VMM1 Phase C 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x4A3D | 0x4B3A | 19005 | 19258 | VMM1 Phase C 1-127st Voltage Harmonics Group | float | R | 254
| 0x4B3B | 0x4C38 | 19259 | 19512 | VMM1 Phase C 1-127st Voltage Angle Harmonics | float | R | 254
| 0x4C39 | 0x4C3A | 19513 | 19514 | VMM1 Average Voltage THD | float | R | 2
| 0x4C3B | 0x4C3C | 19515 | 19516 | VMM1 Average Voltage THD Odd | float | R | 2
| 0x4C3D | 0x4C3E | 19517 | 19518 | VMM1 Average Voltage THD Even | float | R | 2
| 0x4C3F | 0x555A | 19519 | 21850 | VMM2 Voltage Power Quality | float | R | 2332
| 0x555B | 0x555B | 21851 | 21851 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x555C | 0x555D | 21852 | 21853 | CMM1 Input Channel 1 Current TDD | float | R | 2
| 0x555E | 0x555F | 21854 | 21855 | CMM1 Input Channel 1 Current THD | float | R | 2
| 0x5560 | 0x5561 | 21856 | 21857 | CMM1 Input Channel 1 Current THD Odd | float | R | 2
| 0x5562 | 0x5563 | 21858 | 21859 | CMM1 Input Channel 1 Current THD Even | float | R | 2
| 0x5564 | 0x5565 | 21860 | 21861 | CMM1 Input Channel 1 Current Crest Factor | float | R | 2
| 0x5566 | 0x5567 | 21862 | 21863 | CMM1 Input Channel 1 Current K Factor | float | R | 2
| 0x5568 | 0x55E5 | 21864 | 21989 | CMM1 Input Channel 1 1-63st Current Magnitude Harmonics | float | R | 126
| 0x55E6 | 0x5663 | 21990 | 22115 | CMM1 Input Channel 1 1-63st Current Harmonics Group | float | R | 126
| 0x5664 | 0x56E1 | 22116 | 22241 | CMM1 Input Channel 1 1-63st Current Angle Harmonics | float | R | 126
| 0x56E2 | 0x56E2 | 22242 | 22242 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x56E3 | 0x56E4 | 22243 | 22244 | MP1 Current Positive Sequence Magnitude | float | R | 2
| 0x56E5 | 0x56E6 | 22245 | 22246 | MP1 Current Zero Sequence Magnitude | float | R | 2
| 0x56E7 | 0x56E8 | 22247 | 22248 | MP1 Current Negative Sequence Magnitude | float | R | 2
| 0x56E9 | 0x56EA | 22249 | 22250 | MP1 Current Positive Sequence Angle | float | R | 2
| 0x56EB | 0x56EC | 22251 | 22252 | MP1 Current Zero Sequence Angle | float | R | 2
| 0x56ED | 0x56EE | 22253 | 22254 | MP1 Current Negative Sequence Angle | float | R | 2
| 0x56EF | 0x56F0 | 22255 | 22256 | MP1 Current Unbalance Negative | float | R | 2
| 0x56F1 | 0x56F2 | 22257 | 22258 | MP1 Current Unbalance Zero | float | R | 2
Flicker | 0x56F3 | 0x56F4 | 22259 | 22260 | VMM1 Phase A Flicker Pinst Max | float | R | 2
| 0x56F5 | 0x56F6 | 22261 | 22262 | VMM1 Phase B Flicker Pinst Max | float | R | 2
| 0x56F7 | 0x56F8 | 22263 | 22264 | VMM1 Phase C Flicker Pinst Max | float | R | 2
| 0x56F9 | 0x56FA | 22265 | 22266 | VMM2 Phase A Flicker Pinst Max | float | R | 2
| 0x56FB | 0x56FC | 22267 | 22268 | VMM2 Phase B Flicker Pinst Max | float | R | 2
| 0x56FD | 0x56FE | 22269 | 22270 | VMM2 Phase C Flicker Pinst Max | float | R | 2

## 10 Min
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
RMS(10 Min) | 0x5710 | 0x5713 | 22288 | 22291 | 10 Min RMS Param Update Timestamp | uint64_t | R | 4
| 0x5714 | 0x5714 | 22292 | 22292 | 10 Min RMS Param Valid Flag(50160) | uint16_t | R | 1
| 0x5715 | 0x5715 | 22293 | 22293 | 10 Min RMS Param Event Flag | uint16_t | R | 1
| 0x5716 | 0x5716 | 22294 | 22294 | 10 Min RMS Param Block Number | uint16_t | R | 1
| 0x5717 | 0x5718 | 22295 | 22296 | VMM1 System Frequency | float | R | 2
| 0x5719 | 0x571A | 22297 | 22298 | VMM1 Phase A Line-to-Neutral Voltage | float | R | 2
| 0x571B | 0x571C | 22299 | 22300 | VMM1 Phase B Line-to-Neutral Voltage | float | R | 2
| 0x571D | 0x571E | 22301 | 22302 | VMM1 Phase C Line-to-Neutral Voltage | float | R | 2
| 0x571F | 0x5720 | 22303 | 22304 | VMM1 Phase A Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x5721 | 0x5722 | 22305 | 22306 | VMM1 Phase B Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x5723 | 0x5724 | 22307 | 22308 | VMM1 Phase C Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x5725 | 0x5726 | 22309 | 22310 | VMM1 Average Line-to-Neutral Voltage | float | R | 2
| 0x5727 | 0x5728 | 22311 | 22312 | VMM1 Phase AB Line-to-Line Voltage | float | R | 2
| 0x5729 | 0x572A | 22313 | 22314 | VMM1 Phase BC Line-to-Line Voltage | float | R | 2
| 0x572B | 0x572C | 22315 | 22316 | VMM1 Phase CA Line-to-Line Voltage | float | R | 2
| 0x572D | 0x572E | 22317 | 22318 | VMM1 Phase AB Line-to-Line Voltage Phase Angle | float | R | 2
| 0x572F | 0x5730 | 22319 | 22320 | VMM1 Phase BC Line-to-Line Voltage Phase Angle | float | R | 2
| 0x5731 | 0x5732 | 22321 | 22322 | VMM1 Phase CA Line-to-Line Voltage Phase Angle | float | R | 2
| 0x5733 | 0x5734 | 22323 | 22324 | VMM1 Average Line-to-Line Voltage | float | R | 2
| 0x5735 | 0x5736 | 22325 | 22326 | VMM1 Voltage Phase Order | float | R | 2
| 0x5737 | 0x5738 | 22327 | 22328 | VMM1 Phase A Current | float | R | 2
| 0x5739 | 0x573A | 22329 | 22330 | VMM1 Phase B Current | float | R | 2
| 0x573B | 0x573C | 22331 | 22332 | VMM1 Phase C Current | float | R | 2
| 0x573D | 0x573E | 22333 | 22334 | VMM1 Neutral Current | float | R | 2
| 0x573F | 0x5740 | 22335 | 22336 | VMM1 System Average Current | float | R | 2
| 0x5741 | 0x5742 | 22337 | 22338 | VMM1 Phase A Current Phase Angle | float | R | 2
| 0x5743 | 0x5744 | 22339 | 22340 | VMM1 Phase B Current Phase Angle | float | R | 2
| 0x5745 | 0x5746 | 22341 | 22342 | VMM1 Phase C Current Phase Angle | float | R | 2
| 0x5747 | 0x5748 | 22343 | 22344 | VMM1 Neutral Current Phase Angle | float | R | 2
| 0x5749 | 0x5778 | 22345 | 22392 | VMM1 CMM1 Input Channel 1-24 Current Angle | float | R | 48
| 0x5779 | 0x57A8 | 22393 | 22440 | VMM1 CMM2 Input Channel 1-24 Current Angle | float | R | 48
| 0x57A9 | 0x57D8 | 22441 | 22488 | VMM1 CMM3 Input Channel 1-24 Current Angle | float | R | 48
| 0x57D9 | 0x5808 | 22489 | 22536 | VMM1 CMM4 Input Channel 1-24 Current Angle | float | R | 48
| 0x5809 | 0x58FA | 22537 | 22778 | VMM2 Realtime Parameter | float | R | 242
| 0x58FB | 0x592A | 22779 | 22826 | CMM1 Input Channel 1-24 Current | float | R | 48
| 0x592B | 0x595A | 22827 | 22874 | CMM2 Input Channel 25-48 Current | float | R | 48
| 0x595B | 0x598A | 22875 | 22922 | CMM3 Input Channel 49-72 Current | float | R | 48
| 0x598B | 0x59BA | 22923 | 22970 | CMM4 Input Channel 73-96 Current | float | R | 48
| 0x59BB | 0x59BB | 22971 | 22971 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x59BC | 0x59BD | 22972 | 22973 | MP1 Average Current | float | R | 2
| 0x59BE | 0x59BF | 22974 | 22975 | MP1 Neutral Current | float | R | 2
| 0x59C0 | 0x59C1 | 22976 | 22977 | MP1 Neutral Current Phase Angle | float | R | 2
Power(10 Min) | 0x59C2 | 0x59C3 | 22978 | 22979 | VMM1 Phase A Active Power | float | R | 2
| 0x59C4 | 0x59C5 | 22980 | 22981 | VMM1 Phase A Reactive Power | float | R | 2
| 0x59C6 | 0x59C7 | 22982 | 22983 | VMM1 Phase A Apparent Power | float | R | 2
| 0x59C8 | 0x59C9 | 22984 | 22985 | VMM1 Phase A Load Nature | uint32_t | R | 2
| 0x59CA | 0x59CB | 22986 | 22987 | VMM1 Phase A Power Factor | float | R | 2
| 0x59CC | 0x59CD | 22988 | 22989 | VMM1 Phase B Active Power | float | R | 2
| 0x59CE | 0x59CF | 22990 | 22991 | VMM1 Phase B Reactive Power | float | R | 2
| 0x59D0 | 0x59D1 | 22992 | 22993 | VMM1 Phase B Apparent Power | float | R | 2
| 0x59D2 | 0x59D3 | 22994 | 22995 | VMM1 Phase B Load Nature | uint32_t | R | 2
| 0x59D4 | 0x59D5 | 22996 | 22997 | VMM1 Phase B Power Factor | float | R | 2
| 0x59D6 | 0x59D7 | 22998 | 22999 | VMM1 Phase C Active Power | float | R | 2
| 0x59D8 | 0x59D9 | 23000 | 23001 | VMM1 Phase C Reactive Power | float | R | 2
| 0x59DA | 0x59DB | 23002 | 23003 | VMM1 Phase C Apparent Power | float | R | 2
| 0x59DC | 0x59DD | 23004 | 23005 | VMM1 Phase C Load Nature | uint32_t | R | 2
| 0x59DE | 0x59DF | 23006 | 23007 | VMM1 Phase C Power Factor | float | R | 2
| 0x59E0 | 0x59E1 | 23008 | 23009 | VMM1 System Active Power | float | R | 2
| 0x59E2 | 0x59E3 | 23010 | 23011 | VMM1 System Reactive Power | float | R | 2
| 0x59E4 | 0x59E5 | 23012 | 23013 | VMM1 System Apparent Power | float | R | 2
| 0x59E6 | 0x59E7 | 23014 | 23015 | VMM1 System Load Nature | uint32_t | R | 2
| 0x59E8 | 0x59E9 | 23016 | 23017 | VMM1 System Power Factor | float | R | 2
| 0x59EA | 0x59EA | 23018 | 23018 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x59EB | 0x59EC | 23019 | 23020 | VMM1 CMM1 Input Channel 1 Active Power | float | R | 2
| 0x59ED | 0x59EE | 23021 | 23022 | VMM1 CMM1 Input Channel 1 Reactive Powerr | float | R | 2
| 0x59EF | 0x59F0 | 23023 | 23024 | VMM1 CMM1 Input Channel 1 Apparent Power | float | R | 2
| 0x59F1 | 0x59F2 | 23025 | 23026 | VMM1 CMM1 Input Channel 1 Load Naturer | uint32_t | R | 2
| 0x59F3 | 0x59F4 | 23027 | 23028 | VMM1 CMM1 Input Channel 1 Power Factor | float | R | 2
| 0x59F5 | 0x5A27 | 23029 | 23079 | VMM2 Power Parameter |  | R | 51
| 0x5A28 | 0x5A28 | 23080 | 23080 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x5A29 | 0x5A2A | 23081 | 23082 | MPl Active Power | float | R | 2
| 0x5A2B | 0x5A2C | 23083 | 23084 | MPl Reactive Powerr | float | R | 2
| 0x5A2D | 0x5A2E | 23085 | 23086 | MPl Apparent Power | float | R | 2
| 0x5A2F | 0x5A30 | 23087 | 23088 | MPl Load Naturer | uint32_t | R | 2
| 0x5A31 | 0x5A32 | 23089 | 23090 | MPl Power Factor | float | R | 2
Power Quality(10 Min) | 0x5A33 | 0x5A34 | 23091 | 23092 | VMM1 Voltage Positive Sequence Magnitude | float | R | 2
| 0x5A35 | 0x5A36 | 23093 | 23094 | VMM1 Voltage Zero Sequence Magnitude | float | R | 2
| 0x5A37 | 0x5A38 | 23095 | 23096 | VMM1 Voltage Negative Sequence Magnitude | float | R | 2
| 0x5A39 | 0x5A3A | 23097 | 23098 | VMM1 Voltage Positive Sequence Angle | float | R | 2
| 0x5A3B | 0x5A3C | 23099 | 23100 | VMM1 Voltage Zero Sequence Angle | float | R | 2
| 0x5A3D | 0x5A3E | 23101 | 23102 | VMM1 Voltage Negative Sequence Angle | float | R | 2
| 0x5A3F | 0x5A40 | 23103 | 23104 | VMM1 Voltage Unbalance Negative | float | R | 2
| 0x5A41 | 0x5A42 | 23105 | 23106 | VMM1 Voltage Unbalance Zero | float | R | 2
| 0x5A43 | 0x5A44 | 23107 | 23108 | VMM1 Phase A Voltage THD | float | R | 2
| 0x5A45 | 0x5A46 | 23109 | 23110 | VMM1 Phase A Voltage THD Odd | float | R | 2
| 0x5A47 | 0x5A48 | 23111 | 23112 | VMM1 Phase A Voltage THD Even | float | R | 2
| 0x5A49 | 0x5A4A | 23113 | 23114 | VMM1 Phase A Voltage Crest Factor | float | R | 2
| 0x5A4B | 0x5B48 | 23115 | 23368 | VMM1 Phase A 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x5B49 | 0x5C46 | 23369 | 23622 | VMM1 Phase A 1-127st Voltage Harmonics Group | float | R | 254
| 0x5C47 | 0x5D44 | 23623 | 23876 | VMM1 Phase A 1-127st Voltage Angle Harmonics | float | R | 254
| 0x5D45 | 0x5D46 | 23877 | 23878 | VMM1 Phase B Voltage THD | float | R | 2
| 0x5D47 | 0x5D48 | 23879 | 23880 | VMM1 Phase B Voltage THD Odd | float | R | 2
| 0x5D49 | 0x5D4A | 23881 | 23882 | VMM1 Phase B Voltage THD Even | float | R | 2
| 0x5D4B | 0x5D4C | 23883 | 23884 | VMM1 Phase B Voltage Crest Factor | float | R | 2
| 0x5D4D | 0x5E4A | 23885 | 24138 | VMM1 Phase B 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x5E4B | 0x5F48 | 24139 | 24392 | VMM1 Phase B 1-127st Voltage Harmonics Group | float | R | 254
| 0x5F49 | 0x6046 | 24393 | 24646 | VMM1 Phase B 1-127st Voltage Angle Harmonics | float | R | 254
| 0x6047 | 0x6048 | 24647 | 24648 | VMM1 Phase C Voltage THD | float | R | 2
| 0x6049 | 0x604A | 24649 | 24650 | VMM1 Phase C Voltage THD Odd | float | R | 2
| 0x604B | 0x604C | 24651 | 24652 | VMM1 Phase C Voltage THD Even | float | R | 2
| 0x604D | 0x604E | 24653 | 24654 | VMM1 Phase C Voltage Crest Factor | float | R | 2
| 0x604F | 0x614C | 24655 | 24908 | VMM1 Phase C 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x614D | 0x624A | 24909 | 25162 | VMM1 Phase C 1-127st Voltage Harmonics Group | float | R | 254
| 0x624B | 0x6348 | 25163 | 25416 | VMM1 Phase C 1-127st Voltage Angle Harmonics | float | R | 254
| 0x6349 | 0x634A | 25417 | 25418 | VMM1 Average Voltage THD | float | R | 2
| 0x634B | 0x634C | 25419 | 25420 | VMM1 Average Voltage THD Odd | float | R | 2
| 0x634D | 0x634E | 25421 | 25422 | VMM1 Average Voltage THD Even | float | R | 2
| 0x634F | 0x6C6A | 25423 | 27754 | VMM2 Voltage Power Quality | float | R | 2332
| 0x6C6B | 0x6C6B | 27755 | 27755 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x6C6C | 0x6C6D | 27756 | 27757 | CMM1 Input Channel 1 Current TDD | float | R | 2
| 0x6C6E | 0x6C6F | 27758 | 27759 | CMM1 Input Channel 1 Current THD | float | R | 2
| 0x6C70 | 0x6C71 | 27760 | 27761 | CMM1 Input Channel 1 Current THD Odd | float | R | 2
| 0x6C72 | 0x6C73 | 27762 | 27763 | CMM1 Input Channel 1 Current THD Even | float | R | 2
| 0x6C74 | 0x6C75 | 27764 | 27765 | CMM1 Input Channel 1 Current Crest Factor | float | R | 2
| 0x6C76 | 0x6C77 | 27766 | 27767 | CMM1 Input Channel 1 Current K Factor | float | R | 2
| 0x6C78 | 0x6CF5 | 27768 | 27893 | CMM1 Input Channel 1 1-63st Current Magnitude Harmonics | float | R | 126
| 0x6CF6 | 0x6D73 | 27894 | 28019 | CMM1 Input Channel 1 1-63st Current Harmonics Group | float | R | 126
| 0x6D74 | 0x6DF1 | 28020 | 28145 | CMM1 Input Channel 1 1-63st Current Angle Harmonics | float | R | 126
| 0x6DF2 | 0x6DF2 | 28146 | 28146 | MP Number Select | uint16_t | R/W | 1 | 1~192
| 0x6DF3 | 0x6DF4 | 28147 | 28148 | MP1 Current Positive Sequence Magnitude | float | R | 2
| 0x6DF5 | 0x6DF6 | 28149 | 28150 | MP1 Current Zero Sequence Magnitude | float | R | 2
| 0x6DF7 | 0x6DF8 | 28151 | 28152 | MP1 Current Negative Sequence Magnitude | float | R | 2
| 0x6DF9 | 0x6DFA | 28153 | 28154 | MP1 Current Positive Sequence Angle | float | R | 2
| 0x6DFB | 0x6DFC | 28155 | 28156 | MP1 Current Zero Sequence Angle | float | R | 2
| 0x6DFD | 0x6DFE | 28157 | 28158 | MP1 Current Negative Sequence Angle | float | R | 2
| 0x6DFF | 0x6E00 | 28159 | 28160 | MP1 Current Unbalance Negative | float | R | 2
| 0x6E01 | 0x6E02 | 28161 | 28162 | MP1 Current Unbalance Zero | float | R | 2
Flicker(10 Min) | 0x6E03 | 0x6E04 | 28163 | 28164 | VMM1 Phase A Flicker Pinst Max | float | R | 2
| 0x6E05 | 0x6E06 | 28165 | 28166 | VMM1 Phase B Flicker Pinst Max | float | R | 2
| 0x6E07 | 0x6E08 | 28167 | 28168 | VMM1 Phase C Flicker Pinst Max | float | R | 2
| 0x6E09 | 0x6E0A | 28169 | 28170 | VMM2 Phase A Flicker Pinst Max | float | R | 2
| 0x6E0B | 0x6E0C | 28171 | 28172 | VMM2 Phase B Flicker Pinst Max | float | R | 2
| 0x6E0D | 0x6E0E | 28173 | 28174 | VMM2 Phase C Flicker Pinst Max | float | R | 2

## 2 Hr
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
RMS(2Hr) | 0x6E20 | 0x6E23 | 28192 | 28195 | 2 Hr RMS Param Update Timestamp | uint64_t | R | 4
| 0x6E24 | 0x6E24 | 28196 | 28196 | 2 Hr RMS Param Valid Flag(50160) | uint16_t | R | 1
| 0x6E25 | 0x6E25 | 28197 | 28197 | 2 Hr RMS Param Event Flag | uint16_t | R | 1
| 0x6E26 | 0x6E26 | 28198 | 28198 | 2 Hr RMS Param Block Number | uint16_t | R | 1
| 0x6E27 | 0x6E28 | 28199 | 28200 | VMM1 System Frequency | float | R | 2
| 0x6E29 | 0x6E2A | 28201 | 28202 | VMM1 Phase A Line-to-Neutral Voltage | float | R | 2
| 0x6E2B | 0x6E2C | 28203 | 28204 | VMM1 Phase B Line-to-Neutral Voltage | float | R | 2
| 0x6E2D | 0x6E2E | 28205 | 28206 | VMM1 Phase C Line-to-Neutral Voltage | float | R | 2
| 0x6E2F | 0x6E30 | 28207 | 28208 | VMM1 Phase A Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x6E31 | 0x6E32 | 28209 | 28210 | VMM1 Phase B Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x6E33 | 0x6E34 | 28211 | 28212 | VMM1 Phase C Line-to-Neutral Voltage Phase Angle | float | R | 2
| 0x6E35 | 0x6E36 | 28213 | 28214 | VMM1 Average Line-to-Neutral Voltage | float | R | 2
| 0x6E37 | 0x6E38 | 28215 | 28216 | VMM1 Phase AB Line-to-Line Voltage | float | R | 2
| 0x6E39 | 0x6E3A | 28217 | 28218 | VMM1 Phase BC Line-to-Line Voltage | float | R | 2
| 0x6E3B | 0x6E3C | 28219 | 28220 | VMM1 Phase CA Line-to-Line Voltage | float | R | 2
| 0x6E3D | 0x6E3E | 28221 | 28222 | VMM1 Phase AB Line-to-Line Voltage Phase Angle | float | R | 2
| 0x6E3F | 0x6E40 | 28223 | 28224 | VMM1 Phase BC Line-to-Line Voltage Phase Angle | float | R | 2
| 0x6E41 | 0x6E42 | 28225 | 28226 | VMM1 Phase CA Line-to-Line Voltage Phase Angle | float | R | 2
| 0x6E43 | 0x6E44 | 28227 | 28228 | VMM1 Average Line-to-Line Voltage | float | R | 2
| 0x6E45 | 0x6E46 | 28229 | 28230 | VMM1 Voltage Phase Order | float | R | 2
| 0x6E47 | 0x6E48 | 28231 | 28232 | VMM1 Phase A Current | float | R | 2
| 0x6E49 | 0x6E4A | 28233 | 28234 | VMM1 Phase B Current | float | R | 2
| 0x6E4B | 0x6E4C | 28235 | 28236 | VMM1 Phase C Current | float | R | 2
| 0x6E4D | 0x6E4E | 28237 | 28238 | VMM1 Neutral Current | float | R | 2
| 0x6E4F | 0x6E50 | 28239 | 28240 | VMM1 System Average Current | float | R | 2
| 0x6E51 | 0x6E52 | 28241 | 28242 | VMM1 Phase A Current Phase Angle | float | R | 2
| 0x6E53 | 0x6E54 | 28243 | 28244 | VMM1 Phase B Current Phase Angle | float | R | 2
| 0x6E55 | 0x6E56 | 28245 | 28246 | VMM1 Phase C Current Phase Angle | float | R | 2
| 0x6E57 | 0x6E58 | 28247 | 28248 | VMM1 Neutral Current Phase Angle | float | R | 2
| 0x6E59 | 0x6E88 | 28249 | 28296 | VMM1 CMM1 Input Channel 1-24 Current Angle | float | R | 48
| 0x6E89 | 0x6EB8 | 28297 | 28344 | VMM1 CMM2 Input Channel 1-24 Current Angle | float | R | 48
| 0x6EB9 | 0x6EE8 | 28345 | 28392 | VMM1 CMM3 Input Channel 1-24 Current Angle | float | R | 48
| 0x6EE9 | 0x6F18 | 28393 | 28440 | VMM1 CMM4 Input Channel 1-24 Current Angle | float | R | 48
| 0x6F19 | 0x700A | 28441 | 28682 | VMM2 Realtime Parameter | float | R | 242
| 0x700B | 0x703A | 28683 | 28730 | CMM1 Input Channel 1-24 Current | float | R | 48
| 0x703B | 0x706A | 28731 | 28778 | CMM2 Input Channel 25-48 Current | float | R | 48
| 0x706B | 0x709A | 28779 | 28826 | CMM3 Input Channel 49-72 Current | float | R | 48
| 0x709B | 0x70CA | 28827 | 28874 | CMM4 Input Channel 73-96 Current | float | R | 48
| 0x70CB | 0x70CB | 28875 | 28875 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x70CC | 0x70CD | 28876 | 28877 | MP1 Average Current | float | R | 2
| 0x70CE | 0x70CF | 28878 | 28879 | MP1 Neutral Current | float | R | 2
| 0x70D0 | 0x70D1 | 28880 | 28881 | MP1 Neutral Current Phase Angle | float | R | 2
Power(2Hr) | 0x70D2 | 0x70D3 | 28882 | 28883 | VMM1 Phase A Active Power | float | R | 2
| 0x70D4 | 0x70D5 | 28884 | 28885 | VMM1 Phase A Reactive Power | float | R | 2
| 0x70D6 | 0x70D7 | 28886 | 28887 | VMM1 Phase A Apparent Power | float | R | 2
| 0x70D8 | 0x70D9 | 28888 | 28889 | VMM1 Phase A Load Nature | uint32_t | R | 2
| 0x70DA | 0x70DB | 28890 | 28891 | VMM1 Phase A Power Factor | float | R | 2
| 0x70DC | 0x70DD | 28892 | 28893 | VMM1 Phase B Active Power | float | R | 2
| 0x70DE | 0x70DF | 28894 | 28895 | VMM1 Phase B Reactive Power | float | R | 2
| 0x70E0 | 0x70E1 | 28896 | 28897 | VMM1 Phase B Apparent Power | float | R | 2
| 0x70E2 | 0x70E3 | 28898 | 28899 | VMM1 Phase B Load Nature | uint32_t | R | 2
| 0x70E4 | 0x70E5 | 28900 | 28901 | VMM1 Phase B Power Factor | float | R | 2
| 0x70E6 | 0x70E7 | 28902 | 28903 | VMM1 Phase C Active Power | float | R | 2
| 0x70E8 | 0x70E9 | 28904 | 28905 | VMM1 Phase C Reactive Power | float | R | 2
| 0x70EA | 0x70EB | 28906 | 28907 | VMM1 Phase C Apparent Power | float | R | 2
| 0x70EC | 0x70ED | 28908 | 28909 | VMM1 Phase C Load Nature | uint32_t | R | 2
| 0x70EE | 0x70EF | 28910 | 28911 | VMM1 Phase C Power Factor | float | R | 2
| 0x70F0 | 0x70F1 | 28912 | 28913 | VMM1 System Active Power | float | R | 2
| 0x70F2 | 0x70F3 | 28914 | 28915 | VMM1 System Reactive Power | float | R | 2
| 0x70F4 | 0x70F5 | 28916 | 28917 | VMM1 System Apparent Power | float | R | 2
| 0x70F6 | 0x70F7 | 28918 | 28919 | VMM1 System Load Nature | uint32_t | R | 2
| 0x70F8 | 0x70F9 | 28920 | 28921 | VMM1 System Power Factor | float | R | 2
| 0x70FA | 0x70FA | 28922 | 28922 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x70FB | 0x70FC | 28923 | 28924 | VMM1 CMM1 Input Channel 1 Active Power | float | R | 2
| 0x70FD | 0x70FE | 28925 | 28926 | VMM1 CMM1 Input Channel 1 Reactive Powerr | float | R | 2
| 0x70FF | 0x7100 | 28927 | 28928 | VMM1 CMM1 Input Channel 1 Apparent Power | float | R | 2
| 0x7101 | 0x7102 | 28929 | 28930 | VMM1 CMM1 Input Channel 1 Load Naturer | uint32_t | R | 2
| 0x7103 | 0x7104 | 28931 | 28932 | VMM1 CMM1 Input Channel 1 Power Factor | float | R | 2
| 0x7105 | 0x7137 | 28933 | 28983 | VMM2 Power Parameter |  | R | 51
| 0x7138 | 0x7138 | 28984 | 28984 | MP Number Select | uint16_t | R/W | 1 | 1~192 | 1
| 0x7139 | 0x713A | 28985 | 28986 | MPl Active Power | float | R | 2
| 0x713B | 0x713C | 28987 | 28988 | MPl Reactive Powerr | float | R | 2
| 0x713D | 0x713E | 28989 | 28990 | MPl Apparent Power | float | R | 2
| 0x713F | 0x7140 | 28991 | 28992 | MPl Load Naturer | uint32_t | R | 2
| 0x7141 | 0x7142 | 28993 | 28994 | MPl Power Factor | float | R | 2
Power Quality(2Hr) | 0x7143 | 0x7144 | 28995 | 28996 | VMM1 Voltage Positive Sequence Magnitude | float | R | 2
| 0x7145 | 0x7146 | 28997 | 28998 | VMM1 Voltage Zero Sequence Magnitude | float | R | 2
| 0x7147 | 0x7148 | 28999 | 29000 | VMM1 Voltage Negative Sequence Magnitude | float | R | 2
| 0x7149 | 0x714A | 29001 | 29002 | VMM1 Voltage Positive Sequence Angle | float | R | 2
| 0x714B | 0x714C | 29003 | 29004 | VMM1 Voltage Zero Sequence Angle | float | R | 2
| 0x714D | 0x714E | 29005 | 29006 | VMM1 Voltage Negative Sequence Angle | float | R | 2
| 0x714F | 0x7150 | 29007 | 29008 | VMM1 Voltage Unbalance Negative | float | R | 2
| 0x7151 | 0x7152 | 29009 | 29010 | VMM1 Voltage Unbalance Zero | float | R | 2
| 0x7153 | 0x7154 | 29011 | 29012 | VMM1 Phase A Voltage THD | float | R | 2
| 0x7155 | 0x7156 | 29013 | 29014 | VMM1 Phase A Voltage THD Odd | float | R | 2
| 0x7157 | 0x7158 | 29015 | 29016 | VMM1 Phase A Voltage THD Even | float | R | 2
| 0x7159 | 0x715A | 29017 | 29018 | VMM1 Phase A Voltage Crest Factor | float | R | 2
| 0x715B | 0x7258 | 29019 | 29272 | VMM1 Phase A 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x7259 | 0x7356 | 29273 | 29526 | VMM1 Phase A 1-127st Voltage Harmonics Group | float | R | 254
| 0x7357 | 0x7454 | 29527 | 29780 | VMM1 Phase A 1-127st Voltage Angle Harmonics | float | R | 254
| 0x7455 | 0x7456 | 29781 | 29782 | VMM1 Phase B Voltage THD | float | R | 2
| 0x7457 | 0x7458 | 29783 | 29784 | VMM1 Phase B Voltage THD Odd | float | R | 2
| 0x7459 | 0x745A | 29785 | 29786 | VMM1 Phase B Voltage THD Even | float | R | 2
| 0x745B | 0x745C | 29787 | 29788 | VMM1 Phase B Voltage Crest Factor | float | R | 2
| 0x745D | 0x755A | 29789 | 30042 | VMM1 Phase B 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x755B | 0x7658 | 30043 | 30296 | VMM1 Phase B 1-127st Voltage Harmonics Group | float | R | 254
| 0x7659 | 0x7756 | 30297 | 30550 | VMM1 Phase B 1-127st Voltage Angle Harmonics | float | R | 254
| 0x7757 | 0x7758 | 30551 | 30552 | VMM1 Phase C Voltage THD | float | R | 2
| 0x7759 | 0x775A | 30553 | 30554 | VMM1 Phase C Voltage THD Odd | float | R | 2
| 0x775B | 0x775C | 30555 | 30556 | VMM1 Phase C Voltage THD Even | float | R | 2
| 0x775D | 0x775E | 30557 | 30558 | VMM1 Phase C Voltage Crest Factor | float | R | 2
| 0x775F | 0x785C | 30559 | 30812 | VMM1 Phase C 1-127st Voltage Magnitude Harmonics | float | R | 254
| 0x785D | 0x795A | 30813 | 31066 | VMM1 Phase C 1-127st Voltage Harmonics Group | float | R | 254
| 0x795B | 0x7A58 | 31067 | 31320 | VMM1 Phase C 1-127st Voltage Angle Harmonics | float | R | 254
| 0x7A59 | 0x7A5A | 31321 | 31322 | VMM1 Average Voltage THD | float | R | 2
| 0x7A5B | 0x7A5C | 31323 | 31324 | VMM1 Average Voltage THD Odd | float | R | 2
| 0x7A5D | 0x7A5E | 31325 | 31326 | VMM1 Average Voltage THD Even | float | R | 2
| 0x7A5F | 0x837A | 31327 | 33658 | VMM2 Voltage Power Quality | float | R | 2332
| 0x837B | 0x837B | 33659 | 33659 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x837C | 0x837D | 33660 | 33661 | CMM1 Input Channel 1 Current TDD | float | R | 2
| 0x837E | 0x837F | 33662 | 33663 | CMM1 Input Channel 1 Current THD | float | R | 2
| 0x8380 | 0x8381 | 33664 | 33665 | CMM1 Input Channel 1 Current THD Odd | float | R | 2
| 0x8382 | 0x8383 | 33666 | 33667 | CMM1 Input Channel 1 Current THD Even | float | R | 2
| 0x8384 | 0x8385 | 33668 | 33669 | CMM1 Input Channel 1 Current Crest Factor | float | R | 2
| 0x8386 | 0x8387 | 33670 | 33671 | CMM1 Input Channel 1 Current K Factor | float | R | 2
| 0x8388 | 0x8405 | 33672 | 33797 | CMM1 Input Channel 1 1-63st Current Magnitude Harmonics | float | R | 126
| 0x8406 | 0x8483 | 33798 | 33923 | CMM1 Input Channel 1 1-63st Current Harmonics Group | float | R | 126
| 0x8484 | 0x8501 | 33924 | 34049 | CMM1 Input Channel 1 1-63st Current Angle Harmonics | float | R | 126
| 0x8502 | 0x8502 | 34050 | 34050 | MP Number Select | uint16_t | R/W | 1 | 1~192
| 0x8503 | 0x8504 | 34051 | 34052 | MP1 Current Positive Sequence Magnitude | float | R | 2
| 0x8505 | 0x8506 | 34053 | 34054 | MP1 Current Zero Sequence Magnitude | float | R | 2
| 0x8507 | 0x8508 | 34055 | 34056 | MP1 Current Negative Sequence Magnitude | float | R | 2
| 0x8509 | 0x850A | 34057 | 34058 | MP1 Current Positive Sequence Angle | float | R | 2
| 0x850B | 0x850C | 34059 | 34060 | MP1 Current Zero Sequence Angle | float | R | 2
| 0x850D | 0x850E | 34061 | 34062 | MP1 Current Negative Sequence Angle | float | R | 2
| 0x850F | 0x8510 | 34063 | 34064 | MP1 Current Unbalance Negative | float | R | 2
| 0x8511 | 0x8512 | 34065 | 34066 | MP1 Current Unbalance Zero | float | R | 2
Flicker(2Hr) | 0x8513 | 0x8514 | 34067 | 34068 | VMM1 Phase A Flicker Pinst Max | float | R | 2
| 0x8515 | 0x8516 | 34069 | 34070 | VMM1 Phase B Flicker Pinst Max | float | R | 2
| 0x8517 | 0x8518 | 34071 | 34072 | VMM1 Phase C Flicker Pinst Max | float | R | 2
| 0x8519 | 0x851A | 34073 | 34074 | VMM2 Phase A Flicker Pinst Max | float | R | 2
| 0x851B | 0x851C | 34075 | 34076 | VMM2 Phase B Flicker Pinst Max | float | R | 2
| 0x851D | 0x851E | 34077 | 34078 | VMM2 Phase C Flicker Pinst Max | float | R | 2

## 10S Freq
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
10S Freq | 0x8530 | 0x8533 | 34096 | 34099 | VMM1 10s Param Update Time Stamp | uint64_t | R | 4
| 0x8534 | 0x8535 | 34100 | 34101 | VMM1 10s System Frequency | uint32_t | R | 2
| 0x8536 | 0x8536 | 34102 | 34102 | VMM1 10s Param Event Info | uint16_t | R | 1
| 0x8537 | 0x8537 | 34103 | 34103 | VMM1 10s Param Event Flag | uint16_t | R | 1
| 0x8538 | 0x853B | 34104 | 34107 | VMM2 10s Param Update Time Stamp | uint64_t | R | 4
| 0x853C | 0x853D | 34108 | 34109 | VMM2 10s System Frequency | uint32_t | R | 2
| 0x853E | 0x853E | 34110 | 34110 | VMM2 10s Param Event Info | uint16_t | R | 1
| 0x853F | 0x853F | 34111 | 34111 | VMM2 10s Param Event Flag | uint16_t | R | 1

## MaxMin
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Max Record Value | 0x8550 | 0x8551 | 34128 | 34129 | VMM1 System Frequency Max Value | float | R | 2
| 0x8552 | 0x8555 | 34130 | 34133 | VMM1 System Frequency Max Value Timestamp | uint64_t | R | 4
| 0x8556 | 0x8557 | 34134 | 34135 | VMM1 Phase A Line-to-Neutral Voltage Max Value | float | R | 2
| 0x8558 | 0x855B | 34136 | 34139 | VMM1 Phase A Line-to-Neutral Voltage Max Value Timestamp | uint64_t | R | 4
| 0x855C | 0x855D | 34140 | 34141 | VMM1 Phase B Line-to-Neutral Voltage Max Value | float | R | 2
| 0x855E | 0x8561 | 34142 | 34145 | VMM1 Phase B Line-to-Neutral Voltage Max Value Timestamp | uint64_t | R | 4
| 0x8562 | 0x8563 | 34146 | 34147 | VMM1 Phase C Line-to-Neutral Voltage Max Value | float | R | 2
| 0x8564 | 0x8567 | 34148 | 34151 | VMM1 Phase C Line-to-Neutral Voltage Max Value Timestamp | uint64_t | R | 4
| 0x8568 | 0x8569 | 34152 | 34153 | VMM1 Phase AB Line-to-Line Voltage Max Value | float | R | 2
| 0x856A | 0x856D | 34154 | 34157 | VMM1 Phase AB Line-to-Line Voltage Max Value Timestamp | uint64_t | R | 4
| 0x856E | 0x856F | 34158 | 34159 | VMM1 Phase BC Line-to-Line Voltage Max Value | float | R | 2
| 0x8570 | 0x8573 | 34160 | 34163 | VMM1 Phase BC Line-to-Line Voltage Max Value Timestamp | uint64_t | R | 4
| 0x8574 | 0x8575 | 34164 | 34165 | VMM1 Phase CA Line-to-Line Voltage Max Value | float | R | 2
| 0x8576 | 0x8579 | 34166 | 34169 | VMM1 Phase CA Line-to-Line Voltage Max Value Timestamp | uint64_t | R | 4
| 0x857A | 0x857B | 34170 | 34171 | VMM1 Average Line-to-Line Voltage Max Value | float | R | 2
| 0x857C | 0x857F | 34172 | 34175 | VMM1 Average Line-to-Line Voltage Max Value Timestamp | uint64_t | R | 4
| 0x8580 | 0x8581 | 34176 | 34177 | VMM1 Phase A Current Max Value | float | R | 2
| 0x8582 | 0x8585 | 34178 | 34181 | VMM1 Phase A Current Max Value Timestamp | uint64_t | R | 4
| 0x8586 | 0x8587 | 34182 | 34183 | VMM1 Phase B Current Max Value | float | R | 2
| 0x8588 | 0x858B | 34184 | 34187 | VMM1 Phase B Current Max Value Timestamp | uint64_t | R | 4
| 0x858C | 0x858D | 34188 | 34189 | VMM1 Phase C Current Max Value | float | R | 2
| 0x858E | 0x8591 | 34190 | 34193 | VMM1 Phase C Current Max Value Timestamp | uint64_t | R | 4
| 0x8592 | 0x8593 | 34194 | 34195 | VMM1 Neutral Current Max Value | float | R | 2
| 0x8594 | 0x8597 | 34196 | 34199 | VMM1 Neutral Current Max Value Timestamp | uint64_t | R | 4
| 0x8598 | 0x85DF | 34200 | 34271 | VMM2 Realtime Parameter Max Value And Timestamp |  | R | 72
| 0x85E0 | 0x866F | 34272 | 34415 | CMM1 Input Channel 1-24 Current Max Value And Timestamp |  | R | 144
| 0x8670 | 0x86FF | 34416 | 34559 | CMM2 Input Channel 25-48 Current Max Value And Timestamp |  | R | 144
| 0x8700 | 0x878F | 34560 | 34703 | CMM3 Input Channel 49-72 Current Max Value And Timestamp |  | R | 144
| 0x8790 | 0x881F | 34704 | 34847 | CMM4 Input Channel 73-96 Current Max Value And Timestamp |  | R | 144
| 0x8820 | 0x8821 | 34848 | 34849 | VMM1 Phase A Active Power Max Value | float | R | 2
| 0x8822 | 0x8825 | 34850 | 34853 | VMM1 Phase A Active Power Max Value Timestamp | uint64_t | R | 4
| 0x8826 | 0x8827 | 34854 | 34855 | VMM1 Phase A Reactive Power Max Value | float | R | 2
| 0x8828 | 0x882B | 34856 | 34859 | VMM1 Phase A Reactive Power Max Value Timestamp | uint64_t | R | 4
| 0x882C | 0x882D | 34860 | 34861 | VMM1 Phase A Apparent Power Max Value | float | R | 2
| 0x882E | 0x8831 | 34862 | 34865 | VMM1 Phase A Apparent Power Max Value Timestamp | uint64_t | R | 4
| 0x8832 | 0x8833 | 34866 | 34867 | VMM1 Phase A Power Factor Max Value | float | R | 2
| 0x8834 | 0x8837 | 34868 | 34871 | VMM1 Phase A Power Factor Max Value Timestamp | uint64_t | R | 4
| 0x8838 | 0x8839 | 34872 | 34873 | VMM1 Phase B Active Power Max Value | float | R | 2
| 0x883A | 0x883D | 34874 | 34877 | VMM1 Phase B Active Power Max Value Timestamp | uint64_t | R | 4
| 0x883E | 0x883F | 34878 | 34879 | VMM1 Phase B Reactive Power Max Value | float | R | 2
| 0x8840 | 0x8843 | 34880 | 34883 | VMM1 Phase B Reactive Power Max Value Timestamp | uint64_t | R | 4
| 0x8844 | 0x8845 | 34884 | 34885 | VMM1 Phase B Apparent Power Max Value | float | R | 2
| 0x8846 | 0x8849 | 34886 | 34889 | VMM1 Phase B Apparent Power Max Value Timestamp | uint64_t | R | 4
| 0x884A | 0x884B | 34890 | 34891 | VMM1 Phase B Power Factor Max Value | float | R | 2
| 0x884C | 0x884F | 34892 | 34895 | VMM1 Phase B Power Factor Max Value Timestamp | uint64_t | R | 4
| 0x8850 | 0x8851 | 34896 | 34897 | VMM1 Phase C Active Power Max Value | float | R | 2
| 0x8852 | 0x8855 | 34898 | 34901 | VMM1 Phase C Active Power Max Value Timestamp | uint64_t | R | 4
| 0x8856 | 0x8857 | 34902 | 34903 | VMM1 Phase C Reactive Power Max Value | float | R | 2
| 0x8858 | 0x885B | 34904 | 34907 | VMM1 Phase C Reactive Power Max Value Timestamp | uint64_t | R | 4
| 0x885C | 0x885D | 34908 | 34909 | VMM1 Phase C Apparent Power Max Value | float | R | 2
| 0x885E | 0x8861 | 34910 | 34913 | VMM1 Phase C Apparent Power Max Value Timestamp | uint64_t | R | 4
| 0x8862 | 0x8863 | 34914 | 34915 | VMM1 Phase C Power Factor Max Value | float | R | 2
| 0x8864 | 0x8867 | 34916 | 34919 | VMM1 Phase C Power Factor Max Value Timestamp | uint64_t | R | 4
| 0x8868 | 0x8869 | 34920 | 34921 | VMM1 System Average Current Max Value | float | R | 2
| 0x886A | 0x886D | 34922 | 34925 | VMM1 System Average Current Max Value Timestamp | uint64_t | R | 4
| 0x886E | 0x886F | 34926 | 34927 | VMM1 System Active Power Max Value | float | R | 2
| 0x8870 | 0x8873 | 34928 | 34931 | VMM1 System Active Power Max Value Timestamp | uint64_t | R | 4
| 0x8874 | 0x8875 | 34932 | 34933 | VMM1 System Reactive Power Max Value | float | R | 2
| 0x8876 | 0x8879 | 34934 | 34937 | VMM1 System Reactive Power Max Value Timestamp | uint64_t | R | 4
| 0x887A | 0x887B | 34938 | 34939 | VMM1 System Apparent Power Max Value | float | R | 2
| 0x887C | 0x887F | 34940 | 34943 | VMM1 System Apparent Power Max Value Timestamp | uint64_t | R | 4
| 0x8880 | 0x8881 | 34944 | 34945 | VMM1 System Power Factor Max Value | float | R | 2
| 0x8882 | 0x8885 | 34946 | 34949 | VMM1 System Power Factor Max Value Timestamp | uint64_t | R | 4
| 0x8886 | 0x8886 | 34950 | 34950 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x8887 | 0x8888 | 34951 | 34952 | VMM1 CMM1 Input Channel 1 Active Power Max Value | float | R | 2
| 0x8889 | 0x888C | 34953 | 34956 | VMM1 CMM1 Input Channel 1 Active Power Max Value Timestamp | uint64_t | R | 4
| 0x888D | 0x888E | 34957 | 34958 | VMM1 CMM1 Input Channel 1 Reactive Powerr Max Value | float | R | 2
| 0x888F | 0x8892 | 34959 | 34962 | VMM1 CMM1 Input Channel 1 Reactive Powerr Max Value Timestamp | uint64_t | R | 4
| 0x8893 | 0x8894 | 34963 | 34964 | VMM1 CMM1 Input Channel 1 Apparent Power Max Value | float | R | 2
| 0x8895 | 0x8898 | 34965 | 34968 | VMM1 CMM1 Input Channel 1 Apparent Power Max Value Timestamp | uint64_t | R | 4
| 0x8899 | 0x889A | 34969 | 34970 | VMM1 CMM1 Input Channel 1 Power Factor Max Value | float | R | 2
| 0x889B | 0x889E | 34971 | 34974 | VMM1 CMM1 Input Channel 1 Power Factor Max Value Timestamp | uint64_t | R | 4
| 0x889F | 0x891D | 34975 | 35101 | VMM2 Power Parameter Max Value And Timestamp |  | R | 127
| 0x891E | 0x891E | 35102 | 35102 | MP Number Select | uint16_t | R/W | 1 | 1~192
| 0x891F | 0x8920 | 35103 | 35104 | MPl Active Power Max Value | float | R | 2
| 0x8921 | 0x8924 | 35105 | 35108 | MPl Active Power Max Value Timestamp | uint64_t | R | 4
| 0x8925 | 0x8926 | 35109 | 35110 | MPl Reactive Powerr Max Value | float | R | 2
| 0x8927 | 0x892A | 35111 | 35114 | MPl Reactive Powerr Max Value Timestamp | uint64_t | R | 4
| 0x892B | 0x892C | 35115 | 35116 | MPl Apparent Power Max Value | float | R | 2
| 0x892D | 0x8930 | 35117 | 35120 | MPl Apparent Power Max Value Timestamp | uint64_t | R | 4
| 0x8931 | 0x8932 | 35121 | 35122 | MPl Power Factor Max Value | float | R | 2
| 0x8933 | 0x8936 | 35123 | 35126 | MPl Power Factor Max Value Timestamp | uint64_t | R | 4
| 0x8937 | 0x8938 | 35127 | 35128 | VMM1 Voltage Unbalance Negative Max Value | float | R | 2
| 0x8939 | 0x893C | 35129 | 35132 | VMM1 Voltage Unbalance Negative Max Value Timestamp | uint64_t | R | 4
| 0x893D | 0x893E | 35133 | 35134 | VMM1 Voltage Unbalance Zero Max Value | float | R | 2
| 0x893F | 0x8942 | 35135 | 35138 | VMM1 Voltage Unbalance Zero Max Value Timestamp | uint64_t | R | 4
| 0x8943 | 0x8944 | 35139 | 35140 | VMM1 Phase A Voltage THD Max Value | float | R | 2
| 0x8945 | 0x8948 | 35141 | 35144 | VMM1 Phase A Voltage THD Max Value Timestamp | uint64_t | R | 4
| 0x8949 | 0x894A | 35145 | 35146 | VMM1 Phase B Voltage THD Max Value | float | R | 2
| 0x894B | 0x894E | 35147 | 35150 | VMM1 Phase B Voltage THD Max Value Timestamp | uint64_t | R | 4
| 0x894F | 0x8950 | 35151 | 35152 | VMM1 Phase C Voltage THD Max Value | float | R | 2
| 0x8951 | 0x8954 | 35153 | 35156 | VMM1 Phase C Voltage THD Max Value Timestamp | uint64_t | R | 4
| 0x8955 | 0x8956 | 35157 | 35158 | VMM1 Average Voltage THD Max Value | float | R | 2
| 0x8957 | 0x895A | 35159 | 35162 | VMM1 Average Voltage THD Max Value Timestamp | uint64_t | R | 4
| 0x895B | 0x897E | 35163 | 35198 | VMM2 Voltage Power Quality Max Value And Timestamp |  | R | 36
| 0x897F | 0x8980 | 35199 | 35200 | CMM1 Input Channel 1 Current THD Max Value | float | R | 2
| 0x8981 | 0x8984 | 35201 | 35204 | CMM1 Input Channel 1 Current THD Max Value Timestamp | uint64_t | R | 4
| 0x8985 | 0x8A0E | 35205 | 35342 | CMM1 Input Channel 2-24 Power Quality Max Value And Timestamp |  | R | 138
| 0x8A0F | 0x8A9E | 35343 | 35486 | CMM2 Input Channel 25-48 Power Quality Max Value And Timestamp |  | R | 144
| 0x8A9F | 0x8B2E | 35487 | 35630 | CMM3 Input Channel 49-72 Power Quality Max Value And Timestamp |  | R | 144
| 0x8B2F | 0x8BBE | 35631 | 35774 | CMM4 Input Channel 73-96 Power Quality Max Value And Timestamp |  | R | 144
| 0x8BBF | 0x8BBF | 35775 | 35775 | MP Number Select | uint16_t | R/W | 1 | 1~192
| 0x8BC0 | 0x8BC1 | 35776 | 35777 | MP1 Current Unbalance Negative Max Value | float | R | 2
| 0x8BC2 | 0x8BC5 | 35778 | 35781 | MP1 Current Unbalance Negative Max Value Timestamp | uint64_t | R | 4
| 0x8BC6 | 0x8BC7 | 35782 | 35783 | MP1 Current Unbalance Zero Max Value | float | R | 2
| 0x8BC8 | 0x8BCB | 35784 | 35787 | MP1 Current Unbalance Zero Max Value Timestamp | uint64_t | R | 4
Min Record Value | 0x8BE0 | 0x8BE1 | 35808 | 35809 | VMM1 System Frequency Min Value | float | R | 2
| 0x8BE2 | 0x8BE5 | 35810 | 35813 | VMM1 System Frequency Min Value Timestamp | uint64_t | R | 4
| 0x8BE6 | 0x8BE7 | 35814 | 35815 | VMM1 Phase A Line-to-Neutral Voltage Min Value | float | R | 2
| 0x8BE8 | 0x8BEB | 35816 | 35819 | VMM1 Phase A Line-to-Neutral Voltage Min Value Timestamp | uint64_t | R | 4
| 0x8BEC | 0x8BED | 35820 | 35821 | VMM1 Phase B Line-to-Neutral Voltage Min Value | float | R | 2
| 0x8BEE | 0x8BF1 | 35822 | 35825 | VMM1 Phase B Line-to-Neutral Voltage Min Value Timestamp | uint64_t | R | 4
| 0x8BF2 | 0x8BF3 | 35826 | 35827 | VMM1 Phase C Line-to-Neutral Voltage Min Value | float | R | 2
| 0x8BF4 | 0x8BF7 | 35828 | 35831 | VMM1 Phase C Line-to-Neutral Voltage Min Value Timestamp | uint64_t | R | 4
| 0x8BF8 | 0x8BF9 | 35832 | 35833 | VMM1 Phase AB Line-to-Line Voltage Min Value | float | R | 2
| 0x8BFA | 0x8BFD | 35834 | 35837 | VMM1 Phase AB Line-to-Line Voltage Min Value Timestamp | uint64_t | R | 4
| 0x8BFE | 0x8BFF | 35838 | 35839 | VMM1 Phase BC Line-to-Line Voltage Min Value | float | R | 2
| 0x8C00 | 0x8C03 | 35840 | 35843 | VMM1 Phase BC Line-to-Line Voltage Min Value Timestamp | uint64_t | R | 4
| 0x8C04 | 0x8C05 | 35844 | 35845 | VMM1 Phase CA Line-to-Line Voltage Min Value | float | R | 2
| 0x8C06 | 0x8C09 | 35846 | 35849 | VMM1 Phase CA Line-to-Line Voltage Min Value Timestamp | uint64_t | R | 4
| 0x8C0A | 0x8C0B | 35850 | 35851 | VMM1 Average Line-to-Line Voltage Min Value | float | R | 2
| 0x8C0C | 0x8C0F | 35852 | 35855 | VMM1 Average Line-to-Line Voltage Min Value Timestamp | uint64_t | R | 4
| 0x8C10 | 0x8C11 | 35856 | 35857 | VMM1 Phase A Current Min Value | float | R | 2
| 0x8C12 | 0x8C15 | 35858 | 35861 | VMM1 Phase A Current Min Value Timestamp | uint64_t | R | 4
| 0x8C16 | 0x8C17 | 35862 | 35863 | VMM1 Phase B Current Min Value | float | R | 2
| 0x8C18 | 0x8C1B | 35864 | 35867 | VMM1 Phase B Current Min Value Timestamp | uint64_t | R | 4
| 0x8C1C | 0x8C1D | 35868 | 35869 | VMM1 Phase C Current Min Value | float | R | 2
| 0x8C1E | 0x8C21 | 35870 | 35873 | VMM1 Phase C Current Min Value Timestamp | uint64_t | R | 4
| 0x8C22 | 0x8C23 | 35874 | 35875 | VMM1 Neutral Current Min Value | float | R | 2
| 0x8C24 | 0x8C27 | 35876 | 35879 | VMM1 Neutral Current Min Value Timestamp | uint64_t | R | 4
| 0x8C28 | 0x8C6F | 35880 | 35951 | VMM2 Realtime Parameter Min Value And Timestamp |  | R | 72
| 0x8C70 | 0x8CFF | 35952 | 36095 | CMM1 Input Channel 1-24 Current Min Value And Timestamp |  | R | 144
| 0x8D00 | 0x8D8F | 36096 | 36239 | CMM2 Input Channel 25-48 Current Min Value And Timestamp |  | R | 144
| 0x8D90 | 0x8E1F | 36240 | 36383 | CMM3 Input Channel 49-72 Current Min Value And Timestamp |  | R | 144
| 0x8E20 | 0x8EAF | 36384 | 36527 | CMM4 Input Channel 73-96 Current Min Value And Timestamp |  | R | 144
| 0x8EB0 | 0x8EB1 | 36528 | 36529 | VMM1 Phase A Active Power Min Value | float | R | 2
| 0x8EB2 | 0x8EB5 | 36530 | 36533 | VMM1 Phase A Active Power Min Value Timestamp | uint64_t | R | 4
| 0x8EB6 | 0x8EB7 | 36534 | 36535 | VMM1 Phase A Reactive Power Min Value | float | R | 2
| 0x8EB8 | 0x8EBB | 36536 | 36539 | VMM1 Phase A Reactive Power Min Value Timestamp | uint64_t | R | 4
| 0x8EBC | 0x8EBD | 36540 | 36541 | VMM1 Phase A Apparent Power Min Value | float | R | 2
| 0x8EBE | 0x8EC1 | 36542 | 36545 | VMM1 Phase A Apparent Power Min Value Timestamp | uint64_t | R | 4
| 0x8EC2 | 0x8EC3 | 36546 | 36547 | VMM1 Phase A Power Factor Min Value | float | R | 2
| 0x8EC4 | 0x8EC7 | 36548 | 36551 | VMM1 Phase A Power Factor Min Value Timestamp | uint64_t | R | 4
| 0x8EC8 | 0x8EC9 | 36552 | 36553 | VMM1 Phase B Active Power Min Value | float | R | 2
| 0x8ECA | 0x8ECD | 36554 | 36557 | VMM1 Phase B Active Power Min Value Timestamp | uint64_t | R | 4
| 0x8ECE | 0x8ECF | 36558 | 36559 | VMM1 Phase B Reactive Power Min Value | float | R | 2
| 0x8ED0 | 0x8ED3 | 36560 | 36563 | VMM1 Phase B Reactive Power Min Value Timestamp | uint64_t | R | 4
| 0x8ED4 | 0x8ED5 | 36564 | 36565 | VMM1 Phase B Apparent Power Min Value | float | R | 2
| 0x8ED6 | 0x8ED9 | 36566 | 36569 | VMM1 Phase B Apparent Power Min Value Timestamp | uint64_t | R | 4
| 0x8EDA | 0x8EDB | 36570 | 36571 | VMM1 Phase B Power Factor Min Value | float | R | 2
| 0x8EDC | 0x8EDF | 36572 | 36575 | VMM1 Phase B Power Factor Min Value Timestamp | uint64_t | R | 4
| 0x8EE0 | 0x8EE1 | 36576 | 36577 | VMM1 Phase C Active Power Min Value | float | R | 2
| 0x8EE2 | 0x8EE5 | 36578 | 36581 | VMM1 Phase C Active Power Min Value Timestamp | uint64_t | R | 4
| 0x8EE6 | 0x8EE7 | 36582 | 36583 | VMM1 Phase C Reactive Power Min Value | float | R | 2
| 0x8EE8 | 0x8EEB | 36584 | 36587 | VMM1 Phase C Reactive Power Min Value Timestamp | uint64_t | R | 4
| 0x8EEC | 0x8EED | 36588 | 36589 | VMM1 Phase C Apparent Power Min Value | float | R | 2
| 0x8EEE | 0x8EF1 | 36590 | 36593 | VMM1 Phase C Apparent Power Min Value Timestamp | uint64_t | R | 4
| 0x8EF2 | 0x8EF3 | 36594 | 36595 | VMM1 Phase C Power Factor Min Value | float | R | 2
| 0x8EF4 | 0x8EF7 | 36596 | 36599 | VMM1 Phase C Power Factor Min Value Timestamp | uint64_t | R | 4
| 0x8EF8 | 0x8EF9 | 36600 | 36601 | VMM1 System Average Current Min Value | float | R | 2
| 0x8EFA | 0x8EFD | 36602 | 36605 | VMM1 System Average Current Min Value Timestamp | uint64_t | R | 4
| 0x8EFE | 0x8EFF | 36606 | 36607 | VMM1 System Active Power Min Value | float | R | 2
| 0x8F00 | 0x8F03 | 36608 | 36611 | VMM1 System Active Power Min Value Timestamp | uint64_t | R | 4
| 0x8F04 | 0x8F05 | 36612 | 36613 | VMM1 System Reactive Power Min Value | float | R | 2
| 0x8F06 | 0x8F09 | 36614 | 36617 | VMM1 System Reactive Power Min Value Timestamp | uint64_t | R | 4
| 0x8F0A | 0x8F0B | 36618 | 36619 | VMM1 System Apparent Power Min Value | float | R | 2
| 0x8F0C | 0x8F0F | 36620 | 36623 | VMM1 System Apparent Power Min Value Timestamp | uint64_t | R | 4
| 0x8F10 | 0x8F11 | 36624 | 36625 | VMM1 System Power Factor Min Value | float | R | 2
| 0x8F12 | 0x8F15 | 36626 | 36629 | VMM1 System Power Factor Min Value Timestamp | uint64_t | R | 4
| 0x8F16 | 0x8F16 | 36630 | 36630 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x8F17 | 0x8F18 | 36631 | 36632 | VMM1 CMM1 Input Channel 1 Active Power Min Value | float | R | 2
| 0x8F19 | 0x8F1C | 36633 | 36636 | VMM1 CMM1 Input Channel 1 Active Power Min Value Timestamp | uint64_t | R | 4
| 0x8F1D | 0x8F1E | 36637 | 36638 | VMM1 CMM1 Input Channel 1 Reactive Powerr Min Value | float | R | 2
| 0x8F1F | 0x8F22 | 36639 | 36642 | VMM1 CMM1 Input Channel 1 Reactive Powerr Min Value Timestamp | uint64_t | R | 4
| 0x8F23 | 0x8F24 | 36643 | 36644 | VMM1 CMM1 Input Channel 1 Apparent Power Min Value | float | R | 2
| 0x8F25 | 0x8F28 | 36645 | 36648 | VMM1 CMM1 Input Channel 1 Apparent Power Min Value Timestamp | uint64_t | R | 4
| 0x8F29 | 0x8F2A | 36649 | 36650 | VMM1 CMM1 Input Channel 1 Power Factor Min Value | float | R | 2
| 0x8F2B | 0x8F2E | 36651 | 36654 | VMM1 CMM1 Input Channel 1 Power Factor Min Value Timestamp | uint64_t | R | 4
| 0x8F2F | 0x8FAD | 36655 | 36781 | VMM2 Power Parameter Min Value And Timestamp |  | R | 127
| 0x8FAE | 0x8FAE | 36782 | 36782 | MP Number Select | uint16_t | R/W | 1 | 1~192
| 0x8FAF | 0x8FB0 | 36783 | 36784 | MPl Active Power Min Value | float | R | 2
| 0x8FB1 | 0x8FB4 | 36785 | 36788 | MPl Active Power Min Value Timestamp | uint64_t | R | 4
| 0x8FB5 | 0x8FB6 | 36789 | 36790 | MPl Reactive Powerr Min Value | float | R | 2
| 0x8FB7 | 0x8FBA | 36791 | 36794 | MPl Reactive Powerr Min Value Timestamp | uint64_t | R | 4
| 0x8FBB | 0x8FBC | 36795 | 36796 | MPl Apparent Power Min Value | float | R | 2
| 0x8FBD | 0x8FC0 | 36797 | 36800 | MPl Apparent Power Min Value Timestamp | uint64_t | R | 4
| 0x8FC1 | 0x8FC2 | 36801 | 36802 | MPl Power Factor Min Value | float | R | 2
| 0x8FC3 | 0x8FC6 | 36803 | 36806 | MPl Power Factor Min Value Timestamp | uint64_t | R | 4
| 0x8FC7 | 0x8FC8 | 36807 | 36808 | VMM1 Voltage Unbalance Negative Min Value | float | R | 2
| 0x8FC9 | 0x8FCC | 36809 | 36812 | VMM1 Voltage Unbalance Negative Min Value Timestamp | uint64_t | R | 4
| 0x8FCD | 0x8FCE | 36813 | 36814 | VMM1 Voltage Unbalance Zero Min Value | float | R | 2
| 0x8FCF | 0x8FD2 | 36815 | 36818 | VMM1 Voltage Unbalance Zero Min Value Timestamp | uint64_t | R | 4
| 0x8FD3 | 0x8FD4 | 36819 | 36820 | VMM1 Phase A Voltage THD Min Value | float | R | 2
| 0x8FD5 | 0x8FD8 | 36821 | 36824 | VMM1 Phase A Voltage THD Min Value Timestamp | uint64_t | R | 4
| 0x8FD9 | 0x8FDA | 36825 | 36826 | VMM1 Phase B Voltage THD Min Value | float | R | 2
| 0x8FDB | 0x8FDE | 36827 | 36830 | VMM1 Phase B Voltage THD Min Value Timestamp | uint64_t | R | 4
| 0x8FDF | 0x8FE0 | 36831 | 36832 | VMM1 Phase C Voltage THD Min Value | float | R | 2
| 0x8FE1 | 0x8FE4 | 36833 | 36836 | VMM1 Phase C Voltage THD Min Value Timestamp | uint64_t | R | 4
| 0x8FE5 | 0x8FE6 | 36837 | 36838 | VMM1 Average Voltage THD Min Value | float | R | 2
| 0x8FE7 | 0x8FEA | 36839 | 36842 | VMM1 Average Voltage THD Min Value Timestamp | uint64_t | R | 4
| 0x8FEB | 0x900E | 36843 | 36878 | VMM2 Voltage Power Quality Min Value And Timestamp |  | R | 36
| 0x900F | 0x9010 | 36879 | 36880 | CMM1 Input Channel 1 Current THD Min Value | float | R | 2
| 0x9011 | 0x9014 | 36881 | 36884 | CMM1 Input Channel 1 Current THD Min Value Timestamp | uint64_t | R | 4
| 0x9015 | 0x909E | 36885 | 37022 | CMM1 Input Channel 2-24 Power Quality Min Value And Timestamp |  | R | 138
| 0x909F | 0x912E | 37023 | 37166 | CMM2 Input Channel 25-48 Power Quality Min Value And Timestamp |  | R | 144
| 0x912F | 0x91BE | 37167 | 37310 | CMM3 Input Channel 49-72 Power Quality Min Value And Timestamp |  | R | 144
| 0x91BF | 0x924E | 37311 | 37454 | CMM4 Input Channel 73-96 Power Quality Min Value And Timestamp |  | R | 144
| 0x924F | 0x924F | 37455 | 37455 | MP Number Select | uint16_t | R/W | 1 | 1~192
| 0x9250 | 0x9251 | 37456 | 37457 | MP1 Current Unbalance Negative Min Value | float | R | 2
| 0x9252 | 0x9255 | 37458 | 37461 | MP1 Current Unbalance Negative Min Value Timestamp | uint64_t | R | 4
| 0x9256 | 0x9257 | 37462 | 37463 | MP1 Current Unbalance Zero Min Value | float | R | 2
| 0x9258 | 0x925B | 37464 | 37467 | MP1 Current Unbalance Zero Min Value Timestamp | uint64_t | R | 4

## Max Demand
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
MaxDemand | 0x9270 | 0x9271 | 37488 | 37489 | VMM1 Phase A Current Max Demand | float | R | 2
| 0x9272 | 0x9275 | 37490 | 37493 | VMM1 Phase A Current Max Demand Timestamp | uint64_t | R | 4
| 0x9276 | 0x9277 | 37494 | 37495 | VMM1 Phase A Import Active Power Max Demand | float | R | 2
| 0x9278 | 0x927B | 37496 | 37499 | VMM1 Phase A Import Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x927C | 0x927D | 37500 | 37501 | VMM1 Phase A Export Active Power Max Demand | float | R | 2
| 0x927E | 0x9281 | 37502 | 37505 | VMM1 Phase A Export Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x9282 | 0x9283 | 37506 | 37507 | VMM1 Phase A Import Reactive Power Max Demand | float | R | 2
| 0x9284 | 0x9287 | 37508 | 37511 | VMM1 Phase A Import Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x9288 | 0x9289 | 37512 | 37513 | VMM1 Phase A Export Reactive Power Max Demand | float | R | 2
| 0x928A | 0x928D | 37514 | 37517 | VMM1 Phase A Export Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x928E | 0x928F | 37518 | 37519 | VMM1 Phase A Apparent Power Max Demand | float | R | 2
| 0x9290 | 0x9293 | 37520 | 37523 | VMM1 Phase A Apparent Power Max Demand Timestamp | uint64_t | R | 4
| 0x9294 | 0x9295 | 37524 | 37525 | VMM1 Phase B Current Max Demand | float | R | 2
| 0x9296 | 0x9299 | 37526 | 37529 | VMM1 Phase B Current Max Demand Timestamp | uint64_t | R | 4
| 0x929A | 0x929B | 37530 | 37531 | VMM1 Phase B Import Active Power Max Demand | float | R | 2
| 0x929C | 0x929F | 37532 | 37535 | VMM1 Phase B Import Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x92A0 | 0x92A1 | 37536 | 37537 | VMM1 Phase B Export Active Power Max Demand | float | R | 2
| 0x92A2 | 0x92A5 | 37538 | 37541 | VMM1 Phase B Export Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x92A6 | 0x92A7 | 37542 | 37543 | VMM1 Phase B Import Reactive Power Max Demand | float | R | 2
| 0x92A8 | 0x92AB | 37544 | 37547 | VMM1 Phase B Import Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x92AC | 0x92AD | 37548 | 37549 | VMM1 Phase B Export Reactive Power Max Demand | float | R | 2
| 0x92AE | 0x92B1 | 37550 | 37553 | VMM1 Phase B Export Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x92B2 | 0x92B3 | 37554 | 37555 | VMM1 Phase B Apparent Power Max Demand | float | R | 2
| 0x92B4 | 0x92B7 | 37556 | 37559 | VMM1 Phase B Apparent Power Max Demand Timestamp | uint64_t | R | 4
| 0x92B8 | 0x92B9 | 37560 | 37561 | VMM1 Phase C Current Max Demand | float | R | 2
| 0x92BA | 0x92BD | 37562 | 37565 | VMM1 Phase C Current Max Demand Timestamp | uint64_t | R | 4
| 0x92BE | 0x92BF | 37566 | 37567 | VMM1 Phase C Import Active Power Max Demand | float | R | 2
| 0x92C0 | 0x92C3 | 37568 | 37571 | VMM1 Phase C Import Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x92C4 | 0x92C5 | 37572 | 37573 | VMM1 Phase C Export Active Power Max Demand | float | R | 2
| 0x92C6 | 0x92C9 | 37574 | 37577 | VMM1 Phase C Export Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x92CA | 0x92CB | 37578 | 37579 | VMM1 Phase C Import Reactive Power Max Demand | float | R | 2
| 0x92CC | 0x92CF | 37580 | 37583 | VMM1 Phase C Import Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x92D0 | 0x92D1 | 37584 | 37585 | VMM1 Phase C Export Reactive Power Max Demand | float | R | 2
| 0x92D2 | 0x92D5 | 37586 | 37589 | VMM1 Phase C Export Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x92D6 | 0x92D7 | 37590 | 37591 | VMM1 Phase C Apparent Power Max Demand | float | R | 2
| 0x92D8 | 0x92DB | 37592 | 37595 | VMM1 Phase C Apparent Power Max Demand Timestamp | uint64_t | R | 4
| 0x92DC | 0x92DD | 37596 | 37597 | VMM1 System Average Current Max Demand | float | R | 2
| 0x92DE | 0x92E1 | 37598 | 37601 | VMM1 System Average Current Max Demand Timestamp | uint64_t | R | 4
| 0x92E2 | 0x92E3 | 37602 | 37603 | VMM1 System Import Active Power Max Demand | float | R | 2
| 0x92E4 | 0x92E7 | 37604 | 37607 | VMM1 System Import Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x92E8 | 0x92E9 | 37608 | 37609 | VMM1 System Export Active Power Max Demand | float | R | 2
| 0x92EA | 0x92ED | 37610 | 37613 | VMM1 System Export Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x92EE | 0x92EF | 37614 | 37615 | VMM1 System Import Reactive Power Max Demand | float | R | 2
| 0x92F0 | 0x92F3 | 37616 | 37619 | VMM1 System Import Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x92F4 | 0x92F5 | 37620 | 37621 | VMM1 System Export Reactive Power Max Demand | float | R | 2
| 0x92F6 | 0x92F9 | 37622 | 37625 | VMM1 System Export Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x92FA | 0x92FB | 37626 | 37627 | VMM1 System Apparent Power Max Demand | float | R | 2
| 0x92FC | 0x92FF | 37628 | 37631 | VMM1 System Apparent Power Max Demand Timestamp | uint64_t | R | 4
| 0x9300 | 0x938F | 37632 | 37775 | VMM2 Max Demand Parameter And Timestamp |  | R | 144
| 0x9390 | 0x9391 | 37776 | 37777 | CMM1 Input Channel 1 Current Max Demand | float | R | 2
| 0x9392 | 0x9395 | 37778 | 37781 | CMM1 Input Channel 1 Current Max Demand Timestamp | uint64_t | R | 4
| 0x9396 | 0x941F | 37782 | 37919 | CMM1 Input Channel 2-24 Current Max Demand And Timestamp |  | R | 138
| 0x9420 | 0x94AF | 37920 | 38063 | CMM2 Input Channel 25-48 Current Max Demand And Timestamp |  | R | 144
| 0x94B0 | 0x953F | 38064 | 38207 | CMM3 Input Channel 49-72 Current Max Demand And Timestamp |  | R | 144
| 0x9540 | 0x95CF | 38208 | 38351 | CMM4 Input Channel 73-96 Current Max Demand And Timestamp |  | R | 144
| 0x95D0 | 0x95D0 | 38352 | 38352 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x95D1 | 0x95D2 | 38353 | 38354 | VMM1 CMM1 Input Channel 1 Import Active Power Max Demand | float | R | 2
| 0x95D3 | 0x95D6 | 38355 | 38358 | VMM1 CMM1 Input Channel 1 Import Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x95D7 | 0x95D8 | 38359 | 38360 | VMM1 CMM1 Input Channel 1 Export Active Power Max Demand | float | R | 2
| 0x95D9 | 0x95DC | 38361 | 38364 | VMM1 CMM1 Input Channel 1 Export Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x95DD | 0x95DE | 38365 | 38366 | VMM1 CMM1 Input Channel 1 Import Reactive Power Max Demand | float | R | 2
| 0x95DF | 0x95E2 | 38367 | 38370 | VMM1 CMM1 Input Channel 1 Import Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x95E3 | 0x95E4 | 38371 | 38372 | VMM1 CMM1 Input Channel 1 Export Reactive Power Max Demand | float | R | 2
| 0x95E5 | 0x95E8 | 38373 | 38376 | VMM1 CMM1 Input Channel 1 Export Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x95E9 | 0x95EA | 38377 | 38378 | VMM1 CMM1 Input Channel 1 Apparent Power Max Demand | float | R | 2
| 0x95EB | 0x95EE | 38379 | 38382 | VMM1 CMM1 Input Channel 1 Apparent Power Max Demand Timestamp | uint64_t | R | 4
| 0x95EF | 0x960D | 38383 | 38413 | VMM2 CMM1 Input Channel 1-96 Max Demand And Timestamp |  | R | 31
| 0x960E | 0x960E | 38414 | 38414 | MP Number Select | uint16_t | R/W | 1 | 1~192
| 0x960F | 0x9610 | 38415 | 38416 | MP1 Average Current Max Demand | float | R | 2
| 0x9611 | 0x9614 | 38417 | 38420 | MP1 Average Current Max Demand Timestamp | uint64_t | R | 4
| 0x9615 | 0x9616 | 38421 | 38422 | MP1 Import Active Power Max Demand | float | R | 2
| 0x9617 | 0x961A | 38423 | 38426 | MP1 Import Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x961B | 0x961C | 38427 | 38428 | MP1 Export Active Power Max Demand | float | R | 2
| 0x961D | 0x9620 | 38429 | 38432 | MP1 Export Active Power Max Demand Timestamp | uint64_t | R | 4
| 0x9621 | 0x9622 | 38433 | 38434 | MP1 Import Reactive Power Max Demand | float | R | 2
| 0x9623 | 0x9626 | 38435 | 38438 | MP1 Import Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x9627 | 0x9628 | 38439 | 38440 | MP1 Export Reactive Power Max Demand | float | R | 2
| 0x9629 | 0x962C | 38441 | 38444 | MP1 Export Reactive Power Max Demand Timestamp | uint64_t | R | 4
| 0x962D | 0x962E | 38445 | 38446 | MP1 Apparent Power Max Demand | float | R | 2
| 0x962F | 0x9632 | 38447 | 38450 | MP1 Apparent Power Max Demand Timestamp | uint64_t | R | 4

## Waveform¦PQ Event
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Power Quality Event setting | 0x9290 | 0x9291 | 37520 | 37521 | VMM1 Nominal Voltage | uint32_t | R/W | 2
| 0x9292 | 0x9292 | 37522 | 37522 | VMM1 Voltage Sag Enable | uint16_t | R/W | 1
| 0x9293 | 0x9293 | 37523 | 37523 | VMM1 Voltage Sag Threshold | uint16_t | R/W | 1
| 0x9294 | 0x9294 | 37524 | 37524 | VMM1 Voltage Sag Jitter | uint16_t | R/W | 1
| 0x9295 | 0x9295 | 37525 | 37525 | VMM1 Voltage Sag Triggers Waveform Recording | uint16_t | R/W | 1
| 0x9296 | 0x9296 | 37526 | 37526 | VMM1 Voltage Swell Enable | uint16_t | R/W | 1
| 0x9297 | 0x9297 | 37527 | 37527 | VMM1 Voltage Swell Threshold | uint16_t | R/W | 1
| 0x9298 | 0x9298 | 37528 | 37528 | VMM1 Voltage Swell Jitter | uint16_t | R/W | 1
| 0x9299 | 0x9299 | 37529 | 37529 | VMM1 Voltage Swell Triggers Waveform Recording | uint16_t | R/W | 1
| 0x929A | 0x929A | 37530 | 37530 | VMM1 Voltage Interruption Enable | uint16_t | R/W | 1
| 0x929B | 0x929B | 37531 | 37531 | VMM1 Voltage Interruption Threshold | uint16_t | R/W | 1
| 0x929C | 0x929C | 37532 | 37532 | VMM1 Voltage Interruption Jitter | uint16_t | R/W | 1
| 0x929D | 0x929D | 37533 | 37533 | VMM1 Voltage Interruption Triggers Waveform Recording | uint16_t | R/W | 1
| 0x929E | 0x92AB | 37534 | 37547 | VMM2 Voltage Power Quality Event Setting |  | R/W | 14
| 0x92AC | 0x92AC | 37548 | 37548 | Channel Number Select | uint16_t | R/W | 1 | 1~96
| 0x92AD | 0x92AD | 37549 | 37549 | CMM1 Input Channel 1 Norminal Current | uint16_t | R/W | 1
| 0x92AE | 0x92AE | 37550 | 37550 | CMM1 Input Channel 1 Current Swell Enable | uint16_t | R/W | 1
| 0x92AF | 0x92AF | 37551 | 37551 | CMM1 Input Channel 1 Current Swell Threshold | uint16_t | R/W | 1
| 0x92B0 | 0x92B0 | 37552 | 37552 | CMM1 Input Channel 1 Current Swell Jitter | uint16_t | R/W | 1
| 0x92B1 | 0x92B1 | 37553 | 37553 | CMM1 Input Channel 1 Current Swell Triggers Waveform Recording | uint16_t | R/W | 1
Waveform Setting | 0x92B2 | 0x92B2 | 37554 | 37554 | The nth waveform cycle | uint16_t | R/W | 1
| 0x92B3 | 0x92B3 | 37555 | 37555 | The nth register packet of one waveform cycle | uint16_t | R/W | 1
PQ Event Log | 1 |  |  |  | Meter Type | uint16_t | R | 1
| 2 |  |  |  | Meter ID | uint16_t | R | 1
| 3 |  |  |  | PQ Event Log ID | uint16_t | R | 1
| 4 |  |  |  | Log TimeStamp | timestamp | R | 4
| 5 |  |  |  | Event Type | uint16_t | R | 1
| 6 |  |  |  | Event Status | uint16_t | R | 1
| 7 |  |  |  | Trigger channel | uint16_t | R | 1
| 8 |  |  |  | Associate with waveform ID | uint32_t | R | 2
| 9 |  |  |  | Duration of power quality events | uint32_t | R | 2
| 10 |  |  |  | Max Value of Parameter #1 | float | R | 2
| 11 |  |  |  | Max Value of Parameter #2 | float | R | 2
| 12 |  |  |  | Max Value of Parameter #3 | float | R | 2
| 13 |  |  |  | Min Value of Parameter #1 | float | R | 2
| 14 |  |  |  | Min Value of Parameter #2 | float | R | 2
| 15 |  |  |  | Min Value of Parameter #3 | float | R | 2
Waveform Log | 1 |  |  |  | Meter Type | uin16_t | R | 1
| 2 |  |  |  | Meter ID | uin16_t | R | 1
| 3 |  |  |  | Waveform ID | uin16_t | R | 1
| 4 |  |  |  | Reason Mode | uin16_t | R | 1
| 6 |  |  |  | TimeStamp | timestamp | R | 4
| 7 |  |  |  | Trigger Channel | uint32_t | R | 2
| 8 |  |  |  | Data Packets | float | R | 4 | VMM:1024*30*3*4=368640
CMM:128*30*24*4=368640

## Information
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Device Info | 0x9650 | 0x9651 | 38480 | 38481 | Device 1 Type | uint16_t | R | 2
| 0x9652 | 0x9655 | 38482 | 38485 | Device 1 Serial Number | uint8_t | R | 4
| 0x9656 | 0x9656 | 38486 | 38486 | Device 1 Hardware version | uint8_t | R | 1
| 0x9657 | 0x9657 | 38487 | 38487 | Device 1 Firmware Version | uint8_t | R | 1
| 0x9658 | 0x9658 | 38488 | 38488 | Device 1 Firmware release date | uint8_t | R | 1
| 0x9659 | 0x9659 | 38489 | 38489 | Device 1 bootloader version | uint8_t | R | 1
| 0x965A | 0x965A | 38490 | 38490 | Device 1 bootloader release date | uint8_t | R | 1
| 0x965B | 0x965B | 38491 | 38491 | Device 1 Run Mode | uint8_t | R | 1 | 0:NONE 1:BOOT 2:APP
| 0x965C | 0x9700 | 38492 | 38656 | Devic2-Device16 Info | uint8_t | R | 165
MH Info | 0x9710 | 0x9710 | 38672 | 38672 | HM Firmware Version | uint8_t | R | 1
| 0x9711 | 0x9711 | 38673 | 38673 | HM Firmware release date | uint8_t | R | 1
| 0x9712 | 0x9712 | 38674 | 38674 | HM Hardware version | uint8_t | R/W | 1
| 0x9713 | 0x9713 | 38675 | 38675 | Load Time | uint16_t | R/W | 1
| 0x9714 | 0x9714 | 38676 | 38676 | Run Time | uint16_t | R/W | 1

## DeviceStatus
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg Num | Range | Default
Configure Device Running States | 0x9720 | 0x972F | 38688 | 38703 | Device 1 Serial Number | uint8_t | R | 16
| 0x9730 | 0x9730 | 38704 | 38704 | Device 1 Run Mode | uint8_t | R | 1 | 0:None 1:BOOT 2:APP
| 0x9731 | 0x9731 | 38705 | 38705 | Device 1 State | uint8_t | R | 1 | BOOT: 0:Offline 1:Discovered 2:Ready 3:Transferring 4:Success 5:Failed APP: 0:Offline 1:Discovered 2:Configuring 3:Running 4:Software Rejected(Software Version Incompatible) 5:Hardware Rejected(Hardware Version Incompatible)
| 0x9732 | 0x9786 | 38706 | 38790 | Device 2-6 Running States | uint8_t | R | 85