## blockParams
ID | blockId | paramId | address | Start(Dec) | descrption | paramType | unit | check | dataType | byteOrder | RW | Reg | scale | Alarm | Data log default parameter | Trend Log | DataLog | AcuCloud | MQTT | SNMP | BACnetIP | North
1 | 0 | 0-1 | 0 | 0 | IsOnline | IsOnline |  |  | isOnline | 1 | R | 1 | 1
2 | 1 | 1-1 | 0 | 8194 | Phase A Line Current | I_a_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
3 | 1 | 1-2 | 2 | 8196 | Phase B Line Current | I_b_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
4 | 1 | 1-3 | 4 | 8198 | Phase C Line Current | I_c_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
5 | 1 | 1-4 | 6 | 8200 | Average Line-to-Neutral Voltage | VLN_avg_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
6 | 1 | 1-5 | 8 | 8202 | Phase A Line-to-Neutral Voltage | VLN_a_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
7 | 1 | 1-6 | 10 | 8204 | Phase B Line-to-Neutral Voltage | VLN_b_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8 | 1 | 1-7 | 12 | 8206 | Phase C Line-to-Neutral Voltage | VLN_c_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
9 | 1 | 1-8 | 14 | 8208 | Average Line-to-Line Voltage | VLL_avg_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
10 | 1 | 1-9 | 16 | 8210 | Phase A-B Line-to-Line Voltage | VLL_ab_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
11 | 1 | 1-10 | 18 | 8212 | Phase B-C Line-to-Line Voltage | VLL_bc_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
12 | 1 | 1-11 | 20 | 8214 | Phase C-A Line-to-Line Voltage | VLL_ca_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
13 | 1 | 1-12 | 22 | 8216 | System Frequency | FREQ_Hz | Hz |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
14 | 1 | 1-13 | 24 | 8218 | System Active Power | P_kW | kW |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
15 | 1 | 1-14 | 26 | 8220 | Phase A Active Power | P_a_kW | kW |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16 | 1 | 1-15 | 28 | 8222 | Phase B Active Power | P_b_kW | kW |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
17 | 1 | 1-16 | 30 | 8224 | Phase C Active Power | P_c_kW | kW |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
18 | 1 | 1-17 | 32 | 8226 | System Apparent Power | S_kVA | kVA |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
19 | 1 | 1-18 | 34 | 8228 | Phase A Apparent Power | S_a_kVA | kVA |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
20 | 1 | 1-19 | 36 | 8230 | Phase B Apparent Power | S_b_kVA | kVA |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
21 | 1 | 1-20 | 38 | 8232 | Phase C Apparent Power | S_c_kVA | kVA |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
22 | 1 | 1-21 | 40 | 8234 | System Reactive Power | Q_kvar | kvar |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
23 | 1 | 1-22 | 42 | 8236 | Phase A Reactive Power | Q_a_kvar | kvar |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
24 | 1 | 1-23 | 44 | 8238 | Phase B Reactive Power | Q_b_kvar | kvar |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
25 | 1 | 1-24 | 46 | 8240 | Phase C Reactive Power | Q_c_kvar | kvar |  | float32 | 12 | R | 2 | 0.001 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
26 | 1 | 1-25 | 48 | 8242 | System Power Factor | PF |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
27 | 1 | 1-26 | 50 | 8244 | Phase A Power Factor | PF_a |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
28 | 1 | 1-27 | 52 | 8246 | Phase B Power Factor | PF_b |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
29 | 1 | 1-28 | 54 | 8248 | Phase C Power Factor | PF_c |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
30 | 2 | 2-1 | 0 | 8262 | System Export Active Energy | EP_EXP_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
31 | 2 | 2-2 | 2 | 8264 | Phase A Export Active Energy | EP_EXP_a_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
32 | 2 | 2-3 | 4 | 8266 | Phase B Export Active Energy | EP_EXP_b_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
33 | 2 | 2-4 | 6 | 8268 | Phase C Export Active Energy | EP_EXP_c_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
34 | 2 | 2-5 | 8 | 8270 | System Import Active Energy | EP_IMP_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
35 | 2 | 2-6 | 10 | 8272 | Phase A Import Active Energy | EP_IMP_a_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
36 | 2 | 2-7 | 12 | 8274 | Phase B Import Active Energy | EP_IMP_b_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
37 | 2 | 2-8 | 14 | 8276 | Phase C Import Active Energy | EP_IMP_c_kWh | kWh |  | uint32 | 12 | R/W | 2 | 0.1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
38 | 3 | 3-1 | 0 | 4616 | System Active Power Demand | DMD_P_kW | kW |  | float32 | 12 | R | 2 | 0.001 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
39 | 3 | 3-2 | 2 | 4618 | System Reactive Power Demand | DMD_Q_kvar | kvar |  | float32 | 12 | R | 2 | 0.001 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
40 | 3 | 3-3 | 4 | 4620 | System Apparent Power Demand | DMD_S_kVA | kVA |  | float32 | 12 | R | 2 | 0.001 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
41 | 4 | 4-1 | 0 | 512 | Communication Address | Conf_Ch1_Addr |  |  | uint16 | 12 | R/W | 1 | 1
42 | 4 | 4-2 | 1 | 513 | RS485 Communication Baud Rate | Conf_Ch1_Baud |  |  | uint16 | 12 | R/W | 1 | 1
43 | 4 | 4-3 | 2 | 514 | RS485 Communication Parity | Conf_Ch1_Parity |  |  | uint16 | 12 | R/W | 1 | 1
44 | 4 | 4-4 | 3 | 515 | Pulse Parameter | Conf_PulseParam |  |  | uint16 | 12 | R/W | 1 | 1
45 | 4 | 4-5 | 4 | 516 | Demand Method | Conf_Dmd_Method |  |  | uint16 | 12 | R/W | 1 | 1
46 | 4 | 4-6 | 5 | 517 | Demand Window | Conf_Dmd_Window |  |  | uint16 | 12 | R/W | 1 | 1
47 | 4 | 4-7 | 6 | 518 | Demand Sub Interval | Conf_Dmd_SubInterval |  |  | uint16 | 12 | R/W | 1 | 1
48 | 4 | 4-8 | 7 | 519 | Reactive Power Calculation Method | Conf_CalcMethod_Q |  |  | uint16 | 12 | R/W | 1 | 1
49 | 4 | 4-9 | 8 | 520 | VAR/PF Convention | Conf_CalcMethod_VarPF |  |  | uint16 | 12 | R/W | 1 | 1
50 | 4 | 4-10 | 9 | 521 | Non-standard content seal option | Conf_Seal_Option |  |  | uint16 | 12 | R/W | 1 | 1
51 | 4 | 4-11 | 10 | 522 | Communication Permission | Conf_Comm_Perm |  |  | uint16 | 12 | R/W | 1 | 1
52 | 4 | 4-12 | 11 | 523 | Current Password | Conf_Curr_Pwd |  |  | uint16 | 12 | R/W | 1 | 1
53 | 4 | 4-13 | 12 | 524 | New Password | Conf_New_Pwd |  |  | uint16 | 12 | R/W | 1 | 1
54 | 4 | 4-14 | 13 | 525 | Clear Meter Data | Conf_Clr_Data |  |  | uint16 | 12 | R/W | 1 | 1
55 | 4 | 4-15 | 14 | 526 | Optional Display Flag Word 1 | Conf_OptWord1 |  |  | uint16 | 12 | R/W | 1 | 1
56 | 4 | 4-16 | 15 | 527 | Optional Display Flag Word 2 | Conf_OptWord2 |  |  | uint16 | 12 | R/W | 1 | 1
57 | 4 | 4-17 | 16 | 528 | Basic Reading Display Primary/Secondary | Conf_DispFormat_RealTime |  |  | uint16 | 12 | R/W | 1 | 1
58 | 4 | 4-18 | 17 | 529 | Service Configuration | Conf_ServiceConfig |  |  | uint16 | 12 | R/W | 1 | 1
59 | 4 | 4-19 | 18 | 530 | CT2 Value | Conf_CT2 |  |  | uint16 | 12 | R/W | 1 | 1
60 | 4 | 4-20 | 19 | 531 | CT1 Value | Conf_CT1 |  |  | uint16 | 12 | R/W | 1 | 1
61 | 4 | 4-21 | 20 | 532 | CTN Value | Conf_CT41 |  |  | uint16 | 12 | R/W | 1 | 1
62 | 4 | 4-22 | 21 | 533 | PT2 | Conf_PT2 |  |  | uint16 | 12 | R/W | 1 | 0.1
63 | 4 | 4-23 | 22 | 534 | PT1 | Conf_PT1 |  |  | uint32 | 12 | R/W | 2 | 0.1
64 | 4 | 4-24 | 24 | 536 | Pulse Constant | Conf_PulseConst |  |  | uint16 | 12 | R/W | 1 | 1
65 | 4 | 4-25 | 25 | 537 | Pulse Width | Conf_PulseWidth |  |  | uint16 | 12 | R/W | 1 | 1
66 | 4 | 4-26 | 26 | 538 | Energy Display Decimal Digits | Conf_Energy_Digits |  |  | uint16 | 12 | R/W | 1 | 1
67 | 4 | 4-27 | 27 | 539 | RO Output Mode | Conf_RO_Mode |  |  | uint16 | 12 | R/W | 1 | 1
68 | 4 | 4-28 | 28 | 540 | Enable Wiring Error Detection | Conf_Enable_Detect_WireError |  |  | uint16 | 12 | R/W | 1 | 1
69 | 5 | 5-1 | 0 | 256 | Wiring Error | Info_WireError |  |  | uint16 | 12 | R | 1 | 1
70 | 5 | 5-2 | 1 | 257 | Sealing status | Info_Seal_Status |  |  | uint16 | 12 | R | 1 | 1
71 | 5 | 5-3 | 2 | 258 | Enclosure status | Info_Enclosure_Status |  |  | uint16 | 12 | R | 1 | 1
72 | 6 | 6-1 | 0 | 61953 | InfoCT2Type | Info_CT2_Type |  |  | uint16 | 12 | R | 1 | 1