## UnitStandardSet
UnitStandardSet
Hz
V
°
A
kW
kvar
kVA
%
kWh
kvarh
kVAh

## blockParams
Start(Dec) | descrption | paramType | unit | Check | dataType | RW | Reg | scale | Alarm | Data log default parameter | Trend Log | DataLog | AcuCloud | MQTT | SNMP | BACnetIP | North
0 | IsOnline | IsOnline |  |  | isOnline | R | 1 | 1
8192 | System Frequency | FREQ_Hz | Hz |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8194 | Phase A Line-to-Neutral Voltage | VLN_a_V | V |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8196 | Phase B Line-to-Neutral Voltage | VLN_b_V | V |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8198 | Phase C Line-to-Neutral Voltage | VLN_c_V | V |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8200 | Average Line-to-Neutral Voltage | VLN_avg_V | V |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8202 | Phase A-B Line-to-Line Voltage | VLL_ab_V | V |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8204 | Phase B-C Line-to-Line Voltage | VLL_bc_V | V |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8206 | Phase C-A Line-to-Line Voltage | VLL_ca_V | V |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8208 | Average Line-to-Line Voltage | VLL_avg_V | V |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8210 | Phase A Line-to-Neutral Voltage Phase Angle | ANG_VLN_a | ° |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8212 | Phase B Line-to-Neutral Voltage Phase Angle | ANG_VLN_b | ° |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8214 | Phase C Line-to-Neutral Voltage Phase Angle | ANG_VLN_c | ° |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8216 | Phase A Current | I_a_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8218 | Phase A Active Power | P_a_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8220 | Phase A Reactive Power | Q_a_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8222 | Phase A Apparent Power | S_a_kVA | kVA | S_a_Kva修改为S_a_kVA | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8224 | Phase A Load Nature | LC_a |  |  | uint32 | R | 2 | 1
8226 | Phase A Power Factor | PF_a |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8228 | Phase B Current | I_b_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8230 | Phase B Active Power | P_b_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8232 | Phase B Reactive Power | Q_b_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8234 | Phase B Apparent Power | S_b_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8236 | Phase B Load Nature | LC_b |  |  | uint32 | R | 2 | 1
8238 | Phase B Power Factor | PF_b |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8240 | Phase C Current | I_c_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8242 | Phase C Active Power | P_c_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8244 | Phase C Reactive Power | Q_c_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8246 | Phase C Apparent Power | S_c_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8248 | Phase C Load Nature | LC_c |  |  | uint32 | R | 2 | 1
8250 | Phase C Power Factor | PF_c |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8252 | System Average Current | I_avg_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8254 | System Active Power | P_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8256 | System Reactive Power | Q_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8258 | System Apparent Power | S_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8260 | System Load Nature | LC |  |  | uint32 | R | 2 | 1
8262 | System Power Factor | PF |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8264 | Input Channel 1 Current | I_001_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8266 | Input Channel 1 Active Power | P_001_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8268 | Input Channel 1 Reactive Power | Q_001_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8270 | Input Channel 1 Apparent Power | S_001_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8272 | Input Channel 1 Load Nature | LC_001 |  |  | uint32 | R | 2 | 1
8274 | Input Channel 1 Power Factor | PF_001 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8276 | Input Channel 1 Current Phase Angle | ANG_I_001 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8278 | Input Channel 2 Current | I_002_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8280 | Input Channel 2 Active Power | P_002_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8282 | Input Channel 2 Reactive Power | Q_002_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8284 | Input Channel 2 Apparent Power | S_002_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8286 | Input Channel 2 Load Nature | LC_002 |  |  | uint32 | R | 2 | 1
8288 | Input Channel 2 Power Factor | PF_002 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8290 | Input Channel 2 Current Phase Angle | ANG_I_002 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8292 | Input Channel 3 Current | I_003_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8294 | Input Channel 3 Active Power | P_003_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8296 | Input Channel 3 Reactive Power | Q_003_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8298 | Input Channel 3 Apparent Power | S_003_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8300 | Input Channel 3 Load Nature | LC_003 |  |  | uint32 | R | 2 | 1
8302 | Input Channel 3 Power Factor | PF_003 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8304 | Input Channel 3 Current Phase Angle | ANG_I_003 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8306 | Input Channel 4 Current | I_004_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8308 | Input Channel 4 Active Power | P_004_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8310 | Input Channel 4 Reactive Power | Q_004_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8312 | Input Channel 4 Apparent Power | S_004_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8314 | Input Channel 4 Load Nature | LC_004 |  |  | uint32 | R | 2 | 1
8316 | Input Channel 4 Power Factor | PF_004 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8318 | Input Channel 4 Current Phase Angle | ANG_I_004 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8320 | Input Channel 5 Current | I_005_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8322 | Input Channel 5 Active Power | P_005_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8324 | Input Channel 5 Reactive Power | Q_005_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8326 | Input Channel 5 Apparent Power | S_005_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8328 | Input Channel 5 Load Nature | LC_005 |  |  | uint32 | R | 2 | 1
8330 | Input Channel 5 Power Factor | PF_005 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8332 | Input Channel 5 Current Phase Angle | ANG_I_005 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8334 | Input Channel 6 Current | I_006_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8336 | Input Channel 6 Active Power | P_006_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8338 | Input Channel 6 Reactive Power | Q_006_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8340 | Input Channel 6 Apparent Power | S_006_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8342 | Input Channel 6 Load Nature | LC_006 |  |  | uint32 | R | 2 | 1
8344 | Input Channel 6 Power Factor | PF_006 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8346 | Input Channel 6 Current Phase Angle | ANG_I_006 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8348 | Input Channel 7 Current | I_007_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8350 | Input Channel 7 Active Power | P_007_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8352 | Input Channel 7 Reactive Power | Q_007_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8354 | Input Channel 7 Apparent Power | S_007_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8356 | Input Channel 7 Load Nature | LC_007 |  |  | uint32 | R | 2 | 1
8358 | Input Channel 7 Power Factor | PF_007 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8360 | Input Channel 7 Current Phase Angle | ANG_I_007 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8362 | Input Channel 8 Current | I_008_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8364 | Input Channel 8 Active Power | P_008_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8366 | Input Channel 8 Reactive Power | Q_008_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8368 | Input Channel 8 Apparent Power | S_008_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8370 | Input Channel 8 Load Nature | LC_008 |  |  | uint32 | R | 2 | 1
8372 | Input Channel 8 Power Factor | PF_008 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8374 | Input Channel 8 Current Phase Angle | ANG_I_008 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8376 | Input Channel 9 Current | I_009_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8378 | Input Channel 9 Active Power | P_009_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8380 | Input Channel 9 Reactive Power | Q_009_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8382 | Input Channel 9 Apparent Power | S_009_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8384 | Input Channel 9 Load Nature | LC_009 |  |  | uint32 | R | 2 | 1
8386 | Input Channel 9 Power Factor | PF_009 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8388 | Input Channel 9 Current Phase Angle | ANG_I_009 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8390 | Input Channel 10 Current | I_010_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8392 | Input Channel 10 Active Power | P_010_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8394 | Input Channel 10 Reactive Power | Q_010_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8396 | Input Channel 10 Apparent Power | S_010_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8398 | Input Channel 10 Load Nature | LC_010 |  |  | uint32 | R | 2 | 1
8400 | Input Channel 10 Power Factor | PF_010 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8402 | Input Channel 10 Current Phase Angle | ANG_I_010 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8404 | Input Channel 11 Current | I_011_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8406 | Input Channel 11 Active Power | P_011_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8408 | Input Channel 11 Reactive Power | Q_011_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8410 | Input Channel 11 Apparent Power | S_011_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8412 | Input Channel 11 Load Nature | LC_011 |  |  | uint32 | R | 2 | 1
8414 | Input Channel 11 Power Factor | PF_011 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8416 | Input Channel 11 Current Phase Angle | ANG_I_011 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8418 | Input Channel 12 Current | I_012_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8420 | Input Channel 12 Active Power | P_012_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8422 | Input Channel 12 Reactive Power | Q_012_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8424 | Input Channel 12 Apparent Power | S_012_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8426 | Input Channel 12 Load Nature | LC_012 |  |  | uint32 | R | 2 | 1
8428 | Input Channel 12 Power Factor | PF_012 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8430 | Input Channel 12 Current Phase Angle | ANG_I_012 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8432 | Input Channel 13 Current | I_013_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8434 | Input Channel 13 Active Power | P_013_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8436 | Input Channel 13 Reactive Power | Q_013_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8438 | Input Channel 13 Apparent Power | S_013_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8440 | Input Channel 13 Load Nature | LC_013 |  |  | uint32 | R | 2 | 1
8442 | Input Channel 13 Power Factor | PF_013 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8444 | Input Channel 13 Current Phase Angle | ANG_I_013 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8446 | Input Channel 14 Current | I_014_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8448 | Input Channel 14 Active Power | P_014_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8450 | Input Channel 14 Reactive Power | Q_014_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8452 | Input Channel 14 Apparent Power | S_014_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8454 | Input Channel 14 Load Nature | LC_014 |  |  | uint32 | R | 2 | 1
8456 | Input Channel 14 Power Factor | PF_014 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8458 | Input Channel 14 Current Phase Angle | ANG_I_014 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8460 | Input Channel 15 Current | I_015_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8462 | Input Channel 15 Active Power | P_015_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8464 | Input Channel 15 Reactive Power | Q_015_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8466 | Input Channel 15 Apparent Power | S_015_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8468 | Input Channel 15 Load Nature | LC_015 |  |  | uint32 | R | 2 | 1
8470 | Input Channel 15 Power Factor | PF_015 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8472 | Input Channel 15 Current Phase Angle | ANG_I_015 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8474 | Input Channel 16 Current | I_016_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8476 | Input Channel 16 Active Power | P_016_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8478 | Input Channel 16 Reactive Power | Q_016_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8480 | Input Channel 16 Apparent Power | S_016_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8482 | Input Channel 16 Load Nature | LC_016 |  |  | uint32 | R | 2 | 1
8484 | Input Channel 16 Power Factor | PF_016 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8486 | Input Channel 16 Current Phase Angle | ANG_I_016 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8488 | Input Channel 17 Current | I_017_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8490 | Input Channel 17 Active Power | P_017_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8492 | Input Channel 17 Reactive Power | Q_017_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8494 | Input Channel 17 Apparent Power | S_017_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8496 | Input Channel 17 Load Nature | LC_017 |  |  | uint32 | R | 2 | 1
8498 | Input Channel 17 Power Factor | PF_017 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8500 | Input Channel 17 Current Phase Angle | ANG_I_017 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8502 | Input Channel 18 Current | I_018_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8504 | Input Channel 18 Active Power | P_018_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8506 | Input Channel 18 Reactive Power | Q_018_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8508 | Input Channel 18 Apparent Power | S_018_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8510 | Input Channel 18 Load Nature | LC_018 |  |  | uint32 | R | 2 | 1
8512 | Input Channel 18 Power Factor | PF_018 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8514 | Input Channel 18 Current Phase Angle | ANG_I_018 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8516 | Input Channel 19 Current | I_019_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8518 | Input Channel 19 Active Power | P_019_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8520 | Input Channel 19 Reactive Power | Q_019_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8522 | Input Channel 19 Apparent Power | S_019_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8524 | Input Channel 19 Load Nature | LC_019 |  |  | uint32 | R | 2 | 1
8526 | Input Channel 19 Power Factor | PF_019 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8528 | Input Channel 19 Current Phase Angle | ANG_I_019 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8530 | Input Channel 20 Current | I_020_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8532 | Input Channel 20 Active Power | P_020_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8534 | Input Channel 20 Reactive Power | Q_020_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8536 | Input Channel 20 Apparent Power | S_020_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8538 | Input Channel 20 Load Nature | LC_020 |  |  | uint32 | R | 2 | 1
8540 | Input Channel 20 Power Factor | PF_020 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8542 | Input Channel 20 Current Phase Angle | ANG_I_020 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8544 | Input Channel 21 Current | I_021_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8546 | Input Channel 21 Active Power | P_021_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8548 | Input Channel 21 Reactive Power | Q_021_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8550 | Input Channel 21 Apparent Power | S_021_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8552 | Input Channel 21 Load Nature | LC_021 |  |  | uint32 | R | 2 | 1
8554 | Input Channel 21 Power Factor | PF_021 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8556 | Input Channel 21 Current Phase Angle | ANG_I_021 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8558 | Input Channel 22 Current | I_022_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8560 | Input Channel 22 Active Power | P_022_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8562 | Input Channel 22 Reactive Power | Q_022_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8564 | Input Channel 22 Apparent Power | S_022_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8566 | Input Channel 22 Load Nature | LC_022 |  |  | uint32 | R | 2 | 1
8568 | Input Channel 22 Power Factor | PF_022 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8570 | Input Channel 22 Current Phase Angle | ANG_I_022 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8572 | Input Channel 23 Current | I_023_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8574 | Input Channel 23 Active Power | P_023_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8576 | Input Channel 23 Reactive Power | Q_023_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8578 | Input Channel 23 Apparent Power | S_023_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8580 | Input Channel 23 Load Nature | LC_023 |  |  | uint32 | R | 2 | 1
8582 | Input Channel 23 Power Factor | PF_023 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8584 | Input Channel 23 Current Phase Angle | ANG_I_023 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8586 | Input Channel 24 Current | I_024_A | A |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8588 | Input Channel 24 Active Power | P_024_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8590 | Input Channel 24 Reactive Power | Q_024_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8592 | Input Channel 24 Apparent Power | S_024_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8594 | Input Channel 24 Load Nature | LC_024 |  |  | uint32 | R | 2 | 1
8596 | Input Channel 24 Power Factor | PF_024 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8598 | Input Channel 24 Current Phase Angle | ANG_I_024 | ° |  | float32 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8600 | User Channel 1 Current | I_s001_A | A | I_s001_%修改为I_s001_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8602 | User Channel 1 Active Power | P_s001_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8604 | User Channel 1 Reactive Power | Q_s001_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8606 | User Channel 1 Apparent Power | S_s001_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8608 | User Channel 1 Load Nature | LC_s001 |  |  | uint32 | R | 2 | 1
8610 | User Channel 1 Power Factor | PF_s001 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8612 | User Channel 2 Current | I_s002_A | A | I_s002_%修改为I_s002_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8614 | User Channel 2 Active Power | P_s002_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8616 | User Channel 2 Reactive Power | Q_s002_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8618 | User Channel 2 Apparent Power | S_s002_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8620 | User Channel 2 Load Nature | LC_s002 |  |  | uint32 | R | 2 | 1
8622 | User Channel 2 Power Factor | PF_s002 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8624 | User Channel 3 Current | I_s003_A | A | I_s003_%修改为I_s003_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8626 | User Channel 3 Active Power | P_s003_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8628 | User Channel 3 Reactive Power | Q_s003_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8630 | User Channel 3 Apparent Power | S_s003_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8632 | User Channel 3 Load Nature | LC_s003 |  |  | uint32 | R | 2 | 1
8634 | User Channel 3 Power Factor | PF_s003 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8636 | User Channel 4 Current | I_s004_A | A | I_s004_%修改为I_s004_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8638 | User Channel 4 Active Power | P_s004_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8640 | User Channel 4 Reactive Power | Q_s004_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8642 | User Channel 4 Apparent Power | S_s004_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8644 | User Channel 4 Load Nature | LC_s004 |  |  | uint32 | R | 2 | 1
8646 | User Channel 4 Power Factor | PF_s004 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8648 | User Channel 5 Current | I_s005_A | A | I_s005_%修改为I_s005_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8650 | User Channel 5 Active Power | P_s005_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8652 | User Channel 5 Reactive Power | Q_s005_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8654 | User Channel 5 Apparent Power | S_s005_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8656 | User Channel 5 Load Nature | LC_s005 |  |  | uint32 | R | 2 | 1
8658 | User Channel 5 Power Factor | PF_s005 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8660 | User Channel 6 Current | I_s006_A | A | I_s006_%修改为I_s006_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8662 | User Channel 6 Active Power | P_s006_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8664 | User Channel 6 Reactive Power | Q_s006_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8666 | User Channel 6 Apparent Power | S_s006_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8668 | User Channel 6 Load Nature | LC_s006 |  |  | uint32 | R | 2 | 1
8670 | User Channel 6 Power Factor | PF_s006 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8672 | User Channel 7 Current | I_s007_A | A | I_s007_%修改为I_s007_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8674 | User Channel 7 Active Power | P_s007_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8676 | User Channel 7 Reactive Power | Q_s007_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8678 | User Channel 7 Apparent Power | S_s007_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8680 | User Channel 7 Load Nature | LC_s007 |  |  | uint32 | R | 2 | 1
8682 | User Channel 7 Power Factor | PF_s007 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8684 | User Channel 8 Current | I_s008_A | A | I_s008_%修改为I_s008_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8686 | User Channel 8 Active Power | P_s008_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8688 | User Channel 8 Reactive Power | Q_s008_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8690 | User Channel 8 Apparent Power | S_s008_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8692 | User Channel 8 Load Nature | LC_s008 |  |  | uint32 | R | 2 | 1
8694 | User Channel 8 Power Factor | PF_s008 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8696 | User Channel 9 Current | I_s009_A | A | I_s009_%修改为I_s009_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8698 | User Channel 9 Active Power | P_s009_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8700 | User Channel 9 Reactive Power | Q_s009_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8702 | User Channel 9 Apparent Power | S_s009_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8704 | User Channel 9 Load Nature | LC_s009 |  |  | uint32 | R | 2 | 1
8706 | User Channel 9 Power Factor | PF_s009 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8708 | User Channel 10 Current | I_s010_A | A | I_s010_%修改为I_s010_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8710 | User Channel 10 Active Power | P_s010_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8712 | User Channel 10 Reactive Power | Q_s010_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8714 | User Channel 10 Apparent Power | S_s010_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8716 | User Channel 10 Load Nature | LC_s010 |  |  | uint32 | R | 2 | 1
8718 | User Channel 10 Power Factor | PF_s010 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8720 | User Channel 11 Current | I_s011_A | A | I_s011_%修改为I_s011_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8722 | User Channel 11 Active Power | P_s011_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8724 | User Channel 11 Reactive Power | Q_s011_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8726 | User Channel 11 Apparent Power | S_s011_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8728 | User Channel 11 Load Nature | LC_s011 |  |  | uint32 | R | 2 | 1
8730 | User Channel 11 Power Factor | PF_s011 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8732 | User Channel 12 Current | I_s012_A | A | I_s012_%修改为I_s012_A | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8734 | User Channel 12 Active Power | P_s012_kW | kW |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8736 | User Channel 12 Reactive Power | Q_s012_kvar | kvar |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8738 | User Channel 12 Apparent Power | S_s012_kVA | kVA |  | float32 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8740 | User Channel 12 Load Nature | LC_s012 |  |  | uint32 | R | 2 | 1
8742 | User Channel 12 Power Factor | PF_s012 |  | 删除单位 | float32 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8960 | Phase A Current Demand | DMD_I_a_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8962 | Phase A Import Active Power Demand | DMD_IMP_P_a_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8964 | Phase A Export Active Power Demand | DMD_EXP_P_a_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8966 | Phase A Import Reactive Power Demand | DMD_IMP_Q_a_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8968 | Phase A Export Reactive Power Demand | DMD_EXP_Q_a_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8970 | Phase A Apparent Power Demand | DMD_S_a_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8972 | Phase B Current Demand | DMD_I_b_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8974 | Phase B Import Active Power Demand | DMD_IMP_P_b_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8976 | Phase B Export Active Power Demand | DMD_EXP_P_b_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8978 | Phase B Import Reactive Power Demand | DMD_IMP_Q_b_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8980 | Phase B Export Reactive Power Demand | DMD_EXP_Q_b_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8982 | Phase B Apparent Power Demand | DMD_S_b_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8984 | Phase C Current Demand | DMD_I_c_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8986 | Phase C Import Active Power Demand | DMD_IMP_P_c_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8988 | Phase C Export Active Power Demand | DMD_EXP_P_c_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8990 | Phase C Import Reactive Power Demand | DMD_IMP_Q_c_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8992 | Phase C Export Reactive Power Demand | DMD_EXP_Q_c_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8994 | Phase C Apparent Power Demand | DMD_S_c_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8996 | System Average Current Demand | DMD_I_avg_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
8998 | System Import Active Power Demand | DMD_IMP_P_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9000 | System Export Active Power Demand | DMD_EXP_P_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9002 | System Import Reactive Power Demand | DMD_IMP_Q_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9004 | System Export Reactive Power Demand | DMD_EXP_Q_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9006 | System Apparent Power Demand | DMD_S_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9008 | Input Channel 1 Current Demand | DMD_I_001_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9010 | Input Channel 1 Import Active Power Demand | DMD_IMP_P_001_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9012 | Input Channel 1 Export Active Power Demand | DMD_EXP_P_001_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9014 | Input Channel 1 Import Reactive Power Demand | DMD_IMP_Q_001_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9016 | Input Channel 1 Export Reactive Power Demand | DMD_EXP_Q_001_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9018 | Input Channel 1 Apparent Power Demand | DMD_S_001_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9020 | Input Channel 2 Current Demand | DMD_I_002_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9022 | Input Channel 2 Import Active Power Demand | DMD_IMP_P_002_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9024 | Input Channel 2 Export Active Power Demand | DMD_EXP_P_002_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9026 | Input Channel 2 Import Reactive Power Demand | DMD_IMP_Q_002_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9028 | Input Channel 2 Export Reactive Power Demand | DMD_EXP_Q_002_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9030 | Input Channel 2 Apparent Power Demand | DMD_S_002_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9032 | Input Channel 3 Current Demand | DMD_I_003_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9034 | Input Channel 3 Import Active Power Demand | DMD_IMP_P_003_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9036 | Input Channel 3 Export Active Power Demand | DMD_EXP_P_003_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9038 | Input Channel 3 Import Reactive Power Demand | DMD_IMP_Q_003_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9040 | Input Channel 3 Export Reactive Power Demand | DMD_EXP_Q_003_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9042 | Input Channel 3 Apparent Power Demand | DMD_S_003_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9044 | Input Channel 4 Current Demand | DMD_I_004_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9046 | Input Channel 4 Import Active Power Demand | DMD_IMP_P_004_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9048 | Input Channel 4 Export Active Power Demand | DMD_EXP_P_004_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9050 | Input Channel 4 Import Reactive Power Demand | DMD_IMP_Q_004_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9052 | Input Channel 4 Export Reactive Power Demand | DMD_EXP_Q_004_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9054 | Input Channel 4 Apparent Power Demand | DMD_S_004_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9056 | Input Channel 5 Current Demand | DMD_I_005_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9058 | Input Channel 5 Import Active Power Demand | DMD_IMP_P_005_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9060 | Input Channel 5 Export Active Power Demand | DMD_EXP_P_005_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9062 | Input Channel 5 Import Reactive Power Demand | DMD_IMP_Q_005_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9064 | Input Channel 5 Export Reactive Power Demand | DMD_EXP_Q_005_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9066 | Input Channel 5 Apparent Power Demand | DMD_S_005_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9068 | Input Channel 6 Current Demand | DMD_I_006_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9070 | Input Channel 6 Import Active Power Demand | DMD_IMP_P_006_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9072 | Input Channel 6 Export Active Power Demand | DMD_EXP_P_006_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9074 | Input Channel 6 Import Reactive Power Demand | DMD_IMP_Q_006_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9076 | Input Channel 6 Export Reactive Power Demand | DMD_EXP_Q_006_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9078 | Input Channel 6 Apparent Power Demand | DMD_S_006_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9080 | Input Channel 7 Current Demand | DMD_I_007_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9082 | Input Channel 7 Import Active Power Demand | DMD_IMP_P_007_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9084 | Input Channel 7 Export Active Power Demand | DMD_EXP_P_007_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9086 | Input Channel 7 Import Reactive Power Demand | DMD_IMP_Q_007_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9088 | Input Channel 7 Export Reactive Power Demand | DMD_EXP_Q_007_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9090 | Input Channel 7 Apparent Power Demand | DMD_S_007_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9092 | Input Channel 8 Current Demand | DMD_I_008_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9094 | Input Channel 8 Import Active Power Demand | DMD_IMP_P_008_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9096 | Input Channel 8 Export Active Power Demand | DMD_EXP_P_008_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9098 | Input Channel 8 Import Reactive Power Demand | DMD_IMP_Q_008_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9100 | Input Channel 8 Export Reactive Power Demand | DMD_EXP_Q_008_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9102 | Input Channel 8 Apparent Power Demand | DMD_S_008_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9104 | Input Channel 9 Current Demand | DMD_I_009_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9106 | Input Channel 9 Import Active Power Demand | DMD_IMP_P_009_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9108 | Input Channel 9 Export Active Power Demand | DMD_EXP_P_009_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9110 | Input Channel 9 Import Reactive Power Demand | DMD_IMP_Q_009_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9112 | Input Channel 9 Export Reactive Power Demand | DMD_EXP_Q_009_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9114 | Input Channel 9 Apparent Power Demand | DMD_S_009_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9116 | Input Channel 10 Current Demand | DMD_I_010_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9118 | Input Channel 10 Import Active Power Demand | DMD_IMP_P_010_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9120 | Input Channel 10 Export Active Power Demand | DMD_EXP_P_010_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9122 | Input Channel 10 Import Reactive Power Demand | DMD_IMP_Q_010_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9124 | Input Channel 10 Export Reactive Power Demand | DMD_EXP_Q_010_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9126 | Input Channel 10 Apparent Power Demand | DMD_S_010_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9128 | Input Channel 11 Current Demand | DMD_I_011_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9130 | Input Channel 11 Import Active Power Demand | DMD_IMP_P_011_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9132 | Input Channel 11 Export Active Power Demand | DMD_EXP_P_011_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9134 | Input Channel 11 Import Reactive Power Demand | DMD_IMP_Q_011_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9136 | Input Channel 11 Export Reactive Power Demand | DMD_EXP_Q_011_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9138 | Input Channel 11 Apparent Power Demand | DMD_S_011_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9140 | Input Channel 12 Current Demand | DMD_I_012_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9142 | Input Channel 12 Import Active Power Demand | DMD_IMP_P_012_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9144 | Input Channel 12 Export Active Power Demand | DMD_EXP_P_012_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9146 | Input Channel 12 Import Reactive Power Demand | DMD_IMP_Q_012_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9148 | Input Channel 12 Export Reactive Power Demand | DMD_EXP_Q_012_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9150 | Input Channel 12 Apparent Power Demand | DMD_S_012_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9152 | Input Channel 13 Current Demand | DMD_I_013_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9154 | Input Channel 13 Import Active Power Demand | DMD_IMP_P_013_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9156 | Input Channel 13 Export Active Power Demand | DMD_EXP_P_013_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9158 | Input Channel 13 Import Reactive Power Demand | DMD_IMP_Q_013_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9160 | Input Channel 13 Export Reactive Power Demand | DMD_EXP_Q_013_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9162 | Input Channel 13 Apparent Power Demand | DMD_S_013_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9164 | Input Channel 14 Current Demand | DMD_I_014_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9166 | Input Channel 14 Import Active Power Demand | DMD_IMP_P_014_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9168 | Input Channel 14 Export Active Power Demand | DMD_EXP_P_014_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9170 | Input Channel 14 Import Reactive Power Demand | DMD_IMP_Q_014_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9172 | Input Channel 14 Export Reactive Power Demand | DMD_EXP_Q_014_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9174 | Input Channel 14 Apparent Power Demand | DMD_S_014_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9176 | Input Channel 15 Current Demand | DMD_I_015_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9178 | Input Channel 15 Import Active Power Demand | DMD_IMP_P_015_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9180 | Input Channel 15 Export Active Power Demand | DMD_EXP_P_015_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9182 | Input Channel 15 Import Reactive Power Demand | DMD_IMP_Q_015_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9184 | Input Channel 15 Export Reactive Power Demand | DMD_EXP_Q_015_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9186 | Input Channel 15 Apparent Power Demand | DMD_S_015_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9188 | Input Channel 16 Current Demand | DMD_I_016_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9190 | Input Channel 16 Import Active Power Demand | DMD_IMP_P_016_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9192 | Input Channel 16 Export Active Power Demand | DMD_EXP_P_016_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9194 | Input Channel 16 Import Reactive Power Demand | DMD_IMP_Q_016_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9196 | Input Channel 16 Export Reactive Power Demand | DMD_EXP_Q_016_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9198 | Input Channel 16 Apparent Power Demand | DMD_S_016_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9200 | Input Channel 17 Current Demand | DMD_I_017_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9202 | Input Channel 17 Import Active Power Demand | DMD_IMP_P_017_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9204 | Input Channel 17 Export Active Power Demand | DMD_EXP_P_017_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9206 | Input Channel 17 Import Reactive Power Demand | DMD_IMP_Q_017_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9208 | Input Channel 17 Export Reactive Power Demand | DMD_EXP_Q_017_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9210 | Input Channel 17 Apparent Power Demand | DMD_S_017_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9212 | Input Channel 18 Current Demand | DMD_I_018_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9214 | Input Channel 18 Import Active Power Demand | DMD_IMP_P_018_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9216 | Input Channel 18 Export Active Power Demand | DMD_EXP_P_018_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9218 | Input Channel 18 Import Reactive Power Demand | DMD_IMP_Q_018_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9220 | Input Channel 18 Export Reactive Power Demand | DMD_EXP_Q_018_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9222 | Input Channel 18 Apparent Power Demand | DMD_S_018_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9224 | Input Channel 19 Current Demand | DMD_I_019_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9226 | Input Channel 19 Import Active Power Demand | DMD_IMP_P_019_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9228 | Input Channel 19 Export Active Power Demand | DMD_EXP_P_019_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9230 | Input Channel 19 Import Reactive Power Demand | DMD_IMP_Q_019_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9232 | Input Channel 19 Export Reactive Power Demand | DMD_EXP_Q_019_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9234 | Input Channel 19 Apparent Power Demand | DMD_S_019_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9236 | Input Channel 20 Current Demand | DMD_I_020_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9238 | Input Channel 20 Import Active Power Demand | DMD_IMP_P_020_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9240 | Input Channel 20 Export Active Power Demand | DMD_EXP_P_020_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9242 | Input Channel 20 Import Reactive Power Demand | DMD_IMP_Q_020_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9244 | Input Channel 20 Export Reactive Power Demand | DMD_EXP_Q_020_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9246 | Input Channel 20 Apparent Power Demand | DMD_S_020_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9248 | Input Channel 21 Current Demand | DMD_I_021_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9250 | Input Channel 21 Import Active Power Demand | DMD_IMP_P_021_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9252 | Input Channel 21 Export Active Power Demand | DMD_EXP_P_021_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9254 | Input Channel 21 Import Reactive Power Demand | DMD_IMP_Q_021_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9256 | Input Channel 21 Export Reactive Power Demand | DMD_EXP_Q_021_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9258 | Input Channel 21 Apparent Power Demand | DMD_S_021_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9260 | Input Channel 22 Current Demand | DMD_I_022_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9262 | Input Channel 22 Import Active Power Demand | DMD_IMP_P_022_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9264 | Input Channel 22 Export Active Power Demand | DMD_EXP_P_022_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9266 | Input Channel 22 Import Reactive Power Demand | DMD_IMP_Q_022_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9268 | Input Channel 22 Export Reactive Power Demand | DMD_EXP_Q_022_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9270 | Input Channel 22 Apparent Power Demand | DMD_S_022_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9272 | Input Channel 23 Current Demand | DMD_I_023_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9274 | Input Channel 23 Import Active Power Demand | DMD_IMP_P_023_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9276 | Input Channel 23 Export Active Power Demand | DMD_EXP_P_023_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9278 | Input Channel 23 Import Reactive Power Demand | DMD_IMP_Q_023_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9280 | Input Channel 23 Export Reactive Power Demand | DMD_EXP_Q_023_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9282 | Input Channel 23 Apparent Power Demand | DMD_S_023_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9284 | Input Channel 24 Current Demand | DMD_I_024_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9286 | Input Channel 24 Import Active Power Demand | DMD_IMP_P_024_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9288 | Input Channel 24 Export Active Power Demand | DMD_EXP_P_024_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9290 | Input Channel 24 Import Reactive Power Demand | DMD_IMP_Q_024_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9292 | Input Channel 24 Export Reactive Power Demand | DMD_EXP_Q_024_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9294 | Input Channel 24 Apparent Power Demand | DMD_S_024_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9296 | User Channel 1 Current Demand | DMD_I_s001_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9298 | User Channel 1 Import Active Power Demand | DMD_IMP_P_s001_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9300 | User Channel 1 Export Active Power Demand | DMD_EXP_P_s001_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9302 | User Channel 1 Import Reactive Power Demand | DMD_IMP_Q_s001_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9304 | User Channel 1 Export Reactive Power Demand | DMD_EXP_Q_s001_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9306 | User Channel 1 Apparent Power Demand | DMD_S_s001_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9308 | User Channel 2 Current Demand | DMD_I_s002_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9310 | User Channel 2 Import Active Power Demand | DMD_IMP_P_s002_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9312 | User Channel 2 Export Active Power Demand | DMD_EXP_P_s002_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9314 | User Channel 2 Import Reactive Power Demand | DMD_IMP_Q_s002_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9316 | User Channel 2 Export Reactive Power Demand | DMD_EXP_Q_s002_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9318 | User Channel 2 Apparent Power Demand | DMD_S_s002_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9320 | User Channel 3 Current Demand | DMD_I_s003_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9322 | User Channel 3 Import Active Power Demand | DMD_IMP_P_s003_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9324 | User Channel 3 Export Active Power Demand | DMD_EXP_P_s003_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9326 | User Channel 3 Import Reactive Power Demand | DMD_IMP_Q_s003_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9328 | User Channel 3 Export Reactive Power Demand | DMD_EXP_Q_s003_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9330 | User Channel 3 Apparent Power Demand | DMD_S_s003_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9332 | User Channel 4 Current Demand | DMD_I_s004_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9334 | User Channel 4 Import Active Power Demand | DMD_IMP_P_s004_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9336 | User Channel 4 Export Active Power Demand | DMD_EXP_P_s004_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9338 | User Channel 4 Import Reactive Power Demand | DMD_IMP_Q_s004_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9340 | User Channel 4 Export Reactive Power Demand | DMD_EXP_Q_s004_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9342 | User Channel 4 Apparent Power Demand | DMD_S_s004_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9344 | User Channel 5 Current Demand | DMD_I_s005_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9346 | User Channel 5 Import Active Power Demand | DMD_IMP_P_s005_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9348 | User Channel 5 Export Active Power Demand | DMD_EXP_P_s005_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9350 | User Channel 5 Import Reactive Power Demand | DMD_IMP_Q_s005_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9352 | User Channel 5 Export Reactive Power Demand | DMD_EXP_Q_s005_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9354 | User Channel 5 Apparent Power Demand | DMD_S_s005_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9356 | User Channel 6 Current Demand | DMD_I_s006_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9358 | User Channel 6 Import Active Power Demand | DMD_IMP_P_s006_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9360 | User Channel 6 Export Active Power Demand | DMD_EXP_P_s006_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9362 | User Channel 6 Import Reactive Power Demand | DMD_IMP_Q_s006_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9364 | User Channel 6 Export Reactive Power Demand | DMD_EXP_Q_s006_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9366 | User Channel 6 Apparent Power Demand | DMD_S_s006_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9368 | User Channel 7 Current Demand | DMD_I_s007_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9370 | User Channel 7 Import Active Power Demand | DMD_IMP_P_s007_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9372 | User Channel 7 Export Active Power Demand | DMD_EXP_P_s007_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9374 | User Channel 7 Import Reactive Power Demand | DMD_IMP_Q_s007_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9376 | User Channel 7 Export Reactive Power Demand | DMD_EXP_Q_s007_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9378 | User Channel 7 Apparent Power Demand | DMD_S_s007_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9380 | User Channel 8 Current Demand | DMD_I_s008_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9382 | User Channel 8 Import Active Power Demand | DMD_IMP_P_s008_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9384 | User Channel 8 Export Active Power Demand | DMD_EXP_P_s008_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9386 | User Channel 8 Import Reactive Power Demand | DMD_IMP_Q_s008_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9388 | User Channel 8 Export Reactive Power Demand | DMD_EXP_Q_s008_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9390 | User Channel 8 Apparent Power Demand | DMD_S_s008_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9392 | User Channel 9 Current Demand | DMD_I_s009_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9394 | User Channel 9 Import Active Power Demand | DMD_IMP_P_s009_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9396 | User Channel 9 Export Active Power Demand | DMD_EXP_P_s009_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9398 | User Channel 9 Import Reactive Power Demand | DMD_IMP_Q_s009_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9400 | User Channel 9 Export Reactive Power Demand | DMD_EXP_Q_s009_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9402 | User Channel 9 Apparent Power Demand | DMD_S_s009_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9404 | User Channel 10 Current Demand | DMD_I_s010_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9406 | User Channel 10 Import Active Power Demand | DMD_IMP_P_s010_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9408 | User Channel 10 Export Active Power Demand | DMD_EXP_P_s010_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9410 | User Channel 10 Import Reactive Power Demand | DMD_IMP_Q_s010_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9412 | User Channel 10 Export Reactive Power Demand | DMD_EXP_Q_s010_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9414 | User Channel 10 Apparent Power Demand | DMD_S_s010_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9416 | User Channel 11 Current Demand | DMD_I_s011_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9418 | User Channel 11 Import Active Power Demand | DMD_IMP_P_s011_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9420 | User Channel 11 Export Active Power Demand | DMD_EXP_P_s011_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9422 | User Channel 11 Import Reactive Power Demand | DMD_IMP_Q_s011_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9424 | User Channel 11 Export Reactive Power Demand | DMD_EXP_Q_s011_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9426 | User Channel 11 Apparent Power Demand | DMD_S_s011_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9428 | User Channel 12 Current Demand | DMD_I_s012_A | A |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9430 | User Channel 12 Import Active Power Demand | DMD_IMP_P_s012_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9432 | User Channel 12 Export Active Power Demand | DMD_EXP_P_s012_kW | kW |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9434 | User Channel 12 Import Reactive Power Demand | DMD_IMP_Q_s012_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9436 | User Channel 12 Export Reactive Power Demand | DMD_EXP_Q_s012_kvar | kvar |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9438 | User Channel 12 Apparent Power Demand | DMD_S_s012_kVA | kVA |  | float32 | R | 2 | 1 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
9728 | Voltage Positive Sequence Magnitude | MAG_SEQ_POS_V | V |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
9730 | Voltage Zero Sequence Magnitude | MAG_SEQ_ZERO_V | V |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
9732 | Voltage Negative Sequence Magnitude | MAG_SEQ_NEG_V | V |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
9734 | Voltage Positive Sequence Angle | ANG_SEQ_POS_V | ° |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
9736 | Voltage Zero Sequence Angle | ANG_SEQ_ZERO_V | ° |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
9738 | Voltage Negative Sequence Angle | ANG_SEQ_NEG_V | ° |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
9740 | Voltage Unbalance Factor Magnitude | UNBL_V_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
9742 | Phase A Voltage THD | THD_V_a_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9744 | Phase A Voltage THD Odd | OTHD_V_a_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9746 | Phase A Voltage THD Even | ETHD_V_a_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9748 | Phase A Voltage Crest Factor | CF_V_a_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9750 | Phase A Voltage THFF Factor | THFF_V_a_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9752 | Phase A Voltage individual Harmonics 2 percentage | HAR2_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9754 | Phase A Voltage individual Harmonics 3 percentage | HAR3_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9756 | Phase A Voltage individual Harmonics 4 percentage | HAR4_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9758 | Phase A Voltage individual Harmonics 5 percentage | HAR5_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9760 | Phase A Voltage individual Harmonics 6 percentage | HAR6_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9762 | Phase A Voltage individual Harmonics 7 percentage | HAR7_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9764 | Phase A Voltage individual Harmonics 8 percentage | HAR8_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9766 | Phase A Voltage individual Harmonics 9 percentage | HAR9_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9768 | Phase A Voltage individual Harmonics 10 percentage | HAR10_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9770 | Phase A Voltage individual Harmonics 11 percentage | HAR11_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9772 | Phase A Voltage individual Harmonics 12 percentage | HAR12_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9774 | Phase A Voltage individual Harmonics 13 percentage | HAR13_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9776 | Phase A Voltage individual Harmonics 14 percentage | HAR14_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9778 | Phase A Voltage individual Harmonics 15 percentage | HAR15_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9780 | Phase A Voltage individual Harmonics 16 percentage | HAR16_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9782 | Phase A Voltage individual Harmonics 17 percentage | HAR17_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9784 | Phase A Voltage individual Harmonics 18 percentage | HAR18_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9786 | Phase A Voltage individual Harmonics 19 percentage | HAR19_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9788 | Phase A Voltage individual Harmonics 20 percentage | HAR20_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9790 | Phase A Voltage individual Harmonics 21 percentage | HAR21_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9792 | Phase A Voltage individual Harmonics 22 percentage | HAR22_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9794 | Phase A Voltage individual Harmonics 23 percentage | HAR23_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9796 | Phase A Voltage individual Harmonics 24 percentage | HAR24_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9798 | Phase A Voltage individual Harmonics 25 percentage | HAR25_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9800 | Phase A Voltage individual Harmonics 26 percentage | HAR26_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9802 | Phase A Voltage individual Harmonics 27 percentage | HAR27_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9804 | Phase A Voltage individual Harmonics 28 percentage | HAR28_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9806 | Phase A Voltage individual Harmonics 29 percentage | HAR29_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9808 | Phase A Voltage individual Harmonics 30 percentage | HAR30_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9810 | Phase A Voltage individual Harmonics 31 percentage | HAR31_V_a_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9812 | Phase B Voltage THD | THD_V_b_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9814 | Phase B Voltage THD Odd | OTHD_V_b_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9816 | Phase B Voltage THD Even | ETHD_V_b_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9818 | Phase B Voltage Crest Factor | CF_V_b_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9820 | Phase B Voltage THFF Factor | THFF_V_b_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9822 | Phase B Voltage individual Harmonics 2 percentage | HAR2_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9824 | Phase B Voltage individual Harmonics 3 percentage | HAR3_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9826 | Phase B Voltage individual Harmonics 4 percentage | HAR4_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9828 | Phase B Voltage individual Harmonics 5 percentage | HAR5_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9830 | Phase B Voltage individual Harmonics 6 percentage | HAR6_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9832 | Phase B Voltage individual Harmonics 7 percentage | HAR7_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9834 | Phase B Voltage individual Harmonics 8 percentage | HAR8_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9836 | Phase B Voltage individual Harmonics 9 percentage | HAR9_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9838 | Phase B Voltage individual Harmonics 10 percentage | HAR10_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9840 | Phase B Voltage individual Harmonics 11 percentage | HAR11_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9842 | Phase B Voltage individual Harmonics 12 percentage | HAR12_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9844 | Phase B Voltage individual Harmonics 13 percentage | HAR13_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9846 | Phase B Voltage individual Harmonics 14 percentage | HAR14_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9848 | Phase B Voltage individual Harmonics 15 percentage | HAR15_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9850 | Phase B Voltage individual Harmonics 16 percentage | HAR16_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9852 | Phase B Voltage individual Harmonics 17 percentage | HAR17_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9854 | Phase B Voltage individual Harmonics 18 percentage | HAR18_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9856 | Phase B Voltage individual Harmonics 19 percentage | HAR19_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9858 | Phase B Voltage individual Harmonics 20 percentage | HAR20_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9860 | Phase B Voltage individual Harmonics 21 percentage | HAR21_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9862 | Phase B Voltage individual Harmonics 22 percentage | HAR22_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9864 | Phase B Voltage individual Harmonics 23 percentage | HAR23_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9866 | Phase B Voltage individual Harmonics 24 percentage | HAR24_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9868 | Phase B Voltage individual Harmonics 25 percentage | HAR25_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9870 | Phase B Voltage individual Harmonics 26 percentage | HAR26_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9872 | Phase B Voltage individual Harmonics 27 percentage | HAR27_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9874 | Phase B Voltage individual Harmonics 28 percentage | HAR28_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9876 | Phase B Voltage individual Harmonics 29 percentage | HAR29_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9878 | Phase B Voltage individual Harmonics 30 percentage | HAR30_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9880 | Phase B Voltage individual Harmonics 31 percentage | HAR31_V_b_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9882 | Phase C Voltage THD | THD_V_c_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9884 | Phase C Voltage THD Odd | OTHD_V_c_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9886 | Phase C Voltage THD Even | ETHD_V_c_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9888 | Phase C Voltage Crest Factor | CF_V_c_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9890 | Phase C Voltage THFF Factor | THFF_V_c_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9892 | Phase C Voltage individual Harmonics 2 percentage | HAR2_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9894 | Phase C Voltage individual Harmonics 3 percentage | HAR3_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9896 | Phase C Voltage individual Harmonics 4 percentage | HAR4_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9898 | Phase C Voltage individual Harmonics 5 percentage | HAR5_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9900 | Phase C Voltage individual Harmonics 6 percentage | HAR6_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9902 | Phase C Voltage individual Harmonics 7 percentage | HAR7_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9904 | Phase C Voltage individual Harmonics 8 percentage | HAR8_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9906 | Phase C Voltage individual Harmonics 9 percentage | HAR9_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9908 | Phase C Voltage individual Harmonics 10 percentage | HAR10_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9910 | Phase C Voltage individual Harmonics 11 percentage | HAR11_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9912 | Phase C Voltage individual Harmonics 12 percentage | HAR12_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9914 | Phase C Voltage individual Harmonics 13 percentage | HAR13_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9916 | Phase C Voltage individual Harmonics 14 percentage | HAR14_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9918 | Phase C Voltage individual Harmonics 15 percentage | HAR15_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9920 | Phase C Voltage individual Harmonics 16 percentage | HAR16_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9922 | Phase C Voltage individual Harmonics 17 percentage | HAR17_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9924 | Phase C Voltage individual Harmonics 18 percentage | HAR18_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9926 | Phase C Voltage individual Harmonics 19 percentage | HAR19_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9928 | Phase C Voltage individual Harmonics 20 percentage | HAR20_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9930 | Phase C Voltage individual Harmonics 21 percentage | HAR21_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9932 | Phase C Voltage individual Harmonics 22 percentage | HAR22_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9934 | Phase C Voltage individual Harmonics 23 percentage | HAR23_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9936 | Phase C Voltage individual Harmonics 24 percentage | HAR24_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9938 | Phase C Voltage individual Harmonics 25 percentage | HAR25_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9940 | Phase C Voltage individual Harmonics 26 percentage | HAR26_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9942 | Phase C Voltage individual Harmonics 27 percentage | HAR27_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9944 | Phase C Voltage individual Harmonics 28 percentage | HAR28_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9946 | Phase C Voltage individual Harmonics 29 percentage | HAR29_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9948 | Phase C Voltage individual Harmonics 30 percentage | HAR30_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9950 | Phase C Voltage individual Harmonics 31 percentage | HAR31_V_c_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9952 | Average Voltage THD | THD_V_avg_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9954 | Average Voltage THD Odd | OTHD_V_avg_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9956 | Average Voltage THD Even | ETHD_V_avg_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9958 | Input Channel 1 Current THD | THD_I_001_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9960 | Input Channel 1 Current THD Odd | OTHD_I_001_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9962 | Input Channel 1 Current THD Even | ETHD_I_001_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9964 | Input Channel 1 Current K Factor | KF_I_001_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
9966 | Input Channel 1 Current individual Harmonics 2 percentage | HAR2_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9968 | Input Channel 1 Current individual Harmonics 3 percentage | HAR3_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9970 | Input Channel 1 Current individual Harmonics 4 percentage | HAR4_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9972 | Input Channel 1 Current individual Harmonics 5 percentage | HAR5_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9974 | Input Channel 1 Current individual Harmonics 6 percentage | HAR6_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9976 | Input Channel 1 Current individual Harmonics 7 percentage | HAR7_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9978 | Input Channel 1 Current individual Harmonics 8 percentage | HAR8_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9980 | Input Channel 1 Current individual Harmonics 9 percentage | HAR9_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9982 | Input Channel 1 Current individual Harmonics 10 percentage | HAR10_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9984 | Input Channel 1 Current individual Harmonics 11 percentage | HAR11_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9986 | Input Channel 1 Current individual Harmonics 12 percentage | HAR12_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9988 | Input Channel 1 Current individual Harmonics 13 percentage | HAR13_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9990 | Input Channel 1 Current individual Harmonics 14 percentage | HAR14_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9992 | Input Channel 1 Current individual Harmonics 15 percentage | HAR15_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9994 | Input Channel 1 Current individual Harmonics 16 percentage | HAR16_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9996 | Input Channel 1 Current individual Harmonics 17 percentage | HAR17_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
9998 | Input Channel 1 Current individual Harmonics 18 percentage | HAR18_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10000 | Input Channel 1 Current individual Harmonics 19 percentage | HAR19_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10002 | Input Channel 1 Current individual Harmonics 20 percentage | HAR20_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10004 | Input Channel 1 Current individual Harmonics 21 percentage | HAR21_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10006 | Input Channel 1 Current individual Harmonics 22 percentage | HAR22_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10008 | Input Channel 1 Current individual Harmonics 23 percentage | HAR23_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10010 | Input Channel 1 Current individual Harmonics 24 percentage | HAR24_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10012 | Input Channel 1 Current individual Harmonics 25 percentage | HAR25_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10014 | Input Channel 1 Current individual Harmonics 26 percentage | HAR26_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10016 | Input Channel 1 Current individual Harmonics 27 percentage | HAR27_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10018 | Input Channel 1 Current individual Harmonics 28 percentage | HAR28_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10020 | Input Channel 1 Current individual Harmonics 29 percentage | HAR29_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10022 | Input Channel 1 Current individual Harmonics 30 percentage | HAR30_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10024 | Input Channel 1 Current individual Harmonics 31 percentage | HAR31_I_001_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10026 | Input Channel 2 Current THD | THD_I_002_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10028 | Input Channel 2 Current THD Odd | OTHD_I_002_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10030 | Input Channel 2 Current THD Even | ETHD_I_002_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10032 | Input Channel 2 Current K Factor | KF_I_002_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10034 | Input Channel 2 Current individual Harmonics 2 percentage | HAR2_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10036 | Input Channel 2 Current individual Harmonics 3 percentage | HAR3_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10038 | Input Channel 2 Current individual Harmonics 4 percentage | HAR4_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10040 | Input Channel 2 Current individual Harmonics 5 percentage | HAR5_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10042 | Input Channel 2 Current individual Harmonics 6 percentage | HAR6_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10044 | Input Channel 2 Current individual Harmonics 7 percentage | HAR7_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10046 | Input Channel 2 Current individual Harmonics 8 percentage | HAR8_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10048 | Input Channel 2 Current individual Harmonics 9 percentage | HAR9_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10050 | Input Channel 2 Current individual Harmonics 10 percentage | HAR10_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10052 | Input Channel 2 Current individual Harmonics 11 percentage | HAR11_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10054 | Input Channel 2 Current individual Harmonics 12 percentage | HAR12_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10056 | Input Channel 2 Current individual Harmonics 13 percentage | HAR13_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10058 | Input Channel 2 Current individual Harmonics 14 percentage | HAR14_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10060 | Input Channel 2 Current individual Harmonics 15 percentage | HAR15_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10062 | Input Channel 2 Current individual Harmonics 16 percentage | HAR16_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10064 | Input Channel 2 Current individual Harmonics 17 percentage | HAR17_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10066 | Input Channel 2 Current individual Harmonics 18 percentage | HAR18_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10068 | Input Channel 2 Current individual Harmonics 19 percentage | HAR19_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10070 | Input Channel 2 Current individual Harmonics 20 percentage | HAR20_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10072 | Input Channel 2 Current individual Harmonics 21 percentage | HAR21_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10074 | Input Channel 2 Current individual Harmonics 22 percentage | HAR22_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10076 | Input Channel 2 Current individual Harmonics 23 percentage | HAR23_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10078 | Input Channel 2 Current individual Harmonics 24 percentage | HAR24_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10080 | Input Channel 2 Current individual Harmonics 25 percentage | HAR25_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10082 | Input Channel 2 Current individual Harmonics 26 percentage | HAR26_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10084 | Input Channel 2 Current individual Harmonics 27 percentage | HAR27_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10086 | Input Channel 2 Current individual Harmonics 28 percentage | HAR28_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10088 | Input Channel 2 Current individual Harmonics 29 percentage | HAR29_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10090 | Input Channel 2 Current individual Harmonics 30 percentage | HAR30_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10092 | Input Channel 2 Current individual Harmonics 31 percentage | HAR31_I_002_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10094 | Input Channel 3 Current THD | THD_I_003_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10096 | Input Channel 3 Current THD Odd | OTHD_I_003_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10098 | Input Channel 3 Current THD Even | ETHD_I_003_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10100 | Input Channel 3 Current K Factor | KF_I_003_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10102 | Input Channel 3 Current individual Harmonics 2 percentage | HAR2_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10104 | Input Channel 3 Current individual Harmonics 3 percentage | HAR3_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10106 | Input Channel 3 Current individual Harmonics 4 percentage | HAR4_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10108 | Input Channel 3 Current individual Harmonics 5 percentage | HAR5_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10110 | Input Channel 3 Current individual Harmonics 6 percentage | HAR6_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10112 | Input Channel 3 Current individual Harmonics 7 percentage | HAR7_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10114 | Input Channel 3 Current individual Harmonics 8 percentage | HAR8_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10116 | Input Channel 3 Current individual Harmonics 9 percentage | HAR9_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10118 | Input Channel 3 Current individual Harmonics 10 percentage | HAR10_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10120 | Input Channel 3 Current individual Harmonics 11 percentage | HAR11_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10122 | Input Channel 3 Current individual Harmonics 12 percentage | HAR12_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10124 | Input Channel 3 Current individual Harmonics 13 percentage | HAR13_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10126 | Input Channel 3 Current individual Harmonics 14 percentage | HAR14_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10128 | Input Channel 3 Current individual Harmonics 15 percentage | HAR15_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10130 | Input Channel 3 Current individual Harmonics 16 percentage | HAR16_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10132 | Input Channel 3 Current individual Harmonics 17 percentage | HAR17_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10134 | Input Channel 3 Current individual Harmonics 18 percentage | HAR18_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10136 | Input Channel 3 Current individual Harmonics 19 percentage | HAR19_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10138 | Input Channel 3 Current individual Harmonics 20 percentage | HAR20_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10140 | Input Channel 3 Current individual Harmonics 21 percentage | HAR21_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10142 | Input Channel 3 Current individual Harmonics 22 percentage | HAR22_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10144 | Input Channel 3 Current individual Harmonics 23 percentage | HAR23_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10146 | Input Channel 3 Current individual Harmonics 24 percentage | HAR24_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10148 | Input Channel 3 Current individual Harmonics 25 percentage | HAR25_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10150 | Input Channel 3 Current individual Harmonics 26 percentage | HAR26_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10152 | Input Channel 3 Current individual Harmonics 27 percentage | HAR27_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10154 | Input Channel 3 Current individual Harmonics 28 percentage | HAR28_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10156 | Input Channel 3 Current individual Harmonics 29 percentage | HAR29_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10158 | Input Channel 3 Current individual Harmonics 30 percentage | HAR30_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10160 | Input Channel 3 Current individual Harmonics 31 percentage | HAR31_I_003_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10162 | Input Channel 4 Current THD | THD_I_004_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10164 | Input Channel 4 Current THD Odd | OTHD_I_004_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10166 | Input Channel 4 Current THD Even | ETHD_I_004_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10168 | Input Channel 4 Current K Factor | KF_I_004_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10170 | Input Channel 4 Current individual Harmonics 2 percentage | HAR2_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10172 | Input Channel 4 Current individual Harmonics 3 percentage | HAR3_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10174 | Input Channel 4 Current individual Harmonics 4 percentage | HAR4_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10176 | Input Channel 4 Current individual Harmonics 5 percentage | HAR5_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10178 | Input Channel 4 Current individual Harmonics 6 percentage | HAR6_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10180 | Input Channel 4 Current individual Harmonics 7 percentage | HAR7_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10182 | Input Channel 4 Current individual Harmonics 8 percentage | HAR8_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10184 | Input Channel 4 Current individual Harmonics 9 percentage | HAR9_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10186 | Input Channel 4 Current individual Harmonics 10 percentage | HAR10_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10188 | Input Channel 4 Current individual Harmonics 11 percentage | HAR11_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10190 | Input Channel 4 Current individual Harmonics 12 percentage | HAR12_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10192 | Input Channel 4 Current individual Harmonics 13 percentage | HAR13_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10194 | Input Channel 4 Current individual Harmonics 14 percentage | HAR14_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10196 | Input Channel 4 Current individual Harmonics 15 percentage | HAR15_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10198 | Input Channel 4 Current individual Harmonics 16 percentage | HAR16_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10200 | Input Channel 4 Current individual Harmonics 17 percentage | HAR17_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10202 | Input Channel 4 Current individual Harmonics 18 percentage | HAR18_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10204 | Input Channel 4 Current individual Harmonics 19 percentage | HAR19_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10206 | Input Channel 4 Current individual Harmonics 20 percentage | HAR20_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10208 | Input Channel 4 Current individual Harmonics 21 percentage | HAR21_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10210 | Input Channel 4 Current individual Harmonics 22 percentage | HAR22_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10212 | Input Channel 4 Current individual Harmonics 23 percentage | HAR23_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10214 | Input Channel 4 Current individual Harmonics 24 percentage | HAR24_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10216 | Input Channel 4 Current individual Harmonics 25 percentage | HAR25_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10218 | Input Channel 4 Current individual Harmonics 26 percentage | HAR26_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10220 | Input Channel 4 Current individual Harmonics 27 percentage | HAR27_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10222 | Input Channel 4 Current individual Harmonics 28 percentage | HAR28_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10224 | Input Channel 4 Current individual Harmonics 29 percentage | HAR29_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10226 | Input Channel 4 Current individual Harmonics 30 percentage | HAR30_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10228 | Input Channel 4 Current individual Harmonics 31 percentage | HAR31_I_004_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10230 | Input Channel 5 Current THD | THD_I_005_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10232 | Input Channel 5 Current THD Odd | OTHD_I_005_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10234 | Input Channel 5 Current THD Even | ETHD_I_005_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10236 | Input Channel 5 Current K Factor | KF_I_005_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10238 | Input Channel 5 Current individual Harmonics 2 percentage | HAR2_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10240 | Input Channel 5 Current individual Harmonics 3 percentage | HAR3_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10242 | Input Channel 5 Current individual Harmonics 4 percentage | HAR4_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10244 | Input Channel 5 Current individual Harmonics 5 percentage | HAR5_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10246 | Input Channel 5 Current individual Harmonics 6 percentage | HAR6_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10248 | Input Channel 5 Current individual Harmonics 7 percentage | HAR7_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10250 | Input Channel 5 Current individual Harmonics 8 percentage | HAR8_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10252 | Input Channel 5 Current individual Harmonics 9 percentage | HAR9_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10254 | Input Channel 5 Current individual Harmonics 10 percentage | HAR10_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10256 | Input Channel 5 Current individual Harmonics 11 percentage | HAR11_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10258 | Input Channel 5 Current individual Harmonics 12 percentage | HAR12_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10260 | Input Channel 5 Current individual Harmonics 13 percentage | HAR13_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10262 | Input Channel 5 Current individual Harmonics 14 percentage | HAR14_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10264 | Input Channel 5 Current individual Harmonics 15 percentage | HAR15_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10266 | Input Channel 5 Current individual Harmonics 16 percentage | HAR16_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10268 | Input Channel 5 Current individual Harmonics 17 percentage | HAR17_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10270 | Input Channel 5 Current individual Harmonics 18 percentage | HAR18_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10272 | Input Channel 5 Current individual Harmonics 19 percentage | HAR19_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10274 | Input Channel 5 Current individual Harmonics 20 percentage | HAR20_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10276 | Input Channel 5 Current individual Harmonics 21 percentage | HAR21_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10278 | Input Channel 5 Current individual Harmonics 22 percentage | HAR22_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10280 | Input Channel 5 Current individual Harmonics 23 percentage | HAR23_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10282 | Input Channel 5 Current individual Harmonics 24 percentage | HAR24_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10284 | Input Channel 5 Current individual Harmonics 25 percentage | HAR25_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10286 | Input Channel 5 Current individual Harmonics 26 percentage | HAR26_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10288 | Input Channel 5 Current individual Harmonics 27 percentage | HAR27_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10290 | Input Channel 5 Current individual Harmonics 28 percentage | HAR28_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10292 | Input Channel 5 Current individual Harmonics 29 percentage | HAR29_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10294 | Input Channel 5 Current individual Harmonics 30 percentage | HAR30_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10296 | Input Channel 5 Current individual Harmonics 31 percentage | HAR31_I_005_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10298 | Input Channel 6 Current THD | THD_I_006_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10300 | Input Channel 6 Current THD Odd | OTHD_I_006_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10302 | Input Channel 6 Current THD Even | ETHD_I_006_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10304 | Input Channel 6 Current K Factor | KF_I_006_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10306 | Input Channel 6 Current individual Harmonics 2 percentage | HAR2_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10308 | Input Channel 6 Current individual Harmonics 3 percentage | HAR3_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10310 | Input Channel 6 Current individual Harmonics 4 percentage | HAR4_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10312 | Input Channel 6 Current individual Harmonics 5 percentage | HAR5_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10314 | Input Channel 6 Current individual Harmonics 6 percentage | HAR6_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10316 | Input Channel 6 Current individual Harmonics 7 percentage | HAR7_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10318 | Input Channel 6 Current individual Harmonics 8 percentage | HAR8_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10320 | Input Channel 6 Current individual Harmonics 9 percentage | HAR9_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10322 | Input Channel 6 Current individual Harmonics 10 percentage | HAR10_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10324 | Input Channel 6 Current individual Harmonics 11 percentage | HAR11_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10326 | Input Channel 6 Current individual Harmonics 12 percentage | HAR12_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10328 | Input Channel 6 Current individual Harmonics 13 percentage | HAR13_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10330 | Input Channel 6 Current individual Harmonics 14 percentage | HAR14_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10332 | Input Channel 6 Current individual Harmonics 15 percentage | HAR15_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10334 | Input Channel 6 Current individual Harmonics 16 percentage | HAR16_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10336 | Input Channel 6 Current individual Harmonics 17 percentage | HAR17_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10338 | Input Channel 6 Current individual Harmonics 18 percentage | HAR18_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10340 | Input Channel 6 Current individual Harmonics 19 percentage | HAR19_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10342 | Input Channel 6 Current individual Harmonics 20 percentage | HAR20_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10344 | Input Channel 6 Current individual Harmonics 21 percentage | HAR21_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10346 | Input Channel 6 Current individual Harmonics 22 percentage | HAR22_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10348 | Input Channel 6 Current individual Harmonics 23 percentage | HAR23_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10350 | Input Channel 6 Current individual Harmonics 24 percentage | HAR24_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10352 | Input Channel 6 Current individual Harmonics 25 percentage | HAR25_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10354 | Input Channel 6 Current individual Harmonics 26 percentage | HAR26_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10356 | Input Channel 6 Current individual Harmonics 27 percentage | HAR27_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10358 | Input Channel 6 Current individual Harmonics 28 percentage | HAR28_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10360 | Input Channel 6 Current individual Harmonics 29 percentage | HAR29_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10362 | Input Channel 6 Current individual Harmonics 30 percentage | HAR30_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10364 | Input Channel 6 Current individual Harmonics 31 percentage | HAR31_I_006_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10366 | Input Channel 7 Current THD | THD_I_007_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10368 | Input Channel 7 Current THD Odd | OTHD_I_007_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10370 | Input Channel 7 Current THD Even | ETHD_I_007_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10372 | Input Channel 7 Current K Factor | KF_I_007_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10374 | Input Channel 7 Current individual Harmonics 2 percentage | HAR2_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10376 | Input Channel 7 Current individual Harmonics 3 percentage | HAR3_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10378 | Input Channel 7 Current individual Harmonics 4 percentage | HAR4_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10380 | Input Channel 7 Current individual Harmonics 5 percentage | HAR5_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10382 | Input Channel 7 Current individual Harmonics 6 percentage | HAR6_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10384 | Input Channel 7 Current individual Harmonics 7 percentage | HAR7_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10386 | Input Channel 7 Current individual Harmonics 8 percentage | HAR8_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10388 | Input Channel 7 Current individual Harmonics 9 percentage | HAR9_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10390 | Input Channel 7 Current individual Harmonics 10 percentage | HAR10_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10392 | Input Channel 7 Current individual Harmonics 11 percentage | HAR11_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10394 | Input Channel 7 Current individual Harmonics 12 percentage | HAR12_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10396 | Input Channel 7 Current individual Harmonics 13 percentage | HAR13_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10398 | Input Channel 7 Current individual Harmonics 14 percentage | HAR14_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10400 | Input Channel 7 Current individual Harmonics 15 percentage | HAR15_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10402 | Input Channel 7 Current individual Harmonics 16 percentage | HAR16_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10404 | Input Channel 7 Current individual Harmonics 17 percentage | HAR17_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10406 | Input Channel 7 Current individual Harmonics 18 percentage | HAR18_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10408 | Input Channel 7 Current individual Harmonics 19 percentage | HAR19_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10410 | Input Channel 7 Current individual Harmonics 20 percentage | HAR20_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10412 | Input Channel 7 Current individual Harmonics 21 percentage | HAR21_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10414 | Input Channel 7 Current individual Harmonics 22 percentage | HAR22_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10416 | Input Channel 7 Current individual Harmonics 23 percentage | HAR23_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10418 | Input Channel 7 Current individual Harmonics 24 percentage | HAR24_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10420 | Input Channel 7 Current individual Harmonics 25 percentage | HAR25_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10422 | Input Channel 7 Current individual Harmonics 26 percentage | HAR26_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10424 | Input Channel 7 Current individual Harmonics 27 percentage | HAR27_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10426 | Input Channel 7 Current individual Harmonics 28 percentage | HAR28_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10428 | Input Channel 7 Current individual Harmonics 29 percentage | HAR29_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10430 | Input Channel 7 Current individual Harmonics 30 percentage | HAR30_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10432 | Input Channel 7 Current individual Harmonics 31 percentage | HAR31_I_007_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10434 | Input Channel 8 Current THD | THD_I_008_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10436 | Input Channel 8 Current THD Odd | OTHD_I_008_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10438 | Input Channel 8 Current THD Even | ETHD_I_008_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10440 | Input Channel 8 Current K Factor | KF_I_008_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10442 | Input Channel 8 Current individual Harmonics 2 percentage | HAR2_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10444 | Input Channel 8 Current individual Harmonics 3 percentage | HAR3_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10446 | Input Channel 8 Current individual Harmonics 4 percentage | HAR4_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10448 | Input Channel 8 Current individual Harmonics 5 percentage | HAR5_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10450 | Input Channel 8 Current individual Harmonics 6 percentage | HAR6_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10452 | Input Channel 8 Current individual Harmonics 7 percentage | HAR7_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10454 | Input Channel 8 Current individual Harmonics 8 percentage | HAR8_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10456 | Input Channel 8 Current individual Harmonics 9 percentage | HAR9_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10458 | Input Channel 8 Current individual Harmonics 10 percentage | HAR10_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10460 | Input Channel 8 Current individual Harmonics 11 percentage | HAR11_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10462 | Input Channel 8 Current individual Harmonics 12 percentage | HAR12_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10464 | Input Channel 8 Current individual Harmonics 13 percentage | HAR13_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10466 | Input Channel 8 Current individual Harmonics 14 percentage | HAR14_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10468 | Input Channel 8 Current individual Harmonics 15 percentage | HAR15_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10470 | Input Channel 8 Current individual Harmonics 16 percentage | HAR16_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10472 | Input Channel 8 Current individual Harmonics 17 percentage | HAR17_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10474 | Input Channel 8 Current individual Harmonics 18 percentage | HAR18_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10476 | Input Channel 8 Current individual Harmonics 19 percentage | HAR19_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10478 | Input Channel 8 Current individual Harmonics 20 percentage | HAR20_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10480 | Input Channel 8 Current individual Harmonics 21 percentage | HAR21_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10482 | Input Channel 8 Current individual Harmonics 22 percentage | HAR22_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10484 | Input Channel 8 Current individual Harmonics 23 percentage | HAR23_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10486 | Input Channel 8 Current individual Harmonics 24 percentage | HAR24_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10488 | Input Channel 8 Current individual Harmonics 25 percentage | HAR25_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10490 | Input Channel 8 Current individual Harmonics 26 percentage | HAR26_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10492 | Input Channel 8 Current individual Harmonics 27 percentage | HAR27_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10494 | Input Channel 8 Current individual Harmonics 28 percentage | HAR28_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10496 | Input Channel 8 Current individual Harmonics 29 percentage | HAR29_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10498 | Input Channel 8 Current individual Harmonics 30 percentage | HAR30_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10500 | Input Channel 8 Current individual Harmonics 31 percentage | HAR31_I_008_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10502 | Input Channel 9 Current THD | THD_I_009_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10504 | Input Channel 9 Current THD Odd | OTHD_I_009_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10506 | Input Channel 9 Current THD Even | ETHD_I_009_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10508 | Input Channel 9 Current K Factor | KF_I_009_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10510 | Input Channel 9 Current individual Harmonics 2 percentage | HAR2_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10512 | Input Channel 9 Current individual Harmonics 3 percentage | HAR3_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10514 | Input Channel 9 Current individual Harmonics 4 percentage | HAR4_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10516 | Input Channel 9 Current individual Harmonics 5 percentage | HAR5_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10518 | Input Channel 9 Current individual Harmonics 6 percentage | HAR6_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10520 | Input Channel 9 Current individual Harmonics 7 percentage | HAR7_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10522 | Input Channel 9 Current individual Harmonics 8 percentage | HAR8_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10524 | Input Channel 9 Current individual Harmonics 9 percentage | HAR9_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10526 | Input Channel 9 Current individual Harmonics 10 percentage | HAR10_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10528 | Input Channel 9 Current individual Harmonics 11 percentage | HAR11_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10530 | Input Channel 9 Current individual Harmonics 12 percentage | HAR12_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10532 | Input Channel 9 Current individual Harmonics 13 percentage | HAR13_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10534 | Input Channel 9 Current individual Harmonics 14 percentage | HAR14_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10536 | Input Channel 9 Current individual Harmonics 15 percentage | HAR15_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10538 | Input Channel 9 Current individual Harmonics 16 percentage | HAR16_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10540 | Input Channel 9 Current individual Harmonics 17 percentage | HAR17_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10542 | Input Channel 9 Current individual Harmonics 18 percentage | HAR18_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10544 | Input Channel 9 Current individual Harmonics 19 percentage | HAR19_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10546 | Input Channel 9 Current individual Harmonics 20 percentage | HAR20_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10548 | Input Channel 9 Current individual Harmonics 21 percentage | HAR21_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10550 | Input Channel 9 Current individual Harmonics 22 percentage | HAR22_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10552 | Input Channel 9 Current individual Harmonics 23 percentage | HAR23_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10554 | Input Channel 9 Current individual Harmonics 24 percentage | HAR24_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10556 | Input Channel 9 Current individual Harmonics 25 percentage | HAR25_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10558 | Input Channel 9 Current individual Harmonics 26 percentage | HAR26_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10560 | Input Channel 9 Current individual Harmonics 27 percentage | HAR27_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10562 | Input Channel 9 Current individual Harmonics 28 percentage | HAR28_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10564 | Input Channel 9 Current individual Harmonics 29 percentage | HAR29_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10566 | Input Channel 9 Current individual Harmonics 30 percentage | HAR30_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10568 | Input Channel 9 Current individual Harmonics 31 percentage | HAR31_I_009_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10570 | Input Channel 10 Current THD | THD_I_010_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10572 | Input Channel 10 Current THD Odd | OTHD_I_010_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10574 | Input Channel 10 Current THD Even | ETHD_I_010_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10576 | Input Channel 10 Current K Factor | KF_I_010_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10578 | Input Channel 10 Current individual Harmonics 2 percentage | HAR2_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10580 | Input Channel 10 Current individual Harmonics 3 percentage | HAR3_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10582 | Input Channel 10 Current individual Harmonics 4 percentage | HAR4_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10584 | Input Channel 10 Current individual Harmonics 5 percentage | HAR5_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10586 | Input Channel 10 Current individual Harmonics 6 percentage | HAR6_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10588 | Input Channel 10 Current individual Harmonics 7 percentage | HAR7_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10590 | Input Channel 10 Current individual Harmonics 8 percentage | HAR8_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10592 | Input Channel 10 Current individual Harmonics 9 percentage | HAR9_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10594 | Input Channel 10 Current individual Harmonics 10 percentage | HAR10_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10596 | Input Channel 10 Current individual Harmonics 11 percentage | HAR11_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10598 | Input Channel 10 Current individual Harmonics 12 percentage | HAR12_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10600 | Input Channel 10 Current individual Harmonics 13 percentage | HAR13_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10602 | Input Channel 10 Current individual Harmonics 14 percentage | HAR14_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10604 | Input Channel 10 Current individual Harmonics 15 percentage | HAR15_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10606 | Input Channel 10 Current individual Harmonics 16 percentage | HAR16_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10608 | Input Channel 10 Current individual Harmonics 17 percentage | HAR17_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10610 | Input Channel 10 Current individual Harmonics 18 percentage | HAR18_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10612 | Input Channel 10 Current individual Harmonics 19 percentage | HAR19_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10614 | Input Channel 10 Current individual Harmonics 20 percentage | HAR20_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10616 | Input Channel 10 Current individual Harmonics 21 percentage | HAR21_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10618 | Input Channel 10 Current individual Harmonics 22 percentage | HAR22_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10620 | Input Channel 10 Current individual Harmonics 23 percentage | HAR23_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10622 | Input Channel 10 Current individual Harmonics 24 percentage | HAR24_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10624 | Input Channel 10 Current individual Harmonics 25 percentage | HAR25_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10626 | Input Channel 10 Current individual Harmonics 26 percentage | HAR26_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10628 | Input Channel 10 Current individual Harmonics 27 percentage | HAR27_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10630 | Input Channel 10 Current individual Harmonics 28 percentage | HAR28_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10632 | Input Channel 10 Current individual Harmonics 29 percentage | HAR29_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10634 | Input Channel 10 Current individual Harmonics 30 percentage | HAR30_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10636 | Input Channel 10 Current individual Harmonics 31 percentage | HAR31_I_010_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10638 | Input Channel 11 Current THD | THD_I_011_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10640 | Input Channel 11 Current THD Odd | OTHD_I_011_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10642 | Input Channel 11 Current THD Even | ETHD_I_011_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10644 | Input Channel 11 Current K Factor | KF_I_011_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10646 | Input Channel 11 Current individual Harmonics 2 percentage | HAR2_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10648 | Input Channel 11 Current individual Harmonics 3 percentage | HAR3_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10650 | Input Channel 11 Current individual Harmonics 4 percentage | HAR4_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10652 | Input Channel 11 Current individual Harmonics 5 percentage | HAR5_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10654 | Input Channel 11 Current individual Harmonics 6 percentage | HAR6_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10656 | Input Channel 11 Current individual Harmonics 7 percentage | HAR7_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10658 | Input Channel 11 Current individual Harmonics 8 percentage | HAR8_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10660 | Input Channel 11 Current individual Harmonics 9 percentage | HAR9_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10662 | Input Channel 11 Current individual Harmonics 10 percentage | HAR10_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10664 | Input Channel 11 Current individual Harmonics 11 percentage | HAR11_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10666 | Input Channel 11 Current individual Harmonics 12 percentage | HAR12_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10668 | Input Channel 11 Current individual Harmonics 13 percentage | HAR13_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10670 | Input Channel 11 Current individual Harmonics 14 percentage | HAR14_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10672 | Input Channel 11 Current individual Harmonics 15 percentage | HAR15_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10674 | Input Channel 11 Current individual Harmonics 16 percentage | HAR16_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10676 | Input Channel 11 Current individual Harmonics 17 percentage | HAR17_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10678 | Input Channel 11 Current individual Harmonics 18 percentage | HAR18_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10680 | Input Channel 11 Current individual Harmonics 19 percentage | HAR19_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10682 | Input Channel 11 Current individual Harmonics 20 percentage | HAR20_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10684 | Input Channel 11 Current individual Harmonics 21 percentage | HAR21_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10686 | Input Channel 11 Current individual Harmonics 22 percentage | HAR22_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10688 | Input Channel 11 Current individual Harmonics 23 percentage | HAR23_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10690 | Input Channel 11 Current individual Harmonics 24 percentage | HAR24_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10692 | Input Channel 11 Current individual Harmonics 25 percentage | HAR25_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10694 | Input Channel 11 Current individual Harmonics 26 percentage | HAR26_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10696 | Input Channel 11 Current individual Harmonics 27 percentage | HAR27_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10698 | Input Channel 11 Current individual Harmonics 28 percentage | HAR28_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10700 | Input Channel 11 Current individual Harmonics 29 percentage | HAR29_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10702 | Input Channel 11 Current individual Harmonics 30 percentage | HAR30_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10704 | Input Channel 11 Current individual Harmonics 31 percentage | HAR31_I_011_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10706 | Input Channel 12 Current THD | THD_I_012_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10708 | Input Channel 12 Current THD Odd | OTHD_I_012_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10710 | Input Channel 12 Current THD Even | ETHD_I_012_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10712 | Input Channel 12 Current K Factor | KF_I_012_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10714 | Input Channel 12 Current individual Harmonics 2 percentage | HAR2_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10716 | Input Channel 12 Current individual Harmonics 3 percentage | HAR3_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10718 | Input Channel 12 Current individual Harmonics 4 percentage | HAR4_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10720 | Input Channel 12 Current individual Harmonics 5 percentage | HAR5_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10722 | Input Channel 12 Current individual Harmonics 6 percentage | HAR6_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10724 | Input Channel 12 Current individual Harmonics 7 percentage | HAR7_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10726 | Input Channel 12 Current individual Harmonics 8 percentage | HAR8_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10728 | Input Channel 12 Current individual Harmonics 9 percentage | HAR9_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10730 | Input Channel 12 Current individual Harmonics 10 percentage | HAR10_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10732 | Input Channel 12 Current individual Harmonics 11 percentage | HAR11_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10734 | Input Channel 12 Current individual Harmonics 12 percentage | HAR12_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10736 | Input Channel 12 Current individual Harmonics 13 percentage | HAR13_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10738 | Input Channel 12 Current individual Harmonics 14 percentage | HAR14_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10740 | Input Channel 12 Current individual Harmonics 15 percentage | HAR15_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10742 | Input Channel 12 Current individual Harmonics 16 percentage | HAR16_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10744 | Input Channel 12 Current individual Harmonics 17 percentage | HAR17_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10746 | Input Channel 12 Current individual Harmonics 18 percentage | HAR18_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10748 | Input Channel 12 Current individual Harmonics 19 percentage | HAR19_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10750 | Input Channel 12 Current individual Harmonics 20 percentage | HAR20_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10752 | Input Channel 12 Current individual Harmonics 21 percentage | HAR21_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10754 | Input Channel 12 Current individual Harmonics 22 percentage | HAR22_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10756 | Input Channel 12 Current individual Harmonics 23 percentage | HAR23_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10758 | Input Channel 12 Current individual Harmonics 24 percentage | HAR24_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10760 | Input Channel 12 Current individual Harmonics 25 percentage | HAR25_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10762 | Input Channel 12 Current individual Harmonics 26 percentage | HAR26_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10764 | Input Channel 12 Current individual Harmonics 27 percentage | HAR27_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10766 | Input Channel 12 Current individual Harmonics 28 percentage | HAR28_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10768 | Input Channel 12 Current individual Harmonics 29 percentage | HAR29_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10770 | Input Channel 12 Current individual Harmonics 30 percentage | HAR30_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10772 | Input Channel 12 Current individual Harmonics 31 percentage | HAR31_I_012_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10774 | Input Channel 13 Current THD | THD_I_013_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10776 | Input Channel 13 Current THD Odd | OTHD_I_013_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10778 | Input Channel 13 Current THD Even | ETHD_I_013_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10780 | Input Channel 13 Current K Factor | KF_I_013_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10782 | Input Channel 13 Current individual Harmonics 2 percentage | HAR2_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10784 | Input Channel 13 Current individual Harmonics 3 percentage | HAR3_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10786 | Input Channel 13 Current individual Harmonics 4 percentage | HAR4_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10788 | Input Channel 13 Current individual Harmonics 5 percentage | HAR5_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10790 | Input Channel 13 Current individual Harmonics 6 percentage | HAR6_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10792 | Input Channel 13 Current individual Harmonics 7 percentage | HAR7_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10794 | Input Channel 13 Current individual Harmonics 8 percentage | HAR8_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10796 | Input Channel 13 Current individual Harmonics 9 percentage | HAR9_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10798 | Input Channel 13 Current individual Harmonics 10 percentage | HAR10_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10800 | Input Channel 13 Current individual Harmonics 11 percentage | HAR11_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10802 | Input Channel 13 Current individual Harmonics 12 percentage | HAR12_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10804 | Input Channel 13 Current individual Harmonics 13 percentage | HAR13_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10806 | Input Channel 13 Current individual Harmonics 14 percentage | HAR14_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10808 | Input Channel 13 Current individual Harmonics 15 percentage | HAR15_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10810 | Input Channel 13 Current individual Harmonics 16 percentage | HAR16_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10812 | Input Channel 13 Current individual Harmonics 17 percentage | HAR17_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10814 | Input Channel 13 Current individual Harmonics 18 percentage | HAR18_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10816 | Input Channel 13 Current individual Harmonics 19 percentage | HAR19_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10818 | Input Channel 13 Current individual Harmonics 20 percentage | HAR20_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10820 | Input Channel 13 Current individual Harmonics 21 percentage | HAR21_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10822 | Input Channel 13 Current individual Harmonics 22 percentage | HAR22_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10824 | Input Channel 13 Current individual Harmonics 23 percentage | HAR23_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10826 | Input Channel 13 Current individual Harmonics 24 percentage | HAR24_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10828 | Input Channel 13 Current individual Harmonics 25 percentage | HAR25_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10830 | Input Channel 13 Current individual Harmonics 26 percentage | HAR26_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10832 | Input Channel 13 Current individual Harmonics 27 percentage | HAR27_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10834 | Input Channel 13 Current individual Harmonics 28 percentage | HAR28_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10836 | Input Channel 13 Current individual Harmonics 29 percentage | HAR29_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10838 | Input Channel 13 Current individual Harmonics 30 percentage | HAR30_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10840 | Input Channel 13 Current individual Harmonics 31 percentage | HAR31_I_013_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10842 | Input Channel 14 Current THD | THD_I_014_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10844 | Input Channel 14 Current THD Odd | OTHD_I_014_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10846 | Input Channel 14 Current THD Even | ETHD_I_014_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10848 | Input Channel 14 Current K Factor | KF_I_014_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10850 | Input Channel 14 Current individual Harmonics 2 percentage | HAR2_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10852 | Input Channel 14 Current individual Harmonics 3 percentage | HAR3_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10854 | Input Channel 14 Current individual Harmonics 4 percentage | HAR4_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10856 | Input Channel 14 Current individual Harmonics 5 percentage | HAR5_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10858 | Input Channel 14 Current individual Harmonics 6 percentage | HAR6_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10860 | Input Channel 14 Current individual Harmonics 7 percentage | HAR7_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10862 | Input Channel 14 Current individual Harmonics 8 percentage | HAR8_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10864 | Input Channel 14 Current individual Harmonics 9 percentage | HAR9_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10866 | Input Channel 14 Current individual Harmonics 10 percentage | HAR10_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10868 | Input Channel 14 Current individual Harmonics 11 percentage | HAR11_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10870 | Input Channel 14 Current individual Harmonics 12 percentage | HAR12_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10872 | Input Channel 14 Current individual Harmonics 13 percentage | HAR13_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10874 | Input Channel 14 Current individual Harmonics 14 percentage | HAR14_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10876 | Input Channel 14 Current individual Harmonics 15 percentage | HAR15_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10878 | Input Channel 14 Current individual Harmonics 16 percentage | HAR16_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10880 | Input Channel 14 Current individual Harmonics 17 percentage | HAR17_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10882 | Input Channel 14 Current individual Harmonics 18 percentage | HAR18_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10884 | Input Channel 14 Current individual Harmonics 19 percentage | HAR19_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10886 | Input Channel 14 Current individual Harmonics 20 percentage | HAR20_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10888 | Input Channel 14 Current individual Harmonics 21 percentage | HAR21_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10890 | Input Channel 14 Current individual Harmonics 22 percentage | HAR22_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10892 | Input Channel 14 Current individual Harmonics 23 percentage | HAR23_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10894 | Input Channel 14 Current individual Harmonics 24 percentage | HAR24_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10896 | Input Channel 14 Current individual Harmonics 25 percentage | HAR25_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10898 | Input Channel 14 Current individual Harmonics 26 percentage | HAR26_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10900 | Input Channel 14 Current individual Harmonics 27 percentage | HAR27_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10902 | Input Channel 14 Current individual Harmonics 28 percentage | HAR28_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10904 | Input Channel 14 Current individual Harmonics 29 percentage | HAR29_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10906 | Input Channel 14 Current individual Harmonics 30 percentage | HAR30_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10908 | Input Channel 14 Current individual Harmonics 31 percentage | HAR31_I_014_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10910 | Input Channel 15 Current THD | THD_I_015_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10912 | Input Channel 15 Current THD Odd | OTHD_I_015_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10914 | Input Channel 15 Current THD Even | ETHD_I_015_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10916 | Input Channel 15 Current K Factor | KF_I_015_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10918 | Input Channel 15 Current individual Harmonics 2 percentage | HAR2_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10920 | Input Channel 15 Current individual Harmonics 3 percentage | HAR3_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10922 | Input Channel 15 Current individual Harmonics 4 percentage | HAR4_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10924 | Input Channel 15 Current individual Harmonics 5 percentage | HAR5_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10926 | Input Channel 15 Current individual Harmonics 6 percentage | HAR6_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10928 | Input Channel 15 Current individual Harmonics 7 percentage | HAR7_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10930 | Input Channel 15 Current individual Harmonics 8 percentage | HAR8_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10932 | Input Channel 15 Current individual Harmonics 9 percentage | HAR9_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10934 | Input Channel 15 Current individual Harmonics 10 percentage | HAR10_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10936 | Input Channel 15 Current individual Harmonics 11 percentage | HAR11_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10938 | Input Channel 15 Current individual Harmonics 12 percentage | HAR12_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10940 | Input Channel 15 Current individual Harmonics 13 percentage | HAR13_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10942 | Input Channel 15 Current individual Harmonics 14 percentage | HAR14_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10944 | Input Channel 15 Current individual Harmonics 15 percentage | HAR15_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10946 | Input Channel 15 Current individual Harmonics 16 percentage | HAR16_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10948 | Input Channel 15 Current individual Harmonics 17 percentage | HAR17_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10950 | Input Channel 15 Current individual Harmonics 18 percentage | HAR18_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10952 | Input Channel 15 Current individual Harmonics 19 percentage | HAR19_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10954 | Input Channel 15 Current individual Harmonics 20 percentage | HAR20_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10956 | Input Channel 15 Current individual Harmonics 21 percentage | HAR21_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10958 | Input Channel 15 Current individual Harmonics 22 percentage | HAR22_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10960 | Input Channel 15 Current individual Harmonics 23 percentage | HAR23_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10962 | Input Channel 15 Current individual Harmonics 24 percentage | HAR24_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10964 | Input Channel 15 Current individual Harmonics 25 percentage | HAR25_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10966 | Input Channel 15 Current individual Harmonics 26 percentage | HAR26_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10968 | Input Channel 15 Current individual Harmonics 27 percentage | HAR27_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10970 | Input Channel 15 Current individual Harmonics 28 percentage | HAR28_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10972 | Input Channel 15 Current individual Harmonics 29 percentage | HAR29_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10974 | Input Channel 15 Current individual Harmonics 30 percentage | HAR30_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10976 | Input Channel 15 Current individual Harmonics 31 percentage | HAR31_I_015_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10978 | Input Channel 16 Current THD | THD_I_016_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10980 | Input Channel 16 Current THD Odd | OTHD_I_016_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10982 | Input Channel 16 Current THD Even | ETHD_I_016_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10984 | Input Channel 16 Current K Factor | KF_I_016_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
10986 | Input Channel 16 Current individual Harmonics 2 percentage | HAR2_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10988 | Input Channel 16 Current individual Harmonics 3 percentage | HAR3_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10990 | Input Channel 16 Current individual Harmonics 4 percentage | HAR4_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10992 | Input Channel 16 Current individual Harmonics 5 percentage | HAR5_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10994 | Input Channel 16 Current individual Harmonics 6 percentage | HAR6_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10996 | Input Channel 16 Current individual Harmonics 7 percentage | HAR7_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
10998 | Input Channel 16 Current individual Harmonics 8 percentage | HAR8_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11000 | Input Channel 16 Current individual Harmonics 9 percentage | HAR9_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11002 | Input Channel 16 Current individual Harmonics 10 percentage | HAR10_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11004 | Input Channel 16 Current individual Harmonics 11 percentage | HAR11_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11006 | Input Channel 16 Current individual Harmonics 12 percentage | HAR12_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11008 | Input Channel 16 Current individual Harmonics 13 percentage | HAR13_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11010 | Input Channel 16 Current individual Harmonics 14 percentage | HAR14_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11012 | Input Channel 16 Current individual Harmonics 15 percentage | HAR15_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11014 | Input Channel 16 Current individual Harmonics 16 percentage | HAR16_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11016 | Input Channel 16 Current individual Harmonics 17 percentage | HAR17_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11018 | Input Channel 16 Current individual Harmonics 18 percentage | HAR18_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11020 | Input Channel 16 Current individual Harmonics 19 percentage | HAR19_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11022 | Input Channel 16 Current individual Harmonics 20 percentage | HAR20_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11024 | Input Channel 16 Current individual Harmonics 21 percentage | HAR21_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11026 | Input Channel 16 Current individual Harmonics 22 percentage | HAR22_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11028 | Input Channel 16 Current individual Harmonics 23 percentage | HAR23_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11030 | Input Channel 16 Current individual Harmonics 24 percentage | HAR24_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11032 | Input Channel 16 Current individual Harmonics 25 percentage | HAR25_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11034 | Input Channel 16 Current individual Harmonics 26 percentage | HAR26_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11036 | Input Channel 16 Current individual Harmonics 27 percentage | HAR27_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11038 | Input Channel 16 Current individual Harmonics 28 percentage | HAR28_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11040 | Input Channel 16 Current individual Harmonics 29 percentage | HAR29_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11042 | Input Channel 16 Current individual Harmonics 30 percentage | HAR30_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11044 | Input Channel 16 Current individual Harmonics 31 percentage | HAR31_I_016_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11046 | Input Channel 17 Current THD | THD_I_017_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11048 | Input Channel 17 Current THD Odd | OTHD_I_017_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11050 | Input Channel 17 Current THD Even | ETHD_I_017_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11052 | Input Channel 17 Current K Factor | KF_I_017_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11054 | Input Channel 17 Current individual Harmonics 2 percentage | HAR2_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11056 | Input Channel 17 Current individual Harmonics 3 percentage | HAR3_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11058 | Input Channel 17 Current individual Harmonics 4 percentage | HAR4_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11060 | Input Channel 17 Current individual Harmonics 5 percentage | HAR5_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11062 | Input Channel 17 Current individual Harmonics 6 percentage | HAR6_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11064 | Input Channel 17 Current individual Harmonics 7 percentage | HAR7_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11066 | Input Channel 17 Current individual Harmonics 8 percentage | HAR8_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11068 | Input Channel 17 Current individual Harmonics 9 percentage | HAR9_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11070 | Input Channel 17 Current individual Harmonics 10 percentage | HAR10_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11072 | Input Channel 17 Current individual Harmonics 11 percentage | HAR11_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11074 | Input Channel 17 Current individual Harmonics 12 percentage | HAR12_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11076 | Input Channel 17 Current individual Harmonics 13 percentage | HAR13_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11078 | Input Channel 17 Current individual Harmonics 14 percentage | HAR14_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11080 | Input Channel 17 Current individual Harmonics 15 percentage | HAR15_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11082 | Input Channel 17 Current individual Harmonics 16 percentage | HAR16_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11084 | Input Channel 17 Current individual Harmonics 17 percentage | HAR17_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11086 | Input Channel 17 Current individual Harmonics 18 percentage | HAR18_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11088 | Input Channel 17 Current individual Harmonics 19 percentage | HAR19_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11090 | Input Channel 17 Current individual Harmonics 20 percentage | HAR20_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11092 | Input Channel 17 Current individual Harmonics 21 percentage | HAR21_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11094 | Input Channel 17 Current individual Harmonics 22 percentage | HAR22_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11096 | Input Channel 17 Current individual Harmonics 23 percentage | HAR23_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11098 | Input Channel 17 Current individual Harmonics 24 percentage | HAR24_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11100 | Input Channel 17 Current individual Harmonics 25 percentage | HAR25_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11102 | Input Channel 17 Current individual Harmonics 26 percentage | HAR26_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11104 | Input Channel 17 Current individual Harmonics 27 percentage | HAR27_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11106 | Input Channel 17 Current individual Harmonics 28 percentage | HAR28_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11108 | Input Channel 17 Current individual Harmonics 29 percentage | HAR29_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11110 | Input Channel 17 Current individual Harmonics 30 percentage | HAR30_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11112 | Input Channel 17 Current individual Harmonics 31 percentage | HAR31_I_017_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11114 | Input Channel 18 Current THD | THD_I_018_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11116 | Input Channel 18 Current THD Odd | OTHD_I_018_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11118 | Input Channel 18 Current THD Even | ETHD_I_018_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11120 | Input Channel 18 Current K Factor | KF_I_018_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11122 | Input Channel 18 Current individual Harmonics 2 percentage | HAR2_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11124 | Input Channel 18 Current individual Harmonics 3 percentage | HAR3_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11126 | Input Channel 18 Current individual Harmonics 4 percentage | HAR4_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11128 | Input Channel 18 Current individual Harmonics 5 percentage | HAR5_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11130 | Input Channel 18 Current individual Harmonics 6 percentage | HAR6_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11132 | Input Channel 18 Current individual Harmonics 7 percentage | HAR7_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11134 | Input Channel 18 Current individual Harmonics 8 percentage | HAR8_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11136 | Input Channel 18 Current individual Harmonics 9 percentage | HAR9_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11138 | Input Channel 18 Current individual Harmonics 10 percentage | HAR10_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11140 | Input Channel 18 Current individual Harmonics 11 percentage | HAR11_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11142 | Input Channel 18 Current individual Harmonics 12 percentage | HAR12_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11144 | Input Channel 18 Current individual Harmonics 13 percentage | HAR13_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11146 | Input Channel 18 Current individual Harmonics 14 percentage | HAR14_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11148 | Input Channel 18 Current individual Harmonics 15 percentage | HAR15_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11150 | Input Channel 18 Current individual Harmonics 16 percentage | HAR16_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11152 | Input Channel 18 Current individual Harmonics 17 percentage | HAR17_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11154 | Input Channel 18 Current individual Harmonics 18 percentage | HAR18_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11156 | Input Channel 18 Current individual Harmonics 19 percentage | HAR19_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11158 | Input Channel 18 Current individual Harmonics 20 percentage | HAR20_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11160 | Input Channel 18 Current individual Harmonics 21 percentage | HAR21_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11162 | Input Channel 18 Current individual Harmonics 22 percentage | HAR22_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11164 | Input Channel 18 Current individual Harmonics 23 percentage | HAR23_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11166 | Input Channel 18 Current individual Harmonics 24 percentage | HAR24_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11168 | Input Channel 18 Current individual Harmonics 25 percentage | HAR25_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11170 | Input Channel 18 Current individual Harmonics 26 percentage | HAR26_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11172 | Input Channel 18 Current individual Harmonics 27 percentage | HAR27_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11174 | Input Channel 18 Current individual Harmonics 28 percentage | HAR28_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11176 | Input Channel 18 Current individual Harmonics 29 percentage | HAR29_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11178 | Input Channel 18 Current individual Harmonics 30 percentage | HAR30_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11180 | Input Channel 18 Current individual Harmonics 31 percentage | HAR31_I_018_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11182 | Input Channel 19 Current THD | THD_I_019_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11184 | Input Channel 19 Current THD Odd | OTHD_I_019_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11186 | Input Channel 19 Current THD Even | ETHD_I_019_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11188 | Input Channel 19 Current K Factor | KF_I_019_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11190 | Input Channel 19 Current individual Harmonics 2 percentage | HAR2_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11192 | Input Channel 19 Current individual Harmonics 3 percentage | HAR3_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11194 | Input Channel 19 Current individual Harmonics 4 percentage | HAR4_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11196 | Input Channel 19 Current individual Harmonics 5 percentage | HAR5_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11198 | Input Channel 19 Current individual Harmonics 6 percentage | HAR6_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11200 | Input Channel 19 Current individual Harmonics 7 percentage | HAR7_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11202 | Input Channel 19 Current individual Harmonics 8 percentage | HAR8_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11204 | Input Channel 19 Current individual Harmonics 9 percentage | HAR9_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11206 | Input Channel 19 Current individual Harmonics 10 percentage | HAR10_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11208 | Input Channel 19 Current individual Harmonics 11 percentage | HAR11_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11210 | Input Channel 19 Current individual Harmonics 12 percentage | HAR12_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11212 | Input Channel 19 Current individual Harmonics 13 percentage | HAR13_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11214 | Input Channel 19 Current individual Harmonics 14 percentage | HAR14_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11216 | Input Channel 19 Current individual Harmonics 15 percentage | HAR15_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11218 | Input Channel 19 Current individual Harmonics 16 percentage | HAR16_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11220 | Input Channel 19 Current individual Harmonics 17 percentage | HAR17_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11222 | Input Channel 19 Current individual Harmonics 18 percentage | HAR18_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11224 | Input Channel 19 Current individual Harmonics 19 percentage | HAR19_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11226 | Input Channel 19 Current individual Harmonics 20 percentage | HAR20_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11228 | Input Channel 19 Current individual Harmonics 21 percentage | HAR21_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11230 | Input Channel 19 Current individual Harmonics 22 percentage | HAR22_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11232 | Input Channel 19 Current individual Harmonics 23 percentage | HAR23_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11234 | Input Channel 19 Current individual Harmonics 24 percentage | HAR24_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11236 | Input Channel 19 Current individual Harmonics 25 percentage | HAR25_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11238 | Input Channel 19 Current individual Harmonics 26 percentage | HAR26_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11240 | Input Channel 19 Current individual Harmonics 27 percentage | HAR27_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11242 | Input Channel 19 Current individual Harmonics 28 percentage | HAR28_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11244 | Input Channel 19 Current individual Harmonics 29 percentage | HAR29_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11246 | Input Channel 19 Current individual Harmonics 30 percentage | HAR30_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11248 | Input Channel 19 Current individual Harmonics 31 percentage | HAR31_I_019_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11250 | Input Channel 20 Current THD | THD_I_020_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11252 | Input Channel 20 Current THD Odd | OTHD_I_020_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11254 | Input Channel 20 Current THD Even | ETHD_I_020_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11256 | Input Channel 20 Current K Factor | KF_I_020_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11258 | Input Channel 20 Current individual Harmonics 2 percentage | HAR2_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11260 | Input Channel 20 Current individual Harmonics 3 percentage | HAR3_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11262 | Input Channel 20 Current individual Harmonics 4 percentage | HAR4_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11264 | Input Channel 20 Current individual Harmonics 5 percentage | HAR5_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11266 | Input Channel 20 Current individual Harmonics 6 percentage | HAR6_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11268 | Input Channel 20 Current individual Harmonics 7 percentage | HAR7_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11270 | Input Channel 20 Current individual Harmonics 8 percentage | HAR8_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11272 | Input Channel 20 Current individual Harmonics 9 percentage | HAR9_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11274 | Input Channel 20 Current individual Harmonics 10 percentage | HAR10_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11276 | Input Channel 20 Current individual Harmonics 11 percentage | HAR11_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11278 | Input Channel 20 Current individual Harmonics 12 percentage | HAR12_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11280 | Input Channel 20 Current individual Harmonics 13 percentage | HAR13_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11282 | Input Channel 20 Current individual Harmonics 14 percentage | HAR14_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11284 | Input Channel 20 Current individual Harmonics 15 percentage | HAR15_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11286 | Input Channel 20 Current individual Harmonics 16 percentage | HAR16_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11288 | Input Channel 20 Current individual Harmonics 17 percentage | HAR17_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11290 | Input Channel 20 Current individual Harmonics 18 percentage | HAR18_I_020_% | % | HAR18_I_020 %修改为HAR18_I_020_% | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11292 | Input Channel 20 Current individual Harmonics 19 percentage | HAR19_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11294 | Input Channel 20 Current individual Harmonics 20 percentage | HAR20_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11296 | Input Channel 20 Current individual Harmonics 21 percentage | HAR21_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11298 | Input Channel 20 Current individual Harmonics 22 percentage | HAR22_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11300 | Input Channel 20 Current individual Harmonics 23 percentage | HAR23_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11302 | Input Channel 20 Current individual Harmonics 24 percentage | HAR24_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11304 | Input Channel 20 Current individual Harmonics 25 percentage | HAR25_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11306 | Input Channel 20 Current individual Harmonics 26 percentage | HAR26_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11308 | Input Channel 20 Current individual Harmonics 27 percentage | HAR27_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11310 | Input Channel 20 Current individual Harmonics 28 percentage | HAR28_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11312 | Input Channel 20 Current individual Harmonics 29 percentage | HAR29_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11314 | Input Channel 20 Current individual Harmonics 30 percentage | HAR30_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11316 | Input Channel 20 Current individual Harmonics 31 percentage | HAR31_I_020_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11318 | Input Channel 21 Current THD | THD_I_021_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11320 | Input Channel 21 Current THD Odd | OTHD_I_021_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11322 | Input Channel 21 Current THD Even | ETHD_I_021_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11324 | Input Channel 21 Current K Factor | KF_I_021_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11326 | Input Channel 21 Current individual Harmonics 2 percentage | HAR2_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11328 | Input Channel 21 Current individual Harmonics 3 percentage | HAR3_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11330 | Input Channel 21 Current individual Harmonics 4 percentage | HAR4_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11332 | Input Channel 21 Current individual Harmonics 5 percentage | HAR5_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11334 | Input Channel 21 Current individual Harmonics 6 percentage | HAR6_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11336 | Input Channel 21 Current individual Harmonics 7 percentage | HAR7_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11338 | Input Channel 21 Current individual Harmonics 8 percentage | HAR8_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11340 | Input Channel 21 Current individual Harmonics 9 percentage | HAR9_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11342 | Input Channel 21 Current individual Harmonics 10 percentage | HAR10_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11344 | Input Channel 21 Current individual Harmonics 11 percentage | HAR11_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11346 | Input Channel 21 Current individual Harmonics 12 percentage | HAR12_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11348 | Input Channel 21 Current individual Harmonics 13 percentage | HAR13_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11350 | Input Channel 21 Current individual Harmonics 14 percentage | HAR14_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11352 | Input Channel 21 Current individual Harmonics 15 percentage | HAR15_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11354 | Input Channel 21 Current individual Harmonics 16 percentage | HAR16_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11356 | Input Channel 21 Current individual Harmonics 17 percentage | HAR17_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11358 | Input Channel 21 Current individual Harmonics 18 percentage | HAR18_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11360 | Input Channel 21 Current individual Harmonics 19 percentage | HAR19_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11362 | Input Channel 21 Current individual Harmonics 20 percentage | HAR20_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11364 | Input Channel 21 Current individual Harmonics 21 percentage | HAR21_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11366 | Input Channel 21 Current individual Harmonics 22 percentage | HAR22_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11368 | Input Channel 21 Current individual Harmonics 23 percentage | HAR23_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11370 | Input Channel 21 Current individual Harmonics 24 percentage | HAR24_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11372 | Input Channel 21 Current individual Harmonics 25 percentage | HAR25_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11374 | Input Channel 21 Current individual Harmonics 26 percentage | HAR26_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11376 | Input Channel 21 Current individual Harmonics 27 percentage | HAR27_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11378 | Input Channel 21 Current individual Harmonics 28 percentage | HAR28_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11380 | Input Channel 21 Current individual Harmonics 29 percentage | HAR29_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11382 | Input Channel 21 Current individual Harmonics 30 percentage | HAR30_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11384 | Input Channel 21 Current individual Harmonics 31 percentage | HAR31_I_021_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11386 | Input Channel 22 Current THD | THD_I_022_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11388 | Input Channel 22 Current THD Odd | OTHD_I_022_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11390 | Input Channel 22 Current THD Even | ETHD_I_022_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11392 | Input Channel 22 Current K Factor | KF_I_022_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11394 | Input Channel 22 Current individual Harmonics 2 percentage | HAR2_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11396 | Input Channel 22 Current individual Harmonics 3 percentage | HAR3_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11398 | Input Channel 22 Current individual Harmonics 4 percentage | HAR4_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11400 | Input Channel 22 Current individual Harmonics 5 percentage | HAR5_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11402 | Input Channel 22 Current individual Harmonics 6 percentage | HAR6_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11404 | Input Channel 22 Current individual Harmonics 7 percentage | HAR7_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11406 | Input Channel 22 Current individual Harmonics 8 percentage | HAR8_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11408 | Input Channel 22 Current individual Harmonics 9 percentage | HAR9_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11410 | Input Channel 22 Current individual Harmonics 10 percentage | HAR10_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11412 | Input Channel 22 Current individual Harmonics 11 percentage | HAR11_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11414 | Input Channel 22 Current individual Harmonics 12 percentage | HAR12_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11416 | Input Channel 22 Current individual Harmonics 13 percentage | HAR13_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11418 | Input Channel 22 Current individual Harmonics 14 percentage | HAR14_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11420 | Input Channel 22 Current individual Harmonics 15 percentage | HAR15_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11422 | Input Channel 22 Current individual Harmonics 16 percentage | HAR16_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11424 | Input Channel 22 Current individual Harmonics 17 percentage | HAR17_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11426 | Input Channel 22 Current individual Harmonics 18 percentage | HAR18_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11428 | Input Channel 22 Current individual Harmonics 19 percentage | HAR19_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11430 | Input Channel 22 Current individual Harmonics 20 percentage | HAR20_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11432 | Input Channel 22 Current individual Harmonics 21 percentage | HAR21_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11434 | Input Channel 22 Current individual Harmonics 22 percentage | HAR22_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11436 | Input Channel 22 Current individual Harmonics 23 percentage | HAR23_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11438 | Input Channel 22 Current individual Harmonics 24 percentage | HAR24_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11440 | Input Channel 22 Current individual Harmonics 25 percentage | HAR25_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11442 | Input Channel 22 Current individual Harmonics 26 percentage | HAR26_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11444 | Input Channel 22 Current individual Harmonics 27 percentage | HAR27_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11446 | Input Channel 22 Current individual Harmonics 28 percentage | HAR28_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11448 | Input Channel 22 Current individual Harmonics 29 percentage | HAR29_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11450 | Input Channel 22 Current individual Harmonics 30 percentage | HAR30_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11452 | Input Channel 22 Current individual Harmonics 31 percentage | HAR31_I_022_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11454 | Input Channel 23 Current THD | THD_I_023_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11456 | Input Channel 23 Current THD Odd | OTHD_I_023_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11458 | Input Channel 23 Current THD Even | ETHD_I_023_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11460 | Input Channel 23 Current K Factor | KF_I_023_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11462 | Input Channel 23 Current individual Harmonics 2 percentage | HAR2_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11464 | Input Channel 23 Current individual Harmonics 3 percentage | HAR3_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11466 | Input Channel 23 Current individual Harmonics 4 percentage | HAR4_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11468 | Input Channel 23 Current individual Harmonics 5 percentage | HAR5_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11470 | Input Channel 23 Current individual Harmonics 6 percentage | HAR6_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11472 | Input Channel 23 Current individual Harmonics 7 percentage | HAR7_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11474 | Input Channel 23 Current individual Harmonics 8 percentage | HAR8_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11476 | Input Channel 23 Current individual Harmonics 9 percentage | HAR9_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11478 | Input Channel 23 Current individual Harmonics 10 percentage | HAR10_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11480 | Input Channel 23 Current individual Harmonics 11 percentage | HAR11_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11482 | Input Channel 23 Current individual Harmonics 12 percentage | HAR12_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11484 | Input Channel 23 Current individual Harmonics 13 percentage | HAR13_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11486 | Input Channel 23 Current individual Harmonics 14 percentage | HAR14_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11488 | Input Channel 23 Current individual Harmonics 15 percentage | HAR15_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11490 | Input Channel 23 Current individual Harmonics 16 percentage | HAR16_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11492 | Input Channel 23 Current individual Harmonics 17 percentage | HAR17_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11494 | Input Channel 23 Current individual Harmonics 18 percentage | HAR18_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11496 | Input Channel 23 Current individual Harmonics 19 percentage | HAR19_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11498 | Input Channel 23 Current individual Harmonics 20 percentage | HAR20_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11500 | Input Channel 23 Current individual Harmonics 21 percentage | HAR21_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11502 | Input Channel 23 Current individual Harmonics 22 percentage | HAR22_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11504 | Input Channel 23 Current individual Harmonics 23 percentage | HAR23_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11506 | Input Channel 23 Current individual Harmonics 24 percentage | HAR24_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11508 | Input Channel 23 Current individual Harmonics 25 percentage | HAR25_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11510 | Input Channel 23 Current individual Harmonics 26 percentage | HAR26_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11512 | Input Channel 23 Current individual Harmonics 27 percentage | HAR27_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11514 | Input Channel 23 Current individual Harmonics 28 percentage | HAR28_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11516 | Input Channel 23 Current individual Harmonics 29 percentage | HAR29_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11518 | Input Channel 23 Current individual Harmonics 30 percentage | HAR30_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11520 | Input Channel 23 Current individual Harmonics 31 percentage | HAR31_I_023_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11522 | Input Channel 24 Current THD | THD_I_024_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11524 | Input Channel 24 Current THD Odd | OTHD_I_024_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11526 | Input Channel 24 Current THD Even | ETHD_I_024_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11528 | Input Channel 24 Current K Factor | KF_I_024_% | % |  | float32 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
11530 | Input Channel 24 Current individual Harmonics 2 percentage | HAR2_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11532 | Input Channel 24 Current individual Harmonics 3 percentage | HAR3_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11534 | Input Channel 24 Current individual Harmonics 4 percentage | HAR4_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11536 | Input Channel 24 Current individual Harmonics 5 percentage | HAR5_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11538 | Input Channel 24 Current individual Harmonics 6 percentage | HAR6_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11540 | Input Channel 24 Current individual Harmonics 7 percentage | HAR7_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11542 | Input Channel 24 Current individual Harmonics 8 percentage | HAR8_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11544 | Input Channel 24 Current individual Harmonics 9 percentage | HAR9_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11546 | Input Channel 24 Current individual Harmonics 10 percentage | HAR10_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11548 | Input Channel 24 Current individual Harmonics 11 percentage | HAR11_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11550 | Input Channel 24 Current individual Harmonics 12 percentage | HAR12_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11552 | Input Channel 24 Current individual Harmonics 13 percentage | HAR13_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11554 | Input Channel 24 Current individual Harmonics 14 percentage | HAR14_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11556 | Input Channel 24 Current individual Harmonics 15 percentage | HAR15_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11558 | Input Channel 24 Current individual Harmonics 16 percentage | HAR16_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11560 | Input Channel 24 Current individual Harmonics 17 percentage | HAR17_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11562 | Input Channel 24 Current individual Harmonics 18 percentage | HAR18_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11564 | Input Channel 24 Current individual Harmonics 19 percentage | HAR19_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11566 | Input Channel 24 Current individual Harmonics 20 percentage | HAR20_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11568 | Input Channel 24 Current individual Harmonics 21 percentage | HAR21_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11570 | Input Channel 24 Current individual Harmonics 22 percentage | HAR22_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11572 | Input Channel 24 Current individual Harmonics 23 percentage | HAR23_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11574 | Input Channel 24 Current individual Harmonics 24 percentage | HAR24_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11576 | Input Channel 24 Current individual Harmonics 25 percentage | HAR25_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11578 | Input Channel 24 Current individual Harmonics 26 percentage | HAR26_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11580 | Input Channel 24 Current individual Harmonics 27 percentage | HAR27_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11582 | Input Channel 24 Current individual Harmonics 28 percentage | HAR28_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11584 | Input Channel 24 Current individual Harmonics 29 percentage | HAR29_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11586 | Input Channel 24 Current individual Harmonics 30 percentage | HAR30_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11588 | Input Channel 24 Current individual Harmonics 31 percentage | HAR31_I_024_% | % |  | float32 | R | 2 | 1 | [7 empty] | harmonics |  | harmonics
11590 | User Channel 1 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s001 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11592 | User Channel 1 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s001 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11594 | User Channel 1 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s001 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11596 | User Channel 1 Current Positive Sequence Angle | ANG_SEQ_POS_I_s001 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11598 | User Channel 1 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s001 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11600 | User Channel 1 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s001 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11602 | User Channel 1 Current Unbalance Factor Magnitude | UNBL_I_s001_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11604 | User Channel 2 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s002 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11606 | User Channel 2 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s002 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11608 | User Channel 2 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s002 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11610 | User Channel 2 Current Positive Sequence Angle | ANG_SEQ_POS_I_s002 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11612 | User Channel 2 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s002 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11614 | User Channel 2 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s002 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11616 | User Channel 2 Current Unbalance Factor Magnitude | UNBL_I_s002_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11618 | User Channel 3 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s003 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11620 | User Channel 3 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s003 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11622 | User Channel 3 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s003 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11624 | User Channel 3 Current Positive Sequence Angle | ANG_SEQ_POS_I_s003 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11626 | User Channel 3 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s003 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11628 | User Channel 3 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s003 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11630 | User Channel 3 Current Unbalance Factor Magnitude | UNBL_I_s003_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11632 | User Channel 4 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s004 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11634 | User Channel 4 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s004 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11636 | User Channel 4 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s004 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11638 | User Channel 4 Current Positive Sequence Angle | ANG_SEQ_POS_I_s004 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11640 | User Channel 4 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s004 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11642 | User Channel 4 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s004 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11644 | User Channel 4 Current Unbalance Factor Magnitude | UNBL_I_s004_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11646 | User Channel 5 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s005 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11648 | User Channel 5 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s005 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11650 | User Channel 5 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s005 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11652 | User Channel 5 Current Positive Sequence Angle | ANG_SEQ_POS_I_s005 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11654 | User Channel 5 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s005 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11656 | User Channel 5 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s005 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11658 | User Channel 5 Current Unbalance Factor Magnitude | UNBL_I_s005_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11660 | User Channel 6 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s006 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11662 | User Channel 6 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s006 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11664 | User Channel 6 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s006 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11666 | User Channel 6 Current Positive Sequence Angle | ANG_SEQ_POS_I_s006 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11668 | User Channel 6 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s006 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11670 | User Channel 6 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s006 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11672 | User Channel 6 Current Unbalance Factor Magnitude | UNBL_I_s006_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11674 | User Channel 7 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s007 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11676 | User Channel 7 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s007 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11678 | User Channel 7 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s007 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11680 | User Channel 7 Current Positive Sequence Angle | ANG_SEQ_POS_I_s007 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11682 | User Channel 7 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s007 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11684 | User Channel 7 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s007 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11686 | User Channel 7 Current Unbalance Factor Magnitude | UNBL_I_s007_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11688 | User Channel 8 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s008 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11690 | User Channel 8 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s008 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11692 | User Channel 8 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s008 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11694 | User Channel 8 Current Positive Sequence Angle | ANG_SEQ_POS_I_s008 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11696 | User Channel 8 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s008 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11698 | User Channel 8 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s008 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11700 | User Channel 8 Current Unbalance Factor Magnitude | UNBL_I_s008_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11702 | User Channel 9 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s009 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11704 | User Channel 9 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s009 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11706 | User Channel 9 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s009 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11708 | User Channel 9 Current Positive Sequence Angle | ANG_SEQ_POS_I_s009 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11710 | User Channel 9 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s009 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11712 | User Channel 9 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s009 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11714 | User Channel 9 Current Unbalance Factor Magnitude | UNBL_I_s009_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11716 | User Channel 10 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s010 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11718 | User Channel 10 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s010 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11720 | User Channel 10 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s010 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11722 | User Channel 10 Current Positive Sequence Angle | ANG_SEQ_POS_I_s010 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11724 | User Channel 10 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s010 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11726 | User Channel 10 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s010 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11728 | User Channel 10 Current Unbalance Factor Magnitude | UNBL_I_s010_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11730 | User Channel 11 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s011 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11732 | User Channel 11 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s011 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11734 | User Channel 11 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s011 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11736 | User Channel 11 Current Positive Sequence Angle | ANG_SEQ_POS_I_s011 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11738 | User Channel 11 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s011 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11740 | User Channel 11 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s011 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11742 | User Channel 11 Current Unbalance Factor Magnitude | UNBL_I_s011_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11744 | User Channel 12 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s012 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11746 | User Channel 12 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s012 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11748 | User Channel 12 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s012 | A |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11750 | User Channel 12 Current Positive Sequence Angle | ANG_SEQ_POS_I_s012 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11752 | User Channel 12 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s012 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11754 | User Channel 12 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s012 | ° | 单位修改为° | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
11756 | User Channel 12 Current Unbalance Factor Magnitude | UNBL_I_s012_% | % |  | float32 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
12288 | Phase A active energy import | EP_IMP_a_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12292 | Phase A active energy export | EP_EXP_a_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12296 | Phase A active energy net | EP_NET_a_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12300 | Phase A active energy total | EP_TOTAL_a_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12304 | Phase A reactive energy import | EQ_IMP_a_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12308 | Phase A reactive energy export | EQ_EXP_a_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12312 | Phase A reactive energy net | EQ_NET_a_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12316 | Phase A reactive energy total | EQ_TOTAL_a_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12320 | Phase A apparent energy | ES_a_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12324 | Phase B active energy import | EP_IMP_b_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12328 | Phase B active energy export | EP_EXP_b_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12332 | Phase B active energy net | EP_NET_b_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12336 | Phase B active energy total | EP_TOTAL_b_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12340 | Phase B reactive energy import | EQ_IMP_b_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12344 | Phase B reactive energy export | EQ_EXP_b_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12348 | Phase B reactive energy net | EQ_NET_b_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12352 | Phase B reactive energy total | EQ_TOTAL_b_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12356 | Phase B apparent energy | ES_b_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12360 | Phase C active energy import | EP_IMP_c_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12364 | Phase C active energy export | EP_EXP_c_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12368 | Phase C active energy net | EP_NET_c_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12372 | Phase C active energy total | EP_TOTAL_c_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12376 | Phase C reactive energy import | EQ_IMP_c_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12380 | Phase C reactive energy export | EQ_EXP_c_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12384 | Phase C reactive energy net | EQ_NET_c_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12388 | Phase C reactive energy total | EQ_TOTAL_c_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12392 | Phase C apparent energy | ES_c_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12396 | System active energy import | EP_IMP_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12400 | System active energy export | EP_EXP_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12404 | System active energy net | EP_NET_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12408 | System active energy total | EP_TOTAL_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12412 | System reactive energy import | EQ_IMP_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12416 | System reactive energy export | EQ_EXP_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12420 | System reactive energy net | EQ_NET_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12424 | System reactive energy total | EQ_TOTAL_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12428 | System apparent energy | ES_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12432 | Input Channel 1 active energy import | EP_IMP_001_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12436 | Input Channel 1 active energy export | EP_EXP_001_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12440 | Input Channel 1 active energy net | EP_NET_001_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12444 | Input Channel 1 active energy total | EP_TOTAL_001_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12448 | Input Channel 1 reactive energy import | EQ_IMP_001_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12452 | Input Channel 1 reactive energy export | EQ_EXP_001_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12456 | Input Channel 1 reactive energy net | EQ_NET_001_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12460 | Input Channel 1 reactive energy total | EQ_TOTAL_001_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12464 | Input Channel 1 apparent energy | ES_001_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12468 | Input Channel 2 active energy import | EP_IMP_002_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12472 | Input Channel 2 active energy export | EP_EXP_002_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12476 | Input Channel 2 active energy net | EP_NET_002_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12480 | Input Channel 2 active energy total | EP_TOTAL_002_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12484 | Input Channel 2 reactive energy import | EQ_IMP_002_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12488 | Input Channel 2 reactive energy export | EQ_EXP_002_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12492 | Input Channel 2 reactive energy net | EQ_NET_002_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12496 | Input Channel 2 reactive energy total | EQ_TOTAL_002_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12500 | Input Channel 2 apparent energy | ES_002_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12504 | Input Channel 3 active energy import | EP_IMP_003_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12508 | Input Channel 3 active energy export | EP_EXP_003_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12512 | Input Channel 3 active energy net | EP_NET_003_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12516 | Input Channel 3 active energy total | EP_TOTAL_003_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12520 | Input Channel 3 reactive energy import | EQ_IMP_003_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12524 | Input Channel 3 reactive energy export | EQ_EXP_003_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12528 | Input Channel 3 reactive energy net | EQ_NET_003_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12532 | Input Channel 3 reactive energy total | EQ_TOTAL_003_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12536 | Input Channel 3 apparent energy | ES_003_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12540 | Input Channel 4 active energy import | EP_IMP_004_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12544 | Input Channel 4 active energy export | EP_EXP_004_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12548 | Input Channel 4 active energy net | EP_NET_004_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12552 | Input Channel 4 active energy total | EP_TOTAL_004_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12556 | Input Channel 4 reactive energy import | EQ_IMP_004_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12560 | Input Channel 4 reactive energy export | EQ_EXP_004_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12564 | Input Channel 4 reactive energy net | EQ_NET_004_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12568 | Input Channel 4 reactive energy total | EQ_TOTAL_004_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12572 | Input Channel 4 apparent energy | ES_004_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12576 | Input Channel 5 active energy import | EP_IMP_005_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12580 | Input Channel 5 active energy export | EP_EXP_005_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12584 | Input Channel 5 active energy net | EP_NET_005_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12588 | Input Channel 5 active energy total | EP_TOTAL_005_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12592 | Input Channel 5 reactive energy import | EQ_IMP_005_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12596 | Input Channel 5 reactive energy export | EQ_EXP_005_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12600 | Input Channel 5 reactive energy net | EQ_NET_005_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12604 | Input Channel 5 reactive energy total | EQ_TOTAL_005_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12608 | Input Channel 5 apparent energy | ES_005_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12612 | Input Channel 6 active energy import | EP_IMP_006_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12616 | Input Channel 6 active energy export | EP_EXP_006_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12620 | Input Channel 6 active energy net | EP_NET_006_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12624 | Input Channel 6 active energy total | EP_TOTAL_006_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12628 | Input Channel 6 reactive energy import | EQ_IMP_006_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12632 | Input Channel 6 reactive energy export | EQ_EXP_006_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12636 | Input Channel 6 reactive energy net | EQ_NET_006_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12640 | Input Channel 6 reactive energy total | EQ_TOTAL_006_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12644 | Input Channel 6 apparent energy | ES_006_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12648 | Input Channel 7 active energy import | EP_IMP_007_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12652 | Input Channel 7 active energy export | EP_EXP_007_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12656 | Input Channel 7 active energy net | EP_NET_007_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12660 | Input Channel 7 active energy total | EP_TOTAL_007_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12664 | Input Channel 7 reactive energy import | EQ_IMP_007_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12668 | Input Channel 7 reactive energy export | EQ_EXP_007_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12672 | Input Channel 7 reactive energy net | EQ_NET_007_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12676 | Input Channel 7 reactive energy total | EQ_TOTAL_007_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12680 | Input Channel 7 apparent energy | ES_007_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12684 | Input Channel 8 active energy import | EP_IMP_008_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12688 | Input Channel 8 active energy export | EP_EXP_008_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12692 | Input Channel 8 active energy net | EP_NET_008_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12696 | Input Channel 8 active energy total | EP_TOTAL_008_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12700 | Input Channel 8 reactive energy import | EQ_IMP_008_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12704 | Input Channel 8 reactive energy export | EQ_EXP_008_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12708 | Input Channel 8 reactive energy net | EQ_NET_008_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12712 | Input Channel 8 reactive energy total | EQ_TOTAL_008_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12716 | Input Channel 8 apparent energy | ES_008_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12720 | Input Channel 9 active energy import | EP_IMP_009_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12724 | Input Channel 9 active energy export | EP_EXP_009_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12728 | Input Channel 9 active energy net | EP_NET_009_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12732 | Input Channel 9 active energy total | EP_TOTAL_009_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12736 | Input Channel 9 reactive energy import | EQ_IMP_009_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12740 | Input Channel 9 reactive energy export | EQ_EXP_009_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12744 | Input Channel 9 reactive energy net | EQ_NET_009_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12748 | Input Channel 9 reactive energy total | EQ_TOTAL_009_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12752 | Input Channel 9 apparent energy | ES_009_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12756 | Input Channel 10 active energy import | EP_IMP_010_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12760 | Input Channel 10 active energy export | EP_EXP_010_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12764 | Input Channel 10 active energy net | EP_NET_010_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12768 | Input Channel 10 active energy total | EP_TOTAL_010_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12772 | Input Channel 10 reactive energy import | EQ_IMP_010_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12776 | Input Channel 10 reactive energy export | EQ_EXP_010_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12780 | Input Channel 10 reactive energy net | EQ_NET_010_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12784 | Input Channel 10 reactive energy total | EQ_TOTAL_010_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12788 | Input Channel 10 apparent energy | ES_010_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12792 | Input Channel 11 active energy import | EP_IMP_011_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12796 | Input Channel 11 active energy export | EP_EXP_011_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12800 | Input Channel 11 active energy net | EP_NET_011_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12804 | Input Channel 11 active energy total | EP_TOTAL_011_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12808 | Input Channel 11 reactive energy import | EQ_IMP_011_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12812 | Input Channel 11 reactive energy export | EQ_EXP_011_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12816 | Input Channel 11 reactive energy net | EQ_NET_011_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12820 | Input Channel 11 reactive energy total | EQ_TOTAL_011_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12824 | Input Channel 11 apparent energy | ES_011_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12828 | Input Channel 12 active energy import | EP_IMP_012_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12832 | Input Channel 12 active energy export | EP_EXP_012_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12836 | Input Channel 12 active energy net | EP_NET_012_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12840 | Input Channel 12 active energy total | EP_TOTAL_012_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12844 | Input Channel 12 reactive energy import | EQ_IMP_012_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12848 | Input Channel 12 reactive energy export | EQ_EXP_012_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12852 | Input Channel 12 reactive energy net | EQ_NET_012_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12856 | Input Channel 12 reactive energy total | EQ_TOTAL_012_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12860 | Input Channel 12 apparent energy | ES_012_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12864 | Input Channel 13 active energy import | EP_IMP_013_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12868 | Input Channel 13 active energy export | EP_EXP_013_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12872 | Input Channel 13 active energy net | EP_NET_013_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12876 | Input Channel 13 active energy total | EP_TOTAL_013_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12880 | Input Channel 13 reactive energy import | EQ_IMP_013_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12884 | Input Channel 13 reactive energy export | EQ_EXP_013_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12888 | Input Channel 13 reactive energy net | EQ_NET_013_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12892 | Input Channel 13 reactive energy total | EQ_TOTAL_013_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12896 | Input Channel 13 apparent energy | ES_013_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12900 | Input Channel 14 active energy import | EP_IMP_014_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12904 | Input Channel 14 active energy export | EP_EXP_014_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12908 | Input Channel 14 active energy net | EP_NET_014_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12912 | Input Channel 14 active energy total | EP_TOTAL_014_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12916 | Input Channel 14 reactive energy import | EQ_IMP_014_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12920 | Input Channel 14 reactive energy export | EQ_EXP_014_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12924 | Input Channel 14 reactive energy net | EQ_NET_014_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12928 | Input Channel 14 reactive energy total | EQ_TOTAL_014_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12932 | Input Channel 14 apparent energy | ES_014_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12936 | Input Channel 15 active energy import | EP_IMP_015_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12940 | Input Channel 15 active energy export | EP_EXP_015_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12944 | Input Channel 15 active energy net | EP_NET_015_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12948 | Input Channel 15 active energy total | EP_TOTAL_015_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12952 | Input Channel 15 reactive energy import | EQ_IMP_015_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12956 | Input Channel 15 reactive energy export | EQ_EXP_015_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12960 | Input Channel 15 reactive energy net | EQ_NET_015_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12964 | Input Channel 15 reactive energy total | EQ_TOTAL_015_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12968 | Input Channel 15 apparent energy | ES_015_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12972 | Input Channel 16 active energy import | EP_IMP_016_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12976 | Input Channel 16 active energy export | EP_EXP_016_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
12980 | Input Channel 16 active energy net | EP_NET_016_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12984 | Input Channel 16 active energy total | EP_TOTAL_016_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12988 | Input Channel 16 reactive energy import | EQ_IMP_016_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12992 | Input Channel 16 reactive energy export | EQ_EXP_016_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
12996 | Input Channel 16 reactive energy net | EQ_NET_016_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13000 | Input Channel 16 reactive energy total | EQ_TOTAL_016_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13004 | Input Channel 16 apparent energy | ES_016_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13008 | Input Channel 17 active energy import | EP_IMP_017_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13012 | Input Channel 17 active energy export | EP_EXP_017_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13016 | Input Channel 17 active energy net | EP_NET_017_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13020 | Input Channel 17 active energy total | EP_TOTAL_017_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13024 | Input Channel 17 reactive energy import | EQ_IMP_017_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13028 | Input Channel 17 reactive energy export | EQ_EXP_017_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13032 | Input Channel 17 reactive energy net | EQ_NET_017_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13036 | Input Channel 17 reactive energy total | EQ_TOTAL_017_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13040 | Input Channel 17 apparent energy | ES_017_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13044 | Input Channel 18 active energy import | EP_IMP_018_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13048 | Input Channel 18 active energy export | EP_EXP_018_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13052 | Input Channel 18 active energy net | EP_NET_018_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13056 | Input Channel 18 active energy total | EP_TOTAL_018_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13060 | Input Channel 18 reactive energy import | EQ_IMP_018_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13064 | Input Channel 18 reactive energy export | EQ_EXP_018_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13068 | Input Channel 18 reactive energy net | EQ_NET_018_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13072 | Input Channel 18 reactive energy total | EQ_TOTAL_018_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13076 | Input Channel 18 apparent energy | ES_018_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13080 | Input Channel 19 active energy import | EP_IMP_019_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13084 | Input Channel 19 active energy export | EP_EXP_019_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13088 | Input Channel 19 active energy net | EP_NET_019_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13092 | Input Channel 19 active energy total | EP_TOTAL_019_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13096 | Input Channel 19 reactive energy import | EQ_IMP_019_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13100 | Input Channel 19 reactive energy export | EQ_EXP_019_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13104 | Input Channel 19 reactive energy net | EQ_NET_019_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13108 | Input Channel 19 reactive energy total | EQ_TOTAL_019_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13112 | Input Channel 19 apparent energy | ES_019_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13116 | Input Channel 20 active energy import | EP_IMP_020_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13120 | Input Channel 20 active energy export | EP_EXP_020_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13124 | Input Channel 20 active energy net | EP_NET_020_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13128 | Input Channel 20 active energy total | EP_TOTAL_020_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13132 | Input Channel 20 reactive energy import | EQ_IMP_020_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13136 | Input Channel 20 reactive energy export | EQ_EXP_020_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13140 | Input Channel 20 reactive energy net | EQ_NET_020_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13144 | Input Channel 20 reactive energy total | EQ_TOTAL_020_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13148 | Input Channel 20 apparent energy | ES_020_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13152 | Input Channel 21 active energy import | EP_IMP_021_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13156 | Input Channel 21 active energy export | EP_EXP_021_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13160 | Input Channel 21 active energy net | EP_NET_021_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13164 | Input Channel 21 active energy total | EP_TOTAL_021_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13168 | Input Channel 21 reactive energy import | EQ_IMP_021_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13172 | Input Channel 21 reactive energy export | EQ_EXP_021_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13176 | Input Channel 21 reactive energy net | EQ_NET_021_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13180 | Input Channel 21 reactive energy total | EQ_TOTAL_021_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13184 | Input Channel 21 apparent energy | ES_021_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13188 | Input Channel 22 active energy import | EP_IMP_022_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13192 | Input Channel 22 active energy export | EP_EXP_022_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13196 | Input Channel 22 active energy net | EP_NET_022_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13200 | Input Channel 22 active energy total | EP_TOTAL_022_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13204 | Input Channel 22 reactive energy import | EQ_IMP_022_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13208 | Input Channel 22 reactive energy export | EQ_EXP_022_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13212 | Input Channel 22 reactive energy net | EQ_NET_022_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13216 | Input Channel 22 reactive energy total | EQ_TOTAL_022_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13220 | Input Channel 22 apparent energy | ES_022_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13224 | Input Channel 23 active energy import | EP_IMP_023_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13228 | Input Channel 23 active energy export | EP_EXP_023_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13232 | Input Channel 23 active energy net | EP_NET_023_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13236 | Input Channel 23 active energy total | EP_TOTAL_023_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13240 | Input Channel 23 reactive energy import | EQ_IMP_023_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13244 | Input Channel 23 reactive energy export | EQ_EXP_023_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13248 | Input Channel 23 reactive energy net | EQ_NET_023_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13252 | Input Channel 23 reactive energy total | EQ_TOTAL_023_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13256 | Input Channel 23 apparent energy | ES_023_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13260 | Input Channel 24 active energy import | EP_IMP_024_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13264 | Input Channel 24 active energy export | EP_EXP_024_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13268 | Input Channel 24 active energy net | EP_NET_024_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13272 | Input Channel 24 active energy total | EP_TOTAL_024_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13276 | Input Channel 24 reactive energy import | EQ_IMP_024_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13280 | Input Channel 24 reactive energy export | EQ_EXP_024_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13284 | Input Channel 24 reactive energy net | EQ_NET_024_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13288 | Input Channel 24 reactive energy total | EQ_TOTAL_024_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13292 | Input Channel 24 apparent energy | ES_024_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13296 | User Channel 1 active energy import | EP_IMP_s001_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13300 | User Channel 1 active energy export | EP_EXP_s001_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13304 | User Channel 1 active energy net | EP_NET_s001_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13308 | User Channel 1 active energy total | EP_TOTAL_s001_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13312 | User Channel 1 reactive energy import | EQ_IMP_s001_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13316 | User Channel 1 reactive energy export | EQ_EXP_s001_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13320 | User Channel 1 reactive energy net | EQ_NET_s001_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13324 | User Channel 1 reactive energy total | EQ_TOTAL_s001_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13328 | User Channel 1 apparent energy | ES_s001_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13332 | User Channel 2 active energy import | EP_IMP_s002_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13336 | User Channel 2 active energy export | EP_EXP_s002_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13340 | User Channel 2 active energy net | EP_NET_s002_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13344 | User Channel 2 active energy total | EP_TOTAL_s002_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13348 | User Channel 2 reactive energy import | EQ_IMP_s002_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13352 | User Channel 2 reactive energy export | EQ_EXP_s002_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13356 | User Channel 2 reactive energy net | EQ_NET_s002_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13360 | User Channel 2 reactive energy total | EQ_TOTAL_s002_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13364 | User Channel 2 apparent energy | ES_s002_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13368 | User Channel 3 active energy import | EP_IMP_s003_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13372 | User Channel 3 active energy export | EP_EXP_s003_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13376 | User Channel 3 active energy net | EP_NET_s003_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13380 | User Channel 3 active energy total | EP_TOTAL_s003_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13384 | User Channel 3 reactive energy import | EQ_IMP_s003_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13388 | User Channel 3 reactive energy export | EQ_EXP_s003_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13392 | User Channel 3 reactive energy net | EQ_NET_s003_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13396 | User Channel 3 reactive energy total | EQ_TOTAL_s003_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13400 | User Channel 3 apparent energy | ES_s003_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13404 | User Channel 4 active energy import | EP_IMP_s004_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13408 | User Channel 4 active energy export | EP_EXP_s004_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13412 | User Channel 4 active energy net | EP_NET_s004_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13416 | User Channel 4 active energy total | EP_TOTAL_s004_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13420 | User Channel 4 reactive energy import | EQ_IMP_s004_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13424 | User Channel 4 reactive energy export | EQ_EXP_s004_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13428 | User Channel 4 reactive energy net | EQ_NET_s004_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13432 | User Channel 4 reactive energy total | EQ_TOTAL_s004_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13436 | User Channel 4 apparent energy | ES_s004_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13440 | User Channel 5 active energy import | EP_IMP_s005_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13444 | User Channel 5 active energy export | EP_EXP_s005_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13448 | User Channel 5 active energy net | EP_NET_s005_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13452 | User Channel 5 active energy total | EP_TOTAL_s005_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13456 | User Channel 5 reactive energy import | EQ_IMP_s005_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13460 | User Channel 5 reactive energy export | EQ_EXP_s005_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13464 | User Channel 5 reactive energy net | EQ_NET_s005_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13468 | User Channel 5 reactive energy total | EQ_TOTAL_s005_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13472 | User Channel 5 apparent energy | ES_s005_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13476 | User Channel 6 active energy import | EP_IMP_s006_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13480 | User Channel 6 active energy export | EP_EXP_s006_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13484 | User Channel 6 active energy net | EP_NET_s006_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13488 | User Channel 6 active energy total | EP_TOTAL_s006_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13492 | User Channel 6 reactive energy import | EQ_IMP_s006_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13496 | User Channel 6 reactive energy export | EQ_EXP_s006_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13500 | User Channel 6 reactive energy net | EQ_NET_s006_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13504 | User Channel 6 reactive energy total | EQ_TOTAL_s006_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13508 | User Channel 6 apparent energy | ES_s006_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13512 | User Channel 7 active energy import | EP_IMP_s007_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13516 | User Channel 7 active energy export | EP_EXP_s007_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13520 | User Channel 7 active energy net | EP_NET_s007_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13524 | User Channel 7 active energy total | EP_TOTAL_s007_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13528 | User Channel 7 reactive energy import | EQ_IMP_s007_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13532 | User Channel 7 reactive energy export | EQ_EXP_s007_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13536 | User Channel 7 reactive energy net | EQ_NET_s007_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13540 | User Channel 7 reactive energy total | EQ_TOTAL_s007_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13544 | User Channel 7 apparent energy | ES_s007_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13548 | User Channel 8 active energy import | EP_IMP_s008_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13552 | User Channel 8 active energy export | EP_EXP_s008_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13556 | User Channel 8 active energy net | EP_NET_s008_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13560 | User Channel 8 active energy total | EP_TOTAL_s008_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13564 | User Channel 8 reactive energy import | EQ_IMP_s008_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13568 | User Channel 8 reactive energy export | EQ_EXP_s008_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13572 | User Channel 8 reactive energy net | EQ_NET_s008_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13576 | User Channel 8 reactive energy total | EQ_TOTAL_s008_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13580 | User Channel 8 apparent energy | ES_s008_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13584 | User Channel 9 active energy import | EP_IMP_s009_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13588 | User Channel 9 active energy export | EP_EXP_s009_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13592 | User Channel 9 active energy net | EP_NET_s009_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13596 | User Channel 9 active energy total | EP_TOTAL_s009_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13600 | User Channel 9 reactive energy import | EQ_IMP_s009_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13604 | User Channel 9 reactive energy export | EQ_EXP_s009_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13608 | User Channel 9 reactive energy net | EQ_NET_s009_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13612 | User Channel 9 reactive energy total | EQ_TOTAL_s009_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13616 | User Channel 9 apparent energy | ES_s009_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13620 | User Channel 10 active energy import | EP_IMP_s010_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13624 | User Channel 10 active energy export | EP_EXP_s010_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13628 | User Channel 10 active energy net | EP_NET_s010_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13632 | User Channel 10 active energy total | EP_TOTAL_s010_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13636 | User Channel 10 reactive energy import | EQ_IMP_s010_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13640 | User Channel 10 reactive energy export | EQ_EXP_s010_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13644 | User Channel 10 reactive energy net | EQ_NET_s010_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13648 | User Channel 10 reactive energy total | EQ_TOTAL_s010_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13652 | User Channel 10 apparent energy | ES_s010_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13656 | User Channel 11 active energy import | EP_IMP_s011_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13660 | User Channel 11 active energy export | EP_EXP_s011_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13664 | User Channel 11 active energy net | EP_NET_s011_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13668 | User Channel 11 active energy total | EP_TOTAL_s011_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13672 | User Channel 11 reactive energy import | EQ_IMP_s011_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13676 | User Channel 11 reactive energy export | EQ_EXP_s011_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13680 | User Channel 11 reactive energy net | EQ_NET_s011_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13684 | User Channel 11 reactive energy total | EQ_TOTAL_s011_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13688 | User Channel 11 apparent energy | ES_s011_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13692 | User Channel 12 active energy import | EP_IMP_s012_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13696 | User Channel 12 active energy export | EP_EXP_s012_kWh | kWh |  | double | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
13700 | User Channel 12 active energy net | EP_NET_s012_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13704 | User Channel 12 active energy total | EP_TOTAL_s012_kWh | kWh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13708 | User Channel 12 reactive energy import | EQ_IMP_s012_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13712 | User Channel 12 reactive energy export | EQ_EXP_s012_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13716 | User Channel 12 reactive energy net | EQ_NET_s012_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13720 | User Channel 12 reactive energy total | EQ_TOTAL_s012_kvarh | kvarh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
13724 | User Channel 12 apparent energy | ES_s012_kVAh | kVAh |  | double | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
25600 | DI1 pulse count | DI_PC_001 |  |  | uint32 | RW | 2 | 1 |  |  |  | DI | DI | DI | DI | DI | DI | DI
25602 | DI2 pulse count | DI_PC_002 |  |  | uint32 | RW | 2 | 1 |  |  |  | DI | DI | DI | DI | DI | DI | DI
25604 | DI3 pulse count | DI_PC_003 |  |  | uint32 | RW | 2 | 1 |  |  |  | DI | DI | DI | DI | DI | DI | DI
25606 | DI4 pulse count | DI_PC_004 |  |  | uint32 | RW | 2 | 1 |  |  |  | DI | DI | DI | DI | DI | DI | DI
0 | DI1 status | DI_ST_001 |  |  | uint16 | R | 1 | 1 | DI |  |  | DI | DI | DI | DI | DI | DI | DI
1 | DI2 status | DI_ST_002 |  |  | uint16 | R | 1 | 1 | DI |  |  | DI | DI | DI | DI | DI | DI | DI
2 | DI3 status | DI_ST_003 |  |  | uint16 | R | 1 | 1 | DI |  |  | DI | DI | DI | DI | DI | DI | DI
3 | DI4 status | DI_ST_004 |  |  | uint16 | R | 1 | 1 | DI |  |  | DI | DI | DI | DI | DI | DI | DI
0 | DO1 status | DO_ST_001 |  |  | uint16 | RW | 1 | 1 |  |  |  | DO | DO | DO | DO | DO | DO | DO
1 | DO2 status | DO_ST_002 |  |  | uint16 | RW | 1 | 1 |  |  |  | DO | DO | DO | DO | DO | DO | DO
2 | DO3 status | DO_ST_003 |  |  | uint16 | RW | 1 | 1 |  |  |  | DO | DO | DO | DO | DO | DO | DO
3 | DO4 status | DO_ST_004 |  |  | uint16 | RW | 1 | 1 |  |  |  | DO | DO | DO | DO | DO | DO | DO
4 | DO5 status | DO_ST_005 |  |  | uint16 | RW | 1 | 1 |  |  |  | DO | DO | DO | DO | DO | DO | DO
5 | DO6 status | DO_ST_006 |  |  | uint16 | RW | 1 | 1 |  |  |  | DO | DO | DO | DO | DO | DO | DO
6 | DO7 status | DO_ST_007 |  |  | uint16 | RW | 1 | 1 |  |  |  | DO | DO | DO | DO | DO | DO | DO
7 | DO8 status | DO_ST_008 |  |  | uint16 | RW | 1 | 1 |  |  |  | DO | DO | DO | DO | DO | DO | DO
32 | RO1 status | RO_ST_001 |  |  | uint16 | RW | 1 | 1 |  |  |  | RO | RO | RO | RO | RO | RO | RO
33 | RO2 status | RO_ST_002 |  |  | uint16 | RW | 1 | 1 |  |  |  | RO | RO | RO | RO | RO | RO | RO
25856 | Current Rated Value | Conf_NominalCurrent |  |  | uint16 | RW | 1 | 1
25857 | Voltage Rated Value | Conf_NominalVolt |  |  | uint16 | RW | 1 | 1
25858 | Voltage Sag Enable | Conf_VoltSag_Enable |  |  | uint16 | RW | 1 | 1
25859 | Voltage Sag Threshold | Conf_VoltSag_Threshold |  |  | uint16 | RW | 1 | 1
25860 | Voltage Sag Jitter | Conf_VoltSag_Hyst |  |  | uint16 | RW | 1 | 1
25861 | Voltage Sag Triggers Waveform Recording | Conf_VoltSag_TrigWave |  |  | uint16 | RW | 1 | 1
25862 | Voltage Sag - switch to output DO | Conf_VoltSag_TrigDO |  |  | uint16 | RW | 1 | 1
25863 | Voltage Sag - switch to output RO | Conf_VoltSag_TrigRO |  |  | uint16 | RW | 1 | 1
25864 | Voltage Swell Enable | Conf_VoltSwell_Enable |  |  | uint16 | RW | 1 | 1
25865 | Voltage Swell Threshold | Conf_VoltSwell_Threshold |  |  | uint16 | RW | 1 | 1
25866 | Voltage Swell Jitter | Conf_VoltSwell_Hyst |  |  | uint16 | RW | 1 | 1
25867 | Voltage Swell Triggers Waveform Recording | Conf_VoltSwell_TrigWave |  |  | uint16 | RW | 1 | 1
25868 | Voltage Swell - switch to output DO | Conf_VoltSwell_TrigDO |  |  | uint16 | RW | 1 | 1
25869 | Voltage Swell - switch to output RO | Conf_VoltSwell_TrigRO |  |  | uint16 | RW | 1 | 1
25870 | Voltage Interruption Enable | Conf_VoltInt_Enable |  |  | uint16 | RW | 1 | 1
25871 | Voltage Interruption Threshold | Conf_VoltInt_Threshold |  |  | uint16 | RW | 1 | 1
25872 | Voltage Interruption Jitter | Conf_VoltInt_Hyst |  |  | uint16 | RW | 1 | 1
25873 | Voltage Interruption Triggers Waveform Recording | Conf_VoltInt_TrigWave |  |  | uint16 | RW | 1 | 1
25874 | Voltage Interruption - switch to output DO | Conf_VoltInt_TrigDO |  |  | uint16 | RW | 1 | 1
25875 | Voltage Interruption - switch to output RO | Conf_VoltInt_TrigRO |  |  | uint16 | RW | 1 | 1
25876 | Current Swell Enable | Conf_CurrentSwell_Enable |  |  | uint16 | RW | 1 | 1
25877 | Current Swell Threshold | Conf_CurrentSwell_Threshold |  |  | uint16 | RW | 1 | 1
25878 | Current Swell Jitter | Conf_CurrentSwell_Hyst |  |  | uint16 | RW | 1 | 1
25879 | Current Triggers Waveform Recording | Conf_CurrentSwell_TrigWave |  |  | uint16 | RW | 1 | 1
25880 | Current Swell - switch to output DO | Conf_CurrentSwell_TrigDO |  |  | uint16 | RW | 1 | 1
25881 | Current Swell - switch to output RO | Conf_CurrentSwell_TrigRO |  |  | uint16 | RW | 1 | 1
25968 | sampling rate | Conf_SampleRate |  |  | uint16 | RW | 1 | 1
25969 | Number of cycles before the event occurred | Conf_Cyc_Pre_Evt |  |  | uint16 | RW | 1 | 1
25970 | Number of cycles after the event occurred | Conf_Cyc_Post_Evt |  |  | uint16 | RW | 1 | 1
25971 | DI1 Trigger | Conf_DI1_Trig |  |  | uint16 | RW | 1 | 1
25972 | DI2 Trigger | Conf_DI2_Trig |  |  | uint16 | RW | 1 | 1
25973 | DI3 Trigger | Conf_DI3_Trig |  |  | uint16 | RW | 1 | 1
25974 | DI4 Trigger | Conf_DI4_Trig |  |  | uint16 | RW | 1 | 1
25975 | Manually Trigger | Conf_Manual_Trig |  |  | uint16 | RW | 1 | 1
14080 | Phase A Max Current Demand | MAX_DMD_I_a_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14082 | Phase A Max Current Demand Timestamp | MAX_DMDTS_I_a_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14084 | Phase A Max Current Demand Timestamp | MAX_DMDTS_I_a_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14085 | Phase A Import Active Power Max Demand | MAX_DMD_IMP_P_a_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14087 | Phase A Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_a_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14089 | Phase A Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_a_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14090 | Phase A Export Active Power Max Demand | MAX_DMD_EXP_P_a_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14092 | Phase A Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_a_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14094 | Phase A Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_a_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14095 | Phase A Import Reactive Power Max Demand | MAX_DMD_IMP_Q_a_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14097 | Phase A Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_a_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14099 | Phase A Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_a_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14100 | Phase A Export Reactive Power Max Demand | MAX_DMD_EXP_Q_a_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14102 | Phase A Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_a_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14104 | Phase A Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_a_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14105 | Phase A Apparent Power Max Demand | MAX_DMD_S_a_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14107 | Phase A Apparent Power Max Demand Timestamp | MAX_DMDTS_S_a_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14109 | Phase A Apparent Power Max Demand Timestamp | MAX_DMDTS_S_a_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14110 | Phase B Current Max Demand | MAX_DMD_I_b_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14112 | Phase B Current Max Demand Timestamp | MAX_DMDTS_I_b_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14114 | Phase B Current Max Demand Timestamp | MAX_DMDTS_I_b_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14115 | Phase B Import Active Power Max Demand | MAX_DMD_IMP_P_b_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14117 | Phase B Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_b_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14119 | Phase B Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_b_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14120 | Phase B Export Active Power Max Demand | MAX_DMD_EXP_P_b_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14122 | Phase B Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_b_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14124 | Phase B Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_b_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14125 | Phase B Import Reactive Power Max Demand | MAX_DMD_IMP_Q_b_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14127 | Phase B Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_b_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14129 | Phase B Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_b_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14130 | Phase B Export Reactive Power Max Demand | MAX_DMD_EXP_Q_b_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14132 | Phase B Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_b_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14134 | Phase B Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_b_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14135 | Phase B Apparent Power Max Demand | MAX_DMD_S_b_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14137 | Phase B Apparent Power Max Demand Timestamp | MAX_DMDTS_S_b_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14139 | Phase B Apparent Power Max Demand Timestamp | MAX_DMDTS_S_b_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14140 | Phase C Current Max Demand | MAX_DMD_I_c_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14142 | Phase C Current Max Demand Timestamp | MAX_DMDTS_I_c_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14144 | Phase C Current Max Demand Timestamp | MAX_DMDTS_I_c_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14145 | Phase C Import Active Power Max Demand | MAX_DMD_IMP_P_c_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14147 | Phase C Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_c_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14149 | Phase C Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_c_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14150 | Phase C Export Active Power Max Demand | MAX_DMD_EXP_P_c_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14152 | Phase C Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_c_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14154 | Phase C Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_c_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14155 | Phase C Import Reactive Power Max Demand | MAX_DMD_IMP_Q_c_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14157 | Phase C Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_c_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14159 | Phase C Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_c_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14160 | Phase C Export Reactive Power Max Demand | MAX_DMD_EXP_Q_c_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14162 | Phase C Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_c_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14164 | Phase C Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_c_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14165 | Phase C Apparent Power Max Demand | MAX_DMD_S_c_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14167 | Phase C Apparent Power Max Demand Timestamp | MAX_DMDTS_S_c_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14169 | Phase C Apparent Power Max Demand Timestamp | MAX_DMDTS_S_c_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14170 | System Average Current Max Demand | MAX_DMD_I_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14172 | System Average Current Max Demand Timestamp | MAX_DMDTS_I_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14174 | System Average Current Max Demand Timestamp | MAX_DMDTS_I_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14175 | System Import Active Power Max Demand | MAX_DMD_IMP_P_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14177 | System Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14179 | System Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14180 | System Export Active Power Max Demand | MAX_DMD_EXP_P_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14182 | System Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14184 | System Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14185 | System Import Reactive Power Max Demand | MAX_DMD_IMP_Q_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14187 | System Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14189 | System Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14190 | System Export Reactive Power Max Demand | MAX_DMD_EXP_Q_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14192 | System Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14194 | System Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14195 | System Apparent Power Max Demand | MAX_DMD_S_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14197 | System Apparent Power Max Demand Timestamp | MAX_DMDTS_S_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14199 | System Apparent Power Max Demand Timestamp | MAX_DMDTS_S_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14200 | Input Channel 1 Current Max Demand | MAX_DMD_I_001_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14202 | Input Channel 1 Current Max Demand Timestamp | MAX_DMDTS_I_001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14204 | Input Channel 1 Current Max Demand Timestamp | MAX_DMDTS_I_001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14205 | Input Channel 1 Import Active Power Max Demand | MAX_DMD_IMP_P_001_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14207 | Input Channel 1 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14209 | Input Channel 1 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14210 | Input Channel 1 Export Active Power Max Demand | MAX_DMD_EXP_P_001_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14212 | Input Channel 1 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14214 | Input Channel 1 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14215 | Input Channel 1 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_001_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14217 | Input Channel 1 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14219 | Input Channel 1 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14220 | Input Channel 1 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_001_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14222 | Input Channel 1 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14224 | Input Channel 1 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14225 | Input Channel 1 Apparent Power Max Demand | MAX_DMD_S_001_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14227 | Input Channel 1 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14229 | Input Channel 1 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14230 | Input Channel 2 Current Max Demand | MAX_DMD_I_002_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14232 | Input Channel 2 Current Max Demand Timestamp | MAX_DMDTS_I_002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14234 | Input Channel 2 Current Max Demand Timestamp | MAX_DMDTS_I_002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14235 | Input Channel 2 Import Active Power Max Demand | MAX_DMD_IMP_P_002_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14237 | Input Channel 2 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14239 | Input Channel 2 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14240 | Input Channel 2 Export Active Power Max Demand | MAX_DMD_EXP_P_002_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14242 | Input Channel 2 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14244 | Input Channel 2 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14245 | Input Channel 2 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_002_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14247 | Input Channel 2 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14249 | Input Channel 2 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14250 | Input Channel 2 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_002_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14252 | Input Channel 2 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14254 | Input Channel 2 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14255 | Input Channel 2 Apparent Power Max Demand | MAX_DMD_S_002_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14257 | Input Channel 2 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14259 | Input Channel 2 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14260 | Input Channel 3 Current Max Demand | MAX_DMD_I_003_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14262 | Input Channel 3 Current Max Demand Timestamp | MAX_DMDTS_I_003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14264 | Input Channel 3 Current Max Demand Timestamp | MAX_DMDTS_I_003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14265 | Input Channel 3 Import Active Power Max Demand | MAX_DMD_IMP_P_003_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14267 | Input Channel 3 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14269 | Input Channel 3 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14270 | Input Channel 3 Export Active Power Max Demand | MAX_DMD_EXP_P_003_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14272 | Input Channel 3 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14274 | Input Channel 3 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14275 | Input Channel 3 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_003_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14277 | Input Channel 3 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14279 | Input Channel 3 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14280 | Input Channel 3 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_003_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14282 | Input Channel 3 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14284 | Input Channel 3 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14285 | Input Channel 3 Apparent Power Max Demand | MAX_DMD_S_003_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14287 | Input Channel 3 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14289 | Input Channel 3 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14290 | Input Channel 4 Current Max Demand | MAX_DMD_I_004_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14292 | Input Channel 4 Current Max Demand Timestamp | MAX_DMDTS_I_004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14294 | Input Channel 4 Current Max Demand Timestamp | MAX_DMDTS_I_004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14295 | Input Channel 4 Import Active Power Max Demand | MAX_DMD_IMP_P_004_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14297 | Input Channel 4 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14299 | Input Channel 4 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14300 | Input Channel 4 Export Active Power Max Demand | MAX_DMD_EXP_P_004_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14302 | Input Channel 4 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14304 | Input Channel 4 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14305 | Input Channel 4 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_004_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14307 | Input Channel 4 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14309 | Input Channel 4 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14310 | Input Channel 4 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_004_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14312 | Input Channel 4 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14314 | Input Channel 4 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14315 | Input Channel 4 Apparent Power Max Demand | MAX_DMD_S_004_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14317 | Input Channel 4 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14319 | Input Channel 4 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14320 | Input Channel 5 Current Max Demand | MAX_DMD_I_005_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14322 | Input Channel 5 Current Max Demand Timestamp | MAX_DMDTS_I_005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14324 | Input Channel 5 Current Max Demand Timestamp | MAX_DMDTS_I_005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14325 | Input Channel 5 Import Active Power Max Demand | MAX_DMD_IMP_P_005_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14327 | Input Channel 5 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14329 | Input Channel 5 Import Active Power Max Demand timestamp | MAX_DMDTS_IMP_P_005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14330 | Input Channel 5 Export Active Power Max Demand | MAX_DMD_EXP_P_005_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14332 | Input Channel 5 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14334 | Input Channel 5 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14335 | Input Channel 5 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_005_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14337 | Input Channel 5 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14339 | Input Channel 5 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14340 | Input Channel 5 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_005_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14342 | Input Channel 5 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14344 | Input Channel 5 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14345 | Input Channel 5 Apparent Power Max Demand | MAX_DMD_S_005_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14347 | Input Channel 5 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14349 | Input Channel 5 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14350 | Input Channel 6 Current Max Demand | MAX_DMD_I_006_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14352 | Input Channel 6 Current Max Demand Timestamp | MAX_DMDTS_I_006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14354 | Input Channel 6 Current Max Demand Timestamp | MAX_DMDTS_I_006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14355 | Input Channel 6 Import Active Power Max Demand | MAX_DMD_IMP_P_006_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14357 | Input Channel 6 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14359 | Input Channel 6 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14360 | Input Channel 6 Export Active Power Max Demand | MAX_DMD_EXP_P_006_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14362 | Input Channel 6 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14364 | Input Channel 6 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14365 | Input Channel 6 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_006_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14367 | Input Channel 6 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14369 | Input Channel 6 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14370 | Input Channel 6 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_006_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14372 | Input Channel 6 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14374 | Input Channel 6 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14375 | Input Channel 6 Apparent Power Max Demand | MAX_DMD_S_006_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14377 | Input Channel 6 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14379 | Input Channel 6 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14380 | Input Channel 7 Current Max Demand | MAX_DMD_I_007_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14382 | Input Channel 7 Current Max Demand Timestamp | MAX_DMDTS_I_007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14384 | Input Channel 7 Current Max Demand Timestamp | MAX_DMDTS_I_007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14385 | Input Channel 7 Import Active Power Max Demand | MAX_DMD_IMP_P_007_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14387 | Input Channel 7 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14389 | Input Channel 7 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14390 | Input Channel 7 Export Active Power Max Demand | MAX_DMD_EXP_P_007_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14392 | Input Channel 7 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14394 | Input Channel 7 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14395 | Input Channel 7 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_007_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14397 | Input Channel 7 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14399 | Input Channel 7 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14400 | Input Channel 7 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_007_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14402 | Input Channel 7 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14404 | Input Channel 7 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14405 | Input Channel 7 Apparent Power Max Demand | MAX_DMD_S_007_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14407 | Input Channel 7 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14409 | Input Channel 7 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14410 | Input Channel 8 Current Max Demand | MAX_DMD_I_008_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14412 | Input Channel 8 Current Max Demand Timestamp | MAX_DMDTS_I_008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14414 | Input Channel 8 Current Max Demand Timestamp | MAX_DMDTS_I_008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14415 | Input Channel 8 Import Active Power Max Demand | MAX_DMD_IMP_P_008_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14417 | Input Channel 8 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14419 | Input Channel 8 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14420 | Input Channel 8 Export Active Power Max Demand | MAX_DMD_EXP_P_008_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14422 | Input Channel 8 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14424 | Input Channel 8 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14425 | Input Channel 8 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_008_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14427 | Input Channel 8 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14429 | Input Channel 8 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14430 | Input Channel 8 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_008_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14432 | Input Channel 8 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14434 | Input Channel 8 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14435 | Input Channel 8 Apparent Power Max Demand | MAX_DMD_S_008_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14437 | Input Channel 8 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14439 | Input Channel 8 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14440 | Input Channel 9 Current Max Demand | MAX_DMD_I_009_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14442 | Input Channel 9 Current Max Demand Timestamp | MAX_DMDTS_I_009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14444 | Input Channel 9 Current Max Demand Timestamp | MAX_DMDTS_I_009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14445 | Input Channel 9 Import Active Power Max Demand | MAX_DMD_IMP_P_009_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14447 | Input Channel 9 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14449 | Input Channel 9 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14450 | Input Channel 9 Export Active Power Max Demand | MAX_DMD_EXP_P_009_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14452 | Input Channel 9 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14454 | Input Channel 9 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14455 | Input Channel 9 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_009_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14457 | Input Channel 9 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14459 | Input Channel 9 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14460 | Input Channel 9 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_009_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14462 | Input Channel 9 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14464 | Input Channel 9 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14465 | Input Channel 9 Apparent Power Max Demand | MAX_DMD_S_009_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14467 | Input Channel 9 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14469 | Input Channel 9 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14470 | Input Channel 10 Current Max Demand | MAX_DMD_I_010_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14472 | Input Channel 10 Current Max Demand Timestamp | MAX_DMDTS_I_010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14474 | Input Channel 10 Current Max Demand Timestamp | MAX_DMDTS_I_010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14475 | Input Channel 10 Import Active Power Max Demand | MAX_DMD_IMP_P_010_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14477 | Input Channel 10 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14479 | Input Channel 10 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14480 | Input Channel 10 Export Active Power Max Demand | MAX_DMD_EXP_P_010_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14482 | Input Channel 10 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14484 | Input Channel 10 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14485 | Input Channel 10 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_010_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14487 | Input Channel 10 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14489 | Input Channel 10 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14490 | Input Channel 10 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_010_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14492 | Input Channel 10 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14494 | Input Channel 10 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14495 | Input Channel 10 Apparent Power Max Demand | MAX_DMD_S_010_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14497 | Input Channel 10 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14499 | Input Channel 10 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14500 | Input Channel 11 Current Max Demand | MAX_DMD_I_011_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14502 | Input Channel 11 Current Max Demand Timestamp | MAX_DMDTS_I_011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14504 | Input Channel 11 Current Max Demand Timestamp | MAX_DMDTS_I_011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14505 | Input Channel 11 Import Active Power Max Demand | MAX_DMD_IMP_P_011_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14507 | Input Channel 11 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14509 | Input Channel 11 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14510 | Input Channel 11 Export Active Power Max Demand | MAX_DMD_EXP_P_011_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14512 | Input Channel 11 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14514 | Input Channel 11 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14515 | Input Channel 11 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_011_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14517 | Input Channel 11 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14519 | Input Channel 11 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14520 | Input Channel 11 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_011_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14522 | Input Channel 11 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14524 | Input Channel 11 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14525 | Input Channel 11 Apparent Power Max Demand | MAX_DMD_S_011_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14527 | Input Channel 11 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14529 | Input Channel 11 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14530 | Input Channel 12 Current Max Demand | MAX_DMD_I_012_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14532 | Input Channel 12 Current Max Demand Timestamp | MAX_DMDTS_I_012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14534 | Input Channel 12 Current Max Demand Timestamp | MAX_DMDTS_I_012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14535 | Input Channel 12 Import Active Power Max Demand | MAX_DMD_IMP_P_012_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14537 | Input Channel 12 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14539 | Input Channel 12 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14540 | Input Channel 12 Export Active Power Max Demand | MAX_DMD_EXP_P_012_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14542 | Input Channel 12 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14544 | Input Channel 12 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14545 | Input Channel 12 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_012_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14547 | Input Channel 12 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14549 | Input Channel 12 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14550 | Input Channel 12 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_012_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14552 | Input Channel 12 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14554 | Input Channel 12 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14555 | Input Channel 12 Apparent Power Max Demand | MAX_DMD_S_012_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14557 | Input Channel 12 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14559 | Input Channel 12 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14560 | Input Channel 13 Current Max Demand | MAX_DMD_I_013_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14562 | Input Channel 13 Current Max Demand Timestamp | MAX_DMDTS_I_013_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14564 | Input Channel 13 Current Max Demand Timestamp | MAX_DMDTS_I_013_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14565 | Input Channel 13 Import Active Power Max Demand | MAX_DMD_IMP_P_013_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14567 | Input Channel 13 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_013_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14569 | Input Channel 13 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_013_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14570 | Input Channel 13 Export Active Power Max Demand | MAX_DMD_EXP_P_013_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14572 | Input Channel 13 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_013_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14574 | Input Channel 13 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_013_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14575 | Input Channel 13 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_013_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14577 | Input Channel 13 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_013_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14579 | Input Channel 13 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_013_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14580 | Input Channel 13 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_013_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14582 | Input Channel 13 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_013_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14584 | Input Channel 13 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_013_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14585 | Input Channel 13 Apparent Power Max Demand | MAX_DMD_S_013_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14587 | Input Channel 13 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_013_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14589 | Input Channel 13 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_013_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14590 | Input Channel 14 Current Max Demand | MAX_DMD_I_014_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14592 | Input Channel 14 Current Max Demand Timestamp | MAX_DMDTS_I_014_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14594 | Input Channel 14 Current Max Demand Timestamp | MAX_DMDTS_I_014_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14595 | Input Channel 14 Import Active Power Max Demand | MAX_DMD_IMP_P_014_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14597 | Input Channel 14 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_014_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14599 | Input Channel 14 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_014_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14600 | Input Channel 14 Export Active Power Max Demand | MAX_DMD_EXP_P_014_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14602 | Input Channel 14 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_014_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14604 | Input Channel 14 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_014_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14605 | Input Channel 14 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_014_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14607 | Input Channel 14 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_014_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14609 | Input Channel 14 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_014_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14610 | Input Channel 14 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_014_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14612 | Input Channel 14 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_014_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14614 | Input Channel 14 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_014_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14615 | Input Channel 14 Apparent Power Max Demand | MAX_DMD_S_014_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14617 | Input Channel 14 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_014_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14619 | Input Channel 14 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_014_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14620 | Input Channel 15 Current Max Demand | MAX_DMD_I_015_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14622 | Input Channel 15 Current Max Demand Timestamp | MAX_DMDTS_I_015_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14624 | Input Channel 15 Current Max Demand Timestamp | MAX_DMDTS_I_015_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14625 | Input Channel 15 Import Active Power Max Demand | MAX_DMD_IMP_P_015_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14627 | Input Channel 15 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_015_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14629 | Input Channel 15 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_015_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14630 | Input Channel 15 Export Active Power Max Demand | MAX_DMD_EXP_P_015_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14632 | Input Channel 15 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_015_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14634 | Input Channel 15 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_015_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14635 | Input Channel 15 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_015_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14637 | Input Channel 15 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_015_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14639 | Input Channel 15 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_015_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14640 | Input Channel 15 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_015_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14642 | Input Channel 15 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_015_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14644 | Input Channel 15 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_015_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14645 | Input Channel 15 Apparent Power Max Demand | MAX_DMD_S_015_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14647 | Input Channel 15 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_015_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14649 | Input Channel 15 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_015_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14650 | Input Channel 16 Current Max Demand | MAX_DMD_I_016_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14652 | Input Channel 16 Current Max Demand Timestamp | MAX_DMDTS_I_016_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14654 | Input Channel 16 Current Max Demand Timestamp | MAX_DMDTS_I_016_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14655 | Input Channel 16 Import Active Power Max Demand | MAX_DMD_IMP_P_016_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14657 | Input Channel 16 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_016_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14659 | Input Channel 16 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_016_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14660 | Input Channel 16 Export Active Power Max Demand | MAX_DMD_EXP_P_016_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14662 | Input Channel 16 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_016_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14664 | Input Channel 16 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_016_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14665 | Input Channel 16 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_016_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14667 | Input Channel 16 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_016_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14669 | Input Channel 16 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_016_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14670 | Input Channel 16 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_016_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14672 | Input Channel 16 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_016_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14674 | Input Channel 16 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_016_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14675 | Input Channel 16 Apparent Power Max Demand | MAX_DMD_S_016_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14677 | Input Channel 16 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_016_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14679 | Input Channel 16 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_016_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14680 | Input Channel 17 Current Max Demand | MAX_DMD_I_017_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14682 | Input Channel 17 Current Max Demand Timestamp | MAX_DMDTS_I_017_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14684 | Input Channel 17 Current Max Demand Timestamp | MAX_DMDTS_I_017_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14685 | Input Channel 17 Import Active Power Max Demand | MAX_DMD_IMP_P_017_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14687 | Input Channel 17 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_017_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14689 | Input Channel 17 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_017_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14690 | Input Channel 17 Export Active Power Max Demand | MAX_DMD_EXP_P_017_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14692 | Input Channel 17 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_017_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14694 | Input Channel 17 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_017_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14695 | Input Channel 17 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_017_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14697 | Input Channel 17 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_017_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14699 | Input Channel 17 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_017_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14700 | Input Channel 17 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_017_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14702 | Input Channel 17 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_017_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14704 | Input Channel 17 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_017_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14705 | Input Channel 17 Apparent Power Max Demand | MAX_DMD_S_017_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14707 | Input Channel 17 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_017_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14709 | Input Channel 17 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_017_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14710 | Input Channel 18 Current Max Demand | MAX_DMD_I_018_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14712 | Input Channel 18 Current Max Demand Timestamp | MAX_DMDTS_I_018_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14714 | Input Channel 18 Current Max Demand Timestamp | MAX_DMDTS_I_018_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14715 | Input Channel 18 Import Active Power Max Demand | MAX_DMD_IMP_P_018_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14717 | Input Channel 18 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_018_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14719 | Input Channel 18 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_018_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14720 | Input Channel 18 Export Active Power Max Demand | MAX_DMD_EXP_P_018_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14722 | Input Channel 18 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_018_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14724 | Input Channel 18 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_018_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14725 | Input Channel 18 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_018_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14727 | Input Channel 18 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_018_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14729 | Input Channel 18 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_018_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14730 | Input Channel 18 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_018_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14732 | Input Channel 18 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_018_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14734 | Input Channel 18 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_018_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14735 | Input Channel 18 Apparent Power Max Demand | MAX_DMD_S_018_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14737 | Input Channel 18 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_018_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14739 | Input Channel 18 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_018_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14740 | Input Channel 19 Current Max Demand | MAX_DMD_I_019_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14742 | Input Channel 19 Current Max Demand Timestamp | MAX_DMDTS_I_019_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14744 | Input Channel 19 Current Max Demand Timestamp | MAX_DMDTS_I_019_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14745 | Input Channel 19 Import Active Power Max Demand | MAX_DMD_IMP_P_019_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14747 | Input Channel 19 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_019_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14749 | Input Channel 19 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_019_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14750 | Input Channel 19 Export Active Power Max Demand | MAX_DMD_EXP_P_019_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14752 | Input Channel 19 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_019_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14754 | Input Channel 19 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_019_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14755 | Input Channel 19 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_019_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14757 | Input Channel 19 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_019_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14759 | Input Channel 19 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_019_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14760 | Input Channel 19 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_019_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14762 | Input Channel 19 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_019_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14764 | Input Channel 19 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_019_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14765 | Input Channel 19 Apparent Power Max Demand | MAX_DMD_S_019_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14767 | Input Channel 19 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_019_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14769 | Input Channel 19 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_019_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14770 | Input Channel 20 Current Max Demand | MAX_DMD_I_020_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14772 | Input Channel 20 Current Max Demand Timestamp | MAX_DMDTS_I_020_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14774 | Input Channel 20 Current Max Demand Timestamp | MAX_DMDTS_I_020_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14775 | Input Channel 20 Import Active Power Max Demand | MAX_DMD_IMP_P_020_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14777 | Input Channel 20 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_020_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14779 | Input Channel 20 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_020_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14780 | Input Channel 20 Export Active Power Max Demand | MAX_DMD_EXP_P_020_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14782 | Input Channel 20 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_020_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14784 | Input Channel 20 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_020_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14785 | Input Channel 20 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_020_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14787 | Input Channel 20 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_020_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14789 | Input Channel 20 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_020_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14790 | Input Channel 20 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_020_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14792 | Input Channel 20 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_020_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14794 | Input Channel 20 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_020_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14795 | Input Channel 20 Apparent Power Max Demand | MAX_DMD_S_020_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14797 | Input Channel 20 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_020_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14799 | Input Channel 20 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_020_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14800 | Input Channel 21 Current Max Demand | MAX_DMD_I_021_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14802 | Input Channel 21 Current Max Demand Timestamp | MAX_DMDTS_I_021_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14804 | Input Channel 21 Current Max Demand Timestamp | MAX_DMDTS_I_021_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14805 | Input Channel 21 Import Active Power Max Demand | MAX_DMD_IMP_P_021_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14807 | Input Channel 21 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_021_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14809 | Input Channel 21 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_021_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14810 | Input Channel 21 Export Active Power Max Demand | MAX_DMD_EXP_P_021_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14812 | Input Channel 21 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_021_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14814 | Input Channel 21 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_021_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14815 | Input Channel 21 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_021_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14817 | Input Channel 21 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_021_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14819 | Input Channel 21 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_021_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14820 | Input Channel 21 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_021_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14822 | Input Channel 21 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_021_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14824 | Input Channel 21 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_021_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14825 | Input Channel 21 Apparent Power Max Demand | MAX_DMD_S_021_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14827 | Input Channel 21 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_021_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14829 | Input Channel 21 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_021_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14830 | Input Channel 22 Current Max Demand | MAX_DMD_I_022_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14832 | Input Channel 22 Current Max Demand Timestamp | MAX_DMDTS_I_022_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14834 | Input Channel 22 Current Max Demand Timestamp | MAX_DMDTS_I_022_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14835 | Input Channel 22 Import Active Power Max Demand | MAX_DMD_IMP_P_022_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14837 | Input Channel 22 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_022_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14839 | Input Channel 22 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_022_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14840 | Input Channel 22 Export Active Power Max Demand | MAX_DMD_EXP_P_022_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14842 | Input Channel 22 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_022_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14844 | Input Channel 22 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_022_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14845 | Input Channel 22 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_022_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14847 | Input Channel 22 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_022_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14849 | Input Channel 22 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_022_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14850 | Input Channel 22 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_022_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14852 | Input Channel 22 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_022_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14854 | Input Channel 22 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_022_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14855 | Input Channel 22 Apparent Power Max Demand | MAX_DMD_S_022_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14857 | Input Channel 22 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_022_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14859 | Input Channel 22 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_022_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14860 | Input Channel 23 Current Max Demand | MAX_DMD_I_023_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14862 | Input Channel 23 Current Max Demand Timestamp | MAX_DMDTS_I_023_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14864 | Input Channel 23 Current Max Demand Timestamp | MAX_DMDTS_I_023_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14865 | Input Channel 23 Import Active Power Max Demand | MAX_DMD_IMP_P_023_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14867 | Input Channel 23 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_023_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14869 | Input Channel 23 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_023_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14870 | Input Channel 23 Export Active Power Max Demand | MAX_DMD_EXP_P_023_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14872 | Input Channel 23 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_023_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14874 | Input Channel 23 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_023_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14875 | Input Channel 23 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_023_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14877 | Input Channel 23 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_023_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14879 | Input Channel 23 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_023_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14880 | Input Channel 23 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_023_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14882 | Input Channel 23 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_023_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14884 | Input Channel 23 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_023_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14885 | Input Channel 23 Apparent Power Max Demand | MAX_DMD_S_023_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14887 | Input Channel 23 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_023_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14889 | Input Channel 23 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_023_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14890 | Input Channel 24 Current Max Demand | MAX_DMD_I_024_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14892 | Input Channel 24 Current Max Demand Timestamp | MAX_DMDTS_I_024_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14894 | Input Channel 24 Current Max Demand Timestamp | MAX_DMDTS_I_024_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14895 | Input Channel 24 Import Active Power Max Demand | MAX_DMD_IMP_P_024_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14897 | Input Channel 24 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_024_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14899 | Input Channel 24 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_024_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14900 | Input Channel 24 Export Active Power Max Demand | MAX_DMD_EXP_P_024_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14902 | Input Channel 24 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_024_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14904 | Input Channel 24 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_024_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14905 | Input Channel 24 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_024_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14907 | Input Channel 24 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_024_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14909 | Input Channel 24 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_024_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14910 | Input Channel 24 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_024_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14912 | Input Channel 24 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_024_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14914 | Input Channel 24 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_024_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14915 | Input Channel 24 Apparent Power Max Demand | MAX_DMD_S_024_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14917 | Input Channel 24 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_024_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14919 | Input Channel 24 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_024_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14920 | User Channel 1 Current Max Demand | MAX_DMD_I_s001_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14922 | User Channel 1 Current Max Demand Timestamp | MAX_DMDTS_I_s001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14924 | User Channel 1 Current Max Demand Timestamp | MAX_DMDTS_I_s001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14925 | User Channel 1 Import Active Power Max Demand | MAX_DMD_IMP_P_s001_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14927 | User Channel 1 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14929 | User Channel 1 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14930 | User Channel 1 Export Active Power Max Demand | MAX_DMD_EXP_P_s001_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14932 | User Channel 1 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14934 | User Channel 1 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14935 | User Channel 1 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s001_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14937 | User Channel 1 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14939 | User Channel 1 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14940 | User Channel 1 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s001_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14942 | User Channel 1 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14944 | User Channel 1 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14945 | User Channel 1 Apparent Power Max Demand | MAX_DMD_S_s001_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14947 | User Channel 1 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s001_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14949 | User Channel 1 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s001_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14950 | User Channel 2 Current Max Demand | MAX_DMD_I_s002_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14952 | User Channel 2 Current Max Demand Timestamp | MAX_DMDTS_I_s002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14954 | User Channel 2 Current Max Demand Timestamp | MAX_DMDTS_I_s002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14955 | User Channel 2 Import Active Power Max Demand | MAX_DMD_IMP_P_s002_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14957 | User Channel 2 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14959 | User Channel 2 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14960 | User Channel 2 Export Active Power Max Demand | MAX_DMD_EXP_P_s002_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14962 | User Channel 2 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14964 | User Channel 2 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14965 | User Channel 2 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s002_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14967 | User Channel 2 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14969 | User Channel 2 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14970 | User Channel 2 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s002_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14972 | User Channel 2 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14974 | User Channel 2 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14975 | User Channel 2 Apparent Power Max Demand | MAX_DMD_S_s002_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14977 | User Channel 2 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s002_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14979 | User Channel 2 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s002_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14980 | User Channel 3 Current Max Demand | MAX_DMD_I_s003_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14982 | User Channel 3 Current Max Demand Timestamp | MAX_DMDTS_I_s003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14984 | User Channel 3 Current Max Demand Timestamp | MAX_DMDTS_I_s003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14985 | User Channel 3 Import Active Power Max Demand | MAX_DMD_IMP_P_s003_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14987 | User Channel 3 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14989 | User Channel 3 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14990 | User Channel 3 Export Active Power Max Demand | MAX_DMD_EXP_P_s003_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14992 | User Channel 3 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14994 | User Channel 3 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
14995 | User Channel 3 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s003_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
14997 | User Channel 3 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
14999 | User Channel 3 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15000 | User Channel 3 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s003_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15002 | User Channel 3 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15004 | User Channel 3 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15005 | User Channel 3 Apparent Power Max Demand | MAX_DMD_S_s003_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15007 | User Channel 3 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s003_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15009 | User Channel 3 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s003_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15010 | User Channel 4 Current Max Demand | MAX_DMD_I_s004_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15012 | User Channel 4 Current Max Demand Timestamp | MAX_DMDTS_I_s004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15014 | User Channel 4 Current Max Demand Timestamp | MAX_DMDTS_I_s004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15015 | User Channel 4 Import Active Power Max Demand | MAX_DMD_IMP_P_s004_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15017 | User Channel 4 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15019 | User Channel 4 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15020 | User Channel 4 Export Active Power Max Demand | MAX_DMD_EXP_P_s004_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15022 | User Channel 4 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15024 | User Channel 4 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15025 | User Channel 4 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s004_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15027 | User Channel 4 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15029 | User Channel 4 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15030 | User Channel 4 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s004_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15032 | User Channel 4 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15034 | User Channel 4 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15035 | User Channel 4 Apparent Power Max Demand | MAX_DMD_S_s004_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15037 | User Channel 4 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s004_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15039 | User Channel 4 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s004_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15040 | User Channel 5 Current Max Demand | MAX_DMD_I_s005_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15042 | User Channel 5 Current Max Demand Timestamp | MAX_DMDTS_I_s005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15044 | User Channel 5 Current Max Demand Timestamp | MAX_DMDTS_I_s005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15045 | User Channel 5 Import Active Power Max Demand | MAX_DMD_IMP_P_s005_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15047 | User Channel 5 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15049 | User Channel 5 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15050 | User Channel 5 Export Active Power Max Demand | MAX_DMD_EXP_P_s005_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15052 | User Channel 5 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15054 | User Channel 5 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15055 | User Channel 5 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s005_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15057 | User Channel 5 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15059 | User Channel 5 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15060 | User Channel 5 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s005_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15062 | User Channel 5 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15064 | User Channel 5 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15065 | User Channel 5 Apparent Power Max Demand | MAX_DMD_S_s005_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15067 | User Channel 5 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s005_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15069 | User Channel 5 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s005_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15070 | User Channel 6 Current Max Demand | MAX_DMD_I_s006_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15072 | User Channel 6 Current Max Demand Timestamp | MAX_DMDTS_I_s006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15074 | User Channel 6 Current Max Demand Timestamp | MAX_DMDTS_I_s006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15075 | User Channel 6 Import Active Power Max Demand | MAX_DMD_IMP_P_s006_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15077 | User Channel 6 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15079 | User Channel 6 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15080 | User Channel 6 Export Active Power Max Demand | MAX_DMD_EXP_P_s006_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15082 | User Channel 6 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15084 | User Channel 6 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15085 | User Channel 6 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s006_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15087 | User Channel 6 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15089 | User Channel 6 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15090 | User Channel 6 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s006_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15092 | User Channel 6 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15094 | User Channel 6 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15095 | User Channel 6 Apparent Power Max Demand | MAX_DMD_S_s006_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15097 | User Channel 6 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s006_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15099 | User Channel 6 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s006_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15100 | User Channel 7 Current Max Demand | MAX_DMD_I_s007_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15102 | User Channel 7 Current Max Demand Timestamp | MAX_DMDTS_I_s007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15104 | User Channel 7 Current Max Demand Timestamp | MAX_DMDTS_I_s007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15105 | User Channel 7 Import Active Power Max Demand | MAX_DMD_IMP_P_s007_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15107 | User Channel 7 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15109 | User Channel 7 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15110 | User Channel 7 Export Active Power Max Demand | MAX_DMD_EXP_P_s007_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15112 | User Channel 7 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15114 | User Channel 7 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15115 | User Channel 7 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s007_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15117 | User Channel 7 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15119 | User Channel 7 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15120 | User Channel 7 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s007_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15122 | User Channel 7 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15124 | User Channel 7 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15125 | User Channel 7 Apparent Power Max Demand | MAX_DMD_S_s007_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15127 | User Channel 7 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s007_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15129 | User Channel 7 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s007_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15130 | User Channel 8 Current Max Demand | MAX_DMD_I_s008_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15132 | User Channel 8 Current Max Demand Timestamp | MAX_DMDTS_I_s008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15134 | User Channel 8 Current Max Demand Timestamp | MAX_DMDTS_I_s008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15135 | User Channel 8 Import Active Power Max Demand | MAX_DMD_IMP_P_s008_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15137 | User Channel 8 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15139 | User Channel 8 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15140 | User Channel 8 Export Active Power Max Demand | MAX_DMD_EXP_P_s008_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15142 | User Channel 8 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15144 | User Channel 8 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15145 | User Channel 8 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s008_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15147 | User Channel 8 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15149 | User Channel 8 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15150 | User Channel 8 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s008_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15152 | User Channel 8 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15154 | User Channel 8 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15155 | User Channel 8 Apparent Power Max Demand | MAX_DMD_S_s008_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15157 | User Channel 8 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s008_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15159 | User Channel 8 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s008_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15160 | User Channel 9 Current Max Demand | MAX_DMD_I_s009_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15162 | User Channel 9 Current Max Demand Timestamp | MAX_DMDTS_I_s009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15164 | User Channel 9 Current Max Demand Timestamp | MAX_DMDTS_I_s009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15165 | User Channel 9 Import Active Power Max Demand | MAX_DMD_IMP_P_s009_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15167 | User Channel 9 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15169 | User Channel 9 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15170 | User Channel 9 Export Active Power Max Demand | MAX_DMD_EXP_P_s009_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15172 | User Channel 9 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15174 | User Channel 9 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15175 | User Channel 9 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s009_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15177 | User Channel 9 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15179 | User Channel 9 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15180 | User Channel 9 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s009_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15182 | User Channel 9 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15184 | User Channel 9 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15185 | User Channel 9 Apparent Power Max Demand | MAX_DMD_S_s009_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15187 | User Channel 9 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s009_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15189 | User Channel 9 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s009_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15190 | User Channel 10 Current Max Demand | MAX_DMD_I_s010_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15192 | User Channel 10 Current Max Demand Timestamp | MAX_DMDTS_I_s010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15194 | User Channel 10 Current Max Demand Timestamp | MAX_DMDTS_I_s010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15195 | User Channel 10 Import Active Power Max Demand | MAX_DMD_IMP_P_s010_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15197 | User Channel 10 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15199 | User Channel 10 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15200 | User Channel 10 Export Active Power Max Demand | MAX_DMD_EXP_P_s010_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15202 | User Channel 10 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15204 | User Channel 10 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15205 | User Channel 10 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s010_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15207 | User Channel 10 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15209 | User Channel 10 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15210 | User Channel 10 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s010_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15212 | User Channel 10 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15214 | User Channel 10 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15215 | User Channel 10 Apparent Power Max Demand | MAX_DMD_S_s010_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15217 | User Channel 10 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s010_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15219 | User Channel 10 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s010_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15220 | User Channel 11 Current Max Demand | MAX_DMD_I_s011_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15222 | User Channel 11 Current Max Demand Timestamp | MAX_DMDTS_I_s011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15224 | User Channel 11 Current Max Demand Timestamp | MAX_DMDTS_I_s011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15225 | User Channel 11 Import Active Power Max Demand | MAX_DMD_IMP_P_s011_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15227 | User Channel 11 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15229 | User Channel 11 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15230 | User Channel 11 Export Active Power Max Demand | MAX_DMD_EXP_P_s011_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15232 | User Channel 11 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15234 | User Channel 11 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15235 | User Channel 11 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s011_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15237 | User Channel 11 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15239 | User Channel 11 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15240 | User Channel 11 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s011_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15242 | User Channel 11 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15244 | User Channel 11 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15245 | User Channel 11 Apparent Power Max Demand | MAX_DMD_S_s011_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15247 | User Channel 11 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s011_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15249 | User Channel 11 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s011_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15250 | User Channel 12 Current Max Demand | MAX_DMD_I_s012_A | A |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15252 | User Channel 12 Current Max Demand Timestamp | MAX_DMDTS_I_s012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15254 | User Channel 12 Current Max Demand Timestamp | MAX_DMDTS_I_s012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15255 | User Channel 12 Import Active Power Max Demand | MAX_DMD_IMP_P_s012_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15257 | User Channel 12 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15259 | User Channel 12 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15260 | User Channel 12 Export Active Power Max Demand | MAX_DMD_EXP_P_s012_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15262 | User Channel 12 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15264 | User Channel 12 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15265 | User Channel 12 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s012_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15267 | User Channel 12 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15269 | User Channel 12 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15270 | User Channel 12 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s012_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15272 | User Channel 12 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15274 | User Channel 12 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
15275 | User Channel 12 Apparent Power Max Demand | MAX_DMD_S_s012_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | Max Demand
15277 | User Channel 12 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s012_1 |  |  | uint32 | R | 2 | 1 | [9 empty] | Max Demand
15279 | User Channel 12 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s012_2 |  |  | uint16 | R | 1 | 1 | [9 empty] | Max Demand
20992 | System Frequency Max value | MAX_FREQ_Hz | Hz |  | float32 | R | 2 | 1 | [9 empty] | max min
20994 | System Frequency Max value Timestamp | MAX_TS_FREQ |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
20998 | Phase A Line-to-Neutral Voltage Max value | MAX_VLN_a_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
21000 | Phase A Line-to-Neutral Voltage Max value Timestamp | MAX_VLNTS_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21004 | Phase B Line-to-Neutral Voltage Max value | MAX_VLN_b_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
21006 | Phase B Line-to-Neutral Voltage Max value Timestamp | MAX_VLNTS_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21010 | Phase C Line-to-Neutral Voltage Max value | MAX_VLN_c_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
21012 | Phase C Line-to-Neutral Voltage Max value Timestamp | MAX_VLNTS_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21016 | Phase AB Line-to-Line Voltage Max value | MAX_VLL_ab_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
21018 | Phase AB Line-to-Line Voltage Max value Timestamp | MAX_VLLTS_ab_V |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21022 | Phase BC Line-to-Line Voltage Max value | MAX_VLL_bc_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
21024 | Phase BC Line-to-Line Voltage Max value Timestamp | MAX_VLLTS_bc_V |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21028 | Phase CA Line-to-Line Voltage Max value | MAX_VLL_ca_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
21030 | Phase CA Line-to-Line Voltage Max value Timestamp | MAX_VLLTS_ca_V |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21034 | Phase A Current Max value | MAX_I_a_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21036 | Phase A Current Max value Timestamp | MAX_TS_I_a_A |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21040 | Phase A Active Power Max value | MAX_P_a_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21042 | Phase A Active Power Max value Timestamp | MAX_TS_P_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21046 | Phase A Reactive Power Max value | MAX_Q_a_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21048 | Phase A Reactive Power Max value Timestamp | MAX_TS_Q_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21052 | Phase A Apparent Power Max value | MAX_S_a_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21054 | Phase A Apparent Power Max value Timestamp | MAX_TS_S_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21058 | Phase A Power Factor Max value | MAX_PF_a |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21060 | Phase A Power Factor Max value Timestamp | MAX_TS_PF_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21064 | Phase A Voltage THD Max value | MAX_THD_V_a_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21066 | Phase A Voltage THD Max value Timestamp | MAX_TS_THD_V_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21070 | Phase B Current Max value | MAX_I_b_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21072 | Phase B Current Max value Timestamp | MAX_TS_I_b_A |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21076 | Phase B Active Power Max value | MAX_P_b_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21078 | Phase B Active Power Max value Timestamp | MAX_TS_P_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21082 | Phase B Reactive Power Max value | MAX_Q_b_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21084 | Phase B Reactive Power Max value Timestamp | MAX_TS_Q_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21088 | Phase B Apparent Power Max value | MAX_S_b_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21090 | Phase B Apparent Power Max value Timestamp | MAX_TS_S_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21094 | Phase B Power Factor Max value | MAX_PF_b |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21096 | Phase B Power Factor Max value Timestamp | MAX_TS_PF_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21100 | Phase B Voltage THD Max value | MAX_THD_V_b_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21102 | Phase B Voltage THD Max value Timestamp | MAX_TS_THD_V_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21106 | Phase C Current Max value | MAX_I_c_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21108 | Phase C Current Max value Timestamp | MAX_TS_I_c_A |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21112 | Phase C Active Power Max value | MAX_P_c_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21114 | Phase C Active Power Max value Timestamp | MAX_TS_P_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21118 | Phase C Reactive Power Max value | MAX_Q_c_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21120 | Phase C Reactive Power Max value Timestamp | MAX_TS_Q_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21124 | Phase C Apparent Power Max value | MAX_S_c_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21126 | Phase C Apparent Power Max value Timestamp | MAX_TS_S_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21130 | Phase C Power Factor Max value | MAX_PF_c |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21132 | Phase C Power Factor Max value Timestamp | MAX_TS_PF_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21136 | Phase C Voltage THD Max value | MAX_THD_V_c_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21138 | Phase C Voltage THD Max value Timestamp | MAX_TS_THD_V_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21142 | Voltage Unbalance Factor Magnitude Max value | MAX_UNBL_V_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21144 | Voltage Unbalance Factor Magnitude Max value Timestamp | MAX_UNBLTS_V_% |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21148 | Input Channel 1 Current Max value | MAX_I_001_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21150 | Input Channel 1 Current Max value Timestamp | MAX_TS_I_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21154 | Input Channel 1 Active Power Max value | MAX_P_001_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21156 | Input Channel 1 Active Power Max value Timestamp | MAX_TS_P_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21160 | Input Channel 1 Reactive Power Max value | MAX_Q_001_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21162 | Input Channel 1 Reactive Power Max value Timestamp | MAX_TS_Q_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21166 | Input Channel 1 Apparent Power Max value | MAX_S_001_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21168 | Input Channel 1 Apparent Power Max value Timestamp | MAX_TS_S_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21172 | Input Channel 1 Power Factor Max value | MAX_PF_001 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21174 | Input Channel 1 Power Factor Max value Timestamp | MAX_TS_PF_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21178 | Input Channel 1 Current THD Max value | MAX_THD_I_001_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21180 | Input Channel 1 Current THD Max value Timestamp | MAX_TS_THD_I_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21184 | Input Channel 2 Current Max value | MAX_I_002_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21186 | Input Channel 2 Current Max value Timestamp | MAX_TS_I_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21190 | Input Channel 2 Active Power Max value | MAX_P_002_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21192 | Input Channel 2 Active Power Max value Timestamp | MAX_TS_P_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21196 | Input Channel 2 Reactive Power Max value | MAX_Q_002_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21198 | Input Channel 2 Reactive Power Max value Timestamp | MAX_TS_Q_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21202 | Input Channel 2 Apparent Power Max value | MAX_S_002_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21204 | Input Channel 2 Apparent Power Max value Timestamp | MAX_TS_S_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21208 | Input Channel 2 Power Factor Max value | MAX_PF_002 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21210 | Input Channel 2 Power Factor Max value Timestamp | MAX_TS_PF_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21214 | Input Channel 2 Current THD Max value | MAX_THD_I_002_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21216 | Input Channel 2 Current THD Max value Timestamp | MAX_TS_THD_I_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21220 | Input Channel 3 Current Max value | MAX_I_003_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21222 | Input Channel 3 Current Max value Timestamp | MAX_TS_I_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21226 | Input Channel 3 Active Power Max value | MAX_P_003_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21228 | Input Channel 3 Active Power Max value Timestamp | MAX_TS_P_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21232 | Input Channel 3 Reactive Power Max value | MAX_Q_003_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21234 | Input Channel 3 Reactive Power Max value Timestamp | MAX_TS_Q_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21238 | Input Channel 3 Apparent Power Max value | MAX_S_003_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21240 | Input Channel 3 Apparent Power Max value Timestamp | MAX_TS_S_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21244 | Input Channel 3 Power Factor Max value | MAX_PF_003 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21246 | Input Channel 3 Power Factor Max value Timestamp | MAX_TS_PF_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21250 | Input Channel 3 Current THD Max value | MAX_THD_I_003_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21252 | Input Channel 3 Current THD Max value Timestamp | MAX_TS_THD_I_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21256 | Input Channel 4 Current Max value | MAX_I_004_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21258 | Input Channel 4 Current Max value Timestamp | MAX_TS_I_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21262 | Input Channel 4 Active Power Max value | MAX_P_004_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21264 | Input Channel 4 Active Power Max value Timestamp | MAX_TS_P_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21268 | Input Channel 4 Reactive Power Max value | MAX_Q_004_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21270 | Input Channel 4 Reactive Power Max value Timestamp | MAX_TS_Q_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21274 | Input Channel 4 Apparent Power Max value | MAX_S_004_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21276 | Input Channel 4 Apparent Power Max value Timestamp | MAX_TS_S_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21280 | Input Channel 4 Power Factor Max value | MAX_PF_004 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21282 | Input Channel 4 Power Factor Max value Timestamp | MAX_TS_PF_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21286 | Input Channel 4 Current THD Max value | MAX_THD_I_004_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21288 | Input Channel 4 Current THD Max value Timestamp | MAX_TS_THD_I_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21292 | Input Channel 5 Current Max value | MAX_I_005_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21294 | Input Channel 5 Current Max value Timestamp | MAX_TS_I_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21298 | Input Channel 5 Active Power Max value | MAX_P_005_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21300 | Input Channel 5 Active Power Max value Timestamp | MAX_TS_P_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21304 | Input Channel 5 Reactive Power Max value | MAX_Q_005_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21306 | Input Channel 5 Reactive Power Max value Timestamp | MAX_TS_Q_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21310 | Input Channel 5 Apparent Power Max value | MAX_S_005_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21312 | Input Channel 5 Apparent Power Max value Timestamp | MAX_TS_S_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21316 | Input Channel 5 Power Factor Max value | MAX_PF_005 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21318 | Input Channel 5 Power Factor Max value Timestamp | MAX_TS_PF_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21322 | Input Channel 5 Current THD Max value | MAX_THD_I_005_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21324 | Input Channel 5 Current THD Max value Timestamp | MAX_TS_THD_I_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21328 | Input Channel 6 Current Max value | MAX_I_006_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21330 | Input Channel 6 Current Max value Timestamp | MAX_TS_I_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21334 | Input Channel 6 Active Power Max value | MAX_P_006_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21336 | Input Channel 6 Active Power Max value Timestamp | MAX_TS_P_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21340 | Input Channel 6 Reactive Power Max value | MAX_Q_006_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21342 | Input Channel 6 Reactive Power Max value Timestamp | MAX_TS_Q_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21346 | Input Channel 6 Apparent Power Max value | MAX_S_006_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21348 | Input Channel 6 Apparent Power Max value Timestamp | MAX_TS_S_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21352 | Input Channel 6 Power Factor Max value | MAX_PF_006 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21354 | Input Channel 6 Power Factor Max value Timestamp | MAX_TS_PF_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21358 | Input Channel 6 Current THD Max value | MAX_THD_I_006_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21360 | Input Channel 6 Current THD Max value Timestamp | MAX_TS_THD_I_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21364 | Input Channel 7 Current Max value | MAX_I_007_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21366 | Input Channel 7 Current Max value Timestamp | MAX_TS_I_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21370 | Input Channel 7 Active Power Max value | MAX_P_007_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21372 | Input Channel 7 Active Power Max value Timestamp | MAX_TS_P_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21376 | Input Channel 7 Reactive Power Max value | MAX_Q_007_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21378 | Input Channel 7 Reactive Power Max value Timestamp | MAX_TS_Q_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21382 | Input Channel 7 Apparent Power Max value | MAX_S_007_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21384 | Input Channel 7 Apparent Power Max value Timestamp | MAX_TS_S_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21388 | Input Channel 7 Power Factor Max value | MAX_PF_007 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21390 | Input Channel 7 Power Factor Max value Timestamp | MAX_TS_PF_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21394 | Input Channel 7 Current THD Max value | MAX_THD_I_007_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21396 | Input Channel 7 Current THD Max value Timestamp | MAX_TS_THD_I_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21400 | Input Channel 8 Current Max value | MAX_I_008_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21402 | Input Channel 8 Current Max value Timestamp | MAX_TS_I_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21406 | Input Channel 8 Active Power Max value | MAX_P_008_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21408 | Input Channel 8 Active Power Max value Timestamp | MAX_TS_P_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21412 | Input Channel 8 Reactive Power Max value | MAX_Q_008_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21414 | Input Channel 8 Reactive Power Max value Timestamp | MAX_TS_Q_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21418 | Input Channel 8 Apparent Power Max value | MAX_S_008_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21420 | Input Channel 8 Apparent Power Max value Timestamp | MAX_TS_S_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21424 | Input Channel 8 Power Factor Max value | MAX_PF_008 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21426 | Input Channel 8 Power Factor Max value Timestamp | MAX_TS_PF_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21430 | Input Channel 8 Current THD Max value | MAX_THD_I_008_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21432 | Input Channel 8 Current THD Max value Timestamp | MAX_TS_THD_I_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21436 | Input Channel 9 Current Max value | MAX_I_009_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21438 | Input Channel 9 Current Max value Timestamp | MAX_TS_I_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21442 | Input Channel 9 Active Power Max value | MAX_P_009_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21444 | Input Channel 9 Active Power Max value Timestamp | MAX_TS_P_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21448 | Input Channel 9 Reactive Power Max value | MAX_Q_009_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21450 | Input Channel 9 Reactive Power Max value Timestamp | MAX_TS_Q_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21454 | Input Channel 9 Apparent Power Max value | MAX_S_009_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21456 | Input Channel 9 Apparent Power Max value Timestamp | MAX_TS_S_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21460 | Input Channel 9 Power Factor Max value | MAX_PF_009 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21462 | Input Channel 9 Power Factor Max value Timestamp | MAX_TS_PF_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21466 | Input Channel 9 Current THD Max value | MAX_THD_I_009_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21468 | Input Channel 9 Current THD Max value Timestamp | MAX_TS_THD_I_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21472 | Input Channel 10 Current Max value | MAX_I_010_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21474 | Input Channel 10 Current Max value Timestamp | MAX_TS_I_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21478 | Input Channel 10 Active Power Max value | MAX_P_010_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21480 | Input Channel 10 Active Power Max value Timestamp | MAX_TS_P_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21484 | Input Channel 10 Reactive Power Max value | MAX_Q_010_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21486 | Input Channel 10 Reactive Power Max value Timestamp | MAX_TS_Q_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21490 | Input Channel 10 Apparent Power Max value | MAX_S_010_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21492 | Input Channel 10 Apparent Power Max value Timestamp | MAX_TS_S_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21496 | Input Channel 10 Power Factor Max value | MAX_PF_010 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21498 | Input Channel 10 Power Factor Max value Timestamp | MAX_TS_PF_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21502 | Input Channel 10 Current THD Max value | MAX_THD_I_010_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21504 | Input Channel 10 Current THD Max value Timestamp | MAX_TS_THD_I_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21508 | Input Channel 11 Current Max value | MAX_I_011_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21510 | Input Channel 11 Current Max value Timestamp | MAX_TS_I_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21514 | Input Channel 11 Active Power Max value | MAX_P_011_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21516 | Input Channel 11 Active Power Max value Timestamp | MAX_TS_P_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21520 | Input Channel 11 Reactive Power Max value | MAX_Q_011_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21522 | Input Channel 11 Reactive Power Max value Timestamp | MAX_TS_Q_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21526 | Input Channel 11 Apparent Power Max value | MAX_S_011_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21528 | Input Channel 11 Apparent Power Max value Timestamp | MAX_TS_S_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21532 | Input Channel 11 Power Factor Max value | MAX_PF_011 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21534 | Input Channel 11 Power Factor Max value Timestamp | MAX_TS_PF_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21538 | Input Channel 11 Current THD Max value | MAX_THD_I_011_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21540 | Input Channel 11 Current THD Max value Timestamp | MAX_TS_THD_I_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21544 | Input Channel 12 Current Max value | MAX_I_012_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21546 | Input Channel 12 Current Max value Timestamp | MAX_TS_I_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21550 | Input Channel 12 Active Power Max value | MAX_P_012_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21552 | Input Channel 12 Active Power Max value Timestamp | MAX_TS_P_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21556 | Input Channel 12 Reactive Power Max value | MAX_Q_012_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21558 | Input Channel 12 Reactive Power Max value Timestamp | MAX_TS_Q_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21562 | Input Channel 12 Apparent Power Max value | MAX_S_012_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21564 | Input Channel 12 Apparent Power Max value Timestamp | MAX_TS_S_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21568 | Input Channel 12 Power Factor Max value | MAX_PF_012 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21570 | Input Channel 12 Power Factor Max value Timestamp | MAX_TS_PF_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21574 | Input Channel 12 Current THD Max value | MAX_THD_I_012_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21576 | Input Channel 12 Current THD Max value Timestamp | MAX_TS_THD_I_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21580 | Input Channel 13 Current Max value | MAX_I_013_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21582 | Input Channel 13 Current Max value Timestamp | MAX_TS_I_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21586 | Input Channel 13 Active Power Max value | MAX_P_013_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21588 | Input Channel 13 Active Power Max value Timestamp | MAX_TS_P_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21592 | Input Channel 13 Reactive Power Max value | MAX_Q_013_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21594 | Input Channel 13 Reactive Power Max value Timestamp | MAX_TS_Q_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21598 | Input Channel 13 Apparent Power Max value | MAX_S_013_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21600 | Input Channel 13 Apparent Power Max value Timestamp | MAX_TS_S_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21604 | Input Channel 13 Power Factor Max value | MAX_PF_013 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21606 | Input Channel 13 Power Factor Max value Timestamp | MAX_TS_PF_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21610 | Input Channel 13 Current THD Max value | MAX_THD_I_013_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21612 | Input Channel 13 Current THD Max value Timestamp | MAX_TS_THD_I_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21616 | Input Channel 14 Current Max value | MAX_I_014_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21618 | Input Channel 14 Current Max value Timestamp | MAX_TS_I_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21622 | Input Channel 14 Active Power Max value | MAX_P_014_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21624 | Input Channel 14 Active Power Max value Timestamp | MAX_TS_P_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21628 | Input Channel 14 Reactive Power Max value | MAX_Q_014_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21630 | Input Channel 14 Reactive Power Max value Timestamp | MAX_TS_Q_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21634 | Input Channel 14 Apparent Power Max value | MAX_S_014_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21636 | Input Channel 14 Apparent Power Max value Timestamp | MAX_TS_S_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21640 | Input Channel 14 Power Factor Max value | MAX_PF_014 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21642 | Input Channel 14 Power Factor Max value Timestamp | MAX_TS_PF_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21646 | Input Channel 14 Current THD Max value | MAX_THD_I_014_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21648 | Input Channel 14 Current THD Max value Timestamp | MAX_TS_THD_I_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21652 | Input Channel 15 Current Max value | MAX_I_015_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21654 | Input Channel 15 Current Max value Timestamp | MAX_TS_I_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21658 | Input Channel 15 Active Power Max value | MAX_P_015_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21660 | Input Channel 15 Active Power Max value Timestamp | MAX_TS_P_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21664 | Input Channel 15 Reactive Power Max value | MAX_Q_015_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21666 | Input Channel 15 Reactive Power Max value Timestamp | MAX_TS_Q_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21670 | Input Channel 15 Apparent Power Max value | MAX_S_015_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21672 | Input Channel 15 Apparent Power Max value Timestamp | MAX_TS_S_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21676 | Input Channel 15 Power Factor Max value | MAX_PF_015 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21678 | Input Channel 15 Power Factor Max value Timestamp | MAX_TS_PF_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21682 | Input Channel 15 Current THD Max value | MAX_THD_I_015_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21684 | Input Channel 15 Current THD Max value Timestamp | MAX_TS_THD_I_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21688 | Input Channel 16 Current Max value | MAX_I_016_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21690 | Input Channel 16 Current Max value Timestamp | MAX_TS_I_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21694 | Input Channel 16 Active Power Max value | MAX_P_016_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21696 | Input Channel 16 Active Power Max value Timestamp | MAX_TS_P_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21700 | Input Channel 16 Reactive Power Max value | MAX_Q_016_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21702 | Input Channel 16 Reactive Power Max value Timestamp | MAX_TS_Q_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21706 | Input Channel 16 Apparent Power Max value | MAX_S_016_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21708 | Input Channel 16 Apparent Power Max value Timestamp | MAX_TS_S_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21712 | Input Channel 16 Power Factor Max value | MAX_PF_016 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21714 | Input Channel 16 Power Factor Max value Timestamp | MAX_TS_PF_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21718 | Input Channel 16 Current THD Max value | MAX_THD_I_016_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21720 | Input Channel 16 Current THD Max value Timestamp | MAX_TS_THD_I_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21724 | Input Channel 17 Current Max value | MAX_I_017_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21726 | Input Channel 17 Current Max value Timestamp | MAX_TS_I_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21730 | Input Channel 17 Active Power Max value | MAX_P_017_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21732 | Input Channel 17 Active Power Max value Timestamp | MAX_TS_P_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21736 | Input Channel 17 Reactive Power Max value | MAX_Q_017_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21738 | Input Channel 17 Reactive Power Max value Timestamp | MAX_TS_Q_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21742 | Input Channel 17 Apparent Power Max value | MAX_S_017_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21744 | Input Channel 17 Apparent Power Max value Timestamp | MAX_TS_S_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21748 | Input Channel 17 Power Factor Max value | MAX_PF_017 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21750 | Input Channel 17 Power Factor Max value Timestamp | MAX_TS_PF_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21754 | Input Channel 17 Current THD Max value | MAX_THD_I_017_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21756 | Input Channel 17 Current THD Max value Timestamp | MAX_TS_THD_I_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21760 | Input Channel 18 Current Max value | MAX_I_018_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21762 | Input Channel 18 Current Max value Timestamp | MAX_TS_I_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21766 | Input Channel 18 Active Power Max value | MAX_P_018_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21768 | Input Channel 18 Active Power Max value Timestamp | MAX_TS_P_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21772 | Input Channel 18 Reactive Power Max value | MAX_Q_018_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21774 | Input Channel 18 Reactive Power Max value Timestamp | MAX_TS_Q_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21778 | Input Channel 18 Apparent Power Max value | MAX_S_018_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21780 | Input Channel 18 Apparent Power Max value Timestamp | MAX_TS_S_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21784 | Input Channel 18 Power Factor Max value | MAX_PF_018 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21786 | Input Channel 18 Power Factor Max value Timestamp | MAX_TS_PF_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21790 | Input Channel 18 Current THD Max value | MAX_THD_I_018_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21792 | Input Channel 18 Current THD Max value Timestamp | MAX_TS_THD_I_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21796 | Input Channel 19 Current Max value | MAX_I_019_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21798 | Input Channel 19 Current Max value Timestamp | MAX_TS_I_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21802 | Input Channel 19 Active Power Max value | MAX_P_019_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21804 | Input Channel 19 Active Power Max value Timestamp | MAX_TS_P_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21808 | Input Channel 19 Reactive Power Max value | MAX_Q_019_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21810 | Input Channel 19 Reactive Power Max value Timestamp | MAX_TS_Q_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21814 | Input Channel 19 Apparent Power Max value | MAX_S_019_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21816 | Input Channel 19 Apparent Power Max value Timestamp | MAX_TS_S_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21820 | Input Channel 19 Power Factor Max value | MAX_PF_019 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21822 | Input Channel 19 Power Factor Max value Timestamp | MAX_TS_PF_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21826 | Input Channel 19 Current THD Max value | MAX_THD_I_019_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21828 | Input Channel 19 Current THD Max value Timestamp | MAX_TS_THD_I_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21832 | Input Channel 20 Current Max value | MAX_I_020_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21834 | Input Channel 20 Current Max value Timestamp | MAX_TS_I_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21838 | Input Channel 20 Active Power Max value | MAX_P_020_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21840 | Input Channel 20 Active Power Max value Timestamp | MAX_TS_P_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21844 | Input Channel 20 Reactive Power Max value | MAX_Q_020_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21846 | Input Channel 20 Reactive Power Max value Timestamp | MAX_TS_Q_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21850 | Input Channel 20 Apparent Power Max value | MAX_S_020_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21852 | Input Channel 20 Apparent Power Max value Timestamp | MAX_TS_S_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21856 | Input Channel 20 Power Factor Max value | MAX_PF_020 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21858 | Input Channel 20 Power Factor Max value Timestamp | MAX_TS_PF_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21862 | Input Channel 20 Current THD Max value | MAX_THD_I_020_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21864 | Input Channel 20 Current THD Max value Timestamp | MAX_TS_THD_I_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21868 | Input Channel 21 Current Max value | MAX_I_021_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21870 | Input Channel 21 Current Max value Timestamp | MAX_TS_I_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21874 | Input Channel 21 Active Power Max value | MAX_P_021_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21876 | Input Channel 21 Active Power Max value Timestamp | MAX_TS_P_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21880 | Input Channel 21 Reactive Power Max value | MAX_Q_021_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21882 | Input Channel 21 Reactive Power Max value Timestamp | MAX_TS_Q_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21886 | Input Channel 21 Apparent Power Max value | MAX_S_021_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21888 | Input Channel 21 Apparent Power Max value Timestamp | MAX_TS_S_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21892 | Input Channel 21 Power Factor Max value | MAX_PF_021 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21894 | Input Channel 21 Power Factor Max value Timestamp | MAX_TS_PF_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21898 | Input Channel 21 Current THD Max value | MAX_THD_I_021_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21900 | Input Channel 21 Current THD Max value Timestamp | MAX_TS_THD_I_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21904 | Input Channel 22 Current Max value | MAX_I_022_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21906 | Input Channel 22 Current Max value Timestamp | MAX_TS_I_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21910 | Input Channel 22 Active Power Max value | MAX_P_022_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21912 | Input Channel 22 Active Power Max value Timestamp | MAX_TS_P_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21916 | Input Channel 22 Reactive Power Max value | MAX_Q_022_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21918 | Input Channel 22 Reactive Power Max value Timestamp | MAX_TS_Q_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21922 | Input Channel 22 Apparent Power Max value | MAX_S_022_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21924 | Input Channel 22 Apparent Power Max value Timestamp | MAX_TS_S_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21928 | Input Channel 22 Power Factor Max value | MAX_PF_022 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21930 | Input Channel 22 Power Factor Max value Timestamp | MAX_TS_PF_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21934 | Input Channel 22 Current THD Max value | MAX_THD_I_022_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21936 | Input Channel 22 Current THD Max value Timestamp | MAX_TS_THD_I_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21940 | Input Channel 23 Current Max value | MAX_I_023_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21942 | Input Channel 23 Current Max value Timestamp | MAX_TS_I_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21946 | Input Channel 23 Active Power Max value | MAX_P_023_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21948 | Input Channel 23 Active Power Max value Timestamp | MAX_TS_P_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21952 | Input Channel 23 Reactive Power Max value | MAX_Q_023_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21954 | Input Channel 23 Reactive Power Max value Timestamp | MAX_TS_Q_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21958 | Input Channel 23 Apparent Power Max value | MAX_S_023_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21960 | Input Channel 23 Apparent Power Max value Timestamp | MAX_TS_S_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21964 | Input Channel 23 Power Factor Max value | MAX_PF_023 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
21966 | Input Channel 23 Power Factor Max value Timestamp | MAX_TS_PF_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21970 | Input Channel 23 Current THD Max value | MAX_THD_I_023_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
21972 | Input Channel 23 Current THD Max value Timestamp | MAX_TS_THD_I_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21976 | Input Channel 24 Current Max value | MAX_I_024_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
21978 | Input Channel 24 Current Max value Timestamp | MAX_TS_I_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21982 | Input Channel 24 Active Power Max value | MAX_P_024_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
21984 | Input Channel 24 Active Power Max value Timestamp | MAX_TS_P_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21988 | Input Channel 24 Reactive Power Max value | MAX_Q_024_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
21990 | Input Channel 24 Reactive Power Max value Timestamp | MAX_TS_Q_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
21994 | Input Channel 24 Apparent Power Max value | MAX_S_024_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
21996 | Input Channel 24 Apparent Power Max value Timestamp | MAX_TS_S_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22000 | Input Channel 24 Power Factor Max value | MAX_PF_024 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22002 | Input Channel 24 Power Factor Max value Timestamp | MAX_TS_PF_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22006 | Input Channel 24 Current THD Max value | MAX_THD_I_024_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22008 | Input Channel 24 Current THD Max value Timestamp | MAX_TS_THD_I_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22012 | User Channel 1 Current Max value | MAX_I_s001_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22014 | User Channel 1 Current Max value Timestamp | MAX_TS_I_s001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22018 | User Channel 1 Active Power Max value | MAX_P_s001_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22020 | User Channel 1 Active Power Max value Timestamp | MAX_TS_P_s001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22024 | User Channel 1 Reactive Power Max value | MAX_Q_s001_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22026 | User Channel 1 Reactive Power Max value Timestamp | MAX_TS_Q_s001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22030 | User Channel 1 Apparent Power Max value | MAX_S_s001_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22032 | User Channel 1 Apparent Power Max value Timestamp | MAX_TS_S_s001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22036 | Max User Channel 1 Power Factor | MAX_PF_s001 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22038 | Max User Channel 1 Power Factor Timestamp | MAX_TS_PF_s001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22042 | User Channel 2 Current Max value | MAX_I_s002_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22044 | User Channel 2 Current Max value Timestamp | MAX_TS_I_s002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22048 | User Channel 2 Active Power Max value | MAX_P_s002_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22050 | User Channel 2 Active Power Max value Timestamp | MAX_TS_P_s002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22054 | User Channel 2 Reactive Power Max value | MAX_Q_s002_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22056 | User Channel 2 Reactive Power Max value Timestamp | MAX_TS_Q_s002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22060 | User Channel 2 Apparent Power Max value | MAX_S_s002_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22062 | User Channel 2 Apparent Power Max value Timestamp | MAX_TS_S_s002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22066 | Max User Channel 2 Power Factor | MAX_PF_s002 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22068 | Max User Channel 2 Power Factor Timestamp | MAX_TS_PF_s002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22072 | User Channel 3 Current Max value | MAX_I_s003_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22074 | User Channel 3 Current Max value Timestamp | MAX_TS_I_s003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22078 | User Channel 3 Active Power Max value | MAX_P_s003_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22080 | User Channel 3 Active Power Max value Timestamp | MAX_TS_P_s003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22084 | User Channel 3 Reactive Power Max value | MAX_Q_s003_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22086 | User Channel 3 Reactive Power Max value Timestamp | MAX_TS_Q_s003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22090 | User Channel 3 Apparent Power Max value | MAX_S_s003_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22092 | User Channel 3 Apparent Power Max value Timestamp | MAX_TS_S_s003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22096 | Max User Channel 3 Power Factor | MAX_PF_s003 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22098 | Max User Channel 3 Power Factor Timestamp | MAX_TS_PF_s003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22102 | User Channel 4 Current Max value | MAX_I_s004_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22104 | User Channel 4 Current Max value Timestamp | MAX_TS_I_s004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22108 | User Channel 4 Active Power Max value | MAX_P_s004_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22110 | User Channel 4 Active Power Max value Timestamp | MAX_TS_P_s004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22114 | User Channel 4 Reactive Power Max value | MAX_Q_s004_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22116 | User Channel 4 Reactive Power Max value Timestamp | MAX_TS_Q_s004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22120 | User Channel 4 Apparent Power Max value | MAX_S_s004_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22122 | User Channel 4 Apparent Power Max value Timestamp | MAX_TS_S_s004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22126 | Max User Channel 4 Power Factor | MAX_PF_s004 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22128 | Max User Channel 4 Power Factor Timestamp | MAX_TS_PF_s004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22132 | User Channel 5 Current Max value | MAX_I_s005_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22134 | User Channel 5 Current Max value Timestamp | MAX_TS_I_s005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22138 | User Channel 5 Active Power Max value | MAX_P_s005_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22140 | User Channel 5 Active Power Max value Timestamp | MAX_TS_P_s005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22144 | User Channel 5 Reactive Power Max value | MAX_Q_s005_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22146 | User Channel 5 Reactive Power Max value Timestamp | MAX_TS_Q_s005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22150 | User Channel 5 Apparent Power Max value | MAX_S_s005_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22152 | User Channel 5 Apparent Power Max value Timestamp | MAX_TS_S_s005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22156 | Max User Channel 5 Power Factor | MAX_PF_s005 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22158 | Max User Channel 5 Power Factor Timestamp | MAX_TS_PF_s005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22162 | User Channel 6 Current Max value | MAX_I_s006_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22164 | User Channel 6 Current Max value Timestamp | MAX_TS_I_s006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22168 | User Channel 6 Active Power Max value | MAX_P_s006_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22170 | User Channel 6 Active Power Max value Timestamp | MAX_TS_P_s006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22174 | User Channel 6 Reactive Power Max value | MAX_Q_s006_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22176 | User Channel 6 Reactive Power Max value Timestamp | MAX_TS_Q_s006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22180 | User Channel 6 Apparent Power Max value | MAX_S_s006_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22182 | User Channel 6 Apparent Power Max value Timestamp | MAX_TS_S_s006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22186 | Max User Channel 6 Power Factor | MAX_PF_s006 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22188 | Max User Channel 6 Power Factor Timestamp | MAX_TS_PF_s006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22192 | User Channel 7 Current Max value | MAX_I_s007_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22194 | User Channel 7 Current Max value Timestamp | MAX_TS_I_s007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22198 | User Channel 7 Active Power Max value | MAX_P_s007_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22200 | User Channel 7 Active Power Max value Timestamp | MAX_TS_P_s007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22204 | User Channel 7 Reactive Power Max value | MAX_Q_s007_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22206 | User Channel 7 Reactive Power Max value Timestamp | MAX_TS_Q_s007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22210 | User Channel 7 Apparent Power Max value | MAX_S_s007_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22212 | User Channel 7 Apparent Power Max value Timestamp | MAX_TS_S_s007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22216 | Max User Channel 7 Power Factor | MAX_PF_s007 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22218 | Max User Channel 7 Power Factor Timestamp | MAX_TS_PF_s007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22222 | User Channel 8 Current Max value | MAX_I_s008_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22224 | User Channel 8 Current Max value Timestamp | MAX_TS_I_s008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22228 | User Channel 8 Active Power Max value | MAX_P_s008_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22230 | User Channel 8 Active Power Max value Timestamp | MAX_TS_P_s008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22234 | User Channel 8 Reactive Power Max value | MAX_Q_s008_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22236 | User Channel 8 Reactive Power Max value Timestamp | MAX_TS_Q_s008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22240 | User Channel 8 Apparent Power Max value | MAX_S_s008_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22242 | User Channel 8 Apparent Power Max value Timestamp | MAX_TS_S_s008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22246 | Max User Channel 8 Power Factor | MAX_PF_s008 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22248 | Max User Channel 8 Power Factor Timestamp | MAX_TS_PF_s008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22252 | User Channel 9 Current Max value | MAX_I_s009_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22254 | User Channel 9 Current Max value Timestamp | MAX_TS_I_s009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22258 | User Channel 9 Active Power Max value | MAX_P_s009_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22260 | User Channel 9 Active Power Max value Timestamp | MAX_TS_P_s009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22264 | User Channel 9 Reactive Power Max value | MAX_Q_s009_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22266 | User Channel 9 Reactive Power Max value Timestamp | MAX_TS_Q_s009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22270 | User Channel 9 Apparent Power Max value | MAX_S_s009_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22272 | User Channel 9 Apparent Power Max value Timestamp | MAX_TS_S_s009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22276 | Max User Channel 9 Power Factor | MAX_PF_s009 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22278 | Max User Channel 9 Power Factor Timestamp | MAX_TS_PF_s009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22282 | User Channel 10 Current Max value | MAX_I_s010_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22284 | User Channel 10 Current Max value Timestamp | MAX_TS_I_s010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22288 | User Channel 10 Active Power Max value | MAX_P_s010_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22290 | User Channel 10 Active Power Max value Timestamp | MAX_TS_P_s010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22294 | User Channel 10 Reactive Power Max value | MAX_Q_s010_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22296 | User Channel 10 Reactive Power Max value Timestamp | MAX_TS_Q_s010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22300 | User Channel 10 Apparent Power Max value | MAX_S_s010_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22302 | User Channel 10 Apparent Power Max value Timestamp | MAX_TS_S_s010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22306 | Max User Channel 10 Power Factor | MAX_PF_s010 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22308 | Max User Channel 10 Power Factor Timestamp | MAX_TS_PF_s010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22312 | User Channel 11 Current Max value | MAX_I_s011_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22314 | User Channel 11 Current Max value Timestamp | MAX_TS_I_s011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22318 | User Channel 11 Active Power Max value | MAX_P_s011_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22320 | User Channel 11 Active Power Max value Timestamp | MAX_TS_P_s011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22324 | User Channel 11 Reactive Power Max value | MAX_Q_s011_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22326 | User Channel 11 Reactive Power Max value Timestamp | MAX_TS_Q_s011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22330 | User Channel 11 Apparent Power Max value | MAX_S_s011_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22332 | User Channel 11 Apparent Power Max value Timestamp | MAX_TS_S_s011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22336 | Max User Channel 11 Power Factor | MAX_PF_s011 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22338 | Max User Channel 11 Power Factor Timestamp | MAX_TS_PF_s011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22342 | User Channel 12 Current Max value | MAX_I_s012_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22344 | User Channel 12 Current Max value Timestamp | MAX_TS_I_s012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22348 | User Channel 12 Active Power Max value | MAX_P_s012_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22350 | User Channel 12 Active Power Max value Timestamp | MAX_TS_P_s012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22354 | User Channel 12 Reactive Power Max value | MAX_Q_s012_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22356 | User Channel 12 Reactive Power Max value Timestamp | MAX_TS_Q_s012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22360 | User Channel 12 Apparent Power Max value | MAX_S_s012_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22362 | User Channel 12 Apparent Power Max value Timestamp | MAX_TS_S_s012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22366 | Max User Channel 12 Power Factor | MAX_PF_s012 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22368 | Max User Channel 12 Power Factor Timestamp | MAX_TS_PF_s012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22528 | System Frequency Min value | MIN_FREQ_Hz | Hz |  | float32 | R | 2 | 1 | [9 empty] | max min
22530 | System Frequency Min value Timestamp | MIN_TS_FREQ |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22534 | Phase A Line-to-Neutral Voltage Min value | MIN_VLN_a_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
22536 | Phase A Line-to-Neutral Voltage Min value Timestamp | MIN_VLNTS_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22540 | Phase B Line-to-Neutral Voltage Min value | MIN_VLN_b_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
22542 | Phase B Line-to-Neutral Voltage Min value Timestamp | MIN_VLNTS_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22546 | Phase C Line-to-Neutral Voltage Min value | MIN_VLN_c_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
22548 | Phase C Line-to-Neutral Voltage Min value Timestamp | MIN_VLNTS_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22552 | Phase AB Line-to-Line Voltage Min value | MIN_VLL_ab_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
22554 | Phase AB Line-to-Line Voltage Min value Timestamp | MIN_VLLTS_ab_V |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22558 | Phase BC Line-to-Line Voltage Min value | MIN_VLL_bc_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
22560 | Phase BC Line-to-Line Voltage Min value Timestamp | MIN_VLLTS_bc_V |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22564 | Phase CA Line-to-Line Voltage Min value | MIN_VLL_ca_V | V |  | float32 | R | 2 | 1 | [9 empty] | max min
22566 | Phase CA Line-to-Line Voltage Min value Timestamp | MIN_VLLTS_ca_V |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22570 | Phase A Current Min value | MIN_I_a_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22572 | Phase A Current Min value Timestamp | MIN_TS_I_a_A |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22576 | Phase A Active Power Min value | MIN_P_a_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22578 | Phase A Active Power Min value Timestamp | MIN_TS_P_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22582 | Phase A Reactive Power Min value | MIN_Q_a_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22584 | Phase A Reactive Power Min value Timestamp | MIN_TS_Q_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22588 | Phase A Apparent Power Min value | MIN_S_a_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22590 | Phase A Apparent Power Min value Timestamp | MIN_TS_S_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22594 | Phase A Power Factor Min value | MIN_PF_a |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22596 | Phase A Power Factor Min value Timestamp | MIN_TS_PF_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22600 | Phase A Voltage THD Min value | MIN_THD_V_a_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22602 | Phase A Voltage THD Min value Timestamp | MIN_TS_THD_V_a |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22606 | Phase B Current Min value | MIN_I_b_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22608 | Phase B Current Min value Timestamp | MIN_TS_I_b_A |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22612 | Phase B Active Power Min value | MIN_P_b_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22614 | Phase B Active Power Min value Timestamp | MIN_TS_P_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22618 | Phase B Reactive Power Min value | MIN_Q_b_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22620 | Phase B Reactive Power Min value Timestamp | MIN_TS_Q_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22624 | Phase B Apparent Power Min value | MIN_S_b_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22626 | Phase B Apparent Power Min value Timestamp | MIN_TS_S_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22630 | Phase B Power Factor Min value | MIN_PF_b |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22632 | Phase B Power Factor Min value Timestamp | MIN_TS_PF_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22636 | Phase B Voltage THD Min value | MIN_THD_V_b_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22638 | Phase B Voltage THD Min value Timestamp | MIN_TS_THD_V_b |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22642 | Phase C Current Min value | MIN_I_c_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22644 | Phase C Current Min value Timestamp | MIN_TS_I_c_A |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22648 | Phase C Active Power Min value | MIN_P_c_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22650 | Phase C Active Power Min value Timestamp | MIN_TS_P_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22654 | Phase C Reactive Power Min value | MIN_Q_c_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22656 | Phase C Reactive Power Min value Timestamp | MIN_TS_Q_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22660 | Phase C Apparent Power Min value | MIN_S_c_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22662 | Phase C Apparent Power Min value Timestamp | MIN_TS_S_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22666 | Phase C Power Factor Min value | MIN_PF_c |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22668 | Phase C Power Factor Min value Timestamp | MIN_TS_PF_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22672 | Phase C Voltage THD Min value | MIN_THD_V_c_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22674 | Phase C Voltage THD Min value Timestamp | MIN_TS_THD_V_c |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22678 | Voltage Unbalance Factor Magnitude Min value | MIN_UNBL_V_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22680 | Voltage Unbalance Factor Magnitude Min value Timestamp | MIN_UNBLTS_V_% |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22684 | Input Channel 1 Current Min value | MIN_I_001_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22686 | Input Channel 1 Current Min value Timestamp | MIN_TS_I_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22690 | Input Channel 1 Active Power Min value | MIN_P_001_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22692 | Input Channel 1 Active Power Min value Timestamp | MIN_TS_P_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22696 | Input Channel 1 Reactive Power Min value | MIN_Q_001_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22698 | Input Channel 1 Reactive Power Min value Timestamp | MIN_TS_Q_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22702 | Input Channel 1 Apparent Power Min value | MIN_S_001_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22704 | Input Channel 1 Apparent Power Min value Timestamp | MIN_TS_S_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22708 | Input Channel 1 Power Factor Min value | MIN_PF_001 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22710 | Input Channel 1 Power Factor Min value Timestamp | MIN_TS_PF_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22714 | Input Channel 1 Current THD Min value | MIN_THD_I_001_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22716 | Input Channel 1 Current THD Min value Timestamp | MIN_TS_THD_I_001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22720 | Input Channel 2 Current Min value | MIN_I_002_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22722 | Input Channel 2 Current Min value Timestamp | MIN_TS_I_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22726 | Input Channel 2 Active Power Min value | MIN_P_002_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22728 | Input Channel 2 Active Power Min value Timestamp | MIN_TS_P_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22732 | Input Channel 2 Reactive Power Min value | MIN_Q_002_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22734 | Input Channel 2 Reactive Power Min value Timestamp | MIN_TS_Q_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22738 | Input Channel 2 Apparent Power Min value | MIN_S_002_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22740 | Input Channel 2 Apparent Power Min value Timestamp | MIN_TS_S_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22744 | Input Channel 2 Power Factor Min value | MIN_PF_002 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22746 | Input Channel 2 Power Factor Min value Timestamp | MIN_TS_PF_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22750 | Input Channel 2 Current THD Min value | MIN_THD_I_002_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22752 | Input Channel 2 Current THD Min value Timestamp | MIN_TS_THD_I_002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22756 | Input Channel 3 Current Min value | MIN_I_003_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22758 | Input Channel 3 Current Min value Timestamp | MIN_TS_I_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22762 | Input Channel 3 Active Power Min value | MIN_P_003_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22764 | Input Channel 3 Active Power Min value Timestamp | MIN_TS_P_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22768 | Input Channel 3 Reactive Power Min value | MIN_Q_003_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22770 | Input Channel 3 Reactive Power Min value Timestamp | MIN_TS_Q_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22774 | Input Channel 3 Apparent Power Min value | MIN_S_003_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22776 | Input Channel 3 Apparent Power Min value Timestamp | MIN_TS_S_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22780 | Input Channel 3 Power Factor Min value | MIN_PF_003 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22782 | Input Channel 3 Power Factor Min value Timestamp | MIN_TS_PF_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22786 | Input Channel 3 Current THD Min value | MIN_THD_I_003_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22788 | Input Channel 3 Current THD Min value Timestamp | MIN_TS_THD_I_003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22792 | Input Channel 4 Current Min value | MIN_I_004_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22794 | Input Channel 4 Current Min value Timestamp | MIN_TS_I_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22798 | Input Channel 4 Active Power Min value | MIN_P_004_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22800 | Input Channel 4 Active Power Min value Timestamp | MIN_TS_P_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22804 | Input Channel 4 Reactive Power Min value | MIN_Q_004_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22806 | Input Channel 4 Reactive Power Min value Timestamp | MIN_TS_Q_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22810 | Input Channel 4 Apparent Power Min value | MIN_S_004_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22812 | Input Channel 4 Apparent Power Min value Timestamp | MIN_TS_S_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22816 | Input Channel 4 Power Factor Min value | MIN_PF_004 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22818 | Input Channel 4 Power Factor Min value Timestamp | MIN_TS_PF_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22822 | Input Channel 4 Current THD Min value | MIN_THD_I_004_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22824 | Input Channel 4 Current THD Min value Timestamp | MIN_TS_THD_I_004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22828 | Input Channel 5 Current Min value | MIN_I_005_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22830 | Input Channel 5 Current Min value Timestamp | MIN_TS_I_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22834 | Input Channel 5 Active Power Min value | MIN_P_005_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22836 | Input Channel 5 Active Power Min value Timestamp | MIN_TS_P_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22840 | Input Channel 5 Reactive Power Min value | MIN_Q_005_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22842 | Input Channel 5 Reactive Power Min value Timestamp | MIN_TS_Q_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22846 | Input Channel 5 Apparent Power Min value | MIN_S_005_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22848 | Input Channel 5 Apparent Power Min value Timestamp | MIN_TS_S_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22852 | Input Channel 5 Power Factor Min value | MIN_PF_005 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22854 | Input Channel 5 Power Factor Min value Timestamp | MIN_TS_PF_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22858 | Input Channel 5 Current THD Min value | MIN_THD_I_005_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22860 | Input Channel 5 Current THD Min value Timestamp | MIN_TS_THD_I_005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22864 | Input Channel 6 Current Min value | MIN_I_006_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22866 | Input Channel 6 Current Min value Timestamp | MIN_TS_I_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22870 | Input Channel 6 Active Power Min value | MIN_P_006_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22872 | Input Channel 6 Active Power Min value Timestamp | MIN_TS_P_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22876 | Input Channel 6 Reactive Power Min value | MIN_Q_006_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22878 | Input Channel 6 Reactive Power Min value Timestamp | MIN_TS_Q_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22882 | Input Channel 6 Apparent Power Min value | MIN_S_006_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22884 | Input Channel 6 Apparent Power Min value Timestamp | MIN_TS_S_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22888 | Input Channel 6 Power Factor Min value | MIN_PF_006 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22890 | Input Channel 6 Power Factor Min value Timestamp | MIN_TS_PF_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22894 | Input Channel 6 Current THD Min value | MIN_THD_I_006_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22896 | Input Channel 6 Current THD Min value Timestamp | MIN_TS_THD_I_006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22900 | Input Channel 7 Current Min value | MIN_I_007_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22902 | Input Channel 7 Current Min value Timestamp | MIN_TS_I_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22906 | Input Channel 7 Active Power Min value | MIN_P_007_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22908 | Input Channel 7 Active Power Min value Timestamp | MIN_TS_P_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22912 | Input Channel 7 Reactive Power Min value | MIN_Q_007_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22914 | Input Channel 7 Reactive Power Min value Timestamp | MIN_TS_Q_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22918 | Input Channel 7 Apparent Power Min value | MIN_S_007_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22920 | Input Channel 7 Apparent Power Min value Timestamp | MIN_TS_S_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22924 | Input Channel 7 Power Factor Min value | MIN_PF_007 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22926 | Input Channel 7 Power Factor Min value Timestamp | MIN_TS_PF_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22930 | Input Channel 7 Current THD Min value | MIN_THD_I_007_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22932 | Input Channel 7 Current THD Min value Timestamp | MIN_TS_THD_I_007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22936 | Input Channel 8 Current Min value | MIN_I_008_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22938 | Input Channel 8 Current Min value Timestamp | MIN_TS_I_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22942 | Input Channel 8 Active Power Min value | MIN_P_008_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22944 | Input Channel 8 Active Power Min value Timestamp | MIN_TS_P_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22948 | Input Channel 8 Reactive Power Min value | MIN_Q_008_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22950 | Input Channel 8 Reactive Power Min value Timestamp | MIN_TS_Q_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22954 | Input Channel 8 Apparent Power Min value | MIN_S_008_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22956 | Input Channel 8 Apparent Power Min value Timestamp | MIN_TS_S_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22960 | Input Channel 8 Power Factor Min value | MIN_PF_008 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22962 | Input Channel 8 Power Factor Min value Timestamp | MIN_TS_PF_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22966 | Input Channel 8 Current THD Min value | MIN_THD_I_008_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
22968 | Input Channel 8 Current THD Min value Timestamp | MIN_TS_THD_I_008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22972 | Input Channel 9 Current Min value | MIN_I_009_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
22974 | Input Channel 9 Current Min value Timestamp | MIN_TS_I_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22978 | Input Channel 9 Active Power Min value | MIN_P_009_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
22980 | Input Channel 9 Active Power Min value Timestamp | MIN_TS_P_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22984 | Input Channel 9 Reactive Power Min value | MIN_Q_009_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
22986 | Input Channel 9 Reactive Power Min value Timestamp | MIN_TS_Q_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22990 | Input Channel 9 Apparent Power Min value | MIN_S_009_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
22992 | Input Channel 9 Apparent Power Min value Timestamp | MIN_TS_S_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
22996 | Input Channel 9 Power Factor Min value | MIN_PF_009 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
22998 | Input Channel 9 Power Factor Min value Timestamp | MIN_TS_PF_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23002 | Input Channel 9 Current THD Min value | MIN_THD_I_009_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23004 | Input Channel 9 Current THD Min value Timestamp | MIN_TS_THD_I_009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23008 | Input Channel 10 Current Min value | MIN_I_010_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23010 | Input Channel 10 Current Min value Timestamp | MIN_TS_I_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23014 | Input Channel 10 Active Power Min value | MIN_P_010_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23016 | Input Channel 10 Active Power Min value Timestamp | MIN_TS_P_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23020 | Input Channel 10 Reactive Power Min value | MIN_Q_010_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23022 | Input Channel 10 Reactive Power Min value Timestamp | MIN_TS_Q_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23026 | Input Channel 10 Apparent Power Min value | MIN_S_010_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23028 | Input Channel 10 Apparent Power Min value Timestamp | MIN_TS_S_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23032 | Input Channel 10 Power Factor Min value | MIN_PF_010 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23034 | Input Channel 10 Power Factor Min value Timestamp | MIN_TS_PF_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23038 | Input Channel 10 Current THD Min value | MIN_THD_I_010_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23040 | Input Channel 10 Current THD Min value Timestamp | MIN_TS_THD_I_010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23044 | Input Channel 11 Current Min value | MIN_I_011_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23046 | Input Channel 11 Current Min value Timestamp | MIN_TS_I_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23050 | Input Channel 11 Active Power Min value | MIN_P_011_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23052 | Input Channel 11 Active Power Min value Timestamp | MIN_TS_P_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23056 | Input Channel 11 Reactive Power Min value | MIN_Q_011_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23058 | Input Channel 11 Reactive Power Min value Timestamp | MIN_TS_Q_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23062 | Input Channel 11 Apparent Power Min value | MIN_S_011_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23064 | Input Channel 11 Apparent Power Min value Timestamp | MIN_TS_S_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23068 | Input Channel 11 Power Factor Min value | MIN_PF_011 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23070 | Input Channel 11 Power Factor Min value Timestamp | MIN_TS_PF_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23074 | Input Channel 11 Current THD Min value | MIN_THD_I_011_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23076 | Input Channel 11 Current THD Min value Timestamp | MIN_TS_THD_I_011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23080 | Input Channel 12 Current Min value | MIN_I_012_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23082 | Input Channel 12 Current Min value Timestamp | MIN_TS_I_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23086 | Input Channel 12 Active Power Min value | MIN_P_012_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23088 | Input Channel 12 Active Power Min value Timestamp | MIN_TS_P_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23092 | Input Channel 12 Reactive Power Min value | MIN_Q_012_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23094 | Input Channel 12 Reactive Power Min value Timestamp | MIN_TS_Q_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23098 | Input Channel 12 Apparent Power Min value | MIN_S_012_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23100 | Input Channel 12 Apparent Power Min value Timestamp | MIN_TS_S_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23104 | Input Channel 12 Power Factor Min value | MIN_PF_012 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23106 | Input Channel 12 Power Factor Min value Timestamp | MIN_TS_PF_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23110 | Input Channel 12 Current THD Min value | MIN_THD_I_012_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23112 | Input Channel 12 Current THD Min value Timestamp | MIN_TS_THD_I_012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23116 | Input Channel 13 Current Min value | MIN_I_013_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23118 | Input Channel 13 Current Min value Timestamp | MIN_TS_I_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23122 | Input Channel 13 Active Power Min value | MIN_P_013_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23124 | Input Channel 13 Active Power Min value Timestamp | MIN_TS_P_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23128 | Input Channel 13 Reactive Power Min value | MIN_Q_013_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23130 | Input Channel 13 Reactive Power Min value Timestamp | MIN_TS_Q_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23134 | Input Channel 13 Apparent Power Min value | MIN_S_013_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23136 | Input Channel 13 Apparent Power Min value Timestamp | MIN_TS_S_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23140 | Input Channel 13 Power Factor Min value | MIN_PF_013 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23142 | Input Channel 13 Power Factor Min value Timestamp | MIN_TS_PF_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23146 | Input Channel 13 Current THD Min value | MIN_THD_I_013_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23148 | Input Channel 13 Current THD Min value Timestamp | MIN_TS_THD_I_013 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23152 | Input Channel 14 Current Min value | MIN_I_014_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23154 | Input Channel 14 Current Min value Timestamp | MIN_TS_I_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23158 | Input Channel 14 Active Power Min value | MIN_P_014_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23160 | Input Channel 14 Active Power Min value Timestamp | MIN_TS_P_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23164 | Input Channel 14 Reactive Power Min value | MIN_Q_014_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23166 | Input Channel 14 Reactive Power Min value Timestamp | MIN_TS_Q_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23170 | Input Channel 14 Apparent Power Min value | MIN_S_014_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23172 | Input Channel 14 Apparent Power Min value Timestamp | MIN_TS_S_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23176 | Input Channel 14 Power Factor Min value | MIN_PF_014 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23178 | Input Channel 14 Power Factor Min value Timestamp | MIN_TS_PF_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23182 | Input Channel 14 Current THD Min value | MIN_THD_I_014_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23184 | Input Channel 14 Current THD Min value Timestamp | MIN_TS_THD_I_014 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23188 | Input Channel 15 Current Min value | MIN_I_015_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23190 | Input Channel 15 Current Min value Timestamp | MIN_TS_I_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23194 | Input Channel 15 Active Power Min value | MIN_P_015_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23196 | Input Channel 15 Active Power Min value Timestamp | MIN_TS_P_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23200 | Input Channel 15 Reactive Power Min value | MIN_Q_015_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23202 | Input Channel 15 Reactive Power Min value Timestamp | MIN_TS_Q_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23206 | Input Channel 15 Apparent Power Min value | MIN_S_015_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23208 | Input Channel 15 Apparent Power Min value Timestamp | MIN_TS_S_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23212 | Input Channel 15 Power Factor Min value | MIN_PF_015 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23214 | Input Channel 15 Power Factor Min value Timestamp | MIN_TS_PF_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23218 | Input Channel 15 Current THD Min value | MIN_THD_I_015_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23220 | Input Channel 15 Current THD Min value Timestamp | MIN_TS_THD_I_015 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23224 | Input Channel 16 Current Min value | MIN_I_016_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23226 | Input Channel 16 Current Min value Timestamp | MIN_TS_I_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23230 | Input Channel 16 Active Power Min value | MIN_P_016_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23232 | Input Channel 16 Active Power Min value Timestamp | MIN_TS_P_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23236 | Input Channel 16 Reactive Power Min value | MIN_Q_016_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23238 | Input Channel 16 Reactive Power Min value Timestamp | MIN_TS_Q_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23242 | Input Channel 16 Apparent Power Min value | MIN_S_016_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23244 | Input Channel 16 Apparent Power Min value Timestamp | MIN_TS_S_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23248 | Input Channel 16 Power Factor Min value | MIN_PF_016 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23250 | Input Channel 16 Power Factor Min value Timestamp | MIN_TS_PF_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23254 | Input Channel 16 Current THD Min value | MIN_THD_I_016_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23256 | Input Channel 16 Current THD Min value Timestamp | MIN_TS_THD_I_016 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23260 | Input Channel 17 Current Min value | MIN_I_017_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23262 | Input Channel 17 Current Min value Timestamp | MIN_TS_I_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23266 | Input Channel 17 Active Power Min value | MIN_P_017_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23268 | Input Channel 17 Active Power Min value Timestamp | MIN_TS_P_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23272 | Input Channel 17 Reactive Power Min value | MIN_Q_017_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23274 | Input Channel 17 Reactive Power Min value Timestamp | MIN_TS_Q_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23278 | Input Channel 17 Apparent Power Min value | MIN_S_017_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23280 | Input Channel 17 Apparent Power Min value Timestamp | MIN_TS_S_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23284 | Input Channel 17 Power Factor Min value | MIN_PF_017 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23286 | Input Channel 17 Power Factor Min value Timestamp | MIN_TS_PF_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23290 | Input Channel 17 Current THD Min value | MIN_THD_I_017_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23292 | Input Channel 17 Current THD Min value Timestamp | MIN_TS_THD_I_017 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23296 | Input Channel 18 Current Min value | MIN_I_018_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23298 | Input Channel 18 Current Min value Timestamp | MIN_TS_I_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23302 | Input Channel 18 Active Power Min value | MIN_P_018_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23304 | Input Channel 18 Active Power Min value Timestamp | MIN_TS_P_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23308 | Input Channel 18 Reactive Power Min value | MIN_Q_018_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23310 | Input Channel 18 Reactive Power Min value Timestamp | MIN_TS_Q_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23314 | Input Channel 18 Apparent Power Min value | MIN_S_018_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23316 | Input Channel 18 Apparent Power Min value Timestamp | MIN_TS_S_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23320 | Input Channel 18 Power Factor Min value | MIN_PF_018 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23322 | Input Channel 18 Power Factor Min value Timestamp | MIN_TS_PF_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23326 | Input Channel 18 Current THD Min value | MIN_THD_I_018_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23328 | Input Channel 18 Current THD Min value Timestamp | MIN_TS_THD_I_018 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23332 | Input Channel 19 Current Min value | MIN_I_019_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23334 | Input Channel 19 Current Min value Timestamp | MIN_TS_I_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23338 | Input Channel 19 Active Power Min value | MIN_P_019_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23340 | Input Channel 19 Active Power Min value Timestamp | MIN_TS_P_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23344 | Input Channel 19 Reactive Power Min value | MIN_Q_019_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23346 | Input Channel 19 Reactive Power Min value Timestamp | MIN_TS_Q_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23350 | Input Channel 19 Apparent Power Min value | MIN_S_019_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23352 | Input Channel 19 Apparent Power Min value Timestamp | MIN_TS_S_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23356 | Input Channel 19 Power Factor Min value | MIN_PF_019 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23358 | Input Channel 19 Power Factor Min value Timestamp | MIN_TS_PF_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23362 | Input Channel 19 Current THD Min value | MIN_THD_I_019_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23364 | Input Channel 19 Current THD Min value Timestamp | MIN_TS_THD_I_019 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23368 | Input Channel 20 Current Min value | MIN_I_020_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23370 | Input Channel 20 Current Min value Timestamp | MIN_TS_I_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23374 | Input Channel 20 Active Power Min value | MIN_P_020_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23376 | Input Channel 20 Active Power Min value Timestamp | MIN_TS_P_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23380 | Input Channel 20 Reactive Power Min value | MIN_Q_020_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23382 | Input Channel 20 Reactive Power Min value Timestamp | MIN_TS_Q_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23386 | Input Channel 20 Apparent Power Min value | MIN_S_020_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23388 | Input Channel 20 Apparent Power Min value Timestamp | MIN_TS_S_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23392 | Input Channel 20 Power Factor Min value | MIN_PF_020 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23394 | Input Channel 20 Power Factor Min value Timestamp | MIN_TS_PF_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23398 | Input Channel 20 Current THD Min value | MIN_THD_I_020_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23400 | Input Channel 20 Current THD Min value Timestamp | MIN_TS_THD_I_020 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23404 | Input Channel 21 Current Min value | MIN_I_021_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23406 | Input Channel 21 Current Min value Timestamp | MIN_TS_I_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23410 | Input Channel 21 Active Power Min value | MIN_P_021_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23412 | Input Channel 21 Active Power Min value Timestamp | MIN_TS_P_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23416 | Input Channel 21 Reactive Power Min value | MIN_Q_021_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23418 | Input Channel 21 Reactive Power Min value Timestamp | MIN_TS_Q_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23422 | Input Channel 21 Apparent Power Min value | MIN_S_021_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23424 | Input Channel 21 Apparent Power Min value Timestamp | MIN_TS_S_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23428 | Input Channel 21 Power Factor Min value | MIN_PF_021 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23430 | Input Channel 21 Power Factor Min value Timestamp | MIN_TS_PF_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23434 | Input Channel 21 Current THD Min value | MIN_THD_I_021_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23436 | Input Channel 21 Current THD Min value Timestamp | MIN_TS_THD_I_021 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23440 | Input Channel 22 Current Min value | MIN_I_022_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23442 | Input Channel 22 Current Min value Timestamp | MIN_TS_I_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23446 | Input Channel 22 Active Power Min value | MIN_P_022_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23448 | Input Channel 22 Active Power Min value Timestamp | MIN_TS_P_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23452 | Input Channel 22 Reactive Power Min value | MIN_Q_022_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23454 | Input Channel 22 Reactive Power Min value Timestamp | MIN_TS_Q_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23458 | Input Channel 22 Apparent Power Min value | MIN_S_022_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23460 | Input Channel 22 Apparent Power Min value Timestamp | MIN_TS_S_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23464 | Input Channel 22 Power Factor Min value | MIN_PF_022 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23466 | Input Channel 22 Power Factor Min value Timestamp | MIN_TS_PF_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23470 | Input Channel 22 Current THD Min value | MIN_THD_I_022_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23472 | Input Channel 22 Current THD Min value Timestamp | MIN_TS_THD_I_022 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23476 | Input Channel 23 Current Min value | MIN_I_023_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23478 | Input Channel 23 Current Min value Timestamp | MIN_TS_I_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23482 | Input Channel 23 Active Power Min value | MIN_P_023_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23484 | Input Channel 23 Active Power Min value Timestamp | MIN_TS_P_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23488 | Input Channel 23 Reactive Power Min value | MIN_Q_023_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23490 | Input Channel 23 Reactive Power Min value Timestamp | MIN_TS_Q_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23494 | Input Channel 23 Apparent Power Min value | MIN_S_023_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23496 | Input Channel 23 Apparent Power Min value Timestamp | MIN_TS_S_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23500 | Input Channel 23 Power Factor Min value | MIN_PF_023 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23502 | Input Channel 23 Power Factor Min value Timestamp | MIN_TS_PF_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23506 | Input Channel 23 Current THD Min value | MIN_THD_I_023_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23508 | Input Channel 23 Current THD Min value Timestamp | MIN_TS_THD_I_023 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23512 | Input Channel 24 Current Min value | MIN_I_024_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23514 | Input Channel 24 Current Min value Timestamp | MIN_TS_I_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23518 | Input Channel 24 Active Power Min value | MIN_P_024_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23520 | Input Channel 24 Active Power Min value Timestamp | MIN_TS_P_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23524 | Input Channel 24 Reactive Power Min value | MIN_Q_024_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23526 | Input Channel 24 Reactive Power Min value Timestamp | MIN_TS_Q_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23530 | Input Channel 24 Apparent Power Min value | MIN_S_024_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23532 | Input Channel 24 Apparent Power Min value Timestamp | MIN_TS_S_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23536 | Input Channel 24 Power Factor Min value | MIN_PF_024 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23538 | Input Channel 24 Power Factor Min value Timestamp | MIN_TS_PF_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23542 | Input Channel 24 Current THD Min value | MIN_THD_I_024_% | % |  | float32 | R | 2 | 1 | [9 empty] | max min
23544 | Input Channel 24 Current THD Min value Timestamp | MIN_TS_THD_I_024 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23548 | User Channel 1 Current Min value | MIN_I_s001_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23550 | User Channel 1 Current Min value Timestamp | MIN_TS_I_s001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23554 | User Channel 1 Active Power Min value | MIN_P_s001_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23556 | User Channel 1 Active Power Min value Timestamp | MIN_TS_P_s001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23560 | User Channel 1 Reactive Power Min value | MIN_Q_s001_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23562 | User Channel 1 Reactive Power Min value Timestamp | MIN_TS_Q_s001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23566 | User Channel 1 Apparent Power Min value | MIN_S_s001_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23568 | User Channel 1 Apparent Power Min value Timestamp | MIN_TS_S_s001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23572 | Min User Channel 1 Power Factor | MIN_PF_s001 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23574 | User Channel 1 Power Factor Timestamp | MIN_TS_PF_s001 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23578 | User Channel 2 Current Min value | MIN_I_s002_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23580 | User Channel 2 Current Min value Timestamp | MIN_TS_I_s002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23584 | User Channel 2 Active Power Min value | MIN_P_s002_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23586 | User Channel 2 Active Power Min value Timestamp | MIN_TS_P_s002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23590 | User Channel 2 Reactive Power Min value | MIN_Q_s002_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23592 | User Channel 2 Reactive Power Min value Timestamp | MIN_TS_Q_s002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23596 | User Channel 2 Apparent Power Min value | MIN_S_s002_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23598 | User Channel 2 Apparent Power Min value Timestamp | MIN_TS_S_s002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23602 | Min User Channel 2 Power Factor | MIN_PF_s002 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23604 | User Channel 2 Power Factor Timestamp | MIN_TS_PF_s002 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23608 | User Channel 3 Current Min value | MIN_I_s003_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23610 | User Channel 3 Current Min value Timestamp | MIN_TS_I_s003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23614 | User Channel 3 Active Power Min value | MIN_P_s003_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23616 | User Channel 3 Active Power Min value Timestamp | MIN_TS_P_s003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23620 | User Channel 3 Reactive Power Min value | MIN_Q_s003_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23622 | User Channel 3 Reactive Power Min value Timestamp | MIN_TS_Q_s003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23626 | User Channel 3 Apparent Power Min value | MIN_S_s003_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23628 | User Channel 3 Apparent Power Min value Timestamp | MIN_TS_S_s003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23632 | Min User Channel 3 Power Factor | MIN_PF_s003 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23634 | User Channel 3 Power Factor Timestamp | MIN_TS_PF_s003 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23638 | User Channel 4 Current Min value | MIN_I_s004_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23640 | User Channel 4 Current Min value Timestamp | MIN_TS_I_s004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23644 | User Channel 4 Active Power Min value | MIN_P_s004_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23646 | User Channel 4 Active Power Min value Timestamp | MIN_TS_P_s004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23650 | User Channel 4 Reactive Power Min value | MIN_Q_s004_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23652 | User Channel 4 Reactive Power Min value Timestamp | MIN_TS_Q_s004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23656 | User Channel 4 Apparent Power Min value | MIN_S_s004_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23658 | User Channel 4 Apparent Power Min value Timestamp | MIN_TS_S_s004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23662 | Min User Channel 4 Power Factor | MIN_PF_s004 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23664 | User Channel 4 Power Factor Timestamp | MIN_TS_PF_s004 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23668 | User Channel 5 Current Min value | MIN_I_s005_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23670 | User Channel 5 Current Min value Timestamp | MIN_TS_I_s005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23674 | User Channel 5 Active Power Min value | MIN_P_s005_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23676 | User Channel 5 Active Power Min value Timestamp | MIN_TS_P_s005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23680 | User Channel 5 Reactive Power Min value | MIN_Q_s005_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23682 | User Channel 5 Reactive Power Min value Timestamp | MIN_TS_Q_s005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23686 | User Channel 5 Apparent Power Min value | MIN_S_s005_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23688 | User Channel 5 Apparent Power Min value Timestamp | MIN_TS_S_s005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23692 | Min User Channel 5 Power Factor | MIN_PF_s005 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23694 | User Channel 5 Power Factor Timestamp | MIN_TS_PF_s005 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23698 | User Channel 6 Current Min value | MIN_I_s006_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23700 | User Channel 6 Current Min value Timestamp | MIN_TS_I_s006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23704 | User Channel 6 Active Power Min value | MIN_P_s006_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23706 | User Channel 6 Active Power Min value Timestamp | MIN_TS_P_s006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23710 | User Channel 6 Reactive Power Min value | MIN_Q_s006_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23712 | User Channel 6 Reactive Power Min value Timestamp | MIN_TS_Q_s006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23716 | User Channel 6 Apparent Power Min value | MIN_S_s006_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23718 | User Channel 6 Apparent Power Min value Timestamp | MIN_TS_S_s006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23722 | Min User Channel 6 Power Factor | MIN_PF_s006 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23724 | User Channel 6 Power Factor Timestamp | MIN_TS_PF_s006 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23728 | User Channel 7 Current Min value | MIN_I_s007_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23730 | User Channel 7 Current Min value Timestamp | MIN_TS_I_s007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23734 | User Channel 7 Active Power Min value | MIN_P_s007_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23736 | User Channel 7 Active Power Min value Timestamp | MIN_TS_P_s007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23740 | User Channel 7 Reactive Power Min value | MIN_Q_s007_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23742 | User Channel 7 Reactive Power Min value Timestamp | MIN_TS_Q_s007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23746 | User Channel 7 Apparent Power Min value | MIN_S_s007_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23748 | User Channel 7 Apparent Power Min value Timestamp | MIN_TS_S_s007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23752 | Min User Channel 7 Power Factor | MIN_PF_s007 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23754 | User Channel 7 Power Factor Timestamp | MIN_TS_PF_s007 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23758 | User Channel 8 Current Min value | MIN_I_s008_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23760 | User Channel 8 Current Min value Timestamp | MIN_TS_I_s008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23764 | User Channel 8 Active Power Min value | MIN_P_s008_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23766 | User Channel 8 Active Power Min value Timestamp | MIN_TS_P_s008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23770 | User Channel 8 Reactive Power Min value | MIN_Q_s008_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23772 | User Channel 8 Reactive Power Min value Timestamp | MIN_TS_Q_s008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23776 | User Channel 8 Apparent Power Min value | MIN_S_s008_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23778 | User Channel 8 Apparent Power Min value Timestamp | MIN_TS_S_s008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23782 | Min User Channel 8 Power Factor | MIN_PF_s008 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23784 | User Channel 8 Power Factor Timestamp | MIN_TS_PF_s008 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23788 | User Channel 9 Current Min value | MIN_I_s009_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23790 | User Channel 9 Current Min value Timestamp | MIN_TS_I_s009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23794 | User Channel 9 Active Power Min value | MIN_P_s009_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23796 | User Channel 9 Active Power Min value Timestamp | MIN_TS_P_s009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23800 | User Channel 9 Reactive Power Min value | MIN_Q_s009_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23802 | User Channel 9 Reactive Power Min value Timestamp | MIN_TS_Q_s009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23806 | User Channel 9 Apparent Power Min value | MIN_S_s009_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23808 | User Channel 9 Apparent Power Min value Timestamp | MIN_TS_S_s009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23812 | Min User Channel 9 Power Factor | MIN_PF_s009 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23814 | User Channel 9 Power Factor Timestamp | MIN_TS_PF_s009 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23818 | User Channel 10 Current Min value | MIN_I_s010_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23820 | User Channel 10 Current Min value Timestamp | MIN_TS_I_s010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23824 | User Channel 10 Active Power Min value | MIN_P_s010_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23826 | User Channel 10 Active Power Min value Timestamp | MIN_TS_P_s010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23830 | User Channel 10 Reactive Power Min value | MIN_Q_s010_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23832 | User Channel 10 Reactive Power Min value Timestamp | MIN_TS_Q_s010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23836 | User Channel 10 Apparent Power Min value | MIN_S_s010_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23838 | User Channel 10 Apparent Power Min value Timestamp | MIN_TS_S_s010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23842 | Min User Channel 10 Power Factor | MIN_PF_s010 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23844 | User Channel 10 Power Factor Timestamp | MIN_TS_PF_s010 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23848 | User Channel 11 Current Min value | MIN_I_s011_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23850 | User Channel 11 Current Min value Timestamp | MIN_TS_I_s011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23854 | User Channel 11 Active Power Min value | MIN_P_s011_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23856 | User Channel 11 Active Power Min value Timestamp | MIN_TS_P_s011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23860 | User Channel 11 Reactive Power Min value | MIN_Q_s011_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23862 | User Channel 11 Reactive Power Min value Timestamp | MIN_TS_Q_s011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23866 | User Channel 11 Apparent Power Min value | MIN_S_s011_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23868 | User Channel 11 Apparent Power Min value Timestamp | MIN_TS_S_s011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23872 | Min User Channel 11 Power Factor | MIN_PF_s011 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23874 | User Channel 11 Power Factor Timestamp | MIN_TS_PF_s011 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23878 | User Channel 12 Current Min value | MIN_I_s012_A | A |  | float32 | R | 2 | 1 | [9 empty] | max min
23880 | User Channel 12 Current Min value Timestamp | MIN_TS_I_s012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23884 | User Channel 12 Active Power Min value | MIN_P_s012_kW | kW |  | float32 | R | 2 | 1 | [9 empty] | max min
23886 | User Channel 12 Active Power Min value Timestamp | MIN_TS_P_s012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23890 | User Channel 12 Reactive Power Min value | MIN_Q_s012_kvar | kvar |  | float32 | R | 2 | 1 | [9 empty] | max min
23892 | User Channel 12 Reactive Power Min value Timestamp | MIN_TS_Q_s012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23896 | User Channel 12 Apparent Power Min value | MIN_S_s012_kVA | kVA |  | float32 | R | 2 | 1 | [9 empty] | max min
23898 | User Channel 12 Apparent Power Min value Timestamp | MIN_TS_S_s012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
23902 | Min User Channel 12 Power Factor | MIN_PF_s012 |  | 删除单位 | float32 | R | 2 | 1 | [9 empty] | max min
23904 | User Channel 12 Power Factor Timestamp | MIN_TS_PF_s012 |  |  | uint64 | R | 4 | 1 | [9 empty] | max min
26115 | The Number of the Waveform Record Group | totalWaveformNum |  |  | uint16 | R | 1 | 1
26116 | Data state of waveform record window | waveformDataState |  |  | uint16 | R | 1 | 1
26117 | Latest Waveform Record Groupe Number | lastWaveformNum |  |  | uint16 | R | 1 | 1
26369 | The index of the PQEvent Log | lastPQEventNum |  |  | uint16 | R | 1 | 1
26370 | The Number of the PQEvent Log | totalPQEventNum |  |  | uint16 | R | 1 | 1
61504 | Serial Number1 | Conf_Serial_Number1 |  |  | uint64 | RW | 4 | 1
61508 | Serial Number2 | Conf_Serial_Number2 |  |  | uint64 | RW | 4 | 1
61512 | Serial Number3 | Conf_Serial_Number3 |  |  | uint64 | RW | 4 | 1
61516 | Serial Number4 | Conf_Serial_Number4 |  |  | uint64 | RW | 4 | 1
61520 | Hardware version | Conf_Hardware_version |  |  | uint32 | RW | 2 | 1
61522 | Function Model Type | Conf_Function_Model_Type |  |  | uint16 | RW | 1 | 1
61523 | Reserved11 | Conf_Reserved11 |  |  | uint16 | RW | 1 | 1
61524 | Current Input Type | Info_Current_Input_Type |  |  | uint16 | RW | 1 | 1
61525 | Power Supply Type | Power_Supply_Type |  |  | uint16 | RW | 1 | 1
61526 | MAC address1 | Conf_MAC_address1 |  |  | uint64 | RW | 4 | 1
61530 | MAC address2 | Conf_MAC_address2 |  |  | uint64 | RW | 4 | 1
61534 | MAC address3 | Conf_MAC_address3 |  |  | uint64 | RW | 4 | 1
61538 | MAC address4 | Conf_MAC_address4 |  |  | uint64 | RW | 4 | 1
61542 | Certification Type | Conf_Certification_Type |  |  | uint16 | RW | 1 | 1
61543 | AIAO or DIDO flag | Conf_AIAO_or_DIDO_flag |  |  | uint32 | RW | 2 | 1
61545 | Reserved 21 | Conf_Reserved_21 |  |  | uint64 | RW | 4 | 1
61549 | Reserved 22 | Conf_Reserved_22 |  |  | uint32 | RW | 2 | 1
61551 | Reserved 23 | Conf_Reserved_23 |  |  | uint16 | RW | 1 | 1
61552 | Hardware Patch Number | Conf_Hardware_Patch_Number |  |  | uint16 | RW | 1 | 1
61440 | Firmware version | Conf_Firmware_version |  |  | uint32 | R | 2 | 1
61442 | Firmware release date1 | Conf_Firmware_release_date1 |  |  | uint32 | R | 2 | 1
61444 | Firmware release date2 | Conf_Firmware_release_date2 |  |  | uint16 | R | 1 | 1
61445 | Firmware patch number | Conf_Firmware_patch_number |  |  | uint16 | R | 1 | 1
61456 | bootloader product string | Conf_bootloader_product_string |  |  | uint32 | R | 2 | 1
61458 | bootloader version | Conf_bootloader_version |  |  | uint32 | R | 2 | 1
61460 | bootloader release date1 | Conf_bootloader_release_date1 |  |  | uint32 | R | 2 | 1
61462 | bootloader release date2 | Conf_bootloader_release_date2 |  |  | uint16 | R | 1 | 1
61463 | bootloader patch number | Conf_bootloader_patch_number |  |  | uint16 | R | 1 | 1
4096 | Password | Conf_Password |  |  | uint16 | RW | 1 | 1
4097 | Baud Rate | Conf_Baud |  |  | uint16 | RW | 1 | 1
4098 | Parity | Conf_Parity |  |  | uint16 | RW | 1 | 1
4099 | DHCP enable | Conf_DHCP_Enable |  |  | uint16 | RW | 1 | 1
4100 | IP address | Conf_IP |  |  | uint32 | RW | 2 | 1
4102 | Subnet mask | Conf_Mask |  |  | uint32 | RW | 2 | 1
4104 | Gateway | Conf_Gateway |  |  | uint32 | RW | 2 | 1
4106 | DNS primary server | Conf_DNS_Primary |  |  | uint32 | RW | 2 | 1
4108 | DNS secondary server | Conf_DNS_Second |  |  | uint32 | RW | 2 | 1
4110 | Modbus Slave ID | Conf_Slave_Id |  |  | uint16 | RW | 1 | 1
4111 | RS485 protocol | Conf_RS485_Protocal |  |  | uint16 | RW | 1 | 1
4112 | Modbus TCP Enable | Conf_Modbus_TCP_Enable |  |  | uint16 | RW | 1 | 1
4113 | Modbus TCP port | Conf_Modbus_TCP_Port |  |  | uint16 | RW | 1 | 1
4114 | BACnet MS/TP Meter address | Conf_BACnet_Addr |  |  | uint16 | RW | 1 | 1
4115 | BACnet MS/TP Maximum number of message frames | Conf_BACnet_Max_Frames_Number |  |  | uint16 | RW | 1 | 1
4116 | BACnet MS/TP ID | Conf_BACnet_ID |  |  | uint32 | RW | 2 | 1
4118 | BACnet MS/TP Database Revision | Conf_BACnet_DB_Revision |  |  | uint16 | R | 1 | 1
4119 | LCD Backlight Time | Conf_LCD_Backlight_Time |  |  | uint16 | RW | 1 | 1
4120 | Device run time | Conf_Device_Run_Time |  |  | uint32 | RW | 2 | 1
4122 | Device load time | Conf_Device_Load_Time |  |  | uint32 | RW | 2 | 1
4124 | MaxDemand Clear Mode | Conf_MaxDemand_Clear_Mode |  |  | uint16 | RW | 1 | 1
4125 | MaxDemand Clear Date Setting | Conf_MaxDemand_Clear_Date_Setting |  |  | uint32 | RW | 2 | 1
4127 | MaxDemand Clear Total Count | Conf_MaxDemand_Clear_Total_Count |  |  | uint16 | R | 1 | 1
4128 | Timestamp of the most recent MaxDemand Clear | Conf_MaxDemand_Clear_Latest_TS_001 |  |  | uint16 | R | 1 | 1
4129 | Timestamp of the most recent MaxDemand Clear | Conf_MaxDemand_Clear_Latest_TS_002 |  |  | uint16 | R | 1 | 1
4130 | Timestamp of the most recent MaxDemand Clear | Conf_MaxDemand_Clear_Latest_TS_003 |  |  | uint16 | R | 1 | 1
4131 | Non-standard Seal Parameter Select | Conf_Seal_Parameter_Select |  |  | uint16 | RW | 1 | 1
4132 | Week | Conf_Week |  |  | uint16 | RW | 1 | 1
4133 | Year | Conf_Year |  |  | uint16 | RW | 1 | 1
4134 | Month | Conf_Month |  |  | uint16 | RW | 1 | 1
4135 | Day | Conf_Day |  |  | uint16 | RW | 1 | 1
4136 | Hour | Conf_Hour |  |  | uint16 | RW | 1 | 1
4137 | Minute | Conf_Minute |  |  | uint16 | RW | 1 | 1
4138 | Second | Conf_Second |  |  | uint16 | RW | 1 | 1
4139 | TempPassword | TempPassword |  |  | uint16 | R | 1 | 1
4160 | Sealing Status | Conf_Sealing_Status |  |  | uint16 | R | 1 | 1
4161 | Frequency Selection | Conf_Frequency |  |  | uint16 | RW | 1 | 1
4162 | Service Configuration | Conf_Service |  |  | uint16 | RW | 1 | 1
4163 | PT1 | Conf_PT1 |  |  | uint32 | RW | 2 | 1
4165 | PT2 | Conf_PT2 |  |  | uint16 | RW | 1 | 1
4166 | channel1 input wiring | Conf_Input_Wiring_001 |  |  | uint16 | RW | 1 | 1
4167 | channel1 CT type | Conf_CT_Type_001 |  |  | uint16 | RW | 1 | 1
4168 | channel1 primary | Conf_Primary_001 |  |  | uint16 | RW | 1 | 1
4169 | channel1 direction | Conf_Direction_001 |  |  | uint16 | RW | 1 | 1
4170 | channel1 voltage assignment | Conf_Voltage_Assignment_001 |  |  | uint16 | RW | 1 | 1
4171 | channel2 input wiring | Conf_Input_Wiring_002 |  |  | uint16 | RW | 1 | 1
4172 | channel2 CT type | Conf_CT_Type_002 |  |  | uint16 | RW | 1 | 1
4173 | channel2 primary | Conf_Primary_002 |  |  | uint16 | RW | 1 | 1
4174 | channel2 direction | Conf_Direction_002 |  |  | uint16 | RW | 1 | 1
4175 | channel2 voltage assignment | Conf_Voltage_Assignment_002 |  |  | uint16 | RW | 1 | 1
4176 | channel3 input wiring | Conf_Input_Wiring_003 |  |  | uint16 | RW | 1 | 1
4177 | channel3 CT type | Conf_CT_Type_003 |  |  | uint16 | RW | 1 | 1
4178 | channel3 primary | Conf_Primary_003 |  |  | uint16 | RW | 1 | 1
4179 | channel3 direction | Conf_Direction_003 |  |  | uint16 | RW | 1 | 1
4180 | channel3 voltage assignment | Conf_Voltage_Assignment_003 |  |  | uint16 | RW | 1 | 1
4181 | channel4 input wiring | Conf_Input_Wiring_004 |  |  | uint16 | RW | 1 | 1
4182 | channel4 CT type | Conf_CT_Type_004 |  |  | uint16 | RW | 1 | 1
4183 | channel4 primary | Conf_Primary_004 |  |  | uint16 | RW | 1 | 1
4184 | channel4 direction | Conf_Direction_004 |  |  | uint16 | RW | 1 | 1
4185 | channel4 voltage assignment | Conf_Voltage_Assignment_004 |  |  | uint16 | RW | 1 | 1
4186 | channel5 input wiring | Conf_Input_Wiring_005 |  |  | uint16 | RW | 1 | 1
4187 | channel5 CT type | Conf_CT_Type_005 |  |  | uint16 | RW | 1 | 1
4188 | channel5 primary | Conf_Primary_005 |  |  | uint16 | RW | 1 | 1
4189 | channel5 direction | Conf_Direction_005 |  |  | uint16 | RW | 1 | 1
4190 | channel5 voltage assignment | Conf_Voltage_Assignment_005 |  |  | uint16 | RW | 1 | 1
4191 | channel6 input wiring | Conf_Input_Wiring_006 |  |  | uint16 | RW | 1 | 1
4192 | channel6 CT type | Conf_CT_Type_006 |  |  | uint16 | RW | 1 | 1
4193 | channel6 primary | Conf_Primary_006 |  |  | uint16 | RW | 1 | 1
4194 | channel6 direction | Conf_Direction_006 |  |  | uint16 | RW | 1 | 1
4195 | channel6 voltage assignment | Conf_Voltage_Assignment_006 |  |  | uint16 | RW | 1 | 1
4196 | channel7 input wiring | Conf_Input_Wiring_007 |  |  | uint16 | RW | 1 | 1
4197 | channel7 CT type | Conf_CT_Type_007 |  |  | uint16 | RW | 1 | 1
4198 | channel7 primary | Conf_Primary_007 |  |  | uint16 | RW | 1 | 1
4199 | channel7 direction | Conf_Direction_007 |  |  | uint16 | RW | 1 | 1
4200 | channel7 voltage assignment | Conf_Voltage_Assignment_007 |  |  | uint16 | RW | 1 | 1
4201 | channel8 input wiring | Conf_Input_Wiring_008 |  |  | uint16 | RW | 1 | 1
4202 | channel8 CT type | Conf_CT_Type_008 |  |  | uint16 | RW | 1 | 1
4203 | channel8 primary | Conf_Primary_008 |  |  | uint16 | RW | 1 | 1
4204 | channel8 direction | Conf_Direction_008 |  |  | uint16 | RW | 1 | 1
4205 | channel8 voltage assignment | Conf_Voltage_Assignment_008 |  |  | uint16 | RW | 1 | 1
4206 | channel9 input wiring | Conf_Input_Wiring_009 |  |  | uint16 | RW | 1 | 1
4207 | channel9 CT type | Conf_CT_Type_009 |  |  | uint16 | RW | 1 | 1
4208 | channel9 primary | Conf_Primary_009 |  |  | uint16 | RW | 1 | 1
4209 | channel9 direction | Conf_Direction_009 |  |  | uint16 | RW | 1 | 1
4210 | channel9 voltage assignment | Conf_Voltage_Assignment_009 |  |  | uint16 | RW | 1 | 1
4211 | channel10 input wiring | Conf_Input_Wiring_010 |  |  | uint16 | RW | 1 | 1
4212 | channel10 CT type | Conf_CT_Type_010 |  |  | uint16 | RW | 1 | 1
4213 | channel10 primary | Conf_Primary_010 |  |  | uint16 | RW | 1 | 1
4214 | channel10 direction | Conf_Direction_010 |  |  | uint16 | RW | 1 | 1
4215 | channel10 voltage assignment | Conf_Voltage_Assignment_010 |  |  | uint16 | RW | 1 | 1
4216 | channel11 input wiring | Conf_Input_Wiring_011 |  |  | uint16 | RW | 1 | 1
4217 | channel11 CT type | Conf_CT_Type_011 |  |  | uint16 | RW | 1 | 1
4218 | channel11 primary | Conf_Primary_011 |  |  | uint16 | RW | 1 | 1
4219 | channel11 direction | Conf_Direction_011 |  |  | uint16 | RW | 1 | 1
4220 | channel11 voltage assignment | Conf_Voltage_Assignment_011 |  |  | uint16 | RW | 1 | 1
4221 | channel12 input wiring | Conf_Input_Wiring_012 |  |  | uint16 | RW | 1 | 1
4222 | channel12 CT type | Conf_CT_Type_012 |  |  | uint16 | RW | 1 | 1
4223 | channel12 primary | Conf_Primary_012 |  |  | uint16 | RW | 1 | 1
4224 | channel12 direction | Conf_Direction_012 |  |  | uint16 | RW | 1 | 1
4225 | channel12 voltage assignment | Conf_Voltage_Assignment_012 |  |  | uint16 | RW | 1 | 1
4226 | channel13 input wiring | Conf_Input_Wiring_013 |  |  | uint16 | RW | 1 | 1
4227 | channel13 CT type | Conf_CT_Type_013 |  |  | uint16 | RW | 1 | 1
4228 | channel13 primary | Conf_Primary_013 |  |  | uint16 | RW | 1 | 1
4229 | channel13 direction | Conf_Direction_013 |  |  | uint16 | RW | 1 | 1
4230 | channel13 voltage assignment | Conf_Voltage_Assignment_013 |  |  | uint16 | RW | 1 | 1
4231 | channel14 input wiring | Conf_Input_Wiring_014 |  |  | uint16 | RW | 1 | 1
4232 | channel14 CT type | Conf_CT_Type_014 |  |  | uint16 | RW | 1 | 1
4233 | channel14 primary | Conf_Primary_014 |  |  | uint16 | RW | 1 | 1
4234 | channel14 direction | Conf_Direction_014 |  |  | uint16 | RW | 1 | 1
4235 | channel14 voltage assignment | Conf_Voltage_Assignment_014 |  |  | uint16 | RW | 1 | 1
4236 | channel15 input wiring | Conf_Input_Wiring_015 |  |  | uint16 | RW | 1 | 1
4237 | channel15 CT type | Conf_CT_Type_015 |  |  | uint16 | RW | 1 | 1
4238 | channel15 primary | Conf_Primary_015 |  |  | uint16 | RW | 1 | 1
4239 | channel15 direction | Conf_Direction_015 |  |  | uint16 | RW | 1 | 1
4240 | channel15 voltage assignment | Conf_Voltage_Assignment_015 |  |  | uint16 | RW | 1 | 1
4241 | channel16 input wiring | Conf_Input_Wiring_016 |  |  | uint16 | RW | 1 | 1
4242 | channel16 CT type | Conf_CT_Type_016 |  |  | uint16 | RW | 1 | 1
4243 | channel16 primary | Conf_Primary_016 |  |  | uint16 | RW | 1 | 1
4244 | channel16 direction | Conf_Direction_016 |  |  | uint16 | RW | 1 | 1
4245 | channel16 voltage assignment | Conf_Voltage_Assignment_016 |  |  | uint16 | RW | 1 | 1
4246 | channel17 input wiring | Conf_Input_Wiring_017 |  |  | uint16 | RW | 1 | 1
4247 | channel17 CT type | Conf_CT_Type_017 |  |  | uint16 | RW | 1 | 1
4248 | channel17 primary | Conf_Primary_017 |  |  | uint16 | RW | 1 | 1
4249 | channel17 direction | Conf_Direction_017 |  |  | uint16 | RW | 1 | 1
4250 | channel17 voltage assignment | Conf_Voltage_Assignment_017 |  |  | uint16 | RW | 1 | 1
4251 | channel18 input wiring | Conf_Input_Wiring_018 |  |  | uint16 | RW | 1 | 1
4252 | channel18 CT type | Conf_CT_Type_018 |  |  | uint16 | RW | 1 | 1
4253 | channel18 primary | Conf_Primary_018 |  |  | uint16 | RW | 1 | 1
4254 | channel18 direction | Conf_Direction_018 |  |  | uint16 | RW | 1 | 1
4255 | channel18 voltage assignment | Conf_Voltage_Assignment_018 |  |  | uint16 | RW | 1 | 1
4256 | channel19 input wiring | Conf_Input_Wiring_019 |  |  | uint16 | RW | 1 | 1
4257 | channel19 CT type | Conf_CT_Type_019 |  |  | uint16 | RW | 1 | 1
4258 | channel19 primary | Conf_Primary_019 |  |  | uint16 | RW | 1 | 1
4259 | channel19 direction | Conf_Direction_019 |  |  | uint16 | RW | 1 | 1
4260 | channel19 voltage assignment | Conf_Voltage_Assignment_019 |  |  | uint16 | RW | 1 | 1
4261 | channel20 input wiring | Conf_Input_Wiring_020 |  |  | uint16 | RW | 1 | 1
4262 | channel20 CT type | Conf_CT_Type_020 |  |  | uint16 | RW | 1 | 1
4263 | channel20 primary | Conf_Primary_020 |  |  | uint16 | RW | 1 | 1
4264 | channel20 direction | Conf_Direction_020 |  |  | uint16 | RW | 1 | 1
4265 | channel20 voltage assignment | Conf_Voltage_Assignment_020 |  |  | uint16 | RW | 1 | 1
4266 | channel21 input wiring | Conf_Input_Wiring_021 |  |  | uint16 | RW | 1 | 1
4267 | channel21 CT type | Conf_CT_Type_021 |  |  | uint16 | RW | 1 | 1
4268 | channel21 primary | Conf_Primary_021 |  |  | uint16 | RW | 1 | 1
4269 | channel21 direction | Conf_Direction_021 |  |  | uint16 | RW | 1 | 1
4270 | channel21 voltage assignment | Conf_Voltage_Assignment_021 |  |  | uint16 | RW | 1 | 1
4271 | channel22 input wiring | Conf_Input_Wiring_022 |  |  | uint16 | RW | 1 | 1
4272 | channel22 CT type | Conf_CT_Type_022 |  |  | uint16 | RW | 1 | 1
4273 | channel22 primary | Conf_Primary_022 |  |  | uint16 | RW | 1 | 1
4274 | channel22 direction | Conf_Direction_022 |  |  | uint16 | RW | 1 | 1
4275 | channel22 voltage assignment | Conf_Voltage_Assignment_022 |  |  | uint16 | RW | 1 | 1
4276 | channel23 input wiring | Conf_Input_Wiring_023 |  |  | uint16 | RW | 1 | 1
4277 | channel23 CT type | Conf_CT_Type_023 |  |  | uint16 | RW | 1 | 1
4278 | channel23 primary | Conf_Primary_023 |  |  | uint16 | RW | 1 | 1
4279 | channel23 direction | Conf_Direction_023 |  |  | uint16 | RW | 1 | 1
4280 | channel23 voltage assignment | Conf_Voltage_Assignment_023 |  |  | uint16 | RW | 1 | 1
4281 | channel24 input wiring | Conf_Input_Wiring_024 |  |  | uint16 | RW | 1 | 1
4282 | channel24 CT type | Conf_CT_Type_024 |  |  | uint16 | RW | 1 | 1
4283 | channel24 primary | Conf_Primary_024 |  |  | uint16 | RW | 1 | 1
4284 | channel24 direction | Conf_Direction_024 |  |  | uint16 | RW | 1 | 1
4285 | channel24 voltage assignment | Conf_Voltage_Assignment_024 |  |  | uint16 | RW | 1 | 1
4286 | user 1 input channel assignment | Conf_Input_Channel_Assignment_s001 |  |  | uint32 | RW | 2 | 1
4288 | user 2 input channel assignment | Conf_Input_Channel_Assignment_s002 |  |  | uint32 | RW | 2 | 1
4290 | user 3 input channel assignment | Conf_Input_Channel_Assignment_s003 |  |  | uint32 | RW | 2 | 1
4292 | user 4 input channel assignment | Conf_Input_Channel_Assignment_s004 |  |  | uint32 | RW | 2 | 1
4294 | user 5 input channel assignment | Conf_Input_Channel_Assignment_s005 |  |  | uint32 | RW | 2 | 1
4296 | user 6 input channel assignment | Conf_Input_Channel_Assignment_s006 |  |  | uint32 | RW | 2 | 1
4298 | user 7 input channel assignment | Conf_Input_Channel_Assignment_s007 |  |  | uint32 | RW | 2 | 1
4300 | user 8 input channel assignment | Conf_Input_Channel_Assignment_s008 |  |  | uint32 | RW | 2 | 1
4302 | user 9 input channel assignment | Conf_Input_Channel_Assignment_s009 |  |  | uint32 | RW | 2 | 1
4304 | user 10 input channel assignment | Conf_Input_Channel_Assignment_s010 |  |  | uint32 | RW | 2 | 1
4306 | user 11 input channel assignment | Conf_Input_Channel_Assignment_s011 |  |  | uint32 | RW | 2 | 1
4308 | user 12 input channel assignment | Conf_Input_Channel_Assignment_s012 |  |  | uint32 | RW | 2 | 1
4310 | Demand Method | Conf_Demand_Method |  |  | uint16 | RW | 1 | 1
4311 | Demand Interval | Conf_Demand_Interval |  |  | uint16 | RW | 1 | 1
4312 | Demand update rate | Conf_Demand_Update_Rate |  |  | uint16 | RW | 1 | 1
4313 | VAR/PF Convention | Conf_VAR_PF_Convention |  |  | uint16 | RW | 1 | 1
4314 | Energy Calculation Method | Conf_Energy_Calculation_Method |  |  | uint16 | RW | 1 | 1
4315 | Reactive Power Calculation Method | Conf_Reactive_Power_Calculation_Method |  |  | uint16 | RW | 1 | 1
4316 | Phase Order | Conf_Phase_Order |  |  | uint16 | RW | 1 | 1
4317 | Energy Reading Display format | Conf_Energy_Reading_Display_Format |  |  | uint16 | RW | 1 | 1
4318 | Reserve3 | Conf_Reserve3 |  |  | uint16 | RW | 1 | 1
4319 | Energy pulse constant | Conf_Energy_Pulse_Constant |  |  | uint32 | RW | 2 | 0.001
4321 | Pulse LED width | Conf_Pulse_LED_Width |  |  | uint16 | RW | 1 | 1
4322 | Pulse LED parameter selection | Conf_Pulse_LED_Parameter_Selection |  |  | uint16 | RW | 1 | 1
4352 | DO1 Type | Conf_DO_Type_001 |  |  | uint16 | RW | 1 | 1
4353 | DO1 Pulse width | Conf_DO_Pulse_Width_001 |  |  | uint16 | RW | 1 | 1
4354 | DO1 parameter selection | Conf_DO_Parameter_Selection_001 |  |  | uint16 | RW | 1 | 1
4355 | DO2 Type | Conf_DO_Type_002 |  |  | uint16 | RW | 1 | 1
4356 | DO2 Pulse width | Conf_DO_Pulse_Width_002 |  |  | uint16 | RW | 1 | 1
4357 | DO2 parameter selection | Conf_DO_Parameter_Selection_002 |  |  | uint16 | RW | 1 | 1
4358 | DO3 Type | Conf_DO_Type_003 |  |  | uint16 | RW | 1 | 1
4359 | DO3 Pulse width | Conf_DO_Pulse_Width_003 |  |  | uint16 | RW | 1 | 1
4360 | DO3 parameter selection | Conf_DO_Parameter_Selection_003 |  |  | uint16 | RW | 1 | 1
4361 | DO4 Type | Conf_DO_Type_004 |  |  | uint16 | RW | 1 | 1
4362 | DO4 Pulse width | Conf_DO_Pulse_Width_004 |  |  | uint16 | RW | 1 | 1
4363 | DO4 parameter selection | Conf_DO_Parameter_Selection_004 |  |  | uint16 | RW | 1 | 1
4364 | DO5 Type | Conf_DO_Type_005 |  |  | uint16 | RW | 1 | 1
4365 | DO5 Pulse width | Conf_DO_Pulse_Width_005 |  |  | uint16 | RW | 1 | 1
4366 | DO5 parameter selection | Conf_DO_Parameter_Selection_005 |  |  | uint16 | RW | 1 | 1
4367 | DO6 Type | Conf_DO_Type_006 |  |  | uint16 | RW | 1 | 1
4368 | DO6 Pulse width | Conf_DO_Pulse_Width_006 |  |  | uint16 | RW | 1 | 1
4369 | DO6 parameter selection | Conf_DO_Parameter_Selection_006 |  |  | uint16 | RW | 1 | 1
4370 | DO7 Type | Conf_DO_Type_007 |  |  | uint16 | RW | 1 | 1
4371 | DO7 Pulse width | Conf_DO_Pulse_Width_007 |  |  | uint16 | RW | 1 | 1
4372 | DO7 parameter selection | Conf_DO_Parameter_Selection_007 |  |  | uint16 | RW | 1 | 1
4373 | DO8 Type | Conf_DO_Type_008 |  |  | uint16 | RW | 1 | 1
4374 | DO8 Pulse width | Conf_DO_Pulse_Width_008 |  |  | uint16 | RW | 1 | 1
4375 | DO8parameter selection | Conf_DO_Parameter_Selection_008 |  |  | uint16 | RW | 1 | 1
4376 | DI1 Type | Conf_DI_Type_001 |  |  | uint16 | RW | 1 | 1
4377 | DI1 pulse constant | Conf_DI_Pulse_Constant_001 |  |  | uint32 | RW | 2 | 0.001
4379 | DI2 Type | Conf_DI_Type_002 |  |  | uint16 | RW | 1 | 1
4380 | DI2 pulse constant | Conf_DI_Pulse_Constant_002 |  |  | uint32 | RW | 2 | 0.001
4382 | DI3 Type | Conf_DI_Type_003 |  |  | uint16 | RW | 1 | 1
4383 | DI3 pulse constant | Conf_DI_Pulse_Constant_003 |  |  | uint32 | RW | 2 | 0.001
4385 | DI4 Type | Conf_DI_Type_004 |  |  | uint16 | RW | 1 | 1
4386 | DI4 pulse constant | Conf_DI_Pulse_Constant_004 |  |  | uint32 | RW | 2 | 0.001
4388 | RO1 Type | Conf_RO_Type_001 |  |  | uint16 | RW | 1 | 1
4389 | RO1 Control Mode | Conf_RO_Control_Mode_001 |  |  | uint16 | RW | 1 | 1
4390 | RO1 Pulse Width | Conf_RO_Pulse_Width_001 |  |  | uint16 | RW | 1 | 1
4391 | RO2 Type | Conf_RO_Type_002 |  |  | uint16 | RW | 1 | 1
4392 | RO2 Control Mode | Conf_RO_Control_Mode_002 |  |  | uint16 | RW | 1 | 1
4393 | RO2 Pulse Width | Conf_RO_Pulse_Width_002 |  |  | uint16 | RW | 1 | 1
4400 | Clear energy | Conf_Clear_Energy |  |  | uint16 | W | 1 | 1
4401 | Clear Max demand | Conf_Clear_Max_Demand |  |  | uint16 | W | 1 | 1
4402 | Clear MaxDemand ClearCount and Timestamp | Conf_Clear_MaxDemand_ClearCount_Timestamp |  |  | uint16 | W | 1 | 1
4403 | Clear max/min | Conf_Clear_Max_Min |  |  | uint16 | W | 1 | 1
4404 | Clear device run time | Conf_Clear_Device_Run_Time |  |  | uint16 | W | 1 | 1
4405 | Clear load time | Conf_Clear_Load_Time |  |  | uint16 | W | 1 | 1
4406 | Factory reset | Conf_Reset_Factory |  |  | uint16 | W | 1 | 1
4407 | Network reset | Conf_Reset_Network |  |  | uint16 | W | 1 | 1
4408 | Clear SOE Log | Conf_Clear_SOE_Log |  |  | uint16 | W | 1 | 1
4409 | Clear alarm Log | Conf_Clear_Alarm_Log |  |  | uint16 | W | 1 | 1
4410 | Clear PQ event Log | Conf_Clear_PQEvent_Log |  |  | uint16 | W | 1 | 1
4411 | Clear Waveform | Conf_Clear_Waveform |  |  | uint16 | W | 1 | 1
4412 | Clear Data Log1 | Conf_Clear_Data_Log1 |  |  | uint16 | W | 1 | 1
4413 | Clear Data Log2 | Conf_Clear_Data_Log2 |  |  | uint16 | W | 1 | 1
4414 | Clear Data Log3 | Conf_Clear_Data_Log3 |  |  | uint16 | W | 1 | 1
4415 | Clear Trend Log | Conf_Clear_Trend_Log |  |  | uint16 | W | 1 | 1
4416 | Clear DI Count | Conf_Clear_DI_Count |  |  | uint16 | W | 1 | 1
4417 | Clear Year 10 Holiday Number Setting | Conf_Clear_Year10_Holiday_Number_Setting |  |  | uint16 | W | 1 | 1
4418 | Restore TOU factory setting | Conf_Restore_TOU_Factory_Setting |  |  | uint16 | W | 1 | 1
4419 | Clear TOU Energy | Conf_TOU_Energy |  |  | uint16 | W | 1 | 1
4420 | Device Reboot | Conf_Device_Reboot |  |  | uint16 | W | 1 | 1
25344 | The index of the SOE Log | SOE_Index |  |  | uint16 | R | 1 | 1
25345 | Number of the SOE Log | SOE_Number |  |  | uint16 | R | 1 | 1
256 | Web2 Meter Setting Status | Web2_Meter_Setting_Status |  |  | uint32 | RW | 2 | 1
258 | Web2 DHCP enable | Web2_DHCP_Enable |  |  | uint16 | RW | 1 | 1
259 | Web2 Eth1 IP address | Web2_Eth1_IP |  |  | uint32 | RW | 2 | 1
261 | Web2 Eth1 Subnet mask | Web2_Eth1_Mask |  |  | uint32 | RW | 2 | 1
263 | Web2 Eth1 Gateway | Web2_Eth1_Gateway |  |  | uint32 | RW | 2 | 1
265 | Web2 Eth1 DNS primary server | Web2_Eth1_DNS_Primary |  |  | uint32 | RW | 2 | 1
267 | Web2 DNS secondary server | Web2_Eth1_DNS_Second |  |  | uint32 | RW | 2 | 1
269 | Web2 Eth2 IP address | Web2_Eth2_IP |  |  | uint32 | RW | 2 | 1
271 | Web2 WIFI IP address | Web2_WIFI_IP |  |  | uint32 | RW | 2 | 1
273 | Web2 Device Reboot | Web2_Device_Reboot |  |  | uint16 | RW | 1 | 1
274 | Web2 Factory reset | Web2_Reset_Factory |  |  | uint16 | RW | 1 | 1
275 | Web2 Network reset | Web2_Reset_Network |  |  | uint16 | RW | 1 | 1
276 | Web2 Enable clock synchronization | Web2_Enable_Clock_Sync |  |  | uint16 | RW | 1 | 1
277 | Web2 Mode Setting | Web2_Mode_Setting |  |  | uint16 | RW | 1 | 1
278 | Web2 Firmware version1 | Web2_Firmware_version1 |  |  | uint64 | RW | 4 | 1
280 | Web2 Firmware version2 | Web2_Firmware_version2 |  |  | uint64 | RW | 4 | 1
286 | Web2 Serial Number1 | Web2_Serial_Number1 |  |  | uint64 | RW | 4 | 1
290 | Web2 Serial Number2 | Web2_Serial_Number2 |  |  | uint64 | RW | 4 | 1
294 | Web2 Serial Number3 | Web2_Serial_Number3 |  |  | uint64 | RW | 4 | 1
298 | Web2 Serial Number4 | Web2_Serial_Number4 |  |  | uint64 | RW | 4 | 1
302 | Web2 ETH1 MAC address1 | Web2_ETH1_MAC_address1 |  |  | uint64 | RW | 4 | 1
306 | Web2 ETH1 MAC address2 | Web2_ETH1_MAC_address2 |  |  | uint64 | RW | 4 | 1
310 | Web2 ETH1 MAC address3 | Web2_ETH1_MAC_address3 |  |  | uint64 | RW | 4 | 1
314 | Web2 ETH1 MAC address4 | Web2_ETH1_MAC_address4 |  |  | uint64 | RW | 4 | 1
318 | Web2 ETH2 MAC address1 | Web2_ETH2_MAC_address1 |  |  | uint64 | RW | 4 | 1
322 | Web2 ETH2 MAC address2 | Web2_ETH2_MAC_address2 |  |  | uint64 | RW | 4 | 1
326 | Web2 ETH2 MAC address3 | Web2_ETH2_MAC_address3 |  |  | uint64 | RW | 4 | 1
330 | Web2 ETH2 MAC address4 | Web2_ETH2_MAC_address4 |  |  | uint64 | RW | 4 | 1
334 | Web2 WIFI MAC address1 | Web2_WIFI_MAC_address1 |  |  | uint64 | RW | 4 | 1
338 | Web2 WIFI MAC address2 | Web2_WIFI_MAC_address2 |  |  | uint64 | RW | 4 | 1
342 | Web2 WIFI MAC address3 | Web2_WIFI_MAC_address3 |  |  | uint64 | RW | 4 | 1
346 | Web2 WIFI MAC address4 | Web2_WIFI_MAC_address4 |  |  | uint64 | RW | 4 | 1
4608 | User Channel 1 Description | Conf_DESC_s001 |  |  | string | RW | 10
4618 | User Channel 2 Description | Conf_DESC_s002 |  |  | string | RW | 10
4628 | User Channel 3 Description | Conf_DESC_s003 |  |  | string | RW | 10
4638 | User Channel 4 Description | Conf_DESC_s004 |  |  | string | RW | 10
4648 | User Channel 5 Description | Conf_DESC_s005 |  |  | string | RW | 10
4658 | User Channel 6 Description | Conf_DESC_s006 |  |  | string | RW | 10
4668 | User Channel 7 Description | Conf_DESC_s007 |  |  | string | RW | 10
4678 | User Channel 8 Description | Conf_DESC_s008 |  |  | string | RW | 10
4688 | User Channel 9 Description | Conf_DESC_s009 |  |  | string | RW | 10
4698 | User Channel 10 Description | Conf_DESC_s010 |  |  | string | RW | 10
4708 | User Channel 11 Description | Conf_DESC_s011 |  |  | string | RW | 10
4718 | User Channel 12 Description | Conf_DESC_s012 |  |  | string | RW | 10
25882 | Nominal Voltage Hing Byte | Conf_NominalVolt_H |  |  | uint16 | R/W | 1 | 1