## blockParams
Start(Dec) | descrption | paramType | unit | check | dataType | RW | Reg | scale | readings | Alarm | Data log default parameter | Trend Log | DataLog | AcuCloud | MQTT | SNMP | BACnetIP | North
0 | IsOnline | IsOnline |  |  | isOnline | R | 1 | 1 | 14-15
16384 | System Frequency | FREQ_Hz | Hz |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16386 | Phase A Line-to-Neutral Voltage | VLN_a_V | V |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16388 | Phase B Line-to-Neutral Voltage | VLN_b_V | V |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16390 | Phase C Line-to-Neutral Voltage | VLN_c_V | V |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16392 | Average Line-to-Neutral Voltage | VLN_avg_V | V |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16394 | Phase A-B Line-to-Line Voltage | VLL_ab_V | V |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16396 | Phase B-C Line-to-Line Voltage | VLL_bc_V | V |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16398 | Phase C-A Line-to-Line Voltage | VLL_ca_V | V |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16400 | Average Line-to-Line Voltage | VLL_avg_V | V |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16402 | Phase A Line Current | I_a_A | A |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16404 | Phase B Line Current | I_b_A | A |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16406 | Phase C Line Current | I_c_A | A |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16408 | Average Line Current | I_avg_A | A |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16410 | Neutral Current | I_n_A | A |  | float32 | R | 2 | 1 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16412 | Phase A Active Power | P_a_kW | kW |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16414 | Phase B Active Power | P_b_kW | kW |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16416 | Phase C Active Power | P_c_kW | kW |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16418 | System Active Power | P_kW | kW |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16420 | Phase A Reactive Power | Q_a_kvar | kvar |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16422 | Phase B Reactive Power | Q_b_kvar | kvar |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16424 | Phase C Reactive Power | Q_c_kvar | kvar |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16426 | System Reactive Power | Q_kvar | kvar |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16428 | Phase A Apparent Power | S_a_kVA | kVA |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16430 | Phase B Apparent Power | S_b_kVA | kVA |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16432 | Phase C Apparent Power | S_c_kVA | kVA |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16434 | System Apparent Power | S_kVA | kVA |  | float32 | R | 2 | 0.001 | 14-15 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16436 | Phase A Power Factor | PF_a |  | 删除单位 | float32 | R | 2 | 1 | 14-15 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16438 | Phase B Power Factor | PF_b |  | 删除单位 | float32 | R | 2 | 1 | 14-15 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16440 | Phase C Power Factor | PF_c |  | 删除单位 | float32 | R | 2 | 1 | 14-15 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16442 | System Power Factor | PF |  | 删除单位 | float32 | R | 2 | 1 | 14-15 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16444 | Voltage Unbalance Factor | UNBL_V_% | % |  | float32 | R | 2 | 100 | 14-15 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16446 | Current Unbalance Factor | UNBL_I_% | % |  | float32 | R | 2 | 100 | 14-15 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
16448 | Average Load Nature | LC_avg |  | 删除单位 | float32 | R | 2 | 1
16450 | System Active Power Demand | DMD_P_kW | kW |  | float32 | R | 2 | 0.001 | 14-15 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
16452 | System Reactive Power Demand | DMD_Q_kvar | kvar |  | float32 | R | 2 | 0.001 | 14-15 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
16454 | System Apparent Power Demand | DMD_S_kVA | kVA |  | float32 | R | 2 | 0.001 | 14-15 | demand |  | demand | demand | demand | demand | demand | demand | demand | demand
16456 | System Import Active Energy | EP_IMP_kWh | kWh |  | uint32 | R/W | 2 | 0.1 | 14 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
16458 | System Export Active Energy | EP_EXP_kWh | kWh |  | uint32 | R/W | 2 | 0.1 | 14 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
16460 | System Import Reactive Energy | EQ_IMP_kvarh | kvarh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
16462 | System Export Reactive Energy | EQ_EXP_kvarh | kvarh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
16464 | System Total Active Energy | EP_TOTAL_kWh | kWh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
16466 | System Net Active Energy | EP_NET_kWh | kWh |  | int32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
16468 | System Total Reactive Energy | EQ_TOTAL_kvarh | kvarh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
16470 | System Net Reactive Energy | EQ_NET_kvarh | kvarh |  | int32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
16472 | System Apparent Energy | ES_kVAh | kVAh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
16474 | Phase A Voltage THD | THD_V_a_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16475 | Phase B Voltage THD | THD_V_b_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16476 | Phase C Voltage THD | THD_V_c_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16477 | Average Voltage THD | THD_V_avg_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16478 | Phase A Current THD | THD_I_a_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16479 | Phase B Current THD | THD_I_b_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16480 | Phase C Current THD | THD_I_c_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16481 | Average Current THD | THD_I_avg_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16482 | Phase A Voltage 2-th Harmonic | HAR2_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16483 | Phase A Voltage 3-th Harmonic | HAR3_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16484 | Phase A Voltage 4-th Harmonic | HAR4_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16485 | Phase A Voltage 5-th Harmonic | HAR5_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16486 | Phase A Voltage 6-th Harmonic | HAR6_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16487 | Phase A Voltage 7-th Harmonic | HAR7_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16488 | Phase A Voltage 8-th Harmonic | HAR8_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16489 | Phase A Voltage 9-th Harmonic | HAR9_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16490 | Phase A Voltage 10-th Harmonic | HAR10_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16491 | Phase A Voltage 11-th Harmonic | HAR11_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16492 | Phase A Voltage 12-th Harmonic | HAR12_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16493 | Phase A Voltage 13-th Harmonic | HAR13_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16494 | Phase A Voltage 14-th Harmonic | HAR14_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16495 | Phase A Voltage 15-th Harmonic | HAR15_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16496 | Phase A Voltage 16-th Harmonic | HAR16_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16497 | Phase A Voltage 17-th Harmonic | HAR17_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16498 | Phase A Voltage 18-th Harmonic | HAR18_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16499 | Phase A Voltage 19-th Harmonic | HAR19_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16500 | Phase A Voltage 20-th Harmonic | HAR20_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16501 | Phase A Voltage 21-th Harmonic | HAR21_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16502 | Phase A Voltage 22-th Harmonic | HAR22_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16503 | Phase A Voltage 23-th Harmonic | HAR23_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16504 | Phase A Voltage 24-th Harmonic | HAR24_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16505 | Phase A Voltage 25-th Harmonic | HAR25_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16506 | Phase A Voltage 26-th Harmonic | HAR26_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16507 | Phase A Voltage 27-th Harmonic | HAR27_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16508 | Phase A Voltage 28-th Harmonic | HAR28_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16509 | Phase A Voltage 29-th Harmonic | HAR29_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16510 | Phase A Voltage 30-th Harmonic | HAR30_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16511 | Phase A Voltage 31-th Harmonic | HAR31_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16512 | Phase A Voltage Odd THD | OTHD_V_a_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16513 | Phase A Voltage Even THD | ETHD_V_a_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16514 | Phase A Voltage Crest Factor | CF_V_a_% | % |  | int16 | R | 1 | 0.001 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16515 | Phase A Voltage Telephone Harmonic Form Factor | THFF_V_a_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16516 | Phase B Voltage 2-th Harmonic | HAR2_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16517 | Phase B Voltage 3-th Harmonic | HAR3_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16518 | Phase B Voltage 4-th Harmonic | HAR4_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16519 | Phase B Voltage 5-th Harmonic | HAR5_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16520 | Phase B Voltage 6-th Harmonic | HAR6_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16521 | Phase B Voltage 7-th Harmonic | HAR7_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16522 | Phase B Voltage 8-th Harmonic | HAR8_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16523 | Phase B Voltage 9-th Harmonic | HAR9_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16524 | Phase B Voltage 10-th Harmonic | HAR10_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16525 | Phase B Voltage 11-th Harmonic | HAR11_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16526 | Phase B Voltage 12-th Harmonic | HAR12_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16527 | Phase B Voltage 13-th Harmonic | HAR13_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16528 | Phase B Voltage 14-th Harmonic | HAR14_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16529 | Phase B Voltage 15-th Harmonic | HAR15_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16530 | Phase B Voltage 16-th Harmonic | HAR16_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16531 | Phase B Voltage 17-th Harmonic | HAR17_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16532 | Phase B Voltage 18-th Harmonic | HAR18_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16533 | Phase B Voltage 19-th Harmonic | HAR19_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16534 | Phase B Voltage 20-th Harmonic | HAR20_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16535 | Phase B Voltage 21-th Harmonic | HAR21_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16536 | Phase B Voltage 22-th Harmonic | HAR22_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16537 | Phase B Voltage 23-th Harmonic | HAR23_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16538 | Phase B Voltage 24-th Harmonic | HAR24_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16539 | Phase B Voltage 25-th Harmonic | HAR25_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16540 | Phase B Voltage 26-th Harmonic | HAR26_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16541 | Phase B Voltage 27-th Harmonic | HAR27_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16542 | Phase B Voltage 28-th Harmonic | HAR28_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16543 | Phase B Voltage 29-th Harmonic | HAR29_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16544 | Phase B Voltage 30-th Harmonic | HAR30_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16545 | Phase B Voltage 31-th Harmonic | HAR31_V_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16546 | Phase B Voltage Odd THD | OTHD_V_b_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16547 | Phase B Voltage Even THD | ETHD_V_b_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16548 | Phase B Voltage Crest Factor | CF_V_b_% | % |  | int16 | R | 1 | 0.001 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16549 | Phase B Voltage Telephone Harmonic Form Factor | THFF_V_b_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16550 | Phase C Voltage 2-th Harmonic | HAR2_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16551 | Phase C Voltage 3-th Harmonic | HAR3_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16552 | Phase C Voltage 4-th Harmonic | HAR4_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16553 | Phase C Voltage 5-th Harmonic | HAR5_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16554 | Phase C Voltage 6-th Harmonic | HAR6_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16555 | Phase C Voltage 7-th Harmonic | HAR7_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16556 | Phase C Voltage 8-th Harmonic | HAR8_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16557 | Phase C Voltage 9-th Harmonic | HAR9_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16558 | Phase C Voltage 10-th Harmonic | HAR10_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16559 | Phase C Voltage 11-th Harmonic | HAR11_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16560 | Phase C Voltage 12-th Harmonic | HAR12_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16561 | Phase C Voltage 13-th Harmonic | HAR13_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16562 | Phase C Voltage 14-th Harmonic | HAR14_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16563 | Phase C Voltage 15-th Harmonic | HAR15_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16564 | Phase C Voltage 16-th Harmonic | HAR16_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16565 | Phase C Voltage 17-th Harmonic | HAR17_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16566 | Phase C Voltage 18-th Harmonic | HAR18_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16567 | Phase C Voltage 19-th Harmonic | HAR19_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16568 | Phase C Voltage 20-th Harmonic | HAR20_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16569 | Phase C Voltage 21-th Harmonic | HAR21_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16570 | Phase C Voltage 22-th Harmonic | HAR22_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16571 | Phase C Voltage 23-th Harmonic | HAR23_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16572 | Phase C Voltage 24-th Harmonic | HAR24_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16573 | Phase C Voltage 25-th Harmonic | HAR25_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16574 | Phase C Voltage 26-th Harmonic | HAR26_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16575 | Phase C Voltage 27-th Harmonic | HAR27_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16576 | Phase C Voltage 28-th Harmonic | HAR28_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16577 | Phase C Voltage 29-th Harmonic | HAR29_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16578 | Phase C Voltage 30-th Harmonic | HAR30_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16579 | Phase C Voltage 31-th Harmonic | HAR31_V_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16580 | Phase C Voltage Odd THD | OTHD_V_c_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16581 | Phase C Voltage Even THD | ETHD_V_c_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16582 | Phase C Voltage Crest Factor | CF_V_c_% | % |  | int16 | R | 1 | 0.001 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16583 | Phase C Voltage Telephone Harmonic Form Factor | THFF_V_c_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16584 | Phase A Current 2-th Harmonic | HAR2_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16585 | Phase A Current 3-th Harmonic | HAR3_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16586 | Phase A Current 4-th Harmonic | HAR4_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16587 | Phase A Current 5-th Harmonic | HAR5_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16588 | Phase A Current 6-th Harmonic | HAR6_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16589 | Phase A Current 7-th Harmonic | HAR7_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16590 | Phase A Current 8-th Harmonic | HAR8_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16591 | Phase A Current 9-th Harmonic | HAR9_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16592 | Phase A Current 10-th Harmonic | HAR10_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16593 | Phase A Current 11-th Harmonic | HAR11_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16594 | Phase A Current 12-th Harmonic | HAR12_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16595 | Phase A Current 13-th Harmonic | HAR13_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16596 | Phase A Current 14-th Harmonic | HAR14_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16597 | Phase A Current 15-th Harmonic | HAR15_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16598 | Phase A Current 16-th Harmonic | HAR16_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16599 | Phase A Current 17-th Harmonic | HAR17_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16600 | Phase A Current 18-th Harmonic | HAR18_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16601 | Phase A Current 19-th Harmonic | HAR19_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16602 | Phase A Current 20-th Harmonic | HAR20_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16603 | Phase A Current 21-th Harmonic | HAR21_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16604 | Phase A Current 22-th Harmonic | HAR22_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16605 | Phase A Current 23-th Harmonic | HAR23_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16606 | Phase A Current 24-th Harmonic | HAR24_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16607 | Phase A Current 25-th Harmonic | HAR25_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16608 | Phase A Current 26-th Harmonic | HAR26_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16609 | Phase A Current 27-th Harmonic | HAR27_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16610 | Phase A Current 28-th Harmonic | HAR28_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16611 | Phase A Current 29-th Harmonic | HAR29_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16612 | Phase A Current 30-th Harmonic | HAR30_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16613 | Phase A Current 31-th Harmonic | HAR31_I_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16614 | Phase A Current Odd THD | OTHD_I_a_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16615 | Phase A Current Even THD | ETHD_I_a_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16616 | Phase A Current K Factor | KF_I_a_% | % |  | int16 | R | 1 | 0.1 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16617 | Phase B Current 2-th Harmonic | HAR2_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16618 | Phase B Current 3-th Harmonic | HAR3_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16619 | Phase B Current 4-th Harmonic | HAR4_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16620 | Phase B Current 5-th Harmonic | HAR5_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16621 | Phase B Current 6-th Harmonic | HAR6_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16622 | Phase B Current 7-th Harmonic | HAR7_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16623 | Phase B Current 8-th Harmonic | HAR8_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16624 | Phase B Current 9-th Harmonic | HAR9_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16625 | Phase B Current 10-th Harmonic | HAR10_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16626 | Phase B Current 11-th Harmonic | HAR11_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16627 | Phase B Current 12-th Harmonic | HAR12_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16628 | Phase B Current 13-th Harmonic | HAR13_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16629 | Phase B Current 14-th Harmonic | HAR14_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16630 | Phase B Current 15-th Harmonic | HAR15_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16631 | Phase B Current 16-th Harmonic | HAR16_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16632 | Phase B Current 17-th Harmonic | HAR17_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16633 | Phase B Current 18-th Harmonic | HAR18_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16634 | Phase B Current 19-th Harmonic | HAR19_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16635 | Phase B Current 20-th Harmonic | HAR20_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16636 | Phase B Current 21-th Harmonic | HAR21_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16637 | Phase B Current 22-th Harmonic | HAR22_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16638 | Phase B Current 23-th Harmonic | HAR23_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16639 | Phase B Current 24-th Harmonic | HAR24_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16640 | Phase B Current 25-th Harmonic | HAR25_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16641 | Phase B Current 26-th Harmonic | HAR26_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16642 | Phase B Current 27-th Harmonic | HAR27_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16643 | Phase B Current 28-th Harmonic | HAR28_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16644 | Phase B Current 29-th Harmonic | HAR29_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16645 | Phase B Current 30-th Harmonic | HAR30_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16646 | Phase B Current 31-th Harmonic | HAR31_I_b_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16647 | Phase B Current Odd THD | OTHD_I_b_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16648 | Phase B Current Even THD | ETHD_I_b_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16649 | Phase B Current K Factor | KF_I_b_% | % |  | int16 | R | 1 | 0.1 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16650 | Phase C Current 2-th Harmonic | HAR2_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16651 | Phase C Current 3-th Harmonic | HAR3_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16652 | Phase C Current 4-th Harmonic | HAR4_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16653 | Phase C Current 5-th Harmonic | HAR5_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16654 | Phase C Current 6-th Harmonic | HAR6_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16655 | Phase C Current 7-th Harmonic | HAR7_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16656 | Phase C Current 8-th Harmonic | HAR8_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16657 | Phase C Current 9-th Harmonic | HAR9_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16658 | Phase C Current 10-th Harmonic | HAR10_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16659 | Phase C Current 11-th Harmonic | HAR11_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16660 | Phase C Current 12-th Harmonic | HAR12_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16661 | Phase C Current 13-th Harmonic | HAR13_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16662 | Phase C Current 14-th Harmonic | HAR14_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16663 | Phase C Current 15-th Harmonic | HAR15_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16664 | Phase C Current 16-th Harmonic | HAR16_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16665 | Phase C Current 17-th Harmonic | HAR17_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16666 | Phase C Current 18-th Harmonic | HAR18_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16667 | Phase C Current 19-th Harmonic | HAR19_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16668 | Phase C Current 20-th Harmonic | HAR20_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16669 | Phase C Current 21-th Harmonic | HAR21_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16670 | Phase C Current 22-th Harmonic | HAR22_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16671 | Phase C Current 23-th Harmonic | HAR23_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16672 | Phase C Current 24-th Harmonic | HAR24_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16673 | Phase C Current 25-th Harmonic | HAR25_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16674 | Phase C Current 26-th Harmonic | HAR26_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16675 | Phase C Current 27-th Harmonic | HAR27_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16676 | Phase C Current 28-th Harmonic | HAR28_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16677 | Phase C Current 29-th Harmonic | HAR29_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16678 | Phase C Current 30-th Harmonic | HAR30_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16679 | Phase C Current 31-th Harmonic | HAR31_I_c_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
16680 | Phase C Current Odd THD | OTHD_I_c_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16681 | Phase C Current Even THD | ETHD_I_c_% | % |  | int16 | R | 1 | 0.01 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
16682 | Phase C Current K Factor | KF_I_c_% | % |  | int16 | R | 1 | 0.1 | 14-15 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
17044 | Real part of Voltage Positive Sequence | SEQ_POS_REAL_V | V | 增加单位 | int16 | R | 1 | 0.1 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17045 | Imag part of Voltage Postive Sequence | SEQ_POS_IMG_V | V | 增加单位 | int16 | R | 1 | 0.1 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17046 | Real part of Voltage Negative Sequence | SEQ_NEG_REAL_V | V | 增加单位 | int16 | R | 1 | 0.1 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17047 | Imag part of Voltage Negative Sequence | SEQ_NEG_IMG_V | V | 增加单位 | int16 | R | 1 | 0.1 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17048 | Real part of Voltage Zero Sequence | SEQ_ZERO_REAL_V | V | 增加单位 | int16 | R | 1 | 0.1 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17049 | Imag part of Voltage Zero Sequence | SEQ_ZERO_IMG_V | V | 增加单位 | int16 | R | 1 | 0.1 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17050 | Real part of Current Positive Sequence | SEQ_POS_REAL_I | A | 增加单位 | int16 | R | 1 | 0.001 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17051 | Imag part of Current Postive Sequence | SEQ_POS_IMG_I | A | 增加单位 | int16 | R | 1 | 0.001 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17052 | Real part of Current Negative Sequence | SEQ_NEG_REAL_I | A | 增加单位 | int16 | R | 1 | 0.001 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17053 | Imag part of Current Negative Sequence | SEQ_NEG_IMG_I | A | 增加单位 | int16 | R | 1 | 0.001 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17054 | Real part of Current Zero Sequence | SEQ_ZERO_REAL_I | A | 增加单位 | int16 | R | 1 | 0.001 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17055 | Imag part of Current Zero Sequence | SEQ_ZERO_IMG_I | A | 增加单位 | int16 | R | 1 | 0.001 | 14-15 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
17056 | Phase Angle of V2 to V1 | ANG_VLN_b | ° |  | int16 | R | 1 | 0.1 | 14-15 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
17057 | Phase Angle of V3 to V1 | ANG_VLN_c | ° |  | int16 | R | 1 | 0.1 | 14-15 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
17058 | Phase Angle of Phase A Current to V1 | ANG_I_a | ° |  | int16 | R | 1 | 0.1 | 14-15 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
17059 | Phase Angle of Phase B Current to V1 | ANG_I_b | ° |  | int16 | R | 1 | 0.1 | 14-15 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
17060 | Phase Angle of Phase C Current to V1 | ANG_I_c | ° |  | int16 | R | 1 | 0.1 | 14-15 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
17061 | Phase Angle of V1 to V1 | ANG_VLN_a | ° |  | word | R | 1 |  |  | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
17664 | Phase A Voltage 32-th Harmonic | HAR32_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17665 | Phase A Voltage 33-th Harmonic | HAR33_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17666 | Phase A Voltage 34-th Harmonic | HAR34_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17667 | Phase A Voltage 35-th Harmonic | HAR35_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17668 | Phase A Voltage 36-th Harmonic | HAR36_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17669 | Phase A Voltage 37-th Harmonic | HAR37_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17670 | Phase A Voltage 38-th Harmonic | HAR38_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17671 | Phase A Voltage 39-th Harmonic | HAR39_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17672 | Phase A Voltage 40-th Harmonic | HAR40_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17673 | Phase A Voltage 41-th Harmonic | HAR41_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17674 | Phase A Voltage 42-th Harmonic | HAR42_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17675 | Phase A Voltage 43-th Harmonic | HAR43_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17676 | Phase A Voltage 44-th Harmonic | HAR44_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17677 | Phase A Voltage 45-th Harmonic | HAR45_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17678 | Phase A Voltage 46-th Harmonic | HAR46_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17679 | Phase A Voltage 47-th Harmonic | HAR47_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17680 | Phase A Voltage 48-th Harmonic | HAR48_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17681 | Phase A Voltage 49-th Harmonic | HAR49_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17682 | Phase A Voltage 50-th Harmonic | HAR50_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17683 | Phase A Voltage 51-th Harmonic | HAR51_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17684 | Phase A Voltage 52-th Harmonic | HAR52_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17685 | Phase A Voltage 53-th Harmonic | HAR53_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17686 | Phase A Voltage 54-th Harmonic | HAR54_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17687 | Phase A Voltage 55-th Harmonic | HAR55_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17688 | Phase A Voltage 56-th Harmonic | HAR56_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17689 | Phase A Voltage 57-th Harmonic | HAR57_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17690 | Phase A Voltage 58-th Harmonic | HAR58_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17691 | Phase A Voltage 59-th Harmonic | HAR59_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17692 | Phase A Voltage 60-th Harmonic | HAR60_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17693 | Phase A Voltage 61-th Harmonic | HAR61_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17694 | Phase A Voltage 62-th Harmonic | HAR62_V_a_% | % |  | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17695 | Phase A Voltage 63-th Harmonic | HAR63_V_a_% | % | 新增，地址错误 |  | R | 1 | [9 empty] | harmonics |  | harmonics
17696 | Phase B Voltage 32-th Harmonic | HAR32_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17697 | Phase B Voltage 33-th Harmonic | HAR33_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17698 | Phase B Voltage 34-th Harmonic | HAR34_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17699 | Phase B Voltage 35-th Harmonic | HAR35_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17700 | Phase B Voltage 36-th Harmonic | HAR36_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17701 | Phase B Voltage 37-th Harmonic | HAR37_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17702 | Phase B Voltage 38-th Harmonic | HAR38_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17703 | Phase B Voltage 39-th Harmonic | HAR39_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17704 | Phase B Voltage 40-th Harmonic | HAR40_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17705 | Phase B Voltage 41-th Harmonic | HAR41_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17706 | Phase B Voltage 42-th Harmonic | HAR42_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17707 | Phase B Voltage 43-th Harmonic | HAR43_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17708 | Phase B Voltage 44-th Harmonic | HAR44_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17709 | Phase B Voltage 45-th Harmonic | HAR45_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17710 | Phase B Voltage 46-th Harmonic | HAR46_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17711 | Phase B Voltage 47-th Harmonic | HAR47_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17712 | Phase B Voltage 48-th Harmonic | HAR48_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17713 | Phase B Voltage 49-th Harmonic | HAR49_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17714 | Phase B Voltage 50-th Harmonic | HAR50_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17715 | Phase B Voltage 51-th Harmonic | HAR51_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17716 | Phase B Voltage 52-th Harmonic | HAR52_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17717 | Phase B Voltage 53-th Harmonic | HAR53_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17718 | Phase B Voltage 54-th Harmonic | HAR54_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17719 | Phase B Voltage 55-th Harmonic | HAR55_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17720 | Phase B Voltage 56-th Harmonic | HAR56_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17721 | Phase B Voltage 57-th Harmonic | HAR57_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17722 | Phase B Voltage 58-th Harmonic | HAR58_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17723 | Phase B Voltage 59-th Harmonic | HAR59_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17724 | Phase B Voltage 60-th Harmonic | HAR60_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17725 | Phase B Voltage 61-th Harmonic | HAR61_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17726 | Phase B Voltage 62-th Harmonic | HAR62_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17727 | Phase B Voltage 63-th Harmonic | HAR63_V_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17728 | Phase C Voltage 32-th Harmonic | HAR32_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17729 | Phase C Voltage 33-th Harmonic | HAR33_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17730 | Phase C Voltage 34-th Harmonic | HAR34_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17731 | Phase C Voltage 35-th Harmonic | HAR35_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17732 | Phase C Voltage 36-th Harmonic | HAR36_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17733 | Phase C Voltage 37-th Harmonic | HAR37_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17734 | Phase C Voltage 38-th Harmonic | HAR38_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17735 | Phase C Voltage 39-th Harmonic | HAR39_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17736 | Phase C Voltage 40-th Harmonic | HAR40_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17737 | Phase C Voltage 41-th Harmonic | HAR41_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17738 | Phase C Voltage 42-th Harmonic | HAR42_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17739 | Phase C Voltage 43-th Harmonic | HAR43_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17740 | Phase C Voltage 44-th Harmonic | HAR44_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17741 | Phase C Voltage 45-th Harmonic | HAR45_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17742 | Phase C Voltage 46-th Harmonic | HAR46_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17743 | Phase C Voltage 47-th Harmonic | HAR47_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17744 | Phase C Voltage 48-th Harmonic | HAR48_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17745 | Phase C Voltage 49-th Harmonic | HAR49_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17746 | Phase C Voltage 50-th Harmonic | HAR50_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17747 | Phase C Voltage 51-th Harmonic | HAR51_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17748 | Phase C Voltage 52-th Harmonic | HAR52_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17749 | Phase C Voltage 53-th Harmonic | HAR53_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17750 | Phase C Voltage 54-th Harmonic | HAR54_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17751 | Phase C Voltage 55-th Harmonic | HAR55_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17752 | Phase C Voltage 56-th Harmonic | HAR56_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17753 | Phase C Voltage 57-th Harmonic | HAR57_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17754 | Phase C Voltage 58-th Harmonic | HAR58_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17755 | Phase C Voltage 59-th Harmonic | HAR59_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17756 | Phase C Voltage 60-th Harmonic | HAR60_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17757 | Phase C Voltage 61-th Harmonic | HAR61_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17758 | Phase C Voltage 62-th Harmonic | HAR62_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17759 | Phase C Voltage 63-th Harmonic | HAR63_V_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17760 | Phase A Current 32-th Harmonic | HAR32_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17761 | Phase A Current 33-th Harmonic | HAR33_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17762 | Phase A Current 34-th Harmonic | HAR34_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17763 | Phase A Current 35-th Harmonic | HAR35_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17764 | Phase A Current 36-th Harmonic | HAR36_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17765 | Phase A Current 37-th Harmonic | HAR37_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17766 | Phase A Current 38-th Harmonic | HAR38_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17767 | Phase A Current 39-th Harmonic | HAR39_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17768 | Phase A Current 40-th Harmonic | HAR40_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17769 | Phase A Current 41-th Harmonic | HAR41_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17770 | Phase A Current 42-th Harmonic | HAR42_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17771 | Phase A Current 43-th Harmonic | HAR43_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17772 | Phase A Current 44-th Harmonic | HAR44_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17773 | Phase A Current 45-th Harmonic | HAR45_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17774 | Phase A Current 46-th Harmonic | HAR46_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17775 | Phase A Current 47-th Harmonic | HAR47_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17776 | Phase A Current 48-th Harmonic | HAR48_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17777 | Phase A Current 49-th Harmonic | HAR49_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17778 | Phase A Current 50-th Harmonic | HAR50_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17779 | Phase A Current 51-th Harmonic | HAR51_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17780 | Phase A Current 52-th Harmonic | HAR52_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17781 | Phase A Current 53-th Harmonic | HAR53_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17782 | Phase A Current 54-th Harmonic | HAR54_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17783 | Phase A Current 55-th Harmonic | HAR55_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17784 | Phase A Current 56-th Harmonic | HAR56_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17785 | Phase A Current 57-th Harmonic | HAR57_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17786 | Phase A Current 58-th Harmonic | HAR58_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17787 | Phase A Current 59-th Harmonic | HAR59_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17788 | Phase A Current 60-th Harmonic | HAR60_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17789 | Phase A Current 61-th Harmonic | HAR61_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17790 | Phase A Current 62-th Harmonic | HAR62_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17791 | Phase A Current 63-th Harmonic | HAR63_I_a_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17792 | Phase B Current 32-th Harmonic | HAR32_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17793 | Phase B Current 33-th Harmonic | HAR33_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17794 | Phase B Current 34-th Harmonic | HAR34_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17795 | Phase B Current 35-th Harmonic | HAR35_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17796 | Phase B Current 36-th Harmonic | HAR36_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17797 | Phase B Current 37-th Harmonic | HAR37_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17798 | Phase B Current 38-th Harmonic | HAR38_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17799 | Phase B Current 39-th Harmonic | HAR39_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17800 | Phase B Current 40-th Harmonic | HAR40_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17801 | Phase B Current 41-th Harmonic | HAR41_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17802 | Phase B Current 42-th Harmonic | HAR42_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17803 | Phase B Current 43-th Harmonic | HAR43_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17804 | Phase B Current 44-th Harmonic | HAR44_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17805 | Phase B Current 45-th Harmonic | HAR45_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17806 | Phase B Current 46-th Harmonic | HAR46_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17807 | Phase B Current 47-th Harmonic | HAR47_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17808 | Phase B Current 48-th Harmonic | HAR48_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17809 | Phase B Current 49-th Harmonic | HAR49_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17810 | Phase B Current 50-th Harmonic | HAR50_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17811 | Phase B Current 51-th Harmonic | HAR51_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17812 | Phase B Current 52-th Harmonic | HAR52_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17813 | Phase B Current 53-th Harmonic | HAR53_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17814 | Phase B Current 54-th Harmonic | HAR54_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17815 | Phase B Current 55-th Harmonic | HAR55_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17816 | Phase B Current 56-th Harmonic | HAR56_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17817 | Phase B Current 57-th Harmonic | HAR57_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17818 | Phase B Current 58-th Harmonic | HAR58_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17819 | Phase B Current 59-th Harmonic | HAR59_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17820 | Phase B Current 60-th Harmonic | HAR60_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17821 | Phase B Current 61-th Harmonic | HAR61_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17822 | Phase B Current 62-th Harmonic | HAR62_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17823 | Phase B Current 63-th Harmonic | HAR63_I_b_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17824 | Phase C Current 32-th Harmonic | HAR32_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17825 | Phase C Current 33-th Harmonic | HAR33_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17826 | Phase C Current 34-th Harmonic | HAR34_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17827 | Phase C Current 35-th Harmonic | HAR35_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17828 | Phase C Current 36-th Harmonic | HAR36_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17829 | Phase C Current 37-th Harmonic | HAR37_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17830 | Phase C Current 38-th Harmonic | HAR38_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17831 | Phase C Current 39-th Harmonic | HAR39_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17832 | Phase C Current 40-th Harmonic | HAR40_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17833 | Phase C Current 41-th Harmonic | HAR41_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17834 | Phase C Current 42-th Harmonic | HAR42_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17835 | Phase C Current 43-th Harmonic | HAR43_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17836 | Phase C Current 44-th Harmonic | HAR44_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17837 | Phase C Current 45-th Harmonic | HAR45_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17838 | Phase C Current 46-th Harmonic | HAR46_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17839 | Phase C Current 47-th Harmonic | HAR47_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17840 | Phase C Current 48-th Harmonic | HAR48_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17841 | Phase C Current 49-th Harmonic | HAR49_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17842 | Phase C Current 50-th Harmonic | HAR50_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17843 | Phase C Current 51-th Harmonic | HAR51_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17844 | Phase C Current 52-th Harmonic | HAR52_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17845 | Phase C Current 53-th Harmonic | HAR53_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17846 | Phase C Current 54-th Harmonic | HAR54_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17847 | Phase C Current 55-th Harmonic | HAR55_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17848 | Phase C Current 56-th Harmonic | HAR56_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17849 | Phase C Current 57-th Harmonic | HAR57_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17850 | Phase C Current 58-th Harmonic | HAR58_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17851 | Phase C Current 59-th Harmonic | HAR59_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17852 | Phase C Current 60-th Harmonic | HAR60_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17853 | Phase C Current 61-th Harmonic | HAR61_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17854 | Phase C Current 62-th Harmonic | HAR62_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17855 | Phase C Current 63-th Harmonic | HAR63_I_c_% | % | 地址错误，修改地址+1 | int16 | R | 1 | 0.01 | [8 empty] | harmonics |  | harmonics
17952 | Phase A Import Active Energy | EP_IMP_a_kWh | kWh |  | uint32 | R/W | 2 | 0.1 | 14 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
17954 | Phase A Export Active Energy | EP_EXP_a_kWh | kWh |  | uint32 | R/W | 2 | 0.1 | 14 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
17956 | Phase B Import Active Energy | EP_IMP_b_kWh | kWh |  | uint32 | R/W | 2 | 0.1 | 14 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
17958 | Phase B Export Active Energy | EP_EXP_b_kWh | kWh |  | uint32 | R/W | 2 | 0.1 | 14 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
17960 | Phase C Import Active Energy | EP_IMP_c_kWh | kWh |  | uint32 | R/W | 2 | 0.1 | 14 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
17962 | Phase C Export Active Energy | EP_EXP_c_kWh | kWh |  | uint32 | R/W | 2 | 0.1 | 14 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
17964 | Phase A Import Reactive Energy | EQ_IMP_a_kvarh | kvarh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
17966 | Phase A Export Reactive Energy | EQ_EXP_a_kvarh | kvarh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
17968 | Phase B Import Reactive Energy | EQ_IMP_b_kvarh | kvarh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
17970 | Phase B Export Reactive Energy | EQ_EXP_b_kvarh | kvarh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
17972 | Phase C Import Reactive Energy | EQ_IMP_c_kvarh | kvarh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
17974 | Phase C Export Reactive Energy | EQ_EXP_c_kvarh | kvarh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
17976 | Phase A Apparent Energy | ES_a_kVAh | kVAh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
17978 | Phase B Apparent Energy | ES_b_kVAh | kVAh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
17980 | Phase C Apparent Energy | ES_c_kVAh | kVAh |  | uint32 | R/W | 2 | 0.1 | 14 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
4093 | Nominal Frequency | Conf_NominalFreq |  |  | uint16 | R/W | 1 | 1
4094 | Channel 1 Communication Protocol | Conf_Ch1_Proto |  |  | uint16 | R/W | 1 | 1
4095 | Channel 1 Parity | Conf_Ch1_Parity |  |  | uint16 | R/W | 1 | 1
4096 | Password | Conf_Password |  |  | uint16 | R/W | 1 | 1
4097 | Channel 1 Address | Conf_Ch1_Addr |  |  | uint16 | R/W | 1 | 1
4098 | Channel 1 Baud Rate | Conf_Ch1_Baud |  |  | uint16 | R/W | 1 | 1
4099 | Service Configuration | Conf_ServiceConfig |  |  | uint32 | R/W | 2 | 1
4101 | PT1 | Conf_PT1 |  |  | uint32 | R/W | 2 | 0.1
4103 | PT2 | Conf_PT2 |  |  | uint16 | R/W | 1 | 0.1
4104 | CT1 | Conf_CT1 |  |  | uint16 | R/W | 1 | 1
4105 | CT2 | Conf_CT2 |  |  | uint16 | R/W | 1 | 1
4106 | KWh Pulse Constant | Conf_Ep_PulseConst |  |  | uint16 | R/W | 1 | 1
4107 | Kvarh Pulse Constant | Conf_Eq_PulseConst |  |  | uint16 | R/W | 1 | 1
4108 | LCD Backlight Time | Conf_Backlight_Time |  |  | uint16 | R/W | 1 | 1
4109 | Demand Window | Conf_Dmd_Window |  |  | uint16 | R/W | 1 | 1
4110 | Demand Method | Conf_Dmd_Method |  |  | uint16 | R/W | 1 | 1
4111 | Clear Demand | Conf_Clr_Dmd |  |  | uint16 | R/W | 1 | 1
4112 | Clear Max/Min | Conf_Clr_MaxMin |  |  | uint16 | R/W | 1 | 1
4113 | Clear Run Hours | Conf_Clr_RunHours |  |  | uint16 | R/W | 1 | 1
4114 | Current I1 Direction | Conf_I1_Dir |  |  | uint16 | R/W | 1 | 1
4115 | Current I2 Direction | Conf_I2_Dir |  |  | uint16 | R/W | 1 | 1
4116 | Current I3 Direction | Conf_I3_Dir |  |  | uint16 | R/W | 1 | 1
4117 | VAR/PF Convention | Conf_CalcMethod_VarPF |  |  | uint16 | R/W | 1 | 1
4118 | Clear Energy | Conf_Clr_Egy |  |  | uint16 | R/W | 1 | 1
4119 | Energy Calculation Method | Conf_CalcMethod_Energy |  |  | uint16 | R/W | 1 | 1
4120 | Reactive Power Calculation Method | Conf_CalcMethod_Q |  |  | uint16 | R/W | 1 | 1
4121 | Energy Reading Primary/Secondary | Conf_DispFormat_Energy |  |  | uint16 | R/W | 1 | 1
4122 | Reset Ethernet Module | Conf_Rst_EthernetModule |  |  | uint16 | R/W | 1 | 1
4123 | Enable SOE | Conf_Enable_SOE |  |  | uint16 | R/W | 1 | 1
4124 | Clear Pulse Counter | Conf_Clr_PulseCnt |  |  | uint16 | R/W | 1 | 1
4125 | Basic Reading Display Primary/Secondary | Conf_DispFormat_RealTime |  |  | uint16 | R/W | 1 | 1
4126 | Non-Standard Content Seal Option | Conf_Seal_Option |  |  | uint16 | R/W | 1 | 1
4127 | Sealing Status | Info_Seal_Status |  |  | uint16 | R | 1 | 1
4128 | Demand Sub-Interval | Conf_Dmd_SubInterval |  |  | uint16 | R/W | 1 | 1
4129 | Clear Alarm Records | Conf_Clr_Alarm |  |  | uint16 | R/W | 1 | 1
4130 | CT41 | Conf_CT41 |  |  | uint16 | R/W | 1 | 1
4131 | CT42 | Conf_CT42 |  |  | uint16 | R/W | 1 | 1
4132 | JiGuan Customized PT | Conf_JG_PT |  |  | uint16 | R/W | 1 | 1
4133 | JiGuan Customized CT | Conf_JG_CT |  |  | uint16 | R/W | 1 | 1
4134 | Restore Factory Setting | Conf_Restore_FactorySetting |  |  | uint16 | R/W | 1 | 1
4135 | Line N Current Method | Conf_In_Method |  |  | uint16 | R/W | 1 | 1
4136 | Modbus Gateway Enable | Conf_Enable_ModbusGateway |  |  | uint16 | R/W | 1 | 1
4137 | Reserve1 | Conf_Rsv1 |  |  | uint16 | R/W | 1 | 1
4138 | Reserve2 | Conf_Rsv2 |  |  | uint16 | R/W | 1 | 1
4139 | Reserve3 | Conf_Rsv3 |  |  | uint16 | R/W | 1 | 1
4140 | Nominal Full Load Power | Conf_Nom_Full_Load_Power |  |  | uint16 | R/W | 1 | 1
4141 | Load Display Type | Conf_LoadDispType |  |  | uint16 | R/W | 1 | 1
4142 | System Status | Info_Sys_Status |  |  | uint16 | R | 1 | 1
4143 | Channel 2 Baud Rate | Conf_Ch2_Baud |  |  | uint16 | R/W | 1 | 1
4144 | Channel 2 Parity | Conf_Ch2_Parity |  |  | uint16 | R/W | 1 | 1
4145 | Channel 2 Address | Conf_Ch2_Addr |  |  | uint16 | R/W | 1 | 1
4146 | Latest Alarm Group Number | Info_Alm_GroupNumber |  |  | uint16 | R | 1 | 1
4147 | Latest SOE Record Group Number | Info_SOE_GroupNumber |  |  | uint16 | R | 1 | 1
4148 | Run Hour | Info_RunHour |  |  | uint32 | R | 2 | 1
4150 | Module Connection Status | Info_Module_Status |  |  | uint16 | R | 1 | 1
4151 | Temperature (Not in Use) | Info_Old_Temperature |  |  | uint16 | R | 1 | 1
4152 | Channel 2 Communication Protocol | Conf_Ch2_Proto |  |  | uint16 | R/W | 1 | 1
4153 | Enable Downloading TOU Ten Year Configs | Conf_Enable_DL_TOU10YrConfigs |  |  | uint16 | R/W | 1 | 1
4154 | Clear Max Demand - Sharp Tariff | Conf_Clr_MaxDmd_Sharp |  |  | uint16 | R/W | 1 | 1
4155 | Clear Max Demand - Peak Tariff | Conf_Clr_MaxDmd_Peak |  |  | uint16 | R/W | 1 | 1
4156 | Clear Max Demand - Valley Tariff | Conf_Clr_MaxDmd_Valley |  |  | uint16 | R/W | 1 | 1
4157 | Clear Max Demand - Normal Tariff | Conf_Clr_MaxDmd_Norm |  |  | uint16 | R/W | 1 | 1
4158 | Clear Max Demand - All Tariffs | Conf_Clr_MaxDmd_All |  |  | uint16 | R/W | 1 | 1
4159 | Week | Conf_Week |  |  | uint16 | R/W | 1 | 1
4160 | Year | Conf_Year |  |  | uint16 | R/W | 1 | 1
4161 | Month | Conf_Month |  |  | uint16 | R/W | 1 | 1
4162 | Day | Conf_Day |  |  | uint16 | R/W | 1 | 1
4163 | Hour | Conf_Hr |  |  | uint16 | R/W | 1 | 1
4164 | Minute | Conf_Min |  |  | uint16 | R/W | 1 | 1
4165 | Second | Conf_Sec |  |  | uint16 | R/W | 1 | 1
4351 | Phase Order | Conf_Phase_Order |  |  | uint16 | R/W | 1
44901 | Enable Class S PQ Event | Conf_Enable_ClassSPQ |  |  | uint16 | R/W | 1 | 1
44902 | Nominal Voltage | Conf_NominalVolt |  |  | uint16 | R/W | 1 | 1
44903 | Nominal Current | Conf_NominalCurrent |  |  | uint16 | R/W | 1 | 0.001
44904 | Sample Rate | Conf_SampleRate |  |  | uint16 | R/W | 1 | 1
44905 | Voltage Sag Enable | Conf_VoltSag_Enable |  |  | uint16 | R/W | 1 | 1
44906 | Voltage Sag Threshold | Conf_VoltSag_Threshold |  |  | uint16 | R/W | 1 | 1
44907 | Voltage Sag Hysteresis | Conf_VoltSag_Hyst |  |  | uint16 | R/W | 1 | 1
44908 | Voltage Sag Trigger Waveform | Conf_VoltSag_TrigWave |  |  | uint16 | R/W | 1 | 1
44909 | Voltage Sag Trigger DO | Conf_VoltSag_TrigDO |  |  | uint16 | R/W | 1 | 1
44910 | Voltage Sag Trigger RO | Conf_VoltSag_TrigRO |  |  | uint16 | R/W | 1 | 1
44911 | Voltage Swell Enable | Conf_VoltSwell_Enable |  |  | uint16 | R/W | 1 | 1
44912 | Voltage Swell Threshold | Conf_VoltSwell_Threshold |  |  | uint16 | R/W | 1 | 1
44913 | Voltage Swell Hysteresis | Conf_VoltSwell_Hyst |  |  | uint16 | R/W | 1 | 1
44914 | Voltage Swell Trigger Waveform | Conf_VoltSwell_TrigWave |  |  | uint16 | R/W | 1 | 1
44915 | Voltage Swell Trigger DO | Conf_VoltSwell_TrigDO |  |  | uint16 | R/W | 1 | 1
44916 | Voltage Swell Trigger RO | Conf_VoltSwell_TrigRO |  |  | uint16 | R/W | 1 | 1
44917 | Voltage Interrupt Enable | Conf_VoltInt_Enable |  |  | uint16 | R/W | 1 | 1
44918 | Voltage Interrupt Threshold | Conf_VoltInt_Threshold |  |  | uint16 | R/W | 1 | 1
44919 | Voltage Interrupt Hysteresis | Conf_VoltInt_Hyst |  |  | uint16 | R/W | 1 | 1
44920 | Voltage Interrupt Trigger Waveform | Conf_VoltInt_TrigWave |  |  | uint16 | R/W | 1 | 1
44921 | Voltage Interrupt Trigger DO | Conf_VoltInt_TrigDO |  |  | uint16 | R/W | 1 | 1
44922 | Voltage Interrupt Trigger RO | Conf_VoltInt_TrigRO |  |  | uint16 | R/W | 1 | 1
44923 | Voltage Unbalance Enable | Conf_VoltUnbl_Enable |  |  | uint16 | R/W | 1 | 1
44924 | Voltage Unbalance Threshold | Conf_VoltUnbl_Threshold |  |  | uint16 | R/W | 1 | 1
44925 | Voltage Unbalance Hysteresis | Conf_VoltUnbl_Hyst |  |  | uint16 | R/W | 1 | 1
44926 | Voltage Unbalance Trigger Waveform | Conf_VoltUnbl_TrigWave |  |  | uint16 | R/W | 1 | 1
44927 | Voltage Unbalance Trigger DO | Conf_VoltUnbl_TrigDO |  |  | uint16 | R/W | 1 | 1
44928 | Voltage Unbalance Trigger RO | Conf_VoltUnbl_TrigRO |  |  | uint16 | R/W | 1 | 1
44929 | Current Dip Enable | Conf_CurrentDip_Enable |  |  | uint16 | R/W | 1 | 1
44930 | Current Dip Threshold | Conf_CurrentDip_Threshold |  |  | uint16 | R/W | 1 | 1
44931 | Current Dip Hysteresis | Conf_CurrentDip_Hyst |  |  | uint16 | R/W | 1 | 1
44932 | Current Dip Trigger Waveform | Conf_CurrentDip_TrigWave |  |  | uint16 | R/W | 1 | 1
44933 | Current Dip Trigger DO | Conf_CurrentDip_TrigDO |  |  | uint16 | R/W | 1 | 1
44934 | Current Dip Trigger RO | Conf_CurrentDip_TrigRO |  |  | uint16 | R/W | 1 | 1
44935 | Current Swell Enable | Conf_CurrentSwell_Enable |  |  | uint16 | R/W | 1 | 1
44936 | Current Swell Threshold | Conf_CurrentSwell_Threshold |  |  | uint16 | R/W | 1 | 1
44937 | Current Swell Hysteresis | Conf_CurrentSwell_Hyst |  |  | uint16 | R/W | 1 | 1
44938 | Current Swell Trigger Waveform | Conf_CurrentSwell_TrigWave |  |  | uint16 | R/W | 1 | 1
44939 | Current Swell Trigger DO | Conf_CurrentSwell_TrigDO |  |  | uint16 | R/W | 1 | 1
44940 | Current Swell Trigger RO | Conf_CurrentSwell_TrigRO |  |  | uint16 | R/W | 1 | 1
44941 | Current Unbalance Enable | Conf_CurrentUnbl_Enable |  |  | uint16 | R/W | 1 | 1
44942 | Current Unbalance Threshold | Conf_CurrentUnbl_Threshold |  |  | uint16 | R/W | 1 | 1
44943 | Current Unbalance Hysteresis | Conf_CurrentUnbl_Hyst |  |  | uint16 | R/W | 1 | 1
44944 | Current Unbalance Trigger Waveform | Conf_CurrentUnbl_TrigWave |  |  | uint16 | R/W | 1 | 1
44945 | Current Unbalance Trigger DO | Conf_CurrentUnbl_TrigDO |  |  | uint16 | R/W | 1 | 1
44946 | Current Unbalance Trigger RO | Conf_CurrentUnbl_TrigRO |  |  | uint16 | R/W | 1 | 1
32768 | Manually Trigger Waveform | Conf_Mannual_TrigWave |  |  | uint16 | W | 1 | 1
32769 | AXM-IO11 Trigger Waveform | Conf_IO11_TrigWave |  |  | uint16 | R/W | 1 | 1
32770 | AXM-IO21 Trigger Waveform | Conf_IO21_TrigWave |  |  | uint16 | R/W | 1 | 1
32771 | AXM-IO31 Trigger Waveform | Conf_IO31_TrigWave |  |  | uint16 | R/W | 1 | 1
32772 | Voltage Rated Value | Conf_Old_NominalVolt |  |  | uint16 | R/W | 1 | 1
32773 | Voltage Sag Trigger | Conf_Old_VoltSag_Trig |  |  | uint16 | R/W | 1 | 1
32774 | Voltage Sag Threshold | Conf_Old_VoltSag_Threshold |  |  | uint16 | R/W | 1 | 1
32775 | Voltage Sag Half Cycle | Conf_Old_VoltSag_Duration |  |  | uint16 | R/W | 1 | 1
32776 | Voltage Swell Trigger | Conf_Old_VoltSwell_Trig |  |  | uint16 | R/W | 1 | 1
32777 | Voltage Swell Threshold | Conf_Old_VoltSwell_Threshold |  |  | uint16 | R/W | 1 | 1
32778 | Sample Rate | Conf_Old_Samp_Rate |  |  | uint16 | R/W | 1 | 1
32779 | Current Rated Value | Conf_Old_NominalCurrent |  |  | uint16 | R/W | 1 | 1
32780 | Over-Current Trigger | Conf_Old_CurrentSwell_Trig |  |  | uint16 | R/W | 1 | 1
32781 | Over-Current Threshold | Conf_Old_CurrentSwell_Threshold |  |  | uint16 | R/W | 1 | 1
32782 | Clear Waveform | Conf_Clr_Wave |  |  | uint16 | R/W | 1 | 1
32783 | Clear Power Quality Event | Conf_Clr_PQEvent |  |  | uint16 | R/W | 1 | 1
61555 | Number of CT | Info_CT_Num |  |  | uint16 | R | 1 | 1
61936 | CT2 Type | Info_CT2_Type |  |  | uint16 | R | 1 | 1
36611 | Latest Waveform Record Groupe Number | lastWaveformNum |  |  | uint16 | R | 1 | 1
44950 | Latest PQ Event Record Group Number | lastPQEventNum |  |  | uint16 | R | 1 | 1