## block
blockId | type | start | count | isEnable | NAME
0 | VIRTUAL_BLOCK | 0 | 1 | true | isOnline
1 | HOLDING_REGISTER | 8468 | 84 | true | Real time basic 1
2 | HOLDING_REGISTER | 8552 | 50 | true | Real time basic 2
3 | HOLDING_REGISTER | 8602 | 78 | true | Harmonics - THD
4 | HOLDING_REGISTER | 24832 | 8 | true | Demand 1
5 | HOLDING_REGISTER | 24984 | 24 | true | Demand 2
6 | HOLDING_REGISTER | 26048 | 96 | true | Energy 1
7 | HOLDING_REGISTER | 26144 | 48 | true | Energy 2

## blockParams
ID | blockId | paramId | Start(Dec) | descrption | paramType | unit | dataType | byteOrder | RW | Reg | scale | analysisUnitId | datalog | trendreal | trendenergy | north | conf | PowerQuality | range | readings | Alarm | DataLog | AcuCloud | MQTT | SNMP | BACnetIP |  | paramType_AcuCloud | AcuHMI中模板没有的，AcuCloud中有的字段
1 | 0 | 0-1 | 0 | IsOnline | IsOnline |  | isOnline | 1 | R | 1 | 1 | 0 | [6 empty] | 5 | 11-12 | realtime |  | realtime | realtime | realtime | realtime | realtime |  | 2HR_FLICK_Va | 2HR Flick Va (plt)
2 | 1 | 1-1 | 8468 | System Frequency | FREQ_Hz | Hz | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Freq_Hz | 2HR_FLICK_Vb | 2HR Flick Vb (plt)
3 | 1 | 1-2 | 8470 | Phase A Line-to-Neutral Voltage | VLN_a_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | VLNa_V | 2HR_FLICK_Vc | 2HR Flick Vc (plt)
4 | 1 | 1-3 | 8472 | Phase B Line-to-Neutral Voltage | VLN_b_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | VLNb_V | MAG_UNBL_V | Voltage Unbalance Factor
5 | 1 | 1-4 | 8474 | Phase C Line-to-Neutral Voltage | VLN_c_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | VLNc_V | MAG_UNBL_I | Current Unbalance Factor
6 | 1 | 1-5 | 8476 | Average Line-to-Neutral Voltage | VLN_avg_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | VLNavg_V | AcuCloud模板中其余均以10M开头的字段
7 | 1 | 1-6 | 8478 | Phase A-B Line-to-Line Voltage | VLL_ab_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | VLLab_V
8 | 1 | 1-7 | 8480 | Phase B-C Line-to-Line Voltage | VLL_bc_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | VLLbc_V
9 | 1 | 1-8 | 8482 | Phase C-A Line-to-Line Voltage | VLL_ca_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | VLLca_V
10 | 1 | 1-9 | 8484 | Average Line-to-Line Voltage | VLL_avg_V | V | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | VLLavg_V
11 | 1 | 1-10 | 8486 | Phase A Line Current | I_a_A | A | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ia_A
12 | 1 | 1-11 | 8488 | Phase B Line Current | I_b_A | A | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ib_A
13 | 1 | 1-12 | 8490 | Phase C Line Current | I_c_A | A | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Ic_A
14 | 1 | 1-13 | 8492 | Neutral Current | I_n_A | A | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Inn_A
15 | 1 | 1-14 | 8494 | Average Line Current | I_avg_A | A | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Iavg_A
16 | 1 | 1-15 | 8496 | Phase A Active Power | P_a_kW | kW | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Pa_kW
17 | 1 | 1-16 | 8498 | Phase B Active Power | P_b_kW | kW | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Pb_kW
18 | 1 | 1-17 | 8500 | Phase C Active Power | P_c_kW | kW | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Pc_kW
19 | 1 | 1-18 | 8502 | System Active Power | P_kW | kW | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | P_kW
20 | 1 | 1-19 | 8504 | Phase A Reactive Power | Q_a_kvar | kvar | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qa_kvar
21 | 1 | 1-20 | 8506 | Phase B Reactive Power | Q_b_kvar | kvar | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qb_kvar
22 | 1 | 1-21 | 8508 | Phase C Reactive Power | Q_c_kvar | kvar | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Qc_kvar
23 | 1 | 1-22 | 8510 | System Reactive Power | Q_kvar | kvar | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Q_kvar
24 | 1 | 1-23 | 8512 | Phase A Apparent Power | S_a_kVA | kVA | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Sa_kVA
25 | 1 | 1-24 | 8514 | Phase B Apparent Power | S_b_kVA | kVA | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Sb_kVA
26 | 1 | 1-25 | 8516 | Phase C Apparent Power | S_c_kVA | kVA | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | Sc_kVA
27 | 1 | 1-26 | 8518 | System Apparent Power | S_kVA | kVA | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | S_kVA
28 | 1 | 1-27 | 8520 | Phase A Load Nature | LC_a | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | [7 empty] | realtime
29 | 1 | 1-28 | 8522 | Phase B Load Nature | LC_b | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | [7 empty] | realtime
30 | 1 | 1-29 | 8524 | Phase C Load Nature | LC_c | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | [7 empty] | realtime
31 | 1 | 1-30 | 8526 | System Load Nature | LC_avg | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | [7 empty] | realtime
32 | 1 | 1-31 | 8528 | Phase A Power Factor | PF_a | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
33 | 1 | 1-32 | 8530 | Phase B Power Factor | PF_b | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
34 | 1 | 1-33 | 8532 | Phase C Power Factor | PF_c | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
35 | 1 | 1-34 | 8534 | System Power Factor | PF | % | float32 | 12 | R | 2 | 1 | 1 | 1 | 2 |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
36 | 1 | 1-35 | 8536 | Phase A Leading Power Factor | LEAD_PF_a | % | float32 | 12 | R | 2 | 1 | 1 |  |  |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
37 | 1 | 1-36 | 8538 | Phase B Leading Power Factor | LEAD_PF_b | % | float32 | 12 | R | 2 | 1 | 1 |  |  |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
38 | 1 | 1-37 | 8540 | Phase C Leading Power Factor | LEAD_PF_c | % | float32 | 12 | R | 2 | 1 | 1 |  |  |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
39 | 1 | 1-38 | 8542 | System Leading Power Factor | LEAD_PF | % | float32 | 12 | R | 2 | 1 | 1 |  |  |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
40 | 1 | 1-39 | 8544 | Phase A Lagging Power Factor | LAG_PF_a | % | float32 | 12 | R | 2 | 1 | 1 |  |  |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
41 | 1 | 1-40 | 8546 | Phase B Lagging Power Factor | LAG_PF_b | % | float32 | 12 | R | 2 | 1 | 1 |  |  |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
42 | 1 | 1-41 | 8548 | Phase C Lagging Power Factor | LAG_PF_c | % | float32 | 12 | R | 2 | 1 | 1 |  |  |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
43 | 1 | 1-42 | 8550 | System Lagging Power Factor | LAG_PF | % | float32 | 12 | R | 2 | 1 | 1 |  |  |  | 4 |  |  | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime
44 | 2 | 2-1 | 8552 | Phase A Line-to-Neutral Voltage Phase Angle | ANG_VLN_a | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PA_VLNa
45 | 2 | 2-2 | 8554 | Phase B Line-to-Neutral Voltage Phase Angle | ANG_VLN_b | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PA_VLNb
46 | 2 | 2-3 | 8556 | Phase C Line-to-Neutral Voltage Phase Angle | ANG_VLN_c | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PA_VLNc
47 | 2 | 2-4 | 8558 | Phase AB Line-to-Line Voltage Phase Angle | ANG_VLL_ab | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PA_VLLab
48 | 2 | 2-5 | 8560 | Phase BC Line-to-Line Voltage Phase Angle | ANG_VLL_bc | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PA_VLLbc
49 | 2 | 2-6 | 8562 | Phase CA Line-to-Line Voltage Phase Angle | ANG_VLL_ca | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PA_VLLca
50 | 2 | 2-7 | 8564 | Phase A Current Phase Angle | ANG_I_a | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PA_Ia
51 | 2 | 2-8 | 8566 | Phase B Current Phase Angle | ANG_I_b | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PA_Ib
52 | 2 | 2-9 | 8568 | Phase C Current Phase Angle | ANG_I_c | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 5 | 11-12 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | PA_Ic
53 | 2 | 2-10 | 8570 | Voltage Positive Sequence Magnitude | SEQ_POS_MAG_V |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
54 | 2 | 2-11 | 8572 | Voltage Zero Sequence Magnitude | SEQ_ZERO_MAG_V |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
55 | 2 | 2-12 | 8574 | Voltage Negative Sequence Magnitude | SEQ_NEG_MAG_V |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
56 | 2 | 2-13 | 8576 | Voltage Zero Sequence Ratio Magnitude | SEQ_ZERO_RATIO_V_% |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | MAG_SEQ_ZERO_RATIO_V
57 | 2 | 2-14 | 8578 | Voltage Unbalance Factor Magnitude | UNBL_V_% |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
58 | 2 | 2-15 | 8580 | Current Positive Sequence Magnitude | SEQ_POS_MAG_I |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
59 | 2 | 2-16 | 8582 | Current Zero Sequence Magnitude | SEQ_ZERO_MAG_I |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
60 | 2 | 2-17 | 8584 | Current Negative Sequence Magnitude | SEQ_NEG_MAG_I |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
61 | 2 | 2-18 | 8586 | Current Zero Sequence Ratio Magnitude | SEQ_ZERO_RATIO_I_% |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence | MAG_SEQ_ZERO_RATIO_I
62 | 2 | 2-19 | 8588 | Current Unbalance Factor Magnitude | UNBL_I_% |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
63 | 2 | 2-20 | 8590 | Voltage Positive Sequence Angle | SEQ_POS_ANG_V | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
64 | 2 | 2-21 | 8592 | Voltage Zero Sequence Angle | SEQ_ZERO_ANG_V | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
65 | 2 | 2-22 | 8594 | Voltage Negative Sequence Angle | SEQ_NEG_ANG_V | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
66 | 2 | 2-23 | 8596 | Current Positive Sequence Angle | SEQ_POS_ANG_I | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
67 | 2 | 2-24 | 8598 | Current Zero Sequence Angle | SEQ_ZERO_ANG_I | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
68 | 2 | 2-25 | 8600 | Current Negative Sequence Angle | SEQ_NEG_ANG_I | ° | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 10 | 11-12 | sequence | sequence | sequence | sequence | sequence | sequence | sequence
69 | 3 | 3-1 | 8602 | Phase A Voltage THD | THD_V_a_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | THD_Va
70 | 3 | 3-2 | 8604 | Phase B Voltage THD | THD_V_b_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | THD_Vb
71 | 3 | 3-3 | 8606 | Phase C Voltage THD | THD_V_c_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | THD_Vc
72 | 3 | 3-4 | 8608 | Phase A Voltage THD Odd | OTHD_V_a_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | OTHD_Va
73 | 3 | 3-5 | 8610 | Phase B Voltage THD Odd | OTHD_V_b_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | OTHD_Vb
74 | 3 | 3-6 | 8612 | Phase C Voltage THD Odd | OTHD_V_c_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | OTHD_Vc
75 | 3 | 3-7 | 8614 | Phase A Voltage THD Even | ETHD_V_a_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | ETHD_Va
76 | 3 | 3-8 | 8616 | Phase B Voltage THD Even | ETHD_V_b_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | ETHD_Vb
77 | 3 | 3-9 | 8618 | Phase C Voltage THD Even | ETHD_V_c_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | ETHD_Vc
78 | 3 | 3-10 | 8620 | Phase A Voltage Crest Factor | CF_V_a_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | CF_Va
79 | 3 | 3-11 | 8622 | Phase B Voltage Crest Factor | CF_V_b_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | CF_Vb
80 | 3 | 3-12 | 8624 | Phase C Voltage Crest Factor | CF_V_c_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | CF_Vc
81 | 3 | 3-13 | 8626 | Phase A Current THD | THD_I_a_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | THD_Ia
82 | 3 | 3-14 | 8628 | Phase B Current THD | THD_I_b_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | THD_Ib
83 | 3 | 3-15 | 8630 | Phase C Current THD | THD_I_c_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | THD_Ic
84 | 3 | 3-16 | 8632 | Phase N Current THD | THD_I_n_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | THD_Inn
85 | 3 | 3-17 | 8634 | Phase A Current THD Odd | OTHD_I_a_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | OTHD_Ia
86 | 3 | 3-18 | 8636 | Phase B Current THD Odd | OTHD_I_b_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | OTHD_Ib
87 | 3 | 3-19 | 8638 | Phase C Current THD Odd | OTHD_I_c_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | OTHD_Ic
88 | 3 | 3-20 | 8640 | Phase N Current THD Odd | OTHD_I_n_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | OTHD_Inn
89 | 3 | 3-21 | 8642 | Phase A Current THD Even | ETHD_I_a_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | ETHD_Ia
90 | 3 | 3-22 | 8644 | Phase B Current THD Even | ETHD_I_b_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | ETHD_Ib
91 | 3 | 3-23 | 8646 | Phase C Current THD Even | ETHD_I_c_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | ETHD_Ic
92 | 3 | 3-24 | 8648 | Phase N Current THD Even | ETHD_I_n_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | ETHD_Inn
93 | 3 | 3-25 | 8650 | Phase A Current TDD | TDD_I_a_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | TDD_Ia
94 | 3 | 3-26 | 8652 | Phase B Current TDD | TDD_I_b_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | TDD_Ib
95 | 3 | 3-27 | 8654 | Phase C Current TDD | TDD_I_c_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | TDD_Ic
96 | 3 | 3-28 | 8656 | Phase N Current TDD | TDD_I_n_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | TDD_Inn
97 | 3 | 3-29 | 8658 | Phase A Current Crest-Factor | CF_I_a_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | CF_Ia
98 | 3 | 3-30 | 8660 | Phase B Current Crest-Factor | CF_I_b_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | CF_Ib
99 | 3 | 3-31 | 8662 | Phase C Current Crest-Factor | CF_I_c_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | CF_Ic
100 | 3 | 3-32 | 8664 | Phase N Current Crest-Factor | CF_I_n_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | CF_Inn
101 | 3 | 3-33 | 8666 | Phase A Current K-Factor | KF_I_a_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | KF_Ia
102 | 3 | 3-34 | 8668 | Phase B Current K-Factor | KF_I_b_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | KF_Ib
103 | 3 | 3-35 | 8670 | Phase C Current K-Factor | KF_I_c_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | KF_Ic
104 | 3 | 3-36 | 8672 | Phase N Current K-Factor | KF_I_n_% | % | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD | KF_Inn
105 | 3 | 3-37 | 8674 | Phase A Voltage Flicker | FLICK_V_a |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD
106 | 3 | 3-38 | 8676 | Phase B Voltage Flicker | FLICK_V_b |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD
107 | 3 | 3-39 | 8678 | Phase C Voltage Flicker | FLICK_V_c |  | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 8 | 11-12 | THD | THD | THD | THD | THD | THD | THD
108 | 4 | 4-1 | 24832 | Phase A Current Demand | DMD_I_a_A | A | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_Ia_A
109 | 4 | 4-2 | 24834 | Phase B Current Demand | DMD_I_b_A | A | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_Ib_A
110 | 4 | 4-3 | 24836 | Phase C Current Demand | DMD_I_c_A | A | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_Ic_A
111 | 4 | 4-4 | 24838 | Average Current Demand | DMD_I_avg_A | A | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_Iavg_A
112 | 5 | 5-1 | 24984 | Phase A Active Power Demand | DMD_P_a_kW | kW | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_TOTAL_Pa_kW
113 | 5 | 5-2 | 24986 | Phase B Active Power Demand | DMD_P_b_kW | kW | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_TOTAL_Pb_kW
114 | 5 | 5-3 | 24988 | Phase C Active Power Demand | DMD_P_c_kW | kW | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_TOTAL_Pc_kW
115 | 5 | 5-4 | 24990 | System Active Power Demand | DMD_P_kW | kW | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_TOTAL_P_kW
116 | 5 | 5-5 | 24992 | Phase A Reactive Power Demand | DMD_Q_a_kvar | kvar | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_TOTAL_Qa_kvar
117 | 5 | 5-6 | 24994 | Phase B Reactive Power Demand | DMD_Q_b_kvar | kvar | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_TOTAL_Qb_kvar
118 | 5 | 5-7 | 24996 | Phase C Reactive Power Demand | DMD_Q_c_kvar | kvar | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_TOTAL_Qc_kvar
119 | 5 | 5-8 | 24998 | System Reactive Power Demand | DMD_Q_kvar | kvar | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_TOTAL_Q_kvar
120 | 5 | 5-9 | 25000 | Phase A Apparent Power Demand | DMD_S_a_kVA | kVA | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_Sa_kVA
121 | 5 | 5-10 | 25002 | Phase B Apparent Power Demand | DMD_S_b_kVA | kVA | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_Sb_kVA
122 | 5 | 5-11 | 25004 | Phase C Apparent Power Demand | DMD_S_c_kVA | kVA | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_Sc_kVA
123 | 5 | 5-12 | 25006 | System Apparent Power Demand | DMD_S_kVA | kVA | float32 | 12 | R | 2 | 1 | 1 | [6 empty] | 6 | 11-12 | demand | demand | demand | demand | demand | demand | demand | DMD_S_kVA
124 | 6 | 6-1 | 26048 | Phase A Active Energy-Import | EP_IMP_a_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_IMPa_kWh
125 | 6 | 6-2 | 26052 | Phase B Active Energy-Import | EP_IMP_b_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_IMPb_kWh
126 | 6 | 6-3 | 26056 | Phase C Active Energy-Import | EP_IMP_c_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_IMPc_kWh
127 | 6 | 6-4 | 26060 | System Active Energy-Import | EP_IMP_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_IMP_kWh
128 | 6 | 6-5 | 26064 | Phase A Reactive Energy-Import | EQ_IMP_a_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_IMPa_kvarh
129 | 6 | 6-6 | 26068 | Phase B Reactive Energy-Import | EQ_IMP_b_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_IMPb_kvarh
130 | 6 | 6-7 | 26072 | Phase C Reactive Energy-Import | EQ_IMP_c_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_IMPc_kvarh
131 | 6 | 6-8 | 26076 | System Reactive Energy-Import | EQ_IMP_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_IMP_kvarh
132 | 6 | 6-9 | 26080 | Phase A Active Energy-Export | EP_EXP_a_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_EXPa_kWh
133 | 6 | 6-10 | 26084 | Phase B Active Energy-Export | EP_EXP_b_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_EXPb_kWh
134 | 6 | 6-11 | 26088 | Phase C Active Energy-Export | EP_EXP_c_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_EXPc_kWh
135 | 6 | 6-12 | 26092 | System Active Energy-Export | EP_EXP_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_EXP_kWh
136 | 6 | 6-13 | 26096 | Phase A Reactive Energy-Export | EQ_EXP_a_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_EXPa_kvarh
137 | 6 | 6-14 | 26100 | Phase B Reactive Energy-Export | EQ_EXP_b_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_EXPb_kvarh
138 | 6 | 6-15 | 26104 | Phase C Reactive Energy-Export | EQ_EXP_c_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_EXPc_kvarh
139 | 6 | 6-16 | 26108 | System Reactive Energy-Export | EQ_EXP_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_EXP_kvarh
140 | 6 | 6-17 | 26112 | Phase A Active Energy-Net | EP_NET_a_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_NETa_kWh
141 | 6 | 6-18 | 26116 | Phase B Active Energy-Net | EP_NET_b_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_NETb_kWh
142 | 6 | 6-19 | 26120 | Phase C Active Energy-Net | EP_NET_c_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_NETc_kWh
143 | 6 | 6-20 | 26124 | System Active Energy-Net | EP_NET_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_NET_kWh
144 | 6 | 6-21 | 26128 | Phase A Reactive Energy-Net | EQ_NET_a_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_NETa_kvarh
145 | 6 | 6-22 | 26132 | Phase B Reactive Energy-Net | EQ_NET_b_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_NETb_kvarh
146 | 6 | 6-23 | 26136 | Phase C Reactive Energy-Net | EQ_NET_c_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_NETc_kvarh
147 | 6 | 6-24 | 26140 | System Reactive Energy-Net | EQ_NET_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_NET_kvarh
148 | 7 | 7-1 | 26144 | Phase A Active Energy-Total | EP_TOTAL_a_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_TOTALa_kWh
149 | 7 | 7-2 | 26148 | Phase B Active Energy-Total | EP_TOTAL_b_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_TOTALb_kWh
150 | 7 | 7-3 | 26152 | Phase C Active Energy-Total | EP_TOTAL_c_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_TOTALc_kWh
151 | 7 | 7-4 | 26156 | System Active Energy-Total | EP_TOTAL_kWh | kWh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EP_TOTAL_kWh
152 | 7 | 7-5 | 26160 | Phase A Reactive Energy-Total | EQ_TOTAL_a_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_TOTALa_kvarh
153 | 7 | 7-6 | 26164 | Phase B Reactive Energy-Total | EQ_TOTAL_b_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_TOTALb_kvarh
154 | 7 | 7-7 | 26168 | Phase C Reactive Energy-Total | EQ_TOTAL_c_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_TOTALc_kvarh
155 | 7 | 7-8 | 26172 | System Reactive Energy-Total | EQ_TOTAL_kvarh | kvarh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_EQ_TOTAL_kvarh
156 | 7 | 7-9 | 26176 | Phase A Apparent Energy | ES_a_kVAh | kVAh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_ESa_kVAh
157 | 7 | 7-10 | 26180 | Phase B Apparent Energy | ES_b_kVAh | kVAh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_ESb_kVAh
158 | 7 | 7-11 | 26184 | Phase C Apparent Energy | ES_c_kVAh | kVAh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_ESc_kVAh
159 | 7 | 7-12 | 26188 | System Apparent Energy | ES_kVAh | kVAh | double |  | R | 4 | 1 | 1 | 1 |  | 3 | 4 |  |  | 7 | 11 |  | energy | energy | energy |  | energy | energy | ACCUM_ES_kVAh

## analysisUnits
analysisUnitId | analysisUnitTypeName
1 | threePhaseMeterAnalysis

## analysisParams
threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis
three_phase_realtime | three_phase_energy_demand | three_phase_thd | three_phase_harmonics | three_phase_sequence
VLN_a_V | EP_IMP_a_kWh | THD_V_a_% | HAR2_V_a_% | SEQ_POS_REAL_I
ANG_VLN_a | EQ_IMP_a_kvarh | OTHD_V_a_% | HAR3_V_a_% | SEQ_NEG_REAL_I
VLL_ab_V | EP_EXP_a_kWh | ETHD_V_a_% | HAR4_V_a_% | SEQ_ZERO_REAL_I
ANG_VLL_ab | EQ_EXP_a_kvarh | CF_V_a_% | HAR5_V_a_% | SEQ_POS_IMG_I
I_a_A | EP_NET_a_kWh | THD_I_a_% | HAR6_V_a_% | SEQ_NEG_IMG_I
ANG_I_a | EQ_NET_a_kvarh | OTHD_I_a_% | HAR7_V_a_% | SEQ_ZERO_IMG_I
P_a_kW | EP_TOTAL_a_kWh | ETHD_I_a_% | HAR8_V_a_% | SEQ_POS_REAL_V
Q_a_kvar | EQ_TOTAL_a_kvarh | TDD_I_a_% | HAR9_V_a_% | SEQ_NEG_REAL_V
S_a_kVA | ES_a_kVAh | CF_I_a_% | HAR10_V_a_% | SEQ_ZERO_REAL_V
LC_a | EP_IMP_b_kWh | KF_I_a_% | HAR11_V_a_% | SEQ_POS_IMG_V
PF_a | EQ_IMP_b_kvarh | THD_V_b_% | HAR12_V_a_% | SEQ_NEG_IMG_V
LEAD_PF_a | EP_EXP_b_kWh | OTHD_V_b_% | HAR13_V_a_% | SEQ_ZERO_IMG_V
LAG_PF_a | EQ_EXP_b_kvarh | ETHD_V_b_% | HAR14_V_a_% | UNBL_V_%
VLN_b_V | EP_NET_b_kWh | CF_V_b_% | HAR15_V_a_% | UNBL_I_%
ANG_VLN_b | EQ_NET_b_kvarh | THD_I_b_% | HAR16_V_a_% | SEQ_ZERO_RATIO_V_%
VLL_bc_V | EP_TOTAL_b_kWh | OTHD_I_b_% | HAR17_V_a_% | SEQ_ZERO_RATIO_I_%
ANG_VLL_bb | EQ_TOTAL_b_kvarh | ETHD_I_b_% | HAR18_V_a_%
I_b_A | ES_b_kVAh | TDD_I_b_% | HAR19_V_a_%
ANG_I_b | EP_IMP_c_kWh | CF_I_b_% | HAR20_V_a_%
P_b_kW | EQ_IMP_c_kvarh | KF_I_b_% | HAR21_V_a_%
Q_b_kvar | EP_EXP_c_kWh | THD_V_c_% | HAR22_V_a_%
S_b_kVA | EQ_EXP_c_kvarh | OTHD_V_c_% | HAR23_V_a_%
LC_b | EP_NET_c_kWh | ETHD_V_c_% | HAR24_V_a_%
PF_b | EQ_NET_c_kvarh | CF_V_c_% | HAR25_V_a_%
LEAD_PF_b | EP_TOTAL_c_kWh | THD_I_c_% | HAR26_V_a_%
LAG_PF_b | EQ_TOTAL_c_kvarh | OTHD_I_c_% | HAR27_V_a_%
VLN_c_V | ES_c_kVAh | ETHD_I_c_% | HAR28_V_a_%
ANG_VLN_c | EP_IMP_kWh | TDD_I_c_% | HAR29_V_a_%
VLL_ca_V | EQ_IMP_kvarh | CF_I_c_% | HAR30_V_a_%
ANG_VLL_cb | EP_EXP_kWh | KF_I_c_% | HAR31_V_a_%
I_c_A | EQ_EXP_kvarh | THD_V_avg_% | HAR32_V_a_%
ANG_I_c | EP_NET_kWh | OTHD_V_avg_% | HAR33_V_a_%
P_c_kW | EQ_NET_kvarh | ETHD_V_avg_% | HAR34_V_a_%
Q_c_kvar | EP_TOTAL_kWh | CF_V_avg_% | HAR35_V_a_%
S_c_kVA | EQ_TOTAL_kvarh | THD_I_avg_% | HAR36_V_a_%
LC_c | ES_kVAh | OTHD_I_avg_% | HAR37_V_a_%
PF_c | DMD_P_a_kW | ETHD_I_avg_% | HAR38_V_a_%
LEAD_PF_c | DMD_Q_a_kvar | TDD_I_avg_% | HAR39_V_a_%
LAG_PF_c | DMD_S_a_kVA | CF_I_avg_% | HAR40_V_a_%
VLN_avg_V | DMD_P_b_kW | KF_I_avg_% | HAR41_V_a_%
VLL_avg_V | DMD_Q_b_kvar |  | HAR42_V_a_%
I_avg_A | DMD_S_b_kVA |  | HAR43_V_a_%
LC_avg | DMD_P_c_kW |  | HAR44_V_a_%
I_n_A | DMD_Q_c_kvar |  | HAR45_V_a_%
P_kW | DMD_S_c_kVA |  | HAR46_V_a_%
Q_kvar | DMD_P_kW |  | HAR47_V_a_%
S_kVA | DMD_Q_kvar |  | HAR48_V_a_%
PF | DMD_S_kVA |  | HAR49_V_a_%
LEAD_PF |  |  | HAR50_V_a_%
LAG_PF |  |  | HAR51_V_a_%
FREQ_Hz |  |  | HAR52_V_a_%
HAR53_V_a_%
HAR54_V_a_%
HAR55_V_a_%
HAR56_V_a_%
HAR57_V_a_%
HAR58_V_a_%
HAR59_V_a_%
HAR60_V_a_%
HAR61_V_a_%
HAR62_V_a_%
HAR63_V_a_%
HAR64_V_a_%
HAR65_V_a_%
HAR66_V_a_%
HAR67_V_a_%
HAR68_V_a_%
HAR69_V_a_%
HAR70_V_a_%
HAR71_V_a_%
HAR72_V_a_%
HAR73_V_a_%
HAR74_V_a_%
HAR75_V_a_%
HAR76_V_a_%
HAR77_V_a_%
HAR78_V_a_%
HAR79_V_a_%
HAR80_V_a_%
HAR81_V_a_%
HAR82_V_a_%
HAR83_V_a_%
HAR84_V_a_%
HAR85_V_a_%
HAR86_V_a_%
HAR87_V_a_%
HAR88_V_a_%
HAR89_V_a_%
HAR90_V_a_%
HAR91_V_a_%
HAR92_V_a_%
HAR93_V_a_%
HAR94_V_a_%
HAR95_V_a_%
HAR96_V_a_%
HAR97_V_a_%
HAR98_V_a_%
HAR99_V_a_%
HAR100_V_a_%
HAR101_V_a_%
HAR102_V_a_%
HAR103_V_a_%
HAR104_V_a_%
HAR105_V_a_%
HAR106_V_a_%
HAR107_V_a_%
HAR108_V_a_%
HAR109_V_a_%
HAR110_V_a_%
HAR111_V_a_%
HAR112_V_a_%
HAR113_V_a_%
HAR114_V_a_%
HAR115_V_a_%
HAR116_V_a_%
HAR117_V_a_%
HAR118_V_a_%
HAR119_V_a_%
HAR120_V_a_%
HAR121_V_a_%
HAR122_V_a_%
HAR123_V_a_%
HAR124_V_a_%
HAR125_V_a_%
HAR126_V_a_%
HAR127_V_a_%
ANG_HAR2_V_a
ANG_HAR3_V_a
ANG_HAR4_V_a
ANG_HAR5_V_a
ANG_HAR6_V_a
ANG_HAR7_V_a
ANG_HAR8_V_a
ANG_HAR9_V_a
ANG_HAR10_V_a
ANG_HAR11_V_a
ANG_HAR12_V_a
ANG_HAR13_V_a
ANG_HAR14_V_a
ANG_HAR15_V_a
ANG_HAR16_V_a
ANG_HAR17_V_a
ANG_HAR18_V_a
ANG_HAR19_V_a
ANG_HAR20_V_a
ANG_HAR21_V_a
ANG_HAR22_V_a
ANG_HAR23_V_a
ANG_HAR24_V_a
ANG_HAR25_V_a
ANG_HAR26_V_a
ANG_HAR27_V_a
ANG_HAR28_V_a
ANG_HAR29_V_a
ANG_HAR30_V_a
ANG_HAR31_V_a
ANG_HAR32_V_a
ANG_HAR33_V_a
ANG_HAR34_V_a
ANG_HAR35_V_a
ANG_HAR36_V_a
ANG_HAR37_V_a
ANG_HAR38_V_a
ANG_HAR39_V_a
ANG_HAR40_V_a
ANG_HAR41_V_a
ANG_HAR42_V_a
ANG_HAR43_V_a
ANG_HAR44_V_a
ANG_HAR45_V_a
ANG_HAR46_V_a
ANG_HAR47_V_a
ANG_HAR48_V_a
ANG_HAR49_V_a
ANG_HAR50_V_a
ANG_HAR51_V_a
ANG_HAR52_V_a
ANG_HAR53_V_a
ANG_HAR54_V_a
ANG_HAR55_V_a
ANG_HAR56_V_a
ANG_HAR57_V_a
ANG_HAR58_V_a
ANG_HAR59_V_a
ANG_HAR60_V_a
ANG_HAR61_V_a
ANG_HAR62_V_a
ANG_HAR63_V_a
ANG_HAR64_V_a
ANG_HAR65_V_a
ANG_HAR66_V_a
ANG_HAR67_V_a
ANG_HAR68_V_a
ANG_HAR69_V_a
ANG_HAR70_V_a
ANG_HAR71_V_a
ANG_HAR72_V_a
ANG_HAR73_V_a
ANG_HAR74_V_a
ANG_HAR75_V_a
ANG_HAR76_V_a
ANG_HAR77_V_a
ANG_HAR78_V_a
ANG_HAR79_V_a
ANG_HAR80_V_a
ANG_HAR81_V_a
ANG_HAR82_V_a
ANG_HAR83_V_a
ANG_HAR84_V_a
ANG_HAR85_V_a
ANG_HAR86_V_a
ANG_HAR87_V_a
ANG_HAR88_V_a
ANG_HAR89_V_a
ANG_HAR90_V_a
ANG_HAR91_V_a
ANG_HAR92_V_a
ANG_HAR93_V_a
ANG_HAR94_V_a
ANG_HAR95_V_a
ANG_HAR96_V_a
ANG_HAR97_V_a
ANG_HAR98_V_a
ANG_HAR99_V_a
ANG_HAR100_V_a
ANG_HAR101_V_a
ANG_HAR102_V_a
ANG_HAR103_V_a
ANG_HAR104_V_a
ANG_HAR105_V_a
ANG_HAR106_V_a
ANG_HAR107_V_a
ANG_HAR108_V_a
ANG_HAR109_V_a
ANG_HAR110_V_a
ANG_HAR111_V_a
ANG_HAR112_V_a
ANG_HAR113_V_a
ANG_HAR114_V_a
ANG_HAR115_V_a
ANG_HAR116_V_a
ANG_HAR117_V_a
ANG_HAR118_V_a
ANG_HAR119_V_a
ANG_HAR120_V_a
ANG_HAR121_V_a
ANG_HAR122_V_a
ANG_HAR123_V_a
ANG_HAR124_V_a
ANG_HAR125_V_a
ANG_HAR126_V_a
ANG_HAR127_V_a
HAR2_V_b_%
HAR3_V_b_%
HAR4_V_b_%
HAR5_V_b_%
HAR6_V_b_%
HAR7_V_b_%
HAR8_V_b_%
HAR9_V_b_%
HAR10_V_b_%
HAR11_V_b_%
HAR12_V_b_%
HAR13_V_b_%
HAR14_V_b_%
HAR15_V_b_%
HAR16_V_b_%
HAR17_V_b_%
HAR18_V_b_%
HAR19_V_b_%
HAR20_V_b_%
HAR21_V_b_%
HAR22_V_b_%
HAR23_V_b_%
HAR24_V_b_%
HAR25_V_b_%
HAR26_V_b_%
HAR27_V_b_%
HAR28_V_b_%
HAR29_V_b_%
HAR30_V_b_%
HAR31_V_b_%
HAR32_V_b_%
HAR33_V_b_%
HAR34_V_b_%
HAR35_V_b_%
HAR36_V_b_%
HAR37_V_b_%
HAR38_V_b_%
HAR39_V_b_%
HAR40_V_b_%
HAR41_V_b_%
HAR42_V_b_%
HAR43_V_b_%
HAR44_V_b_%
HAR45_V_b_%
HAR46_V_b_%
HAR47_V_b_%
HAR48_V_b_%
HAR49_V_b_%
HAR50_V_b_%
HAR51_V_b_%
HAR52_V_b_%
HAR53_V_b_%
HAR54_V_b_%
HAR55_V_b_%
HAR56_V_b_%
HAR57_V_b_%
HAR58_V_b_%
HAR59_V_b_%
HAR60_V_b_%
HAR61_V_b_%
HAR62_V_b_%
HAR63_V_b_%
HAR64_V_b_%
HAR65_V_b_%
HAR66_V_b_%
HAR67_V_b_%
HAR68_V_b_%
HAR69_V_b_%
HAR70_V_b_%
HAR71_V_b_%
HAR72_V_b_%
HAR73_V_b_%
HAR74_V_b_%
HAR75_V_b_%
HAR76_V_b_%
HAR77_V_b_%
HAR78_V_b_%
HAR79_V_b_%
HAR80_V_b_%
HAR81_V_b_%
HAR82_V_b_%
HAR83_V_b_%
HAR84_V_b_%
HAR85_V_b_%
HAR86_V_b_%
HAR87_V_b_%
HAR88_V_b_%
HAR89_V_b_%
HAR90_V_b_%
HAR91_V_b_%
HAR92_V_b_%
HAR93_V_b_%
HAR94_V_b_%
HAR95_V_b_%
HAR96_V_b_%
HAR97_V_b_%
HAR98_V_b_%
HAR99_V_b_%
HAR100_V_b_%
HAR101_V_b_%
HAR102_V_b_%
HAR103_V_b_%
HAR104_V_b_%
HAR105_V_b_%
HAR106_V_b_%
HAR107_V_b_%
HAR108_V_b_%
HAR109_V_b_%
HAR110_V_b_%
HAR111_V_b_%
HAR112_V_b_%
HAR113_V_b_%
HAR114_V_b_%
HAR115_V_b_%
HAR116_V_b_%
HAR117_V_b_%
HAR118_V_b_%
HAR119_V_b_%
HAR120_V_b_%
HAR121_V_b_%
HAR122_V_b_%
HAR123_V_b_%
HAR124_V_b_%
HAR125_V_b_%
HAR126_V_b_%
HAR127_V_b_%
ANG_HAR2_V_b
ANG_HAR3_V_b
ANG_HAR4_V_b
ANG_HAR5_V_b
ANG_HAR6_V_b
ANG_HAR7_V_b
ANG_HAR8_V_b
ANG_HAR9_V_b
ANG_HAR10_V_b
ANG_HAR11_V_b
ANG_HAR12_V_b
ANG_HAR13_V_b
ANG_HAR14_V_b
ANG_HAR15_V_b
ANG_HAR16_V_b
ANG_HAR17_V_b
ANG_HAR18_V_b
ANG_HAR19_V_b
ANG_HAR20_V_b
ANG_HAR21_V_b
ANG_HAR22_V_b
ANG_HAR23_V_b
ANG_HAR24_V_b
ANG_HAR25_V_b
ANG_HAR26_V_b
ANG_HAR27_V_b
ANG_HAR28_V_b
ANG_HAR29_V_b
ANG_HAR30_V_b
ANG_HAR31_V_b
ANG_HAR32_V_b
ANG_HAR33_V_b
ANG_HAR34_V_b
ANG_HAR35_V_b
ANG_HAR36_V_b
ANG_HAR37_V_b
ANG_HAR38_V_b
ANG_HAR39_V_b
ANG_HAR40_V_b
ANG_HAR41_V_b
ANG_HAR42_V_b
ANG_HAR43_V_b
ANG_HAR44_V_b
ANG_HAR45_V_b
ANG_HAR46_V_b
ANG_HAR47_V_b
ANG_HAR48_V_b
ANG_HAR49_V_b
ANG_HAR50_V_b
ANG_HAR51_V_b
ANG_HAR52_V_b
ANG_HAR53_V_b
ANG_HAR54_V_b
ANG_HAR55_V_b
ANG_HAR56_V_b
ANG_HAR57_V_b
ANG_HAR58_V_b
ANG_HAR59_V_b
ANG_HAR60_V_b
ANG_HAR61_V_b
ANG_HAR62_V_b
ANG_HAR63_V_b
ANG_HAR64_V_b
ANG_HAR65_V_b
ANG_HAR66_V_b
ANG_HAR67_V_b
ANG_HAR68_V_b
ANG_HAR69_V_b
ANG_HAR70_V_b
ANG_HAR71_V_b
ANG_HAR72_V_b
ANG_HAR73_V_b
ANG_HAR74_V_b
ANG_HAR75_V_b
ANG_HAR76_V_b
ANG_HAR77_V_b
ANG_HAR78_V_b
ANG_HAR79_V_b
ANG_HAR80_V_b
ANG_HAR81_V_b
ANG_HAR82_V_b
ANG_HAR83_V_b
ANG_HAR84_V_b
ANG_HAR85_V_b
ANG_HAR86_V_b
ANG_HAR87_V_b
ANG_HAR88_V_b
ANG_HAR89_V_b
ANG_HAR90_V_b
ANG_HAR91_V_b
ANG_HAR92_V_b
ANG_HAR93_V_b
ANG_HAR94_V_b
ANG_HAR95_V_b
ANG_HAR96_V_b
ANG_HAR97_V_b
ANG_HAR98_V_b
ANG_HAR99_V_b
ANG_HAR100_V_b
ANG_HAR101_V_b
ANG_HAR102_V_b
ANG_HAR103_V_b
ANG_HAR104_V_b
ANG_HAR105_V_b
ANG_HAR106_V_b
ANG_HAR107_V_b
ANG_HAR108_V_b
ANG_HAR109_V_b
ANG_HAR110_V_b
ANG_HAR111_V_b
ANG_HAR112_V_b
ANG_HAR113_V_b
ANG_HAR114_V_b
ANG_HAR115_V_b
ANG_HAR116_V_b
ANG_HAR117_V_b
ANG_HAR118_V_b
ANG_HAR119_V_b
ANG_HAR120_V_b
ANG_HAR121_V_b
ANG_HAR122_V_b
ANG_HAR123_V_b
ANG_HAR124_V_b
ANG_HAR125_V_b
ANG_HAR126_V_b
ANG_HAR127_V_b
HAR2_V_c_%
HAR3_V_c_%
HAR4_V_c_%
HAR5_V_c_%
HAR6_V_c_%
HAR7_V_c_%
HAR8_V_c_%
HAR9_V_c_%
HAR10_V_c_%
HAR11_V_c_%
HAR12_V_c_%
HAR13_V_c_%
HAR14_V_c_%
HAR15_V_c_%
HAR16_V_c_%
HAR17_V_c_%
HAR18_V_c_%
HAR19_V_c_%
HAR20_V_c_%
HAR21_V_c_%
HAR22_V_c_%
HAR23_V_c_%
HAR24_V_c_%
HAR25_V_c_%
HAR26_V_c_%
HAR27_V_c_%
HAR28_V_c_%
HAR29_V_c_%
HAR30_V_c_%
HAR31_V_c_%
HAR32_V_c_%
HAR33_V_c_%
HAR34_V_c_%
HAR35_V_c_%
HAR36_V_c_%
HAR37_V_c_%
HAR38_V_c_%
HAR39_V_c_%
HAR40_V_c_%
HAR41_V_c_%
HAR42_V_c_%
HAR43_V_c_%
HAR44_V_c_%
HAR45_V_c_%
HAR46_V_c_%
HAR47_V_c_%
HAR48_V_c_%
HAR49_V_c_%
HAR50_V_c_%
HAR51_V_c_%
HAR52_V_c_%
HAR53_V_c_%
HAR54_V_c_%
HAR55_V_c_%
HAR56_V_c_%
HAR57_V_c_%
HAR58_V_c_%
HAR59_V_c_%
HAR60_V_c_%
HAR61_V_c_%
HAR62_V_c_%
HAR63_V_c_%
HAR64_V_c_%
HAR65_V_c_%
HAR66_V_c_%
HAR67_V_c_%
HAR68_V_c_%
HAR69_V_c_%
HAR70_V_c_%
HAR71_V_c_%
HAR72_V_c_%
HAR73_V_c_%
HAR74_V_c_%
HAR75_V_c_%
HAR76_V_c_%
HAR77_V_c_%
HAR78_V_c_%
HAR79_V_c_%
HAR80_V_c_%
HAR81_V_c_%
HAR82_V_c_%
HAR83_V_c_%
HAR84_V_c_%
HAR85_V_c_%
HAR86_V_c_%
HAR87_V_c_%
HAR88_V_c_%
HAR89_V_c_%
HAR90_V_c_%
HAR91_V_c_%
HAR92_V_c_%
HAR93_V_c_%
HAR94_V_c_%
HAR95_V_c_%
HAR96_V_c_%
HAR97_V_c_%
HAR98_V_c_%
HAR99_V_c_%
HAR100_V_c_%
HAR101_V_c_%
HAR102_V_c_%
HAR103_V_c_%
HAR104_V_c_%
HAR105_V_c_%
HAR106_V_c_%
HAR107_V_c_%
HAR108_V_c_%
HAR109_V_c_%
HAR110_V_c_%
HAR111_V_c_%
HAR112_V_c_%
HAR113_V_c_%
HAR114_V_c_%
HAR115_V_c_%
HAR116_V_c_%
HAR117_V_c_%
HAR118_V_c_%
HAR119_V_c_%
HAR120_V_c_%
HAR121_V_c_%
HAR122_V_c_%
HAR123_V_c_%
HAR124_V_c_%
HAR125_V_c_%
HAR126_V_c_%
HAR127_V_c_%
ANG_HAR2_V_c
ANG_HAR3_V_c
ANG_HAR4_V_c
ANG_HAR5_V_c
ANG_HAR6_V_c
ANG_HAR7_V_c
ANG_HAR8_V_c
ANG_HAR9_V_c
ANG_HAR10_V_c
ANG_HAR11_V_c
ANG_HAR12_V_c
ANG_HAR13_V_c
ANG_HAR14_V_c
ANG_HAR15_V_c
ANG_HAR16_V_c
ANG_HAR17_V_c
ANG_HAR18_V_c
ANG_HAR19_V_c
ANG_HAR20_V_c
ANG_HAR21_V_c
ANG_HAR22_V_c
ANG_HAR23_V_c
ANG_HAR24_V_c
ANG_HAR25_V_c
ANG_HAR26_V_c
ANG_HAR27_V_c
ANG_HAR28_V_c
ANG_HAR29_V_c
ANG_HAR30_V_c
ANG_HAR31_V_c
ANG_HAR32_V_c
ANG_HAR33_V_c
ANG_HAR34_V_c
ANG_HAR35_V_c
ANG_HAR36_V_c
ANG_HAR37_V_c
ANG_HAR38_V_c
ANG_HAR39_V_c
ANG_HAR40_V_c
ANG_HAR41_V_c
ANG_HAR42_V_c
ANG_HAR43_V_c
ANG_HAR44_V_c
ANG_HAR45_V_c
ANG_HAR46_V_c
ANG_HAR47_V_c
ANG_HAR48_V_c
ANG_HAR49_V_c
ANG_HAR50_V_c
ANG_HAR51_V_c
ANG_HAR52_V_c
ANG_HAR53_V_c
ANG_HAR54_V_c
ANG_HAR55_V_c
ANG_HAR56_V_c
ANG_HAR57_V_c
ANG_HAR58_V_c
ANG_HAR59_V_c
ANG_HAR60_V_c
ANG_HAR61_V_c
ANG_HAR62_V_c
ANG_HAR63_V_c
ANG_HAR64_V_c
ANG_HAR65_V_c
ANG_HAR66_V_c
ANG_HAR67_V_c
ANG_HAR68_V_c
ANG_HAR69_V_c
ANG_HAR70_V_c
ANG_HAR71_V_c
ANG_HAR72_V_c
ANG_HAR73_V_c
ANG_HAR74_V_c
ANG_HAR75_V_c
ANG_HAR76_V_c
ANG_HAR77_V_c
ANG_HAR78_V_c
ANG_HAR79_V_c
ANG_HAR80_V_c
ANG_HAR81_V_c
ANG_HAR82_V_c
ANG_HAR83_V_c
ANG_HAR84_V_c
ANG_HAR85_V_c
ANG_HAR86_V_c
ANG_HAR87_V_c
ANG_HAR88_V_c
ANG_HAR89_V_c
ANG_HAR90_V_c
ANG_HAR91_V_c
ANG_HAR92_V_c
ANG_HAR93_V_c
ANG_HAR94_V_c
ANG_HAR95_V_c
ANG_HAR96_V_c
ANG_HAR97_V_c
ANG_HAR98_V_c
ANG_HAR99_V_c
ANG_HAR100_V_c
ANG_HAR101_V_c
ANG_HAR102_V_c
ANG_HAR103_V_c
ANG_HAR104_V_c
ANG_HAR105_V_c
ANG_HAR106_V_c
ANG_HAR107_V_c
ANG_HAR108_V_c
ANG_HAR109_V_c
ANG_HAR110_V_c
ANG_HAR111_V_c
ANG_HAR112_V_c
ANG_HAR113_V_c
ANG_HAR114_V_c
ANG_HAR115_V_c
ANG_HAR116_V_c
ANG_HAR117_V_c
ANG_HAR118_V_c
ANG_HAR119_V_c
ANG_HAR120_V_c
ANG_HAR121_V_c
ANG_HAR122_V_c
ANG_HAR123_V_c
ANG_HAR124_V_c
ANG_HAR125_V_c
ANG_HAR126_V_c
ANG_HAR127_V_c
HAR2_I_a_%
HAR3_I_a_%
HAR4_I_a_%
HAR5_I_a_%
HAR6_I_a_%
HAR7_I_a_%
HAR8_I_a_%
HAR9_I_a_%
HAR10_I_a_%
HAR11_I_a_%
HAR12_I_a_%
HAR13_I_a_%
HAR14_I_a_%
HAR15_I_a_%
HAR16_I_a_%
HAR17_I_a_%
HAR18_I_a_%
HAR19_I_a_%
HAR20_I_a_%
HAR21_I_a_%
HAR22_I_a_%
HAR23_I_a_%
HAR24_I_a_%
HAR25_I_a_%
HAR26_I_a_%
HAR27_I_a_%
HAR28_I_a_%
HAR29_I_a_%
HAR30_I_a_%
HAR31_I_a_%
HAR32_I_a_%
HAR33_I_a_%
HAR34_I_a_%
HAR35_I_a_%
HAR36_I_a_%
HAR37_I_a_%
HAR38_I_a_%
HAR39_I_a_%
HAR40_I_a_%
HAR41_I_a_%
HAR42_I_a_%
HAR43_I_a_%
HAR44_I_a_%
HAR45_I_a_%
HAR46_I_a_%
HAR47_I_a_%
HAR48_I_a_%
HAR49_I_a_%
HAR50_I_a_%
HAR51_I_a_%
HAR52_I_a_%
HAR53_I_a_%
HAR54_I_a_%
HAR55_I_a_%
HAR56_I_a_%
HAR57_I_a_%
HAR58_I_a_%
HAR59_I_a_%
HAR60_I_a_%
HAR61_I_a_%
HAR62_I_a_%
HAR63_I_a_%
HAR64_I_a_%
HAR65_I_a_%
HAR66_I_a_%
HAR67_I_a_%
HAR68_I_a_%
HAR69_I_a_%
HAR70_I_a_%
HAR71_I_a_%
HAR72_I_a_%
HAR73_I_a_%
HAR74_I_a_%
HAR75_I_a_%
HAR76_I_a_%
HAR77_I_a_%
HAR78_I_a_%
HAR79_I_a_%
HAR80_I_a_%
HAR81_I_a_%
HAR82_I_a_%
HAR83_I_a_%
HAR84_I_a_%
HAR85_I_a_%
HAR86_I_a_%
HAR87_I_a_%
HAR88_I_a_%
HAR89_I_a_%
HAR90_I_a_%
HAR91_I_a_%
HAR92_I_a_%
HAR93_I_a_%
HAR94_I_a_%
HAR95_I_a_%
HAR96_I_a_%
HAR97_I_a_%
HAR98_I_a_%
HAR99_I_a_%
HAR100_I_a_%
HAR101_I_a_%
HAR102_I_a_%
HAR103_I_a_%
HAR104_I_a_%
HAR105_I_a_%
HAR106_I_a_%
HAR107_I_a_%
HAR108_I_a_%
HAR109_I_a_%
HAR110_I_a_%
HAR111_I_a_%
HAR112_I_a_%
HAR113_I_a_%
HAR114_I_a_%
HAR115_I_a_%
HAR116_I_a_%
HAR117_I_a_%
HAR118_I_a_%
HAR119_I_a_%
HAR120_I_a_%
HAR121_I_a_%
HAR122_I_a_%
HAR123_I_a_%
HAR124_I_a_%
HAR125_I_a_%
HAR126_I_a_%
HAR127_I_a_%
ANG_HAR2_I_a
ANG_HAR3_I_a
ANG_HAR4_I_a
ANG_HAR5_I_a
ANG_HAR6_I_a
ANG_HAR7_I_a
ANG_HAR8_I_a
ANG_HAR9_I_a
ANG_HAR10_I_a
ANG_HAR11_I_a
ANG_HAR12_I_a
ANG_HAR13_I_a
ANG_HAR14_I_a
ANG_HAR15_I_a
ANG_HAR16_I_a
ANG_HAR17_I_a
ANG_HAR18_I_a
ANG_HAR19_I_a
ANG_HAR20_I_a
ANG_HAR21_I_a
ANG_HAR22_I_a
ANG_HAR23_I_a
ANG_HAR24_I_a
ANG_HAR25_I_a
ANG_HAR26_I_a
ANG_HAR27_I_a
ANG_HAR28_I_a
ANG_HAR29_I_a
ANG_HAR30_I_a
ANG_HAR31_I_a
ANG_HAR32_I_a
ANG_HAR33_I_a
ANG_HAR34_I_a
ANG_HAR35_I_a
ANG_HAR36_I_a
ANG_HAR37_I_a
ANG_HAR38_I_a
ANG_HAR39_I_a
ANG_HAR40_I_a
ANG_HAR41_I_a
ANG_HAR42_I_a
ANG_HAR43_I_a
ANG_HAR44_I_a
ANG_HAR45_I_a
ANG_HAR46_I_a
ANG_HAR47_I_a
ANG_HAR48_I_a
ANG_HAR49_I_a
ANG_HAR50_I_a
ANG_HAR51_I_a
ANG_HAR52_I_a
ANG_HAR53_I_a
ANG_HAR54_I_a
ANG_HAR55_I_a
ANG_HAR56_I_a
ANG_HAR57_I_a
ANG_HAR58_I_a
ANG_HAR59_I_a
ANG_HAR60_I_a
ANG_HAR61_I_a
ANG_HAR62_I_a
ANG_HAR63_I_a
ANG_HAR64_I_a
ANG_HAR65_I_a
ANG_HAR66_I_a
ANG_HAR67_I_a
ANG_HAR68_I_a
ANG_HAR69_I_a
ANG_HAR70_I_a
ANG_HAR71_I_a
ANG_HAR72_I_a
ANG_HAR73_I_a
ANG_HAR74_I_a
ANG_HAR75_I_a
ANG_HAR76_I_a
ANG_HAR77_I_a
ANG_HAR78_I_a
ANG_HAR79_I_a
ANG_HAR80_I_a
ANG_HAR81_I_a
ANG_HAR82_I_a
ANG_HAR83_I_a
ANG_HAR84_I_a
ANG_HAR85_I_a
ANG_HAR86_I_a
ANG_HAR87_I_a
ANG_HAR88_I_a
ANG_HAR89_I_a
ANG_HAR90_I_a
ANG_HAR91_I_a
ANG_HAR92_I_a
ANG_HAR93_I_a
ANG_HAR94_I_a
ANG_HAR95_I_a
ANG_HAR96_I_a
ANG_HAR97_I_a
ANG_HAR98_I_a
ANG_HAR99_I_a
ANG_HAR100_I_a
ANG_HAR101_I_a
ANG_HAR102_I_a
ANG_HAR103_I_a
ANG_HAR104_I_a
ANG_HAR105_I_a
ANG_HAR106_I_a
ANG_HAR107_I_a
ANG_HAR108_I_a
ANG_HAR109_I_a
ANG_HAR110_I_a
ANG_HAR111_I_a
ANG_HAR112_I_a
ANG_HAR113_I_a
ANG_HAR114_I_a
ANG_HAR115_I_a
ANG_HAR116_I_a
ANG_HAR117_I_a
ANG_HAR118_I_a
ANG_HAR119_I_a
ANG_HAR120_I_a
ANG_HAR121_I_a
ANG_HAR122_I_a
ANG_HAR123_I_a
ANG_HAR124_I_a
ANG_HAR125_I_a
ANG_HAR126_I_a
ANG_HAR127_I_a
ANG_HAR128_I_a
HAR2_I_b_%
HAR3_I_b_%
HAR4_I_b_%
HAR5_I_b_%
HAR6_I_b_%
HAR7_I_b_%
HAR8_I_b_%
HAR9_I_b_%
HAR10_I_b_%
HAR11_I_b_%
HAR12_I_b_%
HAR13_I_b_%
HAR14_I_b_%
HAR15_I_b_%
HAR16_I_b_%
HAR17_I_b_%
HAR18_I_b_%
HAR19_I_b_%
HAR20_I_b_%
HAR21_I_b_%
HAR22_I_b_%
HAR23_I_b_%
HAR24_I_b_%
HAR25_I_b_%
HAR26_I_b_%
HAR27_I_b_%
HAR28_I_b_%
HAR29_I_b_%
HAR30_I_b_%
HAR31_I_b_%
HAR32_I_b_%
HAR33_I_b_%
HAR34_I_b_%
HAR35_I_b_%
HAR36_I_b_%
HAR37_I_b_%
HAR38_I_b_%
HAR39_I_b_%
HAR40_I_b_%
HAR41_I_b_%
HAR42_I_b_%
HAR43_I_b_%
HAR44_I_b_%
HAR45_I_b_%
HAR46_I_b_%
HAR47_I_b_%
HAR48_I_b_%
HAR49_I_b_%
HAR50_I_b_%
HAR51_I_b_%
HAR52_I_b_%
HAR53_I_b_%
HAR54_I_b_%
HAR55_I_b_%
HAR56_I_b_%
HAR57_I_b_%
HAR58_I_b_%
HAR59_I_b_%
HAR60_I_b_%
HAR61_I_b_%
HAR62_I_b_%
HAR63_I_b_%
HAR64_I_b_%
HAR65_I_b_%
HAR66_I_b_%
HAR67_I_b_%
HAR68_I_b_%
HAR69_I_b_%
HAR70_I_b_%
HAR71_I_b_%
HAR72_I_b_%
HAR73_I_b_%
HAR74_I_b_%
HAR75_I_b_%
HAR76_I_b_%
HAR77_I_b_%
HAR78_I_b_%
HAR79_I_b_%
HAR80_I_b_%
HAR81_I_b_%
HAR82_I_b_%
HAR83_I_b_%
HAR84_I_b_%
HAR85_I_b_%
HAR86_I_b_%
HAR87_I_b_%
HAR88_I_b_%
HAR89_I_b_%
HAR90_I_b_%
HAR91_I_b_%
HAR92_I_b_%
HAR93_I_b_%
HAR94_I_b_%
HAR95_I_b_%
HAR96_I_b_%
HAR97_I_b_%
HAR98_I_b_%
HAR99_I_b_%
HAR100_I_b_%
HAR101_I_b_%
HAR102_I_b_%
HAR103_I_b_%
HAR104_I_b_%
HAR105_I_b_%
HAR106_I_b_%
HAR107_I_b_%
HAR108_I_b_%
HAR109_I_b_%
HAR110_I_b_%
HAR111_I_b_%
HAR112_I_b_%
HAR113_I_b_%
HAR114_I_b_%
HAR115_I_b_%
HAR116_I_b_%
HAR117_I_b_%
HAR118_I_b_%
HAR119_I_b_%
HAR120_I_b_%
HAR121_I_b_%
HAR122_I_b_%
HAR123_I_b_%
HAR124_I_b_%
HAR125_I_b_%
HAR126_I_b_%
HAR127_I_b_%
ANG_HAR2_I_b
ANG_HAR3_I_b
ANG_HAR4_I_b
ANG_HAR5_I_b
ANG_HAR6_I_b
ANG_HAR7_I_b
ANG_HAR8_I_b
ANG_HAR9_I_b
ANG_HAR10_I_b
ANG_HAR11_I_b
ANG_HAR12_I_b
ANG_HAR13_I_b
ANG_HAR14_I_b
ANG_HAR15_I_b
ANG_HAR16_I_b
ANG_HAR17_I_b
ANG_HAR18_I_b
ANG_HAR19_I_b
ANG_HAR20_I_b
ANG_HAR21_I_b
ANG_HAR22_I_b
ANG_HAR23_I_b
ANG_HAR24_I_b
ANG_HAR25_I_b
ANG_HAR26_I_b
ANG_HAR27_I_b
ANG_HAR28_I_b
ANG_HAR29_I_b
ANG_HAR30_I_b
ANG_HAR31_I_b
ANG_HAR32_I_b
ANG_HAR33_I_b
ANG_HAR34_I_b
ANG_HAR35_I_b
ANG_HAR36_I_b
ANG_HAR37_I_b
ANG_HAR38_I_b
ANG_HAR39_I_b
ANG_HAR40_I_b
ANG_HAR41_I_b
ANG_HAR42_I_b
ANG_HAR43_I_b
ANG_HAR44_I_b
ANG_HAR45_I_b
ANG_HAR46_I_b
ANG_HAR47_I_b
ANG_HAR48_I_b
ANG_HAR49_I_b
ANG_HAR50_I_b
ANG_HAR51_I_b
ANG_HAR52_I_b
ANG_HAR53_I_b
ANG_HAR54_I_b
ANG_HAR55_I_b
ANG_HAR56_I_b
ANG_HAR57_I_b
ANG_HAR58_I_b
ANG_HAR59_I_b
ANG_HAR60_I_b
ANG_HAR61_I_b
ANG_HAR62_I_b
ANG_HAR63_I_b
ANG_HAR64_I_b
ANG_HAR65_I_b
ANG_HAR66_I_b
ANG_HAR67_I_b
ANG_HAR68_I_b
ANG_HAR69_I_b
ANG_HAR70_I_b
ANG_HAR71_I_b
ANG_HAR72_I_b
ANG_HAR73_I_b
ANG_HAR74_I_b
ANG_HAR75_I_b
ANG_HAR76_I_b
ANG_HAR77_I_b
ANG_HAR78_I_b
ANG_HAR79_I_b
ANG_HAR80_I_b
ANG_HAR81_I_b
ANG_HAR82_I_b
ANG_HAR83_I_b
ANG_HAR84_I_b
ANG_HAR85_I_b
ANG_HAR86_I_b
ANG_HAR87_I_b
ANG_HAR88_I_b
ANG_HAR89_I_b
ANG_HAR90_I_b
ANG_HAR91_I_b
ANG_HAR92_I_b
ANG_HAR93_I_b
ANG_HAR94_I_b
ANG_HAR95_I_b
ANG_HAR96_I_b
ANG_HAR97_I_b
ANG_HAR98_I_b
ANG_HAR99_I_b
ANG_HAR100_I_b
ANG_HAR101_I_b
ANG_HAR102_I_b
ANG_HAR103_I_b
ANG_HAR104_I_b
ANG_HAR105_I_b
ANG_HAR106_I_b
ANG_HAR107_I_b
ANG_HAR108_I_b
ANG_HAR109_I_b
ANG_HAR110_I_b
ANG_HAR111_I_b
ANG_HAR112_I_b
ANG_HAR113_I_b
ANG_HAR114_I_b
ANG_HAR115_I_b
ANG_HAR116_I_b
ANG_HAR117_I_b
ANG_HAR118_I_b
ANG_HAR119_I_b
ANG_HAR120_I_b
ANG_HAR121_I_b
ANG_HAR122_I_b
ANG_HAR123_I_b
ANG_HAR124_I_b
ANG_HAR125_I_b
ANG_HAR126_I_b
ANG_HAR127_I_b
HAR2_I_c_%
HAR3_I_c_%
HAR4_I_c_%
HAR5_I_c_%
HAR6_I_c_%
HAR7_I_c_%
HAR8_I_c_%
HAR9_I_c_%
HAR10_I_c_%
HAR11_I_c_%
HAR12_I_c_%
HAR13_I_c_%
HAR14_I_c_%
HAR15_I_c_%
HAR16_I_c_%
HAR17_I_c_%
HAR18_I_c_%
HAR19_I_c_%
HAR20_I_c_%
HAR21_I_c_%
HAR22_I_c_%
HAR23_I_c_%
HAR24_I_c_%
HAR25_I_c_%
HAR26_I_c_%
HAR27_I_c_%
HAR28_I_c_%
HAR29_I_c_%
HAR30_I_c_%
HAR31_I_c_%
HAR32_I_c_%
HAR33_I_c_%
HAR34_I_c_%
HAR35_I_c_%
HAR36_I_c_%
HAR37_I_c_%
HAR38_I_c_%
HAR39_I_c_%
HAR40_I_c_%
HAR41_I_c_%
HAR42_I_c_%
HAR43_I_c_%
HAR44_I_c_%
HAR45_I_c_%
HAR46_I_c_%
HAR47_I_c_%
HAR48_I_c_%
HAR49_I_c_%
HAR50_I_c_%
HAR51_I_c_%
HAR52_I_c_%
HAR53_I_c_%
HAR54_I_c_%
HAR55_I_c_%
HAR56_I_c_%
HAR57_I_c_%
HAR58_I_c_%
HAR59_I_c_%
HAR60_I_c_%
HAR61_I_c_%
HAR62_I_c_%
HAR63_I_c_%
HAR64_I_c_%
HAR65_I_c_%
HAR66_I_c_%
HAR67_I_c_%
HAR68_I_c_%
HAR69_I_c_%
HAR70_I_c_%
HAR71_I_c_%
HAR72_I_c_%
HAR73_I_c_%
HAR74_I_c_%
HAR75_I_c_%
HAR76_I_c_%
HAR77_I_c_%
HAR78_I_c_%
HAR79_I_c_%
HAR80_I_c_%
HAR81_I_c_%
HAR82_I_c_%
HAR83_I_c_%
HAR84_I_c_%
HAR85_I_c_%
HAR86_I_c_%
HAR87_I_c_%
HAR88_I_c_%
HAR89_I_c_%
HAR90_I_c_%
HAR91_I_c_%
HAR92_I_c_%
HAR93_I_c_%
HAR94_I_c_%
HAR95_I_c_%
HAR96_I_c_%
HAR97_I_c_%
HAR98_I_c_%
HAR99_I_c_%
HAR100_I_c_%
HAR101_I_c_%
HAR102_I_c_%
HAR103_I_c_%
HAR104_I_c_%
HAR105_I_c_%
HAR106_I_c_%
HAR107_I_c_%
HAR108_I_c_%
HAR109_I_c_%
HAR110_I_c_%
HAR111_I_c_%
HAR112_I_c_%
HAR113_I_c_%
HAR114_I_c_%
HAR115_I_c_%
HAR116_I_c_%
HAR117_I_c_%
HAR118_I_c_%
HAR119_I_c_%
HAR120_I_c_%
HAR121_I_c_%
HAR122_I_c_%
HAR123_I_c_%
HAR124_I_c_%
HAR125_I_c_%
HAR126_I_c_%
HAR127_I_c_%
ANG_HAR2_I_c
ANG_HAR3_I_c
ANG_HAR4_I_c
ANG_HAR5_I_c
ANG_HAR6_I_c
ANG_HAR7_I_c
ANG_HAR8_I_c
ANG_HAR9_I_c
ANG_HAR10_I_c
ANG_HAR11_I_c
ANG_HAR12_I_c
ANG_HAR13_I_c
ANG_HAR14_I_c
ANG_HAR15_I_c
ANG_HAR16_I_c
ANG_HAR17_I_c
ANG_HAR18_I_c
ANG_HAR19_I_c
ANG_HAR20_I_c
ANG_HAR21_I_c
ANG_HAR22_I_c
ANG_HAR23_I_c
ANG_HAR24_I_c
ANG_HAR25_I_c
ANG_HAR26_I_c
ANG_HAR27_I_c
ANG_HAR28_I_c
ANG_HAR29_I_c
ANG_HAR30_I_c
ANG_HAR31_I_c
ANG_HAR32_I_c
ANG_HAR33_I_c
ANG_HAR34_I_c
ANG_HAR35_I_c
ANG_HAR36_I_c
ANG_HAR37_I_c
ANG_HAR38_I_c
ANG_HAR39_I_c
ANG_HAR40_I_c
ANG_HAR41_I_c
ANG_HAR42_I_c
ANG_HAR43_I_c
ANG_HAR44_I_c
ANG_HAR45_I_c
ANG_HAR46_I_c
ANG_HAR47_I_c
ANG_HAR48_I_c
ANG_HAR49_I_c
ANG_HAR50_I_c
ANG_HAR51_I_c
ANG_HAR52_I_c
ANG_HAR53_I_c
ANG_HAR54_I_c
ANG_HAR55_I_c
ANG_HAR56_I_c
ANG_HAR57_I_c
ANG_HAR58_I_c
ANG_HAR59_I_c
ANG_HAR60_I_c
ANG_HAR61_I_c
ANG_HAR62_I_c
ANG_HAR63_I_c
ANG_HAR64_I_c
ANG_HAR65_I_c
ANG_HAR66_I_c
ANG_HAR67_I_c
ANG_HAR68_I_c
ANG_HAR69_I_c
ANG_HAR70_I_c
ANG_HAR71_I_c
ANG_HAR72_I_c
ANG_HAR73_I_c
ANG_HAR74_I_c
ANG_HAR75_I_c
ANG_HAR76_I_c
ANG_HAR77_I_c
ANG_HAR78_I_c
ANG_HAR79_I_c
ANG_HAR80_I_c
ANG_HAR81_I_c
ANG_HAR82_I_c
ANG_HAR83_I_c
ANG_HAR84_I_c
ANG_HAR85_I_c
ANG_HAR86_I_c
ANG_HAR87_I_c
ANG_HAR88_I_c
ANG_HAR89_I_c
ANG_HAR90_I_c
ANG_HAR91_I_c
ANG_HAR92_I_c
ANG_HAR93_I_c
ANG_HAR94_I_c
ANG_HAR95_I_c
ANG_HAR96_I_c
ANG_HAR97_I_c
ANG_HAR98_I_c
ANG_HAR99_I_c
ANG_HAR100_I_c
ANG_HAR101_I_c
ANG_HAR102_I_c
ANG_HAR103_I_c
ANG_HAR104_I_c
ANG_HAR105_I_c
ANG_HAR106_I_c
ANG_HAR107_I_c
ANG_HAR108_I_c
ANG_HAR109_I_c
ANG_HAR110_I_c
ANG_HAR111_I_c
ANG_HAR112_I_c
ANG_HAR113_I_c
ANG_HAR114_I_c
ANG_HAR115_I_c
ANG_HAR116_I_c
ANG_HAR117_I_c
ANG_HAR118_I_c
ANG_HAR119_I_c
ANG_HAR120_I_c
ANG_HAR121_I_c
ANG_HAR122_I_c
ANG_HAR123_I_c
ANG_HAR124_I_c
ANG_HAR125_I_c
ANG_HAR126_I_c
ANG_HAR127_I_c

## analysisNames
analysisId | analysisUnitId | analysisName
1 | 1 | three_phase_realtime
2 | 1 | three_phase_energy_demand
3 | 1 | three_phase_thd
5 | 1 | three_phase_sequence

## applications
appId | appName | isTimer | groupId | interval | isEnable | jsonConfig | appType
1 | north | false | 4 | 0 | true | "" | 2
2 | alarm | false | 0 | 0 | true | "" | 2
3 | datalog1 | true | 1 | 3000 | true | "" | 1
4 | datalog2 | true | 1 | 3000 | true | "" | 1
5 | datalog3 | true | 1 | 3000 | true | "" | 1
6 | datalog4 | true | 1 | 3000 | true | "" | 1
7 | trendlogreal | true | 2 | 5000 | true | "" | 1
8 | trendlogenergy | true | 3 | 5000 | true | "" | 1
9 | acucloud | true | 11 | 5000 | true | "" | 1
10 | mqtt | true | 17 | 5000 | true | "" | 1
11 | snmp | true | 12 | 5000 | true | "" | 1
12 | bacnet | true | 12 | 5000 | true | "" | 1

## groups
groupId | groupType | paramCount
1 | datalog
2 | trendreal
3 | trendenergy
4 | north
5 | realtimeRange
6 | demandRange
7 | energyRange
8 | thdRange
9 | harmonicsRange
10 | sequenceRange
11 | haveEnergy |  | datalog_range,acucloud_range,mqtt_range,bacnet_range
12 | haveNoEnergy |  | alarm_range,snmp_range
13 | datalogRange
14 | mqtt_range
15 | alarm_range
16 | acucloud_range
17 | mqtt |  | 界面配置时生成，模版不配置
18 | alarm |  | 界面配置时生成，模版不配置

## deviceTemplateInfo
label | description | version | firmwareVersion | deviceType | protocol
Acuvim 3 | Acuvim 3 Power Quality Meter | v1.00p01 | v1.03p09 | threePhaseACMeter | { "type": "Modbus", "transports": ["modbus-tcp", "modbus-rtu"] }