## blockParams
Start(Dec) | descrption | paramType | unit | check | dataType | byteOrder | RW | Reg | scale | Alarm | Data log default parameter | Trend Log | DataLog | AcuCloud | MQTT | SNMP | BACnetIP | North
0 | IsOnline | IsOnline |  |  | isOnline | 1 | R | 1 | 1
8468 | System Frequency | FREQ_Hz | Hz |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8470 | Phase A Line-to-Neutral Voltage | VLN_a_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8472 | Phase B Line-to-Neutral Voltage | VLN_b_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8474 | Phase C Line-to-Neutral Voltage | VLN_c_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8476 | Average Line-to-Neutral Voltage | VLN_avg_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8478 | Phase A-B Line-to-Line Voltage | VLL_ab_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8480 | Phase B-C Line-to-Line Voltage | VLL_bc_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8482 | Phase C-A Line-to-Line Voltage | VLL_ca_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8484 | Average Line-to-Line Voltage | VLL_avg_V | V |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8486 | Phase A Line Current | I_a_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8488 | Phase B Line Current | I_b_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8490 | Phase C Line Current | I_c_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8492 | Neutral Current | I_n_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8494 | Average Line Current | I_avg_A | A |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8496 | Phase A Active Power | P_a_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8498 | Phase B Active Power | P_b_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8500 | Phase C Active Power | P_c_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8502 | System Active Power | P_kW | kW |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8504 | Phase A Reactive Power | Q_a_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8506 | Phase B Reactive Power | Q_b_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8508 | Phase C Reactive Power | Q_c_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8510 | System Reactive Power | Q_kvar | kvar |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8512 | Phase A Apparent Power | S_a_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8514 | Phase B Apparent Power | S_b_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8516 | Phase C Apparent Power | S_c_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8518 | System Apparent Power | S_kVA | kVA |  | float32 | 12 | R | 2 | 1 | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8520 | Phase A Load Nature | LC_a |  | 删除单位 | float32 | 12 | R | 2 | 1 |  |  | realtime | [6 empty] | realtime
8522 | Phase B Load Nature | LC_b |  | 删除单位 | float32 | 12 | R | 2 | 1 |  |  | realtime | [6 empty] | realtime
8524 | Phase C Load Nature | LC_c |  | 删除单位 | float32 | 12 | R | 2 | 1 |  |  | realtime | [6 empty] | realtime
8526 | System Load Nature | LC_avg |  | 删除单位 | float32 | 12 | R | 2 | 1 |  |  | realtime | [6 empty] | realtime
8528 | Phase A Power Factor | PF_a |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8530 | Phase B Power Factor | PF_b |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8532 | Phase C Power Factor | PF_c |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8534 | System Power Factor | PF |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8536 | Phase A Leading Power Factor | LEAD_PF_a |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8538 | Phase B Leading Power Factor | LEAD_PF_b |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8540 | Phase C Leading Power Factor | LEAD_PF_c |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8542 | System Leading Power Factor | LEAD_PF |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8544 | Phase A Lagging Power Factor | LAG_PF_a |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8546 | Phase B Lagging Power Factor | LAG_PF_b |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8548 | Phase C Lagging Power Factor | LAG_PF_c |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8550 | System Lagging Power Factor | LAG_PF |  | 删除单位 | float32 | 12 | R | 2 | 1 | realtime |  |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8552 | Phase A Line-to-Neutral Voltage Phase Angle | ANG_VLN_a | ° |  | float32 | 12 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8554 | Phase B Line-to-Neutral Voltage Phase Angle | ANG_VLN_b | ° |  | float32 | 12 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8556 | Phase C Line-to-Neutral Voltage Phase Angle | ANG_VLN_c | ° |  | float32 | 12 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8558 | Phase AB Line-to-Line Voltage Phase Angle | ANG_VLL_ab | ° |  | float32 | 12 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8560 | Phase BC Line-to-Line Voltage Phase Angle | ANG_VLL_bc | ° | ANG_VLL_bb修改为ANG_VLL_bc | float32 | 12 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8562 | Phase CA Line-to-Line Voltage Phase Angle | ANG_VLL_ca | ° | ANG_VLL_cb修改为ANG_VLL_ca | float32 | 12 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8564 | Phase A Current Phase Angle | ANG_I_a | ° |  | float32 | 12 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8566 | Phase B Current Phase Angle | ANG_I_b | ° |  | float32 | 12 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8568 | Phase C Current Phase Angle | ANG_I_c | ° |  | float32 | 12 | R | 2 | 1 | realtime | realtime |  | realtime | realtime | realtime | realtime | realtime | realtime | realtime
8570 | Voltage Positive Sequence Magnitude | MAG_SEQ_POS_V | V | SEQ_POS_MAG_V修改为MAG_SEQ_POS_V,增加单位 | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8572 | Voltage Zero Sequence Magnitude | MAG_SEQ_ZERO_V | V | SEQ_ZERO_MAG_V修改为MAG_SEQ_ZERO_V,增加单位 | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8574 | Voltage Negative Sequence Magnitude | MAG_SEQ_NEG_V | V | SEQ_NEG_MAG_V修改为MAG_SEQ_NEG_V,增加单位 | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8576 | Voltage Zero Sequence Ratio Magnitude | SEQ_ZERO_RATIO_V_% | % | 增加单位 | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8578 | Voltage Unbalance Factor Magnitude | UNBL_V_% | % | 增加单位 | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8580 | Current Positive Sequence Magnitude | MAG_SEQ_POS_I | A | SEQ_POS_MAG_I修改为MAG_SEQ_POS_I,增加单位 | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8582 | Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I | A | SEQ_ZERO_MAG_I修改为MAG_SEQ_ZERO_I,增加单位 | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8584 | Current Negative Sequence Magnitude | MAG_SEQ_NEG_I | A | SEQ_NEG_MAG_I修改为MAG_SEQ_NEG_I,增加单位 | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8586 | Current Zero Sequence Ratio Magnitude | SEQ_ZERO_RATIO_I_% | % | 增加单位 | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8588 | Current Unbalance Factor Magnitude | UNBL_I_% | % |  | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8590 | Voltage Positive Sequence Angle | ANG_SEQ_POS_V | ° | SEQ_POS_ANG_V修改为ANG_SEQ_POS_V | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8592 | Voltage Zero Sequence Angle | ANG_SEQ_ZERO_V | ° | SEQ_ZERO_ANG_V修改为ANG_SEQ_ZERO_V | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8594 | Voltage Negative Sequence Angle | ANG_SEQ_NEG_V | ° | SEQ_NEG_ANG_V修改为ANG_SEQ_NEG_V | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8596 | Current Positive Sequence Angle | ANG_SEQ_POS_I | ° | SEQ_POS_ANG_I修改为ANG_SEQ_POS_I | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8598 | Current Zero Sequence Angle | ANG_SEQ_ZERO_I | ° | SEQ_ZERO_ANG_I修改为ANG_SEQ_ZERO_I | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8600 | Current Negative Sequence Angle | ANG_SEQ_NEG_I | ° | SEQ_NEG_ANG_I修改为ANG_SEQ_NEG_I | float32 | 12 | R | 2 | 1 | sequence |  |  | sequence | sequence | sequence | sequence | sequence | sequence | sequence
8602 | Phase A Voltage THD | THD_V_a_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8604 | Phase B Voltage THD | THD_V_b_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8606 | Phase C Voltage THD | THD_V_c_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8608 | Phase A Voltage THD Odd | OTHD_V_a_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8610 | Phase B Voltage THD Odd | OTHD_V_b_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8612 | Phase C Voltage THD Odd | OTHD_V_c_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8614 | Phase A Voltage THD Even | ETHD_V_a_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8616 | Phase B Voltage THD Even | ETHD_V_b_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8618 | Phase C Voltage THD Even | ETHD_V_c_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8620 | Phase A Voltage Crest Factor | CF_V_a_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8622 | Phase B Voltage Crest Factor | CF_V_b_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8624 | Phase C Voltage Crest Factor | CF_V_c_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8626 | Phase A Current THD | THD_I_a_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8628 | Phase B Current THD | THD_I_b_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8630 | Phase C Current THD | THD_I_c_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8632 | Phase N Current THD | THD_I_n_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8634 | Phase A Current THD Odd | OTHD_I_a_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8636 | Phase B Current THD Odd | OTHD_I_b_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8638 | Phase C Current THD Odd | OTHD_I_c_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8640 | Phase N Current THD Odd | OTHD_I_n_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8642 | Phase A Current THD Even | ETHD_I_a_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8644 | Phase B Current THD Even | ETHD_I_b_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8646 | Phase C Current THD Even | ETHD_I_c_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8648 | Phase N Current THD Even | ETHD_I_n_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8650 | Phase A Current TDD | TDD_I_a_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8652 | Phase B Current TDD | TDD_I_b_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8654 | Phase C Current TDD | TDD_I_c_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8656 | Phase N Current TDD | TDD_I_n_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8658 | Phase A Current Crest-Factor | CF_I_a_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8660 | Phase B Current Crest-Factor | CF_I_b_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8662 | Phase C Current Crest-Factor | CF_I_c_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8664 | Phase N Current Crest-Factor | CF_I_n_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8666 | Phase A Current K-Factor | KF_I_a_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8668 | Phase B Current K-Factor | KF_I_b_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8670 | Phase C Current K-Factor | KF_I_c_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8672 | Phase N Current K-Factor | KF_I_n_% | % |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8674 | Phase A Voltage Flicker | FLICK_V_a |  |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8676 | Phase B Voltage Flicker | FLICK_V_b |  |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
8678 | Phase C Voltage Flicker | FLICK_V_c |  |  | float32 | 12 | R | 2 | 1 | THD |  |  | THD | THD | THD | THD | THD | THD | THD
24832 | Phase A Current Demand | DMD_I_a_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
24834 | Phase B Current Demand | DMD_I_b_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
24836 | Phase C Current Demand | DMD_I_c_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
24838 | Average Current Demand | DMD_I_avg_A | A |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
24984 | Phase A Active Power Demand | DMD_P_a_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
24986 | Phase B Active Power Demand | DMD_P_b_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
24988 | Phase C Active Power Demand | DMD_P_c_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
24990 | System Active Power Demand | DMD_P_kW | kW |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
24992 | Phase A Reactive Power Demand | DMD_Q_a_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
24994 | Phase B Reactive Power Demand | DMD_Q_b_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
24996 | Phase C Reactive Power Demand | DMD_Q_c_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
24998 | System Reactive Power Demand | DMD_Q_kvar | kvar |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
25000 | Phase A Apparent Power Demand | DMD_S_a_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
25002 | Phase B Apparent Power Demand | DMD_S_b_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
25004 | Phase C Apparent Power Demand | DMD_S_c_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
25006 | System Apparent Power Demand | DMD_S_kVA | kVA |  | float32 | 12 | R | 2 | 1 | demand |  |  | demand | demand | demand | demand | demand | demand | demand
26048 | Phase A Active Energy-Import | EP_IMP_a_kWh | kWh |  | double |  | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
26052 | Phase B Active Energy-Import | EP_IMP_b_kWh | kWh |  | double |  | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
26056 | Phase C Active Energy-Import | EP_IMP_c_kWh | kWh |  | double |  | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
26060 | System Active Energy-Import | EP_IMP_kWh | kWh |  | double |  | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
26064 | Phase A Reactive Energy-Import | EQ_IMP_a_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26068 | Phase B Reactive Energy-Import | EQ_IMP_b_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26072 | Phase C Reactive Energy-Import | EQ_IMP_c_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26076 | System Reactive Energy-Import | EQ_IMP_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26080 | Phase A Active Energy-Export | EP_EXP_a_kWh | kWh |  | double |  | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
26084 | Phase B Active Energy-Export | EP_EXP_b_kWh | kWh |  | double |  | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
26088 | Phase C Active Energy-Export | EP_EXP_c_kWh | kWh |  | double |  | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
26092 | System Active Energy-Export | EP_EXP_kWh | kWh |  | double |  | R | 4 | 1 |  | energy | energy | energy | energy | energy | energy | energy | energy | energy
26096 | Phase A Reactive Energy-Export | EQ_EXP_a_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26100 | Phase B Reactive Energy-Export | EQ_EXP_b_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26104 | Phase C Reactive Energy-Export | EQ_EXP_c_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26108 | System Reactive Energy-Export | EQ_EXP_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26112 | Phase A Active Energy-Net | EP_NET_a_kWh | kWh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26116 | Phase B Active Energy-Net | EP_NET_b_kWh | kWh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26120 | Phase C Active Energy-Net | EP_NET_c_kWh | kWh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26124 | System Active Energy-Net | EP_NET_kWh | kWh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26128 | Phase A Reactive Energy-Net | EQ_NET_a_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26132 | Phase B Reactive Energy-Net | EQ_NET_b_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26136 | Phase C Reactive Energy-Net | EQ_NET_c_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26140 | System Reactive Energy-Net | EQ_NET_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26144 | Phase A Active Energy-Total | EP_TOTAL_a_kWh | kWh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26148 | Phase B Active Energy-Total | EP_TOTAL_b_kWh | kWh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26152 | Phase C Active Energy-Total | EP_TOTAL_c_kWh | kWh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26156 | System Active Energy-Total | EP_TOTAL_kWh | kWh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26160 | Phase A Reactive Energy-Total | EQ_TOTAL_a_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26164 | Phase B Reactive Energy-Total | EQ_TOTAL_b_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26168 | Phase C Reactive Energy-Total | EQ_TOTAL_c_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26172 | System Reactive Energy-Total | EQ_TOTAL_kvarh | kvarh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26176 | Phase A Apparent Energy | ES_a_kVAh | kVAh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26180 | Phase B Apparent Energy | ES_b_kVAh | kVAh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26184 | Phase C Apparent Energy | ES_c_kVAh | kVAh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
26188 | System Apparent Energy | ES_kVAh | kVAh |  | double |  | R | 4 | 1 |  |  | energy | energy | energy | energy | energy | energy | energy | energy
4101 | Service Configuration | Conf_ServiceConfig |  |  | enum |  | W | 1
4127 | Phase Order | Conf_Phase_Order |  |  | enum |  | W | 1