## AcuRev4100
Block code function : 03H Read, 10H Write | Start(Hex) | End(Hex) | Start(Dec) | End(Dec) | Description | Data type | RW | Reg | Range | Default | Factory value | wirte_value | before_reboot | after_reboot | result_compare
Communication | 0x1000 | 0x1000 | 4096 | 4096 | Password | uint16_t | R/W | 1 | 0-9999 | 9999 | 9999 | [9999] | [8888]
| 0x1001 | 0x1001 | 4097 | 4097 | Baud Rate | uint16_t | R/W | 1 | 2400\4800\9600\19200\38400\57600\76800\115200(76800 need send 7680 115200need send 11520) | 19200 | 19200 |  | [19200]
| 0x1002 | 0x1002 | 4098 | 4098 | Parity | uint16_t | R/W | 1 | 0: even 1: odd 2: None2 3: None1 | 3: None1 | 3: None1 |  | [3]
| 0x1003 | 0x1003 | 4099 | 4099 | DHCP enable | uint16_t | R/W | 1 | 0: manual 1: DHCP | 0 | 0 |  | [1]
| 0x1004 | 0x1004 | 4100 | 4100 | IP address 1st byte IP address 2nd byte | uint8_t | R/W | 1 | 0~255 | 192.168.1.254 | 192 168 1 254 |  | [192, 168]
| 0x1005 | 0x1005 | 4101 | 4101 | IP address 3rd byte IP address 4th byte | uint8_t | R/W | 1 | 0~255 |  |  |  | [227, 2]
| 0x1006 | 0x1006 | 4102 | 4102 | Subnet mask 1st byte Subnet mask 2nd byte | uint8_t | R/W | 1 | 0~255 | 255 255 255 0 | 255 255 255 0 |  | [255, 255]
| 0x1007 | 0x1007 | 4103 | 4103 | Subnet mask 3rd byte Subnet mask 4th byte | uint8_t | R/W | 1 | 0~255 |  |  |  | [0, 254]
| 0x1008 | 0x1008 | 4104 | 4104 | Gateway 1st byte Gateway 2nd byte | uint8_t | R/W | 1 | 0~255 | 192.168.1.1 | 192 168 1 1 |  | [192, 168]
| 0x1009 | 0x1009 | 4105 | 4105 | Gateway 3rd byte Gateway 4th byte | uint8_t | R/W | 1 | 0~255 |  |  |  | [1, 3]
| 0x100A | 0x100A | 4106 | 4106 | DNS primary server 1st byte DNS primary server 2nd byte | uint8_t | R/W | 1 | 0~255 | 8 8 8 8 | 8 8 8 8 | [8, 8] | [7, 7]
| 0x100B | 0x100B | 4107 | 4107 | DNS primary server 3rd byte DNS primary server 4th byte | uint8_t | R/W | 1 | 0~255 |  |  | [8, 8] | [9, 9]
| 0x100C | 0x100C | 4108 | 4108 | DNS secondary server 1st byte DNS secondary server 2nd byte | uint8_t | R/W | 1 | 0~255 | 8.8.4.4 | 8.8.4.4 |  | [8, 8]
| 0x100D | 0x100D | 4109 | 4109 | DNS secondary server 3rd byte DNS secondary server 4th byte | uint8_t | R/W | 1 | 0~255 |  |  |  | [4, 4]
| 0x100E | 0x100E | 4110 | 4110 | Modbus Slave ID | uint16_t | R/W | 1 | 1-247, used for both Modbus RTU and TCP | 1 | 1 |  | [1]
| 0x100F | 0x100F | 4111 | 4111 | RS485 protocol | uint16_t | R/W | 1 | 0: disable 1: Modbus RTU 2: BACnet MS/TP | 1 | 1 |  | [1]
| 0x1010 | 0x1010 | 4112 | 4112 | Modbus TCP Enable | uint16_t | R/W | 1 | 0: disable 1: enable | 1 | 1 |  | [1]
| 0x1011 | 0x1011 | 4113 | 4113 | Modbus TCP port | uint16_t | R/W | 1 | 1-65534 | 502 | 502 |  | [502]
| 0x1012 | 0x1012 | 4114 | 4114 | BACnet MS/TP Meter address | uint16_t | R/W | 1 | 0 - 127 | 1 |  |  | [1]
| 0x1013 | 0x1013 | 4115 | 4115 | BACnet MS/TP Maximum number of message frames | uint16_t | R/W | 1 | 1 - 255 | 255 | 255 |  | [255]
| 0x1014 | 0x1015 | 4116 | 4117 | BACnet MS/TP ID | uint32_t | R/W | 2 | 1 - 4194303(0x3FFFFF) | 0 | 0 |  | [1]
| 0x1016 | 0x1016 | 4118 | 4118 | BACnet MS/TP Database Revision | uint16_t | R | 1 | 0 - 65535(0xFFFF) | 0 | 0 |  | [1]
| 0x1017 | 0x1017 | 4119 | 4119 | LCD Backlight Time | uint16_t | R/W | 1 | 0-120 minute | 1 | 1 |  | [1]
| 0x1018 | 0x1019 | 4120 | 4121 | Device run time | uint32_t | R | 2 | uint in second | 0 | 0 |  | [1261404]
| 0x101A | 0x101B | 4122 | 4123 | Device load time | uint32_t | R | 2 | uint in second | 0 | 0 |  | [4290]
| 0x101C | 0x101C | 4124 | 4124 | MaxDemand Clear Mode | uint16_t | R/W | 1 | 0：Manual Mode 1：Automatic Mode 2：Disable | 0 | 0 |  | [0]
| 0x101D | 0x101E | 4125 | 4126 | MaxDemand Clear Data Setting | uint8_t | R/W | 2 | ( day:uint8_t , hour:uint8_t, min:uint8_t , sec: uint8_t) | 0 | 0 |  | [1, 0, 0, 0]
| 0x101F | 0x101F | 4127 | 4127 | MaxDemand Clear Total Count | uint16_t | R | 1 | 0-65535 | 0 | 0 |  | [1]
| 0x1020 | 0x1022 | 4128 | 4130 | Timestamp of the most recent MaxDemand Clear | uint8_t | R | 3 | (year：uint8_t、month：uint8_t、day:uint8_t、hour:uint8_t、min:uint8_t、sec：uint8_t) | 0 | 0 |  | [24, 1, 1, 0, 17, 24]
| 0x1023 | 0x1023 | 4131 | 4131 | Non-standard Seal Parameter Select | uint16_t | R/W | 1 | bit0-4 (0 :NON bit0:RS485 Setting bit1:Ethernet Setting bit2: protocol Setting bit3:Clear Loadtime bit4: Clear Runtime) | 0 | 0 |  | [0]
| 0x1024 | 0x1024 | 4132 | 4132 | Week | uint16_t | R/W | 1 | 1~7 | 1 | 1 |  | [5]
| 0x1025 | 0x1025 | 4133 | 4133 | Year | uint16_t | R/W | 1 | 2000~2099 | 2024 | 2024 |  | [2025]
| 0x1026 | 0x1026 | 4134 | 4134 | Month | uint16_t | R/W | 1 | 1~12 | 1 | 1 |  | [1]
| 0x1027 | 0x1027 | 4135 | 4135 | Day | uint16_t | R/W | 1 | 1~31 | 1 | 1 |  | [17]
| 0x1028 | 0x1028 | 4136 | 4136 | Hour | uint16_t | R/W | 1 | 0~23 | 0 | 0 |  | [3]
| 0x1029 | 0x1029 | 4137 | 4137 | Minute | uint16_t | R/W | 1 | 0~59 | 0 | 0 |  | [42]
| 0x102A | 0x102A | 4138 | 4138 | Second | uint16_t | R/W | 1 | 0~59 | 0 | 0 |  | [58]
| 0x1040 | 0x1040 | 4160 | 4160 | Sealing Status | uint16_t | R | 1 | sealed: 0x0A unsealed: 0 |  |  |  | [0]
| 0x1041 | 0x1041 | 4161 | 4161 | Frequency Selection | uint16_t | R/W | 1 | 0: 50Hz 1: 60Hz | 0 | 0 |  | [1]
| 0x1042 | 0x1042 | 4162 | 4162 | Service Configuration | uint16_t | R/W | 1 | 0: ELEMENT_1_WIRE_2 1: ELEMENT_2_WIRE_3_PHASE_1 2: ELEMENT_2_WIRE_3_DELTA 3: ELEMENT_2_WIRE_3_NETWORK 4: ELEMENT_3_WIRE_4_Y 5：ELEMENT_3_WIRE_4_DELTA | 4 | 4 |  | [4]
| 0x1043 | 0x1044 | 4163 | 4164 | PT1 | uint32_t | R/W | 2 | 50-1000000 | 0 | 0 |  | [0]
| 0x1045 | 0x1045 | 4165 | 4165 | PT2 | uint16_t | R/W | 1 | 50-690 | 400 | 400 |  | [0]
| 0x1046 | 0x1046 | 4166 | 4166 | channel1 input wiring ID | uint16_t | R/W | 1 | 1~24 | 1 | 1 |  | [1]
| 0x1047 | 0x1047 | 4167 | 4167 | channel1 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x1048 | 0x1048 | 4168 | 4168 | channel1 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x1049 | 0x1049 | 4169 | 4169 | channel1 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x104A | 0x104A | 4170 | 4170 | channle1 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0 | 0 |  | [0]
| 0x104B | 0x104B | 4171 | 4171 | channel2 input wiring | uint16_t | R/W | 1 | 1~24 | 2 | 2 |  | [2]
| 0x104C | 0x104C | 4172 | 4172 | channel2 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x104D | 0x104D | 4173 | 4173 | channel2 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x104E | 0x104E | 4174 | 4174 | channel2 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x104F | 0x104F | 4175 | 4175 | channel2 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1 | 1 |  | [1]
| 0x1050 | 0x1050 | 4176 | 4176 | channel3 input wiring | uint16_t | R/W | 1 | 1~24 | 3 | 3 |  | [3]
| 0x1051 | 0x1051 | 4177 | 4177 | channel3 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x1052 | 0x1052 | 4178 | 4178 | channel3 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x1053 | 0x1053 | 4179 | 4179 | channel3 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x1054 | 0x1054 | 4180 | 4180 | channel3 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2 | 2 |  | [2]
| 0x1055 | 0x1055 | 4181 | 4181 | channel4 input wiring | uint16_t | R/W | 1 | 1~24 | 4 | 4 |  | [4]
| 0x1056 | 0x1056 | 4182 | 4182 | channel4 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x1057 | 0x1057 | 4183 | 4183 | channel4 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x1058 | 0x1058 | 4184 | 4184 | channel4 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x1059 | 0x1059 | 4185 | 4185 | channel4 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0 | 0 |  | [0]
| 0x105A | 0x105A | 4186 | 4186 | channel5 input wiring | uint16_t | R/W | 1 | 1~24 | 5 | 5 |  | [5]
| 0x105B | 0x105B | 4187 | 4187 | channel5 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x105C | 0x105C | 4188 | 4188 | channel5 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x105D | 0x105D | 4189 | 4189 | channel5 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x105E | 0x105E | 4190 | 4190 | channel5 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1 | 1 |  | [1]
| 0x105F | 0x105F | 4191 | 4191 | channel6 input wiring | uint16_t | R/W | 1 | 1~24 | 6 | 6 |  | [6]
| 0x1060 | 0x1060 | 4192 | 4192 | channel6 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x1061 | 0x1061 | 4193 | 4193 | channel6 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x1062 | 0x1062 | 4194 | 4194 | channel6 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x1063 | 0x1063 | 4195 | 4195 | channel6 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2 | 2 |  | [2]
| 0x1064 | 0x1064 | 4196 | 4196 | channel7 input wiring | uint16_t | R/W | 1 | 1~24 | 7 | 7 |  | [7]
| 0x1065 | 0x1065 | 4197 | 4197 | channel7 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x1066 | 0x1066 | 4198 | 4198 | channel7 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x1067 | 0x1067 | 4199 | 4199 | channel7 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x1068 | 0x1068 | 4200 | 4200 | channel7 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0 | 0 |  | [0]
| 0x1069 | 0x1069 | 4201 | 4201 | channel8 input wiring | uint16_t | R/W | 1 | 1~24 | 8 | 8 |  | [8]
| 0x106A | 0x106A | 4202 | 4202 | channel8 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x106B | 0x106B | 4203 | 4203 | channel8 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x106C | 0x106C | 4204 | 4204 | channel8 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x106D | 0x106D | 4205 | 4205 | channel8 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1 | 1 |  | [1]
| 0x106E | 0x106E | 4206 | 4206 | channel9 input wiring | uint16_t | R/W | 1 | 1~24 | 9 | 9 |  | [9]
| 0x106F | 0x106F | 4207 | 4207 | channel9 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x1070 | 0x1070 | 4208 | 4208 | channel9 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x1071 | 0x1071 | 4209 | 4209 | channel9 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x1072 | 0x1072 | 4210 | 4210 | channel9 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2 | 2 |  | [2]
| 0x1073 | 0x1073 | 4211 | 4211 | channel10 input wiring | uint16_t | R/W | 1 | 1~24 | 10 | 10 |  | [10]
| 0x1074 | 0x1074 | 4212 | 4212 | channel10 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x1075 | 0x1075 | 4213 | 4213 | channel10 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x1076 | 0x1076 | 4214 | 4214 | channel10 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x1077 | 0x1077 | 4215 | 4215 | channel10 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0 | 0 |  | [0]
| 0x1078 | 0x1078 | 4216 | 4216 | channel11 input wiring | uint16_t | R/W | 1 | 1~24 | 11 | 11 |  | [11]
| 0x1079 | 0x1079 | 4217 | 4217 | channel11 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x107A | 0x107A | 4218 | 4218 | channel11 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x107B | 0x107B | 4219 | 4219 | channel11 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x107C | 0x107C | 4220 | 4220 | channel11 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1 | 1 |  | [1]
| 0x107D | 0x107D | 4221 | 4221 | channel12 input wiring | uint16_t | R/W | 1 | 1~24 | 12 | 12 |  | [12]
| 0x107E | 0x107E | 4222 | 4222 | channel12 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x107F | 0x107F | 4223 | 4223 | channel12 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x1080 | 0x1080 | 4224 | 4224 | channel12 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x1081 | 0x1081 | 4225 | 4225 | channel12 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2 | 2 |  | [2]
| 0x1082 | 0x1082 | 4226 | 4226 | channel13 input wiring | uint16_t | R/W | 1 | 1~24 | 13 | 13 |  | [13]
| 0x1083 | 0x1083 | 4227 | 4227 | channel13 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x1084 | 0x1084 | 4228 | 4228 | channel13 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x1085 | 0x1085 | 4229 | 4229 | channel13 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x1086 | 0x1086 | 4230 | 4230 | channel13 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0 | 0 |  | [0]
| 0x1087 | 0x1087 | 4231 | 4231 | channel14 input wiring | uint16_t | R/W | 1 | 1~24 | 14 | 14 |  | [14]
| 0x1088 | 0x1088 | 4232 | 4232 | channel14 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x1089 | 0x1089 | 4233 | 4233 | channel14 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x108A | 0x108A | 4234 | 4234 | channel14 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x108B | 0x108B | 4235 | 4235 | channel14 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1 | 1 |  | [1]
| 0x108C | 0x108C | 4236 | 4236 | channel15 input wiring | uint16_t | R/W | 1 | 1~24 | 15 | 15 |  | [15]
| 0x108D | 0x108D | 4237 | 4237 | channel15 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x108E | 0x108E | 4238 | 4238 | channel15 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x108F | 0x108F | 4239 | 4239 | channel15 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x1090 | 0x1090 | 4240 | 4240 | channel15 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2 | 2 |  | [2]
| 0x1091 | 0x1091 | 4241 | 4241 | channel16 input wiring | uint16_t | R/W | 1 | 1~24 | 16 | 16 |  | [16]
| 0x1092 | 0x1092 | 4242 | 4242 | channel16 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x1093 | 0x1093 | 4243 | 4243 | channel16 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x1094 | 0x1094 | 4244 | 4244 | channel16 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x1095 | 0x1095 | 4245 | 4245 | channel16 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0 | 0 |  | [0]
| 0x1096 | 0x1096 | 4246 | 4246 | channel17 input wiring | uint16_t | R/W | 1 | 1~24 | 17 | 17 |  | [17]
| 0x1097 | 0x1097 | 4247 | 4247 | channel17 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x1098 | 0x1098 | 4248 | 4248 | channel17 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x1099 | 0x1099 | 4249 | 4249 | channel17 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x109A | 0x109A | 4250 | 4250 | channel17 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1 | 1 |  | [1]
| 0x109B | 0x109B | 4251 | 4251 | channel18 input wiring | uint16_t | R/W | 1 | 1~24 | 18 | 18 |  | [18]
| 0x109C | 0x109C | 4252 | 4252 | channel18 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x109D | 0x109D | 4253 | 4253 | channel18 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x109E | 0x109E | 4254 | 4254 | channel18 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x109F | 0x109F | 4255 | 4255 | channel18voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2 | 2 |  | [2]
| 0x10A0 | 0x10A0 | 4256 | 4256 | channel19 input wiring | uint16_t | R/W | 1 | 1~24 | 19 | 19 |  | [19]
| 0x10A1 | 0x10A1 | 4257 | 4257 | channel19 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x10A2 | 0x10A2 | 4258 | 4258 | channel19 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x10A3 | 0x10A3 | 4259 | 4259 | channel19 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x10A4 | 0x10A4 | 4260 | 4260 | channel19 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0 | 0 |  | [0]
| 0x10A5 | 0x10A5 | 4261 | 4261 | channel20 input wiring | uint16_t | R/W | 1 | 1~24 | 20 | 20 |  | [20]
| 0x10A6 | 0x10A6 | 4262 | 4262 | channel20 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x10A7 | 0x10A7 | 4263 | 4263 | channel20 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x10A8 | 0x10A8 | 4264 | 4264 | channel20 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x10A9 | 0x10A9 | 4265 | 4265 | channel20 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1 | 1 |  | [1]
| 0x10AA | 0x10AA | 4266 | 4266 | channel21 input wiring | uint16_t | R/W | 1 | 1~24 | 21 | 21 |  | [21]
| 0x10AB | 0x10AB | 4267 | 4267 | channel21 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x10AC | 0x10AC | 4268 | 4268 | channel21 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x10AD | 0x10AD | 4269 | 4269 | channel21 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x10AE | 0x10AE | 4270 | 4270 | channel21 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2 | 2 |  | [2]
| 0x10AF | 0x10AF | 4271 | 4271 | channel22 input wiring | uint16_t | R/W | 1 | 1~24 | 22 | 22 |  | [22]
| 0x10B0 | 0x10B0 | 4272 | 4272 | channel22 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x10B1 | 0x10B1 | 4273 | 4273 | channel22 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x10B2 | 0x10B2 | 4274 | 4274 | channel22 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x10B3 | 0x10B3 | 4275 | 4275 | channel22 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 0 | 0 |  | [0]
| 0x10B4 | 0x10B4 | 4276 | 4276 | channel23 input wiring | uint16_t | R/W | 1 | 1~24 | 23 | 23 |  | [23]
| 0x10B5 | 0x10B5 | 4277 | 4277 | channel23 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x10B6 | 0x10B6 | 4278 | 4278 | channel23 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x10B7 | 0x10B7 | 4279 | 4279 | channel23 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x10B8 | 0x10B8 | 4280 | 4280 | channel23 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 1 | 1 |  | [1]
| 0x10B9 | 0x10B9 | 4281 | 4281 | channel24 input wiring | uint16_t | R/W | 1 | 1~24 | 24 | 24 |  | [24]
| 0x10BA | 0x10BA | 4282 | 4282 | channel24 CT type | uint16_t | R/W | 1 | mA type: 0, 1; mV type: 2, 3 0: 100mA 1: 80mA 2: 333mV 3: RCT | 0: 100mA for mA type 2: 333mV for mV type | 0: 100mA for mA type 2: 333mV for mV type |  | [0]
| 0x10BB | 0x10BB | 4283 | 4283 | channel24 primary | uint16_t | R/W | 1 | 1-50000 A | 1000 | 1000 |  | [20]
| 0x10BC | 0x10BC | 4284 | 4284 | channel24 direction | uint16_t | R/W | 1 | 0:positive 1:negative | 0 | 0 |  | [0]
| 0x10BD | 0x10BD | 4285 | 4285 | channel24 voltage assignment | uint16_t | R/W | 1 | 0: Va 1: Vb 2: Vc 3: Vab 4: Vbc 5: Vca | 2 | 2 |  | [2]
| 0x10BE | 0x10BF | 4286 | 4287 | user 1 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 1/2/3, 7 0x07 | channel 1/2/3, 7 0x07 |  | [7]
| 0x10C0 | 0x10C1 | 4288 | 4289 | user 2 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 4/5/6, 56 0x38 | channel 4/5/6, 56 0x38 |  | [56]
| 0x10C2 | 0x10C3 | 4290 | 4291 | user 3 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 7/8/9, 448 0x1C0 | channel 7/8/9, 448 0x1C0 |  | [448]
| 0x10C4 | 0x10C5 | 4292 | 4293 | user 4 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 10/11/12, 3584 0xE00 | channel 10/11/12, 3584 0xE00 |  | [3584]
| 0x10C6 | 0x10C7 | 4294 | 4295 | user 5 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 13/14/15, 28672 0x7000 | channel 13/14/15, 28672 0x7000 |  | [28672]
| 0x10C8 | 0x10C9 | 4296 | 4297 | user 6 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 16/17/18, 229376 0x38000 | channel 16/17/18, 229376 0x38000 |  | [229376]
| 0x10CA | 0x10CB | 4298 | 4299 | user 7 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 19/20/21, 1835008 0x1C0000 | channel 19/20/21, 1835008 0x1C0000 |  | [1835008]
| 0x10CC | 0x10CD | 4300 | 4301 | user 8 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | channel 22/23/24, 14680064 0xE00000 | channel 22/23/24, 14680064 0xE00000 |  | [14680064]
| 0x10CE | 0x10CF | 4302 | 4303 | user 9 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | not in use, 0 | not in use, 0 |  | [0]
| 0x10D0 | 0x10D1 | 4304 | 4305 | user 10 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | not in use, 0 | not in use, 0 |  | [0]
| 0x10D2 | 0x10D3 | 4306 | 4307 | user 11 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | not in use, 0 | not in use, 0 |  | [0]
| 0x10D4 | 0x10D5 | 4308 | 4309 | user 12 input channel assignment | uint32_t | R/W | 2 | bit0~23 for channel1~24，1 is assignment，0 is not assignment | not in use, 0 | not in use, 0 |  | [0]
| 0x10D6 | 0x10D6 | 4310 | 4310 | Demand Method | uint16_t | R/W | 1 | 0: Fixed block, 1: Sliding block | 1 | 1 |  | [1]
| 0x10D7 | 0x10D7 | 4311 | 4311 | Demand Interval | uint16_t | R/W | 1 | 1~30 minute | 15 | 15 |  | [1]
| 0x10D8 | 0x10D8 | 4312 | 4312 | Demand update rate | uint16_t | R/W | 1 | 1~30 minute | 1 | 1 |  | [1]
| 0x10D9 | 0x10D9 | 4313 | 4313 | VAR/PF Convention | uint16_t | R/W | 1 | 0: IEC; 1: IEEE | 0 | 0 |  | [0]
| 0x10DA | 0x10DA | 4314 | 4314 | Energy Calculation Method | uint16_t | R/W | 1 | fixed to 1: Fundament+Harmonics | 1 | 1 |  | [1]
| 0x10DB | 0x10DB | 4315 | 4315 | Reactive Power Calculation Method | uint16_t | R/W | 1 | 0: Generic Reactive Power 1: True Reactive Power | 0 | 0 |  | [0]
| 0x10DC | 0x10DC | 4316 | 4316 | Phase Order | uint16_t | R/W | 1 | 0: ABC 1: ACB | 0 | 0 |  | [0]
| 0x10DD | 0x10DD | 4317 | 4317 | Energy Reading Display format | uint16_t | R/W | 1 | 0: Primary in 0.1 kWh;1:0.01kWh; 2: Primary in 0.001kWh | 0 | 0 |  | [2]
| 0x10DE | 0x10DE | 4318 | 4318 | Basic Reading Display format | uint16_t | R/W | 1 | 0: Secondary 1: Primary | 1 | 1 |  | [0]
| 0x10DF | 0x10E0 | 4319 | 4320 | Energy pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000 |  | [1000]
| 0x10E1 | 0x10E1 | 4321 | 4321 | Pulse LED width | uint16_t | R/W | 1 | 20~100ms | 100 | 100 |  | [100]
| 0x10E2 | 0x10E2 | 4322 | 4322 | Pulse LED parameter selection | uint16_t | R/W | 1 | Energy parameter IDs(1-360) | 0 not in use | 0 |  | [0]
| 0x1100 | 0x1100 | 4352 | 4352 | DO1 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication | 0 | 0 |  | [0]
| 0x1101 | 0x1101 | 4353 | 4353 | DO1 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100 |  | [100]
| 0x1102 | 0x1102 | 4354 | 4354 | DO1 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use | 0 not in use |  | [0]
| 0x1103 | 0x1103 | 4355 | 4355 | DO2 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication | 0 | 0 |  | [0]
| 0x1104 | 0x1104 | 4356 | 4356 | DO2 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100 |  | [100]
| 0x1105 | 0x1105 | 4357 | 4357 | DO2 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use | 0 not in use |  | [0]
| 0x1106 | 0x1106 | 4358 | 4358 | DO3 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication | 0 | 0 |  | [0]
| 0x1107 | 0x1107 | 4359 | 4359 | DO3 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100 |  | [100]
| 0x1108 | 0x1108 | 4360 | 4360 | DO3 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use | 0 not in use |  | [0]
| 0x1109 | 0x1109 | 4361 | 4361 | DO4 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication | 0 | 0 |  | [0]
| 0x110A | 0x110A | 4362 | 4362 | DO4 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100 |  | [100]
| 0x110B | 0x110B | 4363 | 4363 | DO4 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use | 0 not in use |  | [0]
| 0x110C | 0x110C | 4364 | 4364 | DO5 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication | 0 | 0 |  | [0]
| 0x110D | 0x110D | 4365 | 4365 | DO5 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100 |  | [100]
| 0x110E | 0x110E | 4366 | 4366 | DO5 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use | 0 not in use |  | [0]
| 0x110F | 0x110F | 4367 | 4367 | DO6 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication | 0 | 0 |  | [0]
| 0x1110 | 0x1110 | 4368 | 4368 | DO6 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100 |  | [100]
| 0x1111 | 0x1111 | 4369 | 4369 | DO6 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use | 0 not in use |  | [0]
| 0x1112 | 0x1112 | 4370 | 4370 | DO7 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication | 0 | 0 |  | [0]
| 0x1113 | 0x1113 | 4371 | 4371 | DO7 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100 |  | [100]
| 0x1114 | 0x1114 | 4372 | 4372 | DO7 parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use | 0 not in use |  | [0]
| 0x1115 | 0x1115 | 4373 | 4373 | DO8 Type | uint16_t | R/W | 1 | 0: Energy Pulse output 1: Alarm Indication | 0 | 0 |  | [0]
| 0x1116 | 0x1116 | 4374 | 4374 | DO8 Pulse width | uint16_t | R/W | 1 | 20~3000ms | 100 | 100 |  | [100]
| 0x1117 | 0x1117 | 4375 | 4375 | DO8parameter selection | uint16_t | R/W | 1 | Energy parameter IDs | 0 not in use | 0 not in use |  | [0]
| 0x1118 | 0x1118 | 4376 | 4376 | DI1 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0 |  | [0]
| 0x1119 | 0x111A | 4377 | 4378 | DI1 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000 |  | [300]
| 0x111B | 0x111B | 4379 | 4379 | DI2 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0 |  | [0]
| 0x111C | 0x111D | 4380 | 4381 | DI2 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000 |  | [1000]
| 0x111E | 0x111E | 4382 | 4382 | DI3 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0 |  | [0]
| 0x111F | 0x1120 | 4383 | 4384 | DI3 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000 |  | [1000]
| 0x1121 | 0x1121 | 4385 | 4385 | DI4 Type | uint16_t | R/W | 1 | 0: Status Monitor; 1: Pulse Counter | 0 | 0 |  | [0]
| 0x1122 | 0x1123 | 4386 | 4387 | DI4 pulse constant | uint32_t | R/W | 2 | 100—100000000 ( scale:0.001) | 1000 | 1000 |  | [1000]
| 0x1124 | 0x1124 | 4388 | 4388 | RO1 Type | uint16_t | R/W | 1 | 0: Relay Output 1: Alarm Indication | 0 | 0 |  | [0]
| 0x1125 | 0x1125 | 4389 | 4389 | RO1 Control Mode | uint16_t | R/W | 1 | Alarm Indication： 0: Latch 2: Manual Relay Output： 0: Latch 1: Momentary | 0 | 0 |  | [0]
| 0x1126 | 0x1126 | 4390 | 4390 | RO1 Pulse Width | uint16_t | R/W | 1 | 20 - 3000 ms | 1000 | 1000 |  | [100]
| 0x1127 | 0x1127 | 4391 | 4391 | RO2 Type | uint16_t | R/W | 1 | 0: Relay 1: Alarm | 0 | 0 |  | [0]
| 0x1128 | 0x1128 | 4392 | 4392 | RO2 Control Mode | uint16_t | R/W | 1 | 0: Latch 1: Momentary 2: Manual | 0 | 0 |  | [0]
| 0x1129 | 0x1129 | 4393 | 4393 | RO2 Pulse Width | uint16_t | R/W | 1 | 20 - 3000 ms | 1000 | 1000 |  | [100]

## test_case_mV-1e2w1p (hidden)
test_case | Phase_A_Voltage | Phase_B_Voltage | Phase_C_Voltage | Phase_A_Current | Phase_B_Current | Phase_C_Current | Va_angle | Vb_angle | Vc_angle | Ia_angle | Ib_angle | Ic_angle | 等待时间(h) | PF | 接线方式 | 频率（Hz） | voltage_accuracy | current_accuracy | phase_angle_accuracy | active_power_accuracy | reactive_power_accuracy | apparent_power_accuracy | 采样次数 | 采样间隔 | 备注
Acuvim2v3_case98 | 312.3 | 0 | 0 | 2.5 | 0 | 0 | 0 | 240 | 120 | 0 | 240 | 120 | 0 | 1 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP20, 偏差不超过 0.2% | 0 | 0 | 5 | 0.1 | 相比TP20, 偏差不超过 0.2%
Acuvim2v3_case99 | 312.3 | 0 | 0 | 2.5 | 0 | 0 | 0 | 240 | 120 | 300 | 180 | 60 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP21, 偏差不超过 0.4% | 0 | 0 | 5 | 0.1 | 相比TP21, 偏差不超过 0.4%
Acuvim2v3_case100 | 312.3 | 0 | 0 | 2.5 | 0 | 0 | 0 | 240 | 120 | 216.87 | 96.87 | 336.87 | 0 | -0.8 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP22, 偏差不超过 0.4% | 0 | 0 | 5 | 0.1 | 相比TP22, 偏差不超过 0.4%
Acuvim2v3_case101 | 381.7 | 0 | 0 | 2.5 | 0 | 0 | 0 | 240 | 120 | 0 | 240 | 120 | 0 | 1 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP20, 偏差不超过 0.2% | 0 | 0 | 5 | 0.1 | 相比TP20, 偏差不超过 0.2%
Acuvim2v3_case102 | 381.7 | 0 | 0 | 2.5 | 0 | 0 | 0 | 240 | 120 | 300 | 180 | 60 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP21, 偏差不超过 0.4% | 0 | 0 | 5 | 0.1 | 相比TP21, 偏差不超过 0.4%
Acuvim2v3_case103 | 381.7 | 0 | 0 | 2.5 | 0 | 0 | 0 | 240 | 120 | 216.87 | 96.87 | 336.87 | 0 | -0.8 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP22, 偏差不超过 0.4% | 0 | 0 | 5 | 0.1 | 相比TP22, 偏差不超过 0.4%
Acuvim2v3_case104 | 347 | 0 | 0 | 2.5 | 0 | 0 | 0 | 240 | 120 | 0 | 240 | 120 | 0 | 1 | 1E2w1p | 57 | 0.001 | 0.001 | 0.1 | 相比TP20, 偏差不超过 0.2% | 0 | 0 | 5 | 0.1 | 相比TP20, 偏差不超过 0.2%
Acuvim2v3_case105 | 347 | 0 | 0 | 2.5 | 0 | 0 | 0 | 240 | 120 | 0 | 240 | 120 | 0 | 1 | 1E2w1p | 63 | 0.001 | 0.001 | 0.1 | 相比TP20, 偏差不超过 0.2% | 0 | 0 | 5 | 0.1 | 相比TP20, 偏差不超过 0.2%

## test_case_mA-1e2w1p (hidden)
test_case | Phase_A_Voltage | Phase_B_Voltage | Phase_C_Voltage | Phase_A_Current | Phase_B_Current | Phase_C_Current | Va_angle | Vb_angle | Vc_angle | Ia_angle | Ib_angle | Ic_angle | 等待时间(h) | PF | 接线方式 | 频率（Hz） | voltage_accuracy | current_accuracy | phase_angle_accuracy | active_power_accuracy | reactive_power_accuracy | apparent_power_accuracy | 采样次数 | 采样间隔 | 备注
Acuvim2v3_case98 | 312.3 | 0 | 0 | 8 | 0 | 0 | 0 | 240 | 120 | 0 | 240 | 120 | 0 | 1 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP20, 偏差不超过 0.2% | 0 | 0 | 5 | 0.1 | 相比TP20, 偏差不超过 0.2%
Acuvim2v3_case99 | 312.3 | 0 | 0 | 8 | 0 | 0 | 0 | 240 | 120 | 300 | 180 | 60 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP21, 偏差不超过 0.4% | 0 | 0 | 5 | 0.1 | 相比TP21, 偏差不超过 0.4%
Acuvim2v3_case100 | 312.3 | 0 | 0 | 8 | 0 | 0 | 0 | 240 | 120 | 216.87 | 96.87 | 336.87 | 0 | -0.8 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP22, 偏差不超过 0.4% | 0 | 0 | 5 | 0.1 | 相比TP22, 偏差不超过 0.4%
Acuvim2v3_case101 | 381.7 | 0 | 0 | 8 | 0 | 0 | 0 | 240 | 120 | 0 | 240 | 120 | 0 | 1 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP20, 偏差不超过 0.2% | 0 | 0 | 5 | 0.1 | 相比TP20, 偏差不超过 0.2%
Acuvim2v3_case102 | 381.7 | 0 | 0 | 8 | 0 | 0 | 0 | 240 | 120 | 300 | 180 | 60 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP21, 偏差不超过 0.4% | 0 | 0 | 5 | 0.1 | 相比TP21, 偏差不超过 0.4%
Acuvim2v3_case103 | 381.7 | 0 | 0 | 8 | 0 | 0 | 0 | 240 | 120 | 216.87 | 96.87 | 336.87 | 0 | -0.8 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 相比TP22, 偏差不超过 0.4% | 0 | 0 | 5 | 0.1 | 相比TP22, 偏差不超过 0.4%
Acuvim2v3_case104 | 347 | 0 | 0 | 8 | 0 | 0 | 0 | 240 | 120 | 0 | 240 | 120 | 0 | 1 | 1E2w1p | 57 | 0.001 | 0.001 | 0.1 | 相比TP20, 偏差不超过 0.2% | 0 | 0 | 5 | 0.1 | 相比TP20, 偏差不超过 0.2%
Acuvim2v3_case105 | 347 | 0 | 0 | 8 | 0 | 0 | 0 | 240 | 120 | 0 | 240 | 120 | 0 | 1 | 1E2w1p | 63 | 0.001 | 0.001 | 0.1 | 相比TP20, 偏差不超过 0.2% | 0 | 0 | 5 | 0.1 | 相比TP20, 偏差不超过 0.2%

## test_data (hidden)
test_case | Phase_A_Voltage | Phase_B_Voltage | Phase_C_Voltage | Phase_A_Current | Phase_B_Current | Phase_C_Current | Va_angle | Vb_angle | Vc_angle | Ia_angle | Ib_angle | Ic_angle | 等待时间(h) | PF | 接线方式 | 频率（Hz） | voltage_accuracy | current_accuracy | phase_angle_accuracy | active_power_accuracy | reactive_power_accuracy | apparent_power_accuracy | 采样次数 | 采样间隔 | 备注
Acuvim2v3_case1 | 69 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.002 | 0.1 | 0.004 | 0 | 0 | 3000 | 0.1
Acuvim2v3_case2 | 69 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.002 | 0.1 | 0.004 | 0 | 0 | 3000 | 0.1
Acuvim2v3_case3 | 69 | 0 | 0 | 0.5 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.002 | 0.1 | 0.004 | 0 | 0 | 3000 | 0.1
Acuvim2v3_case4 | 69 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.002 | 0.1 | 0.004 | 0 | 0 | 3000 | 0.1
Acuvim2v3_case5 | 69 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.002 | 0.1 | 0.004 | 0 | 0 | 3000 | 0.1
Acuvim2v3_case6 | 69 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.002 | 0.1 | 0.004 | 0 | 0 | 3000 | 0.1
Acuvim2v3_case7 | 69 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.002 | 0.1 | 0.004 | 0 | 0 | 3000 | 0.1
Acuvim2v3_case8 | 69 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0.5 | 1E2w1p | 60 | 0.001 | 0.001 | 0.1 | 0.004 | 0 | 0 | 3000 | 0.1