## 汇总
项目 | 数量
总参数条目 | 2602
PASS | 1969
FAIL | 2
Modbus 读取失败 | 0
无寄存器映射 | 572
通过率 | 97.0%

## 明细
设备 | 视图 | 通道/选项 | 参数 | 列 | 网页值 | Modbus值 | 差值 | 差值% | 寄存器地址(Dec) | 地址(Hex) | 类型 | 寄存器描述 | paramId | 结果
AcuvimIIW | THD | (system) | Voltage THD Odd (%) | Phase A | 0.000 | 0.01 | -0.01 | 1000000000 | 16512 | 0x4080 | int16 | Phase A Voltage Odd THD | 3-39 | PASS
AcuvimIIW | THD | (system) | Voltage THD Odd (%) | Phase B | 0.000 | 0.01 | -0.01 | 1000000000 | 16546 | 0x40A2 | int16 | Phase B Voltage Odd THD | 3-73 | PASS
AcuvimIIW | Realtime | (system) | Reactive Power (kvar) | Phase C | 0.000 | 0.0024 | -0.0024 | 240000000 | 16424 | 0x4028 | float32 | Phase C Reactive Power | 1-21 | PASS
Acurev4100 | Harmonics | (system) | 10 | Phase C | 0.000 | 0.0012 | -0.0012 | 120000000 | 9908 | 0x26B4 | float32 | Phase C Voltage individual Harmonics 10 percentage | 15-14 | PASS
Acurev4100 | Harmonics | (system) | 24 | Phase B | 0.000 | 0.0011 | -0.0011 | 110000000 | 9866 | 0x268A | float32 | Phase B Voltage individual Harmonics 24 percentage | 14-28 | PASS
Acurev4100 | Harmonics | (system) | 12 | Phase A | 0.000 | 0.001 | -0.001 | 100000000 | 9772 | 0x262C | float32 | Phase A Voltage individual Harmonics 12 percentage | 13-23 | PASS
Acurev4100 | Harmonics | (system) | 28 | Phase A | 0.000 | 0.001 | -0.001 | 100000000 | 9804 | 0x264C | float32 | Phase A Voltage individual Harmonics 28 percentage | 13-39 | PASS
Acurev4100 | Harmonics | (system) | 10 | Phase B | 0.000 | 0.0007 | -0.0007 | 70000000 | 9838 | 0x266E | float32 | Phase B Voltage individual Harmonics 10 percentage | 14-14 | PASS
Acurev4100 | Harmonics | (system) | 16 | Phase B | 0.000 | 0.0007 | -0.0007 | 70000000 | 9850 | 0x267A | float32 | Phase B Voltage individual Harmonics 16 percentage | 14-20 | PASS
Acurev4100 | Harmonics | (system) | 16 | Phase C | 0.000 | 0.0007 | -0.0007 | 70000000 | 9920 | 0x26C0 | float32 | Phase C Voltage individual Harmonics 16 percentage | 15-20 | PASS
Acurev4100 | Harmonics | (system) | 24 | Phase C | 0.000 | 0.0006 | -0.0006 | 60000000 | 9936 | 0x26D0 | float32 | Phase C Voltage individual Harmonics 24 percentage | 15-28 | PASS
Acuvim3 | Realtime | (system) | Neutral Current (A) | System | 0.000 | 0.0005 | -0.0005 | 50000000 | 8492 | 0x212C | float32 | Neutral Current | 1-13 | PASS
Acurev4100 | Harmonics | (system) | 28 | Phase C | 0.000 | 0.0004 | -0.0004 | 40000000 | 9944 | 0x26D8 | float32 | Phase C Voltage individual Harmonics 28 percentage | 15-32 | PASS
Acurev4100 | Harmonics | (system) | 20 | Phase A | 0.000 | 0.0003 | -0.0003 | 30000000 | 9788 | 0x263C | float32 | Phase A Voltage individual Harmonics 20 percentage | 13-31 | PASS
Acurev4100 | Harmonics | (system) | 20 | Phase B | 0.000 | 0.0003 | -0.0003 | 30000000 | 9858 | 0x2682 | float32 | Phase B Voltage individual Harmonics 20 percentage | 14-24 | PASS
Acurev4100 | Harmonics | (system) | 20 | Phase C | 0.000 | 0.0002 | -0.0002 | 20000000 | 9928 | 0x26C8 | float32 | Phase C Voltage individual Harmonics 20 percentage | 15-24 | PASS
Acurev4100 | Harmonics | (system) | 22 | Phase B | 0.000 | 0.0002 | -0.0002 | 20000000 | 9862 | 0x2686 | float32 | Phase B Voltage individual Harmonics 22 percentage | 14-26 | PASS
AcuvimIIW | Realtime | (system) | Reactive Power (kvar) | System | -0.003 | 0.0035 | -0.0065 | 216.67 | 16426 | 0x402A | float32 | System Reactive Power | 1-22 | PASS
Acurev4100 | Harmonics | (system) | 2 | Phase B | 0.001 | 0.0025 | -0.0015 | 150 | 9822 | 0x265E | float32 | Phase B Voltage individual Harmonics 2 percentage | 14-6 | PASS
AcuvimIIW | Realtime | (system) | Reactive Power (kvar) | Phase B | -0.003 | 0 | -0.003 | 100 | 16422 | 0x4026 | float32 | Phase B Reactive Power | 1-20 | PASS
AcuvimIIW | THD | (system) | Current THD (%) | Phase B | 0.010 | 0.02 | -0.01 | 100 | 16479 | 0x405F | int16 | Phase B Current THD | 3-6 | PASS
Acurev4100 | Sequence | User Channel 1:name1 | Current Sequence Magnitude | Positive | 0.003 | 0 | 0.003 | 100 | 11590 | 0x2D46 | float32 | User Channel 1 Current Positive Sequence Magnitude | 40-1 | PASS
Acurev4100 | Sequence | User Channel 1:name1 | Current Sequence Magnitude | Negative | 0.003 | 0 | 0.003 | 100 | 11594 | 0x2D4A | float32 | User Channel 1 Current Negative Sequence Magnitude | 40-3 | PASS
Acurev4100 | Sequence | User Channel 1:name1 | Current | Unbalance Factor | 111.276% | 0 | 111.276 | 100 | 11602 | 0x2D52 | float32 | User Channel 1 Current Unbalance Factor Magnitude | 40-7 | FAIL
Acurev4100 | Sequence | User Channel 2:name1 | Current Sequence Magnitude | Positive | 0.003 | 0 | 0.003 | 100 | 11604 | 0x2D54 | float32 | User Channel 2 Current Positive Sequence Magnitude | 40-8 | PASS
Acurev4100 | Sequence | User Channel 2:name1 | Current Sequence Magnitude | Negative | 0.004 | 0 | 0.004 | 100 | 11608 | 0x2D58 | float32 | User Channel 2 Current Negative Sequence Magnitude | 40-10 | PASS
Acurev4100 | Sequence | User Channel 2:name1 | Current | Unbalance Factor | 119.560% | 0 | 119.56 | 100 | 11616 | 0x2D60 | float32 | User Channel 2 Current Unbalance Factor Magnitude | 40-14 | FAIL
Acurev4100 | Sequence | User Channel 6:6666 | Current Sequence Magnitude | Zero | 0.003 | 0 | 0.003 | 100 | 11662 | 0x2D8E | float32 | User Channel 6 Current Zero Sequence Magnitude | 40-37 | PASS
Acurev4100 | Harmonics | (system) | 30 | Phase C | 0.001 | 0.0001 | 0.0009 | 90 | 9948 | 0x26DC | float32 | Phase C Voltage individual Harmonics 30 percentage | 15-34 | PASS
Acurev4100 | Harmonics | (system) | 9 | Phase C | 0.001 | 0.0002 | 0.0008 | 80 | 9906 | 0x26B2 | float32 | Phase C Voltage individual Harmonics 9 percentage | 15-13 | PASS
Acurev4100 | Harmonics | (system) | 6 | Phase B | 0.001 | 0.0003 | 0.0007 | 70 | 9830 | 0x2666 | float32 | Phase B Voltage individual Harmonics 6 percentage | 14-10 | PASS
Acurev4100 | Harmonics | (system) | 17 | Phase C | 0.001 | 0.0017 | -0.0007 | 70 | 9922 | 0x26C2 | float32 | Phase C Voltage individual Harmonics 17 percentage | 15-21 | PASS
Acurev4100 | Harmonics | (system) | 26 | Phase A | 0.001 | 0.0003 | 0.0007 | 70 | 9800 | 0x2648 | float32 | Phase A Voltage individual Harmonics 26 percentage | 13-37 | PASS
Acurev4100 | Harmonics | (system) | 4 | Phase C | 0.001 | 0.0004 | 0.0006 | 60 | 9896 | 0x26A8 | float32 | Phase C Voltage individual Harmonics 4 percentage | 15-8 | PASS
Acurev4100 | Harmonics | (system) | 17 | Phase B | 0.002 | 0.0008 | 0.0012 | 60 | 9852 | 0x267C | float32 | Phase B Voltage individual Harmonics 17 percentage | 14-21 | PASS
AcuvimIIW | Sequence | (system) | Voltage | Unbalance Factor | 0.008% | 0.0127 | -0.0047 | 58.75 | 16444 | 0x403C | float32 | Voltage Unbalance Factor | 1-31 | PASS
Acurev4100 | Sequence | User Channel 2:name1 | Current Sequence Magnitude | Zero | 0.003 | 0.0046 | -0.0016 | 53.33 | 11606 | 0x2D56 | float32 | User Channel 2 Current Zero Sequence Magnitude | 40-9 | PASS
Acurev4100 | Harmonics | (system) | 4 | Phase A | 0.001 | 0.0005 | 0.0005 | 50 | 9756 | 0x261C | float32 | Phase A Voltage individual Harmonics 4 percentage | 13-15 | PASS
Acurev4100 | Harmonics | (system) | 8 | Phase A | 0.001 | 0.0005 | 0.0005 | 50 | 9764 | 0x2624 | float32 | Phase A Voltage individual Harmonics 8 percentage | 13-19 | PASS
Acurev4100 | Harmonics | (system) | 11 | Phase C | 0.001 | 0.0005 | 0.0005 | 50 | 9910 | 0x26B6 | float32 | Phase C Voltage individual Harmonics 11 percentage | 15-15 | PASS
Acurev4100 | Harmonics | (system) | 12 | Phase C | 0.001 | 0.0005 | 0.0005 | 50 | 9912 | 0x26B8 | float32 | Phase C Voltage individual Harmonics 12 percentage | 15-16 | PASS
Acurev4100 | Harmonics | (system) | 14 | Phase B | 0.001 | 0.0005 | 0.0005 | 50 | 9846 | 0x2676 | float32 | Phase B Voltage individual Harmonics 14 percentage | 14-18 | PASS
Acurev4100 | Harmonics | (system) | 14 | Phase C | 0.001 | 0.0005 | 0.0005 | 50 | 9916 | 0x26BC | float32 | Phase C Voltage individual Harmonics 14 percentage | 15-18 | PASS
Acurev4100 | Harmonics | (system) | 24 | Phase A | 0.001 | 0.0005 | 0.0005 | 50 | 9796 | 0x2644 | float32 | Phase A Voltage individual Harmonics 24 percentage | 13-35 | PASS
Acurev4100 | Harmonics | (system) | 26 | Phase C | 0.001 | 0.0005 | 0.0005 | 50 | 9940 | 0x26D4 | float32 | Phase C Voltage individual Harmonics 26 percentage | 15-30 | PASS
Acurev4100 | Harmonics | (system) | 30 | Phase A | 0.001 | 0.0015 | -0.0005 | 50 | 9808 | 0x2650 | float32 | Phase A Voltage individual Harmonics 30 percentage | 13-41 | PASS
Acurev4100 | Harmonics | (system) | 30 | Phase B | 0.001 | 0.0005 | 0.0005 | 50 | 9878 | 0x2696 | float32 | Phase B Voltage individual Harmonics 30 percentage | 14-34 | PASS
Acurev4100 | Harmonics | (system) | 29 | Phase B | 0.003 | 0.0044 | -0.0014 | 46.67 | 9876 | 0x2694 | float32 | Phase B Voltage individual Harmonics 29 percentage | 14-33 | PASS
Acurev4100 | Harmonics | (system) | 11 | Phase B | 0.001 | 0.0014 | -0.0004 | 40 | 9840 | 0x2670 | float32 | Phase B Voltage individual Harmonics 11 percentage | 14-15 | PASS
Acurev4100 | Harmonics | (system) | 14 | Phase A | 0.001 | 0.0006 | 0.0004 | 40 | 9776 | 0x2630 | float32 | Phase A Voltage individual Harmonics 14 percentage | 13-25 | PASS
Acurev4100 | Harmonics | (system) | 18 | Phase A | 0.001 | 0.0006 | 0.0004 | 40 | 9784 | 0x2638 | float32 | Phase A Voltage individual Harmonics 18 percentage | 13-29 | PASS
Acurev4100 | Harmonics | (system) | 18 | Phase B | 0.001 | 0.0006 | 0.0004 | 40 | 9854 | 0x267E | float32 | Phase B Voltage individual Harmonics 18 percentage | 14-22 | PASS
Acurev4100 | Harmonics | (system) | 18 | Phase C | 0.001 | 0.0014 | -0.0004 | 40 | 9924 | 0x26C4 | float32 | Phase C Voltage individual Harmonics 18 percentage | 15-22 | PASS
Acurev4100 | Harmonics | (system) | 9 | Phase B | 0.002 | 0.0013 | 0.0007 | 35 | 9836 | 0x266C | float32 | Phase B Voltage individual Harmonics 9 percentage | 14-13 | PASS
Acurev4100 | Harmonics | (system) | 11 | Phase A | 0.002 | 0.0013 | 0.0007 | 35 | 9770 | 0x262A | float32 | Phase A Voltage individual Harmonics 11 percentage | 13-22 | PASS
AcuvimIIW | THD | (system) | Voltage THD (%) | Phase A | 0.030 | 0.02 | 0.01 | 33.33 | 16474 | 0x405A | int16 | Phase A Voltage THD | 3-1 | PASS
AcuvimIIW | THD | (system) | Voltage THD (%) | Phase B | 0.030 | 0.02 | 0.01 | 33.33 | 16475 | 0x405B | int16 | Phase B Voltage THD | 3-2 | PASS
AcuvimIIW | THD | (system) | Voltage THD (%) | Phase C | 0.030 | 0.02 | 0.01 | 33.33 | 16476 | 0x405C | int16 | Phase C Voltage THD | 3-3 | PASS
AcuvimIIW | THD | (system) | Voltage THD (%) | Average | 0.030 | 0.02 | 0.01 | 33.33 | 16477 | 0x405D | int16 | Average Voltage THD | 3-4 | PASS
AcuvimIIW | THD | (system) | Voltage THD Even (%) | Phase A | 0.030 | 0.02 | 0.01 | 33.33 | 16513 | 0x4081 | int16 | Phase A Voltage Even THD | 3-40 | PASS
AcuvimIIW | THD | (system) | Voltage THD Even (%) | Phase B | 0.030 | 0.02 | 0.01 | 33.33 | 16547 | 0x40A3 | int16 | Phase B Voltage Even THD | 3-74 | PASS
Acurev4100 | Harmonics | (system) | 9 | Phase A | 0.002 | 0.0014 | 0.0006 | 30 | 9766 | 0x2626 | float32 | Phase A Voltage individual Harmonics 9 percentage | 13-20 | PASS
Acurev4100 | Harmonics | (system) | 10 | Phase A | 0.001 | 0.0013 | -0.0003 | 30 | 9768 | 0x2628 | float32 | Phase A Voltage individual Harmonics 10 percentage | 13-21 | PASS
Acurev4100 | Harmonics | (system) | 16 | Phase A | 0.001 | 0.0007 | 0.0003 | 30 | 9780 | 0x2634 | float32 | Phase A Voltage individual Harmonics 16 percentage | 13-27 | PASS
Acurev4100 | Harmonics | (system) | 22 | Phase A | 0.001 | 0.0007 | 0.0003 | 30 | 9792 | 0x2640 | float32 | Phase A Voltage individual Harmonics 22 percentage | 13-33 | PASS
Acurev4100 | Harmonics | (system) | 22 | Phase C | 0.001 | 0.0013 | -0.0003 | 30 | 9932 | 0x26CC | float32 | Phase C Voltage individual Harmonics 22 percentage | 15-26 | PASS
Acurev4100 | Harmonics | (system) | 5 | Phase B | 0.004 | 0.0051 | -0.0011 | 27.5 | 9828 | 0x2664 | float32 | Phase B Voltage individual Harmonics 5 percentage | 14-9 | PASS
Acurev4100 | Harmonics | (system) | 13 | Phase B | 0.004 | 0.0029 | 0.0011 | 27.5 | 9844 | 0x2674 | float32 | Phase B Voltage individual Harmonics 13 percentage | 14-17 | PASS
Acurev4100 | Harmonics | (system) | 19 | Phase C | 0.003 | 0.0022 | 0.0008 | 26.67 | 9926 | 0x26C6 | float32 | Phase C Voltage individual Harmonics 19 percentage | 15-23 | PASS
Acurev4100 | Harmonics | (system) | 21 | Phase B | 0.003 | 0.0022 | 0.0008 | 26.67 | 9860 | 0x2684 | float32 | Phase B Voltage individual Harmonics 21 percentage | 14-25 | PASS
Acurev4100 | Harmonics | (system) | 31 | Phase C | 0.003 | 0.0022 | 0.0008 | 26.67 | 9950 | 0x26DE | float32 | Phase C Voltage individual Harmonics 31 percentage | 15-35 | PASS
Acurev4100 | Harmonics | (system) | 29 | Phase A | 0.005 | 0.0062 | -0.0012 | 24 | 9806 | 0x264E | float32 | Phase A Voltage individual Harmonics 29 percentage | 13-40 | PASS
Acurev4100 | Harmonics | (system) | 19 | Phase B | 0.003 | 0.0037 | -0.0007 | 23.33 | 9856 | 0x2680 | float32 | Phase B Voltage individual Harmonics 19 percentage | 14-23 | PASS
Acurev4100 | Harmonics | (system) | 23 | Phase B | 0.003 | 0.0037 | -0.0007 | 23.33 | 9864 | 0x2688 | float32 | Phase B Voltage individual Harmonics 23 percentage | 14-27 | PASS
Acurev4100 | THD | (system) | Voltage THD Even | Phase A | 0.004 | 0.0048 | -0.0008 | 20 | 9746 | 0x2612 | float32 | Phase A Voltage THD Even | 13-10 | PASS
Acurev4100 | THD | (system) | Voltage THD Even | Phase B | 0.003 | 0.0036 | -0.0006 | 20 | 9816 | 0x2658 | float32 | Phase B Voltage THD Even | 14-3 | PASS
Acurev4100 | Harmonics | (system) | 2 | Phase C | 0.001 | 0.0012 | -0.0002 | 20 | 9892 | 0x26A4 | float32 | Phase C Voltage individual Harmonics 2 percentage | 15-6 | PASS
Acurev4100 | Harmonics | (system) | 8 | Phase B | 0.001 | 0.0008 | 0.0002 | 20 | 9834 | 0x266A | float32 | Phase B Voltage individual Harmonics 8 percentage | 14-12 | PASS
Acurev4100 | Harmonics | (system) | 12 | Phase B | 0.001 | 0.0008 | 0.0002 | 20 | 9842 | 0x2672 | float32 | Phase B Voltage individual Harmonics 12 percentage | 14-16 | PASS
Acurev4100 | Harmonics | (system) | 23 | Phase C | 0.004 | 0.0032 | 0.0008 | 20 | 9934 | 0x26CE | float32 | Phase C Voltage individual Harmonics 23 percentage | 15-27 | PASS
Acurev4100 | Harmonics | (system) | 25 | Phase B | 0.006 | 0.0048 | 0.0012 | 20 | 9868 | 0x268C | float32 | Phase B Voltage individual Harmonics 25 percentage | 14-29 | PASS
Acurev4100 | Harmonics | (system) | 27 | Phase A | 0.008 | 0.0096 | -0.0016 | 20 | 9802 | 0x264A | float32 | Phase A Voltage individual Harmonics 27 percentage | 13-38 | PASS
Acurev4100 | Harmonics | (system) | 27 | Phase B | 0.004 | 0.0048 | -0.0008 | 20 | 9872 | 0x2690 | float32 | Phase B Voltage individual Harmonics 27 percentage | 14-31 | PASS
Acurev4100 | Harmonics | (system) | 25 | Phase C | 0.005 | 0.0059 | -0.0009 | 18 | 9938 | 0x26D2 | float32 | Phase C Voltage individual Harmonics 25 percentage | 15-29 | PASS
Acurev4100 | Harmonics | (system) | 7 | Phase A | 0.004 | 0.0033 | 0.0007 | 17.5 | 9762 | 0x2622 | float32 | Phase A Voltage individual Harmonics 7 percentage | 13-18 | PASS
Acurev4100 | Harmonics | (system) | 13 | Phase C | 0.003 | 0.0035 | -0.0005 | 16.67 | 9914 | 0x26BA | float32 | Phase C Voltage individual Harmonics 13 percentage | 15-17 | PASS
AcuvimIIW | Sequence | (system) | Current | Unbalance Factor | 0.006% | 0.0069 | -0.0009 | 15 | 16446 | 0x403E | float32 | Current Unbalance Factor | 1-32 | PASS
Acurev4100 | Harmonics | (system) | 2 | Phase A | 0.002 | 0.0023 | -0.0003 | 15 | 9752 | 0x2618 | float32 | Phase A Voltage individual Harmonics 2 percentage | 13-13 | PASS
Acurev4100 | Harmonics | (system) | 15 | Phase B | 0.004 | 0.0034 | 0.0006 | 15 | 9848 | 0x2678 | float32 | Phase B Voltage individual Harmonics 15 percentage | 14-19 | PASS
Acurev4100 | Harmonics | (system) | 3 | Phase A | 0.012 | 0.0136 | -0.0016 | 13.33 | 9754 | 0x261A | float32 | Phase A Voltage individual Harmonics 3 percentage | 13-14 | PASS
Acurev4100 | Harmonics | (system) | 7 | Phase B | 0.003 | 0.0026 | 0.0004 | 13.33 | 9832 | 0x2668 | float32 | Phase B Voltage individual Harmonics 7 percentage | 14-11 | PASS
Acurev4100 | Harmonics | (system) | 27 | Phase C | 0.004 | 0.0045 | -0.0005 | 12.5 | 9942 | 0x26D6 | float32 | Phase C Voltage individual Harmonics 27 percentage | 15-31 | PASS
Acurev4100 | THD | (system) | Voltage THD Even | Phase C | 0.005 | 0.0044 | 0.0006 | 12 | 9886 | 0x269E | float32 | Phase C Voltage THD Even | 15-3 | PASS
Acurev4100 | THD | (system) | Voltage THD | Phase C | 0.024 | 0.0267 | -0.0027 | 11.25 | 9882 | 0x269A | float32 | Phase C Voltage THD | 15-1 | PASS
Acurev4100 | Harmonics | (system) | 5 | Phase A | 0.007 | 0.0063 | 0.0007 | 10 | 9758 | 0x261E | float32 | Phase A Voltage individual Harmonics 5 percentage | 13-16 | PASS
Acurev4100 | Harmonics | (system) | 8 | Phase C | 0.001 | 0.0011 | -0.0001 | 10 | 9904 | 0x26B0 | float32 | Phase C Voltage individual Harmonics 8 percentage | 15-12 | PASS
Acurev4100 | Harmonics | (system) | 25 | Phase A | 0.009 | 0.0099 | -0.0009 | 10 | 9798 | 0x2646 | float32 | Phase A Voltage individual Harmonics 25 percentage | 13-36 | PASS
Acurev4100 | Harmonics | (system) | 26 | Phase B | 0.001 | 0.0009 | 0.0001 | 10 | 9870 | 0x268E | float32 | Phase B Voltage individual Harmonics 26 percentage | 14-30 | PASS
Acurev4100 | Harmonics | (system) | 28 | Phase B | 0.001 | 0.0009 | 0.0001 | 10 | 9874 | 0x2692 | float32 | Phase B Voltage individual Harmonics 28 percentage | 14-32 | PASS
Acurev4100 | Harmonics | (system) | 29 | Phase C | 0.003 | 0.0033 | -0.0003 | 10 | 9946 | 0x26DA | float32 | Phase C Voltage individual Harmonics 29 percentage | 15-33 | PASS
Acurev4100 | Harmonics | (system) | 31 | Phase A | 0.007 | 0.0063 | 0.0007 | 10 | 9810 | 0x2652 | float32 | Phase A Voltage individual Harmonics 31 percentage | 13-42 | PASS
Acurev4100 | Harmonics | (system) | 31 | Phase B | 0.003 | 0.0027 | 0.0003 | 10 | 9880 | 0x2698 | float32 | Phase B Voltage individual Harmonics 31 percentage | 14-35 | PASS
Acurev4100 | THD | (system) | Voltage THD Odd | Phase C | 0.024 | 0.0263 | -0.0023 | 9.58 | 9884 | 0x269C | float32 | Phase C Voltage THD Odd | 15-2 | PASS
Acurev4100 | THD | (system) | Voltage THD | Phase B | 0.018 | 0.0197 | -0.0017 | 9.44 | 9812 | 0x2654 | float32 | Phase B Voltage THD | 14-1 | PASS
Acurev4100 | THD | (system) | Voltage THD Odd | Average | 0.022 | 0.024 | -0.002 | 9.09 | 9954 | 0x26E2 | float32 | Average Voltage THD Odd | 16-2 | PASS
Acurev4100 | Harmonics | (system) | 5 | Phase C | 0.006 | 0.0065 | -0.0005 | 8.33 | 9898 | 0x26AA | float32 | Phase C Voltage individual Harmonics 5 percentage | 15-9 | PASS
Acurev4100 | Harmonics | (system) | 13 | Phase A | 0.005 | 0.0054 | -0.0004 | 8 | 9774 | 0x262E | float32 | Phase A Voltage individual Harmonics 13 percentage | 13-24 | PASS
Acurev4100 | THD | (system) | Voltage THD Odd | Phase B | 0.018 | 0.0194 | -0.0014 | 7.78 | 9814 | 0x2656 | float32 | Phase B Voltage THD Odd | 14-2 | PASS
Acurev4100 | THD | (system) | Voltage THD Even | Average | 0.004 | 0.0043 | -0.0003 | 7.5 | 9956 | 0x26E4 | float32 | Average Voltage THD Even | 16-3 | PASS
Acurev4100 | Harmonics | (system) | 15 | Phase C | 0.004 | 0.0043 | -0.0003 | 7.5 | 9918 | 0x26BE | float32 | Phase C Voltage individual Harmonics 15 percentage | 15-19 | PASS
Acurev4100 | Harmonics | (system) | 17 | Phase A | 0.003 | 0.0032 | -0.0002 | 6.67 | 9782 | 0x2636 | float32 | Phase A Voltage individual Harmonics 17 percentage | 13-28 | PASS
Acurev4100 | Harmonics | (system) | 19 | Phase A | 0.006 | 0.0056 | 0.0004 | 6.67 | 9786 | 0x263A | float32 | Phase A Voltage individual Harmonics 19 percentage | 13-30 | PASS
Acurev4100 | Harmonics | (system) | 21 | Phase C | 0.003 | 0.0032 | -0.0002 | 6.67 | 9930 | 0x26CA | float32 | Phase C Voltage individual Harmonics 21 percentage | 15-25 | PASS
Acurev4100 | Harmonics | (system) | 15 | Phase A | 0.007 | 0.0066 | 0.0004 | 5.71 | 9778 | 0x2632 | float32 | Phase A Voltage individual Harmonics 15 percentage | 13-26 | PASS
Acurev4100 | THD | (system) | Voltage THD | Average | 0.023 | 0.0243 | -0.0013 | 5.65 | 9952 | 0x26E0 | float32 | Average Voltage THD | 16-1 | PASS
Acurev4100 | Harmonics | (system) | 3 | Phase B | 0.017 | 0.0161 | 0.0009 | 5.29 | 9824 | 0x2660 | float32 | Phase B Voltage individual Harmonics 3 percentage | 14-7 | PASS
Acurev4100 | Harmonics | (system) | 4 | Phase B | 0.002 | 0.0019 | 0.0001 | 5 | 9826 | 0x2662 | float32 | Phase B Voltage individual Harmonics 4 percentage | 14-8 | PASS
Acurev4100 | Harmonics | (system) | 23 | Phase A | 0.007 | 0.0072 | -0.0002 | 2.86 | 9794 | 0x2642 | float32 | Phase A Voltage individual Harmonics 23 percentage | 13-34 | PASS
Acurev4100 | Harmonics | (system) | 3 | Phase C | 0.023 | 0.0236 | -0.0006 | 2.61 | 9894 | 0x26A6 | float32 | Phase C Voltage individual Harmonics 3 percentage | 15-7 | PASS
Acurev4100 | THD | (system) | Voltage THD | Phase A | 0.026 | 0.0266 | -0.0006 | 2.31 | 9742 | 0x260E | float32 | Phase A Voltage THD | 13-8 | PASS
Acurev4100 | Harmonics | (system) | 21 | Phase A | 0.006 | 0.0061 | -0.0001 | 1.67 | 9790 | 0x263E | float32 | Phase A Voltage individual Harmonics 21 percentage | 13-32 | PASS
Acurev4100 | THD | (system) | Voltage THD Odd | Phase A | 0.026 | 0.0262 | -0.0002 | 0.77 | 9744 | 0x2610 | float32 | Phase A Voltage THD Odd | 13-9 | PASS
AcuRev2100 | Realtime | 9 | Current (A) | Phase B | 58759.961 | 58691.8047 | 68.1563 | 0.12 | 8212 | 0x2014 | float32 | Phase B Line Current | 1-11 | PASS
AcuRev2100 | Realtime | 9 | Current (A) | Phase A | 59119.238 | 59054.5039 | 64.7341 | 0.11 | 8210 | 0x2012 | float32 | Phase A Line Current | 1-10 | PASS
AcuRev2100 | Realtime | 9 | Current (A) | Phase C | 59083.953 | 59019.6719 | 64.2811 | 0.11 | 8214 | 0x2016 | float32 | Phase C Line Current | 1-12 | PASS
AcuRev2100 | Realtime | 9 | Current (A) | Average | 58987.719 | 58922.0625 | 65.6565 | 0.11 | 8216 | 0x2018 | float32 | Average Line Current | 1-13 | PASS
AcuvimIIW | Realtime | (system) | Active Power (kW) | Phase A | 0.100 | 0.0999 | 0.0001 | 0.1 | 16412 | 0x401C | float32 | Phase A Active Power | 1-15 | PASS
AcuRev2100 | Realtime | 8 | Current (A) | Phase A | 59119.238 | 59058.4297 | 60.8083 | 0.1 | 8210 | 0x2012 | float32 | Phase A Line Current | 1-10 | PASS
AcuRev2100 | Realtime | 8 | Current (A) | Phase B | 58759.961 | 58700.5547 | 59.4063 | 0.1 | 8212 | 0x2014 | float32 | Phase B Line Current | 1-11 | PASS
AcuRev2100 | Realtime | 8 | Current (A) | Phase C | 59083.953 | 59024.1289 | 59.8241 | 0.1 | 8214 | 0x2016 | float32 | Phase C Line Current | 1-12 | PASS
AcuRev2100 | Realtime | 8 | Current (A) | Average | 58987.719 | 58927.8711 | 59.8479 | 0.1 | 8216 | 0x2018 | float32 | Average Line Current | 1-13 | PASS
AcuRev2100 | Realtime | 6 | Current (A) | Phase B | 58759.961 | 58709.2109 | 50.7501 | 0.09 | 8212 | 0x2014 | float32 | Phase B Line Current | 1-11 | PASS
AcuRev2100 | Realtime | 6 | Current (A) | Phase C | 59083.953 | 59033.6328 | 50.3202 | 0.09 | 8214 | 0x2016 | float32 | Phase C Line Current | 1-12 | PASS
AcuRev2100 | Realtime | 7 | Current (A) | Phase A | 59119.238 | 59063.2148 | 56.0232 | 0.09 | 8210 | 0x2012 | float32 | Phase A Line Current | 1-10 | PASS
AcuRev2100 | Realtime | 7 | Current (A) | Phase B | 58759.961 | 58708.4609 | 51.5001 | 0.09 | 8212 | 0x2014 | float32 | Phase B Line Current | 1-11 | PASS
AcuRev2100 | Realtime | 7 | Current (A) | Phase C | 59083.953 | 59027.9531 | 55.9999 | 0.09 | 8214 | 0x2016 | float32 | Phase C Line Current | 1-12 | PASS
AcuRev2100 | Realtime | 7 | Current (A) | Average | 58987.719 | 58932.9727 | 54.7463 | 0.09 | 8216 | 0x2018 | float32 | Average Line Current | 1-13 | PASS
Acurev4100 | Realtime | (system) | Line-to-Neutral Voltage (V) | Phase C | 98.382 | 98.308 | 0.074 | 0.08 | 8198 | 0x2006 | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
AcuRev2100 | Realtime | 6 | Current (A) | Phase A | 59119.238 | 59069.5781 | 49.6599 | 0.08 | 8210 | 0x2012 | float32 | Phase A Line Current | 1-10 | PASS
AcuRev2100 | Realtime | 6 | Current (A) | Average | 58987.719 | 58937.6719 | 50.0471 | 0.08 | 8216 | 0x2018 | float32 | Average Line Current | 1-13 | PASS
AcuRev2100 | Realtime | 5 | Current (A) | Phase A | 59119.238 | 59080.0664 | 39.1716 | 0.07 | 8210 | 0x2012 | float32 | Phase A Line Current | 1-10 | PASS
AcuRev2100 | Realtime | 5 | Current (A) | Phase B | 58759.961 | 58720.3086 | 39.6524 | 0.07 | 8212 | 0x2014 | float32 | Phase B Line Current | 1-11 | PASS
AcuRev2100 | Realtime | 5 | Current (A) | Phase C | 59083.953 | 59045.1562 | 38.7968 | 0.07 | 8214 | 0x2016 | float32 | Phase C Line Current | 1-12 | PASS
AcuRev2100 | Realtime | 5 | Current (A) | Average | 58987.719 | 58948.4023 | 39.3167 | 0.07 | 8216 | 0x2018 | float32 | Average Line Current | 1-13 | PASS
Acurev4100 | THD | (system) | Voltage THFF Factor | Phase A | 0.444 | 0.4438 | 0.0002 | 0.05 | 9750 | 0x2616 | float32 | Phase A Voltage THFF Factor | 13-12 | PASS
Acurev4100 | THD | (system) | Voltage THFF Factor | Phase B | 0.444 | 0.4438 | 0.0002 | 0.05 | 9820 | 0x265C | float32 | Phase B Voltage THFF Factor | 14-5 | PASS
Acurev4100 | THD | (system) | Voltage THFF Factor | Phase C | 0.444 | 0.4438 | 0.0002 | 0.05 | 9890 | 0x26A2 | float32 | Phase C Voltage THFF Factor | 15-5 | PASS
AcuRev2100 | Realtime | 4 | Current (A) | Phase A | 59119.238 | 59087.4727 | 31.7653 | 0.05 | 8210 | 0x2012 | float32 | Phase A Line Current | 1-10 | PASS
AcuRev2100 | Realtime | 4 | Current (A) | Phase C | 59083.953 | 59052.1523 | 31.8007 | 0.05 | 8214 | 0x2016 | float32 | Phase C Line Current | 1-12 | PASS
AcuRev2100 | Realtime | 4 | Current (A) | Average | 58987.719 | 58957.7148 | 30.0042 | 0.05 | 8216 | 0x2018 | float32 | Average Line Current | 1-13 | PASS
AcuvimIIW | Realtime | (system) | Current (A) | Phase B | 1.000 | 0.9996 | 0.0004 | 0.04 | 16404 | 0x4014 | float32 | Phase B Line Current | 1-11 | PASS
AcuvimIIW | Realtime | (system) | Power Factor | Phase B | 0.999 | 0.9994 | -0.0004 | 0.04 | 16438 | 0x4036 | float32 | Phase B Power Factor | 1-28 | PASS
Acurev4100 | Realtime | (system) | Line-to-Line Voltage (V) | Phase C | 171.029 | 170.9612 | 0.0678 | 0.04 | 8206 | 0x200E | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
Acurev4100 | THD | (system) | Voltage Crest Factor | Phase A | 1.414 | 1.4145 | -0.0005 | 0.04 | 9748 | 0x2614 | float32 | Phase A Voltage Crest Factor | 13-11 | PASS
Acurev4100 | THD | (system) | Voltage Crest Factor | Phase C | 1.414 | 1.4146 | -0.0006 | 0.04 | 9888 | 0x26A0 | float32 | Phase C Voltage Crest Factor | 15-4 | PASS
Acurev4100 | Sequence | (system) | Voltage Sequence Magnitude | Negative | 98.702 | 98.7399 | -0.0379 | 0.04 | 9732 | 0x2604 | float32 | Voltage Negative Sequence Magnitude | 13-3 | PASS
AcuRev2100 | Realtime | 3 | Current (A) | Phase A | 59119.238 | 59095.2773 | 23.9607 | 0.04 | 8210 | 0x2012 | float32 | Phase A Line Current | 1-10 | PASS
AcuRev2100 | Realtime | 3 | Current (A) | Phase C | 59083.953 | 59058.9219 | 25.0311 | 0.04 | 8214 | 0x2016 | float32 | Phase C Line Current | 1-12 | PASS
AcuRev2100 | Realtime | 3 | Current (A) | Average | 58987.719 | 58964.625 | 23.094 | 0.04 | 8216 | 0x2018 | float32 | Average Line Current | 1-13 | PASS
AcuRev2100 | Realtime | 4 | Current (A) | Phase B | 58759.961 | 58734.1328 | 25.8282 | 0.04 | 8212 | 0x2014 | float32 | Phase B Line Current | 1-11 | PASS
AcuvimIIW | Realtime | (system) | Current (A) | Average | 1.000 | 0.9997 | 0.0003 | 0.03 | 16408 | 0x4018 | float32 | Average Line Current | 1-13 | PASS
AcuvimIIW | Realtime | (system) | Active Power (kW) | System | 0.300 | 0.2999 | 0.0001 | 0.03 | 16418 | 0x4022 | float32 | System Active Power | 1-18 | PASS
AcuvimIIW | Realtime | (system) | Apparent Power (kVA) | System | 0.300 | 0.2999 | 0.0001 | 0.03 | 16434 | 0x4032 | float32 | System Apparent Power | 1-26 | PASS
AcuRev2100 | Realtime | 2 | Current (A) | Phase A | 59119.238 | 59101.3047 | 17.9333 | 0.03 | 8210 | 0x2012 | float32 | Phase A Line Current | 1-10 | PASS
AcuRev2100 | Realtime | 3 | Current (A) | Phase B | 58759.961 | 58740.0781 | 19.8829 | 0.03 | 8212 | 0x2014 | float32 | Phase B Line Current | 1-11 | PASS
AcuvimIIW | Realtime | (system) | Current (A) | Phase A | 1.000 | 0.9998 | 0.0002 | 0.02 | 16402 | 0x4012 | float32 | Phase A Line Current | 1-10 | PASS
AcuvimIIW | Realtime | (system) | Current (A) | Phase C | 1.000 | 0.9998 | 0.0002 | 0.02 | 16406 | 0x4016 | float32 | Phase C Line Current | 1-12 | PASS
AcuvimIIW | Realtime | (system) | Power Factor | System | 1.000 | -0.9998 | 0.0002 | 0.02 | 16442 | 0x403A | float32 | System Power Factor | 1-30 | PASS
Acurev4100 | Realtime | (system) | Line-to-Neutral Voltage (V) | Average | 98.690 | 98.6721 | 0.0179 | 0.02 | 8200 | 0x2008 | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
Acurev4100 | Realtime | (system) | Line-to-Line Voltage (V) | Average | 170.935 | 170.9053 | 0.0297 | 0.02 | 8208 | 0x2010 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
Acurev4100 | THD | (system) | Voltage Crest Factor | Phase B | 1.414 | 1.4143 | -0.0003 | 0.02 | 9818 | 0x265A | float32 | Phase B Voltage Crest Factor | 14-4 | PASS
AcuRev2100 | Realtime | 1 | Current (A) | Phase A | 59119.238 | 59108.5742 | 10.6638 | 0.02 | 8210 | 0x2012 | float32 | Phase A Line Current | 1-10 | PASS
AcuRev2100 | Realtime | 1 | Current (A) | Phase C | 59083.953 | 59074.7891 | 9.1639 | 0.02 | 8214 | 0x2016 | float32 | Phase C Line Current | 1-12 | PASS
AcuRev2100 | Realtime | 1 | Current (A) | Average | 58987.719 | 58978.4336 | 9.2854 | 0.02 | 8216 | 0x2018 | float32 | Average Line Current | 1-13 | PASS
AcuRev2100 | Realtime | 2 | Current (A) | Phase B | 58759.961 | 58750.6641 | 9.2969 | 0.02 | 8212 | 0x2014 | float32 | Phase B Line Current | 1-11 | PASS
AcuRev2100 | Realtime | 2 | Current (A) | Phase C | 59083.953 | 59070.125 | 13.828 | 0.02 | 8214 | 0x2016 | float32 | Phase C Line Current | 1-12 | PASS
AcuRev2100 | Realtime | 2 | Current (A) | Average | 58987.719 | 58973.7148 | 14.0042 | 0.02 | 8216 | 0x2018 | float32 | Average Line Current | 1-13 | PASS
AcuvimIIW | Realtime | (system) | Line-to-Line Voltage (V) | Phase C | 173.166 | 173.1413 | 0.0247 | 0.01 | 16398 | 0x400E | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
Acurev4100 | Realtime | (system) | Line-to-Neutral Voltage (V) | Phase A | 99.204 | 99.2151 | -0.0111 | 0.01 | 8194 | 0x2002 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
Acurev4100 | Realtime | (system) | Line-to-Neutral Voltage (V) | Phase B | 98.485 | 98.4933 | -0.0083 | 0.01 | 8196 | 0x2004 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
Acurev4100 | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Phase B | 239.961 | 239.9883 | 0.0273 | 0.01 | 8212 | 0x2014 | float32 | Phase B Line-to-Neutral Voltage Phase Angle | 1-11 | PASS
Acurev4100 | Realtime | (system) | Line-to-Line Voltage (V) | Phase B | 170.545 | 170.5226 | 0.0224 | 0.01 | 8204 | 0x200C | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
AcuRev2100 | Realtime | 1 | Current (A) | Phase B | 58759.961 | 58752.9922 | 6.9688 | 0.01 | 8212 | 0x2014 | float32 | Phase B Line Current | 1-11 | PASS
AcuvimIIW | Realtime | (system) | Line-to-Neutral Voltage (V) | Phase A | 99.975 | 99.9735 | 0.0015 | 0 | 16386 | 0x4002 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
AcuvimIIW | Realtime | (system) | Line-to-Neutral Voltage (V) | Phase B | 100.002 | 100.0003 | 0.0017 | 0 | 16388 | 0x4004 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
AcuvimIIW | Realtime | (system) | Line-to-Neutral Voltage (V) | Phase C | 99.970 | 99.9663 | 0.0037 | 0 | 16390 | 0x4006 | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
AcuvimIIW | Realtime | (system) | Line-to-Neutral Voltage (V) | Average | 99.982 | 99.9787 | 0.0033 | 0 | 16392 | 0x4008 | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
AcuvimIIW | Realtime | (system) | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Phase A | 0.000 | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Phase B | 240.000 | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Phase C | 120.000 | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Average | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | System | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Line-to-Line Voltage (V) | Phase A | 173.188 | 173.1846 | 0.0034 | 0 | 16394 | 0x400A | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
AcuvimIIW | Realtime | (system) | Line-to-Line Voltage (V) | Phase B | 173.168 | 173.1649 | 0.0031 | 0 | 16396 | 0x400C | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
AcuvimIIW | Realtime | (system) | Line-to-Line Voltage (V) | Average | 173.174 | 173.1729 | 0.0011 | 0 | 16400 | 0x4010 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
AcuvimIIW | Realtime | (system) | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Current (A) | System | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Current Phase Angle (°) | Phase A | 0.000 | 0 | 0 | 0 | 17058 | 0x42A2 | int16 | Phase Angle of Phase A Current to V1 | 5-15 | PASS
AcuvimIIW | Realtime | (system) | Current Phase Angle (°) | Phase B | 240.000 | 240 | 0 | 0 | 17059 | 0x42A3 | int16 | Phase Angle of Phase B Current to V1 | 5-16 | PASS
AcuvimIIW | Realtime | (system) | Current Phase Angle (°) | Phase C | 120.000 | 120 | 0 | 0 | 17060 | 0x42A4 | int16 | Phase Angle of Phase C Current to V1 | 5-17 | PASS
AcuvimIIW | Realtime | (system) | Current Phase Angle (°) | Average | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Current Phase Angle (°) | System | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Neutral Current (A) | Phase A | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Neutral Current (A) | Phase B | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Neutral Current (A) | Phase C | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Neutral Current (A) | Average | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Neutral Current (A) | System | 0.000 | 0 | 0 | 0 | 16410 | 0x401A | float32 | Neutral Current | 1-14 | PASS
AcuvimIIW | Realtime | (system) | Active Power (kW) | Phase B | 0.100 | 0.1 | 0 | 0 | 16414 | 0x401E | float32 | Phase B Active Power | 1-16 | PASS
AcuvimIIW | Realtime | (system) | Active Power (kW) | Phase C | 0.100 | 0.1 | 0 | 0 | 16416 | 0x4020 | float32 | Phase C Active Power | 1-17 | PASS
AcuvimIIW | Realtime | (system) | Active Power (kW) | Average | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Reactive Power (kvar) | Phase A | -0.000 | 0 | 0 | 0 | 16420 | 0x4024 | float32 | Phase A Reactive Power | 1-19 | PASS
AcuvimIIW | Realtime | (system) | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Apparent Power (kVA) | Phase A | 0.100 | 0.1 | 0 | 0 | 16428 | 0x402C | float32 | Phase A Apparent Power | 1-23 | PASS
AcuvimIIW | Realtime | (system) | Apparent Power (kVA) | Phase B | 0.100 | 0.1 | 0 | 0 | 16430 | 0x402E | float32 | Phase B Apparent Power | 1-24 | PASS
AcuvimIIW | Realtime | (system) | Apparent Power (kVA) | Phase C | 0.100 | 0.1 | 0 | 0 | 16432 | 0x4030 | float32 | Phase C Apparent Power | 1-25 | PASS
AcuvimIIW | Realtime | (system) | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Load Nature | Phase A | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Load Nature | Phase B | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Load Nature | Phase C | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Load Nature | Average | R | 82 |  |  | 16448 | 0x4040 | float32 | Average Load Nature | 1-33 | N/A
AcuvimIIW | Realtime | (system) | Load Nature | System | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Power Factor | Phase A | -1.000 | -1 | 0 | 0 | 16436 | 0x4034 | float32 | Phase A Power Factor | 1-27 | PASS
AcuvimIIW | Realtime | (system) | Power Factor | Phase C | -1.000 | -1 | 0 | 0 | 16440 | 0x4038 | float32 | Phase C Power Factor | 1-29 | PASS
AcuvimIIW | Realtime | (system) | Power Factor | Average | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Frequency (Hz) | Average | - | [8 empty] | 无寄存器
AcuvimIIW | Realtime | (system) | Frequency (Hz) | System | 49.999 | 49.999 | 0 | 0 | 16384 | 0x4000 | float32 | System Frequency | 1-1 | PASS
AcuvimIIW | THD | (system) | Voltage THD Odd (%) | Phase C | 0.010 | 0.01 | 0 | 0 | 16580 | 0x40C4 | int16 | Phase C Voltage Odd THD | 4-7 | PASS
AcuvimIIW | THD | (system) | Voltage THD Odd (%) | Average | - | [8 empty] | 无寄存器
AcuvimIIW | THD | (system) | Voltage THD Even (%) | Phase C | 0.030 | 0.03 | 0 | 0 | 16581 | 0x40C5 | int16 | Phase C Voltage Even THD | 4-8 | PASS
AcuvimIIW | THD | (system) | Voltage THD Even (%) | Average | - | [8 empty] | 无寄存器
AcuvimIIW | THD | (system) | Voltage Crest Factor | Phase A | 1.416 | 1.416 | 0 | 0 | 16514 | 0x4082 | int16 | Phase A Voltage Crest Factor | 3-41 | PASS
AcuvimIIW | THD | (system) | Voltage Crest Factor | Phase B | 1.416 | 1.416 | 0 | 0 | 16548 | 0x40A4 | int16 | Phase B Voltage Crest Factor | 3-75 | PASS
AcuvimIIW | THD | (system) | Voltage Crest Factor | Phase C | 1.416 | 1.416 | 0 | 0 | 16582 | 0x40C6 | int16 | Phase C Voltage Crest Factor | 4-9 | PASS
AcuvimIIW | THD | (system) | Voltage Crest Factor | Average | - | [8 empty] | 无寄存器
AcuvimIIW | THD | (system) | Current THD (%) | Phase A | 0.020 | 0.02 | 0 | 0 | 16478 | 0x405E | int16 | Phase A Current THD | 3-5 | PASS
AcuvimIIW | THD | (system) | Current THD (%) | Phase C | 0.020 | 0.02 | 0 | 0 | 16480 | 0x4060 | int16 | Phase C Current THD | 3-7 | PASS
AcuvimIIW | THD | (system) | Current THD (%) | Average | 0.020 | 0.02 | 0 | 0 | 16481 | 0x4061 | int16 | Average Current THD | 3-8 | PASS
AcuvimIIW | THD | (system) | Current THD Odd (%) | Phase A | 0.020 | 0.02 | 0 | 0 | 16614 | 0x40E6 | int16 | Phase A Current Odd THD | 4-41 | PASS
AcuvimIIW | THD | (system) | Current THD Odd (%) | Phase B | 0.010 | 0.01 | 0 | 0 | 16647 | 0x4107 | int16 | Phase B Current Odd THD | 4-74 | PASS
AcuvimIIW | THD | (system) | Current THD Odd (%) | Phase C | 0.020 | 0.02 | 0 | 0 | 16680 | 0x4128 | int16 | Phase C Current Odd THD | 4-107 | PASS
AcuvimIIW | THD | (system) | Current THD Odd (%) | Average | - | [8 empty] | 无寄存器
AcuvimIIW | THD | (system) | Current THD Even (%) | Phase A | 0.010 | 0.01 | 0 | 0 | 16615 | 0x40E7 | int16 | Phase A Current Even THD | 4-42 | PASS
AcuvimIIW | THD | (system) | Current THD Even (%) | Phase B | 0.010 | 0.01 | 0 | 0 | 16648 | 0x4108 | int16 | Phase B Current Even THD | 4-75 | PASS
AcuvimIIW | THD | (system) | Current THD Even (%) | Phase C | 0.010 | 0.01 | 0 | 0 | 16681 | 0x4129 | int16 | Phase C Current Even THD | 4-108 | PASS
AcuvimIIW | THD | (system) | Current THD Even (%) | Average | - | [8 empty] | 无寄存器
AcuvimIIW | THD | (system) | Current K-Factor | Phase A | 1.000 | 1 | 0 | 0 | 16616 | 0x40E8 | int16 | Phase A Current K Factor | 4-43 | PASS
AcuvimIIW | THD | (system) | Current K-Factor | Phase B | 1.000 | 1 | 0 | 0 | 16649 | 0x4109 | int16 | Phase B Current K Factor | 4-76 | PASS
AcuvimIIW | THD | (system) | Current K-Factor | Phase C | 1.000 | 1 | 0 | 0 | 16682 | 0x412A | int16 | Phase C Current K Factor | 4-109 | PASS
AcuvimIIW | THD | (system) | Current K-Factor | Average | - | [8 empty] | 无寄存器
AcuvimIIW | Sequence | (system) | Voltage | Positive | 99.900∠0.0° | 99.9 |  |  | 17044 | 0x4294 | int16 | Real part of Voltage Positive Sequence | 5-1 | N/A
AcuvimIIW | Sequence | (system) | Voltage | Negative | 0.000∠0.0° | 0 |  |  | 17046 | 0x4296 | int16 | Real part of Voltage Negative Sequence | 5-3 | N/A
AcuvimIIW | Sequence | (system) | Voltage | Zero | 0.000∠0.0° | 0 |  |  | 17048 | 0x4298 | int16 | Real part of Voltage Zero Sequence | 5-5 | N/A
AcuvimIIW | Sequence | (system) | Current | Positive | 0.999∠0.0° | 0.999 |  |  | 17050 | 0x429A | int16 | Real part of Current Positive Sequence | 5-7 | N/A
AcuvimIIW | Sequence | (system) | Current | Negative | 0.000∠0.0° | 0 |  |  | 17052 | 0x429C | int16 | Real part of Current Negative Sequence | 5-9 | N/A
AcuvimIIW | Sequence | (system) | Current | Zero | 0.000∠0.0° | 0 |  |  | 17054 | 0x429E | int16 | Real part of Current Zero Sequence | 5-11 | N/A
Acurev4100 | Realtime | (system) | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Phase A | 0.000 | 0 | 0 | 0 | 8210 | 0x2012 | float32 | Phase A Line-to-Neutral Voltage Phase Angle | 1-10 | PASS
Acurev4100 | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Phase C | 119.899 | 119.8861 | 0.0129 | 0 | 8214 | 0x2016 | float32 | Phase C Line-to-Neutral Voltage Phase Angle | 1-12 | PASS
Acurev4100 | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Average | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | System | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | Line-to-Line Voltage (V) | Phase A | 171.238 | 171.231 | 0.007 | 0 | 8202 | 0x200A | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
Acurev4100 | Realtime | (system) | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | Current (A) | Phase A | 0.000 | 0 | 0 | 0 | 8216 | 0x2018 | float32 | Phase A Current | 1-13 | PASS
Acurev4100 | Realtime | (system) | Current (A) | Phase B | 0.000 | 0 | 0 | 0 | 8228 | 0x2024 | float32 | Phase B Current | 1-19 | PASS
Acurev4100 | Realtime | (system) | Current (A) | Phase C | 0.000 | 0 | 0 | 0 | 8240 | 0x2030 | float32 | Phase C Current | 1-25 | PASS
Acurev4100 | Realtime | (system) | Current (A) | Average | 0.000 | 0 | 0 | 0 | 8252 | 0x203C | float32 | System Average Current | 1-31 | PASS
Acurev4100 | Realtime | (system) | Current (A) | System | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | Active Power (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8218 | 0x201A | float32 | Phase A Active Power | 1-14 | PASS
Acurev4100 | Realtime | (system) | Active Power (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8230 | 0x2026 | float32 | Phase B Active Power | 1-20 | PASS
Acurev4100 | Realtime | (system) | Active Power (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8242 | 0x2032 | float32 | Phase C Active Power | 1-26 | PASS
Acurev4100 | Realtime | (system) | Active Power (kW) | Average | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | Active Power (kW) | System | 0.000 | 0 | 0 | 0 | 8254 | 0x203E | float32 | System Active Power | 1-32 | PASS
Acurev4100 | Realtime | (system) | Reactive Power (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8220 | 0x201C | float32 | Phase A Reactive Power | 1-15 | PASS
Acurev4100 | Realtime | (system) | Reactive Power (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8232 | 0x2028 | float32 | Phase B Reactive Power | 1-21 | PASS
Acurev4100 | Realtime | (system) | Reactive Power (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8244 | 0x2034 | float32 | Phase C Reactive Power | 1-27 | PASS
Acurev4100 | Realtime | (system) | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | Reactive Power (kvar) | System | 0.000 | 0 | 0 | 0 | 8256 | 0x2040 | float32 | System Reactive Power | 1-33 | PASS
Acurev4100 | Realtime | (system) | Apparent Power (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8222 | 0x201E | float32 | Phase A Apparent Power | 1-16 | PASS
Acurev4100 | Realtime | (system) | Apparent Power (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8234 | 0x202A | float32 | Phase B Apparent Power | 1-22 | PASS
Acurev4100 | Realtime | (system) | Apparent Power (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8246 | 0x2036 | float32 | Phase C Apparent Power | 1-28 | PASS
Acurev4100 | Realtime | (system) | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | Apparent Power (kVA) | System | 0.000 | 0 | 0 | 0 | 8258 | 0x2042 | float32 | System Apparent Power | 1-34 | PASS
Acurev4100 | Realtime | (system) | Load Nature | Phase A | R | 0 |  |  | 8224 | 0x2020 | uint32 | Phase A Load Nature | 1-17 | N/A
Acurev4100 | Realtime | (system) | Load Nature | Phase B | R | 0 |  |  | 8236 | 0x202C | uint32 | Phase B Load Nature | 1-23 | N/A
Acurev4100 | Realtime | (system) | Load Nature | Phase C | R | 0 |  |  | 8248 | 0x2038 | uint32 | Phase C Load Nature | 1-29 | N/A
Acurev4100 | Realtime | (system) | Load Nature | Average | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | Load Nature | System | R | 0 |  |  | 8260 | 0x2044 | uint32 | System Load Nature | 1-35 | N/A
Acurev4100 | Realtime | (system) | Power Factor | Phase A | 0.000 | 0 | 0 | 0 | 8226 | 0x2022 | float32 | Phase A Power Factor | 1-18 | PASS
Acurev4100 | Realtime | (system) | Power Factor | Phase B | 0.000 | 0 | 0 | 0 | 8238 | 0x202E | float32 | Phase B Power Factor | 1-24 | PASS
Acurev4100 | Realtime | (system) | Power Factor | Phase C | 0.000 | 0 | 0 | 0 | 8250 | 0x203A | float32 | Phase C Power Factor | 1-30 | PASS
Acurev4100 | Realtime | (system) | Power Factor | Average | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | Power Factor | System | 0.000 | 0 | 0 | 0 | 8262 | 0x2046 | float32 | System Power Factor | 1-36 | PASS
Acurev4100 | Realtime | (system) | System Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | System Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | System Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | System Frequency (Hz) | Average | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | (system) | System Frequency (Hz) | System | 50.000 | 49.9998 | 0.0002 | 0 | 8192 | 0x2000 | float32 | System Frequency | 1-1 | PASS
Acurev4100 | Realtime | User Channel 1:name1 | Current (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Current (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Current (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Current (A) | User Channel | 0.000 | 0 | 0 | 0 | 8600 | 0x2198 | float32 | User Channel 1 Current | 5-1 | PASS
Acurev4100 | Realtime | User Channel 1:name1 | Active Power (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Active Power (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Active Power (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Active Power (kW) | User Channel | 0.000 | 0 | 0 | 0 | 8602 | 0x219A | float32 | User Channel 1 Active Power | 5-2 | PASS
Acurev4100 | Realtime | User Channel 1:name1 | Reactive Power (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Reactive Power (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Reactive Power (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Reactive Power (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 8604 | 0x219C | float32 | User Channel 1 Reactive Power | 5-3 | PASS
Acurev4100 | Realtime | User Channel 1:name1 | Apparent Power (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Apparent Power (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Apparent Power (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Apparent Power (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 8606 | 0x219E | float32 | User Channel 1 Apparent Power | 5-4 | PASS
Acurev4100 | Realtime | User Channel 1:name1 | Load Nature | Phase A | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Load Nature | Phase B | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Load Nature | Phase C | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Load Nature | User Channel | R | 0 |  |  | 8608 | 0x21A0 | uint32 | User Channel 1 Load Nature | 5-5 | N/A
Acurev4100 | Realtime | User Channel 1:name1 | Power Factor | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Power Factor | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Power Factor | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Power Factor | User Channel | 0.000 | 0 | 0 | 0 | 8610 | 0x21A2 | float32 | User Channel 1 Power Factor | 5-6 | PASS
Acurev4100 | Realtime | User Channel 1:name1 | Current Phase Angle (°) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Current Phase Angle (°) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Current Phase Angle (°) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 1:name1 | Current Phase Angle (°) | User Channel | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Current (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Current (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Current (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Current (A) | User Channel | 0.000 | 0 | 0 | 0 | 8612 | 0x21A4 | float32 | User Channel 2 Current | 5-7 | PASS
Acurev4100 | Realtime | User Channel 2:name1 | Active Power (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Active Power (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Active Power (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Active Power (kW) | User Channel | 0.000 | 0 | 0 | 0 | 8614 | 0x21A6 | float32 | User Channel 2 Active Power | 5-8 | PASS
Acurev4100 | Realtime | User Channel 2:name1 | Reactive Power (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Reactive Power (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Reactive Power (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Reactive Power (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 8616 | 0x21A8 | float32 | User Channel 2 Reactive Power | 5-9 | PASS
Acurev4100 | Realtime | User Channel 2:name1 | Apparent Power (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Apparent Power (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Apparent Power (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Apparent Power (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 8618 | 0x21AA | float32 | User Channel 2 Apparent Power | 5-10 | PASS
Acurev4100 | Realtime | User Channel 2:name1 | Load Nature | Phase A | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Load Nature | Phase B | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Load Nature | Phase C | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Load Nature | User Channel | R | 0 |  |  | 8620 | 0x21AC | uint32 | User Channel 2 Load Nature | 5-11 | N/A
Acurev4100 | Realtime | User Channel 2:name1 | Power Factor | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Power Factor | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Power Factor | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Power Factor | User Channel | 0.000 | 0 | 0 | 0 | 8622 | 0x21AE | float32 | User Channel 2 Power Factor | 5-12 | PASS
Acurev4100 | Realtime | User Channel 2:name1 | Current Phase Angle (°) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Current Phase Angle (°) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Current Phase Angle (°) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 2:name1 | Current Phase Angle (°) | User Channel | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Current (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Current (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Current (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Current (A) | User Channel | 0.000 | 0 | 0 | 0 | 8624 | 0x21B0 | float32 | User Channel 3 Current | 5-13 | PASS
Acurev4100 | Realtime | User Channel 3:name2 | Active Power (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Active Power (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Active Power (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Active Power (kW) | User Channel | 0.000 | 0 | 0 | 0 | 8626 | 0x21B2 | float32 | User Channel 3 Active Power | 5-14 | PASS
Acurev4100 | Realtime | User Channel 3:name2 | Reactive Power (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Reactive Power (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Reactive Power (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Reactive Power (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 8628 | 0x21B4 | float32 | User Channel 3 Reactive Power | 5-15 | PASS
Acurev4100 | Realtime | User Channel 3:name2 | Apparent Power (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Apparent Power (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Apparent Power (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Apparent Power (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 8630 | 0x21B6 | float32 | User Channel 3 Apparent Power | 5-16 | PASS
Acurev4100 | Realtime | User Channel 3:name2 | Load Nature | Phase A | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Load Nature | Phase B | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Load Nature | Phase C | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Load Nature | User Channel | R | 0 |  |  | 8632 | 0x21B8 | uint32 | User Channel 3 Load Nature | 5-17 | N/A
Acurev4100 | Realtime | User Channel 3:name2 | Power Factor | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Power Factor | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Power Factor | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Power Factor | User Channel | 0.000 | 0 | 0 | 0 | 8634 | 0x21BA | float32 | User Channel 3 Power Factor | 5-18 | PASS
Acurev4100 | Realtime | User Channel 3:name2 | Current Phase Angle (°) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Current Phase Angle (°) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Current Phase Angle (°) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 3:name2 | Current Phase Angle (°) | User Channel | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Current (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Current (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Current (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Current (A) | User Channel | 0.000 | 0 | 0 | 0 | 8636 | 0x21BC | float32 | User Channel 4 Current | 5-19 | PASS
Acurev4100 | Realtime | User Channel 4:name2 | Active Power (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Active Power (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Active Power (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Active Power (kW) | User Channel | 0.000 | 0 | 0 | 0 | 8638 | 0x21BE | float32 | User Channel 4 Active Power | 5-20 | PASS
Acurev4100 | Realtime | User Channel 4:name2 | Reactive Power (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Reactive Power (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Reactive Power (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Reactive Power (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 8640 | 0x21C0 | float32 | User Channel 4 Reactive Power | 5-21 | PASS
Acurev4100 | Realtime | User Channel 4:name2 | Apparent Power (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Apparent Power (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Apparent Power (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Apparent Power (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 8642 | 0x21C2 | float32 | User Channel 4 Apparent Power | 5-22 | PASS
Acurev4100 | Realtime | User Channel 4:name2 | Load Nature | Phase A | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Load Nature | Phase B | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Load Nature | Phase C | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Load Nature | User Channel | R | 0 |  |  | 8644 | 0x21C4 | uint32 | User Channel 4 Load Nature | 5-23 | N/A
Acurev4100 | Realtime | User Channel 4:name2 | Power Factor | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Power Factor | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Power Factor | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Power Factor | User Channel | 0.000 | 0 | 0 | 0 | 8646 | 0x21C6 | float32 | User Channel 4 Power Factor | 5-24 | PASS
Acurev4100 | Realtime | User Channel 4:name2 | Current Phase Angle (°) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Current Phase Angle (°) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Current Phase Angle (°) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 4:name2 | Current Phase Angle (°) | User Channel | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Current (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Current (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Current (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Current (A) | User Channel | 0.000 | 0 | 0 | 0 | 8648 | 0x21C8 | float32 | User Channel 5 Current | 5-25 | PASS
Acurev4100 | Realtime | User Channel 5:name5 | Active Power (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Active Power (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Active Power (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Active Power (kW) | User Channel | 0.000 | 0 | 0 | 0 | 8650 | 0x21CA | float32 | User Channel 5 Active Power | 5-26 | PASS
Acurev4100 | Realtime | User Channel 5:name5 | Reactive Power (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Reactive Power (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Reactive Power (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Reactive Power (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 8652 | 0x21CC | float32 | User Channel 5 Reactive Power | 5-27 | PASS
Acurev4100 | Realtime | User Channel 5:name5 | Apparent Power (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Apparent Power (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Apparent Power (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Apparent Power (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 8654 | 0x21CE | float32 | User Channel 5 Apparent Power | 5-28 | PASS
Acurev4100 | Realtime | User Channel 5:name5 | Load Nature | Phase A | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Load Nature | Phase B | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Load Nature | Phase C | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Load Nature | User Channel | R | 0 |  |  | 8656 | 0x21D0 | uint32 | User Channel 5 Load Nature | 5-29 | N/A
Acurev4100 | Realtime | User Channel 5:name5 | Power Factor | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Power Factor | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Power Factor | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Power Factor | User Channel | 0.000 | 0 | 0 | 0 | 8658 | 0x21D2 | float32 | User Channel 5 Power Factor | 5-30 | PASS
Acurev4100 | Realtime | User Channel 5:name5 | Current Phase Angle (°) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Current Phase Angle (°) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Current Phase Angle (°) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 5:name5 | Current Phase Angle (°) | User Channel | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Current (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Current (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Current (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Current (A) | User Channel | 0.000 | 0 | 0 | 0 | 8660 | 0x21D4 | float32 | User Channel 6 Current | 5-31 | PASS
Acurev4100 | Realtime | User Channel 6:6666 | Active Power (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Active Power (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Active Power (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Active Power (kW) | User Channel | 0.000 | 0 | 0 | 0 | 8662 | 0x21D6 | float32 | User Channel 6 Active Power | 5-32 | PASS
Acurev4100 | Realtime | User Channel 6:6666 | Reactive Power (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Reactive Power (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Reactive Power (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Reactive Power (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 8664 | 0x21D8 | float32 | User Channel 6 Reactive Power | 5-33 | PASS
Acurev4100 | Realtime | User Channel 6:6666 | Apparent Power (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Apparent Power (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Apparent Power (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Apparent Power (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 8666 | 0x21DA | float32 | User Channel 6 Apparent Power | 5-34 | PASS
Acurev4100 | Realtime | User Channel 6:6666 | Load Nature | Phase A | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Load Nature | Phase B | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Load Nature | Phase C | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Load Nature | User Channel | R | 0 |  |  | 8668 | 0x21DC | uint32 | User Channel 6 Load Nature | 5-35 | N/A
Acurev4100 | Realtime | User Channel 6:6666 | Power Factor | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Power Factor | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Power Factor | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Power Factor | User Channel | 0.000 | 0 | 0 | 0 | 8670 | 0x21DE | float32 | User Channel 6 Power Factor | 5-36 | PASS
Acurev4100 | Realtime | User Channel 6:6666 | Current Phase Angle (°) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Current Phase Angle (°) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Current Phase Angle (°) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 6:6666 | Current Phase Angle (°) | User Channel | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Current (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Current (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Current (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Current (A) | User Channel | 0.000 | 0 | 0 | 0 | 8672 | 0x21E0 | float32 | User Channel 7 Current | 6-1 | PASS
Acurev4100 | Realtime | User Channel 7:7777 | Active Power (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Active Power (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Active Power (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Active Power (kW) | User Channel | 0.000 | 0 | 0 | 0 | 8674 | 0x21E2 | float32 | User Channel 7 Active Power | 6-2 | PASS
Acurev4100 | Realtime | User Channel 7:7777 | Reactive Power (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Reactive Power (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Reactive Power (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Reactive Power (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 8676 | 0x21E4 | float32 | User Channel 7 Reactive Power | 6-3 | PASS
Acurev4100 | Realtime | User Channel 7:7777 | Apparent Power (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Apparent Power (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Apparent Power (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Apparent Power (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 8678 | 0x21E6 | float32 | User Channel 7 Apparent Power | 6-4 | PASS
Acurev4100 | Realtime | User Channel 7:7777 | Load Nature | Phase A | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Load Nature | Phase B | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Load Nature | Phase C | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Load Nature | User Channel | R | 0 |  |  | 8680 | 0x21E8 | uint32 | User Channel 7 Load Nature | 6-5 | N/A
Acurev4100 | Realtime | User Channel 7:7777 | Power Factor | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Power Factor | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Power Factor | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Power Factor | User Channel | 0.000 | 0 | 0 | 0 | 8682 | 0x21EA | float32 | User Channel 7 Power Factor | 6-6 | PASS
Acurev4100 | Realtime | User Channel 7:7777 | Current Phase Angle (°) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Current Phase Angle (°) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Current Phase Angle (°) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 7:7777 | Current Phase Angle (°) | User Channel | - | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Current (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Current (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Current (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Current (A) | User Channel | 0.000 | 0 | 0 | 0 | 8684 | 0x21EC | float32 | User Channel 8 Current | 6-7 | PASS
Acurev4100 | Realtime | User Channel 8:9999 | Active Power (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Active Power (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Active Power (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Active Power (kW) | User Channel | 0.000 | 0 | 0 | 0 | 8686 | 0x21EE | float32 | User Channel 8 Active Power | 6-8 | PASS
Acurev4100 | Realtime | User Channel 8:9999 | Reactive Power (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Reactive Power (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Reactive Power (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Reactive Power (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 8688 | 0x21F0 | float32 | User Channel 8 Reactive Power | 6-9 | PASS
Acurev4100 | Realtime | User Channel 8:9999 | Apparent Power (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Apparent Power (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Apparent Power (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Apparent Power (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 8690 | 0x21F2 | float32 | User Channel 8 Apparent Power | 6-10 | PASS
Acurev4100 | Realtime | User Channel 8:9999 | Load Nature | Phase A | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Load Nature | Phase B | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Load Nature | Phase C | R | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Load Nature | User Channel | R | 0 |  |  | 8692 | 0x21F4 | uint32 | User Channel 8 Load Nature | 6-11 | N/A
Acurev4100 | Realtime | User Channel 8:9999 | Power Factor | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Power Factor | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Power Factor | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Power Factor | User Channel | 0.000 | 0 | 0 | 0 | 8694 | 0x21F6 | float32 | User Channel 8 Power Factor | 6-12 | PASS
Acurev4100 | Realtime | User Channel 8:9999 | Current Phase Angle (°) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Current Phase Angle (°) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Current Phase Angle (°) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Realtime | User Channel 8:9999 | Current Phase Angle (°) | User Channel | - | [8 empty] | 无寄存器
Acurev4100 | Demand | (system) | Current Demand (A) | Phase A | 0.000 | 0 | 0 | 0 | 8960 | 0x2300 | float32 | Phase A Current Demand | 7-1 | PASS
Acurev4100 | Demand | (system) | Current Demand (A) | Phase B | 0.000 | 0 | 0 | 0 | 8972 | 0x230C | float32 | Phase B Current Demand | 7-7 | PASS
Acurev4100 | Demand | (system) | Current Demand (A) | Phase C | 0.000 | 0 | 0 | 0 | 8984 | 0x2318 | float32 | Phase C Current Demand | 7-13 | PASS
Acurev4100 | Demand | (system) | Current Demand (A) | System | 0.000 | 0 | 0 | 0 | 8996 | 0x2324 | float32 | System Average Current Demand | 7-19 | PASS
Acurev4100 | Demand | (system) | Import Active Power Demand (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8962 | 0x2302 | float32 | Phase A Import Active Power Demand | 7-2 | PASS
Acurev4100 | Demand | (system) | Import Active Power Demand (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8974 | 0x230E | float32 | Phase B Import Active Power Demand | 7-8 | PASS
Acurev4100 | Demand | (system) | Import Active Power Demand (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8986 | 0x231A | float32 | Phase C Import Active Power Demand | 7-14 | PASS
Acurev4100 | Demand | (system) | Import Active Power Demand (kW) | System | 0.000 | 0 | 0 | 0 | 8998 | 0x2326 | float32 | System Import Active Power Demand | 7-20 | PASS
Acurev4100 | Demand | (system) | Export Active Power Demand (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8964 | 0x2304 | float32 | Phase A Export Active Power Demand | 7-3 | PASS
Acurev4100 | Demand | (system) | Export Active Power Demand (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8976 | 0x2310 | float32 | Phase B Export Active Power Demand | 7-9 | PASS
Acurev4100 | Demand | (system) | Export Active Power Demand (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8988 | 0x231C | float32 | Phase C Export Active Power Demand | 7-15 | PASS
Acurev4100 | Demand | (system) | Export Active Power Demand (kW) | System | 0.000 | 0 | 0 | 0 | 9000 | 0x2328 | float32 | System Export Active Power Demand | 7-21 | PASS
Acurev4100 | Demand | (system) | Import Reactive Power Demand (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8966 | 0x2306 | float32 | Phase A Import Reactive Power Demand | 7-4 | PASS
Acurev4100 | Demand | (system) | Import Reactive Power Demand (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8978 | 0x2312 | float32 | Phase B Import Reactive Power Demand | 7-10 | PASS
Acurev4100 | Demand | (system) | Import Reactive Power Demand (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8990 | 0x231E | float32 | Phase C Import Reactive Power Demand | 7-16 | PASS
Acurev4100 | Demand | (system) | Import Reactive Power Demand (kvar) | System | 0.000 | 0 | 0 | 0 | 9002 | 0x232A | float32 | System Import Reactive Power Demand | 7-22 | PASS
Acurev4100 | Demand | (system) | Export Reactive Power Demand (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8968 | 0x2308 | float32 | Phase A Export Reactive Power Demand | 7-5 | PASS
Acurev4100 | Demand | (system) | Export Reactive Power Demand (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8980 | 0x2314 | float32 | Phase B Export Reactive Power Demand | 7-11 | PASS
Acurev4100 | Demand | (system) | Export Reactive Power Demand (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8992 | 0x2320 | float32 | Phase C Export Reactive Power Demand | 7-17 | PASS
Acurev4100 | Demand | (system) | Export Reactive Power Demand (kvar) | System | 0.000 | 0 | 0 | 0 | 9004 | 0x232C | float32 | System Export Reactive Power Demand | 7-23 | PASS
Acurev4100 | Demand | (system) | Apparent Power Demand (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8970 | 0x230A | float32 | Phase A Apparent Power Demand | 7-6 | PASS
Acurev4100 | Demand | (system) | Apparent Power Demand (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8982 | 0x2316 | float32 | Phase B Apparent Power Demand | 7-12 | PASS
Acurev4100 | Demand | (system) | Apparent Power Demand (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8994 | 0x2322 | float32 | Phase C Apparent Power Demand | 7-18 | PASS
Acurev4100 | Demand | (system) | Apparent Power Demand (kVA) | System | 0.000 | 0 | 0 | 0 | 9006 | 0x232E | float32 | System Apparent Power Demand | 7-24 | PASS
Acurev4100 | Demand | User Channel 1:name1 | Current Demand (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Current Demand (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Current Demand (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Current Demand (A) | User Channel | 0.000 | 0 | 0 | 0 | 9296 | 0x2450 | float32 | User Channel 1 Current Demand | 11-1 | PASS
Acurev4100 | Demand | User Channel 1:name1 | Import Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Import Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Import Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Import Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9298 | 0x2452 | float32 | User Channel 1 Import Active Power Demand | 11-2 | PASS
Acurev4100 | Demand | User Channel 1:name1 | Export Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Export Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Export Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Export Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9300 | 0x2454 | float32 | User Channel 1 Export Active Power Demand | 11-3 | PASS
Acurev4100 | Demand | User Channel 1:name1 | Import Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Import Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Import Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Import Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9302 | 0x2456 | float32 | User Channel 1 Import Reactive Power Demand | 11-4 | PASS
Acurev4100 | Demand | User Channel 1:name1 | Export Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Export Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Export Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Export Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9304 | 0x2458 | float32 | User Channel 1 Export Reactive Power Demand | 11-5 | PASS
Acurev4100 | Demand | User Channel 1:name1 | Apparent Power Demand (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Apparent Power Demand (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Apparent Power Demand (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 1:name1 | Apparent Power Demand (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 9306 | 0x245A | float32 | User Channel 1 Apparent Power Demand | 11-6 | PASS
Acurev4100 | Demand | User Channel 2:name1 | Current Demand (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Current Demand (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Current Demand (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Current Demand (A) | User Channel | 0.000 | 0 | 0 | 0 | 9308 | 0x245C | float32 | User Channel 2 Current Demand | 11-7 | PASS
Acurev4100 | Demand | User Channel 2:name1 | Import Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Import Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Import Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Import Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9310 | 0x245E | float32 | User Channel 2 Import Active Power Demand | 11-8 | PASS
Acurev4100 | Demand | User Channel 2:name1 | Export Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Export Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Export Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Export Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9312 | 0x2460 | float32 | User Channel 2 Export Active Power Demand | 11-9 | PASS
Acurev4100 | Demand | User Channel 2:name1 | Import Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Import Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Import Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Import Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9314 | 0x2462 | float32 | User Channel 2 Import Reactive Power Demand | 11-10 | PASS
Acurev4100 | Demand | User Channel 2:name1 | Export Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Export Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Export Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Export Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9316 | 0x2464 | float32 | User Channel 2 Export Reactive Power Demand | 11-11 | PASS
Acurev4100 | Demand | User Channel 2:name1 | Apparent Power Demand (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Apparent Power Demand (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Apparent Power Demand (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 2:name1 | Apparent Power Demand (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 9318 | 0x2466 | float32 | User Channel 2 Apparent Power Demand | 11-12 | PASS
Acurev4100 | Demand | User Channel 3:name2 | Current Demand (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Current Demand (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Current Demand (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Current Demand (A) | User Channel | 0.000 | 0 | 0 | 0 | 9320 | 0x2468 | float32 | User Channel 3 Current Demand | 11-13 | PASS
Acurev4100 | Demand | User Channel 3:name2 | Import Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Import Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Import Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Import Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9322 | 0x246A | float32 | User Channel 3 Import Active Power Demand | 11-14 | PASS
Acurev4100 | Demand | User Channel 3:name2 | Export Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Export Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Export Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Export Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9324 | 0x246C | float32 | User Channel 3 Export Active Power Demand | 11-15 | PASS
Acurev4100 | Demand | User Channel 3:name2 | Import Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Import Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Import Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Import Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9326 | 0x246E | float32 | User Channel 3 Import Reactive Power Demand | 11-16 | PASS
Acurev4100 | Demand | User Channel 3:name2 | Export Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Export Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Export Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Export Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9328 | 0x2470 | float32 | User Channel 3 Export Reactive Power Demand | 11-17 | PASS
Acurev4100 | Demand | User Channel 3:name2 | Apparent Power Demand (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Apparent Power Demand (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Apparent Power Demand (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 3:name2 | Apparent Power Demand (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 9330 | 0x2472 | float32 | User Channel 3 Apparent Power Demand | 11-18 | PASS
Acurev4100 | Demand | User Channel 4:name2 | Current Demand (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Current Demand (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Current Demand (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Current Demand (A) | User Channel | 0.000 | 0 | 0 | 0 | 9332 | 0x2474 | float32 | User Channel 4 Current Demand | 11-19 | PASS
Acurev4100 | Demand | User Channel 4:name2 | Import Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Import Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Import Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Import Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9334 | 0x2476 | float32 | User Channel 4 Import Active Power Demand | 11-20 | PASS
Acurev4100 | Demand | User Channel 4:name2 | Export Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Export Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Export Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Export Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9336 | 0x2478 | float32 | User Channel 4 Export Active Power Demand | 11-21 | PASS
Acurev4100 | Demand | User Channel 4:name2 | Import Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Import Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Import Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Import Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9338 | 0x247A | float32 | User Channel 4 Import Reactive Power Demand | 11-22 | PASS
Acurev4100 | Demand | User Channel 4:name2 | Export Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Export Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Export Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Export Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9340 | 0x247C | float32 | User Channel 4 Export Reactive Power Demand | 11-23 | PASS
Acurev4100 | Demand | User Channel 4:name2 | Apparent Power Demand (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Apparent Power Demand (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Apparent Power Demand (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 4:name2 | Apparent Power Demand (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 9342 | 0x247E | float32 | User Channel 4 Apparent Power Demand | 11-24 | PASS
Acurev4100 | Demand | User Channel 5:name5 | Current Demand (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Current Demand (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Current Demand (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Current Demand (A) | User Channel | 0.000 | 0 | 0 | 0 | 9344 | 0x2480 | float32 | User Channel 5 Current Demand | 11-25 | PASS
Acurev4100 | Demand | User Channel 5:name5 | Import Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Import Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Import Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Import Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9346 | 0x2482 | float32 | User Channel 5 Import Active Power Demand | 11-26 | PASS
Acurev4100 | Demand | User Channel 5:name5 | Export Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Export Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Export Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Export Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9348 | 0x2484 | float32 | User Channel 5 Export Active Power Demand | 11-27 | PASS
Acurev4100 | Demand | User Channel 5:name5 | Import Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Import Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Import Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Import Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9350 | 0x2486 | float32 | User Channel 5 Import Reactive Power Demand | 11-28 | PASS
Acurev4100 | Demand | User Channel 5:name5 | Export Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Export Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Export Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Export Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9352 | 0x2488 | float32 | User Channel 5 Export Reactive Power Demand | 11-29 | PASS
Acurev4100 | Demand | User Channel 5:name5 | Apparent Power Demand (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Apparent Power Demand (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Apparent Power Demand (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 5:name5 | Apparent Power Demand (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 9354 | 0x248A | float32 | User Channel 5 Apparent Power Demand | 11-30 | PASS
Acurev4100 | Demand | User Channel 6:6666 | Current Demand (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Current Demand (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Current Demand (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Current Demand (A) | User Channel | 0.000 | 0 | 0 | 0 | 9356 | 0x248C | float32 | User Channel 6 Current Demand | 11-31 | PASS
Acurev4100 | Demand | User Channel 6:6666 | Import Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Import Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Import Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Import Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9358 | 0x248E | float32 | User Channel 6 Import Active Power Demand | 11-32 | PASS
Acurev4100 | Demand | User Channel 6:6666 | Export Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Export Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Export Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Export Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9360 | 0x2490 | float32 | User Channel 6 Export Active Power Demand | 11-33 | PASS
Acurev4100 | Demand | User Channel 6:6666 | Import Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Import Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Import Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Import Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9362 | 0x2492 | float32 | User Channel 6 Import Reactive Power Demand | 11-34 | PASS
Acurev4100 | Demand | User Channel 6:6666 | Export Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Export Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Export Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Export Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9364 | 0x2494 | float32 | User Channel 6 Export Reactive Power Demand | 11-35 | PASS
Acurev4100 | Demand | User Channel 6:6666 | Apparent Power Demand (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Apparent Power Demand (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Apparent Power Demand (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 6:6666 | Apparent Power Demand (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 9366 | 0x2496 | float32 | User Channel 6 Apparent Power Demand | 11-36 | PASS
Acurev4100 | Demand | User Channel 7:7777 | Current Demand (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Current Demand (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Current Demand (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Current Demand (A) | User Channel | 0.000 | 0 | 0 | 0 | 9368 | 0x2498 | float32 | User Channel 7 Current Demand | 12-1 | PASS
Acurev4100 | Demand | User Channel 7:7777 | Import Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Import Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Import Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Import Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9370 | 0x249A | float32 | User Channel 7 Import Active Power Demand | 12-2 | PASS
Acurev4100 | Demand | User Channel 7:7777 | Export Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Export Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Export Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Export Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9372 | 0x249C | float32 | User Channel 7 Export Active Power Demand | 12-3 | PASS
Acurev4100 | Demand | User Channel 7:7777 | Import Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Import Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Import Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Import Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9374 | 0x249E | float32 | User Channel 7 Import Reactive Power Demand | 12-4 | PASS
Acurev4100 | Demand | User Channel 7:7777 | Export Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Export Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Export Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Export Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9376 | 0x24A0 | float32 | User Channel 7 Export Reactive Power Demand | 12-5 | PASS
Acurev4100 | Demand | User Channel 7:7777 | Apparent Power Demand (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Apparent Power Demand (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Apparent Power Demand (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 7:7777 | Apparent Power Demand (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 9378 | 0x24A2 | float32 | User Channel 7 Apparent Power Demand | 12-6 | PASS
Acurev4100 | Demand | User Channel 8:9999 | Current Demand (A) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Current Demand (A) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Current Demand (A) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Current Demand (A) | User Channel | 0.000 | 0 | 0 | 0 | 9380 | 0x24A4 | float32 | User Channel 8 Current Demand | 12-7 | PASS
Acurev4100 | Demand | User Channel 8:9999 | Import Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Import Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Import Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Import Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9382 | 0x24A6 | float32 | User Channel 8 Import Active Power Demand | 12-8 | PASS
Acurev4100 | Demand | User Channel 8:9999 | Export Active Power Demand (kW) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Export Active Power Demand (kW) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Export Active Power Demand (kW) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Export Active Power Demand (kW) | User Channel | 0.000 | 0 | 0 | 0 | 9384 | 0x24A8 | float32 | User Channel 8 Export Active Power Demand | 12-9 | PASS
Acurev4100 | Demand | User Channel 8:9999 | Import Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Import Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Import Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Import Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9386 | 0x24AA | float32 | User Channel 8 Import Reactive Power Demand | 12-10 | PASS
Acurev4100 | Demand | User Channel 8:9999 | Export Reactive Power Demand (kvar) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Export Reactive Power Demand (kvar) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Export Reactive Power Demand (kvar) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Export Reactive Power Demand (kvar) | User Channel | 0.000 | 0 | 0 | 0 | 9388 | 0x24AC | float32 | User Channel 8 Export Reactive Power Demand | 12-11 | PASS
Acurev4100 | Demand | User Channel 8:9999 | Apparent Power Demand (kVA) | Phase A | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Apparent Power Demand (kVA) | Phase B | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Apparent Power Demand (kVA) | Phase C | 0.000 | [8 empty] | 无寄存器
Acurev4100 | Demand | User Channel 8:9999 | Apparent Power Demand (kVA) | User Channel | 0.000 | 0 | 0 | 0 | 9390 | 0x24AE | float32 | User Channel 8 Apparent Power Demand | 12-12 | PASS
Acurev4100 | Energy | (system) | Import Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12288 | 0x3000 | double | Phase A active energy import | 42-1 | PASS
Acurev4100 | Energy | (system) | Import Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12324 | 0x3024 | double | Phase B active energy import | 42-10 | PASS
Acurev4100 | Energy | (system) | Import Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12360 | 0x3048 | double | Phase C active energy import | 42-19 | PASS
Acurev4100 | Energy | (system) | Import Active Energy (kWh) | System | 0.000 | 0 | 0 | 0 | 12396 | 0x306C | double | System active energy import | 42-28 | PASS
Acurev4100 | Energy | (system) | Export Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12292 | 0x3004 | double | Phase A active energy export | 42-2 | PASS
Acurev4100 | Energy | (system) | Export Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12328 | 0x3028 | double | Phase B active energy export | 42-11 | PASS
Acurev4100 | Energy | (system) | Export Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12364 | 0x304C | double | Phase C active energy export | 42-20 | PASS
Acurev4100 | Energy | (system) | Export Active Energy (kWh) | System | 0.000 | 0 | 0 | 0 | 12400 | 0x3070 | double | System active energy export | 42-29 | PASS
Acurev4100 | Energy | (system) | Net Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12296 | 0x3008 | double | Phase A active energy net | 42-3 | PASS
Acurev4100 | Energy | (system) | Net Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12332 | 0x302C | double | Phase B active energy net | 42-12 | PASS
Acurev4100 | Energy | (system) | Net Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12368 | 0x3050 | double | Phase C active energy net | 42-21 | PASS
Acurev4100 | Energy | (system) | Net Active Energy (kWh) | System | 0.000 | 0 | 0 | 0 | 12404 | 0x3074 | double | System active energy net | 42-30 | PASS
Acurev4100 | Energy | (system) | Total Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12300 | 0x300C | double | Phase A active energy total | 42-4 | PASS
Acurev4100 | Energy | (system) | Total Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12336 | 0x3030 | double | Phase B active energy total | 42-13 | PASS
Acurev4100 | Energy | (system) | Total Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12372 | 0x3054 | double | Phase C active energy total | 42-22 | PASS
Acurev4100 | Energy | (system) | Total Active Energy (kWh) | System | 0.000 | 0 | 0 | 0 | 12408 | 0x3078 | double | System active energy total | 42-31 | PASS
Acurev4100 | Energy | (system) | Import Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12304 | 0x3010 | double | Phase A reactive energy import | 42-5 | PASS
Acurev4100 | Energy | (system) | Import Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12340 | 0x3034 | double | Phase B reactive energy import | 42-14 | PASS
Acurev4100 | Energy | (system) | Import Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12376 | 0x3058 | double | Phase C reactive energy import | 42-23 | PASS
Acurev4100 | Energy | (system) | Import Reactive Energy (kvarh) | System | 0.000 | 0 | 0 | 0 | 12412 | 0x307C | double | System reactive energy import | 43-1 | PASS
Acurev4100 | Energy | (system) | Export Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12308 | 0x3014 | double | Phase A reactive energy export | 42-6 | PASS
Acurev4100 | Energy | (system) | Export Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12344 | 0x3038 | double | Phase B reactive energy export | 42-15 | PASS
Acurev4100 | Energy | (system) | Export Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12380 | 0x305C | double | Phase C reactive energy export | 42-24 | PASS
Acurev4100 | Energy | (system) | Export Reactive Energy (kvarh) | System | 0.000 | 0 | 0 | 0 | 12416 | 0x3080 | double | System reactive energy export | 43-2 | PASS
Acurev4100 | Energy | (system) | Net Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12312 | 0x3018 | double | Phase A reactive energy net | 42-7 | PASS
Acurev4100 | Energy | (system) | Net Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12348 | 0x303C | double | Phase B reactive energy net | 42-16 | PASS
Acurev4100 | Energy | (system) | Net Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12384 | 0x3060 | double | Phase C reactive energy net | 42-25 | PASS
Acurev4100 | Energy | (system) | Net Reactive Energy (kvarh) | System | 0.000 | 0 | 0 | 0 | 12420 | 0x3084 | double | System reactive energy net | 43-3 | PASS
Acurev4100 | Energy | (system) | Total Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12316 | 0x301C | double | Phase A reactive energy total | 42-8 | PASS
Acurev4100 | Energy | (system) | Total Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12352 | 0x3040 | double | Phase B reactive energy total | 42-17 | PASS
Acurev4100 | Energy | (system) | Total Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12388 | 0x3064 | double | Phase C reactive energy total | 42-26 | PASS
Acurev4100 | Energy | (system) | Total Reactive Energy (kvarh) | System | 0.000 | 0 | 0 | 0 | 12424 | 0x3088 | double | System reactive energy total | 43-4 | PASS
Acurev4100 | Energy | (system) | Apparent Energy (kVAh) | Phase A | 0.000 | 0 | 0 | 0 | 12320 | 0x3020 | double | Phase A apparent energy | 42-9 | PASS
Acurev4100 | Energy | (system) | Apparent Energy (kVAh) | Phase B | 0.000 | 0 | 0 | 0 | 12356 | 0x3044 | double | Phase B apparent energy | 42-18 | PASS
Acurev4100 | Energy | (system) | Apparent Energy (kVAh) | Phase C | 0.000 | 0 | 0 | 0 | 12392 | 0x3068 | double | Phase C apparent energy | 42-27 | PASS
Acurev4100 | Energy | (system) | Apparent Energy (kVAh) | System | 0.000 | 0 | 0 | 0 | 12428 | 0x308C | double | System apparent energy | 43-5 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Import Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12288 | 0x3000 | double | Phase A active energy import | 42-1 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Import Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12324 | 0x3024 | double | Phase B active energy import | 42-10 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Import Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12360 | 0x3048 | double | Phase C active energy import | 42-19 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Import Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13296 | 0x33F0 | double | User Channel 1 active energy import | 50-5 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Export Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12292 | 0x3004 | double | Phase A active energy export | 42-2 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Export Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12328 | 0x3028 | double | Phase B active energy export | 42-11 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Export Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12364 | 0x304C | double | Phase C active energy export | 42-20 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Export Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13300 | 0x33F4 | double | User Channel 1 active energy export | 50-6 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Net Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12296 | 0x3008 | double | Phase A active energy net | 42-3 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Net Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12332 | 0x302C | double | Phase B active energy net | 42-12 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Net Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12368 | 0x3050 | double | Phase C active energy net | 42-21 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Net Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13304 | 0x33F8 | double | User Channel 1 active energy net | 50-7 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Total Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12300 | 0x300C | double | Phase A active energy total | 42-4 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Total Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12336 | 0x3030 | double | Phase B active energy total | 42-13 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Total Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12372 | 0x3054 | double | Phase C active energy total | 42-22 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Total Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13308 | 0x33FC | double | User Channel 1 active energy total | 50-8 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Import Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12304 | 0x3010 | double | Phase A reactive energy import | 42-5 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Import Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12340 | 0x3034 | double | Phase B reactive energy import | 42-14 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Import Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12376 | 0x3058 | double | Phase C reactive energy import | 42-23 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Import Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13312 | 0x3400 | double | User Channel 1 reactive energy import | 50-9 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Export Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12308 | 0x3014 | double | Phase A reactive energy export | 42-6 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Export Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12344 | 0x3038 | double | Phase B reactive energy export | 42-15 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Export Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12380 | 0x305C | double | Phase C reactive energy export | 42-24 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Export Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13316 | 0x3404 | double | User Channel 1 reactive energy export | 50-10 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Net Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12312 | 0x3018 | double | Phase A reactive energy net | 42-7 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Net Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12348 | 0x303C | double | Phase B reactive energy net | 42-16 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Net Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12384 | 0x3060 | double | Phase C reactive energy net | 42-25 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Net Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13320 | 0x3408 | double | User Channel 1 reactive energy net | 50-11 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Total Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12316 | 0x301C | double | Phase A reactive energy total | 42-8 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Total Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12352 | 0x3040 | double | Phase B reactive energy total | 42-17 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Total Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12388 | 0x3064 | double | Phase C reactive energy total | 42-26 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Total Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13324 | 0x340C | double | User Channel 1 reactive energy total | 50-12 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Apparent Energy (kVAh) | Phase A | 0.000 | 0 | 0 | 0 | 12320 | 0x3020 | double | Phase A apparent energy | 42-9 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Apparent Energy (kVAh) | Phase B | 0.000 | 0 | 0 | 0 | 12356 | 0x3044 | double | Phase B apparent energy | 42-18 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Apparent Energy (kVAh) | Phase C | 0.000 | 0 | 0 | 0 | 12392 | 0x3068 | double | Phase C apparent energy | 42-27 | PASS
Acurev4100 | Energy | User Channel 1:name1 | Apparent Energy (kVAh) | User Channel | 0.000 | 0 | 0 | 0 | 13328 | 0x3410 | double | User Channel 1 apparent energy | 50-13 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Import Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12288 | 0x3000 | double | Phase A active energy import | 42-1 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Import Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12324 | 0x3024 | double | Phase B active energy import | 42-10 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Import Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12360 | 0x3048 | double | Phase C active energy import | 42-19 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Import Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13296 | 0x33F0 | double | User Channel 1 active energy import | 50-5 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Export Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12292 | 0x3004 | double | Phase A active energy export | 42-2 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Export Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12328 | 0x3028 | double | Phase B active energy export | 42-11 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Export Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12364 | 0x304C | double | Phase C active energy export | 42-20 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Export Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13300 | 0x33F4 | double | User Channel 1 active energy export | 50-6 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Net Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12296 | 0x3008 | double | Phase A active energy net | 42-3 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Net Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12332 | 0x302C | double | Phase B active energy net | 42-12 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Net Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12368 | 0x3050 | double | Phase C active energy net | 42-21 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Net Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13304 | 0x33F8 | double | User Channel 1 active energy net | 50-7 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Total Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12300 | 0x300C | double | Phase A active energy total | 42-4 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Total Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12336 | 0x3030 | double | Phase B active energy total | 42-13 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Total Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12372 | 0x3054 | double | Phase C active energy total | 42-22 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Total Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13308 | 0x33FC | double | User Channel 1 active energy total | 50-8 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Import Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12304 | 0x3010 | double | Phase A reactive energy import | 42-5 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Import Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12340 | 0x3034 | double | Phase B reactive energy import | 42-14 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Import Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12376 | 0x3058 | double | Phase C reactive energy import | 42-23 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Import Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13312 | 0x3400 | double | User Channel 1 reactive energy import | 50-9 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Export Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12308 | 0x3014 | double | Phase A reactive energy export | 42-6 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Export Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12344 | 0x3038 | double | Phase B reactive energy export | 42-15 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Export Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12380 | 0x305C | double | Phase C reactive energy export | 42-24 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Export Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13316 | 0x3404 | double | User Channel 1 reactive energy export | 50-10 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Net Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12312 | 0x3018 | double | Phase A reactive energy net | 42-7 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Net Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12348 | 0x303C | double | Phase B reactive energy net | 42-16 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Net Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12384 | 0x3060 | double | Phase C reactive energy net | 42-25 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Net Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13320 | 0x3408 | double | User Channel 1 reactive energy net | 50-11 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Total Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12316 | 0x301C | double | Phase A reactive energy total | 42-8 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Total Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12352 | 0x3040 | double | Phase B reactive energy total | 42-17 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Total Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12388 | 0x3064 | double | Phase C reactive energy total | 42-26 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Total Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13324 | 0x340C | double | User Channel 1 reactive energy total | 50-12 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Apparent Energy (kVAh) | Phase A | 0.000 | 0 | 0 | 0 | 12320 | 0x3020 | double | Phase A apparent energy | 42-9 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Apparent Energy (kVAh) | Phase B | 0.000 | 0 | 0 | 0 | 12356 | 0x3044 | double | Phase B apparent energy | 42-18 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Apparent Energy (kVAh) | Phase C | 0.000 | 0 | 0 | 0 | 12392 | 0x3068 | double | Phase C apparent energy | 42-27 | PASS
Acurev4100 | Energy | User Channel 2:name1 | Apparent Energy (kVAh) | User Channel | 0.000 | 0 | 0 | 0 | 13328 | 0x3410 | double | User Channel 1 apparent energy | 50-13 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Import Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12288 | 0x3000 | double | Phase A active energy import | 42-1 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Import Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12324 | 0x3024 | double | Phase B active energy import | 42-10 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Import Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12360 | 0x3048 | double | Phase C active energy import | 42-19 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Import Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13296 | 0x33F0 | double | User Channel 1 active energy import | 50-5 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Export Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12292 | 0x3004 | double | Phase A active energy export | 42-2 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Export Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12328 | 0x3028 | double | Phase B active energy export | 42-11 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Export Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12364 | 0x304C | double | Phase C active energy export | 42-20 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Export Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13300 | 0x33F4 | double | User Channel 1 active energy export | 50-6 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Net Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12296 | 0x3008 | double | Phase A active energy net | 42-3 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Net Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12332 | 0x302C | double | Phase B active energy net | 42-12 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Net Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12368 | 0x3050 | double | Phase C active energy net | 42-21 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Net Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13304 | 0x33F8 | double | User Channel 1 active energy net | 50-7 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Total Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12300 | 0x300C | double | Phase A active energy total | 42-4 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Total Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12336 | 0x3030 | double | Phase B active energy total | 42-13 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Total Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12372 | 0x3054 | double | Phase C active energy total | 42-22 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Total Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13308 | 0x33FC | double | User Channel 1 active energy total | 50-8 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Import Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12304 | 0x3010 | double | Phase A reactive energy import | 42-5 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Import Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12340 | 0x3034 | double | Phase B reactive energy import | 42-14 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Import Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12376 | 0x3058 | double | Phase C reactive energy import | 42-23 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Import Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13312 | 0x3400 | double | User Channel 1 reactive energy import | 50-9 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Export Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12308 | 0x3014 | double | Phase A reactive energy export | 42-6 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Export Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12344 | 0x3038 | double | Phase B reactive energy export | 42-15 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Export Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12380 | 0x305C | double | Phase C reactive energy export | 42-24 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Export Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13316 | 0x3404 | double | User Channel 1 reactive energy export | 50-10 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Net Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12312 | 0x3018 | double | Phase A reactive energy net | 42-7 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Net Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12348 | 0x303C | double | Phase B reactive energy net | 42-16 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Net Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12384 | 0x3060 | double | Phase C reactive energy net | 42-25 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Net Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13320 | 0x3408 | double | User Channel 1 reactive energy net | 50-11 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Total Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12316 | 0x301C | double | Phase A reactive energy total | 42-8 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Total Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12352 | 0x3040 | double | Phase B reactive energy total | 42-17 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Total Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12388 | 0x3064 | double | Phase C reactive energy total | 42-26 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Total Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13324 | 0x340C | double | User Channel 1 reactive energy total | 50-12 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Apparent Energy (kVAh) | Phase A | 0.000 | 0 | 0 | 0 | 12320 | 0x3020 | double | Phase A apparent energy | 42-9 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Apparent Energy (kVAh) | Phase B | 0.000 | 0 | 0 | 0 | 12356 | 0x3044 | double | Phase B apparent energy | 42-18 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Apparent Energy (kVAh) | Phase C | 0.000 | 0 | 0 | 0 | 12392 | 0x3068 | double | Phase C apparent energy | 42-27 | PASS
Acurev4100 | Energy | User Channel 3:name2 | Apparent Energy (kVAh) | User Channel | 0.000 | 0 | 0 | 0 | 13328 | 0x3410 | double | User Channel 1 apparent energy | 50-13 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Import Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12288 | 0x3000 | double | Phase A active energy import | 42-1 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Import Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12324 | 0x3024 | double | Phase B active energy import | 42-10 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Import Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12360 | 0x3048 | double | Phase C active energy import | 42-19 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Import Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13296 | 0x33F0 | double | User Channel 1 active energy import | 50-5 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Export Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12292 | 0x3004 | double | Phase A active energy export | 42-2 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Export Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12328 | 0x3028 | double | Phase B active energy export | 42-11 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Export Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12364 | 0x304C | double | Phase C active energy export | 42-20 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Export Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13300 | 0x33F4 | double | User Channel 1 active energy export | 50-6 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Net Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12296 | 0x3008 | double | Phase A active energy net | 42-3 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Net Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12332 | 0x302C | double | Phase B active energy net | 42-12 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Net Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12368 | 0x3050 | double | Phase C active energy net | 42-21 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Net Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13304 | 0x33F8 | double | User Channel 1 active energy net | 50-7 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Total Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12300 | 0x300C | double | Phase A active energy total | 42-4 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Total Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12336 | 0x3030 | double | Phase B active energy total | 42-13 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Total Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12372 | 0x3054 | double | Phase C active energy total | 42-22 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Total Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13308 | 0x33FC | double | User Channel 1 active energy total | 50-8 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Import Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12304 | 0x3010 | double | Phase A reactive energy import | 42-5 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Import Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12340 | 0x3034 | double | Phase B reactive energy import | 42-14 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Import Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12376 | 0x3058 | double | Phase C reactive energy import | 42-23 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Import Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13312 | 0x3400 | double | User Channel 1 reactive energy import | 50-9 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Export Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12308 | 0x3014 | double | Phase A reactive energy export | 42-6 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Export Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12344 | 0x3038 | double | Phase B reactive energy export | 42-15 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Export Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12380 | 0x305C | double | Phase C reactive energy export | 42-24 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Export Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13316 | 0x3404 | double | User Channel 1 reactive energy export | 50-10 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Net Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12312 | 0x3018 | double | Phase A reactive energy net | 42-7 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Net Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12348 | 0x303C | double | Phase B reactive energy net | 42-16 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Net Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12384 | 0x3060 | double | Phase C reactive energy net | 42-25 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Net Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13320 | 0x3408 | double | User Channel 1 reactive energy net | 50-11 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Total Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12316 | 0x301C | double | Phase A reactive energy total | 42-8 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Total Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12352 | 0x3040 | double | Phase B reactive energy total | 42-17 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Total Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12388 | 0x3064 | double | Phase C reactive energy total | 42-26 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Total Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13324 | 0x340C | double | User Channel 1 reactive energy total | 50-12 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Apparent Energy (kVAh) | Phase A | 0.000 | 0 | 0 | 0 | 12320 | 0x3020 | double | Phase A apparent energy | 42-9 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Apparent Energy (kVAh) | Phase B | 0.000 | 0 | 0 | 0 | 12356 | 0x3044 | double | Phase B apparent energy | 42-18 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Apparent Energy (kVAh) | Phase C | 0.000 | 0 | 0 | 0 | 12392 | 0x3068 | double | Phase C apparent energy | 42-27 | PASS
Acurev4100 | Energy | User Channel 4:name2 | Apparent Energy (kVAh) | User Channel | 0.000 | 0 | 0 | 0 | 13328 | 0x3410 | double | User Channel 1 apparent energy | 50-13 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Import Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12288 | 0x3000 | double | Phase A active energy import | 42-1 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Import Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12324 | 0x3024 | double | Phase B active energy import | 42-10 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Import Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12360 | 0x3048 | double | Phase C active energy import | 42-19 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Import Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13296 | 0x33F0 | double | User Channel 1 active energy import | 50-5 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Export Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12292 | 0x3004 | double | Phase A active energy export | 42-2 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Export Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12328 | 0x3028 | double | Phase B active energy export | 42-11 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Export Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12364 | 0x304C | double | Phase C active energy export | 42-20 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Export Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13300 | 0x33F4 | double | User Channel 1 active energy export | 50-6 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Net Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12296 | 0x3008 | double | Phase A active energy net | 42-3 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Net Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12332 | 0x302C | double | Phase B active energy net | 42-12 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Net Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12368 | 0x3050 | double | Phase C active energy net | 42-21 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Net Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13304 | 0x33F8 | double | User Channel 1 active energy net | 50-7 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Total Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12300 | 0x300C | double | Phase A active energy total | 42-4 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Total Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12336 | 0x3030 | double | Phase B active energy total | 42-13 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Total Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12372 | 0x3054 | double | Phase C active energy total | 42-22 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Total Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13308 | 0x33FC | double | User Channel 1 active energy total | 50-8 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Import Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12304 | 0x3010 | double | Phase A reactive energy import | 42-5 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Import Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12340 | 0x3034 | double | Phase B reactive energy import | 42-14 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Import Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12376 | 0x3058 | double | Phase C reactive energy import | 42-23 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Import Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13312 | 0x3400 | double | User Channel 1 reactive energy import | 50-9 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Export Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12308 | 0x3014 | double | Phase A reactive energy export | 42-6 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Export Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12344 | 0x3038 | double | Phase B reactive energy export | 42-15 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Export Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12380 | 0x305C | double | Phase C reactive energy export | 42-24 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Export Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13316 | 0x3404 | double | User Channel 1 reactive energy export | 50-10 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Net Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12312 | 0x3018 | double | Phase A reactive energy net | 42-7 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Net Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12348 | 0x303C | double | Phase B reactive energy net | 42-16 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Net Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12384 | 0x3060 | double | Phase C reactive energy net | 42-25 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Net Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13320 | 0x3408 | double | User Channel 1 reactive energy net | 50-11 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Total Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12316 | 0x301C | double | Phase A reactive energy total | 42-8 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Total Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12352 | 0x3040 | double | Phase B reactive energy total | 42-17 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Total Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12388 | 0x3064 | double | Phase C reactive energy total | 42-26 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Total Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13324 | 0x340C | double | User Channel 1 reactive energy total | 50-12 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Apparent Energy (kVAh) | Phase A | 0.000 | 0 | 0 | 0 | 12320 | 0x3020 | double | Phase A apparent energy | 42-9 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Apparent Energy (kVAh) | Phase B | 0.000 | 0 | 0 | 0 | 12356 | 0x3044 | double | Phase B apparent energy | 42-18 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Apparent Energy (kVAh) | Phase C | 0.000 | 0 | 0 | 0 | 12392 | 0x3068 | double | Phase C apparent energy | 42-27 | PASS
Acurev4100 | Energy | User Channel 5:name5 | Apparent Energy (kVAh) | User Channel | 0.000 | 0 | 0 | 0 | 13328 | 0x3410 | double | User Channel 1 apparent energy | 50-13 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Import Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12288 | 0x3000 | double | Phase A active energy import | 42-1 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Import Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12324 | 0x3024 | double | Phase B active energy import | 42-10 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Import Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12360 | 0x3048 | double | Phase C active energy import | 42-19 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Import Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13296 | 0x33F0 | double | User Channel 1 active energy import | 50-5 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Export Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12292 | 0x3004 | double | Phase A active energy export | 42-2 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Export Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12328 | 0x3028 | double | Phase B active energy export | 42-11 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Export Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12364 | 0x304C | double | Phase C active energy export | 42-20 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Export Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13300 | 0x33F4 | double | User Channel 1 active energy export | 50-6 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Net Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12296 | 0x3008 | double | Phase A active energy net | 42-3 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Net Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12332 | 0x302C | double | Phase B active energy net | 42-12 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Net Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12368 | 0x3050 | double | Phase C active energy net | 42-21 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Net Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13304 | 0x33F8 | double | User Channel 1 active energy net | 50-7 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Total Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12300 | 0x300C | double | Phase A active energy total | 42-4 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Total Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12336 | 0x3030 | double | Phase B active energy total | 42-13 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Total Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12372 | 0x3054 | double | Phase C active energy total | 42-22 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Total Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13308 | 0x33FC | double | User Channel 1 active energy total | 50-8 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Import Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12304 | 0x3010 | double | Phase A reactive energy import | 42-5 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Import Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12340 | 0x3034 | double | Phase B reactive energy import | 42-14 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Import Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12376 | 0x3058 | double | Phase C reactive energy import | 42-23 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Import Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13312 | 0x3400 | double | User Channel 1 reactive energy import | 50-9 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Export Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12308 | 0x3014 | double | Phase A reactive energy export | 42-6 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Export Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12344 | 0x3038 | double | Phase B reactive energy export | 42-15 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Export Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12380 | 0x305C | double | Phase C reactive energy export | 42-24 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Export Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13316 | 0x3404 | double | User Channel 1 reactive energy export | 50-10 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Net Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12312 | 0x3018 | double | Phase A reactive energy net | 42-7 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Net Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12348 | 0x303C | double | Phase B reactive energy net | 42-16 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Net Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12384 | 0x3060 | double | Phase C reactive energy net | 42-25 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Net Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13320 | 0x3408 | double | User Channel 1 reactive energy net | 50-11 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Total Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12316 | 0x301C | double | Phase A reactive energy total | 42-8 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Total Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12352 | 0x3040 | double | Phase B reactive energy total | 42-17 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Total Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12388 | 0x3064 | double | Phase C reactive energy total | 42-26 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Total Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13324 | 0x340C | double | User Channel 1 reactive energy total | 50-12 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Apparent Energy (kVAh) | Phase A | 0.000 | 0 | 0 | 0 | 12320 | 0x3020 | double | Phase A apparent energy | 42-9 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Apparent Energy (kVAh) | Phase B | 0.000 | 0 | 0 | 0 | 12356 | 0x3044 | double | Phase B apparent energy | 42-18 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Apparent Energy (kVAh) | Phase C | 0.000 | 0 | 0 | 0 | 12392 | 0x3068 | double | Phase C apparent energy | 42-27 | PASS
Acurev4100 | Energy | User Channel 6:6666 | Apparent Energy (kVAh) | User Channel | 0.000 | 0 | 0 | 0 | 13328 | 0x3410 | double | User Channel 1 apparent energy | 50-13 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Import Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12288 | 0x3000 | double | Phase A active energy import | 42-1 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Import Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12324 | 0x3024 | double | Phase B active energy import | 42-10 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Import Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12360 | 0x3048 | double | Phase C active energy import | 42-19 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Import Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13296 | 0x33F0 | double | User Channel 1 active energy import | 50-5 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Export Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12292 | 0x3004 | double | Phase A active energy export | 42-2 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Export Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12328 | 0x3028 | double | Phase B active energy export | 42-11 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Export Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12364 | 0x304C | double | Phase C active energy export | 42-20 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Export Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13300 | 0x33F4 | double | User Channel 1 active energy export | 50-6 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Net Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12296 | 0x3008 | double | Phase A active energy net | 42-3 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Net Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12332 | 0x302C | double | Phase B active energy net | 42-12 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Net Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12368 | 0x3050 | double | Phase C active energy net | 42-21 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Net Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13304 | 0x33F8 | double | User Channel 1 active energy net | 50-7 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Total Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12300 | 0x300C | double | Phase A active energy total | 42-4 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Total Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12336 | 0x3030 | double | Phase B active energy total | 42-13 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Total Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12372 | 0x3054 | double | Phase C active energy total | 42-22 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Total Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13308 | 0x33FC | double | User Channel 1 active energy total | 50-8 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Import Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12304 | 0x3010 | double | Phase A reactive energy import | 42-5 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Import Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12340 | 0x3034 | double | Phase B reactive energy import | 42-14 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Import Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12376 | 0x3058 | double | Phase C reactive energy import | 42-23 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Import Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13312 | 0x3400 | double | User Channel 1 reactive energy import | 50-9 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Export Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12308 | 0x3014 | double | Phase A reactive energy export | 42-6 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Export Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12344 | 0x3038 | double | Phase B reactive energy export | 42-15 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Export Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12380 | 0x305C | double | Phase C reactive energy export | 42-24 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Export Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13316 | 0x3404 | double | User Channel 1 reactive energy export | 50-10 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Net Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12312 | 0x3018 | double | Phase A reactive energy net | 42-7 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Net Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12348 | 0x303C | double | Phase B reactive energy net | 42-16 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Net Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12384 | 0x3060 | double | Phase C reactive energy net | 42-25 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Net Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13320 | 0x3408 | double | User Channel 1 reactive energy net | 50-11 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Total Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12316 | 0x301C | double | Phase A reactive energy total | 42-8 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Total Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12352 | 0x3040 | double | Phase B reactive energy total | 42-17 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Total Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12388 | 0x3064 | double | Phase C reactive energy total | 42-26 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Total Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13324 | 0x340C | double | User Channel 1 reactive energy total | 50-12 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Apparent Energy (kVAh) | Phase A | 0.000 | 0 | 0 | 0 | 12320 | 0x3020 | double | Phase A apparent energy | 42-9 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Apparent Energy (kVAh) | Phase B | 0.000 | 0 | 0 | 0 | 12356 | 0x3044 | double | Phase B apparent energy | 42-18 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Apparent Energy (kVAh) | Phase C | 0.000 | 0 | 0 | 0 | 12392 | 0x3068 | double | Phase C apparent energy | 42-27 | PASS
Acurev4100 | Energy | User Channel 7:7777 | Apparent Energy (kVAh) | User Channel | 0.000 | 0 | 0 | 0 | 13328 | 0x3410 | double | User Channel 1 apparent energy | 50-13 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Import Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12288 | 0x3000 | double | Phase A active energy import | 42-1 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Import Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12324 | 0x3024 | double | Phase B active energy import | 42-10 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Import Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12360 | 0x3048 | double | Phase C active energy import | 42-19 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Import Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13296 | 0x33F0 | double | User Channel 1 active energy import | 50-5 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Export Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12292 | 0x3004 | double | Phase A active energy export | 42-2 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Export Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12328 | 0x3028 | double | Phase B active energy export | 42-11 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Export Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12364 | 0x304C | double | Phase C active energy export | 42-20 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Export Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13300 | 0x33F4 | double | User Channel 1 active energy export | 50-6 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Net Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12296 | 0x3008 | double | Phase A active energy net | 42-3 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Net Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12332 | 0x302C | double | Phase B active energy net | 42-12 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Net Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12368 | 0x3050 | double | Phase C active energy net | 42-21 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Net Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13304 | 0x33F8 | double | User Channel 1 active energy net | 50-7 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Total Active Energy (kWh) | Phase A | 0.000 | 0 | 0 | 0 | 12300 | 0x300C | double | Phase A active energy total | 42-4 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Total Active Energy (kWh) | Phase B | 0.000 | 0 | 0 | 0 | 12336 | 0x3030 | double | Phase B active energy total | 42-13 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Total Active Energy (kWh) | Phase C | 0.000 | 0 | 0 | 0 | 12372 | 0x3054 | double | Phase C active energy total | 42-22 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Total Active Energy (kWh) | User Channel | 0.000 | 0 | 0 | 0 | 13308 | 0x33FC | double | User Channel 1 active energy total | 50-8 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Import Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12304 | 0x3010 | double | Phase A reactive energy import | 42-5 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Import Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12340 | 0x3034 | double | Phase B reactive energy import | 42-14 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Import Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12376 | 0x3058 | double | Phase C reactive energy import | 42-23 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Import Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13312 | 0x3400 | double | User Channel 1 reactive energy import | 50-9 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Export Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12308 | 0x3014 | double | Phase A reactive energy export | 42-6 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Export Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12344 | 0x3038 | double | Phase B reactive energy export | 42-15 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Export Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12380 | 0x305C | double | Phase C reactive energy export | 42-24 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Export Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13316 | 0x3404 | double | User Channel 1 reactive energy export | 50-10 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Net Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12312 | 0x3018 | double | Phase A reactive energy net | 42-7 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Net Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12348 | 0x303C | double | Phase B reactive energy net | 42-16 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Net Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12384 | 0x3060 | double | Phase C reactive energy net | 42-25 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Net Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13320 | 0x3408 | double | User Channel 1 reactive energy net | 50-11 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Total Reactive Energy (kvarh) | Phase A | 0.000 | 0 | 0 | 0 | 12316 | 0x301C | double | Phase A reactive energy total | 42-8 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Total Reactive Energy (kvarh) | Phase B | 0.000 | 0 | 0 | 0 | 12352 | 0x3040 | double | Phase B reactive energy total | 42-17 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Total Reactive Energy (kvarh) | Phase C | 0.000 | 0 | 0 | 0 | 12388 | 0x3064 | double | Phase C reactive energy total | 42-26 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Total Reactive Energy (kvarh) | User Channel | 0.000 | 0 | 0 | 0 | 13324 | 0x340C | double | User Channel 1 reactive energy total | 50-12 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Apparent Energy (kVAh) | Phase A | 0.000 | 0 | 0 | 0 | 12320 | 0x3020 | double | Phase A apparent energy | 42-9 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Apparent Energy (kVAh) | Phase B | 0.000 | 0 | 0 | 0 | 12356 | 0x3044 | double | Phase B apparent energy | 42-18 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Apparent Energy (kVAh) | Phase C | 0.000 | 0 | 0 | 0 | 12392 | 0x3068 | double | Phase C apparent energy | 42-27 | PASS
Acurev4100 | Energy | User Channel 8:9999 | Apparent Energy (kVAh) | User Channel | 0.000 | 0 | 0 | 0 | 13328 | 0x3410 | double | User Channel 1 apparent energy | 50-13 | PASS
Acurev4100 | THD | (system) | Voltage Crest Factor | Average | - | [8 empty] | 无寄存器
Acurev4100 | THD | (system) | Voltage THFF Factor | Average | - | [8 empty] | 无寄存器
Acurev4100 | THD | Input Channel 1 | Current THD | Value | 0.000 | 0 | 0 | 0 | 9958 | 0x26E6 | float32 | Input Channel 1 Current THD | 16-4 | PASS
Acurev4100 | THD | Input Channel 1 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 9960 | 0x26E8 | float32 | Input Channel 1 Current THD Odd | 16-5 | PASS
Acurev4100 | THD | Input Channel 1 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 9962 | 0x26EA | float32 | Input Channel 1 Current THD Even | 16-6 | PASS
Acurev4100 | THD | Input Channel 1 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 9964 | 0x26EC | float32 | Input Channel 1 Current K Factor | 16-7 | PASS
Acurev4100 | THD | Input Channel 2 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10026 | 0x272A | float32 | Input Channel 2 Current THD | 17-1 | PASS
Acurev4100 | THD | Input Channel 2 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10028 | 0x272C | float32 | Input Channel 2 Current THD Odd | 17-2 | PASS
Acurev4100 | THD | Input Channel 2 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10030 | 0x272E | float32 | Input Channel 2 Current THD Even | 17-3 | PASS
Acurev4100 | THD | Input Channel 2 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10032 | 0x2730 | float32 | Input Channel 2 Current K Factor | 17-4 | PASS
Acurev4100 | THD | Input Channel 3 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10094 | 0x276E | float32 | Input Channel 3 Current THD | 18-1 | PASS
Acurev4100 | THD | Input Channel 3 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10096 | 0x2770 | float32 | Input Channel 3 Current THD Odd | 18-2 | PASS
Acurev4100 | THD | Input Channel 3 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10098 | 0x2772 | float32 | Input Channel 3 Current THD Even | 18-3 | PASS
Acurev4100 | THD | Input Channel 3 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10100 | 0x2774 | float32 | Input Channel 3 Current K Factor | 18-4 | PASS
Acurev4100 | THD | Input Channel 4 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10162 | 0x27B2 | float32 | Input Channel 4 Current THD | 19-1 | PASS
Acurev4100 | THD | Input Channel 4 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10164 | 0x27B4 | float32 | Input Channel 4 Current THD Odd | 19-2 | PASS
Acurev4100 | THD | Input Channel 4 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10166 | 0x27B6 | float32 | Input Channel 4 Current THD Even | 19-3 | PASS
Acurev4100 | THD | Input Channel 4 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10168 | 0x27B8 | float32 | Input Channel 4 Current K Factor | 19-4 | PASS
Acurev4100 | THD | Input Channel 5 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10230 | 0x27F6 | float32 | Input Channel 5 Current THD | 20-1 | PASS
Acurev4100 | THD | Input Channel 5 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10232 | 0x27F8 | float32 | Input Channel 5 Current THD Odd | 20-2 | PASS
Acurev4100 | THD | Input Channel 5 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10234 | 0x27FA | float32 | Input Channel 5 Current THD Even | 20-3 | PASS
Acurev4100 | THD | Input Channel 5 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10236 | 0x27FC | float32 | Input Channel 5 Current K Factor | 20-4 | PASS
Acurev4100 | THD | Input Channel 6 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10298 | 0x283A | float32 | Input Channel 6 Current THD | 21-1 | PASS
Acurev4100 | THD | Input Channel 6 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10300 | 0x283C | float32 | Input Channel 6 Current THD Odd | 21-2 | PASS
Acurev4100 | THD | Input Channel 6 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10302 | 0x283E | float32 | Input Channel 6 Current THD Even | 21-3 | PASS
Acurev4100 | THD | Input Channel 6 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10304 | 0x2840 | float32 | Input Channel 6 Current K Factor | 21-4 | PASS
Acurev4100 | THD | Input Channel 7 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10366 | 0x287E | float32 | Input Channel 7 Current THD | 22-1 | PASS
Acurev4100 | THD | Input Channel 7 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10368 | 0x2880 | float32 | Input Channel 7 Current THD Odd | 22-2 | PASS
Acurev4100 | THD | Input Channel 7 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10370 | 0x2882 | float32 | Input Channel 7 Current THD Even | 22-3 | PASS
Acurev4100 | THD | Input Channel 7 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10372 | 0x2884 | float32 | Input Channel 7 Current K Factor | 22-4 | PASS
Acurev4100 | THD | Input Channel 8 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10434 | 0x28C2 | float32 | Input Channel 8 Current THD | 23-1 | PASS
Acurev4100 | THD | Input Channel 8 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10436 | 0x28C4 | float32 | Input Channel 8 Current THD Odd | 23-2 | PASS
Acurev4100 | THD | Input Channel 8 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10438 | 0x28C6 | float32 | Input Channel 8 Current THD Even | 23-3 | PASS
Acurev4100 | THD | Input Channel 8 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10440 | 0x28C8 | float32 | Input Channel 8 Current K Factor | 23-4 | PASS
Acurev4100 | THD | Input Channel 9 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10502 | 0x2906 | float32 | Input Channel 9 Current THD | 24-1 | PASS
Acurev4100 | THD | Input Channel 9 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10504 | 0x2908 | float32 | Input Channel 9 Current THD Odd | 24-2 | PASS
Acurev4100 | THD | Input Channel 9 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10506 | 0x290A | float32 | Input Channel 9 Current THD Even | 24-3 | PASS
Acurev4100 | THD | Input Channel 9 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10508 | 0x290C | float32 | Input Channel 9 Current K Factor | 24-4 | PASS
Acurev4100 | THD | Input Channel 10 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10570 | 0x294A | float32 | Input Channel 10 Current THD | 25-1 | PASS
Acurev4100 | THD | Input Channel 10 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10572 | 0x294C | float32 | Input Channel 10 Current THD Odd | 25-2 | PASS
Acurev4100 | THD | Input Channel 10 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10574 | 0x294E | float32 | Input Channel 10 Current THD Even | 25-3 | PASS
Acurev4100 | THD | Input Channel 10 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10576 | 0x2950 | float32 | Input Channel 10 Current K Factor | 25-4 | PASS
Acurev4100 | THD | Input Channel 11 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10638 | 0x298E | float32 | Input Channel 11 Current THD | 26-1 | PASS
Acurev4100 | THD | Input Channel 11 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10640 | 0x2990 | float32 | Input Channel 11 Current THD Odd | 26-2 | PASS
Acurev4100 | THD | Input Channel 11 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10642 | 0x2992 | float32 | Input Channel 11 Current THD Even | 26-3 | PASS
Acurev4100 | THD | Input Channel 11 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10644 | 0x2994 | float32 | Input Channel 11 Current K Factor | 26-4 | PASS
Acurev4100 | THD | Input Channel 12 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10706 | 0x29D2 | float32 | Input Channel 12 Current THD | 27-1 | PASS
Acurev4100 | THD | Input Channel 12 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10708 | 0x29D4 | float32 | Input Channel 12 Current THD Odd | 27-2 | PASS
Acurev4100 | THD | Input Channel 12 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10710 | 0x29D6 | float32 | Input Channel 12 Current THD Even | 27-3 | PASS
Acurev4100 | THD | Input Channel 12 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10712 | 0x29D8 | float32 | Input Channel 12 Current K Factor | 27-4 | PASS
Acurev4100 | THD | Input Channel 13 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10774 | 0x2A16 | float32 | Input Channel 13 Current THD | 28-1 | PASS
Acurev4100 | THD | Input Channel 13 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10776 | 0x2A18 | float32 | Input Channel 13 Current THD Odd | 28-2 | PASS
Acurev4100 | THD | Input Channel 13 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10778 | 0x2A1A | float32 | Input Channel 13 Current THD Even | 28-3 | PASS
Acurev4100 | THD | Input Channel 13 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10780 | 0x2A1C | float32 | Input Channel 13 Current K Factor | 28-4 | PASS
Acurev4100 | THD | Input Channel 14 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10842 | 0x2A5A | float32 | Input Channel 14 Current THD | 29-1 | PASS
Acurev4100 | THD | Input Channel 14 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10844 | 0x2A5C | float32 | Input Channel 14 Current THD Odd | 29-2 | PASS
Acurev4100 | THD | Input Channel 14 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10846 | 0x2A5E | float32 | Input Channel 14 Current THD Even | 29-3 | PASS
Acurev4100 | THD | Input Channel 14 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10848 | 0x2A60 | float32 | Input Channel 14 Current K Factor | 29-4 | PASS
Acurev4100 | THD | Input Channel 15 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10910 | 0x2A9E | float32 | Input Channel 15 Current THD | 30-1 | PASS
Acurev4100 | THD | Input Channel 15 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10912 | 0x2AA0 | float32 | Input Channel 15 Current THD Odd | 30-2 | PASS
Acurev4100 | THD | Input Channel 15 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10914 | 0x2AA2 | float32 | Input Channel 15 Current THD Even | 30-3 | PASS
Acurev4100 | THD | Input Channel 15 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10916 | 0x2AA4 | float32 | Input Channel 15 Current K Factor | 30-4 | PASS
Acurev4100 | THD | Input Channel 16 | Current THD | Value | 0.000 | 0 | 0 | 0 | 10978 | 0x2AE2 | float32 | Input Channel 16 Current THD | 31-1 | PASS
Acurev4100 | THD | Input Channel 16 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 10980 | 0x2AE4 | float32 | Input Channel 16 Current THD Odd | 31-2 | PASS
Acurev4100 | THD | Input Channel 16 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 10982 | 0x2AE6 | float32 | Input Channel 16 Current THD Even | 31-3 | PASS
Acurev4100 | THD | Input Channel 16 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 10984 | 0x2AE8 | float32 | Input Channel 16 Current K Factor | 31-4 | PASS
Acurev4100 | THD | Input Channel 17 | Current THD | Value | 0.000 | 0 | 0 | 0 | 11046 | 0x2B26 | float32 | Input Channel 17 Current THD | 32-1 | PASS
Acurev4100 | THD | Input Channel 17 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 11048 | 0x2B28 | float32 | Input Channel 17 Current THD Odd | 32-2 | PASS
Acurev4100 | THD | Input Channel 17 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 11050 | 0x2B2A | float32 | Input Channel 17 Current THD Even | 32-3 | PASS
Acurev4100 | THD | Input Channel 17 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 11052 | 0x2B2C | float32 | Input Channel 17 Current K Factor | 32-4 | PASS
Acurev4100 | THD | Input Channel 18 | Current THD | Value | 0.000 | 0 | 0 | 0 | 11114 | 0x2B6A | float32 | Input Channel 18 Current THD | 33-1 | PASS
Acurev4100 | THD | Input Channel 18 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 11116 | 0x2B6C | float32 | Input Channel 18 Current THD Odd | 33-2 | PASS
Acurev4100 | THD | Input Channel 18 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 11118 | 0x2B6E | float32 | Input Channel 18 Current THD Even | 33-3 | PASS
Acurev4100 | THD | Input Channel 18 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 11120 | 0x2B70 | float32 | Input Channel 18 Current K Factor | 33-4 | PASS
Acurev4100 | THD | Input Channel 19 | Current THD | Value | 0.000 | 0 | 0 | 0 | 11182 | 0x2BAE | float32 | Input Channel 19 Current THD | 34-1 | PASS
Acurev4100 | THD | Input Channel 19 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 11184 | 0x2BB0 | float32 | Input Channel 19 Current THD Odd | 34-2 | PASS
Acurev4100 | THD | Input Channel 19 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 11186 | 0x2BB2 | float32 | Input Channel 19 Current THD Even | 34-3 | PASS
Acurev4100 | THD | Input Channel 19 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 11188 | 0x2BB4 | float32 | Input Channel 19 Current K Factor | 34-4 | PASS
Acurev4100 | THD | Input Channel 20 | Current THD | Value | 0.000 | 0 | 0 | 0 | 11250 | 0x2BF2 | float32 | Input Channel 20 Current THD | 35-1 | PASS
Acurev4100 | THD | Input Channel 20 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 11252 | 0x2BF4 | float32 | Input Channel 20 Current THD Odd | 35-2 | PASS
Acurev4100 | THD | Input Channel 20 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 11254 | 0x2BF6 | float32 | Input Channel 20 Current THD Even | 35-3 | PASS
Acurev4100 | THD | Input Channel 20 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 11256 | 0x2BF8 | float32 | Input Channel 20 Current K Factor | 35-4 | PASS
Acurev4100 | THD | Input Channel 21 | Current THD | Value | 0.000 | 0 | 0 | 0 | 11318 | 0x2C36 | float32 | Input Channel 21 Current THD | 36-1 | PASS
Acurev4100 | THD | Input Channel 21 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 11320 | 0x2C38 | float32 | Input Channel 21 Current THD Odd | 36-2 | PASS
Acurev4100 | THD | Input Channel 21 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 11322 | 0x2C3A | float32 | Input Channel 21 Current THD Even | 36-3 | PASS
Acurev4100 | THD | Input Channel 21 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 11324 | 0x2C3C | float32 | Input Channel 21 Current K Factor | 36-4 | PASS
Acurev4100 | THD | Input Channel 22 | Current THD | Value | 0.000 | 0 | 0 | 0 | 11386 | 0x2C7A | float32 | Input Channel 22 Current THD | 37-1 | PASS
Acurev4100 | THD | Input Channel 22 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 11388 | 0x2C7C | float32 | Input Channel 22 Current THD Odd | 37-2 | PASS
Acurev4100 | THD | Input Channel 22 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 11390 | 0x2C7E | float32 | Input Channel 22 Current THD Even | 37-3 | PASS
Acurev4100 | THD | Input Channel 22 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 11392 | 0x2C80 | float32 | Input Channel 22 Current K Factor | 37-4 | PASS
Acurev4100 | THD | Input Channel 23 | Current THD | Value | 0.000 | 0 | 0 | 0 | 11454 | 0x2CBE | float32 | Input Channel 23 Current THD | 38-1 | PASS
Acurev4100 | THD | Input Channel 23 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 11456 | 0x2CC0 | float32 | Input Channel 23 Current THD Odd | 38-2 | PASS
Acurev4100 | THD | Input Channel 23 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 11458 | 0x2CC2 | float32 | Input Channel 23 Current THD Even | 38-3 | PASS
Acurev4100 | THD | Input Channel 23 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 11460 | 0x2CC4 | float32 | Input Channel 23 Current K Factor | 38-4 | PASS
Acurev4100 | THD | Input Channel 24 | Current THD | Value | 0.000 | 0 | 0 | 0 | 11522 | 0x2D02 | float32 | Input Channel 24 Current THD | 39-1 | PASS
Acurev4100 | THD | Input Channel 24 | Current THD Odd | Value | 0.000 | 0 | 0 | 0 | 11524 | 0x2D04 | float32 | Input Channel 24 Current THD Odd | 39-2 | PASS
Acurev4100 | THD | Input Channel 24 | Current THD Even | Value | 0.000 | 0 | 0 | 0 | 11526 | 0x2D06 | float32 | Input Channel 24 Current THD Even | 39-3 | PASS
Acurev4100 | THD | Input Channel 24 | Current K Factor | Value | 0.000 | 0 | 0 | 0 | 11528 | 0x2D08 | float32 | Input Channel 24 Current K Factor | 39-4 | PASS
Acurev4100 | Sequence | (system) | Voltage Sequence Magnitude | Positive | 0.000 | 0 | 0 | 0 | 9728 | 0x2600 | float32 | Voltage Positive Sequence Magnitude | 13-1 | PASS
Acurev4100 | Sequence | (system) | Voltage Sequence Magnitude | Zero | 0.000 | 0 | 0 | 0 | 9730 | 0x2602 | float32 | Voltage Zero Sequence Magnitude | 13-2 | PASS
Acurev4100 | Sequence | (system) | Voltage Sequence Angle | Positive | 0.000 | 0 | 0 | 0 | 9734 | 0x2606 | float32 | Voltage Positive Sequence Angle | 13-4 | PASS
Acurev4100 | Sequence | (system) | Voltage Sequence Angle | Negative | 0.035 | 0.0497 | 0.0147 | 0 | 9738 | 0x260A | float32 | Voltage Negative Sequence Angle | 13-6 | PASS
Acurev4100 | Sequence | (system) | Voltage Sequence Angle | Zero | 0.000 | 0 | 0 | 0 | 9736 | 0x2608 | float32 | Voltage Zero Sequence Angle | 13-5 | PASS
Acurev4100 | Sequence | (system) | Voltage | Unbalance Factor | 150.000% | 150 | 0 | 0 | 9740 | 0x260C | float32 | Voltage Unbalance Factor Magnitude | 13-7 | PASS
Acurev4100 | Sequence | User Channel 1:name1 | Current Sequence Magnitude | Zero | 0.000 | 0 | 0 | 0 | 11592 | 0x2D48 | float32 | User Channel 1 Current Zero Sequence Magnitude | 40-2 | PASS
Acurev4100 | Sequence | User Channel 1:name1 | Current Sequence Angle | Positive | 0.000 | 0 | 0 | 0 | 11596 | 0x2D4C | float32 | User Channel 1 Current Positive Sequence Angle | 40-4 | PASS
Acurev4100 | Sequence | User Channel 1:name1 | Current Sequence Angle | Negative | 0.000 | 0 | 0 | 0 | 11600 | 0x2D50 | float32 | User Channel 1 Current Negative Sequence Angle | 40-6 | PASS
Acurev4100 | Sequence | User Channel 1:name1 | Current Sequence Angle | Zero | 0.000 | 0 | 0 | 0 | 11598 | 0x2D4E | float32 | User Channel 1 Current Zero Sequence Angle | 40-5 | PASS
Acurev4100 | Sequence | User Channel 2:name1 | Current Sequence Angle | Positive | 0.000 | 0 | 0 | 0 | 11610 | 0x2D5A | float32 | User Channel 2 Current Positive Sequence Angle | 40-11 | PASS
Acurev4100 | Sequence | User Channel 2:name1 | Current Sequence Angle | Negative | 0.000 | 0 | 0 | 0 | 11614 | 0x2D5E | float32 | User Channel 2 Current Negative Sequence Angle | 40-13 | PASS
Acurev4100 | Sequence | User Channel 2:name1 | Current Sequence Angle | Zero | 0.000 | 0 | 0 | 0 | 11612 | 0x2D5C | float32 | User Channel 2 Current Zero Sequence Angle | 40-12 | PASS
Acurev4100 | Sequence | User Channel 3:name2 | Current Sequence Magnitude | Positive | 0.000 | 0 | 0 | 0 | 11618 | 0x2D62 | float32 | User Channel 3 Current Positive Sequence Magnitude | 40-15 | PASS
Acurev4100 | Sequence | User Channel 3:name2 | Current Sequence Magnitude | Negative | 0.000 | 0 | 0 | 0 | 11622 | 0x2D66 | float32 | User Channel 3 Current Negative Sequence Magnitude | 40-17 | PASS
Acurev4100 | Sequence | User Channel 3:name2 | Current Sequence Magnitude | Zero | 0.000 | 0 | 0 | 0 | 11620 | 0x2D64 | float32 | User Channel 3 Current Zero Sequence Magnitude | 40-16 | PASS
Acurev4100 | Sequence | User Channel 3:name2 | Current Sequence Angle | Positive | 0.000 | 0 | 0 | 0 | 11624 | 0x2D68 | float32 | User Channel 3 Current Positive Sequence Angle | 40-18 | PASS
Acurev4100 | Sequence | User Channel 3:name2 | Current Sequence Angle | Negative | 0.000 | 0 | 0 | 0 | 11628 | 0x2D6C | float32 | User Channel 3 Current Negative Sequence Angle | 40-20 | PASS
Acurev4100 | Sequence | User Channel 3:name2 | Current Sequence Angle | Zero | 0.000 | 0 | 0 | 0 | 11626 | 0x2D6A | float32 | User Channel 3 Current Zero Sequence Angle | 40-19 | PASS
Acurev4100 | Sequence | User Channel 3:name2 | Current | Unbalance Factor | 0.000% | 0 | 0 | 0 | 11630 | 0x2D6E | float32 | User Channel 3 Current Unbalance Factor Magnitude | 40-21 | PASS
Acurev4100 | Sequence | User Channel 4:name2 | Current Sequence Magnitude | Positive | 0.000 | 0 | 0 | 0 | 11632 | 0x2D70 | float32 | User Channel 4 Current Positive Sequence Magnitude | 40-22 | PASS
Acurev4100 | Sequence | User Channel 4:name2 | Current Sequence Magnitude | Negative | 0.000 | 0 | 0 | 0 | 11636 | 0x2D74 | float32 | User Channel 4 Current Negative Sequence Magnitude | 40-24 | PASS
Acurev4100 | Sequence | User Channel 4:name2 | Current Sequence Magnitude | Zero | 0.000 | 0 | 0 | 0 | 11634 | 0x2D72 | float32 | User Channel 4 Current Zero Sequence Magnitude | 40-23 | PASS
Acurev4100 | Sequence | User Channel 4:name2 | Current Sequence Angle | Positive | 0.000 | 0 | 0 | 0 | 11638 | 0x2D76 | float32 | User Channel 4 Current Positive Sequence Angle | 40-25 | PASS
Acurev4100 | Sequence | User Channel 4:name2 | Current Sequence Angle | Negative | 0.000 | 0 | 0 | 0 | 11642 | 0x2D7A | float32 | User Channel 4 Current Negative Sequence Angle | 40-27 | PASS
Acurev4100 | Sequence | User Channel 4:name2 | Current Sequence Angle | Zero | 0.000 | 0 | 0 | 0 | 11640 | 0x2D78 | float32 | User Channel 4 Current Zero Sequence Angle | 40-26 | PASS
Acurev4100 | Sequence | User Channel 4:name2 | Current | Unbalance Factor | 0.000% | 0 | 0 | 0 | 11644 | 0x2D7C | float32 | User Channel 4 Current Unbalance Factor Magnitude | 40-28 | PASS
Acurev4100 | Sequence | User Channel 5:name5 | Current Sequence Magnitude | Positive | 0.000 | 0 | 0 | 0 | 11646 | 0x2D7E | float32 | User Channel 5 Current Positive Sequence Magnitude | 40-29 | PASS
Acurev4100 | Sequence | User Channel 5:name5 | Current Sequence Magnitude | Negative | 0.000 | 0 | 0 | 0 | 11650 | 0x2D82 | float32 | User Channel 5 Current Negative Sequence Magnitude | 40-31 | PASS
Acurev4100 | Sequence | User Channel 5:name5 | Current Sequence Magnitude | Zero | 0.000 | 0 | 0 | 0 | 11648 | 0x2D80 | float32 | User Channel 5 Current Zero Sequence Magnitude | 40-30 | PASS
Acurev4100 | Sequence | User Channel 5:name5 | Current Sequence Angle | Positive | 0.000 | 0 | 0 | 0 | 11652 | 0x2D84 | float32 | User Channel 5 Current Positive Sequence Angle | 40-32 | PASS
Acurev4100 | Sequence | User Channel 5:name5 | Current Sequence Angle | Negative | 0.000 | 0 | 0 | 0 | 11656 | 0x2D88 | float32 | User Channel 5 Current Negative Sequence Angle | 40-34 | PASS
Acurev4100 | Sequence | User Channel 5:name5 | Current Sequence Angle | Zero | 0.000 | 0 | 0 | 0 | 11654 | 0x2D86 | float32 | User Channel 5 Current Zero Sequence Angle | 40-33 | PASS
Acurev4100 | Sequence | User Channel 5:name5 | Current | Unbalance Factor | 0.000% | 0 | 0 | 0 | 11658 | 0x2D8A | float32 | User Channel 5 Current Unbalance Factor Magnitude | 40-35 | PASS
Acurev4100 | Sequence | User Channel 6:6666 | Current Sequence Magnitude | Positive | 0.000 | 0 | 0 | 0 | 11660 | 0x2D8C | float32 | User Channel 6 Current Positive Sequence Magnitude | 40-36 | PASS
Acurev4100 | Sequence | User Channel 6:6666 | Current Sequence Magnitude | Negative | 0.000 | 0 | 0 | 0 | 11664 | 0x2D90 | float32 | User Channel 6 Current Negative Sequence Magnitude | 40-38 | PASS
Acurev4100 | Sequence | User Channel 6:6666 | Current Sequence Angle | Positive | 0.000 | 0 | 0 | 0 | 11666 | 0x2D92 | float32 | User Channel 6 Current Positive Sequence Angle | 40-39 | PASS
Acurev4100 | Sequence | User Channel 6:6666 | Current Sequence Angle | Negative | 0.000 | 0 | 0 | 0 | 11670 | 0x2D96 | float32 | User Channel 6 Current Negative Sequence Angle | 40-41 | PASS
Acurev4100 | Sequence | User Channel 6:6666 | Current Sequence Angle | Zero | 0.000 | 0 | 0 | 0 | 11668 | 0x2D94 | float32 | User Channel 6 Current Zero Sequence Angle | 40-40 | PASS
Acurev4100 | Sequence | User Channel 6:6666 | Current | Unbalance Factor | 0.000% | 0 | 0 | 0 | 11672 | 0x2D98 | float32 | User Channel 6 Current Unbalance Factor Magnitude | 40-42 | PASS
Acurev4100 | Sequence | User Channel 7:7777 | Current Sequence Magnitude | Positive | 0.000 | 0 | 0 | 0 | 11674 | 0x2D9A | float32 | User Channel 7 Current Positive Sequence Magnitude | 41-1 | PASS
Acurev4100 | Sequence | User Channel 7:7777 | Current Sequence Magnitude | Negative | 0.000 | 0 | 0 | 0 | 11678 | 0x2D9E | float32 | User Channel 7 Current Negative Sequence Magnitude | 41-3 | PASS
Acurev4100 | Sequence | User Channel 7:7777 | Current Sequence Magnitude | Zero | 0.000 | 0 | 0 | 0 | 11676 | 0x2D9C | float32 | User Channel 7 Current Zero Sequence Magnitude | 41-2 | PASS
Acurev4100 | Sequence | User Channel 7:7777 | Current Sequence Angle | Positive | 0.000 | 0 | 0 | 0 | 11680 | 0x2DA0 | float32 | User Channel 7 Current Positive Sequence Angle | 41-4 | PASS
Acurev4100 | Sequence | User Channel 7:7777 | Current Sequence Angle | Negative | 0.000 | 0 | 0 | 0 | 11684 | 0x2DA4 | float32 | User Channel 7 Current Negative Sequence Angle | 41-6 | PASS
Acurev4100 | Sequence | User Channel 7:7777 | Current Sequence Angle | Zero | 0.000 | 0 | 0 | 0 | 11682 | 0x2DA2 | float32 | User Channel 7 Current Zero Sequence Angle | 41-5 | PASS
Acurev4100 | Sequence | User Channel 7:7777 | Current | Unbalance Factor | 0.000% | 0 | 0 | 0 | 11686 | 0x2DA6 | float32 | User Channel 7 Current Unbalance Factor Magnitude | 41-7 | PASS
Acurev4100 | Sequence | User Channel 8:9999 | Current Sequence Magnitude | Positive | 0.000 | 0 | 0 | 0 | 11688 | 0x2DA8 | float32 | User Channel 8 Current Positive Sequence Magnitude | 41-8 | PASS
Acurev4100 | Sequence | User Channel 8:9999 | Current Sequence Magnitude | Negative | 0.000 | 0 | 0 | 0 | 11692 | 0x2DAC | float32 | User Channel 8 Current Negative Sequence Magnitude | 41-10 | PASS
Acurev4100 | Sequence | User Channel 8:9999 | Current Sequence Magnitude | Zero | 0.000 | 0 | 0 | 0 | 11690 | 0x2DAA | float32 | User Channel 8 Current Zero Sequence Magnitude | 41-9 | PASS
Acurev4100 | Sequence | User Channel 8:9999 | Current Sequence Angle | Positive | 0.000 | 0 | 0 | 0 | 11694 | 0x2DAE | float32 | User Channel 8 Current Positive Sequence Angle | 41-11 | PASS
Acurev4100 | Sequence | User Channel 8:9999 | Current Sequence Angle | Negative | 0.000 | 0 | 0 | 0 | 11698 | 0x2DB2 | float32 | User Channel 8 Current Negative Sequence Angle | 41-13 | PASS
Acurev4100 | Sequence | User Channel 8:9999 | Current Sequence Angle | Zero | 0.000 | 0 | 0 | 0 | 11696 | 0x2DB0 | float32 | User Channel 8 Current Zero Sequence Angle | 41-12 | PASS
Acurev4100 | Sequence | User Channel 8:9999 | Current | Unbalance Factor | 0.000% | 0 | 0 | 0 | 11700 | 0x2DB4 | float32 | User Channel 8 Current Unbalance Factor Magnitude | 41-14 | PASS
Acurev4100 | Harmonics | (system) | 6 | Phase A | 0.001 | 0.001 | 0 | 0 | 9760 | 0x2620 | float32 | Phase A Voltage individual Harmonics 6 percentage | 13-17 | PASS
Acurev4100 | Harmonics | (system) | 6 | Phase C | 0.001 | 0.001 | 0 | 0 | 9900 | 0x26AC | float32 | Phase C Voltage individual Harmonics 6 percentage | 15-10 | PASS
Acurev4100 | Harmonics | (system) | 7 | Phase C | 0.004 | 0.004 | 0 | 0 | 9902 | 0x26AE | float32 | Phase C Voltage individual Harmonics 7 percentage | 15-11 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 2 | value | 0.000 | 0 | 0 | 0 | 9966 | 0x26EE | float32 | Input Channel 1 Current individual Harmonics 2 percentage | 16-8 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 3 | value | 0.000 | 0 | 0 | 0 | 9968 | 0x26F0 | float32 | Input Channel 1 Current individual Harmonics 3 percentage | 16-9 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 4 | value | 0.000 | 0 | 0 | 0 | 9970 | 0x26F2 | float32 | Input Channel 1 Current individual Harmonics 4 percentage | 16-10 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 5 | value | 0.000 | 0 | 0 | 0 | 9972 | 0x26F4 | float32 | Input Channel 1 Current individual Harmonics 5 percentage | 16-11 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 6 | value | 0.000 | 0 | 0 | 0 | 9974 | 0x26F6 | float32 | Input Channel 1 Current individual Harmonics 6 percentage | 16-12 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 7 | value | 0.000 | 0 | 0 | 0 | 9976 | 0x26F8 | float32 | Input Channel 1 Current individual Harmonics 7 percentage | 16-13 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 8 | value | 0.000 | 0 | 0 | 0 | 9978 | 0x26FA | float32 | Input Channel 1 Current individual Harmonics 8 percentage | 16-14 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 9 | value | 0.000 | 0 | 0 | 0 | 9980 | 0x26FC | float32 | Input Channel 1 Current individual Harmonics 9 percentage | 16-15 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 10 | value | 0.000 | 0 | 0 | 0 | 9982 | 0x26FE | float32 | Input Channel 1 Current individual Harmonics 10 percentage | 16-16 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 11 | value | 0.000 | 0 | 0 | 0 | 9984 | 0x2700 | float32 | Input Channel 1 Current individual Harmonics 11 percentage | 16-17 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 12 | value | 0.000 | 0 | 0 | 0 | 9986 | 0x2702 | float32 | Input Channel 1 Current individual Harmonics 12 percentage | 16-18 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 13 | value | 0.000 | 0 | 0 | 0 | 9988 | 0x2704 | float32 | Input Channel 1 Current individual Harmonics 13 percentage | 16-19 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 14 | value | 0.000 | 0 | 0 | 0 | 9990 | 0x2706 | float32 | Input Channel 1 Current individual Harmonics 14 percentage | 16-20 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 15 | value | 0.000 | 0 | 0 | 0 | 9992 | 0x2708 | float32 | Input Channel 1 Current individual Harmonics 15 percentage | 16-21 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 16 | value | 0.000 | 0 | 0 | 0 | 9994 | 0x270A | float32 | Input Channel 1 Current individual Harmonics 16 percentage | 16-22 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 17 | value | 0.000 | 0 | 0 | 0 | 9996 | 0x270C | float32 | Input Channel 1 Current individual Harmonics 17 percentage | 16-23 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 18 | value | 0.000 | 0 | 0 | 0 | 9998 | 0x270E | float32 | Input Channel 1 Current individual Harmonics 18 percentage | 16-24 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 19 | value | 0.000 | 0 | 0 | 0 | 10000 | 0x2710 | float32 | Input Channel 1 Current individual Harmonics 19 percentage | 16-25 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 20 | value | 0.000 | 0 | 0 | 0 | 10002 | 0x2712 | float32 | Input Channel 1 Current individual Harmonics 20 percentage | 16-26 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 21 | value | 0.000 | 0 | 0 | 0 | 10004 | 0x2714 | float32 | Input Channel 1 Current individual Harmonics 21 percentage | 16-27 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 22 | value | 0.000 | 0 | 0 | 0 | 10006 | 0x2716 | float32 | Input Channel 1 Current individual Harmonics 22 percentage | 16-28 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 23 | value | 0.000 | 0 | 0 | 0 | 10008 | 0x2718 | float32 | Input Channel 1 Current individual Harmonics 23 percentage | 16-29 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 24 | value | 0.000 | 0 | 0 | 0 | 10010 | 0x271A | float32 | Input Channel 1 Current individual Harmonics 24 percentage | 16-30 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 25 | value | 0.000 | 0 | 0 | 0 | 10012 | 0x271C | float32 | Input Channel 1 Current individual Harmonics 25 percentage | 16-31 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 26 | value | 0.000 | 0 | 0 | 0 | 10014 | 0x271E | float32 | Input Channel 1 Current individual Harmonics 26 percentage | 16-32 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 27 | value | 0.000 | 0 | 0 | 0 | 10016 | 0x2720 | float32 | Input Channel 1 Current individual Harmonics 27 percentage | 16-33 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 28 | value | 0.000 | 0 | 0 | 0 | 10018 | 0x2722 | float32 | Input Channel 1 Current individual Harmonics 28 percentage | 16-34 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 29 | value | 0.000 | 0 | 0 | 0 | 10020 | 0x2724 | float32 | Input Channel 1 Current individual Harmonics 29 percentage | 16-35 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 30 | value | 0.000 | 0 | 0 | 0 | 10022 | 0x2726 | float32 | Input Channel 1 Current individual Harmonics 30 percentage | 16-36 | PASS
Acurev4100 | Harmonics | Input Channel 1 | 31 | value | 0.000 | 0 | 0 | 0 | 10024 | 0x2728 | float32 | Input Channel 1 Current individual Harmonics 31 percentage | 16-37 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 2 | value | 0.000 | 0 | 0 | 0 | 10034 | 0x2732 | float32 | Input Channel 2 Current individual Harmonics 2 percentage | 17-5 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 3 | value | 0.000 | 0 | 0 | 0 | 10036 | 0x2734 | float32 | Input Channel 2 Current individual Harmonics 3 percentage | 17-6 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 4 | value | 0.000 | 0 | 0 | 0 | 10038 | 0x2736 | float32 | Input Channel 2 Current individual Harmonics 4 percentage | 17-7 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 5 | value | 0.000 | 0 | 0 | 0 | 10040 | 0x2738 | float32 | Input Channel 2 Current individual Harmonics 5 percentage | 17-8 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 6 | value | 0.000 | 0 | 0 | 0 | 10042 | 0x273A | float32 | Input Channel 2 Current individual Harmonics 6 percentage | 17-9 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 7 | value | 0.000 | 0 | 0 | 0 | 10044 | 0x273C | float32 | Input Channel 2 Current individual Harmonics 7 percentage | 17-10 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 8 | value | 0.000 | 0 | 0 | 0 | 10046 | 0x273E | float32 | Input Channel 2 Current individual Harmonics 8 percentage | 17-11 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 9 | value | 0.000 | 0 | 0 | 0 | 10048 | 0x2740 | float32 | Input Channel 2 Current individual Harmonics 9 percentage | 17-12 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 10 | value | 0.000 | 0 | 0 | 0 | 10050 | 0x2742 | float32 | Input Channel 2 Current individual Harmonics 10 percentage | 17-13 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 11 | value | 0.000 | 0 | 0 | 0 | 10052 | 0x2744 | float32 | Input Channel 2 Current individual Harmonics 11 percentage | 17-14 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 12 | value | 0.000 | 0 | 0 | 0 | 10054 | 0x2746 | float32 | Input Channel 2 Current individual Harmonics 12 percentage | 17-15 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 13 | value | 0.000 | 0 | 0 | 0 | 10056 | 0x2748 | float32 | Input Channel 2 Current individual Harmonics 13 percentage | 17-16 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 14 | value | 0.000 | 0 | 0 | 0 | 10058 | 0x274A | float32 | Input Channel 2 Current individual Harmonics 14 percentage | 17-17 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 15 | value | 0.000 | 0 | 0 | 0 | 10060 | 0x274C | float32 | Input Channel 2 Current individual Harmonics 15 percentage | 17-18 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 16 | value | 0.000 | 0 | 0 | 0 | 10062 | 0x274E | float32 | Input Channel 2 Current individual Harmonics 16 percentage | 17-19 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 17 | value | 0.000 | 0 | 0 | 0 | 10064 | 0x2750 | float32 | Input Channel 2 Current individual Harmonics 17 percentage | 17-20 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 18 | value | 0.000 | 0 | 0 | 0 | 10066 | 0x2752 | float32 | Input Channel 2 Current individual Harmonics 18 percentage | 17-21 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 19 | value | 0.000 | 0 | 0 | 0 | 10068 | 0x2754 | float32 | Input Channel 2 Current individual Harmonics 19 percentage | 17-22 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 20 | value | 0.000 | 0 | 0 | 0 | 10070 | 0x2756 | float32 | Input Channel 2 Current individual Harmonics 20 percentage | 17-23 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 21 | value | 0.000 | 0 | 0 | 0 | 10072 | 0x2758 | float32 | Input Channel 2 Current individual Harmonics 21 percentage | 17-24 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 22 | value | 0.000 | 0 | 0 | 0 | 10074 | 0x275A | float32 | Input Channel 2 Current individual Harmonics 22 percentage | 17-25 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 23 | value | 0.000 | 0 | 0 | 0 | 10076 | 0x275C | float32 | Input Channel 2 Current individual Harmonics 23 percentage | 17-26 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 24 | value | 0.000 | 0 | 0 | 0 | 10078 | 0x275E | float32 | Input Channel 2 Current individual Harmonics 24 percentage | 17-27 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 25 | value | 0.000 | 0 | 0 | 0 | 10080 | 0x2760 | float32 | Input Channel 2 Current individual Harmonics 25 percentage | 17-28 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 26 | value | 0.000 | 0 | 0 | 0 | 10082 | 0x2762 | float32 | Input Channel 2 Current individual Harmonics 26 percentage | 17-29 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 27 | value | 0.000 | 0 | 0 | 0 | 10084 | 0x2764 | float32 | Input Channel 2 Current individual Harmonics 27 percentage | 17-30 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 28 | value | 0.000 | 0 | 0 | 0 | 10086 | 0x2766 | float32 | Input Channel 2 Current individual Harmonics 28 percentage | 17-31 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 29 | value | 0.000 | 0 | 0 | 0 | 10088 | 0x2768 | float32 | Input Channel 2 Current individual Harmonics 29 percentage | 17-32 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 30 | value | 0.000 | 0 | 0 | 0 | 10090 | 0x276A | float32 | Input Channel 2 Current individual Harmonics 30 percentage | 17-33 | PASS
Acurev4100 | Harmonics | Input Channel 2 | 31 | value | 0.000 | 0 | 0 | 0 | 10092 | 0x276C | float32 | Input Channel 2 Current individual Harmonics 31 percentage | 17-34 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 2 | value | 0.000 | 0 | 0 | 0 | 10102 | 0x2776 | float32 | Input Channel 3 Current individual Harmonics 2 percentage | 18-5 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 3 | value | 0.000 | 0 | 0 | 0 | 10104 | 0x2778 | float32 | Input Channel 3 Current individual Harmonics 3 percentage | 18-6 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 4 | value | 0.000 | 0 | 0 | 0 | 10106 | 0x277A | float32 | Input Channel 3 Current individual Harmonics 4 percentage | 18-7 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 5 | value | 0.000 | 0 | 0 | 0 | 10108 | 0x277C | float32 | Input Channel 3 Current individual Harmonics 5 percentage | 18-8 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 6 | value | 0.000 | 0 | 0 | 0 | 10110 | 0x277E | float32 | Input Channel 3 Current individual Harmonics 6 percentage | 18-9 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 7 | value | 0.000 | 0 | 0 | 0 | 10112 | 0x2780 | float32 | Input Channel 3 Current individual Harmonics 7 percentage | 18-10 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 8 | value | 0.000 | 0 | 0 | 0 | 10114 | 0x2782 | float32 | Input Channel 3 Current individual Harmonics 8 percentage | 18-11 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 9 | value | 0.000 | 0 | 0 | 0 | 10116 | 0x2784 | float32 | Input Channel 3 Current individual Harmonics 9 percentage | 18-12 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 10 | value | 0.000 | 0 | 0 | 0 | 10118 | 0x2786 | float32 | Input Channel 3 Current individual Harmonics 10 percentage | 18-13 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 11 | value | 0.000 | 0 | 0 | 0 | 10120 | 0x2788 | float32 | Input Channel 3 Current individual Harmonics 11 percentage | 18-14 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 12 | value | 0.000 | 0 | 0 | 0 | 10122 | 0x278A | float32 | Input Channel 3 Current individual Harmonics 12 percentage | 18-15 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 13 | value | 0.000 | 0 | 0 | 0 | 10124 | 0x278C | float32 | Input Channel 3 Current individual Harmonics 13 percentage | 18-16 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 14 | value | 0.000 | 0 | 0 | 0 | 10126 | 0x278E | float32 | Input Channel 3 Current individual Harmonics 14 percentage | 18-17 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 15 | value | 0.000 | 0 | 0 | 0 | 10128 | 0x2790 | float32 | Input Channel 3 Current individual Harmonics 15 percentage | 18-18 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 16 | value | 0.000 | 0 | 0 | 0 | 10130 | 0x2792 | float32 | Input Channel 3 Current individual Harmonics 16 percentage | 18-19 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 17 | value | 0.000 | 0 | 0 | 0 | 10132 | 0x2794 | float32 | Input Channel 3 Current individual Harmonics 17 percentage | 18-20 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 18 | value | 0.000 | 0 | 0 | 0 | 10134 | 0x2796 | float32 | Input Channel 3 Current individual Harmonics 18 percentage | 18-21 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 19 | value | 0.000 | 0 | 0 | 0 | 10136 | 0x2798 | float32 | Input Channel 3 Current individual Harmonics 19 percentage | 18-22 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 20 | value | 0.000 | 0 | 0 | 0 | 10138 | 0x279A | float32 | Input Channel 3 Current individual Harmonics 20 percentage | 18-23 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 21 | value | 0.000 | 0 | 0 | 0 | 10140 | 0x279C | float32 | Input Channel 3 Current individual Harmonics 21 percentage | 18-24 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 22 | value | 0.000 | 0 | 0 | 0 | 10142 | 0x279E | float32 | Input Channel 3 Current individual Harmonics 22 percentage | 18-25 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 23 | value | 0.000 | 0 | 0 | 0 | 10144 | 0x27A0 | float32 | Input Channel 3 Current individual Harmonics 23 percentage | 18-26 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 24 | value | 0.000 | 0 | 0 | 0 | 10146 | 0x27A2 | float32 | Input Channel 3 Current individual Harmonics 24 percentage | 18-27 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 25 | value | 0.000 | 0 | 0 | 0 | 10148 | 0x27A4 | float32 | Input Channel 3 Current individual Harmonics 25 percentage | 18-28 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 26 | value | 0.000 | 0 | 0 | 0 | 10150 | 0x27A6 | float32 | Input Channel 3 Current individual Harmonics 26 percentage | 18-29 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 27 | value | 0.000 | 0 | 0 | 0 | 10152 | 0x27A8 | float32 | Input Channel 3 Current individual Harmonics 27 percentage | 18-30 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 28 | value | 0.000 | 0 | 0 | 0 | 10154 | 0x27AA | float32 | Input Channel 3 Current individual Harmonics 28 percentage | 18-31 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 29 | value | 0.000 | 0 | 0 | 0 | 10156 | 0x27AC | float32 | Input Channel 3 Current individual Harmonics 29 percentage | 18-32 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 30 | value | 0.000 | 0 | 0 | 0 | 10158 | 0x27AE | float32 | Input Channel 3 Current individual Harmonics 30 percentage | 18-33 | PASS
Acurev4100 | Harmonics | Input Channel 3 | 31 | value | 0.000 | 0 | 0 | 0 | 10160 | 0x27B0 | float32 | Input Channel 3 Current individual Harmonics 31 percentage | 18-34 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 2 | value | 0.000 | 0 | 0 | 0 | 10170 | 0x27BA | float32 | Input Channel 4 Current individual Harmonics 2 percentage | 19-5 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 3 | value | 0.000 | 0 | 0 | 0 | 10172 | 0x27BC | float32 | Input Channel 4 Current individual Harmonics 3 percentage | 19-6 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 4 | value | 0.000 | 0 | 0 | 0 | 10174 | 0x27BE | float32 | Input Channel 4 Current individual Harmonics 4 percentage | 19-7 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 5 | value | 0.000 | 0 | 0 | 0 | 10176 | 0x27C0 | float32 | Input Channel 4 Current individual Harmonics 5 percentage | 19-8 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 6 | value | 0.000 | 0 | 0 | 0 | 10178 | 0x27C2 | float32 | Input Channel 4 Current individual Harmonics 6 percentage | 19-9 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 7 | value | 0.000 | 0 | 0 | 0 | 10180 | 0x27C4 | float32 | Input Channel 4 Current individual Harmonics 7 percentage | 19-10 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 8 | value | 0.000 | 0 | 0 | 0 | 10182 | 0x27C6 | float32 | Input Channel 4 Current individual Harmonics 8 percentage | 19-11 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 9 | value | 0.000 | 0 | 0 | 0 | 10184 | 0x27C8 | float32 | Input Channel 4 Current individual Harmonics 9 percentage | 19-12 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 10 | value | 0.000 | 0 | 0 | 0 | 10186 | 0x27CA | float32 | Input Channel 4 Current individual Harmonics 10 percentage | 19-13 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 11 | value | 0.000 | 0 | 0 | 0 | 10188 | 0x27CC | float32 | Input Channel 4 Current individual Harmonics 11 percentage | 19-14 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 12 | value | 0.000 | 0 | 0 | 0 | 10190 | 0x27CE | float32 | Input Channel 4 Current individual Harmonics 12 percentage | 19-15 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 13 | value | 0.000 | 0 | 0 | 0 | 10192 | 0x27D0 | float32 | Input Channel 4 Current individual Harmonics 13 percentage | 19-16 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 14 | value | 0.000 | 0 | 0 | 0 | 10194 | 0x27D2 | float32 | Input Channel 4 Current individual Harmonics 14 percentage | 19-17 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 15 | value | 0.000 | 0 | 0 | 0 | 10196 | 0x27D4 | float32 | Input Channel 4 Current individual Harmonics 15 percentage | 19-18 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 16 | value | 0.000 | 0 | 0 | 0 | 10198 | 0x27D6 | float32 | Input Channel 4 Current individual Harmonics 16 percentage | 19-19 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 17 | value | 0.000 | 0 | 0 | 0 | 10200 | 0x27D8 | float32 | Input Channel 4 Current individual Harmonics 17 percentage | 19-20 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 18 | value | 0.000 | 0 | 0 | 0 | 10202 | 0x27DA | float32 | Input Channel 4 Current individual Harmonics 18 percentage | 19-21 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 19 | value | 0.000 | 0 | 0 | 0 | 10204 | 0x27DC | float32 | Input Channel 4 Current individual Harmonics 19 percentage | 19-22 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 20 | value | 0.000 | 0 | 0 | 0 | 10206 | 0x27DE | float32 | Input Channel 4 Current individual Harmonics 20 percentage | 19-23 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 21 | value | 0.000 | 0 | 0 | 0 | 10208 | 0x27E0 | float32 | Input Channel 4 Current individual Harmonics 21 percentage | 19-24 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 22 | value | 0.000 | 0 | 0 | 0 | 10210 | 0x27E2 | float32 | Input Channel 4 Current individual Harmonics 22 percentage | 19-25 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 23 | value | 0.000 | 0 | 0 | 0 | 10212 | 0x27E4 | float32 | Input Channel 4 Current individual Harmonics 23 percentage | 19-26 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 24 | value | 0.000 | 0 | 0 | 0 | 10214 | 0x27E6 | float32 | Input Channel 4 Current individual Harmonics 24 percentage | 19-27 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 25 | value | 0.000 | 0 | 0 | 0 | 10216 | 0x27E8 | float32 | Input Channel 4 Current individual Harmonics 25 percentage | 19-28 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 26 | value | 0.000 | 0 | 0 | 0 | 10218 | 0x27EA | float32 | Input Channel 4 Current individual Harmonics 26 percentage | 19-29 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 27 | value | 0.000 | 0 | 0 | 0 | 10220 | 0x27EC | float32 | Input Channel 4 Current individual Harmonics 27 percentage | 19-30 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 28 | value | 0.000 | 0 | 0 | 0 | 10222 | 0x27EE | float32 | Input Channel 4 Current individual Harmonics 28 percentage | 19-31 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 29 | value | 0.000 | 0 | 0 | 0 | 10224 | 0x27F0 | float32 | Input Channel 4 Current individual Harmonics 29 percentage | 19-32 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 30 | value | 0.000 | 0 | 0 | 0 | 10226 | 0x27F2 | float32 | Input Channel 4 Current individual Harmonics 30 percentage | 19-33 | PASS
Acurev4100 | Harmonics | Input Channel 4 | 31 | value | 0.000 | 0 | 0 | 0 | 10228 | 0x27F4 | float32 | Input Channel 4 Current individual Harmonics 31 percentage | 19-34 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 2 | value | 0.000 | 0 | 0 | 0 | 10238 | 0x27FE | float32 | Input Channel 5 Current individual Harmonics 2 percentage | 20-5 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 3 | value | 0.000 | 0 | 0 | 0 | 10240 | 0x2800 | float32 | Input Channel 5 Current individual Harmonics 3 percentage | 20-6 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 4 | value | 0.000 | 0 | 0 | 0 | 10242 | 0x2802 | float32 | Input Channel 5 Current individual Harmonics 4 percentage | 20-7 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 5 | value | 0.000 | 0 | 0 | 0 | 10244 | 0x2804 | float32 | Input Channel 5 Current individual Harmonics 5 percentage | 20-8 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 6 | value | 0.000 | 0 | 0 | 0 | 10246 | 0x2806 | float32 | Input Channel 5 Current individual Harmonics 6 percentage | 20-9 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 7 | value | 0.000 | 0 | 0 | 0 | 10248 | 0x2808 | float32 | Input Channel 5 Current individual Harmonics 7 percentage | 20-10 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 8 | value | 0.000 | 0 | 0 | 0 | 10250 | 0x280A | float32 | Input Channel 5 Current individual Harmonics 8 percentage | 20-11 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 9 | value | 0.000 | 0 | 0 | 0 | 10252 | 0x280C | float32 | Input Channel 5 Current individual Harmonics 9 percentage | 20-12 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 10 | value | 0.000 | 0 | 0 | 0 | 10254 | 0x280E | float32 | Input Channel 5 Current individual Harmonics 10 percentage | 20-13 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 11 | value | 0.000 | 0 | 0 | 0 | 10256 | 0x2810 | float32 | Input Channel 5 Current individual Harmonics 11 percentage | 20-14 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 12 | value | 0.000 | 0 | 0 | 0 | 10258 | 0x2812 | float32 | Input Channel 5 Current individual Harmonics 12 percentage | 20-15 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 13 | value | 0.000 | 0 | 0 | 0 | 10260 | 0x2814 | float32 | Input Channel 5 Current individual Harmonics 13 percentage | 20-16 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 14 | value | 0.000 | 0 | 0 | 0 | 10262 | 0x2816 | float32 | Input Channel 5 Current individual Harmonics 14 percentage | 20-17 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 15 | value | 0.000 | 0 | 0 | 0 | 10264 | 0x2818 | float32 | Input Channel 5 Current individual Harmonics 15 percentage | 20-18 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 16 | value | 0.000 | 0 | 0 | 0 | 10266 | 0x281A | float32 | Input Channel 5 Current individual Harmonics 16 percentage | 20-19 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 17 | value | 0.000 | 0 | 0 | 0 | 10268 | 0x281C | float32 | Input Channel 5 Current individual Harmonics 17 percentage | 20-20 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 18 | value | 0.000 | 0 | 0 | 0 | 10270 | 0x281E | float32 | Input Channel 5 Current individual Harmonics 18 percentage | 20-21 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 19 | value | 0.000 | 0 | 0 | 0 | 10272 | 0x2820 | float32 | Input Channel 5 Current individual Harmonics 19 percentage | 20-22 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 20 | value | 0.000 | 0 | 0 | 0 | 10274 | 0x2822 | float32 | Input Channel 5 Current individual Harmonics 20 percentage | 20-23 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 21 | value | 0.000 | 0 | 0 | 0 | 10276 | 0x2824 | float32 | Input Channel 5 Current individual Harmonics 21 percentage | 20-24 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 22 | value | 0.000 | 0 | 0 | 0 | 10278 | 0x2826 | float32 | Input Channel 5 Current individual Harmonics 22 percentage | 20-25 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 23 | value | 0.000 | 0 | 0 | 0 | 10280 | 0x2828 | float32 | Input Channel 5 Current individual Harmonics 23 percentage | 20-26 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 24 | value | 0.000 | 0 | 0 | 0 | 10282 | 0x282A | float32 | Input Channel 5 Current individual Harmonics 24 percentage | 20-27 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 25 | value | 0.000 | 0 | 0 | 0 | 10284 | 0x282C | float32 | Input Channel 5 Current individual Harmonics 25 percentage | 20-28 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 26 | value | 0.000 | 0 | 0 | 0 | 10286 | 0x282E | float32 | Input Channel 5 Current individual Harmonics 26 percentage | 20-29 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 27 | value | 0.000 | 0 | 0 | 0 | 10288 | 0x2830 | float32 | Input Channel 5 Current individual Harmonics 27 percentage | 20-30 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 28 | value | 0.000 | 0 | 0 | 0 | 10290 | 0x2832 | float32 | Input Channel 5 Current individual Harmonics 28 percentage | 20-31 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 29 | value | 0.000 | 0 | 0 | 0 | 10292 | 0x2834 | float32 | Input Channel 5 Current individual Harmonics 29 percentage | 20-32 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 30 | value | 0.000 | 0 | 0 | 0 | 10294 | 0x2836 | float32 | Input Channel 5 Current individual Harmonics 30 percentage | 20-33 | PASS
Acurev4100 | Harmonics | Input Channel 5 | 31 | value | 0.000 | 0 | 0 | 0 | 10296 | 0x2838 | float32 | Input Channel 5 Current individual Harmonics 31 percentage | 20-34 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 2 | value | 0.000 | 0 | 0 | 0 | 10306 | 0x2842 | float32 | Input Channel 6 Current individual Harmonics 2 percentage | 21-5 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 3 | value | 0.000 | 0 | 0 | 0 | 10308 | 0x2844 | float32 | Input Channel 6 Current individual Harmonics 3 percentage | 21-6 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 4 | value | 0.000 | 0 | 0 | 0 | 10310 | 0x2846 | float32 | Input Channel 6 Current individual Harmonics 4 percentage | 21-7 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 5 | value | 0.000 | 0 | 0 | 0 | 10312 | 0x2848 | float32 | Input Channel 6 Current individual Harmonics 5 percentage | 21-8 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 6 | value | 0.000 | 0 | 0 | 0 | 10314 | 0x284A | float32 | Input Channel 6 Current individual Harmonics 6 percentage | 21-9 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 7 | value | 0.000 | 0 | 0 | 0 | 10316 | 0x284C | float32 | Input Channel 6 Current individual Harmonics 7 percentage | 21-10 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 8 | value | 0.000 | 0 | 0 | 0 | 10318 | 0x284E | float32 | Input Channel 6 Current individual Harmonics 8 percentage | 21-11 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 9 | value | 0.000 | 0 | 0 | 0 | 10320 | 0x2850 | float32 | Input Channel 6 Current individual Harmonics 9 percentage | 21-12 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 10 | value | 0.000 | 0 | 0 | 0 | 10322 | 0x2852 | float32 | Input Channel 6 Current individual Harmonics 10 percentage | 21-13 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 11 | value | 0.000 | 0 | 0 | 0 | 10324 | 0x2854 | float32 | Input Channel 6 Current individual Harmonics 11 percentage | 21-14 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 12 | value | 0.000 | 0 | 0 | 0 | 10326 | 0x2856 | float32 | Input Channel 6 Current individual Harmonics 12 percentage | 21-15 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 13 | value | 0.000 | 0 | 0 | 0 | 10328 | 0x2858 | float32 | Input Channel 6 Current individual Harmonics 13 percentage | 21-16 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 14 | value | 0.000 | 0 | 0 | 0 | 10330 | 0x285A | float32 | Input Channel 6 Current individual Harmonics 14 percentage | 21-17 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 15 | value | 0.000 | 0 | 0 | 0 | 10332 | 0x285C | float32 | Input Channel 6 Current individual Harmonics 15 percentage | 21-18 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 16 | value | 0.000 | 0 | 0 | 0 | 10334 | 0x285E | float32 | Input Channel 6 Current individual Harmonics 16 percentage | 21-19 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 17 | value | 0.000 | 0 | 0 | 0 | 10336 | 0x2860 | float32 | Input Channel 6 Current individual Harmonics 17 percentage | 21-20 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 18 | value | 0.000 | 0 | 0 | 0 | 10338 | 0x2862 | float32 | Input Channel 6 Current individual Harmonics 18 percentage | 21-21 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 19 | value | 0.000 | 0 | 0 | 0 | 10340 | 0x2864 | float32 | Input Channel 6 Current individual Harmonics 19 percentage | 21-22 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 20 | value | 0.000 | 0 | 0 | 0 | 10342 | 0x2866 | float32 | Input Channel 6 Current individual Harmonics 20 percentage | 21-23 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 21 | value | 0.000 | 0 | 0 | 0 | 10344 | 0x2868 | float32 | Input Channel 6 Current individual Harmonics 21 percentage | 21-24 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 22 | value | 0.000 | 0 | 0 | 0 | 10346 | 0x286A | float32 | Input Channel 6 Current individual Harmonics 22 percentage | 21-25 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 23 | value | 0.000 | 0 | 0 | 0 | 10348 | 0x286C | float32 | Input Channel 6 Current individual Harmonics 23 percentage | 21-26 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 24 | value | 0.000 | 0 | 0 | 0 | 10350 | 0x286E | float32 | Input Channel 6 Current individual Harmonics 24 percentage | 21-27 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 25 | value | 0.000 | 0 | 0 | 0 | 10352 | 0x2870 | float32 | Input Channel 6 Current individual Harmonics 25 percentage | 21-28 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 26 | value | 0.000 | 0 | 0 | 0 | 10354 | 0x2872 | float32 | Input Channel 6 Current individual Harmonics 26 percentage | 21-29 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 27 | value | 0.000 | 0 | 0 | 0 | 10356 | 0x2874 | float32 | Input Channel 6 Current individual Harmonics 27 percentage | 21-30 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 28 | value | 0.000 | 0 | 0 | 0 | 10358 | 0x2876 | float32 | Input Channel 6 Current individual Harmonics 28 percentage | 21-31 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 29 | value | 0.000 | 0 | 0 | 0 | 10360 | 0x2878 | float32 | Input Channel 6 Current individual Harmonics 29 percentage | 21-32 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 30 | value | 0.000 | 0 | 0 | 0 | 10362 | 0x287A | float32 | Input Channel 6 Current individual Harmonics 30 percentage | 21-33 | PASS
Acurev4100 | Harmonics | Input Channel 6 | 31 | value | 0.000 | 0 | 0 | 0 | 10364 | 0x287C | float32 | Input Channel 6 Current individual Harmonics 31 percentage | 21-34 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 2 | value | 0.000 | 0 | 0 | 0 | 10374 | 0x2886 | float32 | Input Channel 7 Current individual Harmonics 2 percentage | 22-5 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 3 | value | 0.000 | 0 | 0 | 0 | 10376 | 0x2888 | float32 | Input Channel 7 Current individual Harmonics 3 percentage | 22-6 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 4 | value | 0.000 | 0 | 0 | 0 | 10378 | 0x288A | float32 | Input Channel 7 Current individual Harmonics 4 percentage | 22-7 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 5 | value | 0.000 | 0 | 0 | 0 | 10380 | 0x288C | float32 | Input Channel 7 Current individual Harmonics 5 percentage | 22-8 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 6 | value | 0.000 | 0 | 0 | 0 | 10382 | 0x288E | float32 | Input Channel 7 Current individual Harmonics 6 percentage | 22-9 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 7 | value | 0.000 | 0 | 0 | 0 | 10384 | 0x2890 | float32 | Input Channel 7 Current individual Harmonics 7 percentage | 22-10 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 8 | value | 0.000 | 0 | 0 | 0 | 10386 | 0x2892 | float32 | Input Channel 7 Current individual Harmonics 8 percentage | 22-11 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 9 | value | 0.000 | 0 | 0 | 0 | 10388 | 0x2894 | float32 | Input Channel 7 Current individual Harmonics 9 percentage | 22-12 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 10 | value | 0.000 | 0 | 0 | 0 | 10390 | 0x2896 | float32 | Input Channel 7 Current individual Harmonics 10 percentage | 22-13 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 11 | value | 0.000 | 0 | 0 | 0 | 10392 | 0x2898 | float32 | Input Channel 7 Current individual Harmonics 11 percentage | 22-14 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 12 | value | 0.000 | 0 | 0 | 0 | 10394 | 0x289A | float32 | Input Channel 7 Current individual Harmonics 12 percentage | 22-15 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 13 | value | 0.000 | 0 | 0 | 0 | 10396 | 0x289C | float32 | Input Channel 7 Current individual Harmonics 13 percentage | 22-16 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 14 | value | 0.000 | 0 | 0 | 0 | 10398 | 0x289E | float32 | Input Channel 7 Current individual Harmonics 14 percentage | 22-17 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 15 | value | 0.000 | 0 | 0 | 0 | 10400 | 0x28A0 | float32 | Input Channel 7 Current individual Harmonics 15 percentage | 22-18 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 16 | value | 0.000 | 0 | 0 | 0 | 10402 | 0x28A2 | float32 | Input Channel 7 Current individual Harmonics 16 percentage | 22-19 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 17 | value | 0.000 | 0 | 0 | 0 | 10404 | 0x28A4 | float32 | Input Channel 7 Current individual Harmonics 17 percentage | 22-20 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 18 | value | 0.000 | 0 | 0 | 0 | 10406 | 0x28A6 | float32 | Input Channel 7 Current individual Harmonics 18 percentage | 22-21 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 19 | value | 0.000 | 0 | 0 | 0 | 10408 | 0x28A8 | float32 | Input Channel 7 Current individual Harmonics 19 percentage | 22-22 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 20 | value | 0.000 | 0 | 0 | 0 | 10410 | 0x28AA | float32 | Input Channel 7 Current individual Harmonics 20 percentage | 22-23 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 21 | value | 0.000 | 0 | 0 | 0 | 10412 | 0x28AC | float32 | Input Channel 7 Current individual Harmonics 21 percentage | 22-24 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 22 | value | 0.000 | 0 | 0 | 0 | 10414 | 0x28AE | float32 | Input Channel 7 Current individual Harmonics 22 percentage | 22-25 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 23 | value | 0.000 | 0 | 0 | 0 | 10416 | 0x28B0 | float32 | Input Channel 7 Current individual Harmonics 23 percentage | 22-26 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 24 | value | 0.000 | 0 | 0 | 0 | 10418 | 0x28B2 | float32 | Input Channel 7 Current individual Harmonics 24 percentage | 22-27 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 25 | value | 0.000 | 0 | 0 | 0 | 10420 | 0x28B4 | float32 | Input Channel 7 Current individual Harmonics 25 percentage | 22-28 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 26 | value | 0.000 | 0 | 0 | 0 | 10422 | 0x28B6 | float32 | Input Channel 7 Current individual Harmonics 26 percentage | 22-29 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 27 | value | 0.000 | 0 | 0 | 0 | 10424 | 0x28B8 | float32 | Input Channel 7 Current individual Harmonics 27 percentage | 22-30 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 28 | value | 0.000 | 0 | 0 | 0 | 10426 | 0x28BA | float32 | Input Channel 7 Current individual Harmonics 28 percentage | 22-31 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 29 | value | 0.000 | 0 | 0 | 0 | 10428 | 0x28BC | float32 | Input Channel 7 Current individual Harmonics 29 percentage | 22-32 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 30 | value | 0.000 | 0 | 0 | 0 | 10430 | 0x28BE | float32 | Input Channel 7 Current individual Harmonics 30 percentage | 22-33 | PASS
Acurev4100 | Harmonics | Input Channel 7 | 31 | value | 0.000 | 0 | 0 | 0 | 10432 | 0x28C0 | float32 | Input Channel 7 Current individual Harmonics 31 percentage | 22-34 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 2 | value | 0.000 | 0 | 0 | 0 | 10442 | 0x28CA | float32 | Input Channel 8 Current individual Harmonics 2 percentage | 23-5 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 3 | value | 0.000 | 0 | 0 | 0 | 10444 | 0x28CC | float32 | Input Channel 8 Current individual Harmonics 3 percentage | 23-6 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 4 | value | 0.000 | 0 | 0 | 0 | 10446 | 0x28CE | float32 | Input Channel 8 Current individual Harmonics 4 percentage | 23-7 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 5 | value | 0.000 | 0 | 0 | 0 | 10448 | 0x28D0 | float32 | Input Channel 8 Current individual Harmonics 5 percentage | 23-8 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 6 | value | 0.000 | 0 | 0 | 0 | 10450 | 0x28D2 | float32 | Input Channel 8 Current individual Harmonics 6 percentage | 23-9 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 7 | value | 0.000 | 0 | 0 | 0 | 10452 | 0x28D4 | float32 | Input Channel 8 Current individual Harmonics 7 percentage | 23-10 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 8 | value | 0.000 | 0 | 0 | 0 | 10454 | 0x28D6 | float32 | Input Channel 8 Current individual Harmonics 8 percentage | 23-11 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 9 | value | 0.000 | 0 | 0 | 0 | 10456 | 0x28D8 | float32 | Input Channel 8 Current individual Harmonics 9 percentage | 23-12 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 10 | value | 0.000 | 0 | 0 | 0 | 10458 | 0x28DA | float32 | Input Channel 8 Current individual Harmonics 10 percentage | 23-13 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 11 | value | 0.000 | 0 | 0 | 0 | 10460 | 0x28DC | float32 | Input Channel 8 Current individual Harmonics 11 percentage | 23-14 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 12 | value | 0.000 | 0 | 0 | 0 | 10462 | 0x28DE | float32 | Input Channel 8 Current individual Harmonics 12 percentage | 23-15 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 13 | value | 0.000 | 0 | 0 | 0 | 10464 | 0x28E0 | float32 | Input Channel 8 Current individual Harmonics 13 percentage | 23-16 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 14 | value | 0.000 | 0 | 0 | 0 | 10466 | 0x28E2 | float32 | Input Channel 8 Current individual Harmonics 14 percentage | 23-17 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 15 | value | 0.000 | 0 | 0 | 0 | 10468 | 0x28E4 | float32 | Input Channel 8 Current individual Harmonics 15 percentage | 23-18 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 16 | value | 0.000 | 0 | 0 | 0 | 10470 | 0x28E6 | float32 | Input Channel 8 Current individual Harmonics 16 percentage | 23-19 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 17 | value | 0.000 | 0 | 0 | 0 | 10472 | 0x28E8 | float32 | Input Channel 8 Current individual Harmonics 17 percentage | 23-20 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 18 | value | 0.000 | 0 | 0 | 0 | 10474 | 0x28EA | float32 | Input Channel 8 Current individual Harmonics 18 percentage | 23-21 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 19 | value | 0.000 | 0 | 0 | 0 | 10476 | 0x28EC | float32 | Input Channel 8 Current individual Harmonics 19 percentage | 23-22 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 20 | value | 0.000 | 0 | 0 | 0 | 10478 | 0x28EE | float32 | Input Channel 8 Current individual Harmonics 20 percentage | 23-23 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 21 | value | 0.000 | 0 | 0 | 0 | 10480 | 0x28F0 | float32 | Input Channel 8 Current individual Harmonics 21 percentage | 23-24 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 22 | value | 0.000 | 0 | 0 | 0 | 10482 | 0x28F2 | float32 | Input Channel 8 Current individual Harmonics 22 percentage | 23-25 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 23 | value | 0.000 | 0 | 0 | 0 | 10484 | 0x28F4 | float32 | Input Channel 8 Current individual Harmonics 23 percentage | 23-26 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 24 | value | 0.000 | 0 | 0 | 0 | 10486 | 0x28F6 | float32 | Input Channel 8 Current individual Harmonics 24 percentage | 23-27 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 25 | value | 0.000 | 0 | 0 | 0 | 10488 | 0x28F8 | float32 | Input Channel 8 Current individual Harmonics 25 percentage | 23-28 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 26 | value | 0.000 | 0 | 0 | 0 | 10490 | 0x28FA | float32 | Input Channel 8 Current individual Harmonics 26 percentage | 23-29 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 27 | value | 0.000 | 0 | 0 | 0 | 10492 | 0x28FC | float32 | Input Channel 8 Current individual Harmonics 27 percentage | 23-30 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 28 | value | 0.000 | 0 | 0 | 0 | 10494 | 0x28FE | float32 | Input Channel 8 Current individual Harmonics 28 percentage | 23-31 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 29 | value | 0.000 | 0 | 0 | 0 | 10496 | 0x2900 | float32 | Input Channel 8 Current individual Harmonics 29 percentage | 23-32 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 30 | value | 0.000 | 0 | 0 | 0 | 10498 | 0x2902 | float32 | Input Channel 8 Current individual Harmonics 30 percentage | 23-33 | PASS
Acurev4100 | Harmonics | Input Channel 8 | 31 | value | 0.000 | 0 | 0 | 0 | 10500 | 0x2904 | float32 | Input Channel 8 Current individual Harmonics 31 percentage | 23-34 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 2 | value | 0.000 | 0 | 0 | 0 | 10510 | 0x290E | float32 | Input Channel 9 Current individual Harmonics 2 percentage | 24-5 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 3 | value | 0.000 | 0 | 0 | 0 | 10512 | 0x2910 | float32 | Input Channel 9 Current individual Harmonics 3 percentage | 24-6 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 4 | value | 0.000 | 0 | 0 | 0 | 10514 | 0x2912 | float32 | Input Channel 9 Current individual Harmonics 4 percentage | 24-7 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 5 | value | 0.000 | 0 | 0 | 0 | 10516 | 0x2914 | float32 | Input Channel 9 Current individual Harmonics 5 percentage | 24-8 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 6 | value | 0.000 | 0 | 0 | 0 | 10518 | 0x2916 | float32 | Input Channel 9 Current individual Harmonics 6 percentage | 24-9 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 7 | value | 0.000 | 0 | 0 | 0 | 10520 | 0x2918 | float32 | Input Channel 9 Current individual Harmonics 7 percentage | 24-10 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 8 | value | 0.000 | 0 | 0 | 0 | 10522 | 0x291A | float32 | Input Channel 9 Current individual Harmonics 8 percentage | 24-11 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 9 | value | 0.000 | 0 | 0 | 0 | 10524 | 0x291C | float32 | Input Channel 9 Current individual Harmonics 9 percentage | 24-12 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 10 | value | 0.000 | 0 | 0 | 0 | 10526 | 0x291E | float32 | Input Channel 9 Current individual Harmonics 10 percentage | 24-13 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 11 | value | 0.000 | 0 | 0 | 0 | 10528 | 0x2920 | float32 | Input Channel 9 Current individual Harmonics 11 percentage | 24-14 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 12 | value | 0.000 | 0 | 0 | 0 | 10530 | 0x2922 | float32 | Input Channel 9 Current individual Harmonics 12 percentage | 24-15 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 13 | value | 0.000 | 0 | 0 | 0 | 10532 | 0x2924 | float32 | Input Channel 9 Current individual Harmonics 13 percentage | 24-16 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 14 | value | 0.000 | 0 | 0 | 0 | 10534 | 0x2926 | float32 | Input Channel 9 Current individual Harmonics 14 percentage | 24-17 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 15 | value | 0.000 | 0 | 0 | 0 | 10536 | 0x2928 | float32 | Input Channel 9 Current individual Harmonics 15 percentage | 24-18 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 16 | value | 0.000 | 0 | 0 | 0 | 10538 | 0x292A | float32 | Input Channel 9 Current individual Harmonics 16 percentage | 24-19 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 17 | value | 0.000 | 0 | 0 | 0 | 10540 | 0x292C | float32 | Input Channel 9 Current individual Harmonics 17 percentage | 24-20 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 18 | value | 0.000 | 0 | 0 | 0 | 10542 | 0x292E | float32 | Input Channel 9 Current individual Harmonics 18 percentage | 24-21 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 19 | value | 0.000 | 0 | 0 | 0 | 10544 | 0x2930 | float32 | Input Channel 9 Current individual Harmonics 19 percentage | 24-22 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 20 | value | 0.000 | 0 | 0 | 0 | 10546 | 0x2932 | float32 | Input Channel 9 Current individual Harmonics 20 percentage | 24-23 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 21 | value | 0.000 | 0 | 0 | 0 | 10548 | 0x2934 | float32 | Input Channel 9 Current individual Harmonics 21 percentage | 24-24 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 22 | value | 0.000 | 0 | 0 | 0 | 10550 | 0x2936 | float32 | Input Channel 9 Current individual Harmonics 22 percentage | 24-25 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 23 | value | 0.000 | 0 | 0 | 0 | 10552 | 0x2938 | float32 | Input Channel 9 Current individual Harmonics 23 percentage | 24-26 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 24 | value | 0.000 | 0 | 0 | 0 | 10554 | 0x293A | float32 | Input Channel 9 Current individual Harmonics 24 percentage | 24-27 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 25 | value | 0.000 | 0 | 0 | 0 | 10556 | 0x293C | float32 | Input Channel 9 Current individual Harmonics 25 percentage | 24-28 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 26 | value | 0.000 | 0 | 0 | 0 | 10558 | 0x293E | float32 | Input Channel 9 Current individual Harmonics 26 percentage | 24-29 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 27 | value | 0.000 | 0 | 0 | 0 | 10560 | 0x2940 | float32 | Input Channel 9 Current individual Harmonics 27 percentage | 24-30 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 28 | value | 0.000 | 0 | 0 | 0 | 10562 | 0x2942 | float32 | Input Channel 9 Current individual Harmonics 28 percentage | 24-31 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 29 | value | 0.000 | 0 | 0 | 0 | 10564 | 0x2944 | float32 | Input Channel 9 Current individual Harmonics 29 percentage | 24-32 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 30 | value | 0.000 | 0 | 0 | 0 | 10566 | 0x2946 | float32 | Input Channel 9 Current individual Harmonics 30 percentage | 24-33 | PASS
Acurev4100 | Harmonics | Input Channel 9 | 31 | value | 0.000 | 0 | 0 | 0 | 10568 | 0x2948 | float32 | Input Channel 9 Current individual Harmonics 31 percentage | 24-34 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 2 | value | 0.000 | 0 | 0 | 0 | 10578 | 0x2952 | float32 | Input Channel 10 Current individual Harmonics 2 percentage | 25-5 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 3 | value | 0.000 | 0 | 0 | 0 | 10580 | 0x2954 | float32 | Input Channel 10 Current individual Harmonics 3 percentage | 25-6 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 4 | value | 0.000 | 0 | 0 | 0 | 10582 | 0x2956 | float32 | Input Channel 10 Current individual Harmonics 4 percentage | 25-7 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 5 | value | 0.000 | 0 | 0 | 0 | 10584 | 0x2958 | float32 | Input Channel 10 Current individual Harmonics 5 percentage | 25-8 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 6 | value | 0.000 | 0 | 0 | 0 | 10586 | 0x295A | float32 | Input Channel 10 Current individual Harmonics 6 percentage | 25-9 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 7 | value | 0.000 | 0 | 0 | 0 | 10588 | 0x295C | float32 | Input Channel 10 Current individual Harmonics 7 percentage | 25-10 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 8 | value | 0.000 | 0 | 0 | 0 | 10590 | 0x295E | float32 | Input Channel 10 Current individual Harmonics 8 percentage | 25-11 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 9 | value | 0.000 | 0 | 0 | 0 | 10592 | 0x2960 | float32 | Input Channel 10 Current individual Harmonics 9 percentage | 25-12 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 10 | value | 0.000 | 0 | 0 | 0 | 10594 | 0x2962 | float32 | Input Channel 10 Current individual Harmonics 10 percentage | 25-13 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 11 | value | 0.000 | 0 | 0 | 0 | 10596 | 0x2964 | float32 | Input Channel 10 Current individual Harmonics 11 percentage | 25-14 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 12 | value | 0.000 | 0 | 0 | 0 | 10598 | 0x2966 | float32 | Input Channel 10 Current individual Harmonics 12 percentage | 25-15 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 13 | value | 0.000 | 0 | 0 | 0 | 10600 | 0x2968 | float32 | Input Channel 10 Current individual Harmonics 13 percentage | 25-16 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 14 | value | 0.000 | 0 | 0 | 0 | 10602 | 0x296A | float32 | Input Channel 10 Current individual Harmonics 14 percentage | 25-17 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 15 | value | 0.000 | 0 | 0 | 0 | 10604 | 0x296C | float32 | Input Channel 10 Current individual Harmonics 15 percentage | 25-18 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 16 | value | 0.000 | 0 | 0 | 0 | 10606 | 0x296E | float32 | Input Channel 10 Current individual Harmonics 16 percentage | 25-19 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 17 | value | 0.000 | 0 | 0 | 0 | 10608 | 0x2970 | float32 | Input Channel 10 Current individual Harmonics 17 percentage | 25-20 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 18 | value | 0.000 | 0 | 0 | 0 | 10610 | 0x2972 | float32 | Input Channel 10 Current individual Harmonics 18 percentage | 25-21 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 19 | value | 0.000 | 0 | 0 | 0 | 10612 | 0x2974 | float32 | Input Channel 10 Current individual Harmonics 19 percentage | 25-22 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 20 | value | 0.000 | 0 | 0 | 0 | 10614 | 0x2976 | float32 | Input Channel 10 Current individual Harmonics 20 percentage | 25-23 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 21 | value | 0.000 | 0 | 0 | 0 | 10616 | 0x2978 | float32 | Input Channel 10 Current individual Harmonics 21 percentage | 25-24 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 22 | value | 0.000 | 0 | 0 | 0 | 10618 | 0x297A | float32 | Input Channel 10 Current individual Harmonics 22 percentage | 25-25 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 23 | value | 0.000 | 0 | 0 | 0 | 10620 | 0x297C | float32 | Input Channel 10 Current individual Harmonics 23 percentage | 25-26 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 24 | value | 0.000 | 0 | 0 | 0 | 10622 | 0x297E | float32 | Input Channel 10 Current individual Harmonics 24 percentage | 25-27 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 25 | value | 0.000 | 0 | 0 | 0 | 10624 | 0x2980 | float32 | Input Channel 10 Current individual Harmonics 25 percentage | 25-28 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 26 | value | 0.000 | 0 | 0 | 0 | 10626 | 0x2982 | float32 | Input Channel 10 Current individual Harmonics 26 percentage | 25-29 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 27 | value | 0.000 | 0 | 0 | 0 | 10628 | 0x2984 | float32 | Input Channel 10 Current individual Harmonics 27 percentage | 25-30 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 28 | value | 0.000 | 0 | 0 | 0 | 10630 | 0x2986 | float32 | Input Channel 10 Current individual Harmonics 28 percentage | 25-31 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 29 | value | 0.000 | 0 | 0 | 0 | 10632 | 0x2988 | float32 | Input Channel 10 Current individual Harmonics 29 percentage | 25-32 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 30 | value | 0.000 | 0 | 0 | 0 | 10634 | 0x298A | float32 | Input Channel 10 Current individual Harmonics 30 percentage | 25-33 | PASS
Acurev4100 | Harmonics | Input Channel 10 | 31 | value | 0.000 | 0 | 0 | 0 | 10636 | 0x298C | float32 | Input Channel 10 Current individual Harmonics 31 percentage | 25-34 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 2 | value | 0.000 | 0 | 0 | 0 | 10646 | 0x2996 | float32 | Input Channel 11 Current individual Harmonics 2 percentage | 26-5 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 3 | value | 0.000 | 0 | 0 | 0 | 10648 | 0x2998 | float32 | Input Channel 11 Current individual Harmonics 3 percentage | 26-6 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 4 | value | 0.000 | 0 | 0 | 0 | 10650 | 0x299A | float32 | Input Channel 11 Current individual Harmonics 4 percentage | 26-7 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 5 | value | 0.000 | 0 | 0 | 0 | 10652 | 0x299C | float32 | Input Channel 11 Current individual Harmonics 5 percentage | 26-8 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 6 | value | 0.000 | 0 | 0 | 0 | 10654 | 0x299E | float32 | Input Channel 11 Current individual Harmonics 6 percentage | 26-9 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 7 | value | 0.000 | 0 | 0 | 0 | 10656 | 0x29A0 | float32 | Input Channel 11 Current individual Harmonics 7 percentage | 26-10 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 8 | value | 0.000 | 0 | 0 | 0 | 10658 | 0x29A2 | float32 | Input Channel 11 Current individual Harmonics 8 percentage | 26-11 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 9 | value | 0.000 | 0 | 0 | 0 | 10660 | 0x29A4 | float32 | Input Channel 11 Current individual Harmonics 9 percentage | 26-12 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 10 | value | 0.000 | 0 | 0 | 0 | 10662 | 0x29A6 | float32 | Input Channel 11 Current individual Harmonics 10 percentage | 26-13 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 11 | value | 0.000 | 0 | 0 | 0 | 10664 | 0x29A8 | float32 | Input Channel 11 Current individual Harmonics 11 percentage | 26-14 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 12 | value | 0.000 | 0 | 0 | 0 | 10666 | 0x29AA | float32 | Input Channel 11 Current individual Harmonics 12 percentage | 26-15 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 13 | value | 0.000 | 0 | 0 | 0 | 10668 | 0x29AC | float32 | Input Channel 11 Current individual Harmonics 13 percentage | 26-16 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 14 | value | 0.000 | 0 | 0 | 0 | 10670 | 0x29AE | float32 | Input Channel 11 Current individual Harmonics 14 percentage | 26-17 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 15 | value | 0.000 | 0 | 0 | 0 | 10672 | 0x29B0 | float32 | Input Channel 11 Current individual Harmonics 15 percentage | 26-18 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 16 | value | 0.000 | 0 | 0 | 0 | 10674 | 0x29B2 | float32 | Input Channel 11 Current individual Harmonics 16 percentage | 26-19 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 17 | value | 0.000 | 0 | 0 | 0 | 10676 | 0x29B4 | float32 | Input Channel 11 Current individual Harmonics 17 percentage | 26-20 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 18 | value | 0.000 | 0 | 0 | 0 | 10678 | 0x29B6 | float32 | Input Channel 11 Current individual Harmonics 18 percentage | 26-21 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 19 | value | 0.000 | 0 | 0 | 0 | 10680 | 0x29B8 | float32 | Input Channel 11 Current individual Harmonics 19 percentage | 26-22 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 20 | value | 0.000 | 0 | 0 | 0 | 10682 | 0x29BA | float32 | Input Channel 11 Current individual Harmonics 20 percentage | 26-23 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 21 | value | 0.000 | 0 | 0 | 0 | 10684 | 0x29BC | float32 | Input Channel 11 Current individual Harmonics 21 percentage | 26-24 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 22 | value | 0.000 | 0 | 0 | 0 | 10686 | 0x29BE | float32 | Input Channel 11 Current individual Harmonics 22 percentage | 26-25 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 23 | value | 0.000 | 0 | 0 | 0 | 10688 | 0x29C0 | float32 | Input Channel 11 Current individual Harmonics 23 percentage | 26-26 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 24 | value | 0.000 | 0 | 0 | 0 | 10690 | 0x29C2 | float32 | Input Channel 11 Current individual Harmonics 24 percentage | 26-27 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 25 | value | 0.000 | 0 | 0 | 0 | 10692 | 0x29C4 | float32 | Input Channel 11 Current individual Harmonics 25 percentage | 26-28 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 26 | value | 0.000 | 0 | 0 | 0 | 10694 | 0x29C6 | float32 | Input Channel 11 Current individual Harmonics 26 percentage | 26-29 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 27 | value | 0.000 | 0 | 0 | 0 | 10696 | 0x29C8 | float32 | Input Channel 11 Current individual Harmonics 27 percentage | 26-30 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 28 | value | 0.000 | 0 | 0 | 0 | 10698 | 0x29CA | float32 | Input Channel 11 Current individual Harmonics 28 percentage | 26-31 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 29 | value | 0.000 | 0 | 0 | 0 | 10700 | 0x29CC | float32 | Input Channel 11 Current individual Harmonics 29 percentage | 26-32 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 30 | value | 0.000 | 0 | 0 | 0 | 10702 | 0x29CE | float32 | Input Channel 11 Current individual Harmonics 30 percentage | 26-33 | PASS
Acurev4100 | Harmonics | Input Channel 11 | 31 | value | 0.000 | 0 | 0 | 0 | 10704 | 0x29D0 | float32 | Input Channel 11 Current individual Harmonics 31 percentage | 26-34 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 2 | value | 0.000 | 0 | 0 | 0 | 10714 | 0x29DA | float32 | Input Channel 12 Current individual Harmonics 2 percentage | 27-5 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 3 | value | 0.000 | 0 | 0 | 0 | 10716 | 0x29DC | float32 | Input Channel 12 Current individual Harmonics 3 percentage | 27-6 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 4 | value | 0.000 | 0 | 0 | 0 | 10718 | 0x29DE | float32 | Input Channel 12 Current individual Harmonics 4 percentage | 27-7 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 5 | value | 0.000 | 0 | 0 | 0 | 10720 | 0x29E0 | float32 | Input Channel 12 Current individual Harmonics 5 percentage | 27-8 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 6 | value | 0.000 | 0 | 0 | 0 | 10722 | 0x29E2 | float32 | Input Channel 12 Current individual Harmonics 6 percentage | 27-9 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 7 | value | 0.000 | 0 | 0 | 0 | 10724 | 0x29E4 | float32 | Input Channel 12 Current individual Harmonics 7 percentage | 27-10 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 8 | value | 0.000 | 0 | 0 | 0 | 10726 | 0x29E6 | float32 | Input Channel 12 Current individual Harmonics 8 percentage | 27-11 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 9 | value | 0.000 | 0 | 0 | 0 | 10728 | 0x29E8 | float32 | Input Channel 12 Current individual Harmonics 9 percentage | 27-12 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 10 | value | 0.000 | 0 | 0 | 0 | 10730 | 0x29EA | float32 | Input Channel 12 Current individual Harmonics 10 percentage | 27-13 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 11 | value | 0.000 | 0 | 0 | 0 | 10732 | 0x29EC | float32 | Input Channel 12 Current individual Harmonics 11 percentage | 27-14 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 12 | value | 0.000 | 0 | 0 | 0 | 10734 | 0x29EE | float32 | Input Channel 12 Current individual Harmonics 12 percentage | 27-15 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 13 | value | 0.000 | 0 | 0 | 0 | 10736 | 0x29F0 | float32 | Input Channel 12 Current individual Harmonics 13 percentage | 27-16 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 14 | value | 0.000 | 0 | 0 | 0 | 10738 | 0x29F2 | float32 | Input Channel 12 Current individual Harmonics 14 percentage | 27-17 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 15 | value | 0.000 | 0 | 0 | 0 | 10740 | 0x29F4 | float32 | Input Channel 12 Current individual Harmonics 15 percentage | 27-18 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 16 | value | 0.000 | 0 | 0 | 0 | 10742 | 0x29F6 | float32 | Input Channel 12 Current individual Harmonics 16 percentage | 27-19 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 17 | value | 0.000 | 0 | 0 | 0 | 10744 | 0x29F8 | float32 | Input Channel 12 Current individual Harmonics 17 percentage | 27-20 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 18 | value | 0.000 | 0 | 0 | 0 | 10746 | 0x29FA | float32 | Input Channel 12 Current individual Harmonics 18 percentage | 27-21 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 19 | value | 0.000 | 0 | 0 | 0 | 10748 | 0x29FC | float32 | Input Channel 12 Current individual Harmonics 19 percentage | 27-22 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 20 | value | 0.000 | 0 | 0 | 0 | 10750 | 0x29FE | float32 | Input Channel 12 Current individual Harmonics 20 percentage | 27-23 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 21 | value | 0.000 | 0 | 0 | 0 | 10752 | 0x2A00 | float32 | Input Channel 12 Current individual Harmonics 21 percentage | 27-24 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 22 | value | 0.000 | 0 | 0 | 0 | 10754 | 0x2A02 | float32 | Input Channel 12 Current individual Harmonics 22 percentage | 27-25 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 23 | value | 0.000 | 0 | 0 | 0 | 10756 | 0x2A04 | float32 | Input Channel 12 Current individual Harmonics 23 percentage | 27-26 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 24 | value | 0.000 | 0 | 0 | 0 | 10758 | 0x2A06 | float32 | Input Channel 12 Current individual Harmonics 24 percentage | 27-27 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 25 | value | 0.000 | 0 | 0 | 0 | 10760 | 0x2A08 | float32 | Input Channel 12 Current individual Harmonics 25 percentage | 27-28 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 26 | value | 0.000 | 0 | 0 | 0 | 10762 | 0x2A0A | float32 | Input Channel 12 Current individual Harmonics 26 percentage | 27-29 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 27 | value | 0.000 | 0 | 0 | 0 | 10764 | 0x2A0C | float32 | Input Channel 12 Current individual Harmonics 27 percentage | 27-30 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 28 | value | 0.000 | 0 | 0 | 0 | 10766 | 0x2A0E | float32 | Input Channel 12 Current individual Harmonics 28 percentage | 27-31 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 29 | value | 0.000 | 0 | 0 | 0 | 10768 | 0x2A10 | float32 | Input Channel 12 Current individual Harmonics 29 percentage | 27-32 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 30 | value | 0.000 | 0 | 0 | 0 | 10770 | 0x2A12 | float32 | Input Channel 12 Current individual Harmonics 30 percentage | 27-33 | PASS
Acurev4100 | Harmonics | Input Channel 12 | 31 | value | 0.000 | 0 | 0 | 0 | 10772 | 0x2A14 | float32 | Input Channel 12 Current individual Harmonics 31 percentage | 27-34 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 2 | value | 0.000 | 0 | 0 | 0 | 10782 | 0x2A1E | float32 | Input Channel 13 Current individual Harmonics 2 percentage | 28-5 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 3 | value | 0.000 | 0 | 0 | 0 | 10784 | 0x2A20 | float32 | Input Channel 13 Current individual Harmonics 3 percentage | 28-6 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 4 | value | 0.000 | 0 | 0 | 0 | 10786 | 0x2A22 | float32 | Input Channel 13 Current individual Harmonics 4 percentage | 28-7 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 5 | value | 0.000 | 0 | 0 | 0 | 10788 | 0x2A24 | float32 | Input Channel 13 Current individual Harmonics 5 percentage | 28-8 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 6 | value | 0.000 | 0 | 0 | 0 | 10790 | 0x2A26 | float32 | Input Channel 13 Current individual Harmonics 6 percentage | 28-9 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 7 | value | 0.000 | 0 | 0 | 0 | 10792 | 0x2A28 | float32 | Input Channel 13 Current individual Harmonics 7 percentage | 28-10 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 8 | value | 0.000 | 0 | 0 | 0 | 10794 | 0x2A2A | float32 | Input Channel 13 Current individual Harmonics 8 percentage | 28-11 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 9 | value | 0.000 | 0 | 0 | 0 | 10796 | 0x2A2C | float32 | Input Channel 13 Current individual Harmonics 9 percentage | 28-12 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 10 | value | 0.000 | 0 | 0 | 0 | 10798 | 0x2A2E | float32 | Input Channel 13 Current individual Harmonics 10 percentage | 28-13 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 11 | value | 0.000 | 0 | 0 | 0 | 10800 | 0x2A30 | float32 | Input Channel 13 Current individual Harmonics 11 percentage | 28-14 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 12 | value | 0.000 | 0 | 0 | 0 | 10802 | 0x2A32 | float32 | Input Channel 13 Current individual Harmonics 12 percentage | 28-15 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 13 | value | 0.000 | 0 | 0 | 0 | 10804 | 0x2A34 | float32 | Input Channel 13 Current individual Harmonics 13 percentage | 28-16 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 14 | value | 0.000 | 0 | 0 | 0 | 10806 | 0x2A36 | float32 | Input Channel 13 Current individual Harmonics 14 percentage | 28-17 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 15 | value | 0.000 | 0 | 0 | 0 | 10808 | 0x2A38 | float32 | Input Channel 13 Current individual Harmonics 15 percentage | 28-18 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 16 | value | 0.000 | 0 | 0 | 0 | 10810 | 0x2A3A | float32 | Input Channel 13 Current individual Harmonics 16 percentage | 28-19 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 17 | value | 0.000 | 0 | 0 | 0 | 10812 | 0x2A3C | float32 | Input Channel 13 Current individual Harmonics 17 percentage | 28-20 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 18 | value | 0.000 | 0 | 0 | 0 | 10814 | 0x2A3E | float32 | Input Channel 13 Current individual Harmonics 18 percentage | 28-21 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 19 | value | 0.000 | 0 | 0 | 0 | 10816 | 0x2A40 | float32 | Input Channel 13 Current individual Harmonics 19 percentage | 28-22 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 20 | value | 0.000 | 0 | 0 | 0 | 10818 | 0x2A42 | float32 | Input Channel 13 Current individual Harmonics 20 percentage | 28-23 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 21 | value | 0.000 | 0 | 0 | 0 | 10820 | 0x2A44 | float32 | Input Channel 13 Current individual Harmonics 21 percentage | 28-24 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 22 | value | 0.000 | 0 | 0 | 0 | 10822 | 0x2A46 | float32 | Input Channel 13 Current individual Harmonics 22 percentage | 28-25 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 23 | value | 0.000 | 0 | 0 | 0 | 10824 | 0x2A48 | float32 | Input Channel 13 Current individual Harmonics 23 percentage | 28-26 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 24 | value | 0.000 | 0 | 0 | 0 | 10826 | 0x2A4A | float32 | Input Channel 13 Current individual Harmonics 24 percentage | 28-27 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 25 | value | 0.000 | 0 | 0 | 0 | 10828 | 0x2A4C | float32 | Input Channel 13 Current individual Harmonics 25 percentage | 28-28 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 26 | value | 0.000 | 0 | 0 | 0 | 10830 | 0x2A4E | float32 | Input Channel 13 Current individual Harmonics 26 percentage | 28-29 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 27 | value | 0.000 | 0 | 0 | 0 | 10832 | 0x2A50 | float32 | Input Channel 13 Current individual Harmonics 27 percentage | 28-30 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 28 | value | 0.000 | 0 | 0 | 0 | 10834 | 0x2A52 | float32 | Input Channel 13 Current individual Harmonics 28 percentage | 28-31 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 29 | value | 0.000 | 0 | 0 | 0 | 10836 | 0x2A54 | float32 | Input Channel 13 Current individual Harmonics 29 percentage | 28-32 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 30 | value | 0.000 | 0 | 0 | 0 | 10838 | 0x2A56 | float32 | Input Channel 13 Current individual Harmonics 30 percentage | 28-33 | PASS
Acurev4100 | Harmonics | Input Channel 13 | 31 | value | 0.000 | 0 | 0 | 0 | 10840 | 0x2A58 | float32 | Input Channel 13 Current individual Harmonics 31 percentage | 28-34 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 2 | value | 0.000 | 0 | 0 | 0 | 10850 | 0x2A62 | float32 | Input Channel 14 Current individual Harmonics 2 percentage | 29-5 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 3 | value | 0.000 | 0 | 0 | 0 | 10852 | 0x2A64 | float32 | Input Channel 14 Current individual Harmonics 3 percentage | 29-6 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 4 | value | 0.000 | 0 | 0 | 0 | 10854 | 0x2A66 | float32 | Input Channel 14 Current individual Harmonics 4 percentage | 29-7 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 5 | value | 0.000 | 0 | 0 | 0 | 10856 | 0x2A68 | float32 | Input Channel 14 Current individual Harmonics 5 percentage | 29-8 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 6 | value | 0.000 | 0 | 0 | 0 | 10858 | 0x2A6A | float32 | Input Channel 14 Current individual Harmonics 6 percentage | 29-9 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 7 | value | 0.000 | 0 | 0 | 0 | 10860 | 0x2A6C | float32 | Input Channel 14 Current individual Harmonics 7 percentage | 29-10 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 8 | value | 0.000 | 0 | 0 | 0 | 10862 | 0x2A6E | float32 | Input Channel 14 Current individual Harmonics 8 percentage | 29-11 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 9 | value | 0.000 | 0 | 0 | 0 | 10864 | 0x2A70 | float32 | Input Channel 14 Current individual Harmonics 9 percentage | 29-12 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 10 | value | 0.000 | 0 | 0 | 0 | 10866 | 0x2A72 | float32 | Input Channel 14 Current individual Harmonics 10 percentage | 29-13 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 11 | value | 0.000 | 0 | 0 | 0 | 10868 | 0x2A74 | float32 | Input Channel 14 Current individual Harmonics 11 percentage | 29-14 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 12 | value | 0.000 | 0 | 0 | 0 | 10870 | 0x2A76 | float32 | Input Channel 14 Current individual Harmonics 12 percentage | 29-15 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 13 | value | 0.000 | 0 | 0 | 0 | 10872 | 0x2A78 | float32 | Input Channel 14 Current individual Harmonics 13 percentage | 29-16 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 14 | value | 0.000 | 0 | 0 | 0 | 10874 | 0x2A7A | float32 | Input Channel 14 Current individual Harmonics 14 percentage | 29-17 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 15 | value | 0.000 | 0 | 0 | 0 | 10876 | 0x2A7C | float32 | Input Channel 14 Current individual Harmonics 15 percentage | 29-18 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 16 | value | 0.000 | 0 | 0 | 0 | 10878 | 0x2A7E | float32 | Input Channel 14 Current individual Harmonics 16 percentage | 29-19 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 17 | value | 0.000 | 0 | 0 | 0 | 10880 | 0x2A80 | float32 | Input Channel 14 Current individual Harmonics 17 percentage | 29-20 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 18 | value | 0.000 | 0 | 0 | 0 | 10882 | 0x2A82 | float32 | Input Channel 14 Current individual Harmonics 18 percentage | 29-21 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 19 | value | 0.000 | 0 | 0 | 0 | 10884 | 0x2A84 | float32 | Input Channel 14 Current individual Harmonics 19 percentage | 29-22 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 20 | value | 0.000 | 0 | 0 | 0 | 10886 | 0x2A86 | float32 | Input Channel 14 Current individual Harmonics 20 percentage | 29-23 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 21 | value | 0.000 | 0 | 0 | 0 | 10888 | 0x2A88 | float32 | Input Channel 14 Current individual Harmonics 21 percentage | 29-24 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 22 | value | 0.000 | 0 | 0 | 0 | 10890 | 0x2A8A | float32 | Input Channel 14 Current individual Harmonics 22 percentage | 29-25 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 23 | value | 0.000 | 0 | 0 | 0 | 10892 | 0x2A8C | float32 | Input Channel 14 Current individual Harmonics 23 percentage | 29-26 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 24 | value | 0.000 | 0 | 0 | 0 | 10894 | 0x2A8E | float32 | Input Channel 14 Current individual Harmonics 24 percentage | 29-27 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 25 | value | 0.000 | 0 | 0 | 0 | 10896 | 0x2A90 | float32 | Input Channel 14 Current individual Harmonics 25 percentage | 29-28 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 26 | value | 0.000 | 0 | 0 | 0 | 10898 | 0x2A92 | float32 | Input Channel 14 Current individual Harmonics 26 percentage | 29-29 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 27 | value | 0.000 | 0 | 0 | 0 | 10900 | 0x2A94 | float32 | Input Channel 14 Current individual Harmonics 27 percentage | 29-30 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 28 | value | 0.000 | 0 | 0 | 0 | 10902 | 0x2A96 | float32 | Input Channel 14 Current individual Harmonics 28 percentage | 29-31 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 29 | value | 0.000 | 0 | 0 | 0 | 10904 | 0x2A98 | float32 | Input Channel 14 Current individual Harmonics 29 percentage | 29-32 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 30 | value | 0.000 | 0 | 0 | 0 | 10906 | 0x2A9A | float32 | Input Channel 14 Current individual Harmonics 30 percentage | 29-33 | PASS
Acurev4100 | Harmonics | Input Channel 14 | 31 | value | 0.000 | 0 | 0 | 0 | 10908 | 0x2A9C | float32 | Input Channel 14 Current individual Harmonics 31 percentage | 29-34 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 2 | value | 0.000 | 0 | 0 | 0 | 10918 | 0x2AA6 | float32 | Input Channel 15 Current individual Harmonics 2 percentage | 30-5 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 3 | value | 0.000 | 0 | 0 | 0 | 10920 | 0x2AA8 | float32 | Input Channel 15 Current individual Harmonics 3 percentage | 30-6 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 4 | value | 0.000 | 0 | 0 | 0 | 10922 | 0x2AAA | float32 | Input Channel 15 Current individual Harmonics 4 percentage | 30-7 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 5 | value | 0.000 | 0 | 0 | 0 | 10924 | 0x2AAC | float32 | Input Channel 15 Current individual Harmonics 5 percentage | 30-8 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 6 | value | 0.000 | 0 | 0 | 0 | 10926 | 0x2AAE | float32 | Input Channel 15 Current individual Harmonics 6 percentage | 30-9 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 7 | value | 0.000 | 0 | 0 | 0 | 10928 | 0x2AB0 | float32 | Input Channel 15 Current individual Harmonics 7 percentage | 30-10 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 8 | value | 0.000 | 0 | 0 | 0 | 10930 | 0x2AB2 | float32 | Input Channel 15 Current individual Harmonics 8 percentage | 30-11 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 9 | value | 0.000 | 0 | 0 | 0 | 10932 | 0x2AB4 | float32 | Input Channel 15 Current individual Harmonics 9 percentage | 30-12 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 10 | value | 0.000 | 0 | 0 | 0 | 10934 | 0x2AB6 | float32 | Input Channel 15 Current individual Harmonics 10 percentage | 30-13 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 11 | value | 0.000 | 0 | 0 | 0 | 10936 | 0x2AB8 | float32 | Input Channel 15 Current individual Harmonics 11 percentage | 30-14 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 12 | value | 0.000 | 0 | 0 | 0 | 10938 | 0x2ABA | float32 | Input Channel 15 Current individual Harmonics 12 percentage | 30-15 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 13 | value | 0.000 | 0 | 0 | 0 | 10940 | 0x2ABC | float32 | Input Channel 15 Current individual Harmonics 13 percentage | 30-16 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 14 | value | 0.000 | 0 | 0 | 0 | 10942 | 0x2ABE | float32 | Input Channel 15 Current individual Harmonics 14 percentage | 30-17 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 15 | value | 0.000 | 0 | 0 | 0 | 10944 | 0x2AC0 | float32 | Input Channel 15 Current individual Harmonics 15 percentage | 30-18 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 16 | value | 0.000 | 0 | 0 | 0 | 10946 | 0x2AC2 | float32 | Input Channel 15 Current individual Harmonics 16 percentage | 30-19 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 17 | value | 0.000 | 0 | 0 | 0 | 10948 | 0x2AC4 | float32 | Input Channel 15 Current individual Harmonics 17 percentage | 30-20 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 18 | value | 0.000 | 0 | 0 | 0 | 10950 | 0x2AC6 | float32 | Input Channel 15 Current individual Harmonics 18 percentage | 30-21 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 19 | value | 0.000 | 0 | 0 | 0 | 10952 | 0x2AC8 | float32 | Input Channel 15 Current individual Harmonics 19 percentage | 30-22 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 20 | value | 0.000 | 0 | 0 | 0 | 10954 | 0x2ACA | float32 | Input Channel 15 Current individual Harmonics 20 percentage | 30-23 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 21 | value | 0.000 | 0 | 0 | 0 | 10956 | 0x2ACC | float32 | Input Channel 15 Current individual Harmonics 21 percentage | 30-24 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 22 | value | 0.000 | 0 | 0 | 0 | 10958 | 0x2ACE | float32 | Input Channel 15 Current individual Harmonics 22 percentage | 30-25 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 23 | value | 0.000 | 0 | 0 | 0 | 10960 | 0x2AD0 | float32 | Input Channel 15 Current individual Harmonics 23 percentage | 30-26 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 24 | value | 0.000 | 0 | 0 | 0 | 10962 | 0x2AD2 | float32 | Input Channel 15 Current individual Harmonics 24 percentage | 30-27 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 25 | value | 0.000 | 0 | 0 | 0 | 10964 | 0x2AD4 | float32 | Input Channel 15 Current individual Harmonics 25 percentage | 30-28 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 26 | value | 0.000 | 0 | 0 | 0 | 10966 | 0x2AD6 | float32 | Input Channel 15 Current individual Harmonics 26 percentage | 30-29 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 27 | value | 0.000 | 0 | 0 | 0 | 10968 | 0x2AD8 | float32 | Input Channel 15 Current individual Harmonics 27 percentage | 30-30 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 28 | value | 0.000 | 0 | 0 | 0 | 10970 | 0x2ADA | float32 | Input Channel 15 Current individual Harmonics 28 percentage | 30-31 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 29 | value | 0.000 | 0 | 0 | 0 | 10972 | 0x2ADC | float32 | Input Channel 15 Current individual Harmonics 29 percentage | 30-32 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 30 | value | 0.000 | 0 | 0 | 0 | 10974 | 0x2ADE | float32 | Input Channel 15 Current individual Harmonics 30 percentage | 30-33 | PASS
Acurev4100 | Harmonics | Input Channel 15 | 31 | value | 0.000 | 0 | 0 | 0 | 10976 | 0x2AE0 | float32 | Input Channel 15 Current individual Harmonics 31 percentage | 30-34 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 2 | value | 0.000 | 0 | 0 | 0 | 10986 | 0x2AEA | float32 | Input Channel 16 Current individual Harmonics 2 percentage | 31-5 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 3 | value | 0.000 | 0 | 0 | 0 | 10988 | 0x2AEC | float32 | Input Channel 16 Current individual Harmonics 3 percentage | 31-6 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 4 | value | 0.000 | 0 | 0 | 0 | 10990 | 0x2AEE | float32 | Input Channel 16 Current individual Harmonics 4 percentage | 31-7 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 5 | value | 0.000 | 0 | 0 | 0 | 10992 | 0x2AF0 | float32 | Input Channel 16 Current individual Harmonics 5 percentage | 31-8 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 6 | value | 0.000 | 0 | 0 | 0 | 10994 | 0x2AF2 | float32 | Input Channel 16 Current individual Harmonics 6 percentage | 31-9 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 7 | value | 0.000 | 0 | 0 | 0 | 10996 | 0x2AF4 | float32 | Input Channel 16 Current individual Harmonics 7 percentage | 31-10 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 8 | value | 0.000 | 0 | 0 | 0 | 10998 | 0x2AF6 | float32 | Input Channel 16 Current individual Harmonics 8 percentage | 31-11 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 9 | value | 0.000 | 0 | 0 | 0 | 11000 | 0x2AF8 | float32 | Input Channel 16 Current individual Harmonics 9 percentage | 31-12 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 10 | value | 0.000 | 0 | 0 | 0 | 11002 | 0x2AFA | float32 | Input Channel 16 Current individual Harmonics 10 percentage | 31-13 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 11 | value | 0.000 | 0 | 0 | 0 | 11004 | 0x2AFC | float32 | Input Channel 16 Current individual Harmonics 11 percentage | 31-14 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 12 | value | 0.000 | 0 | 0 | 0 | 11006 | 0x2AFE | float32 | Input Channel 16 Current individual Harmonics 12 percentage | 31-15 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 13 | value | 0.000 | 0 | 0 | 0 | 11008 | 0x2B00 | float32 | Input Channel 16 Current individual Harmonics 13 percentage | 31-16 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 14 | value | 0.000 | 0 | 0 | 0 | 11010 | 0x2B02 | float32 | Input Channel 16 Current individual Harmonics 14 percentage | 31-17 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 15 | value | 0.000 | 0 | 0 | 0 | 11012 | 0x2B04 | float32 | Input Channel 16 Current individual Harmonics 15 percentage | 31-18 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 16 | value | 0.000 | 0 | 0 | 0 | 11014 | 0x2B06 | float32 | Input Channel 16 Current individual Harmonics 16 percentage | 31-19 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 17 | value | 0.000 | 0 | 0 | 0 | 11016 | 0x2B08 | float32 | Input Channel 16 Current individual Harmonics 17 percentage | 31-20 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 18 | value | 0.000 | 0 | 0 | 0 | 11018 | 0x2B0A | float32 | Input Channel 16 Current individual Harmonics 18 percentage | 31-21 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 19 | value | 0.000 | 0 | 0 | 0 | 11020 | 0x2B0C | float32 | Input Channel 16 Current individual Harmonics 19 percentage | 31-22 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 20 | value | 0.000 | 0 | 0 | 0 | 11022 | 0x2B0E | float32 | Input Channel 16 Current individual Harmonics 20 percentage | 31-23 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 21 | value | 0.000 | 0 | 0 | 0 | 11024 | 0x2B10 | float32 | Input Channel 16 Current individual Harmonics 21 percentage | 31-24 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 22 | value | 0.000 | 0 | 0 | 0 | 11026 | 0x2B12 | float32 | Input Channel 16 Current individual Harmonics 22 percentage | 31-25 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 23 | value | 0.000 | 0 | 0 | 0 | 11028 | 0x2B14 | float32 | Input Channel 16 Current individual Harmonics 23 percentage | 31-26 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 24 | value | 0.000 | 0 | 0 | 0 | 11030 | 0x2B16 | float32 | Input Channel 16 Current individual Harmonics 24 percentage | 31-27 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 25 | value | 0.000 | 0 | 0 | 0 | 11032 | 0x2B18 | float32 | Input Channel 16 Current individual Harmonics 25 percentage | 31-28 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 26 | value | 0.000 | 0 | 0 | 0 | 11034 | 0x2B1A | float32 | Input Channel 16 Current individual Harmonics 26 percentage | 31-29 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 27 | value | 0.000 | 0 | 0 | 0 | 11036 | 0x2B1C | float32 | Input Channel 16 Current individual Harmonics 27 percentage | 31-30 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 28 | value | 0.000 | 0 | 0 | 0 | 11038 | 0x2B1E | float32 | Input Channel 16 Current individual Harmonics 28 percentage | 31-31 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 29 | value | 0.000 | 0 | 0 | 0 | 11040 | 0x2B20 | float32 | Input Channel 16 Current individual Harmonics 29 percentage | 31-32 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 30 | value | 0.000 | 0 | 0 | 0 | 11042 | 0x2B22 | float32 | Input Channel 16 Current individual Harmonics 30 percentage | 31-33 | PASS
Acurev4100 | Harmonics | Input Channel 16 | 31 | value | 0.000 | 0 | 0 | 0 | 11044 | 0x2B24 | float32 | Input Channel 16 Current individual Harmonics 31 percentage | 31-34 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 2 | value | 0.000 | 0 | 0 | 0 | 11054 | 0x2B2E | float32 | Input Channel 17 Current individual Harmonics 2 percentage | 32-5 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 3 | value | 0.000 | 0 | 0 | 0 | 11056 | 0x2B30 | float32 | Input Channel 17 Current individual Harmonics 3 percentage | 32-6 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 4 | value | 0.000 | 0 | 0 | 0 | 11058 | 0x2B32 | float32 | Input Channel 17 Current individual Harmonics 4 percentage | 32-7 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 5 | value | 0.000 | 0 | 0 | 0 | 11060 | 0x2B34 | float32 | Input Channel 17 Current individual Harmonics 5 percentage | 32-8 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 6 | value | 0.000 | 0 | 0 | 0 | 11062 | 0x2B36 | float32 | Input Channel 17 Current individual Harmonics 6 percentage | 32-9 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 7 | value | 0.000 | 0 | 0 | 0 | 11064 | 0x2B38 | float32 | Input Channel 17 Current individual Harmonics 7 percentage | 32-10 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 8 | value | 0.000 | 0 | 0 | 0 | 11066 | 0x2B3A | float32 | Input Channel 17 Current individual Harmonics 8 percentage | 32-11 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 9 | value | 0.000 | 0 | 0 | 0 | 11068 | 0x2B3C | float32 | Input Channel 17 Current individual Harmonics 9 percentage | 32-12 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 10 | value | 0.000 | 0 | 0 | 0 | 11070 | 0x2B3E | float32 | Input Channel 17 Current individual Harmonics 10 percentage | 32-13 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 11 | value | 0.000 | 0 | 0 | 0 | 11072 | 0x2B40 | float32 | Input Channel 17 Current individual Harmonics 11 percentage | 32-14 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 12 | value | 0.000 | 0 | 0 | 0 | 11074 | 0x2B42 | float32 | Input Channel 17 Current individual Harmonics 12 percentage | 32-15 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 13 | value | 0.000 | 0 | 0 | 0 | 11076 | 0x2B44 | float32 | Input Channel 17 Current individual Harmonics 13 percentage | 32-16 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 14 | value | 0.000 | 0 | 0 | 0 | 11078 | 0x2B46 | float32 | Input Channel 17 Current individual Harmonics 14 percentage | 32-17 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 15 | value | 0.000 | 0 | 0 | 0 | 11080 | 0x2B48 | float32 | Input Channel 17 Current individual Harmonics 15 percentage | 32-18 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 16 | value | 0.000 | 0 | 0 | 0 | 11082 | 0x2B4A | float32 | Input Channel 17 Current individual Harmonics 16 percentage | 32-19 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 17 | value | 0.000 | 0 | 0 | 0 | 11084 | 0x2B4C | float32 | Input Channel 17 Current individual Harmonics 17 percentage | 32-20 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 18 | value | 0.000 | 0 | 0 | 0 | 11086 | 0x2B4E | float32 | Input Channel 17 Current individual Harmonics 18 percentage | 32-21 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 19 | value | 0.000 | 0 | 0 | 0 | 11088 | 0x2B50 | float32 | Input Channel 17 Current individual Harmonics 19 percentage | 32-22 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 20 | value | 0.000 | 0 | 0 | 0 | 11090 | 0x2B52 | float32 | Input Channel 17 Current individual Harmonics 20 percentage | 32-23 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 21 | value | 0.000 | 0 | 0 | 0 | 11092 | 0x2B54 | float32 | Input Channel 17 Current individual Harmonics 21 percentage | 32-24 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 22 | value | 0.000 | 0 | 0 | 0 | 11094 | 0x2B56 | float32 | Input Channel 17 Current individual Harmonics 22 percentage | 32-25 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 23 | value | 0.000 | 0 | 0 | 0 | 11096 | 0x2B58 | float32 | Input Channel 17 Current individual Harmonics 23 percentage | 32-26 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 24 | value | 0.000 | 0 | 0 | 0 | 11098 | 0x2B5A | float32 | Input Channel 17 Current individual Harmonics 24 percentage | 32-27 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 25 | value | 0.000 | 0 | 0 | 0 | 11100 | 0x2B5C | float32 | Input Channel 17 Current individual Harmonics 25 percentage | 32-28 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 26 | value | 0.000 | 0 | 0 | 0 | 11102 | 0x2B5E | float32 | Input Channel 17 Current individual Harmonics 26 percentage | 32-29 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 27 | value | 0.000 | 0 | 0 | 0 | 11104 | 0x2B60 | float32 | Input Channel 17 Current individual Harmonics 27 percentage | 32-30 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 28 | value | 0.000 | 0 | 0 | 0 | 11106 | 0x2B62 | float32 | Input Channel 17 Current individual Harmonics 28 percentage | 32-31 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 29 | value | 0.000 | 0 | 0 | 0 | 11108 | 0x2B64 | float32 | Input Channel 17 Current individual Harmonics 29 percentage | 32-32 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 30 | value | 0.000 | 0 | 0 | 0 | 11110 | 0x2B66 | float32 | Input Channel 17 Current individual Harmonics 30 percentage | 32-33 | PASS
Acurev4100 | Harmonics | Input Channel 17 | 31 | value | 0.000 | 0 | 0 | 0 | 11112 | 0x2B68 | float32 | Input Channel 17 Current individual Harmonics 31 percentage | 32-34 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 2 | value | 0.000 | 0 | 0 | 0 | 11122 | 0x2B72 | float32 | Input Channel 18 Current individual Harmonics 2 percentage | 33-5 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 3 | value | 0.000 | 0 | 0 | 0 | 11124 | 0x2B74 | float32 | Input Channel 18 Current individual Harmonics 3 percentage | 33-6 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 4 | value | 0.000 | 0 | 0 | 0 | 11126 | 0x2B76 | float32 | Input Channel 18 Current individual Harmonics 4 percentage | 33-7 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 5 | value | 0.000 | 0 | 0 | 0 | 11128 | 0x2B78 | float32 | Input Channel 18 Current individual Harmonics 5 percentage | 33-8 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 6 | value | 0.000 | 0 | 0 | 0 | 11130 | 0x2B7A | float32 | Input Channel 18 Current individual Harmonics 6 percentage | 33-9 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 7 | value | 0.000 | 0 | 0 | 0 | 11132 | 0x2B7C | float32 | Input Channel 18 Current individual Harmonics 7 percentage | 33-10 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 8 | value | 0.000 | 0 | 0 | 0 | 11134 | 0x2B7E | float32 | Input Channel 18 Current individual Harmonics 8 percentage | 33-11 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 9 | value | 0.000 | 0 | 0 | 0 | 11136 | 0x2B80 | float32 | Input Channel 18 Current individual Harmonics 9 percentage | 33-12 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 10 | value | 0.000 | 0 | 0 | 0 | 11138 | 0x2B82 | float32 | Input Channel 18 Current individual Harmonics 10 percentage | 33-13 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 11 | value | 0.000 | 0 | 0 | 0 | 11140 | 0x2B84 | float32 | Input Channel 18 Current individual Harmonics 11 percentage | 33-14 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 12 | value | 0.000 | 0 | 0 | 0 | 11142 | 0x2B86 | float32 | Input Channel 18 Current individual Harmonics 12 percentage | 33-15 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 13 | value | 0.000 | 0 | 0 | 0 | 11144 | 0x2B88 | float32 | Input Channel 18 Current individual Harmonics 13 percentage | 33-16 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 14 | value | 0.000 | 0 | 0 | 0 | 11146 | 0x2B8A | float32 | Input Channel 18 Current individual Harmonics 14 percentage | 33-17 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 15 | value | 0.000 | 0 | 0 | 0 | 11148 | 0x2B8C | float32 | Input Channel 18 Current individual Harmonics 15 percentage | 33-18 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 16 | value | 0.000 | 0 | 0 | 0 | 11150 | 0x2B8E | float32 | Input Channel 18 Current individual Harmonics 16 percentage | 33-19 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 17 | value | 0.000 | 0 | 0 | 0 | 11152 | 0x2B90 | float32 | Input Channel 18 Current individual Harmonics 17 percentage | 33-20 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 18 | value | 0.000 | 0 | 0 | 0 | 11154 | 0x2B92 | float32 | Input Channel 18 Current individual Harmonics 18 percentage | 33-21 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 19 | value | 0.000 | 0 | 0 | 0 | 11156 | 0x2B94 | float32 | Input Channel 18 Current individual Harmonics 19 percentage | 33-22 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 20 | value | 0.000 | 0 | 0 | 0 | 11158 | 0x2B96 | float32 | Input Channel 18 Current individual Harmonics 20 percentage | 33-23 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 21 | value | 0.000 | 0 | 0 | 0 | 11160 | 0x2B98 | float32 | Input Channel 18 Current individual Harmonics 21 percentage | 33-24 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 22 | value | 0.000 | 0 | 0 | 0 | 11162 | 0x2B9A | float32 | Input Channel 18 Current individual Harmonics 22 percentage | 33-25 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 23 | value | 0.000 | 0 | 0 | 0 | 11164 | 0x2B9C | float32 | Input Channel 18 Current individual Harmonics 23 percentage | 33-26 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 24 | value | 0.000 | 0 | 0 | 0 | 11166 | 0x2B9E | float32 | Input Channel 18 Current individual Harmonics 24 percentage | 33-27 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 25 | value | 0.000 | 0 | 0 | 0 | 11168 | 0x2BA0 | float32 | Input Channel 18 Current individual Harmonics 25 percentage | 33-28 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 26 | value | 0.000 | 0 | 0 | 0 | 11170 | 0x2BA2 | float32 | Input Channel 18 Current individual Harmonics 26 percentage | 33-29 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 27 | value | 0.000 | 0 | 0 | 0 | 11172 | 0x2BA4 | float32 | Input Channel 18 Current individual Harmonics 27 percentage | 33-30 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 28 | value | 0.000 | 0 | 0 | 0 | 11174 | 0x2BA6 | float32 | Input Channel 18 Current individual Harmonics 28 percentage | 33-31 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 29 | value | 0.000 | 0 | 0 | 0 | 11176 | 0x2BA8 | float32 | Input Channel 18 Current individual Harmonics 29 percentage | 33-32 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 30 | value | 0.000 | 0 | 0 | 0 | 11178 | 0x2BAA | float32 | Input Channel 18 Current individual Harmonics 30 percentage | 33-33 | PASS
Acurev4100 | Harmonics | Input Channel 18 | 31 | value | 0.000 | 0 | 0 | 0 | 11180 | 0x2BAC | float32 | Input Channel 18 Current individual Harmonics 31 percentage | 33-34 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 2 | value | 0.000 | 0 | 0 | 0 | 11190 | 0x2BB6 | float32 | Input Channel 19 Current individual Harmonics 2 percentage | 34-5 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 3 | value | 0.000 | 0 | 0 | 0 | 11192 | 0x2BB8 | float32 | Input Channel 19 Current individual Harmonics 3 percentage | 34-6 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 4 | value | 0.000 | 0 | 0 | 0 | 11194 | 0x2BBA | float32 | Input Channel 19 Current individual Harmonics 4 percentage | 34-7 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 5 | value | 0.000 | 0 | 0 | 0 | 11196 | 0x2BBC | float32 | Input Channel 19 Current individual Harmonics 5 percentage | 34-8 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 6 | value | 0.000 | 0 | 0 | 0 | 11198 | 0x2BBE | float32 | Input Channel 19 Current individual Harmonics 6 percentage | 34-9 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 7 | value | 0.000 | 0 | 0 | 0 | 11200 | 0x2BC0 | float32 | Input Channel 19 Current individual Harmonics 7 percentage | 34-10 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 8 | value | 0.000 | 0 | 0 | 0 | 11202 | 0x2BC2 | float32 | Input Channel 19 Current individual Harmonics 8 percentage | 34-11 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 9 | value | 0.000 | 0 | 0 | 0 | 11204 | 0x2BC4 | float32 | Input Channel 19 Current individual Harmonics 9 percentage | 34-12 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 10 | value | 0.000 | 0 | 0 | 0 | 11206 | 0x2BC6 | float32 | Input Channel 19 Current individual Harmonics 10 percentage | 34-13 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 11 | value | 0.000 | 0 | 0 | 0 | 11208 | 0x2BC8 | float32 | Input Channel 19 Current individual Harmonics 11 percentage | 34-14 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 12 | value | 0.000 | 0 | 0 | 0 | 11210 | 0x2BCA | float32 | Input Channel 19 Current individual Harmonics 12 percentage | 34-15 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 13 | value | 0.000 | 0 | 0 | 0 | 11212 | 0x2BCC | float32 | Input Channel 19 Current individual Harmonics 13 percentage | 34-16 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 14 | value | 0.000 | 0 | 0 | 0 | 11214 | 0x2BCE | float32 | Input Channel 19 Current individual Harmonics 14 percentage | 34-17 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 15 | value | 0.000 | 0 | 0 | 0 | 11216 | 0x2BD0 | float32 | Input Channel 19 Current individual Harmonics 15 percentage | 34-18 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 16 | value | 0.000 | 0 | 0 | 0 | 11218 | 0x2BD2 | float32 | Input Channel 19 Current individual Harmonics 16 percentage | 34-19 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 17 | value | 0.000 | 0 | 0 | 0 | 11220 | 0x2BD4 | float32 | Input Channel 19 Current individual Harmonics 17 percentage | 34-20 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 18 | value | 0.000 | 0 | 0 | 0 | 11222 | 0x2BD6 | float32 | Input Channel 19 Current individual Harmonics 18 percentage | 34-21 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 19 | value | 0.000 | 0 | 0 | 0 | 11224 | 0x2BD8 | float32 | Input Channel 19 Current individual Harmonics 19 percentage | 34-22 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 20 | value | 0.000 | 0 | 0 | 0 | 11226 | 0x2BDA | float32 | Input Channel 19 Current individual Harmonics 20 percentage | 34-23 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 21 | value | 0.000 | 0 | 0 | 0 | 11228 | 0x2BDC | float32 | Input Channel 19 Current individual Harmonics 21 percentage | 34-24 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 22 | value | 0.000 | 0 | 0 | 0 | 11230 | 0x2BDE | float32 | Input Channel 19 Current individual Harmonics 22 percentage | 34-25 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 23 | value | 0.000 | 0 | 0 | 0 | 11232 | 0x2BE0 | float32 | Input Channel 19 Current individual Harmonics 23 percentage | 34-26 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 24 | value | 0.000 | 0 | 0 | 0 | 11234 | 0x2BE2 | float32 | Input Channel 19 Current individual Harmonics 24 percentage | 34-27 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 25 | value | 0.000 | 0 | 0 | 0 | 11236 | 0x2BE4 | float32 | Input Channel 19 Current individual Harmonics 25 percentage | 34-28 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 26 | value | 0.000 | 0 | 0 | 0 | 11238 | 0x2BE6 | float32 | Input Channel 19 Current individual Harmonics 26 percentage | 34-29 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 27 | value | 0.000 | 0 | 0 | 0 | 11240 | 0x2BE8 | float32 | Input Channel 19 Current individual Harmonics 27 percentage | 34-30 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 28 | value | 0.000 | 0 | 0 | 0 | 11242 | 0x2BEA | float32 | Input Channel 19 Current individual Harmonics 28 percentage | 34-31 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 29 | value | 0.000 | 0 | 0 | 0 | 11244 | 0x2BEC | float32 | Input Channel 19 Current individual Harmonics 29 percentage | 34-32 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 30 | value | 0.000 | 0 | 0 | 0 | 11246 | 0x2BEE | float32 | Input Channel 19 Current individual Harmonics 30 percentage | 34-33 | PASS
Acurev4100 | Harmonics | Input Channel 19 | 31 | value | 0.000 | 0 | 0 | 0 | 11248 | 0x2BF0 | float32 | Input Channel 19 Current individual Harmonics 31 percentage | 34-34 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 2 | value | 0.000 | 0 | 0 | 0 | 11258 | 0x2BFA | float32 | Input Channel 20 Current individual Harmonics 2 percentage | 35-5 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 3 | value | 0.000 | 0 | 0 | 0 | 11260 | 0x2BFC | float32 | Input Channel 20 Current individual Harmonics 3 percentage | 35-6 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 4 | value | 0.000 | 0 | 0 | 0 | 11262 | 0x2BFE | float32 | Input Channel 20 Current individual Harmonics 4 percentage | 35-7 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 5 | value | 0.000 | 0 | 0 | 0 | 11264 | 0x2C00 | float32 | Input Channel 20 Current individual Harmonics 5 percentage | 35-8 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 6 | value | 0.000 | 0 | 0 | 0 | 11266 | 0x2C02 | float32 | Input Channel 20 Current individual Harmonics 6 percentage | 35-9 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 7 | value | 0.000 | 0 | 0 | 0 | 11268 | 0x2C04 | float32 | Input Channel 20 Current individual Harmonics 7 percentage | 35-10 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 8 | value | 0.000 | 0 | 0 | 0 | 11270 | 0x2C06 | float32 | Input Channel 20 Current individual Harmonics 8 percentage | 35-11 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 9 | value | 0.000 | 0 | 0 | 0 | 11272 | 0x2C08 | float32 | Input Channel 20 Current individual Harmonics 9 percentage | 35-12 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 10 | value | 0.000 | 0 | 0 | 0 | 11274 | 0x2C0A | float32 | Input Channel 20 Current individual Harmonics 10 percentage | 35-13 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 11 | value | 0.000 | 0 | 0 | 0 | 11276 | 0x2C0C | float32 | Input Channel 20 Current individual Harmonics 11 percentage | 35-14 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 12 | value | 0.000 | 0 | 0 | 0 | 11278 | 0x2C0E | float32 | Input Channel 20 Current individual Harmonics 12 percentage | 35-15 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 13 | value | 0.000 | 0 | 0 | 0 | 11280 | 0x2C10 | float32 | Input Channel 20 Current individual Harmonics 13 percentage | 35-16 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 14 | value | 0.000 | 0 | 0 | 0 | 11282 | 0x2C12 | float32 | Input Channel 20 Current individual Harmonics 14 percentage | 35-17 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 15 | value | 0.000 | 0 | 0 | 0 | 11284 | 0x2C14 | float32 | Input Channel 20 Current individual Harmonics 15 percentage | 35-18 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 16 | value | 0.000 | 0 | 0 | 0 | 11286 | 0x2C16 | float32 | Input Channel 20 Current individual Harmonics 16 percentage | 35-19 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 17 | value | 0.000 | 0 | 0 | 0 | 11288 | 0x2C18 | float32 | Input Channel 20 Current individual Harmonics 17 percentage | 35-20 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 18 | value | 0.000 | 0 | 0 | 0 | 11290 | 0x2C1A | float32 | Input Channel 20 Current individual Harmonics 18 percentage | 35-21 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 19 | value | 0.000 | 0 | 0 | 0 | 11292 | 0x2C1C | float32 | Input Channel 20 Current individual Harmonics 19 percentage | 35-22 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 20 | value | 0.000 | 0 | 0 | 0 | 11294 | 0x2C1E | float32 | Input Channel 20 Current individual Harmonics 20 percentage | 35-23 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 21 | value | 0.000 | 0 | 0 | 0 | 11296 | 0x2C20 | float32 | Input Channel 20 Current individual Harmonics 21 percentage | 35-24 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 22 | value | 0.000 | 0 | 0 | 0 | 11298 | 0x2C22 | float32 | Input Channel 20 Current individual Harmonics 22 percentage | 35-25 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 23 | value | 0.000 | 0 | 0 | 0 | 11300 | 0x2C24 | float32 | Input Channel 20 Current individual Harmonics 23 percentage | 35-26 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 24 | value | 0.000 | 0 | 0 | 0 | 11302 | 0x2C26 | float32 | Input Channel 20 Current individual Harmonics 24 percentage | 35-27 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 25 | value | 0.000 | 0 | 0 | 0 | 11304 | 0x2C28 | float32 | Input Channel 20 Current individual Harmonics 25 percentage | 35-28 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 26 | value | 0.000 | 0 | 0 | 0 | 11306 | 0x2C2A | float32 | Input Channel 20 Current individual Harmonics 26 percentage | 35-29 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 27 | value | 0.000 | 0 | 0 | 0 | 11308 | 0x2C2C | float32 | Input Channel 20 Current individual Harmonics 27 percentage | 35-30 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 28 | value | 0.000 | 0 | 0 | 0 | 11310 | 0x2C2E | float32 | Input Channel 20 Current individual Harmonics 28 percentage | 35-31 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 29 | value | 0.000 | 0 | 0 | 0 | 11312 | 0x2C30 | float32 | Input Channel 20 Current individual Harmonics 29 percentage | 35-32 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 30 | value | 0.000 | 0 | 0 | 0 | 11314 | 0x2C32 | float32 | Input Channel 20 Current individual Harmonics 30 percentage | 35-33 | PASS
Acurev4100 | Harmonics | Input Channel 20 | 31 | value | 0.000 | 0 | 0 | 0 | 11316 | 0x2C34 | float32 | Input Channel 20 Current individual Harmonics 31 percentage | 35-34 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 2 | value | 0.000 | 0 | 0 | 0 | 11326 | 0x2C3E | float32 | Input Channel 21 Current individual Harmonics 2 percentage | 36-5 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 3 | value | 0.000 | 0 | 0 | 0 | 11328 | 0x2C40 | float32 | Input Channel 21 Current individual Harmonics 3 percentage | 36-6 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 4 | value | 0.000 | 0 | 0 | 0 | 11330 | 0x2C42 | float32 | Input Channel 21 Current individual Harmonics 4 percentage | 36-7 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 5 | value | 0.000 | 0 | 0 | 0 | 11332 | 0x2C44 | float32 | Input Channel 21 Current individual Harmonics 5 percentage | 36-8 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 6 | value | 0.000 | 0 | 0 | 0 | 11334 | 0x2C46 | float32 | Input Channel 21 Current individual Harmonics 6 percentage | 36-9 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 7 | value | 0.000 | 0 | 0 | 0 | 11336 | 0x2C48 | float32 | Input Channel 21 Current individual Harmonics 7 percentage | 36-10 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 8 | value | 0.000 | 0 | 0 | 0 | 11338 | 0x2C4A | float32 | Input Channel 21 Current individual Harmonics 8 percentage | 36-11 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 9 | value | 0.000 | 0 | 0 | 0 | 11340 | 0x2C4C | float32 | Input Channel 21 Current individual Harmonics 9 percentage | 36-12 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 10 | value | 0.000 | 0 | 0 | 0 | 11342 | 0x2C4E | float32 | Input Channel 21 Current individual Harmonics 10 percentage | 36-13 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 11 | value | 0.000 | 0 | 0 | 0 | 11344 | 0x2C50 | float32 | Input Channel 21 Current individual Harmonics 11 percentage | 36-14 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 12 | value | 0.000 | 0 | 0 | 0 | 11346 | 0x2C52 | float32 | Input Channel 21 Current individual Harmonics 12 percentage | 36-15 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 13 | value | 0.000 | 0 | 0 | 0 | 11348 | 0x2C54 | float32 | Input Channel 21 Current individual Harmonics 13 percentage | 36-16 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 14 | value | 0.000 | 0 | 0 | 0 | 11350 | 0x2C56 | float32 | Input Channel 21 Current individual Harmonics 14 percentage | 36-17 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 15 | value | 0.000 | 0 | 0 | 0 | 11352 | 0x2C58 | float32 | Input Channel 21 Current individual Harmonics 15 percentage | 36-18 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 16 | value | 0.000 | 0 | 0 | 0 | 11354 | 0x2C5A | float32 | Input Channel 21 Current individual Harmonics 16 percentage | 36-19 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 17 | value | 0.000 | 0 | 0 | 0 | 11356 | 0x2C5C | float32 | Input Channel 21 Current individual Harmonics 17 percentage | 36-20 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 18 | value | 0.000 | 0 | 0 | 0 | 11358 | 0x2C5E | float32 | Input Channel 21 Current individual Harmonics 18 percentage | 36-21 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 19 | value | 0.000 | 0 | 0 | 0 | 11360 | 0x2C60 | float32 | Input Channel 21 Current individual Harmonics 19 percentage | 36-22 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 20 | value | 0.000 | 0 | 0 | 0 | 11362 | 0x2C62 | float32 | Input Channel 21 Current individual Harmonics 20 percentage | 36-23 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 21 | value | 0.000 | 0 | 0 | 0 | 11364 | 0x2C64 | float32 | Input Channel 21 Current individual Harmonics 21 percentage | 36-24 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 22 | value | 0.000 | 0 | 0 | 0 | 11366 | 0x2C66 | float32 | Input Channel 21 Current individual Harmonics 22 percentage | 36-25 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 23 | value | 0.000 | 0 | 0 | 0 | 11368 | 0x2C68 | float32 | Input Channel 21 Current individual Harmonics 23 percentage | 36-26 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 24 | value | 0.000 | 0 | 0 | 0 | 11370 | 0x2C6A | float32 | Input Channel 21 Current individual Harmonics 24 percentage | 36-27 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 25 | value | 0.000 | 0 | 0 | 0 | 11372 | 0x2C6C | float32 | Input Channel 21 Current individual Harmonics 25 percentage | 36-28 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 26 | value | 0.000 | 0 | 0 | 0 | 11374 | 0x2C6E | float32 | Input Channel 21 Current individual Harmonics 26 percentage | 36-29 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 27 | value | 0.000 | 0 | 0 | 0 | 11376 | 0x2C70 | float32 | Input Channel 21 Current individual Harmonics 27 percentage | 36-30 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 28 | value | 0.000 | 0 | 0 | 0 | 11378 | 0x2C72 | float32 | Input Channel 21 Current individual Harmonics 28 percentage | 36-31 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 29 | value | 0.000 | 0 | 0 | 0 | 11380 | 0x2C74 | float32 | Input Channel 21 Current individual Harmonics 29 percentage | 36-32 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 30 | value | 0.000 | 0 | 0 | 0 | 11382 | 0x2C76 | float32 | Input Channel 21 Current individual Harmonics 30 percentage | 36-33 | PASS
Acurev4100 | Harmonics | Input Channel 21 | 31 | value | 0.000 | 0 | 0 | 0 | 11384 | 0x2C78 | float32 | Input Channel 21 Current individual Harmonics 31 percentage | 36-34 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 2 | value | 0.000 | 0 | 0 | 0 | 11394 | 0x2C82 | float32 | Input Channel 22 Current individual Harmonics 2 percentage | 37-5 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 3 | value | 0.000 | 0 | 0 | 0 | 11396 | 0x2C84 | float32 | Input Channel 22 Current individual Harmonics 3 percentage | 37-6 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 4 | value | 0.000 | 0 | 0 | 0 | 11398 | 0x2C86 | float32 | Input Channel 22 Current individual Harmonics 4 percentage | 37-7 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 5 | value | 0.000 | 0 | 0 | 0 | 11400 | 0x2C88 | float32 | Input Channel 22 Current individual Harmonics 5 percentage | 37-8 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 6 | value | 0.000 | 0 | 0 | 0 | 11402 | 0x2C8A | float32 | Input Channel 22 Current individual Harmonics 6 percentage | 37-9 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 7 | value | 0.000 | 0 | 0 | 0 | 11404 | 0x2C8C | float32 | Input Channel 22 Current individual Harmonics 7 percentage | 37-10 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 8 | value | 0.000 | 0 | 0 | 0 | 11406 | 0x2C8E | float32 | Input Channel 22 Current individual Harmonics 8 percentage | 37-11 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 9 | value | 0.000 | 0 | 0 | 0 | 11408 | 0x2C90 | float32 | Input Channel 22 Current individual Harmonics 9 percentage | 37-12 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 10 | value | 0.000 | 0 | 0 | 0 | 11410 | 0x2C92 | float32 | Input Channel 22 Current individual Harmonics 10 percentage | 37-13 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 11 | value | 0.000 | 0 | 0 | 0 | 11412 | 0x2C94 | float32 | Input Channel 22 Current individual Harmonics 11 percentage | 37-14 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 12 | value | 0.000 | 0 | 0 | 0 | 11414 | 0x2C96 | float32 | Input Channel 22 Current individual Harmonics 12 percentage | 37-15 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 13 | value | 0.000 | 0 | 0 | 0 | 11416 | 0x2C98 | float32 | Input Channel 22 Current individual Harmonics 13 percentage | 37-16 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 14 | value | 0.000 | 0 | 0 | 0 | 11418 | 0x2C9A | float32 | Input Channel 22 Current individual Harmonics 14 percentage | 37-17 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 15 | value | 0.000 | 0 | 0 | 0 | 11420 | 0x2C9C | float32 | Input Channel 22 Current individual Harmonics 15 percentage | 37-18 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 16 | value | 0.000 | 0 | 0 | 0 | 11422 | 0x2C9E | float32 | Input Channel 22 Current individual Harmonics 16 percentage | 37-19 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 17 | value | 0.000 | 0 | 0 | 0 | 11424 | 0x2CA0 | float32 | Input Channel 22 Current individual Harmonics 17 percentage | 37-20 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 18 | value | 0.000 | 0 | 0 | 0 | 11426 | 0x2CA2 | float32 | Input Channel 22 Current individual Harmonics 18 percentage | 37-21 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 19 | value | 0.000 | 0 | 0 | 0 | 11428 | 0x2CA4 | float32 | Input Channel 22 Current individual Harmonics 19 percentage | 37-22 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 20 | value | 0.000 | 0 | 0 | 0 | 11430 | 0x2CA6 | float32 | Input Channel 22 Current individual Harmonics 20 percentage | 37-23 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 21 | value | 0.000 | 0 | 0 | 0 | 11432 | 0x2CA8 | float32 | Input Channel 22 Current individual Harmonics 21 percentage | 37-24 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 22 | value | 0.000 | 0 | 0 | 0 | 11434 | 0x2CAA | float32 | Input Channel 22 Current individual Harmonics 22 percentage | 37-25 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 23 | value | 0.000 | 0 | 0 | 0 | 11436 | 0x2CAC | float32 | Input Channel 22 Current individual Harmonics 23 percentage | 37-26 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 24 | value | 0.000 | 0 | 0 | 0 | 11438 | 0x2CAE | float32 | Input Channel 22 Current individual Harmonics 24 percentage | 37-27 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 25 | value | 0.000 | 0 | 0 | 0 | 11440 | 0x2CB0 | float32 | Input Channel 22 Current individual Harmonics 25 percentage | 37-28 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 26 | value | 0.000 | 0 | 0 | 0 | 11442 | 0x2CB2 | float32 | Input Channel 22 Current individual Harmonics 26 percentage | 37-29 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 27 | value | 0.000 | 0 | 0 | 0 | 11444 | 0x2CB4 | float32 | Input Channel 22 Current individual Harmonics 27 percentage | 37-30 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 28 | value | 0.000 | 0 | 0 | 0 | 11446 | 0x2CB6 | float32 | Input Channel 22 Current individual Harmonics 28 percentage | 37-31 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 29 | value | 0.000 | 0 | 0 | 0 | 11448 | 0x2CB8 | float32 | Input Channel 22 Current individual Harmonics 29 percentage | 37-32 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 30 | value | 0.000 | 0 | 0 | 0 | 11450 | 0x2CBA | float32 | Input Channel 22 Current individual Harmonics 30 percentage | 37-33 | PASS
Acurev4100 | Harmonics | Input Channel 22 | 31 | value | 0.000 | 0 | 0 | 0 | 11452 | 0x2CBC | float32 | Input Channel 22 Current individual Harmonics 31 percentage | 37-34 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 2 | value | 0.000 | 0 | 0 | 0 | 11462 | 0x2CC6 | float32 | Input Channel 23 Current individual Harmonics 2 percentage | 38-5 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 3 | value | 0.000 | 0 | 0 | 0 | 11464 | 0x2CC8 | float32 | Input Channel 23 Current individual Harmonics 3 percentage | 38-6 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 4 | value | 0.000 | 0 | 0 | 0 | 11466 | 0x2CCA | float32 | Input Channel 23 Current individual Harmonics 4 percentage | 38-7 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 5 | value | 0.000 | 0 | 0 | 0 | 11468 | 0x2CCC | float32 | Input Channel 23 Current individual Harmonics 5 percentage | 38-8 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 6 | value | 0.000 | 0 | 0 | 0 | 11470 | 0x2CCE | float32 | Input Channel 23 Current individual Harmonics 6 percentage | 38-9 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 7 | value | 0.000 | 0 | 0 | 0 | 11472 | 0x2CD0 | float32 | Input Channel 23 Current individual Harmonics 7 percentage | 38-10 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 8 | value | 0.000 | 0 | 0 | 0 | 11474 | 0x2CD2 | float32 | Input Channel 23 Current individual Harmonics 8 percentage | 38-11 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 9 | value | 0.000 | 0 | 0 | 0 | 11476 | 0x2CD4 | float32 | Input Channel 23 Current individual Harmonics 9 percentage | 38-12 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 10 | value | 0.000 | 0 | 0 | 0 | 11478 | 0x2CD6 | float32 | Input Channel 23 Current individual Harmonics 10 percentage | 38-13 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 11 | value | 0.000 | 0 | 0 | 0 | 11480 | 0x2CD8 | float32 | Input Channel 23 Current individual Harmonics 11 percentage | 38-14 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 12 | value | 0.000 | 0 | 0 | 0 | 11482 | 0x2CDA | float32 | Input Channel 23 Current individual Harmonics 12 percentage | 38-15 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 13 | value | 0.000 | 0 | 0 | 0 | 11484 | 0x2CDC | float32 | Input Channel 23 Current individual Harmonics 13 percentage | 38-16 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 14 | value | 0.000 | 0 | 0 | 0 | 11486 | 0x2CDE | float32 | Input Channel 23 Current individual Harmonics 14 percentage | 38-17 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 15 | value | 0.000 | 0 | 0 | 0 | 11488 | 0x2CE0 | float32 | Input Channel 23 Current individual Harmonics 15 percentage | 38-18 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 16 | value | 0.000 | 0 | 0 | 0 | 11490 | 0x2CE2 | float32 | Input Channel 23 Current individual Harmonics 16 percentage | 38-19 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 17 | value | 0.000 | 0 | 0 | 0 | 11492 | 0x2CE4 | float32 | Input Channel 23 Current individual Harmonics 17 percentage | 38-20 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 18 | value | 0.000 | 0 | 0 | 0 | 11494 | 0x2CE6 | float32 | Input Channel 23 Current individual Harmonics 18 percentage | 38-21 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 19 | value | 0.000 | 0 | 0 | 0 | 11496 | 0x2CE8 | float32 | Input Channel 23 Current individual Harmonics 19 percentage | 38-22 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 20 | value | 0.000 | 0 | 0 | 0 | 11498 | 0x2CEA | float32 | Input Channel 23 Current individual Harmonics 20 percentage | 38-23 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 21 | value | 0.000 | 0 | 0 | 0 | 11500 | 0x2CEC | float32 | Input Channel 23 Current individual Harmonics 21 percentage | 38-24 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 22 | value | 0.000 | 0 | 0 | 0 | 11502 | 0x2CEE | float32 | Input Channel 23 Current individual Harmonics 22 percentage | 38-25 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 23 | value | 0.000 | 0 | 0 | 0 | 11504 | 0x2CF0 | float32 | Input Channel 23 Current individual Harmonics 23 percentage | 38-26 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 24 | value | 0.000 | 0 | 0 | 0 | 11506 | 0x2CF2 | float32 | Input Channel 23 Current individual Harmonics 24 percentage | 38-27 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 25 | value | 0.000 | 0 | 0 | 0 | 11508 | 0x2CF4 | float32 | Input Channel 23 Current individual Harmonics 25 percentage | 38-28 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 26 | value | 0.000 | 0 | 0 | 0 | 11510 | 0x2CF6 | float32 | Input Channel 23 Current individual Harmonics 26 percentage | 38-29 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 27 | value | 0.000 | 0 | 0 | 0 | 11512 | 0x2CF8 | float32 | Input Channel 23 Current individual Harmonics 27 percentage | 38-30 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 28 | value | 0.000 | 0 | 0 | 0 | 11514 | 0x2CFA | float32 | Input Channel 23 Current individual Harmonics 28 percentage | 38-31 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 29 | value | 0.000 | 0 | 0 | 0 | 11516 | 0x2CFC | float32 | Input Channel 23 Current individual Harmonics 29 percentage | 38-32 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 30 | value | 0.000 | 0 | 0 | 0 | 11518 | 0x2CFE | float32 | Input Channel 23 Current individual Harmonics 30 percentage | 38-33 | PASS
Acurev4100 | Harmonics | Input Channel 23 | 31 | value | 0.000 | 0 | 0 | 0 | 11520 | 0x2D00 | float32 | Input Channel 23 Current individual Harmonics 31 percentage | 38-34 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 2 | value | 0.000 | 0 | 0 | 0 | 11530 | 0x2D0A | float32 | Input Channel 24 Current individual Harmonics 2 percentage | 39-5 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 3 | value | 0.000 | 0 | 0 | 0 | 11532 | 0x2D0C | float32 | Input Channel 24 Current individual Harmonics 3 percentage | 39-6 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 4 | value | 0.000 | 0 | 0 | 0 | 11534 | 0x2D0E | float32 | Input Channel 24 Current individual Harmonics 4 percentage | 39-7 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 5 | value | 0.000 | 0 | 0 | 0 | 11536 | 0x2D10 | float32 | Input Channel 24 Current individual Harmonics 5 percentage | 39-8 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 6 | value | 0.000 | 0 | 0 | 0 | 11538 | 0x2D12 | float32 | Input Channel 24 Current individual Harmonics 6 percentage | 39-9 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 7 | value | 0.000 | 0 | 0 | 0 | 11540 | 0x2D14 | float32 | Input Channel 24 Current individual Harmonics 7 percentage | 39-10 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 8 | value | 0.000 | 0 | 0 | 0 | 11542 | 0x2D16 | float32 | Input Channel 24 Current individual Harmonics 8 percentage | 39-11 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 9 | value | 0.000 | 0 | 0 | 0 | 11544 | 0x2D18 | float32 | Input Channel 24 Current individual Harmonics 9 percentage | 39-12 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 10 | value | 0.000 | 0 | 0 | 0 | 11546 | 0x2D1A | float32 | Input Channel 24 Current individual Harmonics 10 percentage | 39-13 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 11 | value | 0.000 | 0 | 0 | 0 | 11548 | 0x2D1C | float32 | Input Channel 24 Current individual Harmonics 11 percentage | 39-14 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 12 | value | 0.000 | 0 | 0 | 0 | 11550 | 0x2D1E | float32 | Input Channel 24 Current individual Harmonics 12 percentage | 39-15 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 13 | value | 0.000 | 0 | 0 | 0 | 11552 | 0x2D20 | float32 | Input Channel 24 Current individual Harmonics 13 percentage | 39-16 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 14 | value | 0.000 | 0 | 0 | 0 | 11554 | 0x2D22 | float32 | Input Channel 24 Current individual Harmonics 14 percentage | 39-17 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 15 | value | 0.000 | 0 | 0 | 0 | 11556 | 0x2D24 | float32 | Input Channel 24 Current individual Harmonics 15 percentage | 39-18 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 16 | value | 0.000 | 0 | 0 | 0 | 11558 | 0x2D26 | float32 | Input Channel 24 Current individual Harmonics 16 percentage | 39-19 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 17 | value | 0.000 | 0 | 0 | 0 | 11560 | 0x2D28 | float32 | Input Channel 24 Current individual Harmonics 17 percentage | 39-20 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 18 | value | 0.000 | 0 | 0 | 0 | 11562 | 0x2D2A | float32 | Input Channel 24 Current individual Harmonics 18 percentage | 39-21 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 19 | value | 0.000 | 0 | 0 | 0 | 11564 | 0x2D2C | float32 | Input Channel 24 Current individual Harmonics 19 percentage | 39-22 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 20 | value | 0.000 | 0 | 0 | 0 | 11566 | 0x2D2E | float32 | Input Channel 24 Current individual Harmonics 20 percentage | 39-23 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 21 | value | 0.000 | 0 | 0 | 0 | 11568 | 0x2D30 | float32 | Input Channel 24 Current individual Harmonics 21 percentage | 39-24 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 22 | value | 0.000 | 0 | 0 | 0 | 11570 | 0x2D32 | float32 | Input Channel 24 Current individual Harmonics 22 percentage | 39-25 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 23 | value | 0.000 | 0 | 0 | 0 | 11572 | 0x2D34 | float32 | Input Channel 24 Current individual Harmonics 23 percentage | 39-26 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 24 | value | 0.000 | 0 | 0 | 0 | 11574 | 0x2D36 | float32 | Input Channel 24 Current individual Harmonics 24 percentage | 39-27 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 25 | value | 0.000 | 0 | 0 | 0 | 11576 | 0x2D38 | float32 | Input Channel 24 Current individual Harmonics 25 percentage | 39-28 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 26 | value | 0.000 | 0 | 0 | 0 | 11578 | 0x2D3A | float32 | Input Channel 24 Current individual Harmonics 26 percentage | 39-29 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 27 | value | 0.000 | 0 | 0 | 0 | 11580 | 0x2D3C | float32 | Input Channel 24 Current individual Harmonics 27 percentage | 39-30 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 28 | value | 0.000 | 0 | 0 | 0 | 11582 | 0x2D3E | float32 | Input Channel 24 Current individual Harmonics 28 percentage | 39-31 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 29 | value | 0.000 | 0 | 0 | 0 | 11584 | 0x2D40 | float32 | Input Channel 24 Current individual Harmonics 29 percentage | 39-32 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 30 | value | 0.000 | 0 | 0 | 0 | 11586 | 0x2D42 | float32 | Input Channel 24 Current individual Harmonics 30 percentage | 39-33 | PASS
Acurev4100 | Harmonics | Input Channel 24 | 31 | value | 0.000 | 0 | 0 | 0 | 11588 | 0x2D44 | float32 | Input Channel 24 Current individual Harmonics 31 percentage | 39-34 | PASS
Acuvim3 | Realtime | (system) | Line-to-Neutral Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8470 | 0x2116 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
Acuvim3 | Realtime | (system) | Line-to-Neutral Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8472 | 0x2118 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
Acuvim3 | Realtime | (system) | Line-to-Neutral Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8474 | 0x211A | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
Acuvim3 | Realtime | (system) | Line-to-Neutral Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8476 | 0x211C | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
Acuvim3 | Realtime | (system) | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Phase A | 0.000 | 0 | 0 | 0 | 8552 | 0x2168 | float32 | Phase A Line-to-Neutral Voltage Phase Angle | 2-1 | PASS
Acuvim3 | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Phase B | 0.000 | 0 | 0 | 0 | 8554 | 0x216A | float32 | Phase B Line-to-Neutral Voltage Phase Angle | 2-2 | PASS
Acuvim3 | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Phase C | 0.000 | 0 | 0 | 0 | 8556 | 0x216C | float32 | Phase C Line-to-Neutral Voltage Phase Angle | 2-3 | PASS
Acuvim3 | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | Average | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Line-to-Neutral Voltage Phase Angle (°) | System | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Line-to-Line Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8478 | 0x211E | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
Acuvim3 | Realtime | (system) | Line-to-Line Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8480 | 0x2120 | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
Acuvim3 | Realtime | (system) | Line-to-Line Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8482 | 0x2122 | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
Acuvim3 | Realtime | (system) | Line-to-Line Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8484 | 0x2124 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
Acuvim3 | Realtime | (system) | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Line-to-Line Voltage Phase Angle (°) | Phase A | 0.000 | 0 | 0 | 0 | 8478 | 0x211E | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
Acuvim3 | Realtime | (system) | Line-to-Line Voltage Phase Angle (°) | Phase B | 0.000 | 0 | 0 | 0 | 8480 | 0x2120 | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
Acuvim3 | Realtime | (system) | Line-to-Line Voltage Phase Angle (°) | Phase C | 0.000 | 0 | 0 | 0 | 8482 | 0x2122 | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
Acuvim3 | Realtime | (system) | Line-to-Line Voltage Phase Angle (°) | Average | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Line-to-Line Voltage Phase Angle (°) | System | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Current (A) | Phase A | 0.000 | 0 | 0 | 0 | 8650 | 0x21CA | float32 | Phase A Current TDD | 3-25 | PASS
Acuvim3 | Realtime | (system) | Current (A) | Phase B | 0.000 | 0 | 0 | 0 | 8652 | 0x21CC | float32 | Phase B Current TDD | 3-26 | PASS
Acuvim3 | Realtime | (system) | Current (A) | Phase C | 0.000 | 0 | 0 | 0 | 8654 | 0x21CE | float32 | Phase C Current TDD | 3-27 | PASS
Acuvim3 | Realtime | (system) | Current (A) | Average | 0.000 | 0 | 0 | 0 | 8494 | 0x212E | float32 | Average Line Current | 1-14 | PASS
Acuvim3 | Realtime | (system) | Current (A) | System | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Current Phase Angle (°) | Phase A | 0.000 | 0 | 0 | 0 | 8564 | 0x2174 | float32 | Phase A Current Phase Angle | 2-7 | PASS
Acuvim3 | Realtime | (system) | Current Phase Angle (°) | Phase B | 0.000 | 0 | 0 | 0 | 8566 | 0x2176 | float32 | Phase B Current Phase Angle | 2-8 | PASS
Acuvim3 | Realtime | (system) | Current Phase Angle (°) | Phase C | 0.000 | 0 | 0 | 0 | 8568 | 0x2178 | float32 | Phase C Current Phase Angle | 2-9 | PASS
Acuvim3 | Realtime | (system) | Current Phase Angle (°) | Average | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Current Phase Angle (°) | System | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Neutral Current (A) | Phase A | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Neutral Current (A) | Phase B | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Neutral Current (A) | Phase C | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Neutral Current (A) | Average | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Active Power (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8496 | 0x2130 | float32 | Phase A Active Power | 1-15 | PASS
Acuvim3 | Realtime | (system) | Active Power (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8498 | 0x2132 | float32 | Phase B Active Power | 1-16 | PASS
Acuvim3 | Realtime | (system) | Active Power (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8500 | 0x2134 | float32 | Phase C Active Power | 1-17 | PASS
Acuvim3 | Realtime | (system) | Active Power (kW) | Average | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Active Power (kW) | System | 0.000 | 0 | 0 | 0 | 8502 | 0x2136 | float32 | System Active Power | 1-18 | PASS
Acuvim3 | Realtime | (system) | Reactive Power (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8504 | 0x2138 | float32 | Phase A Reactive Power | 1-19 | PASS
Acuvim3 | Realtime | (system) | Reactive Power (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8506 | 0x213A | float32 | Phase B Reactive Power | 1-20 | PASS
Acuvim3 | Realtime | (system) | Reactive Power (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8508 | 0x213C | float32 | Phase C Reactive Power | 1-21 | PASS
Acuvim3 | Realtime | (system) | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Reactive Power (kvar) | System | 0.000 | 0 | 0 | 0 | 8510 | 0x213E | float32 | System Reactive Power | 1-22 | PASS
Acuvim3 | Realtime | (system) | Apparent Power (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8512 | 0x2140 | float32 | Phase A Apparent Power | 1-23 | PASS
Acuvim3 | Realtime | (system) | Apparent Power (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8514 | 0x2142 | float32 | Phase B Apparent Power | 1-24 | PASS
Acuvim3 | Realtime | (system) | Apparent Power (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8516 | 0x2144 | float32 | Phase C Apparent Power | 1-25 | PASS
Acuvim3 | Realtime | (system) | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Apparent Power (kVA) | System | 0.000 | 0 | 0 | 0 | 8518 | 0x2146 | float32 | System Apparent Power | 1-26 | PASS
Acuvim3 | Realtime | (system) | Load Nature | Phase A | e | 0 |  |  | 8520 | 0x2148 | float32 | Phase A Load Nature | 1-27 | N/A
Acuvim3 | Realtime | (system) | Load Nature | Phase B | e | 0 |  |  | 8522 | 0x214A | float32 | Phase B Load Nature | 1-28 | N/A
Acuvim3 | Realtime | (system) | Load Nature | Phase C | e | 0 |  |  | 8524 | 0x214C | float32 | Phase C Load Nature | 1-29 | N/A
Acuvim3 | Realtime | (system) | Load Nature | Average | e | 0 |  |  | 8526 | 0x214E | float32 | System Load Nature | 1-30 | N/A
Acuvim3 | Realtime | (system) | Load Nature | System | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Power Factor | Phase A | 0.000 | 0 | 0 | 0 | 8528 | 0x2150 | float32 | Phase A Power Factor | 1-31 | PASS
Acuvim3 | Realtime | (system) | Power Factor | Phase B | 0.000 | 0 | 0 | 0 | 8530 | 0x2152 | float32 | Phase B Power Factor | 1-32 | PASS
Acuvim3 | Realtime | (system) | Power Factor | Phase C | 0.000 | 0 | 0 | 0 | 8532 | 0x2154 | float32 | Phase C Power Factor | 1-33 | PASS
Acuvim3 | Realtime | (system) | Power Factor | Average | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Power Factor | System | 0.000 | 0 | 0 | 0 | 8534 | 0x2156 | float32 | System Power Factor | 1-34 | PASS
Acuvim3 | Realtime | (system) | Leading Power Factor | Phase A | 0.000 | 0 | 0 | 0 | 8528 | 0x2150 | float32 | Phase A Power Factor | 1-31 | PASS
Acuvim3 | Realtime | (system) | Leading Power Factor | Phase B | 0.000 | 0 | 0 | 0 | 8530 | 0x2152 | float32 | Phase B Power Factor | 1-32 | PASS
Acuvim3 | Realtime | (system) | Leading Power Factor | Phase C | 0.000 | 0 | 0 | 0 | 8532 | 0x2154 | float32 | Phase C Power Factor | 1-33 | PASS
Acuvim3 | Realtime | (system) | Leading Power Factor | Average | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Leading Power Factor | System | 0.000 | 0 | 0 | 0 | 8534 | 0x2156 | float32 | System Power Factor | 1-34 | PASS
Acuvim3 | Realtime | (system) | Lagging Power Factor | Phase A | 0.000 | 0 | 0 | 0 | 8528 | 0x2150 | float32 | Phase A Power Factor | 1-31 | PASS
Acuvim3 | Realtime | (system) | Lagging Power Factor | Phase B | 0.000 | 0 | 0 | 0 | 8530 | 0x2152 | float32 | Phase B Power Factor | 1-32 | PASS
Acuvim3 | Realtime | (system) | Lagging Power Factor | Phase C | 0.000 | 0 | 0 | 0 | 8532 | 0x2154 | float32 | Phase C Power Factor | 1-33 | PASS
Acuvim3 | Realtime | (system) | Lagging Power Factor | Average | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Lagging Power Factor | System | 0.000 | 0 | 0 | 0 | 8534 | 0x2156 | float32 | System Power Factor | 1-34 | PASS
Acuvim3 | Realtime | (system) | Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Frequency (Hz) | Average | - | [8 empty] | 无寄存器
Acuvim3 | Realtime | (system) | Frequency (Hz) | System | 0.000 | 0 | 0 | 0 | 8468 | 0x2114 | float32 | System Frequency | 1-1 | PASS
Acuvim3 | THD | (system) | Voltage THD (%) | Phase A | 0.000 | 0 | 0 | 0 | 8602 | 0x219A | float32 | Phase A Voltage THD | 3-1 | PASS
Acuvim3 | THD | (system) | Voltage THD (%) | Phase B | 0.000 | 0 | 0 | 0 | 8604 | 0x219C | float32 | Phase B Voltage THD | 3-2 | PASS
Acuvim3 | THD | (system) | Voltage THD (%) | Phase C | 0.000 | 0 | 0 | 0 | 8606 | 0x219E | float32 | Phase C Voltage THD | 3-3 | PASS
Acuvim3 | THD | (system) | Voltage THD Odd (%) | Phase A | 0.000 | 0 | 0 | 0 | 8608 | 0x21A0 | float32 | Phase A Voltage THD Odd | 3-4 | PASS
Acuvim3 | THD | (system) | Voltage THD Odd (%) | Phase B | 0.000 | 0 | 0 | 0 | 8610 | 0x21A2 | float32 | Phase B Voltage THD Odd | 3-5 | PASS
Acuvim3 | THD | (system) | Voltage THD Odd (%) | Phase C | 0.000 | 0 | 0 | 0 | 8612 | 0x21A4 | float32 | Phase C Voltage THD Odd | 3-6 | PASS
Acuvim3 | THD | (system) | Voltage THD Even (%) | Phase A | 0.000 | 0 | 0 | 0 | 8614 | 0x21A6 | float32 | Phase A Voltage THD Even | 3-7 | PASS
Acuvim3 | THD | (system) | Voltage THD Even (%) | Phase B | 0.000 | 0 | 0 | 0 | 8616 | 0x21A8 | float32 | Phase B Voltage THD Even | 3-8 | PASS
Acuvim3 | THD | (system) | Voltage THD Even (%) | Phase C | 0.000 | 0 | 0 | 0 | 8618 | 0x21AA | float32 | Phase C Voltage THD Even | 3-9 | PASS
Acuvim3 | THD | (system) | Voltage Crest Factor | Phase A | 0.000 | 0 | 0 | 0 | 8620 | 0x21AC | float32 | Phase A Voltage Crest Factor | 3-10 | PASS
Acuvim3 | THD | (system) | Voltage Crest Factor | Phase B | 0.000 | 0 | 0 | 0 | 8622 | 0x21AE | float32 | Phase B Voltage Crest Factor | 3-11 | PASS
Acuvim3 | THD | (system) | Voltage Crest Factor | Phase C | 0.000 | 0 | 0 | 0 | 8624 | 0x21B0 | float32 | Phase C Voltage Crest Factor | 3-12 | PASS
Acuvim3 | THD | (system) | Current THD (%) | Phase A | 0.000 | 0 | 0 | 0 | 8626 | 0x21B2 | float32 | Phase A Current THD | 3-13 | PASS
Acuvim3 | THD | (system) | Current THD (%) | Phase B | 0.000 | 0 | 0 | 0 | 8628 | 0x21B4 | float32 | Phase B Current THD | 3-14 | PASS
Acuvim3 | THD | (system) | Current THD (%) | Phase C | 0.000 | 0 | 0 | 0 | 8630 | 0x21B6 | float32 | Phase C Current THD | 3-15 | PASS
Acuvim3 | THD | (system) | Current THD Odd (%) | Phase A | 0.000 | 0 | 0 | 0 | 8634 | 0x21BA | float32 | Phase A Current THD Odd | 3-17 | PASS
Acuvim3 | THD | (system) | Current THD Odd (%) | Phase B | 0.000 | 0 | 0 | 0 | 8636 | 0x21BC | float32 | Phase B Current THD Odd | 3-18 | PASS
Acuvim3 | THD | (system) | Current THD Odd (%) | Phase C | 0.000 | 0 | 0 | 0 | 8638 | 0x21BE | float32 | Phase C Current THD Odd | 3-19 | PASS
Acuvim3 | THD | (system) | Current THD Even (%) | Phase A | 0.000 | 0 | 0 | 0 | 8642 | 0x21C2 | float32 | Phase A Current THD Even | 3-21 | PASS
Acuvim3 | THD | (system) | Current THD Even (%) | Phase B | 0.000 | 0 | 0 | 0 | 8644 | 0x21C4 | float32 | Phase B Current THD Even | 3-22 | PASS
Acuvim3 | THD | (system) | Current THD Even (%) | Phase C | 0.000 | 0 | 0 | 0 | 8646 | 0x21C6 | float32 | Phase C Current THD Even | 3-23 | PASS
Acuvim3 | THD | (system) | Current TDD (%) | Phase A | 0.000 | 0 | 0 | 0 | 8650 | 0x21CA | float32 | Phase A Current TDD | 3-25 | PASS
Acuvim3 | THD | (system) | Current TDD (%) | Phase B | 0.000 | 0 | 0 | 0 | 8652 | 0x21CC | float32 | Phase B Current TDD | 3-26 | PASS
Acuvim3 | THD | (system) | Current TDD (%) | Phase C | 0.000 | 0 | 0 | 0 | 8654 | 0x21CE | float32 | Phase C Current TDD | 3-27 | PASS
Acuvim3 | THD | (system) | Current Crest-Factor | Phase A | 0.000 | 0 | 0 | 0 | 8650 | 0x21CA | float32 | Phase A Current TDD | 3-25 | PASS
Acuvim3 | THD | (system) | Current Crest-Factor | Phase B | 0.000 | 0 | 0 | 0 | 8652 | 0x21CC | float32 | Phase B Current TDD | 3-26 | PASS
Acuvim3 | THD | (system) | Current Crest-Factor | Phase C | 0.000 | 0 | 0 | 0 | 8654 | 0x21CE | float32 | Phase C Current TDD | 3-27 | PASS
Acuvim3 | THD | (system) | Current K-Factor | Phase A | 0.000 | 0 | 0 | 0 | 8666 | 0x21DA | float32 | Phase A Current K-Factor | 3-33 | PASS
Acuvim3 | THD | (system) | Current K-Factor | Phase B | 0.000 | 0 | 0 | 0 | 8668 | 0x21DC | float32 | Phase B Current K-Factor | 3-34 | PASS
Acuvim3 | THD | (system) | Current K-Factor | Phase C | 0.000 | 0 | 0 | 0 | 8670 | 0x21DE | float32 | Phase C Current K-Factor | 3-35 | PASS
AcuRev2100 | Realtime | 1 | Line-to-Neutral Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8194 | 0x2002 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
AcuRev2100 | Realtime | 1 | Line-to-Neutral Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8196 | 0x2004 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
AcuRev2100 | Realtime | 1 | Line-to-Neutral Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8198 | 0x2006 | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
AcuRev2100 | Realtime | 1 | Line-to-Neutral Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8200 | 0x2008 | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
AcuRev2100 | Realtime | 1 | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Line-to-Line Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8202 | 0x200A | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
AcuRev2100 | Realtime | 1 | Line-to-Line Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8204 | 0x200C | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
AcuRev2100 | Realtime | 1 | Line-to-Line Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8206 | 0x200E | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
AcuRev2100 | Realtime | 1 | Line-to-Line Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8208 | 0x2010 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
AcuRev2100 | Realtime | 1 | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Current (A) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Active Power (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8228 | 0x2024 | float32 | Phase A Active Power | 1-19 | PASS
AcuRev2100 | Realtime | 1 | Active Power (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8230 | 0x2026 | float32 | Phase B Active Power | 1-20 | PASS
AcuRev2100 | Realtime | 1 | Active Power (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8232 | 0x2028 | float32 | Phase C Active Power | 1-21 | PASS
AcuRev2100 | Realtime | 1 | Active Power (kW) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Active Power (kW) | System | 0.000 | 0 | 0 | 0 | 8218 | 0x201A | float32 | System Active Power | 1-14 | PASS
AcuRev2100 | Realtime | 1 | Reactive Power (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8234 | 0x202A | float32 | Phase A Reactive Power | 1-22 | PASS
AcuRev2100 | Realtime | 1 | Reactive Power (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8236 | 0x202C | float32 | Phase B Reactive Power | 1-23 | PASS
AcuRev2100 | Realtime | 1 | Reactive Power (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8238 | 0x202E | float32 | Phase C Reactive Power | 1-24 | PASS
AcuRev2100 | Realtime | 1 | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Reactive Power (kvar) | System | 0.000 | 0 | 0 | 0 | 8220 | 0x201C | float32 | System Reactive Power | 1-15 | PASS
AcuRev2100 | Realtime | 1 | Apparent Power (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8240 | 0x2030 | float32 | Phase A Apparent Power | 1-25 | PASS
AcuRev2100 | Realtime | 1 | Apparent Power (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8242 | 0x2032 | float32 | Phase B Apparent Power | 1-26 | PASS
AcuRev2100 | Realtime | 1 | Apparent Power (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8244 | 0x2034 | float32 | Phase C Apparent Power | 1-27 | PASS
AcuRev2100 | Realtime | 1 | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Apparent Power (kVA) | System | 0.000 | 0 | 0 | 0 | 8222 | 0x201E | float32 | System Apparent Power | 1-16 | PASS
AcuRev2100 | Realtime | 1 | Load Nature | Phase A | R | 1 |  |  | 8252 | 0x203C | float32 | Phase A Load Nature | 1-31 | N/A
AcuRev2100 | Realtime | 1 | Load Nature | Phase B | R | 1 |  |  | 8254 | 0x203E | float32 | Phase B Load Nature | 1-32 | N/A
AcuRev2100 | Realtime | 1 | Load Nature | Phase C | R | 1 |  |  | 8256 | 0x2040 | float32 | Phase C Load Nature | 1-33 | N/A
AcuRev2100 | Realtime | 1 | Load Nature | Average | R | 1 |  |  | 8226 | 0x2022 | float32 | Average Load Nature | 1-18 | N/A
AcuRev2100 | Realtime | 1 | Load Nature | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Power Factor | Phase A | 1.000 | 1 | 0 | 0 | 8246 | 0x2036 | float32 | Phase A Power Factor | 1-28 | PASS
AcuRev2100 | Realtime | 1 | Power Factor | Phase B | 1.000 | 1 | 0 | 0 | 8248 | 0x2038 | float32 | Phase B Power Factor | 1-29 | PASS
AcuRev2100 | Realtime | 1 | Power Factor | Phase C | 1.000 | 1 | 0 | 0 | 8250 | 0x203A | float32 | Phase C Power Factor | 1-30 | PASS
AcuRev2100 | Realtime | 1 | Power Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Power Factor | System | 1.000 | 1 | 0 | 0 | 8224 | 0x2020 | float32 | System Power Factor | 1-17 | PASS
AcuRev2100 | Realtime | 1 | Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Frequency (Hz) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Frequency (Hz) | System | 0.000 | 0 | 0 | 0 | 8192 | 0x2000 | float32 | System Frequency | 1-1 | PASS
AcuRev2100 | Realtime | 1 | Current Phase Angle (°) | Phase A | 310.000 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Current Phase Angle (°) | Phase B | 284.000 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 1 | Current Phase Angle (°) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Line-to-Neutral Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8194 | 0x2002 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
AcuRev2100 | Realtime | 2 | Line-to-Neutral Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8196 | 0x2004 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
AcuRev2100 | Realtime | 2 | Line-to-Neutral Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8198 | 0x2006 | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
AcuRev2100 | Realtime | 2 | Line-to-Neutral Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8200 | 0x2008 | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
AcuRev2100 | Realtime | 2 | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Line-to-Line Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8202 | 0x200A | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
AcuRev2100 | Realtime | 2 | Line-to-Line Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8204 | 0x200C | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
AcuRev2100 | Realtime | 2 | Line-to-Line Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8206 | 0x200E | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
AcuRev2100 | Realtime | 2 | Line-to-Line Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8208 | 0x2010 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
AcuRev2100 | Realtime | 2 | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Current (A) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Active Power (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8228 | 0x2024 | float32 | Phase A Active Power | 1-19 | PASS
AcuRev2100 | Realtime | 2 | Active Power (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8230 | 0x2026 | float32 | Phase B Active Power | 1-20 | PASS
AcuRev2100 | Realtime | 2 | Active Power (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8232 | 0x2028 | float32 | Phase C Active Power | 1-21 | PASS
AcuRev2100 | Realtime | 2 | Active Power (kW) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Active Power (kW) | System | 0.000 | 0 | 0 | 0 | 8218 | 0x201A | float32 | System Active Power | 1-14 | PASS
AcuRev2100 | Realtime | 2 | Reactive Power (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8234 | 0x202A | float32 | Phase A Reactive Power | 1-22 | PASS
AcuRev2100 | Realtime | 2 | Reactive Power (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8236 | 0x202C | float32 | Phase B Reactive Power | 1-23 | PASS
AcuRev2100 | Realtime | 2 | Reactive Power (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8238 | 0x202E | float32 | Phase C Reactive Power | 1-24 | PASS
AcuRev2100 | Realtime | 2 | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Reactive Power (kvar) | System | 0.000 | 0 | 0 | 0 | 8220 | 0x201C | float32 | System Reactive Power | 1-15 | PASS
AcuRev2100 | Realtime | 2 | Apparent Power (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8240 | 0x2030 | float32 | Phase A Apparent Power | 1-25 | PASS
AcuRev2100 | Realtime | 2 | Apparent Power (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8242 | 0x2032 | float32 | Phase B Apparent Power | 1-26 | PASS
AcuRev2100 | Realtime | 2 | Apparent Power (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8244 | 0x2034 | float32 | Phase C Apparent Power | 1-27 | PASS
AcuRev2100 | Realtime | 2 | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Apparent Power (kVA) | System | 0.000 | 0 | 0 | 0 | 8222 | 0x201E | float32 | System Apparent Power | 1-16 | PASS
AcuRev2100 | Realtime | 2 | Load Nature | Phase A | R | 1 |  |  | 8252 | 0x203C | float32 | Phase A Load Nature | 1-31 | N/A
AcuRev2100 | Realtime | 2 | Load Nature | Phase B | R | 1 |  |  | 8254 | 0x203E | float32 | Phase B Load Nature | 1-32 | N/A
AcuRev2100 | Realtime | 2 | Load Nature | Phase C | R | 1 |  |  | 8256 | 0x2040 | float32 | Phase C Load Nature | 1-33 | N/A
AcuRev2100 | Realtime | 2 | Load Nature | Average | R | 1 |  |  | 8226 | 0x2022 | float32 | Average Load Nature | 1-18 | N/A
AcuRev2100 | Realtime | 2 | Load Nature | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Power Factor | Phase A | 1.000 | 1 | 0 | 0 | 8246 | 0x2036 | float32 | Phase A Power Factor | 1-28 | PASS
AcuRev2100 | Realtime | 2 | Power Factor | Phase B | 1.000 | 1 | 0 | 0 | 8248 | 0x2038 | float32 | Phase B Power Factor | 1-29 | PASS
AcuRev2100 | Realtime | 2 | Power Factor | Phase C | 1.000 | 1 | 0 | 0 | 8250 | 0x203A | float32 | Phase C Power Factor | 1-30 | PASS
AcuRev2100 | Realtime | 2 | Power Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Power Factor | System | 1.000 | 1 | 0 | 0 | 8224 | 0x2020 | float32 | System Power Factor | 1-17 | PASS
AcuRev2100 | Realtime | 2 | Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Frequency (Hz) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Frequency (Hz) | System | 0.000 | 0 | 0 | 0 | 8192 | 0x2000 | float32 | System Frequency | 1-1 | PASS
AcuRev2100 | Realtime | 2 | Current Phase Angle (°) | Phase A | 310.500 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Current Phase Angle (°) | Phase C | 314.900 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 2 | Current Phase Angle (°) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Line-to-Neutral Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8194 | 0x2002 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
AcuRev2100 | Realtime | 3 | Line-to-Neutral Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8196 | 0x2004 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
AcuRev2100 | Realtime | 3 | Line-to-Neutral Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8198 | 0x2006 | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
AcuRev2100 | Realtime | 3 | Line-to-Neutral Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8200 | 0x2008 | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
AcuRev2100 | Realtime | 3 | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Line-to-Line Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8202 | 0x200A | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
AcuRev2100 | Realtime | 3 | Line-to-Line Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8204 | 0x200C | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
AcuRev2100 | Realtime | 3 | Line-to-Line Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8206 | 0x200E | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
AcuRev2100 | Realtime | 3 | Line-to-Line Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8208 | 0x2010 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
AcuRev2100 | Realtime | 3 | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Current (A) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Active Power (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8228 | 0x2024 | float32 | Phase A Active Power | 1-19 | PASS
AcuRev2100 | Realtime | 3 | Active Power (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8230 | 0x2026 | float32 | Phase B Active Power | 1-20 | PASS
AcuRev2100 | Realtime | 3 | Active Power (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8232 | 0x2028 | float32 | Phase C Active Power | 1-21 | PASS
AcuRev2100 | Realtime | 3 | Active Power (kW) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Active Power (kW) | System | 0.000 | 0 | 0 | 0 | 8218 | 0x201A | float32 | System Active Power | 1-14 | PASS
AcuRev2100 | Realtime | 3 | Reactive Power (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8234 | 0x202A | float32 | Phase A Reactive Power | 1-22 | PASS
AcuRev2100 | Realtime | 3 | Reactive Power (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8236 | 0x202C | float32 | Phase B Reactive Power | 1-23 | PASS
AcuRev2100 | Realtime | 3 | Reactive Power (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8238 | 0x202E | float32 | Phase C Reactive Power | 1-24 | PASS
AcuRev2100 | Realtime | 3 | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Reactive Power (kvar) | System | 0.000 | 0 | 0 | 0 | 8220 | 0x201C | float32 | System Reactive Power | 1-15 | PASS
AcuRev2100 | Realtime | 3 | Apparent Power (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8240 | 0x2030 | float32 | Phase A Apparent Power | 1-25 | PASS
AcuRev2100 | Realtime | 3 | Apparent Power (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8242 | 0x2032 | float32 | Phase B Apparent Power | 1-26 | PASS
AcuRev2100 | Realtime | 3 | Apparent Power (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8244 | 0x2034 | float32 | Phase C Apparent Power | 1-27 | PASS
AcuRev2100 | Realtime | 3 | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Apparent Power (kVA) | System | 0.000 | 0 | 0 | 0 | 8222 | 0x201E | float32 | System Apparent Power | 1-16 | PASS
AcuRev2100 | Realtime | 3 | Load Nature | Phase A | R | 1 |  |  | 8252 | 0x203C | float32 | Phase A Load Nature | 1-31 | N/A
AcuRev2100 | Realtime | 3 | Load Nature | Phase B | R | 1 |  |  | 8254 | 0x203E | float32 | Phase B Load Nature | 1-32 | N/A
AcuRev2100 | Realtime | 3 | Load Nature | Phase C | R | 1 |  |  | 8256 | 0x2040 | float32 | Phase C Load Nature | 1-33 | N/A
AcuRev2100 | Realtime | 3 | Load Nature | Average | R | 1 |  |  | 8226 | 0x2022 | float32 | Average Load Nature | 1-18 | N/A
AcuRev2100 | Realtime | 3 | Load Nature | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Power Factor | Phase A | 1.000 | 1 | 0 | 0 | 8246 | 0x2036 | float32 | Phase A Power Factor | 1-28 | PASS
AcuRev2100 | Realtime | 3 | Power Factor | Phase B | 1.000 | 1 | 0 | 0 | 8248 | 0x2038 | float32 | Phase B Power Factor | 1-29 | PASS
AcuRev2100 | Realtime | 3 | Power Factor | Phase C | 1.000 | 1 | 0 | 0 | 8250 | 0x203A | float32 | Phase C Power Factor | 1-30 | PASS
AcuRev2100 | Realtime | 3 | Power Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Power Factor | System | 1.000 | 1 | 0 | 0 | 8224 | 0x2020 | float32 | System Power Factor | 1-17 | PASS
AcuRev2100 | Realtime | 3 | Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Frequency (Hz) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Frequency (Hz) | System | 0.000 | 0 | 0 | 0 | 8192 | 0x2000 | float32 | System Frequency | 1-1 | PASS
AcuRev2100 | Realtime | 3 | Current Phase Angle (°) | Phase B | 306.900 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Current Phase Angle (°) | Phase C | 329.700 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 3 | Current Phase Angle (°) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Line-to-Neutral Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8194 | 0x2002 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
AcuRev2100 | Realtime | 4 | Line-to-Neutral Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8196 | 0x2004 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
AcuRev2100 | Realtime | 4 | Line-to-Neutral Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8198 | 0x2006 | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
AcuRev2100 | Realtime | 4 | Line-to-Neutral Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8200 | 0x2008 | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
AcuRev2100 | Realtime | 4 | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Line-to-Line Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8202 | 0x200A | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
AcuRev2100 | Realtime | 4 | Line-to-Line Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8204 | 0x200C | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
AcuRev2100 | Realtime | 4 | Line-to-Line Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8206 | 0x200E | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
AcuRev2100 | Realtime | 4 | Line-to-Line Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8208 | 0x2010 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
AcuRev2100 | Realtime | 4 | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Current (A) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Active Power (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8228 | 0x2024 | float32 | Phase A Active Power | 1-19 | PASS
AcuRev2100 | Realtime | 4 | Active Power (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8230 | 0x2026 | float32 | Phase B Active Power | 1-20 | PASS
AcuRev2100 | Realtime | 4 | Active Power (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8232 | 0x2028 | float32 | Phase C Active Power | 1-21 | PASS
AcuRev2100 | Realtime | 4 | Active Power (kW) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Active Power (kW) | System | 0.000 | 0 | 0 | 0 | 8218 | 0x201A | float32 | System Active Power | 1-14 | PASS
AcuRev2100 | Realtime | 4 | Reactive Power (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8234 | 0x202A | float32 | Phase A Reactive Power | 1-22 | PASS
AcuRev2100 | Realtime | 4 | Reactive Power (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8236 | 0x202C | float32 | Phase B Reactive Power | 1-23 | PASS
AcuRev2100 | Realtime | 4 | Reactive Power (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8238 | 0x202E | float32 | Phase C Reactive Power | 1-24 | PASS
AcuRev2100 | Realtime | 4 | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Reactive Power (kvar) | System | 0.000 | 0 | 0 | 0 | 8220 | 0x201C | float32 | System Reactive Power | 1-15 | PASS
AcuRev2100 | Realtime | 4 | Apparent Power (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8240 | 0x2030 | float32 | Phase A Apparent Power | 1-25 | PASS
AcuRev2100 | Realtime | 4 | Apparent Power (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8242 | 0x2032 | float32 | Phase B Apparent Power | 1-26 | PASS
AcuRev2100 | Realtime | 4 | Apparent Power (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8244 | 0x2034 | float32 | Phase C Apparent Power | 1-27 | PASS
AcuRev2100 | Realtime | 4 | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Apparent Power (kVA) | System | 0.000 | 0 | 0 | 0 | 8222 | 0x201E | float32 | System Apparent Power | 1-16 | PASS
AcuRev2100 | Realtime | 4 | Load Nature | Phase A | R | 1 |  |  | 8252 | 0x203C | float32 | Phase A Load Nature | 1-31 | N/A
AcuRev2100 | Realtime | 4 | Load Nature | Phase B | R | 1 |  |  | 8254 | 0x203E | float32 | Phase B Load Nature | 1-32 | N/A
AcuRev2100 | Realtime | 4 | Load Nature | Phase C | R | 1 |  |  | 8256 | 0x2040 | float32 | Phase C Load Nature | 1-33 | N/A
AcuRev2100 | Realtime | 4 | Load Nature | Average | R | 1 |  |  | 8226 | 0x2022 | float32 | Average Load Nature | 1-18 | N/A
AcuRev2100 | Realtime | 4 | Load Nature | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Power Factor | Phase A | 1.000 | 1 | 0 | 0 | 8246 | 0x2036 | float32 | Phase A Power Factor | 1-28 | PASS
AcuRev2100 | Realtime | 4 | Power Factor | Phase B | 1.000 | 1 | 0 | 0 | 8248 | 0x2038 | float32 | Phase B Power Factor | 1-29 | PASS
AcuRev2100 | Realtime | 4 | Power Factor | Phase C | 1.000 | 1 | 0 | 0 | 8250 | 0x203A | float32 | Phase C Power Factor | 1-30 | PASS
AcuRev2100 | Realtime | 4 | Power Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Power Factor | System | 1.000 | 1 | 0 | 0 | 8224 | 0x2020 | float32 | System Power Factor | 1-17 | PASS
AcuRev2100 | Realtime | 4 | Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Frequency (Hz) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Frequency (Hz) | System | 0.000 | 0 | 0 | 0 | 8192 | 0x2000 | float32 | System Frequency | 1-1 | PASS
AcuRev2100 | Realtime | 4 | Current Phase Angle (°) | Phase A | 327.100 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Current Phase Angle (°) | Phase B | 292.500 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 4 | Current Phase Angle (°) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Line-to-Neutral Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8194 | 0x2002 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
AcuRev2100 | Realtime | 5 | Line-to-Neutral Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8196 | 0x2004 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
AcuRev2100 | Realtime | 5 | Line-to-Neutral Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8198 | 0x2006 | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
AcuRev2100 | Realtime | 5 | Line-to-Neutral Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8200 | 0x2008 | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
AcuRev2100 | Realtime | 5 | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Line-to-Line Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8202 | 0x200A | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
AcuRev2100 | Realtime | 5 | Line-to-Line Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8204 | 0x200C | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
AcuRev2100 | Realtime | 5 | Line-to-Line Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8206 | 0x200E | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
AcuRev2100 | Realtime | 5 | Line-to-Line Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8208 | 0x2010 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
AcuRev2100 | Realtime | 5 | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Current (A) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Active Power (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8228 | 0x2024 | float32 | Phase A Active Power | 1-19 | PASS
AcuRev2100 | Realtime | 5 | Active Power (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8230 | 0x2026 | float32 | Phase B Active Power | 1-20 | PASS
AcuRev2100 | Realtime | 5 | Active Power (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8232 | 0x2028 | float32 | Phase C Active Power | 1-21 | PASS
AcuRev2100 | Realtime | 5 | Active Power (kW) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Active Power (kW) | System | 0.000 | 0 | 0 | 0 | 8218 | 0x201A | float32 | System Active Power | 1-14 | PASS
AcuRev2100 | Realtime | 5 | Reactive Power (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8234 | 0x202A | float32 | Phase A Reactive Power | 1-22 | PASS
AcuRev2100 | Realtime | 5 | Reactive Power (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8236 | 0x202C | float32 | Phase B Reactive Power | 1-23 | PASS
AcuRev2100 | Realtime | 5 | Reactive Power (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8238 | 0x202E | float32 | Phase C Reactive Power | 1-24 | PASS
AcuRev2100 | Realtime | 5 | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Reactive Power (kvar) | System | 0.000 | 0 | 0 | 0 | 8220 | 0x201C | float32 | System Reactive Power | 1-15 | PASS
AcuRev2100 | Realtime | 5 | Apparent Power (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8240 | 0x2030 | float32 | Phase A Apparent Power | 1-25 | PASS
AcuRev2100 | Realtime | 5 | Apparent Power (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8242 | 0x2032 | float32 | Phase B Apparent Power | 1-26 | PASS
AcuRev2100 | Realtime | 5 | Apparent Power (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8244 | 0x2034 | float32 | Phase C Apparent Power | 1-27 | PASS
AcuRev2100 | Realtime | 5 | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Apparent Power (kVA) | System | 0.000 | 0 | 0 | 0 | 8222 | 0x201E | float32 | System Apparent Power | 1-16 | PASS
AcuRev2100 | Realtime | 5 | Load Nature | Phase A | R | 1 |  |  | 8252 | 0x203C | float32 | Phase A Load Nature | 1-31 | N/A
AcuRev2100 | Realtime | 5 | Load Nature | Phase B | R | 1 |  |  | 8254 | 0x203E | float32 | Phase B Load Nature | 1-32 | N/A
AcuRev2100 | Realtime | 5 | Load Nature | Phase C | R | 1 |  |  | 8256 | 0x2040 | float32 | Phase C Load Nature | 1-33 | N/A
AcuRev2100 | Realtime | 5 | Load Nature | Average | R | 1 |  |  | 8226 | 0x2022 | float32 | Average Load Nature | 1-18 | N/A
AcuRev2100 | Realtime | 5 | Load Nature | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Power Factor | Phase A | 1.000 | 1 | 0 | 0 | 8246 | 0x2036 | float32 | Phase A Power Factor | 1-28 | PASS
AcuRev2100 | Realtime | 5 | Power Factor | Phase B | 1.000 | 1 | 0 | 0 | 8248 | 0x2038 | float32 | Phase B Power Factor | 1-29 | PASS
AcuRev2100 | Realtime | 5 | Power Factor | Phase C | 1.000 | 1 | 0 | 0 | 8250 | 0x203A | float32 | Phase C Power Factor | 1-30 | PASS
AcuRev2100 | Realtime | 5 | Power Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Power Factor | System | 1.000 | 1 | 0 | 0 | 8224 | 0x2020 | float32 | System Power Factor | 1-17 | PASS
AcuRev2100 | Realtime | 5 | Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Frequency (Hz) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Frequency (Hz) | System | 0.000 | 0 | 0 | 0 | 8192 | 0x2000 | float32 | System Frequency | 1-1 | PASS
AcuRev2100 | Realtime | 5 | Current Phase Angle (°) | Phase A | 286.800 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Current Phase Angle (°) | Phase C | 308.700 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 5 | Current Phase Angle (°) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Line-to-Neutral Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8194 | 0x2002 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
AcuRev2100 | Realtime | 6 | Line-to-Neutral Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8196 | 0x2004 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
AcuRev2100 | Realtime | 6 | Line-to-Neutral Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8198 | 0x2006 | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
AcuRev2100 | Realtime | 6 | Line-to-Neutral Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8200 | 0x2008 | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
AcuRev2100 | Realtime | 6 | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Line-to-Line Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8202 | 0x200A | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
AcuRev2100 | Realtime | 6 | Line-to-Line Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8204 | 0x200C | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
AcuRev2100 | Realtime | 6 | Line-to-Line Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8206 | 0x200E | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
AcuRev2100 | Realtime | 6 | Line-to-Line Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8208 | 0x2010 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
AcuRev2100 | Realtime | 6 | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Current (A) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Active Power (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8228 | 0x2024 | float32 | Phase A Active Power | 1-19 | PASS
AcuRev2100 | Realtime | 6 | Active Power (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8230 | 0x2026 | float32 | Phase B Active Power | 1-20 | PASS
AcuRev2100 | Realtime | 6 | Active Power (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8232 | 0x2028 | float32 | Phase C Active Power | 1-21 | PASS
AcuRev2100 | Realtime | 6 | Active Power (kW) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Active Power (kW) | System | 0.000 | 0 | 0 | 0 | 8218 | 0x201A | float32 | System Active Power | 1-14 | PASS
AcuRev2100 | Realtime | 6 | Reactive Power (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8234 | 0x202A | float32 | Phase A Reactive Power | 1-22 | PASS
AcuRev2100 | Realtime | 6 | Reactive Power (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8236 | 0x202C | float32 | Phase B Reactive Power | 1-23 | PASS
AcuRev2100 | Realtime | 6 | Reactive Power (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8238 | 0x202E | float32 | Phase C Reactive Power | 1-24 | PASS
AcuRev2100 | Realtime | 6 | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Reactive Power (kvar) | System | 0.000 | 0 | 0 | 0 | 8220 | 0x201C | float32 | System Reactive Power | 1-15 | PASS
AcuRev2100 | Realtime | 6 | Apparent Power (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8240 | 0x2030 | float32 | Phase A Apparent Power | 1-25 | PASS
AcuRev2100 | Realtime | 6 | Apparent Power (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8242 | 0x2032 | float32 | Phase B Apparent Power | 1-26 | PASS
AcuRev2100 | Realtime | 6 | Apparent Power (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8244 | 0x2034 | float32 | Phase C Apparent Power | 1-27 | PASS
AcuRev2100 | Realtime | 6 | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Apparent Power (kVA) | System | 0.000 | 0 | 0 | 0 | 8222 | 0x201E | float32 | System Apparent Power | 1-16 | PASS
AcuRev2100 | Realtime | 6 | Load Nature | Phase A | R | 1 |  |  | 8252 | 0x203C | float32 | Phase A Load Nature | 1-31 | N/A
AcuRev2100 | Realtime | 6 | Load Nature | Phase B | R | 1 |  |  | 8254 | 0x203E | float32 | Phase B Load Nature | 1-32 | N/A
AcuRev2100 | Realtime | 6 | Load Nature | Phase C | R | 1 |  |  | 8256 | 0x2040 | float32 | Phase C Load Nature | 1-33 | N/A
AcuRev2100 | Realtime | 6 | Load Nature | Average | R | 1 |  |  | 8226 | 0x2022 | float32 | Average Load Nature | 1-18 | N/A
AcuRev2100 | Realtime | 6 | Load Nature | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Power Factor | Phase A | 1.000 | 1 | 0 | 0 | 8246 | 0x2036 | float32 | Phase A Power Factor | 1-28 | PASS
AcuRev2100 | Realtime | 6 | Power Factor | Phase B | 1.000 | 1 | 0 | 0 | 8248 | 0x2038 | float32 | Phase B Power Factor | 1-29 | PASS
AcuRev2100 | Realtime | 6 | Power Factor | Phase C | 1.000 | 1 | 0 | 0 | 8250 | 0x203A | float32 | Phase C Power Factor | 1-30 | PASS
AcuRev2100 | Realtime | 6 | Power Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Power Factor | System | 1.000 | 1 | 0 | 0 | 8224 | 0x2020 | float32 | System Power Factor | 1-17 | PASS
AcuRev2100 | Realtime | 6 | Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Frequency (Hz) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Frequency (Hz) | System | 0.000 | 0 | 0 | 0 | 8192 | 0x2000 | float32 | System Frequency | 1-1 | PASS
AcuRev2100 | Realtime | 6 | Current Phase Angle (°) | Phase B | 300.700 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Current Phase Angle (°) | Phase C | 305.900 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 6 | Current Phase Angle (°) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Line-to-Neutral Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8194 | 0x2002 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
AcuRev2100 | Realtime | 7 | Line-to-Neutral Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8196 | 0x2004 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
AcuRev2100 | Realtime | 7 | Line-to-Neutral Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8198 | 0x2006 | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
AcuRev2100 | Realtime | 7 | Line-to-Neutral Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8200 | 0x2008 | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
AcuRev2100 | Realtime | 7 | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Line-to-Line Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8202 | 0x200A | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
AcuRev2100 | Realtime | 7 | Line-to-Line Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8204 | 0x200C | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
AcuRev2100 | Realtime | 7 | Line-to-Line Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8206 | 0x200E | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
AcuRev2100 | Realtime | 7 | Line-to-Line Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8208 | 0x2010 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
AcuRev2100 | Realtime | 7 | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Current (A) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Active Power (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8228 | 0x2024 | float32 | Phase A Active Power | 1-19 | PASS
AcuRev2100 | Realtime | 7 | Active Power (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8230 | 0x2026 | float32 | Phase B Active Power | 1-20 | PASS
AcuRev2100 | Realtime | 7 | Active Power (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8232 | 0x2028 | float32 | Phase C Active Power | 1-21 | PASS
AcuRev2100 | Realtime | 7 | Active Power (kW) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Active Power (kW) | System | 0.000 | 0 | 0 | 0 | 8218 | 0x201A | float32 | System Active Power | 1-14 | PASS
AcuRev2100 | Realtime | 7 | Reactive Power (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8234 | 0x202A | float32 | Phase A Reactive Power | 1-22 | PASS
AcuRev2100 | Realtime | 7 | Reactive Power (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8236 | 0x202C | float32 | Phase B Reactive Power | 1-23 | PASS
AcuRev2100 | Realtime | 7 | Reactive Power (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8238 | 0x202E | float32 | Phase C Reactive Power | 1-24 | PASS
AcuRev2100 | Realtime | 7 | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Reactive Power (kvar) | System | 0.000 | 0 | 0 | 0 | 8220 | 0x201C | float32 | System Reactive Power | 1-15 | PASS
AcuRev2100 | Realtime | 7 | Apparent Power (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8240 | 0x2030 | float32 | Phase A Apparent Power | 1-25 | PASS
AcuRev2100 | Realtime | 7 | Apparent Power (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8242 | 0x2032 | float32 | Phase B Apparent Power | 1-26 | PASS
AcuRev2100 | Realtime | 7 | Apparent Power (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8244 | 0x2034 | float32 | Phase C Apparent Power | 1-27 | PASS
AcuRev2100 | Realtime | 7 | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Apparent Power (kVA) | System | 0.000 | 0 | 0 | 0 | 8222 | 0x201E | float32 | System Apparent Power | 1-16 | PASS
AcuRev2100 | Realtime | 7 | Load Nature | Phase A | R | 1 |  |  | 8252 | 0x203C | float32 | Phase A Load Nature | 1-31 | N/A
AcuRev2100 | Realtime | 7 | Load Nature | Phase B | R | 1 |  |  | 8254 | 0x203E | float32 | Phase B Load Nature | 1-32 | N/A
AcuRev2100 | Realtime | 7 | Load Nature | Phase C | R | 1 |  |  | 8256 | 0x2040 | float32 | Phase C Load Nature | 1-33 | N/A
AcuRev2100 | Realtime | 7 | Load Nature | Average | R | 1 |  |  | 8226 | 0x2022 | float32 | Average Load Nature | 1-18 | N/A
AcuRev2100 | Realtime | 7 | Load Nature | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Power Factor | Phase A | 1.000 | 1 | 0 | 0 | 8246 | 0x2036 | float32 | Phase A Power Factor | 1-28 | PASS
AcuRev2100 | Realtime | 7 | Power Factor | Phase B | 1.000 | 1 | 0 | 0 | 8248 | 0x2038 | float32 | Phase B Power Factor | 1-29 | PASS
AcuRev2100 | Realtime | 7 | Power Factor | Phase C | 1.000 | 1 | 0 | 0 | 8250 | 0x203A | float32 | Phase C Power Factor | 1-30 | PASS
AcuRev2100 | Realtime | 7 | Power Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Power Factor | System | 1.000 | 1 | 0 | 0 | 8224 | 0x2020 | float32 | System Power Factor | 1-17 | PASS
AcuRev2100 | Realtime | 7 | Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Frequency (Hz) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Frequency (Hz) | System | 0.000 | 0 | 0 | 0 | 8192 | 0x2000 | float32 | System Frequency | 1-1 | PASS
AcuRev2100 | Realtime | 7 | Current Phase Angle (°) | Phase A | 289.800 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Current Phase Angle (°) | Phase B | 303.500 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 7 | Current Phase Angle (°) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Line-to-Neutral Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8194 | 0x2002 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
AcuRev2100 | Realtime | 8 | Line-to-Neutral Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8196 | 0x2004 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
AcuRev2100 | Realtime | 8 | Line-to-Neutral Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8198 | 0x2006 | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
AcuRev2100 | Realtime | 8 | Line-to-Neutral Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8200 | 0x2008 | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
AcuRev2100 | Realtime | 8 | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Line-to-Line Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8202 | 0x200A | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
AcuRev2100 | Realtime | 8 | Line-to-Line Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8204 | 0x200C | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
AcuRev2100 | Realtime | 8 | Line-to-Line Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8206 | 0x200E | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
AcuRev2100 | Realtime | 8 | Line-to-Line Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8208 | 0x2010 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
AcuRev2100 | Realtime | 8 | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Current (A) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Active Power (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8228 | 0x2024 | float32 | Phase A Active Power | 1-19 | PASS
AcuRev2100 | Realtime | 8 | Active Power (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8230 | 0x2026 | float32 | Phase B Active Power | 1-20 | PASS
AcuRev2100 | Realtime | 8 | Active Power (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8232 | 0x2028 | float32 | Phase C Active Power | 1-21 | PASS
AcuRev2100 | Realtime | 8 | Active Power (kW) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Active Power (kW) | System | 0.000 | 0 | 0 | 0 | 8218 | 0x201A | float32 | System Active Power | 1-14 | PASS
AcuRev2100 | Realtime | 8 | Reactive Power (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8234 | 0x202A | float32 | Phase A Reactive Power | 1-22 | PASS
AcuRev2100 | Realtime | 8 | Reactive Power (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8236 | 0x202C | float32 | Phase B Reactive Power | 1-23 | PASS
AcuRev2100 | Realtime | 8 | Reactive Power (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8238 | 0x202E | float32 | Phase C Reactive Power | 1-24 | PASS
AcuRev2100 | Realtime | 8 | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Reactive Power (kvar) | System | 0.000 | 0 | 0 | 0 | 8220 | 0x201C | float32 | System Reactive Power | 1-15 | PASS
AcuRev2100 | Realtime | 8 | Apparent Power (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8240 | 0x2030 | float32 | Phase A Apparent Power | 1-25 | PASS
AcuRev2100 | Realtime | 8 | Apparent Power (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8242 | 0x2032 | float32 | Phase B Apparent Power | 1-26 | PASS
AcuRev2100 | Realtime | 8 | Apparent Power (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8244 | 0x2034 | float32 | Phase C Apparent Power | 1-27 | PASS
AcuRev2100 | Realtime | 8 | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Apparent Power (kVA) | System | 0.000 | 0 | 0 | 0 | 8222 | 0x201E | float32 | System Apparent Power | 1-16 | PASS
AcuRev2100 | Realtime | 8 | Load Nature | Phase A | R | 1 |  |  | 8252 | 0x203C | float32 | Phase A Load Nature | 1-31 | N/A
AcuRev2100 | Realtime | 8 | Load Nature | Phase B | R | 1 |  |  | 8254 | 0x203E | float32 | Phase B Load Nature | 1-32 | N/A
AcuRev2100 | Realtime | 8 | Load Nature | Phase C | R | 1 |  |  | 8256 | 0x2040 | float32 | Phase C Load Nature | 1-33 | N/A
AcuRev2100 | Realtime | 8 | Load Nature | Average | R | 1 |  |  | 8226 | 0x2022 | float32 | Average Load Nature | 1-18 | N/A
AcuRev2100 | Realtime | 8 | Load Nature | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Power Factor | Phase A | 1.000 | 1 | 0 | 0 | 8246 | 0x2036 | float32 | Phase A Power Factor | 1-28 | PASS
AcuRev2100 | Realtime | 8 | Power Factor | Phase B | 1.000 | 1 | 0 | 0 | 8248 | 0x2038 | float32 | Phase B Power Factor | 1-29 | PASS
AcuRev2100 | Realtime | 8 | Power Factor | Phase C | 1.000 | 1 | 0 | 0 | 8250 | 0x203A | float32 | Phase C Power Factor | 1-30 | PASS
AcuRev2100 | Realtime | 8 | Power Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Power Factor | System | 1.000 | 1 | 0 | 0 | 8224 | 0x2020 | float32 | System Power Factor | 1-17 | PASS
AcuRev2100 | Realtime | 8 | Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Frequency (Hz) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Frequency (Hz) | System | 0.000 | 0 | 0 | 0 | 8192 | 0x2000 | float32 | System Frequency | 1-1 | PASS
AcuRev2100 | Realtime | 8 | Current Phase Angle (°) | Phase A | 287.500 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Current Phase Angle (°) | Phase C | 309.900 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 8 | Current Phase Angle (°) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Line-to-Neutral Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8194 | 0x2002 | float32 | Phase A Line-to-Neutral Voltage | 1-2 | PASS
AcuRev2100 | Realtime | 9 | Line-to-Neutral Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8196 | 0x2004 | float32 | Phase B Line-to-Neutral Voltage | 1-3 | PASS
AcuRev2100 | Realtime | 9 | Line-to-Neutral Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8198 | 0x2006 | float32 | Phase C Line-to-Neutral Voltage | 1-4 | PASS
AcuRev2100 | Realtime | 9 | Line-to-Neutral Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8200 | 0x2008 | float32 | Average Line-to-Neutral Voltage | 1-5 | PASS
AcuRev2100 | Realtime | 9 | Line-to-Neutral Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Line-to-Line Voltage (V) | Phase A | 0.000 | 0 | 0 | 0 | 8202 | 0x200A | float32 | Phase A-B Line-to-Line Voltage | 1-6 | PASS
AcuRev2100 | Realtime | 9 | Line-to-Line Voltage (V) | Phase B | 0.000 | 0 | 0 | 0 | 8204 | 0x200C | float32 | Phase B-C Line-to-Line Voltage | 1-7 | PASS
AcuRev2100 | Realtime | 9 | Line-to-Line Voltage (V) | Phase C | 0.000 | 0 | 0 | 0 | 8206 | 0x200E | float32 | Phase C-A Line-to-Line Voltage | 1-8 | PASS
AcuRev2100 | Realtime | 9 | Line-to-Line Voltage (V) | Average | 0.000 | 0 | 0 | 0 | 8208 | 0x2010 | float32 | Average Line-to-Line Voltage | 1-9 | PASS
AcuRev2100 | Realtime | 9 | Line-to-Line Voltage (V) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Current (A) | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Active Power (kW) | Phase A | 0.000 | 0 | 0 | 0 | 8228 | 0x2024 | float32 | Phase A Active Power | 1-19 | PASS
AcuRev2100 | Realtime | 9 | Active Power (kW) | Phase B | 0.000 | 0 | 0 | 0 | 8230 | 0x2026 | float32 | Phase B Active Power | 1-20 | PASS
AcuRev2100 | Realtime | 9 | Active Power (kW) | Phase C | 0.000 | 0 | 0 | 0 | 8232 | 0x2028 | float32 | Phase C Active Power | 1-21 | PASS
AcuRev2100 | Realtime | 9 | Active Power (kW) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Active Power (kW) | System | 0.000 | 0 | 0 | 0 | 8218 | 0x201A | float32 | System Active Power | 1-14 | PASS
AcuRev2100 | Realtime | 9 | Reactive Power (kvar) | Phase A | 0.000 | 0 | 0 | 0 | 8234 | 0x202A | float32 | Phase A Reactive Power | 1-22 | PASS
AcuRev2100 | Realtime | 9 | Reactive Power (kvar) | Phase B | 0.000 | 0 | 0 | 0 | 8236 | 0x202C | float32 | Phase B Reactive Power | 1-23 | PASS
AcuRev2100 | Realtime | 9 | Reactive Power (kvar) | Phase C | 0.000 | 0 | 0 | 0 | 8238 | 0x202E | float32 | Phase C Reactive Power | 1-24 | PASS
AcuRev2100 | Realtime | 9 | Reactive Power (kvar) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Reactive Power (kvar) | System | 0.000 | 0 | 0 | 0 | 8220 | 0x201C | float32 | System Reactive Power | 1-15 | PASS
AcuRev2100 | Realtime | 9 | Apparent Power (kVA) | Phase A | 0.000 | 0 | 0 | 0 | 8240 | 0x2030 | float32 | Phase A Apparent Power | 1-25 | PASS
AcuRev2100 | Realtime | 9 | Apparent Power (kVA) | Phase B | 0.000 | 0 | 0 | 0 | 8242 | 0x2032 | float32 | Phase B Apparent Power | 1-26 | PASS
AcuRev2100 | Realtime | 9 | Apparent Power (kVA) | Phase C | 0.000 | 0 | 0 | 0 | 8244 | 0x2034 | float32 | Phase C Apparent Power | 1-27 | PASS
AcuRev2100 | Realtime | 9 | Apparent Power (kVA) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Apparent Power (kVA) | System | 0.000 | 0 | 0 | 0 | 8222 | 0x201E | float32 | System Apparent Power | 1-16 | PASS
AcuRev2100 | Realtime | 9 | Load Nature | Phase A | R | 1 |  |  | 8252 | 0x203C | float32 | Phase A Load Nature | 1-31 | N/A
AcuRev2100 | Realtime | 9 | Load Nature | Phase B | R | 1 |  |  | 8254 | 0x203E | float32 | Phase B Load Nature | 1-32 | N/A
AcuRev2100 | Realtime | 9 | Load Nature | Phase C | R | 1 |  |  | 8256 | 0x2040 | float32 | Phase C Load Nature | 1-33 | N/A
AcuRev2100 | Realtime | 9 | Load Nature | Average | R | 1 |  |  | 8226 | 0x2022 | float32 | Average Load Nature | 1-18 | N/A
AcuRev2100 | Realtime | 9 | Load Nature | System | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Power Factor | Phase A | 1.000 | 1 | 0 | 0 | 8246 | 0x2036 | float32 | Phase A Power Factor | 1-28 | PASS
AcuRev2100 | Realtime | 9 | Power Factor | Phase B | 1.000 | 1 | 0 | 0 | 8248 | 0x2038 | float32 | Phase B Power Factor | 1-29 | PASS
AcuRev2100 | Realtime | 9 | Power Factor | Phase C | 1.000 | 1 | 0 | 0 | 8250 | 0x203A | float32 | Phase C Power Factor | 1-30 | PASS
AcuRev2100 | Realtime | 9 | Power Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Power Factor | System | 1.000 | 1 | 0 | 0 | 8224 | 0x2020 | float32 | System Power Factor | 1-17 | PASS
AcuRev2100 | Realtime | 9 | Frequency (Hz) | Phase A | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Frequency (Hz) | Phase B | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Frequency (Hz) | Phase C | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Frequency (Hz) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Frequency (Hz) | System | 0.000 | 0 | 0 | 0 | 8192 | 0x2000 | float32 | System Frequency | 1-1 | PASS
AcuRev2100 | Realtime | 9 | Current Phase Angle (°) | Phase B | 34.400 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Current Phase Angle (°) | Phase C | 317.000 | [8 empty] | 无寄存器
AcuRev2100 | Realtime | 9 | Current Phase Angle (°) | System | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 1 | Voltage THD (%) | Phase A | 0.000 | 0 | 0 | 0 | 12801 | 0x3201 | int16 | Phase A Voltage THD | 19-2 | PASS
AcuRev2100 | THD | 1 | Voltage THD (%) | Phase B | 0.000 | 0 | 0 | 0 | 12802 | 0x3202 | int16 | Phase B Voltage THD | 19-3 | PASS
AcuRev2100 | THD | 1 | Voltage THD (%) | Phase C | 0.000 | 0 | 0 | 0 | 12803 | 0x3203 | int16 | Phase C Voltage THD | 19-4 | PASS
AcuRev2100 | THD | 1 | Voltage THD (%) | Average | 0.000 | 0 | 0 | 0 | 12804 | 0x3204 | int16 | Average Voltage THD | 19-5 | PASS
AcuRev2100 | THD | 1 | Voltage THD Odd (%) | Phase A | 0.000 | 0 | 0 | 0 | 12896 | 0x3260 | int16 | Phase A Voltage Odd THD | 19-97 | PASS
AcuRev2100 | THD | 1 | Voltage THD Odd (%) | Phase B | 0.000 | 0 | 0 | 0 | 12900 | 0x3264 | int16 | Phase B Voltage Odd THD | 19-101 | PASS
AcuRev2100 | THD | 1 | Voltage THD Odd (%) | Phase C | 0.000 | 0 | 0 | 0 | 12904 | 0x3268 | int16 | Phase C Voltage Odd THD | 19-105 | PASS
AcuRev2100 | THD | 1 | Voltage THD Odd (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 1 | Voltage THD Even (%) | Phase A | 0.000 | 0 | 0 | 0 | 12897 | 0x3261 | int16 | Phase A Voltage Even THD | 19-98 | PASS
AcuRev2100 | THD | 1 | Voltage THD Even (%) | Phase B | 0.000 | 0 | 0 | 0 | 12901 | 0x3265 | int16 | Phase B Voltage Even THD | 19-102 | PASS
AcuRev2100 | THD | 1 | Voltage THD Even (%) | Phase C | 0.000 | 0 | 0 | 0 | 12905 | 0x3269 | int16 | Phase C Voltage Even THD | 19-106 | PASS
AcuRev2100 | THD | 1 | Voltage THD Even (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 1 | Voltage Crest Factor | Phase A | 0.000 | 0 | 0 | 0 | 12898 | 0x3262 | int16 | Phase A Voltage Crest Factor | 19-99 | PASS
AcuRev2100 | THD | 1 | Voltage Crest Factor | Phase B | 0.000 | 0 | 0 | 0 | 12902 | 0x3266 | int16 | Phase B Voltage Crest Factor | 19-103 | PASS
AcuRev2100 | THD | 1 | Voltage Crest Factor | Phase C | 0.000 | 0 | 0 | 0 | 12906 | 0x326A | int16 | Phase C Voltage Crest Factor | 19-107 | PASS
AcuRev2100 | THD | 1 | Voltage Crest Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 1 | Current THD (%) | Phase A | 33.880 | [8 empty] | 无寄存器
AcuRev2100 | THD | 1 | Current THD (%) | Phase B | 35.160 | [8 empty] | 无寄存器
AcuRev2100 | THD | 2 | Voltage THD (%) | Phase A | 0.000 | 0 | 0 | 0 | 12801 | 0x3201 | int16 | Phase A Voltage THD | 19-2 | PASS
AcuRev2100 | THD | 2 | Voltage THD (%) | Phase B | 0.000 | 0 | 0 | 0 | 12802 | 0x3202 | int16 | Phase B Voltage THD | 19-3 | PASS
AcuRev2100 | THD | 2 | Voltage THD (%) | Phase C | 0.000 | 0 | 0 | 0 | 12803 | 0x3203 | int16 | Phase C Voltage THD | 19-4 | PASS
AcuRev2100 | THD | 2 | Voltage THD (%) | Average | 0.000 | 0 | 0 | 0 | 12804 | 0x3204 | int16 | Average Voltage THD | 19-5 | PASS
AcuRev2100 | THD | 2 | Voltage THD Odd (%) | Phase A | 0.000 | 0 | 0 | 0 | 12896 | 0x3260 | int16 | Phase A Voltage Odd THD | 19-97 | PASS
AcuRev2100 | THD | 2 | Voltage THD Odd (%) | Phase B | 0.000 | 0 | 0 | 0 | 12900 | 0x3264 | int16 | Phase B Voltage Odd THD | 19-101 | PASS
AcuRev2100 | THD | 2 | Voltage THD Odd (%) | Phase C | 0.000 | 0 | 0 | 0 | 12904 | 0x3268 | int16 | Phase C Voltage Odd THD | 19-105 | PASS
AcuRev2100 | THD | 2 | Voltage THD Odd (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 2 | Voltage THD Even (%) | Phase A | 0.000 | 0 | 0 | 0 | 12897 | 0x3261 | int16 | Phase A Voltage Even THD | 19-98 | PASS
AcuRev2100 | THD | 2 | Voltage THD Even (%) | Phase B | 0.000 | 0 | 0 | 0 | 12901 | 0x3265 | int16 | Phase B Voltage Even THD | 19-102 | PASS
AcuRev2100 | THD | 2 | Voltage THD Even (%) | Phase C | 0.000 | 0 | 0 | 0 | 12905 | 0x3269 | int16 | Phase C Voltage Even THD | 19-106 | PASS
AcuRev2100 | THD | 2 | Voltage THD Even (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 2 | Voltage Crest Factor | Phase A | 0.000 | 0 | 0 | 0 | 12898 | 0x3262 | int16 | Phase A Voltage Crest Factor | 19-99 | PASS
AcuRev2100 | THD | 2 | Voltage Crest Factor | Phase B | 0.000 | 0 | 0 | 0 | 12902 | 0x3266 | int16 | Phase B Voltage Crest Factor | 19-103 | PASS
AcuRev2100 | THD | 2 | Voltage Crest Factor | Phase C | 0.000 | 0 | 0 | 0 | 12906 | 0x326A | int16 | Phase C Voltage Crest Factor | 19-107 | PASS
AcuRev2100 | THD | 2 | Voltage Crest Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 2 | Current THD (%) | Phase A | 27.660 | [8 empty] | 无寄存器
AcuRev2100 | THD | 2 | Current THD (%) | Phase C | 36.400 | [8 empty] | 无寄存器
AcuRev2100 | THD | 3 | Voltage THD (%) | Phase A | 0.000 | 0 | 0 | 0 | 12801 | 0x3201 | int16 | Phase A Voltage THD | 19-2 | PASS
AcuRev2100 | THD | 3 | Voltage THD (%) | Phase B | 0.000 | 0 | 0 | 0 | 12802 | 0x3202 | int16 | Phase B Voltage THD | 19-3 | PASS
AcuRev2100 | THD | 3 | Voltage THD (%) | Phase C | 0.000 | 0 | 0 | 0 | 12803 | 0x3203 | int16 | Phase C Voltage THD | 19-4 | PASS
AcuRev2100 | THD | 3 | Voltage THD (%) | Average | 0.000 | 0 | 0 | 0 | 12804 | 0x3204 | int16 | Average Voltage THD | 19-5 | PASS
AcuRev2100 | THD | 3 | Voltage THD Odd (%) | Phase A | 0.000 | 0 | 0 | 0 | 12896 | 0x3260 | int16 | Phase A Voltage Odd THD | 19-97 | PASS
AcuRev2100 | THD | 3 | Voltage THD Odd (%) | Phase B | 0.000 | 0 | 0 | 0 | 12900 | 0x3264 | int16 | Phase B Voltage Odd THD | 19-101 | PASS
AcuRev2100 | THD | 3 | Voltage THD Odd (%) | Phase C | 0.000 | 0 | 0 | 0 | 12904 | 0x3268 | int16 | Phase C Voltage Odd THD | 19-105 | PASS
AcuRev2100 | THD | 3 | Voltage THD Odd (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 3 | Voltage THD Even (%) | Phase A | 0.000 | 0 | 0 | 0 | 12897 | 0x3261 | int16 | Phase A Voltage Even THD | 19-98 | PASS
AcuRev2100 | THD | 3 | Voltage THD Even (%) | Phase B | 0.000 | 0 | 0 | 0 | 12901 | 0x3265 | int16 | Phase B Voltage Even THD | 19-102 | PASS
AcuRev2100 | THD | 3 | Voltage THD Even (%) | Phase C | 0.000 | 0 | 0 | 0 | 12905 | 0x3269 | int16 | Phase C Voltage Even THD | 19-106 | PASS
AcuRev2100 | THD | 3 | Voltage THD Even (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 3 | Voltage Crest Factor | Phase A | 0.000 | 0 | 0 | 0 | 12898 | 0x3262 | int16 | Phase A Voltage Crest Factor | 19-99 | PASS
AcuRev2100 | THD | 3 | Voltage Crest Factor | Phase B | 0.000 | 0 | 0 | 0 | 12902 | 0x3266 | int16 | Phase B Voltage Crest Factor | 19-103 | PASS
AcuRev2100 | THD | 3 | Voltage Crest Factor | Phase C | 0.000 | 0 | 0 | 0 | 12906 | 0x326A | int16 | Phase C Voltage Crest Factor | 19-107 | PASS
AcuRev2100 | THD | 3 | Voltage Crest Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 3 | Current THD (%) | Phase B | 31.340 | [8 empty] | 无寄存器
AcuRev2100 | THD | 3 | Current THD (%) | Phase C | 30.770 | [8 empty] | 无寄存器
AcuRev2100 | THD | 4 | Voltage THD (%) | Phase A | 0.000 | 0 | 0 | 0 | 12801 | 0x3201 | int16 | Phase A Voltage THD | 19-2 | PASS
AcuRev2100 | THD | 4 | Voltage THD (%) | Phase B | 0.000 | 0 | 0 | 0 | 12802 | 0x3202 | int16 | Phase B Voltage THD | 19-3 | PASS
AcuRev2100 | THD | 4 | Voltage THD (%) | Phase C | 0.000 | 0 | 0 | 0 | 12803 | 0x3203 | int16 | Phase C Voltage THD | 19-4 | PASS
AcuRev2100 | THD | 4 | Voltage THD (%) | Average | 0.000 | 0 | 0 | 0 | 12804 | 0x3204 | int16 | Average Voltage THD | 19-5 | PASS
AcuRev2100 | THD | 4 | Voltage THD Odd (%) | Phase A | 0.000 | 0 | 0 | 0 | 12896 | 0x3260 | int16 | Phase A Voltage Odd THD | 19-97 | PASS
AcuRev2100 | THD | 4 | Voltage THD Odd (%) | Phase B | 0.000 | 0 | 0 | 0 | 12900 | 0x3264 | int16 | Phase B Voltage Odd THD | 19-101 | PASS
AcuRev2100 | THD | 4 | Voltage THD Odd (%) | Phase C | 0.000 | 0 | 0 | 0 | 12904 | 0x3268 | int16 | Phase C Voltage Odd THD | 19-105 | PASS
AcuRev2100 | THD | 4 | Voltage THD Odd (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 4 | Voltage THD Even (%) | Phase A | 0.000 | 0 | 0 | 0 | 12897 | 0x3261 | int16 | Phase A Voltage Even THD | 19-98 | PASS
AcuRev2100 | THD | 4 | Voltage THD Even (%) | Phase B | 0.000 | 0 | 0 | 0 | 12901 | 0x3265 | int16 | Phase B Voltage Even THD | 19-102 | PASS
AcuRev2100 | THD | 4 | Voltage THD Even (%) | Phase C | 0.000 | 0 | 0 | 0 | 12905 | 0x3269 | int16 | Phase C Voltage Even THD | 19-106 | PASS
AcuRev2100 | THD | 4 | Voltage THD Even (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 4 | Voltage Crest Factor | Phase A | 0.000 | 0 | 0 | 0 | 12898 | 0x3262 | int16 | Phase A Voltage Crest Factor | 19-99 | PASS
AcuRev2100 | THD | 4 | Voltage Crest Factor | Phase B | 0.000 | 0 | 0 | 0 | 12902 | 0x3266 | int16 | Phase B Voltage Crest Factor | 19-103 | PASS
AcuRev2100 | THD | 4 | Voltage Crest Factor | Phase C | 0.000 | 0 | 0 | 0 | 12906 | 0x326A | int16 | Phase C Voltage Crest Factor | 19-107 | PASS
AcuRev2100 | THD | 4 | Voltage Crest Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 4 | Current THD (%) | Phase A | 73.170 | [8 empty] | 无寄存器
AcuRev2100 | THD | 4 | Current THD (%) | Phase B | 94.010 | [8 empty] | 无寄存器
AcuRev2100 | THD | 5 | Voltage THD (%) | Phase A | 0.000 | 0 | 0 | 0 | 12801 | 0x3201 | int16 | Phase A Voltage THD | 19-2 | PASS
AcuRev2100 | THD | 5 | Voltage THD (%) | Phase B | 0.000 | 0 | 0 | 0 | 12802 | 0x3202 | int16 | Phase B Voltage THD | 19-3 | PASS
AcuRev2100 | THD | 5 | Voltage THD (%) | Phase C | 0.000 | 0 | 0 | 0 | 12803 | 0x3203 | int16 | Phase C Voltage THD | 19-4 | PASS
AcuRev2100 | THD | 5 | Voltage THD (%) | Average | 0.000 | 0 | 0 | 0 | 12804 | 0x3204 | int16 | Average Voltage THD | 19-5 | PASS
AcuRev2100 | THD | 5 | Voltage THD Odd (%) | Phase A | 0.000 | 0 | 0 | 0 | 12896 | 0x3260 | int16 | Phase A Voltage Odd THD | 19-97 | PASS
AcuRev2100 | THD | 5 | Voltage THD Odd (%) | Phase B | 0.000 | 0 | 0 | 0 | 12900 | 0x3264 | int16 | Phase B Voltage Odd THD | 19-101 | PASS
AcuRev2100 | THD | 5 | Voltage THD Odd (%) | Phase C | 0.000 | 0 | 0 | 0 | 12904 | 0x3268 | int16 | Phase C Voltage Odd THD | 19-105 | PASS
AcuRev2100 | THD | 5 | Voltage THD Odd (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 5 | Voltage THD Even (%) | Phase A | 0.000 | 0 | 0 | 0 | 12897 | 0x3261 | int16 | Phase A Voltage Even THD | 19-98 | PASS
AcuRev2100 | THD | 5 | Voltage THD Even (%) | Phase B | 0.000 | 0 | 0 | 0 | 12901 | 0x3265 | int16 | Phase B Voltage Even THD | 19-102 | PASS
AcuRev2100 | THD | 5 | Voltage THD Even (%) | Phase C | 0.000 | 0 | 0 | 0 | 12905 | 0x3269 | int16 | Phase C Voltage Even THD | 19-106 | PASS
AcuRev2100 | THD | 5 | Voltage THD Even (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 5 | Voltage Crest Factor | Phase A | 0.000 | 0 | 0 | 0 | 12898 | 0x3262 | int16 | Phase A Voltage Crest Factor | 19-99 | PASS
AcuRev2100 | THD | 5 | Voltage Crest Factor | Phase B | 0.000 | 0 | 0 | 0 | 12902 | 0x3266 | int16 | Phase B Voltage Crest Factor | 19-103 | PASS
AcuRev2100 | THD | 5 | Voltage Crest Factor | Phase C | 0.000 | 0 | 0 | 0 | 12906 | 0x326A | int16 | Phase C Voltage Crest Factor | 19-107 | PASS
AcuRev2100 | THD | 5 | Voltage Crest Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 5 | Current THD (%) | Phase A | 58.250 | [8 empty] | 无寄存器
AcuRev2100 | THD | 5 | Current THD (%) | Phase C | 20.200 | [8 empty] | 无寄存器
AcuRev2100 | THD | 6 | Voltage THD (%) | Phase A | 0.000 | 0 | 0 | 0 | 12801 | 0x3201 | int16 | Phase A Voltage THD | 19-2 | PASS
AcuRev2100 | THD | 6 | Voltage THD (%) | Phase B | 0.000 | 0 | 0 | 0 | 12802 | 0x3202 | int16 | Phase B Voltage THD | 19-3 | PASS
AcuRev2100 | THD | 6 | Voltage THD (%) | Phase C | 0.000 | 0 | 0 | 0 | 12803 | 0x3203 | int16 | Phase C Voltage THD | 19-4 | PASS
AcuRev2100 | THD | 6 | Voltage THD (%) | Average | 0.000 | 0 | 0 | 0 | 12804 | 0x3204 | int16 | Average Voltage THD | 19-5 | PASS
AcuRev2100 | THD | 6 | Voltage THD Odd (%) | Phase A | 0.000 | 0 | 0 | 0 | 12896 | 0x3260 | int16 | Phase A Voltage Odd THD | 19-97 | PASS
AcuRev2100 | THD | 6 | Voltage THD Odd (%) | Phase B | 0.000 | 0 | 0 | 0 | 12900 | 0x3264 | int16 | Phase B Voltage Odd THD | 19-101 | PASS
AcuRev2100 | THD | 6 | Voltage THD Odd (%) | Phase C | 0.000 | 0 | 0 | 0 | 12904 | 0x3268 | int16 | Phase C Voltage Odd THD | 19-105 | PASS
AcuRev2100 | THD | 6 | Voltage THD Odd (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 6 | Voltage THD Even (%) | Phase A | 0.000 | 0 | 0 | 0 | 12897 | 0x3261 | int16 | Phase A Voltage Even THD | 19-98 | PASS
AcuRev2100 | THD | 6 | Voltage THD Even (%) | Phase B | 0.000 | 0 | 0 | 0 | 12901 | 0x3265 | int16 | Phase B Voltage Even THD | 19-102 | PASS
AcuRev2100 | THD | 6 | Voltage THD Even (%) | Phase C | 0.000 | 0 | 0 | 0 | 12905 | 0x3269 | int16 | Phase C Voltage Even THD | 19-106 | PASS
AcuRev2100 | THD | 6 | Voltage THD Even (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 6 | Voltage Crest Factor | Phase A | 0.000 | 0 | 0 | 0 | 12898 | 0x3262 | int16 | Phase A Voltage Crest Factor | 19-99 | PASS
AcuRev2100 | THD | 6 | Voltage Crest Factor | Phase B | 0.000 | 0 | 0 | 0 | 12902 | 0x3266 | int16 | Phase B Voltage Crest Factor | 19-103 | PASS
AcuRev2100 | THD | 6 | Voltage Crest Factor | Phase C | 0.000 | 0 | 0 | 0 | 12906 | 0x326A | int16 | Phase C Voltage Crest Factor | 19-107 | PASS
AcuRev2100 | THD | 6 | Voltage Crest Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 6 | Current THD (%) | Phase B | 99.990 | [8 empty] | 无寄存器
AcuRev2100 | THD | 6 | Current THD (%) | Phase C | 68.200 | [8 empty] | 无寄存器
AcuRev2100 | THD | 7 | Voltage THD (%) | Phase A | 0.000 | 0 | 0 | 0 | 12801 | 0x3201 | int16 | Phase A Voltage THD | 19-2 | PASS
AcuRev2100 | THD | 7 | Voltage THD (%) | Phase B | 0.000 | 0 | 0 | 0 | 12802 | 0x3202 | int16 | Phase B Voltage THD | 19-3 | PASS
AcuRev2100 | THD | 7 | Voltage THD (%) | Phase C | 0.000 | 0 | 0 | 0 | 12803 | 0x3203 | int16 | Phase C Voltage THD | 19-4 | PASS
AcuRev2100 | THD | 7 | Voltage THD (%) | Average | 0.000 | 0 | 0 | 0 | 12804 | 0x3204 | int16 | Average Voltage THD | 19-5 | PASS
AcuRev2100 | THD | 7 | Voltage THD Odd (%) | Phase A | 0.000 | 0 | 0 | 0 | 12896 | 0x3260 | int16 | Phase A Voltage Odd THD | 19-97 | PASS
AcuRev2100 | THD | 7 | Voltage THD Odd (%) | Phase B | 0.000 | 0 | 0 | 0 | 12900 | 0x3264 | int16 | Phase B Voltage Odd THD | 19-101 | PASS
AcuRev2100 | THD | 7 | Voltage THD Odd (%) | Phase C | 0.000 | 0 | 0 | 0 | 12904 | 0x3268 | int16 | Phase C Voltage Odd THD | 19-105 | PASS
AcuRev2100 | THD | 7 | Voltage THD Odd (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 7 | Voltage THD Even (%) | Phase A | 0.000 | 0 | 0 | 0 | 12897 | 0x3261 | int16 | Phase A Voltage Even THD | 19-98 | PASS
AcuRev2100 | THD | 7 | Voltage THD Even (%) | Phase B | 0.000 | 0 | 0 | 0 | 12901 | 0x3265 | int16 | Phase B Voltage Even THD | 19-102 | PASS
AcuRev2100 | THD | 7 | Voltage THD Even (%) | Phase C | 0.000 | 0 | 0 | 0 | 12905 | 0x3269 | int16 | Phase C Voltage Even THD | 19-106 | PASS
AcuRev2100 | THD | 7 | Voltage THD Even (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 7 | Voltage Crest Factor | Phase A | 0.000 | 0 | 0 | 0 | 12898 | 0x3262 | int16 | Phase A Voltage Crest Factor | 19-99 | PASS
AcuRev2100 | THD | 7 | Voltage Crest Factor | Phase B | 0.000 | 0 | 0 | 0 | 12902 | 0x3266 | int16 | Phase B Voltage Crest Factor | 19-103 | PASS
AcuRev2100 | THD | 7 | Voltage Crest Factor | Phase C | 0.000 | 0 | 0 | 0 | 12906 | 0x326A | int16 | Phase C Voltage Crest Factor | 19-107 | PASS
AcuRev2100 | THD | 7 | Voltage Crest Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 7 | Current THD (%) | Phase A | 20.820 | [8 empty] | 无寄存器
AcuRev2100 | THD | 7 | Current THD (%) | Phase B | 30.210 | [8 empty] | 无寄存器
AcuRev2100 | THD | 8 | Voltage THD (%) | Phase A | 0.000 | 0 | 0 | 0 | 12801 | 0x3201 | int16 | Phase A Voltage THD | 19-2 | PASS
AcuRev2100 | THD | 8 | Voltage THD (%) | Phase B | 0.000 | 0 | 0 | 0 | 12802 | 0x3202 | int16 | Phase B Voltage THD | 19-3 | PASS
AcuRev2100 | THD | 8 | Voltage THD (%) | Phase C | 0.000 | 0 | 0 | 0 | 12803 | 0x3203 | int16 | Phase C Voltage THD | 19-4 | PASS
AcuRev2100 | THD | 8 | Voltage THD (%) | Average | 0.000 | 0 | 0 | 0 | 12804 | 0x3204 | int16 | Average Voltage THD | 19-5 | PASS
AcuRev2100 | THD | 8 | Voltage THD Odd (%) | Phase A | 0.000 | 0 | 0 | 0 | 12896 | 0x3260 | int16 | Phase A Voltage Odd THD | 19-97 | PASS
AcuRev2100 | THD | 8 | Voltage THD Odd (%) | Phase B | 0.000 | 0 | 0 | 0 | 12900 | 0x3264 | int16 | Phase B Voltage Odd THD | 19-101 | PASS
AcuRev2100 | THD | 8 | Voltage THD Odd (%) | Phase C | 0.000 | 0 | 0 | 0 | 12904 | 0x3268 | int16 | Phase C Voltage Odd THD | 19-105 | PASS
AcuRev2100 | THD | 8 | Voltage THD Odd (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 8 | Voltage THD Even (%) | Phase A | 0.000 | 0 | 0 | 0 | 12897 | 0x3261 | int16 | Phase A Voltage Even THD | 19-98 | PASS
AcuRev2100 | THD | 8 | Voltage THD Even (%) | Phase B | 0.000 | 0 | 0 | 0 | 12901 | 0x3265 | int16 | Phase B Voltage Even THD | 19-102 | PASS
AcuRev2100 | THD | 8 | Voltage THD Even (%) | Phase C | 0.000 | 0 | 0 | 0 | 12905 | 0x3269 | int16 | Phase C Voltage Even THD | 19-106 | PASS
AcuRev2100 | THD | 8 | Voltage THD Even (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 8 | Voltage Crest Factor | Phase A | 0.000 | 0 | 0 | 0 | 12898 | 0x3262 | int16 | Phase A Voltage Crest Factor | 19-99 | PASS
AcuRev2100 | THD | 8 | Voltage Crest Factor | Phase B | 0.000 | 0 | 0 | 0 | 12902 | 0x3266 | int16 | Phase B Voltage Crest Factor | 19-103 | PASS
AcuRev2100 | THD | 8 | Voltage Crest Factor | Phase C | 0.000 | 0 | 0 | 0 | 12906 | 0x326A | int16 | Phase C Voltage Crest Factor | 19-107 | PASS
AcuRev2100 | THD | 8 | Voltage Crest Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 8 | Current THD (%) | Phase A | 43.820 | [8 empty] | 无寄存器
AcuRev2100 | THD | 8 | Current THD (%) | Phase C | 57.250 | [8 empty] | 无寄存器
AcuRev2100 | THD | 9 | Voltage THD (%) | Phase A | 0.000 | 0 | 0 | 0 | 12801 | 0x3201 | int16 | Phase A Voltage THD | 19-2 | PASS
AcuRev2100 | THD | 9 | Voltage THD (%) | Phase B | 0.000 | 0 | 0 | 0 | 12802 | 0x3202 | int16 | Phase B Voltage THD | 19-3 | PASS
AcuRev2100 | THD | 9 | Voltage THD (%) | Phase C | 0.000 | 0 | 0 | 0 | 12803 | 0x3203 | int16 | Phase C Voltage THD | 19-4 | PASS
AcuRev2100 | THD | 9 | Voltage THD (%) | Average | 0.000 | 0 | 0 | 0 | 12804 | 0x3204 | int16 | Average Voltage THD | 19-5 | PASS
AcuRev2100 | THD | 9 | Voltage THD Odd (%) | Phase A | 0.000 | 0 | 0 | 0 | 12896 | 0x3260 | int16 | Phase A Voltage Odd THD | 19-97 | PASS
AcuRev2100 | THD | 9 | Voltage THD Odd (%) | Phase B | 0.000 | 0 | 0 | 0 | 12900 | 0x3264 | int16 | Phase B Voltage Odd THD | 19-101 | PASS
AcuRev2100 | THD | 9 | Voltage THD Odd (%) | Phase C | 0.000 | 0 | 0 | 0 | 12904 | 0x3268 | int16 | Phase C Voltage Odd THD | 19-105 | PASS
AcuRev2100 | THD | 9 | Voltage THD Odd (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 9 | Voltage THD Even (%) | Phase A | 0.000 | 0 | 0 | 0 | 12897 | 0x3261 | int16 | Phase A Voltage Even THD | 19-98 | PASS
AcuRev2100 | THD | 9 | Voltage THD Even (%) | Phase B | 0.000 | 0 | 0 | 0 | 12901 | 0x3265 | int16 | Phase B Voltage Even THD | 19-102 | PASS
AcuRev2100 | THD | 9 | Voltage THD Even (%) | Phase C | 0.000 | 0 | 0 | 0 | 12905 | 0x3269 | int16 | Phase C Voltage Even THD | 19-106 | PASS
AcuRev2100 | THD | 9 | Voltage THD Even (%) | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 9 | Voltage Crest Factor | Phase A | 0.000 | 0 | 0 | 0 | 12898 | 0x3262 | int16 | Phase A Voltage Crest Factor | 19-99 | PASS
AcuRev2100 | THD | 9 | Voltage Crest Factor | Phase B | 0.000 | 0 | 0 | 0 | 12902 | 0x3266 | int16 | Phase B Voltage Crest Factor | 19-103 | PASS
AcuRev2100 | THD | 9 | Voltage Crest Factor | Phase C | 0.000 | 0 | 0 | 0 | 12906 | 0x326A | int16 | Phase C Voltage Crest Factor | 19-107 | PASS
AcuRev2100 | THD | 9 | Voltage Crest Factor | Average | - | [8 empty] | 无寄存器
AcuRev2100 | THD | 9 | Current THD (%) | Phase B | 99.990 | [8 empty] | 无寄存器
AcuRev2100 | THD | 9 | Current THD (%) | Phase C | 69.760 | [8 empty] | 无寄存器

## 用例Mapping
用例ID | 用例名称（Class::method） | 测试步骤 | 验证点
DC-001 | TestCollect::test_json_generated | 采集 | Step1 采集结果文件 metering_collect.json 正常生成
DC-002 | TestCollect::test_has_devices | 采集 | 至少采集到 1 台设备数据
DC-003 | TestCollect::test_connection_info | 采集 | 每台设备均抓取到 Connection IP 地址
DC-004 | TestCollect::test_metering_views | 采集 | 每台设备至少包含 1 个 Metering 视图数据
DC-005 | TestCollect::test_param_count | 采集 | 总采集参数条目数量 > 0
DC-006 | TestMatch::test_csv_generated | 匹配 | Step2 匹配结果文件 metering_register_match.csv 正常生成
DC-007 | TestMatch::test_match_count | 匹配 | 匹配结果总条目数量 > 0
DC-008 | TestMatch::test_exact_match_ratio | 匹配 | 精确匹配率 ≥ 80%（排除 N/A 条目）
DC-009 | TestMatch::test_no_unmatched_excess | 匹配 | 未匹配条目数量 ≤ 20
DC-010 | TestCompare::test_xlsx_generated | 比对 | Step3 比对报告 metering_compare.xlsx 正常生成
DC-011 | TestCompare::test_fail_count_zero | 比对 | FAIL 条目 = 0（所有网页值与 Modbus 直读值在容差内）
DC-012 | TestCompare::test_pass_rate | 比对 | 有效比对通过率 ≥ 95%（排除无寄存器映射条目）
DC-013 | TestCompare::test_modbus_read_failure_zero | 比对 | Modbus 读取失败条目 = 0