## 汇总
设备 | 真实IP | ModbusID | 可比对项 | 数值量一致 | 数值量项 | 一致率
AcuvimIIW | 192.168.2.27 | 2 | 106 | 101 | 106 | 95%
AcuRev2100 | 192.168.2.64 | 101 | 595 | 574 | 595 | 96%
Acuvim3 | 192.168.2.32 | 1 | 154 | 154 | 154 | 100%
Acurev4100 | 192.168.2.242 | 1 | 1061 | 1058 | 1060 | 100%

## 对比明细
设备 | 参数 | 量类型 | 类型 | 网关值(A路) | 电表实读值(B路) | 差值 | 差值% | 是否一致
AcuvimIIW | Phase C Reactive Power | 波动量 | float32 | 98531.6016 | 0 | 98531.6016 | 100.0% | ✗
AcuvimIIW | Phase A Voltage THD | 波动量 | uint16 | 0 | 1 | -1 | 100.0% | ✗
Acurev4100 | Slave ID | 其他 | uint16 | 13568 | 0 | 13568 | 100.0% | ✗
Acurev4100 | Voltage Negative Sequence Angle | 波动量 | float32 | 359.9576 | 0.0476 | 359.91 | 100.0% | ✗
AcuRev2100 | Phase Angle of Load 10 Current to V10 | 波动量 | uint16 | 2838 | 132 | 2706 | 95.3% | ✗
AcuRev2100 | Phase Angle of Load 8 Current to V8 | 波动量 | uint16 | 2608 | 173 | 2435 | 93.4% | ✗
AcuRev2100 | Phase Angle of Load 9 Current to V9 | 波动量 | uint16 | 2737 | 218 | 2519 | 92.0% | ✗
AcuRev2100 | Phase Angle of Load 6 Current to V6 | 波动量 | uint16 | 2766 | 231 | 2535 | 91.6% | ✗
AcuRev2100 | Phase Angle of Load 7 Current to V7 | 波动量 | uint16 | 2625 | 226 | 2399 | 91.4% | ✗
AcuRev2100 | Phase Angle of Load 18 Current to V18 | 波动量 | uint16 | 2766 | 473 | 2293 | 82.9% | ✗
AcuRev2100 | Phase Angle of Load 2 Current to V2 | 波动量 | uint16 | 2730 | 574 | 2156 | 79.0% | ✗
AcuRev2100 | Phase Angle of Load 1 Current to V1 | 波动量 | uint16 | 2902 | 777 | 2125 | 73.2% | ✗
AcuRev2100 | Phase Angle of Load 5 Current to V5 | 波动量 | uint16 | 2780 | 749 | 2031 | 73.1% | ✗
AcuRev2100 | Phase Angle of Load 4 Current to V4 | 波动量 | uint16 | 2774 | 840 | 1934 | 69.7% | ✗
AcuRev2100 | Phase Angle of Load 3 Current to V3 | 波动量 | uint16 | 2632 | 953 | 1679 | 63.8% | ✗
AcuvimIIW | System Reactive Power | 波动量 | float32 | 299070.4375 | 122578.2422 | 176492.1953 | 59.0% | ✗
AcuRev2100 | Phase Angle of Load 16 Current to V16 | 波动量 | uint16 | 3099 | 1343 | 1756 | 56.7% | ✗
AcuRev2100 | Phase Angle of Load 13 Current to V13 | 波动量 | uint16 | 2802 | 1388 | 1414 | 50.5% | ✗
AcuvimIIW | Phase B Current THD | 波动量 | uint16 | 1 | 2 | -1 | 50.0% | ✗
AcuRev2100 | Current Unbalance Factor | 波动量 | uint16 | 688 | 350 | 338 | 49.1% | ✗
AcuRev2100 | Phase Angle of Load 11 Current to V11 | 波动量 | uint16 | 2223 | 1190 | 1033 | 46.5% | ✗
AcuRev2100 | Phase Angle of Load 15 Current to V15 | 波动量 | uint16 | 2788 | 1500 | 1288 | 46.2% | ✗
AcuRev2100 | Phase Angle of Load 14 Current to V14 | 波动量 | uint16 | 2608 | 1423 | 1185 | 45.4% | ✗
Acurev4100 | Phase A Voltage THD Even | 波动量 | float32 | 0.0058 | 0.01 | -0.0041 | 41.4% | ✓
AcuRev2100 | Phase Angle of Load 17 Current to V17 | 波动量 | uint16 | 2697 | 1796 | 901 | 33.4% | ✗
AcuRev2100 | Input Channel 17 current | 波动量 | float32 | 179.0732 | 241.9483 | -62.8752 | 26.0% | ✗
AcuvimIIW | Voltage Unbalance Factor | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 21.6% | ✓
Acurev4100 | Phase A Voltage THD | 波动量 | float32 | 0.0137 | 0.0169 | -0.0032 | 18.9% | ✓
AcuvimIIW | Phase A Reactive Power | 波动量 | float32 | 200538.8281 | 166543.6094 | 33995.2188 | 17.0% | ✗
AcuRev2100 | Phase Angle of Load 12 Current to V12 | 波动量 | uint16 | 2781 | 2388 | 393 | 14.1% | ✗
Acurev4100 | Phase A Voltage THD Odd | 波动量 | float32 | 0.0124 | 0.0137 | -0.0013 | 9.2% | ✓
Acurev4100 | Average Voltage THD Even | 波动量 | float32 | 0.0061 | 0.0065 | -0.0005 | 6.9% | ✓
AcuRev2100 | Input Channel 17 Current Demand Predict | 波动量 | float32 | 195.5205 | 207.5621 | -12.0416 | 5.8% | ✗
Acurev4100 | Phase C Voltage THD | 波动量 | float32 | 0.0262 | 0.0248 | 0.0014 | 5.3% | ✓
Acurev4100 | Phase B Voltage THD Odd | 波动量 | float32 | 0.0176 | 0.0185 | -0.0009 | 5.0% | ✓
Acurev4100 | Phase C Voltage THD Even | 波动量 | float32 | 0.0049 | 0.0051 | -0.0003 | 5.0% | ✓
Acurev4100 | Phase B Voltage THD | 波动量 | float32 | 0.0183 | 0.0191 | -0.0009 | 4.5% | ✓
Acurev4100 | Phase B Voltage THD Even | 波动量 | float32 | 0.005 | 0.0048 | 0.0002 | 3.2% | ✓
AcuvimIIW | Current Unbalance Factor | 波动量 | float32 | 0.0002 | 0.0002 | 0 | 3.1% | ✓
Acurev4100 | Average Voltage THD Odd | 波动量 | float32 | 0.0192 | 0.0188 | 0.0004 | 2.3% | ✓
Acuvim3 | Phase N Current Crest-Factor | 波动量 | float32 | 4.2129 | 4.1656 | 0.0473 | 1.1% | ✓
AcuvimIIW | Phase B Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.8% | ✓
AcuvimIIW | Phase C Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.8% | ✓
AcuRev2100 | User Channel 9 Current Unbalance Factor | 波动量 | uint16 | 968 | 974 | -6 | 0.6% | ✓
Acurev4100 | Average Voltage THD | 波动量 | float32 | 0.0203 | 0.0202 | 0.0001 | 0.6% | ✓
Acurev4100 | Phase C Voltage THD Odd | 波动量 | float32 | 0.0257 | 0.0256 | 0.0001 | 0.4% | ✓
AcuRev2100 | Input Channel 11 current | 波动量 | float32 | 8697.0957 | 8734.6592 | -37.5635 | 0.4% | ✓
AcuRev2100 | Phase B Line Current | 波动量 | float32 | 48322.6094 | 48447.2812 | -124.6719 | 0.3% | ✓
AcuRev2100 | Average Line Current | 波动量 | float32 | 55542.0352 | 55629.5625 | -87.5273 | 0.2% | ✓
AcuRev2100 | Phase C Line Current | 波动量 | float32 | 59145.3398 | 59212.4531 | -67.1133 | 0.1% | ✓
AcuRev2100 | Input Channel 1 current | 波动量 | float32 | 9861.8467 | 9872.8799 | -11.0332 | 0.1% | ✓
AcuRev2100 | Input Channel 18 current | 波动量 | float32 | 9856.6904 | 9867.5332 | -10.8428 | 0.1% | ✓
AcuRev2100 | Phase A Line Current | 波动量 | float32 | 59158.1562 | 59223.1836 | -65.0273 | 0.1% | ✓
AcuRev2100 | Input Channel 10 current | 波动量 | float32 | 9856.4561 | 9867.2891 | -10.833 | 0.1% | ✓
AcuRev2100 | Input Channel 7 current | 波动量 | float32 | 9862.7959 | 9873.624 | -10.8281 | 0.1% | ✓
AcuRev2100 | Input Channel 12 current | 波动量 | float32 | 9857.6162 | 9868.3291 | -10.7129 | 0.1% | ✓
AcuRev2100 | Input Channel 5 current | 波动量 | float32 | 9864.6807 | 9875.375 | -10.6943 | 0.1% | ✓
AcuRev2100 | Input Channel 9 current | 波动量 | float32 | 9855.5918 | 9866.2744 | -10.6826 | 0.1% | ✓
AcuRev2100 | Input Channel 2 current | 波动量 | float32 | 9864.0508 | 9874.71 | -10.6592 | 0.1% | ✓
AcuRev2100 | Input Channel 3 current | 波动量 | float32 | 9857.585 | 9868.2246 | -10.6396 | 0.1% | ✓
AcuRev2100 | Input Channel 8 current | 波动量 | float32 | 9859.3936 | 9869.9717 | -10.5781 | 0.1% | ✓
AcuRev2100 | Input Channel 15 current | 波动量 | float32 | 9857.5293 | 9868.0254 | -10.4961 | 0.1% | ✓
AcuRev2100 | Input Channel 16 current | 波动量 | float32 | 9856.7568 | 9867.2285 | -10.4717 | 0.1% | ✓
AcuRev2100 | Input Channel 13 current | 波动量 | float32 | 9858.9766 | 9869.4014 | -10.4248 | 0.1% | ✓
AcuRev2100 | Input Channel 6 current | 波动量 | float32 | 9860.8271 | 9871.2041 | -10.377 | 0.1% | ✓
AcuRev2100 | Input Channel 4 current | 波动量 | float32 | 9862.333 | 9872.6299 | -10.2969 | 0.1% | ✓
AcuRev2100 | Input Channel 14 current | 波动量 | float32 | 9861.9688 | 9872.1123 | -10.1436 | 0.1% | ✓
AcuvimIIW | Phase Angle of V3 to V1 | 波动量 | uint16 | 1200 | 1199 | 1 | 0.1% | ✓
Acurev4100 | Phase C Voltage Crest Factor | 波动量 | float32 | 1.4144 | 1.4135 | 0.0009 | 0.1% | ✓
AcuvimIIW | Phase C Active Power | 波动量 | float32 | -6246052 | -6249826 | 3774 | 0.1% | ✓
AcuRev2100 | Input Channel 11 Current Demand Predict | 波动量 | float32 | 8704.582 | 8709.0615 | -4.4795 | 0.1% | ✓
AcuRev2100 | Phase B Current Demand Predict | 波动量 | float32 | 48362.707 | 48385.8203 | -23.1133 | 0.0% | ✓
AcuvimIIW | Phase B Apparent Power | 波动量 | float32 | 6251602.5 | 6248716 | 2886.5 | 0.0% | ✓
AcuvimIIW | Phase A Power Factor | 波动量 | float32 | 0.9995 | 0.9999 | -0.0004 | 0.0% | ✓
AcuvimIIW | Phase Angle of Phase C Current to V1 | 波动量 | uint16 | 3000 | 2999 | 1 | 0.0% | ✓
AcuvimIIW | System Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Power Factor | 波动量 | float32 | 0.9999 | 0.9996 | 0.0003 | 0.0% | ✓
AcuvimIIW | System Export Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | System Total Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | System Net Active Energy | 稳定量 | float32 | -2.0691e+24 | -2.0686e+24 | -4.3206e+20 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current Demand Predict | 波动量 | float32 | 9864.0107 | 9865.498 | -1.4873 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current Demand Predict | 波动量 | float32 | 9859.5742 | 9861.0596 | -1.4854 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current Demand Predict | 波动量 | float32 | 9861.25 | 9862.7285 | -1.4785 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current Demand Predict | 波动量 | float32 | 9865.0996 | 9866.5674 | -1.4678 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current Demand Predict | 波动量 | float32 | 9858.4346 | 9859.8877 | -1.4531 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current Demand Predict | 波动量 | float32 | 9862.25 | 9863.7031 | -1.4531 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current Demand Predict | 波动量 | float32 | 9867.1025 | 9868.543 | -1.4404 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current Demand Predict | 波动量 | float32 | 9862.5693 | 9864.0088 | -1.4395 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current Demand Predict | 波动量 | float32 | 9867.8311 | 9869.2666 | -1.4355 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current Demand Predict | 波动量 | float32 | 9861.4336 | 9862.8643 | -1.4307 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current Demand Predict | 波动量 | float32 | 9864.7354 | 9866.1543 | -1.4189 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current Demand Predict | 波动量 | float32 | 9860.291 | 9861.709 | -1.418 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current Demand Predict | 波动量 | float32 | 9865.5293 | 9866.9385 | -1.4092 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current Demand Predict | 波动量 | float32 | 9865.9922 | 9867.4014 | -1.4092 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current Demand Predict | 波动量 | float32 | 9859.9336 | 9861.3398 | -1.4062 | 0.0% | ✓
AcuRev2100 | Phase C Current Demand Predict | 波动量 | float32 | 59166.1172 | 59174.5156 | -8.3984 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current Demand Predict | 波动量 | float32 | 9860.7002 | 9862.0752 | -1.375 | 0.0% | ✓
AcuRev2100 | Phase A Current Demand Predict | 波动量 | float32 | 59178.0156 | 59186.1484 | -8.1328 | 0.0% | ✓
Acurev4100 | Phase B Voltage Crest Factor | 波动量 | float32 | 1.4144 | 1.4142 | 0.0002 | 0.0% | ✓
AcuvimIIW | Phase B-C Line-to-Line Voltage | 稳定量 | float32 | 216.4615 | 216.4436 | 0.018 | 0.0% | ✓
AcuvimIIW | Phase B Line Current | 波动量 | float32 | 49991.1992 | 49995.3203 | -4.1211 | 0.0% | ✓
AcuvimIIW | Phase C-A Line-to-Line Voltage | 稳定量 | float32 | 216.4462 | 216.4298 | 0.0165 | 0.0% | ✓
Acurev4100 | Phase C Line-to-Neutral Voltage | 稳定量 | float32 | 56.7211 | 56.7169 | 0.0041 | 0.0% | ✓
AcuvimIIW | Phase A Active Power | 波动量 | float32 | -6244053.5 | -6244497.5 | 444 | 0.0% | ✓
AcuvimIIW | Phase C Apparent Power | 波动量 | float32 | 6246828.5 | 6246384.5 | 444 | 0.0% | ✓
Acurev4100 | Phase C-A Line-to-Line Voltage | 稳定量 | float32 | 98.6596 | 98.6538 | 0.0058 | 0.0% | ✓
Acurev4100 | Phase B-C Line-to-Line Voltage | 稳定量 | float32 | 98.3897 | 98.3847 | 0.005 | 0.0% | ✓
Acurev4100 | Average Line-to-Neutral Voltage | 稳定量 | float32 | 56.9396 | 56.9367 | 0.0028 | 0.0% | ✓
Acurev4100 | Phase A Line-to-Neutral Voltage | 稳定量 | float32 | 57.2516 | 57.2488 | 0.0028 | 0.0% | ✓
Acurev4100 | Phase A-B Line-to-Line Voltage | 稳定量 | float32 | 98.8177 | 98.8138 | 0.0039 | 0.0% | ✓
AcuvimIIW | Phase B Line-to-Neutral Voltage | 稳定量 | float32 | 124.9759 | 124.9809 | -0.0049 | 0.0% | ✓
AcuvimIIW | System Power Factor | 波动量 | float32 | 0.9998 | 0.9998 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Line-to-Neutral Voltage | 稳定量 | float32 | 124.9649 | 124.9686 | -0.0037 | 0.0% | ✓
Acurev4100 | Average Line-to-Line Voltage | 稳定量 | float32 | 98.6202 | 98.6174 | 0.0028 | 0.0% | ✓
AcuvimIIW | Phase A Line-to-Neutral Voltage | 稳定量 | float32 | 124.9804 | 124.977 | 0.0034 | 0.0% | ✓
Acurev4100 | Phase C Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 119.9116 | 119.9142 | -0.0026 | 0.0% | ✓
AcuvimIIW | Phase C Line Current | 波动量 | float32 | 49986.9062 | 49987.7969 | -0.8906 | 0.0% | ✓
AcuvimIIW | Phase B Active Power | 波动量 | float32 | -6251602.5 | -6251491.5 | -111 | 0.0% | ✓
AcuvimIIW | Phase A-B Line-to-Line Voltage | 稳定量 | float32 | 216.4749 | 216.4779 | -0.003 | 0.0% | ✓
AcuvimIIW | Phase A Line Current | 波动量 | float32 | 49988.0898 | 49987.4141 | 0.6758 | 0.0% | ✓
Acurev4100 | System Frequency | 稳定量 | float32 | 49.9995 | 50.0001 | -0.0007 | 0.0% | ✓
Acurev4100 | Phase A Voltage Crest Factor | 波动量 | float32 | 1.414 | 1.414 | 0 | 0.0% | ✓
AcuvimIIW | Average Line-to-Neutral Voltage | 稳定量 | float32 | 124.9738 | 124.9748 | -0.0011 | 0.0% | ✓
AcuvimIIW | System Active Power | 波动量 | float32 | -18741708 | -18741596 | -112 | 0.0% | ✓
AcuvimIIW | System Apparent Power | 波动量 | float32 | 18745704 | 18745592 | 112 | 0.0% | ✓
Acurev4100 | Phase B Line-to-Neutral Voltage | 稳定量 | float32 | 56.846 | 56.8458 | 0.0003 | 0.0% | ✓
AcuvimIIW | System Net Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage THFF Factor | 波动量 | float32 | 0.4438 | 0.4438 | 0 | 0.0% | ✓
AcuvimIIW | Average Line-to-Line Voltage | 稳定量 | float32 | 216.4609 | 216.4604 | 0.0005 | 0.0% | ✓
AcuvimIIW | Phase A Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage THFF Factor | 波动量 | float32 | 0.4438 | 0.4438 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Export Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Average Line Current | 波动量 | float32 | 49988.7305 | 49988.7969 | -0.0664 | 0.0% | ✓
AcuvimIIW | Phase C Export Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Export Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage THFF Factor | 波动量 | float32 | 0.4438 | 0.4438 | 0 | 0.0% | ✓
Acurev4100 | Phase B Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 239.9877 | 239.988 | -0.0002 | 0.0% | ✓
Acurev4100 | Voltage Negative Sequence Magnitude | 波动量 | float32 | 56.9536 | 56.9536 | 0 | 0.0% | ✓
AcuvimIIW | System Total Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | System Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | System Frequency | 稳定量 | float32 | 50 | 50 | 0 | 0.0% | ✓
AcuvimIIW | Neutral Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Apparent Power | 波动量 | float32 | 6247273 | 6247273 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Power Factor | 波动量 | float32 | -1 | -1 | 0 | 0.0% | ✓
AcuvimIIW | System Active Power Demand | 波动量 | float32 | -6247186.5 | -6247186.5 | 0 | 0.0% | ✓
AcuvimIIW | System Reactive Power Demand | 波动量 | float32 | 82811.6016 | 82811.6016 | 0 | 0.0% | ✓
AcuvimIIW | System Apparent Power Demand | 波动量 | float32 | 6248407.5 | 6248407.5 | 0 | 0.0% | ✓
AcuvimIIW | System Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | System Export Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage THD | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage THD | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Average Voltage THD | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current THD | 波动量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current THD | 波动量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
AcuvimIIW | Average Current THD | 波动量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage Odd THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage Even THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage Crest Factor | 波动量 | uint16 | 1416 | 1416 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage Telephone Harmonic Form Factor | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage Odd THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage Even THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage Crest Factor | 波动量 | uint16 | 1416 | 1416 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage Telephone Harmonic Form Factor | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage Odd THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage Even THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage Crest Factor | 波动量 | uint16 | 1416 | 1416 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage Telephone Harmonic Form Factor | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current Odd THD | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current Even THD | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current K Factor | 波动量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current Odd THD | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current Even THD | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current K Factor | 波动量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current Odd THD | 波动量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current Even THD | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current K Factor | 波动量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Voltage Positive Sequence | 波动量 | uint16 | 999 | 999 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Voltage Postive Sequence | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Voltage Negative Sequence | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Voltage Negative Sequence | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Voltage Zero Sequence | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Voltage Zero Sequence | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Current Positive Sequence | 波动量 | uint16 | 64537 | 64537 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Current Postive Sequence | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Current Negative Sequence | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Current Negative Sequence | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Current Zero Sequence | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Current Zero Sequence | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase Angle of V2 to V1 | 波动量 | uint16 | 2399 | 2399 | 0 | 0.0% | ✓
AcuvimIIW | Phase Angle of Phase A Current to V1 | 波动量 | uint16 | 1800 | 1800 | 0 | 0.0% | ✓
AcuvimIIW | Phase Angle of Phase B Current to V1 | 波动量 | uint16 | 600 | 600 | 0 | 0.0% | ✓
AcuvimIIW | Phase Angle of V1 to V1 | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Export Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Export Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Export Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Frequency | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Average Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A-B Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B-C Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C-A Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Average Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Import Active | 其他 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Import Active Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Import Reactive Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Apparent Energy | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Current Demand | 波动量 | float32 | 59181.7109 | 59181.7109 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Current Demand | 波动量 | float32 | 48356.6523 | 48356.6523 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Current Demand | 波动量 | float32 | 59169.8984 | 59169.8984 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current Demand | 波动量 | float32 | 9865.373 | 9865.373 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current Demand | 波动量 | float32 | 9867.7402 | 9867.7402 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current Demand | 波动量 | float32 | 9862.0469 | 9862.0469 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current Demand | 波动量 | float32 | 9866.1084 | 9866.1084 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current Demand | 波动量 | float32 | 9868.4443 | 9868.4443 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current Demand | 波动量 | float32 | 9864.6582 | 9864.6582 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current Demand | 波动量 | float32 | 9866.583 | 9866.583 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current Demand | 波动量 | float32 | 9863.2197 | 9863.2197 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current Demand | 波动量 | float32 | 9859.0557 | 9859.0557 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current Demand | 波动量 | float32 | 9860.2334 | 9860.2334 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current Demand | 波动量 | float32 | 8700.5205 | 8700.5205 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current Demand | 波动量 | float32 | 9861.917 | 9861.917 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current Demand | 波动量 | float32 | 9862.8682 | 9862.8682 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current Demand | 波动量 | float32 | 9865.7412 | 9865.7412 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current Demand | 波动量 | float32 | 9861.3105 | 9861.3105 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current Demand | 波动量 | float32 | 9860.5488 | 9860.5488 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current Demand | 波动量 | float32 | 190.9892 | 190.9892 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current Demand | 波动量 | float32 | 9860.9053 | 9860.9053 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Voltage Unbalance Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Average Voltage THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage Odd THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage Even THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage Crest Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage Telephone Harmonic Form Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage Odd THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage Even THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage Crest Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage Telephone Harmonic Form Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage Odd THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage Even THD | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage Crest Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage Telephone Harmonic Form Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current Odd THD | 波动量 | uint16 | 2112 | 2112 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current Even THD | 波动量 | uint16 | 2407 | 2407 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current K Factor | 波动量 | uint16 | 296 | 296 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current Odd THD | 波动量 | uint16 | 2233 | 2233 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current Even THD | 波动量 | uint16 | 2591 | 2591 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current K Factor | 波动量 | uint16 | 315 | 315 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current Odd THD | 波动量 | uint16 | 2211 | 2211 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current Even THD | 波动量 | uint16 | 2019 | 2019 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current K Factor | 波动量 | uint16 | 292 | 292 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current Odd THD | 波动量 | uint16 | 1608 | 1608 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current Even THD | 波动量 | uint16 | 1584 | 1584 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current K Factor | 波动量 | uint16 | 181 | 181 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current Odd THD | 波动量 | uint16 | 2103 | 2103 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current Even THD | 波动量 | uint16 | 2192 | 2192 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current K Factor | 波动量 | uint16 | 295 | 295 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current Odd THD | 波动量 | uint16 | 1856 | 1856 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current Even THD | 波动量 | uint16 | 2163 | 2163 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current K Factor | 波动量 | uint16 | 254 | 254 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current Odd THD | 波动量 | uint16 | 4691 | 4691 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current Even THD | 波动量 | uint16 | 4850 | 4850 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current K Factor | 波动量 | uint16 | 1118 | 1118 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current Odd THD | 波动量 | uint16 | 7762 | 7762 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current Even THD | 波动量 | uint16 | 7360 | 7360 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current K Factor | 波动量 | uint16 | 1922 | 1922 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current Odd THD | 波动量 | uint16 | 1669 | 1669 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current Even THD | 波动量 | uint16 | 1867 | 1867 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current K Factor | 波动量 | uint16 | 216 | 216 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current Odd THD | 波动量 | uint16 | 4289 | 4289 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current Even THD | 波动量 | uint16 | 4424 | 4424 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current K Factor | 波动量 | uint16 | 930 | 930 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current Odd THD | 波动量 | uint16 | 8021 | 8021 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current Even THD | 波动量 | uint16 | 7885 | 7885 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current K Factor | 波动量 | uint16 | 2046 | 2046 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current Odd THD | 波动量 | uint16 | 4938 | 4938 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current Even THD | 波动量 | uint16 | 4889 | 4889 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current K Factor | 波动量 | uint16 | 1164 | 1164 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current Odd THD | 波动量 | uint16 | 2193 | 2193 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current Even THD | 波动量 | uint16 | 2063 | 2063 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current K Factor | 波动量 | uint16 | 274 | 274 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current Odd THD | 波动量 | uint16 | 2687 | 2687 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current Even THD | 波动量 | uint16 | 2769 | 2769 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current K Factor | 波动量 | uint16 | 478 | 478 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current Odd THD | 波动量 | uint16 | 4138 | 4138 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current Even THD | 波动量 | uint16 | 4107 | 4107 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current K Factor | 波动量 | uint16 | 854 | 854 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current Odd THD | 波动量 | uint16 | 3154 | 3154 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current Even THD | 波动量 | uint16 | 3223 | 3223 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current K Factor | 波动量 | uint16 | 541 | 541 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current Odd THD | 波动量 | uint16 | 7061 | 7061 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current Even THD | 波动量 | uint16 | 7084 | 7084 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current K Factor | 波动量 | uint16 | 1743 | 1743 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current Odd THD | 波动量 | uint16 | 5328 | 5328 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current Even THD | 波动量 | uint16 | 5497 | 5497 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current K Factor | 波动量 | uint16 | 1320 | 1320 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current THD | 波动量 | uint16 | 3202 | 3202 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current THD | 波动量 | uint16 | 3420 | 3420 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current THD | 波动量 | uint16 | 2994 | 2994 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current THD | 波动量 | uint16 | 2257 | 2257 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current THD | 波动量 | uint16 | 3037 | 3037 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current THD | 波动量 | uint16 | 2850 | 2850 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current THD | 波动量 | uint16 | 6747 | 6747 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current THD | 波动量 | uint16 | 9999 | 9999 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current THD | 波动量 | uint16 | 2504 | 2504 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current THD | 波动量 | uint16 | 6161 | 6161 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current THD | 波动量 | uint16 | 9999 | 9999 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current THD | 波动量 | uint16 | 6948 | 6948 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current THD | 波动量 | uint16 | 3010 | 3010 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current THD | 波动量 | uint16 | 3858 | 3858 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current THD | 波动量 | uint16 | 5830 | 5830 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current THD | 波动量 | uint16 | 4509 | 4509 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current THD | 波动量 | uint16 | 9999 | 9999 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current THD | 波动量 | uint16 | 7655 | 7655 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Current Unbalance Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Current Unbalance Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Current Unbalance Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Current Unbalance Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Current Unbalance Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Current Unbalance Factor | 波动量 | uint16 | 61 | 61 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Current Unbalance Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Current Unbalance Factor | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of V2 to V1 | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of V3 to V1 | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Frequency | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Average Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A-B Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B-C Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C-A Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Average Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Line Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Line Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Line Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Neutral Current | 波动量 | float32 | 0.0005 | 0.0005 | 0 | 0.0% | ✓
Acuvim3 | Average Line Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Leading Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Leading Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Leading Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Leading Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Lagging Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Lagging Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Lagging Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Lagging Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase AB Line-to-Line Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase BC Line-to-Line Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase CA Line-to-Line Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Zero Sequence Ratio Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Zero Sequence Ratio Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Voltage THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Voltage THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Voltage THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Voltage THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Voltage THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Voltage THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Voltage THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Voltage THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Voltage THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Voltage Crest Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Voltage Crest Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Voltage Crest Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase N Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase N Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase N Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current TDD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current TDD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current TDD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase N Current TDD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current Crest-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current Crest-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current Crest-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current K-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current K-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current K-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase N Current K-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Voltage Flicker | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Voltage Flicker | 波动量 | float32 | 17.0167 | 17.0167 | 0 | 0.0% | ✓
Acuvim3 | Phase C Voltage Flicker | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Average Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Energy-Import | 稳定量 | float64 | 13.4214 | 13.4214 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Energy-Import | 稳定量 | float64 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Energy-Import | 稳定量 | float64 | 14.5859 | 14.5859 | 0 | 0.0% | ✓
Acuvim3 | System Active Energy-Import | 稳定量 | float64 | 9.0281 | 9.0281 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Energy-Import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Energy-Import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Energy-Import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Energy-Import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Energy-Export | 稳定量 | float64 | 0.1512 | 0.1512 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Energy-Export | 稳定量 | float64 | 0.0024 | 0.0024 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Energy-Export | 稳定量 | float64 | 0.1452 | 0.1452 | 0 | 0.0% | ✓
Acuvim3 | System Active Energy-Export | 稳定量 | float64 | 0.0055 | 0.0055 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Energy-Export | 稳定量 | float64 | 3.6346 | 3.6346 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Energy-Export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Energy-Export | 稳定量 | float64 | 2.6844 | 2.6844 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Energy-Export | 稳定量 | float64 | 4.8445 | 4.8445 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Energy-Net | 稳定量 | float64 | 13.2703 | 13.2703 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Energy-Net | 稳定量 | float64 | -0.0023 | -0.0023 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Energy-Net | 稳定量 | float64 | 14.4407 | 14.4407 | 0 | 0.0% | ✓
Acuvim3 | System Active Energy-Net | 稳定量 | float64 | 9.0225 | 9.0225 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Energy-Net | 稳定量 | float64 | -3.6346 | -3.6346 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Energy-Net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Energy-Net | 稳定量 | float64 | -2.6844 | -2.6844 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Energy-Net | 稳定量 | float64 | -4.8445 | -4.8445 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Energy-Total | 稳定量 | float64 | 13.5726 | 13.5726 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Energy-Total | 稳定量 | float64 | 0.0025 | 0.0025 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Energy-Total | 稳定量 | float64 | 14.7311 | 14.7311 | 0 | 0.0% | ✓
Acuvim3 | System Active Energy-Total | 稳定量 | float64 | 9.0337 | 9.0337 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Energy-Total | 稳定量 | float64 | 3.6346 | 3.6346 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Energy-Total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Energy-Total | 稳定量 | float64 | 2.6844 | 2.6844 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Energy-Total | 稳定量 | float64 | 4.8445 | 4.8445 | 0 | 0.0% | ✓
Acuvim3 | Phase A Apparent Energy | 稳定量 | float64 | 14.5733 | 14.5733 | 0 | 0.0% | ✓
Acuvim3 | Phase B Apparent Energy | 稳定量 | float64 | 0.0031 | 0.0031 | 0 | 0.0% | ✓
Acuvim3 | Phase C Apparent Energy | 稳定量 | float64 | 15.489 | 15.489 | 0 | 0.0% | ✓
Acuvim3 | System Apparent Energy | 稳定量 | float64 | 10.3145 | 10.3145 | 0 | 0.0% | ✓
Acurev4100 | DO1 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO2 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO3 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO4 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO5 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO6 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO7 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO8 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | RO1 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | RO2 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI1 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI2 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI3 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI4 status | 其他 | bit | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Average Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Average Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Unbalance Factor Magnitude | 波动量 | float32 | 150 | 150 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI1 pulse count | 其他 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI2 pulse count | 其他 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI3 pulse count | 其他 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI4 pulse count | 其他 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Serial Number | 其他 | string | Acurev4100 | d1.01p05 |  |  | ✗

## 用例Mapping
用例ID | 用例函数名 | 测试类型 | 验证点 | 关联TC编号
DM-001 | test_dm_001_config_and_export | 功能 | 启用Device Mirror + 选全Ethernet设备 + 唯一SlaveID + Download All + 映射表可解析 | TestCase_AcuHMI_008_04_case06
DM-002 | test_dm_002_modbus_read | 功能 | 按导出CSV经网关逐参数Modbus读取，读取成功率达标 | TestCase_AcuHMI_008_04_case05(子)
DM-003 | test_dm_003_mirror_matches_direct | 数据正确性 | 镜像路径(A) ↔ 直连真实电表(B) 逐寄存器数值一致率达标 | TestCase_AcuHMI_008_04_case05
DM-004 | test_dm_case01_enable_disable_toggle | 功能 | Disable+Save后经Mirror读取停止；Enable+Save后恢复读取 | TestCase_AcuHMI_008_04_case01
DM-005 | test_dm_case02_valid_slaveid_save | 边界 | 有效SlaveID(2–99)保存成功且持久化生效 | TestCase_AcuHMI_008_04_case02
DM-006 | test_dm_case03_slaveid_boundary | 边界 | 越界SlaveID(1/100)被拒；边界值(2/99)保存成功 | TestCase_AcuHMI_008_04_case03
DM-007 | test_dm_case04_duplicate_slaveid | 异常 | 两设备配置相同SlaveID应被拒绝或不同时生效 | TestCase_AcuHMI_008_04_case04
DM-008 | test_dm_case07_offline_stability | 稳定性 | 设备离线后系统稳定、其他设备不受影响（需人工执行，自动化skip） | TestCase_AcuHMI_008_04_case07
DM-009 | test_dm_case08_concurrent_masters | 并发 | 多Modbus主站并发读不同SlaveID，各自正常、无串扰 | TestCase_AcuHMI_008_04_case08