## 汇总
设备 | 真实IP | ModbusID | 可比对项 | 数值量一致 | 数值量项 | 一致率
AcuvimIIW | 192.168.2.27 | 2 | 617 | 615 | 617 | 100%
AcuRev2100 | 192.168.2.64 | 101 | 1521 | 1516 | 1521 | 100%
Acuvim3 | 192.168.2.32 | 1 | 160 | 160 | 160 | 100%
Acurev4100 | 192.168.2.242 | 1 | 3159 | 3159 | 3159 | 100%

## 对比明细
设备 | 参数 | 量类型 | 类型 | 透传值(A路) | 电表实读值(B路) | 差值 | 差值% | 是否一致
AcuvimIIW | Phase A Reactive Power | 波动量 | float32 | 117766.2109 | 0 | 117766.2109 | 100.0% | ✓
AcuvimIIW | Phase A Voltage Odd THD | 波动量 | int16 | 0 | 1 | -1 | 100.0% | ✗
AcuRev2100 | Phase Angle of Load 7 Current to V7 | 波动量 | int16 | 3035 | 398 | 2637 | 86.9% | ✗
AcuRev2100 | Phase Angle of Load 15 Current to V15 | 波动量 | int16 | 813 | 2082 | -1269 | 61.0% | ✗
Acurev4100 | Phase C Voltage individual Harmonics 18 percentage | 波动量 | float32 | 0.0004 | 0.001 | -0.0006 | 60.3% | ✓
AcuvimIIW | System Reactive Power | 波动量 | float32 | 123516.9922 | 220299.8438 | -96782.8516 | 43.9% | ✗
AcuRev2100 | Phase Angle of Load 5 Current to V5 | 波动量 | int16 | 1784 | 3026 | -1242 | 41.0% | ✗
Acurev4100 | Phase A Voltage individual Harmonics 28 percentage | 波动量 | float32 | 0.0004 | 0.0007 | -0.0003 | 39.5% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 11 percentage | 波动量 | float32 | 0.0019 | 0.0013 | 0.0006 | 33.2% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 11 percentage | 波动量 | float32 | 0.0028 | 0.002 | 0.0008 | 29.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 6 percentage | 波动量 | float32 | 0.0009 | 0.0007 | 0.0002 | 25.3% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 4 percentage | 波动量 | float32 | 0.0018 | 0.0015 | 0.0003 | 18.3% | ✓
Acurev4100 | Phase B Voltage THD Even | 波动量 | float32 | 0.0047 | 0.0053 | -0.0006 | 11.3% | ✓
AcuRev2100 | Input Channel 8 Current 31-th Harmonic | 波动量 | int16 | 1954 | 2137 | -183 | 8.6% | ✗
AcuRev2100 | Phase Angle of Load 12 Current to V12 | 波动量 | int16 | 2525 | 2384 | 141 | 5.6% | ✗
AcuvimIIW | System Apparent Power | 波动量 | float32 | 6246940 | 6250270.5 | -3330.5 | 0.1% | ✓
AcuRev2100 | Input Channel 17 current | 波动量 | float32 | 117.9312 | 117.992 | -0.0608 | 0.1% | ✓
AcuvimIIW | System Active Power | 波动量 | float32 | -6243165 | -6245830 | 2665 | 0.0% | ✓
AcuvimIIW | System Power Factor | 波动量 | float32 | 0.9998 | 0.9994 | 0.0004 | 0.0% | ✓
Acurev4100 | Phase B Voltage Crest Factor | 波动量 | float32 | 1.4142 | 1.414 | 0.0001 | 0.0% | ✓
AcuvimIIW | Average Line-to-Neutral Voltage | 稳定量 | float32 | 124.9615 | 124.9495 | 0.0121 | 0.0% | ✓
AcuRev2100 | Input Channel 11 current | 波动量 | float32 | 8685.3896 | 8685.6895 | -0.2998 | 0.0% | ✓
AcuvimIIW | Phase A Active Power | 波动量 | float32 | -6245496.5 | -6245607.5 | 111 | 0.0% | ✓
AcuvimIIW | Phase A Power Factor | 波动量 | float32 | 0.9998 | 0.9998 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 current | 波动量 | float32 | 9859.9141 | 9860.0889 | -0.1748 | 0.0% | ✓
AcuRev2100 | Phase B Line Current | 波动量 | float32 | 48432.668 | 48433.5117 | -0.8438 | 0.0% | ✓
AcuvimIIW | Phase A Line-to-Neutral Voltage | 稳定量 | float32 | 124.9622 | 124.96 | 0.0022 | 0.0% | ✓
AcuvimIIW | Average Line Current | 波动量 | float32 | 49991.875 | 49991.0156 | 0.8594 | 0.0% | ✓
AcuRev2100 | Input Channel 7 current | 波动量 | float32 | 9869.6494 | 9869.4844 | 0.165 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current Demand Predict | 波动量 | float32 | 9866.4375 | 9866.5938 | -0.1562 | 0.0% | ✓
AcuRev2100 | Input Channel 8 current | 波动量 | float32 | 9865.3955 | 9865.2451 | 0.1504 | 0.0% | ✓
Acurev4100 | Phase B Line-to-Neutral Voltage | 稳定量 | float32 | 56.8602 | 56.8593 | 0.0009 | 0.0% | ✓
AcuRev2100 | Input Channel 4 current | 波动量 | float32 | 9871.9375 | 9871.8096 | 0.1279 | 0.0% | ✓
AcuRev2100 | Input Channel 3 current | 波动量 | float32 | 9868.1904 | 9868.0723 | 0.1182 | 0.0% | ✓
AcuRev2100 | Input Channel 10 current | 波动量 | float32 | 9859.5537 | 9859.4395 | 0.1143 | 0.0% | ✓
AcuvimIIW | Phase A Line Current | 波动量 | float32 | 49992.582 | 49992.0469 | 0.5352 | 0.0% | ✓
AcuRev2100 | Input Channel 18 current | 波动量 | float32 | 9854.0811 | 9853.9805 | 0.1006 | 0.0% | ✓
AcuRev2100 | Input Channel 15 current | 波动量 | float32 | 9854.8711 | 9854.9697 | -0.0986 | 0.0% | ✓
AcuRev2100 | Input Channel 12 current | 波动量 | float32 | 9858.5254 | 9858.624 | -0.0986 | 0.0% | ✓
AcuRev2100 | Input Channel 2 current | 波动量 | float32 | 9874.5801 | 9874.6406 | -0.0605 | 0.0% | ✓
AcuRev2100 | Input Channel 1 current | 波动量 | float32 | 9872.5195 | 9872.46 | 0.0596 | 0.0% | ✓
AcuRev2100 | Input Channel 13 current | 波动量 | float32 | 9857.9023 | 9857.8467 | 0.0557 | 0.0% | ✓
AcuRev2100 | Input Channel 6 current | 波动量 | float32 | 9868.8975 | 9868.8457 | 0.0518 | 0.0% | ✓
AcuRev2100 | Input Channel 9 current | 波动量 | float32 | 9860.4043 | 9860.3545 | 0.0498 | 0.0% | ✓
AcuRev2100 | Input Channel 16 current | 波动量 | float32 | 9853.7725 | 9853.7256 | 0.0469 | 0.0% | ✓
AcuRev2100 | Phase C Line Current | 波动量 | float32 | 59212.4766 | 59212.6523 | -0.1758 | 0.0% | ✓
AcuRev2100 | Input Channel 5 current | 波动量 | float32 | 9873.8145 | 9873.8379 | -0.0234 | 0.0% | ✓
Acurev4100 | Phase B Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 239.9749 | 239.9745 | 0.0004 | 0.0% | ✓
AcuRev2100 | Average Line Current | 波动量 | float32 | 55625.25 | 55625.1875 | 0.0625 | 0.0% | ✓
AcuRev2100 | Phase A Line Current | 波动量 | float32 | 59223.3984 | 59223.4062 | -0.0078 | 0.0% | ✓
AcuvimIIW | IsOnline | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | System Frequency | 稳定量 | float32 | 50 | 50 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A-B Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B-C Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C-A Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Average Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Line Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Line Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Neutral Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Apparent Power | 波动量 | float32 | 6246940 | 6246940 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Unbalance Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Current Unbalance Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Average Load Nature | 其他 | float32 | 82 | 82 | 0 | 0.0% | ✓
AcuvimIIW | System Active Power Demand | 波动量 | float32 | -6247127 | -6247127 | 0 | 0.0% | ✓
AcuvimIIW | System Reactive Power Demand | 波动量 | float32 | 84453.7344 | 84453.7344 | 0 | 0.0% | ✓
AcuvimIIW | System Apparent Power Demand | 波动量 | float32 | 6248372.5 | 6248372.5 | 0 | 0.0% | ✓
AcuvimIIW | System Import Active Energy | 稳定量 | uint32 | 1684879 | 1684879 | 0 | 0.0% | ✓
AcuvimIIW | System Export Active Energy | 稳定量 | uint32 | 406648443 | 406648443 | 0 | 0.0% | ✓
AcuvimIIW | System Import Reactive Energy | 稳定量 | uint32 | 21359279 | 21359279 | 0 | 0.0% | ✓
AcuvimIIW | System Export Reactive Energy | 稳定量 | uint32 | 21089584 | 21089584 | 0 | 0.0% | ✓
AcuvimIIW | System Total Active Energy | 稳定量 | uint32 | 408333354 | 408333354 | 0 | 0.0% | ✓
AcuvimIIW | System Net Active Energy | 稳定量 | uint16 | 59356 | 59356 | 0 | 0.0% | ✓
AcuvimIIW | System Total Reactive Energy | 稳定量 | uint32 | 42448864 | 42448864 | 0 | 0.0% | ✓
AcuvimIIW | System Net Reactive Energy | 稳定量 | uint16 | 4 | 4 | 0 | 0.0% | ✓
AcuvimIIW | System Apparent Energy | 稳定量 | uint32 | 420094350 | 420094350 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage THD | 波动量 | int16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Average Voltage THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current THD | 波动量 | int16 | 2 | 2 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Average Current THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 2-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 3-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 4-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 5-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 6-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 7-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 8-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 9-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 10-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 11-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 12-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 13-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 14-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 15-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 16-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 17-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 18-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 19-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 20-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 21-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 22-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 23-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 24-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 25-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 26-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 27-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 28-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 29-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 30-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 31-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage Even THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage Crest Factor | 波动量 | int16 | 1416 | 1416 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage Telephone Harmonic Form Factor | 波动量 | int16 | 2 | 2 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 2-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 3-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 4-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 5-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 6-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 7-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 8-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 9-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 10-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 11-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 12-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 13-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 14-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 15-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 16-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 17-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 18-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 19-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 20-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 21-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 22-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 23-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 24-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 25-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 26-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 27-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 28-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 29-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 30-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 31-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage Odd THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage Even THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage Crest Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage Telephone Harmonic Form Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 2-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 3-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 4-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 5-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 6-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 7-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 8-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 9-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 10-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 11-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 12-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 13-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 14-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 15-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 16-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 17-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 18-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 19-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 20-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 21-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 22-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 23-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 24-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 25-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 26-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 27-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 28-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 29-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 30-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 31-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage Odd THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage Even THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage Crest Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage Telephone Harmonic Form Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 2-th Harmonic | 波动量 | int16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 3-th Harmonic | 波动量 | int16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 4-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 5-th Harmonic | 波动量 | int16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 6-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 7-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 8-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 9-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 10-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 11-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 12-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 13-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 14-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 15-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 16-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 17-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 18-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 19-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 20-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 21-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 22-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 23-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 24-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 25-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 26-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 27-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 28-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 29-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 30-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 31-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current Odd THD | 波动量 | int16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current Even THD | 波动量 | int16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current K Factor | 波动量 | int16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 2-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 3-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 4-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 5-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 6-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 7-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 8-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 9-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 10-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 11-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 12-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 13-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 14-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 15-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 16-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 17-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 18-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 19-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 20-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 21-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 22-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 23-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 24-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 25-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 26-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 27-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 28-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 29-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 30-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 31-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current Odd THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current Even THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current K Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 2-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 3-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 4-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 5-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 6-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 7-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 8-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 9-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 10-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 11-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 12-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 13-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 14-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 15-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 16-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 17-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 18-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 19-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 20-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 21-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 22-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 23-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 24-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 25-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 26-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 27-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 28-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 29-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 30-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 31-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current Odd THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current Even THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current K Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Voltage Positive Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Voltage Postive Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Voltage Negative Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Voltage Negative Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Voltage Zero Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Voltage Zero Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Current Positive Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Current Postive Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Current Negative Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Current Negative Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Real part of Current Zero Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Imag part of Current Zero Sequence | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase Angle of V2 to V1 | 波动量 | int16 | 2399 | 2399 | 0 | 0.0% | ✓
AcuvimIIW | Phase Angle of V3 to V1 | 波动量 | int16 | 1199 | 1199 | 0 | 0.0% | ✓
AcuvimIIW | Phase Angle of Phase A Current to V1 | 波动量 | int16 | 1800 | 1800 | 0 | 0.0% | ✓
AcuvimIIW | Phase Angle of Phase B Current to V1 | 波动量 | int16 | 600 | 600 | 0 | 0.0% | ✓
AcuvimIIW | Phase Angle of Phase C Current to V1 | 波动量 | int16 | 3000 | 3000 | 0 | 0.0% | ✓
AcuvimIIW | Phase Angle of V1 to V1 | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 32-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 33-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 34-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 35-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 36-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 37-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 38-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 39-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 40-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 41-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 42-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 43-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 44-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 45-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 46-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 47-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 48-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 49-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 50-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 51-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 52-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 53-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 54-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 55-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 56-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 57-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 58-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 59-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 60-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 61-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 62-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Voltage 63-th Harmonic | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 32-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 33-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 34-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 35-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 36-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 37-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 38-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 39-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 40-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 41-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 42-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 43-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 44-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 45-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 46-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 47-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 48-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 49-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 50-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 51-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 52-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 53-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 54-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 55-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 56-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 57-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 58-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 59-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 60-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 61-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 62-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Voltage 63-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 32-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 33-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 34-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 35-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 36-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 37-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 38-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 39-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 40-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 41-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 42-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 43-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 44-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 45-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 46-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 47-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 48-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 49-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 50-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 51-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 52-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 53-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 54-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 55-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 56-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 57-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 58-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 59-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 60-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 61-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 62-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Voltage 63-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 32-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 33-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 34-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 35-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 36-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 37-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 38-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 39-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 40-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 41-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 42-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 43-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 44-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 45-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 46-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 47-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 48-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 49-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 50-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 51-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 52-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 53-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 54-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 55-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 56-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 57-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 58-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 59-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 60-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 61-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 62-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Current 63-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 32-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 33-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 34-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 35-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 36-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 37-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 38-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 39-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 40-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 41-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 42-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 43-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 44-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 45-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 46-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 47-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 48-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 49-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 50-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 51-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 52-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 53-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 54-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 55-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 56-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 57-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 58-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 59-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 60-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 61-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 62-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Current 63-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 32-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 33-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 34-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 35-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 36-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 37-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 38-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 39-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 40-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 41-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 42-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 43-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 44-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 45-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 46-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 47-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 48-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 49-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 50-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 51-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 52-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 53-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 54-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 55-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 56-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 57-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 58-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 59-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 60-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 61-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 62-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Current 63-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Import Active Energy | 稳定量 | uint32 | 32475 | 32475 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Export Active Energy | 稳定量 | uint32 | 81800423 | 81800423 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Import Active Energy | 稳定量 | uint32 | 29892 | 29892 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Export Active Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Import Active Energy | 稳定量 | uint32 | 33083 | 33083 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Export Active Energy | 稳定量 | uint32 | 82325244 | 82325244 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Import Reactive Energy | 稳定量 | uint32 | 10551 | 10551 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Export Reactive Energy | 稳定量 | uint32 | 21080411 | 21080411 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Import Reactive Energy | 稳定量 | uint32 | 15580 | 15580 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Export Reactive Energy | 稳定量 | uint32 | 214 | 214 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Import Reactive Energy | 稳定量 | uint32 | 21130957 | 21130957 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Export Reactive Energy | 稳定量 | uint32 | 3142 | 3142 | 0 | 0.0% | ✓
AcuvimIIW | Phase A Apparent Energy | 稳定量 | uint32 | 87480102 | 87480102 | 0 | 0.0% | ✓
AcuvimIIW | Phase B Apparent Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Phase C Apparent Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Nominal Frequency | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Channel 1 Communication Protocol | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Channel 1 Parity | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Password | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Channel 1 Address | 其他 | uint16 | 8 | 8 | 0 | 0.0% | ✓
AcuvimIIW | Channel 1 Baud Rate | 其他 | uint16 | 19200 | 19200 | 0 | 0.0% | ✓
AcuvimIIW | Service Configuration | 其他 | uint32 | 65537 | 65537 | 0 | 0.0% | ✓
AcuvimIIW | PT1 | 其他 | uint32 | 5000 | 5000 | 0 | 0.0% | ✓
AcuvimIIW | PT2 | 其他 | uint16 | 4000 | 4000 | 0 | 0.0% | ✓
AcuvimIIW | CT1 | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuvimIIW | CT2 | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | KWh Pulse Constant | 其他 | uint16 | 5000 | 5000 | 0 | 0.0% | ✓
AcuvimIIW | Kvarh Pulse Constant | 其他 | uint16 | 5000 | 5000 | 0 | 0.0% | ✓
AcuvimIIW | LCD Backlight Time | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Demand Window | 波动量 | uint16 | 30 | 30 | 0 | 0.0% | ✓
AcuvimIIW | Demand Method | 波动量 | uint16 | 3 | 3 | 0 | 0.0% | ✓
AcuvimIIW | Clear Demand | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Clear Max/Min | 其他 | uint16 | 85 | 85 | 0 | 0.0% | ✓
AcuvimIIW | Clear Run Hours | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Current I1 Direction | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Current I2 Direction | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Current I3 Direction | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | VAR/PF Convention | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Clear Energy | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Energy Calculation Method | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Reactive Power Calculation Method | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Energy Reading Primary/Secondary | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Reset Ethernet Module | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Enable SOE | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Clear Pulse Counter | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Basic Reading Display Primary/Secondary | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Non-Standard Content Seal Option | 其他 | uint16 | 16 | 16 | 0 | 0.0% | ✓
AcuvimIIW | Sealing Status | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Demand Sub-Interval | 波动量 | uint16 | 30 | 30 | 0 | 0.0% | ✓
AcuvimIIW | Clear Alarm Records | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | CT41 | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuvimIIW | CT42 | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | JiGuan Customized PT | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | JiGuan Customized CT | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Restore Factory Setting | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Line N Current Method | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Modbus Gateway Enable | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Reserve1 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Reserve2 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Reserve3 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Nominal Full Load Power | 波动量 | uint16 | 6000 | 6000 | 0 | 0.0% | ✓
AcuvimIIW | Load Display Type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | System Status | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Channel 2 Baud Rate | 其他 | uint16 | 11520 | 11520 | 0 | 0.0% | ✓
AcuvimIIW | Channel 2 Parity | 其他 | uint16 | 3 | 3 | 0 | 0.0% | ✓
AcuvimIIW | Channel 2 Address | 其他 | uint16 | 2 | 2 | 0 | 0.0% | ✓
AcuvimIIW | Latest Alarm Group Number | 其他 | uint16 | 14 | 14 | 0 | 0.0% | ✓
AcuvimIIW | Latest SOE Record Group Number | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Run Hour | 其他 | uint32 | 196349 | 196349 | 0 | 0.0% | ✓
AcuvimIIW | Module Connection Status | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Temperature (Not in Use) | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Channel 2 Communication Protocol | 其他 | uint16 | 4 | 4 | 0 | 0.0% | ✓
AcuvimIIW | Enable Downloading TOU Ten Year Configs | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Clear Max Demand - Sharp Tariff | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Clear Max Demand - Peak Tariff | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Clear Max Demand - Valley Tariff | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Clear Max Demand - Normal Tariff | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Clear Max Demand - All Tariffs | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Week | 其他 | uint16 | 3 | 3 | 0 | 0.0% | ✓
AcuvimIIW | Year | 其他 | uint16 | 2026 | 2026 | 0 | 0.0% | ✓
AcuvimIIW | Month | 其他 | uint16 | 6 | 6 | 0 | 0.0% | ✓
AcuvimIIW | Day | 其他 | uint16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Hour | 其他 | uint16 | 5 | 5 | 0 | 0.0% | ✓
AcuvimIIW | Minute | 其他 | uint16 | 6 | 6 | 0 | 0.0% | ✓
AcuvimIIW | Second | 其他 | uint16 | 50 | 50 | 0 | 0.0% | ✓
AcuvimIIW | Phase Order | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Enable Class S PQ Event | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Nominal Voltage | 稳定量 | uint16 | 200 | 200 | 0 | 0.0% | ✓
AcuvimIIW | Nominal Current | 波动量 | uint16 | 5000 | 5000 | 0 | 0.0% | ✓
AcuvimIIW | Sample Rate | 其他 | uint16 | 5 | 5 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Sag Enable | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Sag Threshold | 稳定量 | uint16 | 50 | 50 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Sag Hysteresis | 稳定量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Sag Trigger Waveform | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Sag Trigger DO | 稳定量 | uint16 | 4 | 4 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Sag Trigger RO | 稳定量 | uint16 | 64 | 64 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Swell Enable | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Swell Threshold | 稳定量 | uint16 | 100 | 100 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Swell Hysteresis | 稳定量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Swell Trigger Waveform | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Swell Trigger DO | 稳定量 | uint16 | 4 | 4 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Swell Trigger RO | 稳定量 | uint16 | 64 | 64 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Interrupt Enable | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Interrupt Threshold | 稳定量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Interrupt Hysteresis | 稳定量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Interrupt Trigger Waveform | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Interrupt Trigger DO | 稳定量 | uint16 | 4 | 4 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Interrupt Trigger RO | 稳定量 | uint16 | 64 | 64 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Unbalance Enable | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Unbalance Threshold | 波动量 | uint16 | 50 | 50 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Unbalance Hysteresis | 波动量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Unbalance Trigger Waveform | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Unbalance Trigger DO | 波动量 | uint16 | 4 | 4 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Unbalance Trigger RO | 波动量 | uint16 | 64 | 64 | 0 | 0.0% | ✓
AcuvimIIW | Current Dip Enable | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Current Dip Threshold | 波动量 | uint16 | 90 | 90 | 0 | 0.0% | ✓
AcuvimIIW | Current Dip Hysteresis | 波动量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
AcuvimIIW | Current Dip Trigger Waveform | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Current Dip Trigger DO | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Current Dip Trigger RO | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Current Swell Enable | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Current Swell Threshold | 波动量 | uint16 | 150 | 150 | 0 | 0.0% | ✓
AcuvimIIW | Current Swell Hysteresis | 波动量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Current Swell Trigger Waveform | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Current Swell Trigger DO | 波动量 | uint16 | 4 | 4 | 0 | 0.0% | ✓
AcuvimIIW | Current Swell Trigger RO | 波动量 | uint16 | 64 | 64 | 0 | 0.0% | ✓
AcuvimIIW | Current Unbalance Enable | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Current Unbalance Threshold | 波动量 | uint16 | 50 | 50 | 0 | 0.0% | ✓
AcuvimIIW | Current Unbalance Hysteresis | 波动量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
AcuvimIIW | Current Unbalance Trigger Waveform | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Current Unbalance Trigger DO | 波动量 | uint16 | 4 | 4 | 0 | 0.0% | ✓
AcuvimIIW | Current Unbalance Trigger RO | 波动量 | uint16 | 64 | 64 | 0 | 0.0% | ✓
AcuvimIIW | Manually Trigger Waveform | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | AXM-IO11 Trigger Waveform | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | AXM-IO21 Trigger Waveform | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | AXM-IO31 Trigger Waveform | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Rated Value | 稳定量 | uint16 | 400 | 400 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Sag Trigger | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Sag Threshold | 稳定量 | uint16 | 50 | 50 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Sag Half Cycle | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Swell Trigger | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Voltage Swell Threshold | 稳定量 | uint16 | 100 | 100 | 0 | 0.0% | ✓
AcuvimIIW | Sample Rate | 其他 | uint16 | 5 | 5 | 0 | 0.0% | ✓
AcuvimIIW | Current Rated Value | 波动量 | uint16 | 5000 | 5000 | 0 | 0.0% | ✓
AcuvimIIW | Over-Current Trigger | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Over-Current Threshold | 波动量 | uint16 | 100 | 100 | 0 | 0.0% | ✓
AcuvimIIW | Clear Waveform | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Clear Power Quality Event | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | Number of CT | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuvimIIW | CT2 Type | 其他 | uint16 | 5 | 5 | 0 | 0.0% | ✓
AcuvimIIW | Latest Waveform Record Groupe Number | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuvimIIW | Latest PQ Event Record Group Number | 其他 | uint16 | 759 | 759 | 0 | 0.0% | ✓
AcuRev2100 | System Frequency | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Average Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A-B Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B-C Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C-A Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Average Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Average Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Load Nature | 其他 | float32 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Import Active Energy | 稳定量 | uint32 | 2884530 | 2884530 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Import Active Energy | 稳定量 | uint32 | 171950 | 171950 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Import Active Energy | 稳定量 | uint32 | 247 | 247 | 0 | 0.0% | ✓
AcuRev2100 | System Import Active | 其他 | uint32 | 3056727 | 3056727 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Import Active Energy | 稳定量 | uint32 | 481409 | 481409 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Import Active Energy | 稳定量 | uint32 | 31794 | 31794 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Import Active Energy | 稳定量 | uint32 | 17 | 17 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Import Active Energy | 稳定量 | uint32 | 480662 | 480662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Import Active Energy | 稳定量 | uint32 | 31795 | 31795 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Import Active Energy | 稳定量 | uint32 | 17 | 17 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Import Active Energy | 稳定量 | uint32 | 480682 | 480682 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Import Active Energy | 稳定量 | uint32 | 30421 | 30421 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Import Active Energy | 稳定量 | uint32 | 17 | 17 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Import Active Energy | 稳定量 | uint32 | 480544 | 480544 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Import Active Energy | 稳定量 | uint32 | 17006 | 17006 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Import Active Energy | 稳定量 | uint32 | 17 | 17 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Import Active Energy | 稳定量 | uint32 | 480524 | 480524 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Import Active Energy | 稳定量 | uint32 | 30486 | 30486 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Import Active Energy | 稳定量 | uint32 | 162 | 162 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Import Active Energy | 稳定量 | uint32 | 480709 | 480709 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Import Active Energy | 稳定量 | uint32 | 30448 | 30448 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Import Active Energy | 稳定量 | uint32 | 17 | 17 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Import Active Energy | 稳定量 | uint32 | 513120 | 513120 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Import Active Energy | 稳定量 | uint32 | 484907 | 484907 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Import Active Energy | 稳定量 | uint32 | 33659 | 33659 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Import Active Energy | 稳定量 | uint32 | 510231 | 510231 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Import Active Energy | 稳定量 | uint32 | 483489 | 483489 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Import Active Energy | 稳定量 | uint32 | 21092 | 21092 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Import Active Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Import Active Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Import Active Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Import Reactive Energy | 稳定量 | uint32 | 180310 | 180310 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Import Reactive Energy | 稳定量 | uint32 | 2530787 | 2530787 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Import Reactive Energy | 稳定量 | uint32 | 2613568 | 2613568 | 0 | 0.0% | ✓
AcuRev2100 | System Import Reactive Energy | 稳定量 | uint32 | 5324565 | 5324565 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Import Reactive Energy | 稳定量 | uint32 | 33919 | 33919 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Import Reactive Energy | 稳定量 | uint32 | 422385 | 422385 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Import Reactive Energy | 稳定量 | uint32 | 438546 | 438546 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Import Reactive Energy | 稳定量 | uint32 | 33952 | 33952 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Import Reactive Energy | 稳定量 | uint32 | 421130 | 421130 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Import Reactive Energy | 稳定量 | uint32 | 439433 | 439433 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Import Reactive Energy | 稳定量 | uint32 | 34844 | 34844 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Import Reactive Energy | 稳定量 | uint32 | 420345 | 420345 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Import Reactive Energy | 稳定量 | uint32 | 438368 | 438368 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Import Reactive Energy | 稳定量 | uint32 | 33835 | 33835 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Import Reactive Energy | 稳定量 | uint32 | 426025 | 426025 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Import Reactive Energy | 稳定量 | uint32 | 438731 | 438731 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Import Reactive Energy | 稳定量 | uint32 | 33803 | 33803 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Import Reactive Energy | 稳定量 | uint32 | 420437 | 420437 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Import Reactive Energy | 稳定量 | uint32 | 420497 | 420497 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Import Reactive Energy | 稳定量 | uint32 | 9957 | 9957 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Import Reactive Energy | 稳定量 | uint32 | 420465 | 420465 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Import Reactive Energy | 稳定量 | uint32 | 437893 | 437893 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Import Reactive Energy | 稳定量 | uint32 | 460701 | 460701 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Import Reactive Energy | 稳定量 | uint32 | 475986 | 475986 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Import Reactive Energy | 稳定量 | uint32 | 862669 | 862669 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Import Reactive Energy | 稳定量 | uint32 | 459084 | 459084 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Import Reactive Energy | 稳定量 | uint32 | 474650 | 474650 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Import Reactive Energy | 稳定量 | uint32 | 863654 | 863654 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Apparent Energy | 稳定量 | uint32 | 3039844 | 3039844 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Apparent Energy | 稳定量 | uint32 | 3065857 | 3065857 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Apparent Energy | 稳定量 | uint32 | 3062196 | 3062196 | 0 | 0.0% | ✓
AcuRev2100 | System Apparent Energy | 稳定量 | uint32 | 9167897 | 9167897 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Apparent Energy | 稳定量 | uint32 | 511959 | 511959 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Apparent Energy | 稳定量 | uint32 | 514800 | 514800 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Apparent Energy | 稳定量 | uint32 | 512635 | 512635 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Apparent Energy | 稳定量 | uint32 | 511213 | 511213 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Apparent Energy | 稳定量 | uint32 | 513338 | 513338 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Apparent Energy | 稳定量 | uint32 | 514343 | 514343 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Apparent Energy | 稳定量 | uint32 | 512159 | 512159 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Apparent Energy | 稳定量 | uint32 | 511635 | 511635 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Apparent Energy | 稳定量 | uint32 | 512553 | 512553 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Apparent Energy | 稳定量 | uint32 | 510756 | 510756 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Apparent Energy | 稳定量 | uint32 | 502555 | 502555 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Apparent Energy | 稳定量 | uint32 | 513257 | 513257 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Apparent Energy | 稳定量 | uint32 | 510749 | 510749 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Apparent Energy | 稳定量 | uint32 | 511835 | 511835 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Apparent Energy | 稳定量 | uint32 | 497744 | 497744 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Apparent Energy | 稳定量 | uint32 | 483008 | 483008 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Apparent Energy | 稳定量 | uint32 | 511694 | 511694 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Apparent Energy | 稳定量 | uint32 | 511664 | 511664 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Apparent Energy | 稳定量 | uint32 | 1030980 | 1030980 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Apparent Energy | 稳定量 | uint32 | 1030236 | 1030236 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Apparent Energy | 稳定量 | uint32 | 1028990 | 1028990 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Apparent Energy | 稳定量 | uint32 | 1026680 | 1026680 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Apparent Energy | 稳定量 | uint32 | 1027670 | 1027670 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Apparent Energy | 稳定量 | uint32 | 1015609 | 1015609 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Import Reactive Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Import Reactive Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Import Reactive Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Apparent Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Apparent Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Apparent Energy | 稳定量 | uint32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | System Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | System Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | System Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Current Demand | 波动量 | float32 | 59185.3164 | 59185.3164 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Current Demand Predict | 波动量 | float32 | 59188.7656 | 59188.7656 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Max Current Demand | 波动量 | float32 | 59185.3164 | 59185.3164 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Current Demand | 波动量 | float32 | 48365.7695 | 48365.7695 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Current Demand Predict | 波动量 | float32 | 48352.5938 | 48352.5938 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Max Current Demand | 波动量 | float32 | 48436.6211 | 48436.6211 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Current Demand | 波动量 | float32 | 59173.9102 | 59173.9102 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Current Demand Predict | 波动量 | float32 | 59168.4727 | 59168.4727 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Max Current Demand | 波动量 | float32 | 59173.9102 | 59173.9102 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current Demand | 波动量 | float32 | 9865.9512 | 9865.9512 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current Demand Predict | 波动量 | float32 | 9864.4834 | 9864.4834 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Max Current Demand | 波动量 | float32 | 9865.9512 | 9865.9512 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current Demand | 波动量 | float32 | 9868.3906 | 9868.3906 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current Demand Predict | 波动量 | float32 | 9866.8076 | 9866.8076 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Max Current Demand | 波动量 | float32 | 9868.3906 | 9868.3906 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current Demand | 波动量 | float32 | 9862.7236 | 9862.7236 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current Demand Predict | 波动量 | float32 | 9861.0938 | 9861.0938 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Max Current Demand | 波动量 | float32 | 9862.7236 | 9862.7236 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current Demand | 波动量 | float32 | 9866.709 | 9866.709 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current Demand Predict | 波动量 | float32 | 9865.2764 | 9865.2764 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Max Current Demand | 波动量 | float32 | 9866.709 | 9866.709 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current Demand | 波动量 | float32 | 9869.0645 | 9869.0645 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current Demand Predict | 波动量 | float32 | 9867.7178 | 9867.7178 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Max Current Demand | 波动量 | float32 | 9869.0645 | 9869.0645 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current Demand | 波动量 | float32 | 9865.3154 | 9865.3154 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current Demand Predict | 波动量 | float32 | 9864.249 | 9864.249 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Max Current Demand | 波动量 | float32 | 9865.3154 | 9865.3154 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current Demand | 波动量 | float32 | 9867.1572 | 9867.1572 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Max Current Demand | 波动量 | float32 | 9867.1572 | 9867.1572 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current Demand | 波动量 | float32 | 9863.8721 | 9863.8721 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current Demand Predict | 波动量 | float32 | 9863.7109 | 9863.7109 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Max Current Demand | 波动量 | float32 | 9863.8721 | 9863.8721 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current Demand | 波动量 | float32 | 9859.7363 | 9859.7363 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current Demand Predict | 波动量 | float32 | 9859.9941 | 9859.9941 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Max Current Demand | 波动量 | float32 | 9859.7363 | 9859.7363 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current Demand | 波动量 | float32 | 9860.8623 | 9860.8623 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current Demand Predict | 波动量 | float32 | 9861.5273 | 9861.5273 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Max Current Demand | 波动量 | float32 | 9860.8623 | 9860.8623 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current Demand | 波动量 | float32 | 8705.7832 | 8705.7832 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current Demand Predict | 波动量 | float32 | 8704.8467 | 8704.8467 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Max Current Demand | 波动量 | float32 | 8751.0488 | 8751.0488 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current Demand | 波动量 | float32 | 9862.584 | 9862.584 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current Demand Predict | 波动量 | float32 | 9863.5049 | 9863.5049 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Max Current Demand | 波动量 | float32 | 9862.584 | 9862.584 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current Demand | 波动量 | float32 | 9863.4902 | 9863.4902 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current Demand Predict | 波动量 | float32 | 9864.3311 | 9864.3311 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Max Current Demand | 波动量 | float32 | 9863.4902 | 9863.4902 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current Demand | 波动量 | float32 | 9866.4092 | 9866.4092 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current Demand Predict | 波动量 | float32 | 9867.0908 | 9867.0908 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Max Current Demand | 波动量 | float32 | 9866.4092 | 9866.4092 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current Demand | 波动量 | float32 | 9861.9785 | 9861.9785 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current Demand Predict | 波动量 | float32 | 9862.3398 | 9862.3398 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Max Current Demand | 波动量 | float32 | 9861.9785 | 9861.9785 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current Demand | 波动量 | float32 | 9861.1436 | 9861.1436 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current Demand Predict | 波动量 | float32 | 9860.9209 | 9860.9209 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Max Current Demand | 波动量 | float32 | 9861.1436 | 9861.1436 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current Demand | 波动量 | float32 | 192.2486 | 192.2486 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current Demand Predict | 波动量 | float32 | 179.8702 | 179.8702 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Max Current Demand | 波动量 | float32 | 232.7065 | 232.7065 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current Demand | 波动量 | float32 | 9861.5742 | 9861.5742 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current Demand Predict | 波动量 | float32 | 9860.7734 | 9860.7734 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Max Current Demand | 波动量 | float32 | 9861.5742 | 9861.5742 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Max Current Demand Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Reactive Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Max Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Max Reactive Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Apparent Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Max Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Max Apparent Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Active Power Demand Predict | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Max Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Max Active Power Demand Timestamp | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 16-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 17-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 18-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 19-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 20-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 21-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 22-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 23-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 24-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 25-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 26-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 27-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 28-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 29-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 30-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage 31-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 2-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 3-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 4-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 5-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 6-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 7-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 8-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 9-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 10-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 11-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 12-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 13-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 14-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 15-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 16-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 17-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 18-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 19-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 20-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 21-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 22-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 23-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 24-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 25-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 26-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 27-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 28-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 29-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 30-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage 31-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 2-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 3-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 4-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 5-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 6-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 7-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 8-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 9-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 10-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 11-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 12-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 13-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 14-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 15-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 16-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 17-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 18-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 19-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 20-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 21-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 22-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 23-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 24-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 25-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 26-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 27-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 28-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 29-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 30-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage 31-th Harmonic | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Current Unbalance Factor | 波动量 | int16 | 889 | 889 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage Odd THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage Even THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage Crest Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase A Voltage Telephone Harmonic Form Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage Odd THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage Even THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage Crest Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase B Voltage Telephone Harmonic Form Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage Odd THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage Even THD | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage Crest Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase C Voltage Telephone Harmonic Form Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current Odd THD | 波动量 | int16 | 2315 | 2315 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current Even THD | 波动量 | int16 | 2632 | 2632 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current K Factor | 波动量 | int16 | 367 | 367 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current Odd THD | 波动量 | int16 | 2183 | 2183 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current Even THD | 波动量 | int16 | 2598 | 2598 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current K Factor | 波动量 | int16 | 317 | 317 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current Odd THD | 波动量 | int16 | 2177 | 2177 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current Even THD | 波动量 | int16 | 1944 | 1944 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current K Factor | 波动量 | int16 | 297 | 297 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current Odd THD | 波动量 | int16 | 1769 | 1769 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current Even THD | 波动量 | int16 | 1853 | 1853 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current K Factor | 波动量 | int16 | 225 | 225 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current Odd THD | 波动量 | int16 | 2324 | 2324 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current Even THD | 波动量 | int16 | 2300 | 2300 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current K Factor | 波动量 | int16 | 367 | 367 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current Odd THD | 波动量 | int16 | 1987 | 1987 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current Even THD | 波动量 | int16 | 1835 | 1835 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current K Factor | 波动量 | int16 | 248 | 248 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current Odd THD | 波动量 | int16 | 5082 | 5082 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current Even THD | 波动量 | int16 | 5040 | 5040 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current K Factor | 波动量 | int16 | 1211 | 1211 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current Odd THD | 波动量 | int16 | 7852 | 7852 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current Even THD | 波动量 | int16 | 7648 | 7648 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current K Factor | 波动量 | int16 | 1891 | 1891 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current Odd THD | 波动量 | int16 | 2020 | 2020 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current Even THD | 波动量 | int16 | 2035 | 2035 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current K Factor | 波动量 | int16 | 261 | 261 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current Odd THD | 波动量 | int16 | 4382 | 4382 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current Even THD | 波动量 | int16 | 4571 | 4571 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current K Factor | 波动量 | int16 | 971 | 971 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current Odd THD | 波动量 | int16 | 7068 | 7068 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current Even THD | 波动量 | int16 | 7278 | 7278 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current K Factor | 波动量 | int16 | 1704 | 1704 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current Odd THD | 波动量 | int16 | 5096 | 5096 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current Even THD | 波动量 | int16 | 4994 | 4994 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current K Factor | 波动量 | int16 | 1203 | 1203 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current Odd THD | 波动量 | int16 | 2326 | 2326 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current Even THD | 波动量 | int16 | 2347 | 2347 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current K Factor | 波动量 | int16 | 337 | 337 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current Odd THD | 波动量 | int16 | 2802 | 2802 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current Even THD | 波动量 | int16 | 2802 | 2802 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current K Factor | 波动量 | int16 | 476 | 476 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current Odd THD | 波动量 | int16 | 4389 | 4389 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current Even THD | 波动量 | int16 | 4404 | 4404 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current K Factor | 波动量 | int16 | 957 | 957 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current Odd THD | 波动量 | int16 | 3381 | 3381 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current Even THD | 波动量 | int16 | 3590 | 3590 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current K Factor | 波动量 | int16 | 676 | 676 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current Odd THD | 波动量 | int16 | 9999 | 9999 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current Even THD | 波动量 | int16 | 9999 | 9999 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current K Factor | 波动量 | int16 | 2387 | 2387 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current Odd THD | 波动量 | int16 | 5265 | 5265 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current Even THD | 波动量 | int16 | 5437 | 5437 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current K Factor | 波动量 | int16 | 1211 | 1211 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current THD | 波动量 | int16 | 2931 | 2931 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 2-th Harmonic | 波动量 | int16 | 422 | 422 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 3-th Harmonic | 波动量 | int16 | 439 | 439 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 4-th Harmonic | 波动量 | int16 | 296 | 296 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 5-th Harmonic | 波动量 | int16 | 465 | 465 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 6-th Harmonic | 波动量 | int16 | 271 | 271 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 7-th Harmonic | 波动量 | int16 | 532 | 532 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 8-th Harmonic | 波动量 | int16 | 1309 | 1309 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 9-th Harmonic | 波动量 | int16 | 549 | 549 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 10-th Harmonic | 波动量 | int16 | 371 | 371 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 11-th Harmonic | 波动量 | int16 | 620 | 620 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 12-th Harmonic | 波动量 | int16 | 300 | 300 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 13-th Harmonic | 波动量 | int16 | 611 | 611 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 14-th Harmonic | 波动量 | int16 | 475 | 475 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 15-th Harmonic | 波动量 | int16 | 527 | 527 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 16-th Harmonic | 波动量 | int16 | 504 | 504 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 17-th Harmonic | 波动量 | int16 | 527 | 527 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 18-th Harmonic | 波动量 | int16 | 374 | 374 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 19-th Harmonic | 波动量 | int16 | 504 | 504 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 20-th Harmonic | 波动量 | int16 | 327 | 327 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 21-th Harmonic | 波动量 | int16 | 460 | 460 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 22-th Harmonic | 波动量 | int16 | 475 | 475 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 23-th Harmonic | 波动量 | int16 | 377 | 377 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 24-th Harmonic | 波动量 | int16 | 371 | 371 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 25-th Harmonic | 波动量 | int16 | 327 | 327 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 26-th Harmonic | 波动量 | int16 | 551 | 551 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 27-th Harmonic | 波动量 | int16 | 728 | 728 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 28-th Harmonic | 波动量 | int16 | 462 | 462 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 29-th Harmonic | 波动量 | int16 | 801 | 801 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 30-th Harmonic | 波动量 | int16 | 490 | 490 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 Current 31-th Harmonic | 波动量 | int16 | 511 | 511 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current THD | 波动量 | int16 | 3309 | 3309 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 2-th Harmonic | 波动量 | int16 | 464 | 464 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 3-th Harmonic | 波动量 | int16 | 522 | 522 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 4-th Harmonic | 波动量 | int16 | 469 | 469 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 5-th Harmonic | 波动量 | int16 | 595 | 595 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 6-th Harmonic | 波动量 | int16 | 536 | 536 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 7-th Harmonic | 波动量 | int16 | 484 | 484 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 8-th Harmonic | 波动量 | int16 | 1267 | 1267 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 9-th Harmonic | 波动量 | int16 | 456 | 456 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 10-th Harmonic | 波动量 | int16 | 562 | 562 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 11-th Harmonic | 波动量 | int16 | 558 | 558 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 12-th Harmonic | 波动量 | int16 | 418 | 418 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 13-th Harmonic | 波动量 | int16 | 664 | 664 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 14-th Harmonic | 波动量 | int16 | 607 | 607 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 15-th Harmonic | 波动量 | int16 | 487 | 487 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 16-th Harmonic | 波动量 | int16 | 642 | 642 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 17-th Harmonic | 波动量 | int16 | 474 | 474 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 18-th Harmonic | 波动量 | int16 | 718 | 718 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 19-th Harmonic | 波动量 | int16 | 645 | 645 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 20-th Harmonic | 波动量 | int16 | 451 | 451 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 21-th Harmonic | 波动量 | int16 | 538 | 538 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 22-th Harmonic | 波动量 | int16 | 575 | 575 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 23-th Harmonic | 波动量 | int16 | 591 | 591 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 24-th Harmonic | 波动量 | int16 | 443 | 443 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 25-th Harmonic | 波动量 | int16 | 487 | 487 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 26-th Harmonic | 波动量 | int16 | 649 | 649 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 27-th Harmonic | 波动量 | int16 | 653 | 653 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 28-th Harmonic | 波动量 | int16 | 506 | 506 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 29-th Harmonic | 波动量 | int16 | 677 | 677 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 30-th Harmonic | 波动量 | int16 | 640 | 640 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 Current 31-th Harmonic | 波动量 | int16 | 536 | 536 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current THD | 波动量 | int16 | 2800 | 2800 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 2-th Harmonic | 波动量 | int16 | 456 | 456 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 3-th Harmonic | 波动量 | int16 | 456 | 456 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 4-th Harmonic | 波动量 | int16 | 414 | 414 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 5-th Harmonic | 波动量 | int16 | 467 | 467 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 6-th Harmonic | 波动量 | int16 | 514 | 514 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 7-th Harmonic | 波动量 | int16 | 497 | 497 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 8-th Harmonic | 波动量 | int16 | 519 | 519 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 9-th Harmonic | 波动量 | int16 | 484 | 484 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 10-th Harmonic | 波动量 | int16 | 479 | 479 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 11-th Harmonic | 波动量 | int16 | 669 | 669 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 12-th Harmonic | 波动量 | int16 | 469 | 469 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 13-th Harmonic | 波动量 | int16 | 417 | 417 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 14-th Harmonic | 波动量 | int16 | 600 | 600 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 15-th Harmonic | 波动量 | int16 | 399 | 399 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 16-th Harmonic | 波动量 | int16 | 467 | 467 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 17-th Harmonic | 波动量 | int16 | 559 | 559 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 18-th Harmonic | 波动量 | int16 | 635 | 635 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 19-th Harmonic | 波动量 | int16 | 628 | 628 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 20-th Harmonic | 波动量 | int16 | 420 | 420 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 21-th Harmonic | 波动量 | int16 | 316 | 316 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 22-th Harmonic | 波动量 | int16 | 509 | 509 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 23-th Harmonic | 波动量 | int16 | 649 | 649 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 24-th Harmonic | 波动量 | int16 | 526 | 526 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 25-th Harmonic | 波动量 | int16 | 507 | 507 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 26-th Harmonic | 波动量 | int16 | 577 | 577 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 27-th Harmonic | 波动量 | int16 | 539 | 539 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 28-th Harmonic | 波动量 | int16 | 420 | 420 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 29-th Harmonic | 波动量 | int16 | 439 | 439 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 30-th Harmonic | 波动量 | int16 | 570 | 570 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 Current 31-th Harmonic | 波动量 | int16 | 537 | 537 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current THD | 波动量 | int16 | 2331 | 2331 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 2-th Harmonic | 波动量 | int16 | 301 | 301 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 3-th Harmonic | 波动量 | int16 | 373 | 373 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 4-th Harmonic | 波动量 | int16 | 285 | 285 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 5-th Harmonic | 波动量 | int16 | 385 | 385 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 6-th Harmonic | 波动量 | int16 | 369 | 369 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 7-th Harmonic | 波动量 | int16 | 359 | 359 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 8-th Harmonic | 波动量 | int16 | 391 | 391 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 9-th Harmonic | 波动量 | int16 | 366 | 366 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 10-th Harmonic | 波动量 | int16 | 281 | 281 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 11-th Harmonic | 波动量 | int16 | 448 | 448 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 12-th Harmonic | 波动量 | int16 | 356 | 356 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 13-th Harmonic | 波动量 | int16 | 432 | 432 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 14-th Harmonic | 波动量 | int16 | 435 | 435 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 15-th Harmonic | 波动量 | int16 | 489 | 489 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 16-th Harmonic | 波动量 | int16 | 421 | 421 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 17-th Harmonic | 波动量 | int16 | 435 | 435 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 18-th Harmonic | 波动量 | int16 | 562 | 562 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 19-th Harmonic | 波动量 | int16 | 499 | 499 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 20-th Harmonic | 波动量 | int16 | 577 | 577 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 21-th Harmonic | 波动量 | int16 | 332 | 332 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 22-th Harmonic | 波动量 | int16 | 508 | 508 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 23-th Harmonic | 波动量 | int16 | 359 | 359 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 24-th Harmonic | 波动量 | int16 | 504 | 504 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 25-th Harmonic | 波动量 | int16 | 446 | 446 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 26-th Harmonic | 波动量 | int16 | 379 | 379 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 27-th Harmonic | 波动量 | int16 | 429 | 429 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 28-th Harmonic | 波动量 | int16 | 504 | 504 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 29-th Harmonic | 波动量 | int16 | 492 | 492 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 30-th Harmonic | 波动量 | int16 | 359 | 359 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 Current 31-th Harmonic | 波动量 | int16 | 474 | 474 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current THD | 波动量 | int16 | 2658 | 2658 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 2-th Harmonic | 波动量 | int16 | 549 | 549 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 3-th Harmonic | 波动量 | int16 | 503 | 503 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 4-th Harmonic | 波动量 | int16 | 581 | 581 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 5-th Harmonic | 波动量 | int16 | 457 | 457 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 6-th Harmonic | 波动量 | int16 | 524 | 524 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 7-th Harmonic | 波动量 | int16 | 605 | 605 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 8-th Harmonic | 波动量 | int16 | 376 | 376 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 9-th Harmonic | 波动量 | int16 | 537 | 537 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 10-th Harmonic | 波动量 | int16 | 488 | 488 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 11-th Harmonic | 波动量 | int16 | 421 | 421 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 12-th Harmonic | 波动量 | int16 | 443 | 443 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 13-th Harmonic | 波动量 | int16 | 627 | 627 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 14-th Harmonic | 波动量 | int16 | 485 | 485 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 15-th Harmonic | 波动量 | int16 | 584 | 584 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 16-th Harmonic | 波动量 | int16 | 598 | 598 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 17-th Harmonic | 波动量 | int16 | 579 | 579 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 18-th Harmonic | 波动量 | int16 | 595 | 595 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 19-th Harmonic | 波动量 | int16 | 781 | 781 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 20-th Harmonic | 波动量 | int16 | 440 | 440 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 21-th Harmonic | 波动量 | int16 | 576 | 576 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 22-th Harmonic | 波动量 | int16 | 473 | 473 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 23-th Harmonic | 波动量 | int16 | 586 | 586 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 24-th Harmonic | 波动量 | int16 | 523 | 523 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 25-th Harmonic | 波动量 | int16 | 591 | 591 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 26-th Harmonic | 波动量 | int16 | 593 | 593 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 27-th Harmonic | 波动量 | int16 | 607 | 607 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 28-th Harmonic | 波动量 | int16 | 320 | 320 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 29-th Harmonic | 波动量 | int16 | 529 | 529 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 30-th Harmonic | 波动量 | int16 | 482 | 482 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 Current 31-th Harmonic | 波动量 | int16 | 449 | 449 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current THD | 波动量 | int16 | 3192 | 3192 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 2-th Harmonic | 波动量 | int16 | 695 | 695 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 3-th Harmonic | 波动量 | int16 | 599 | 599 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 4-th Harmonic | 波动量 | int16 | 707 | 707 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 5-th Harmonic | 波动量 | int16 | 517 | 517 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 6-th Harmonic | 波动量 | int16 | 543 | 543 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 7-th Harmonic | 波动量 | int16 | 561 | 561 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 8-th Harmonic | 波动量 | int16 | 493 | 493 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 9-th Harmonic | 波动量 | int16 | 410 | 410 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 10-th Harmonic | 波动量 | int16 | 495 | 495 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 11-th Harmonic | 波动量 | int16 | 563 | 563 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 12-th Harmonic | 波动量 | int16 | 601 | 601 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 13-th Harmonic | 波动量 | int16 | 472 | 472 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 14-th Harmonic | 波动量 | int16 | 619 | 619 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 15-th Harmonic | 波动量 | int16 | 578 | 578 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 16-th Harmonic | 波动量 | int16 | 610 | 610 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 17-th Harmonic | 波动量 | int16 | 520 | 520 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 18-th Harmonic | 波动量 | int16 | 563 | 563 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 19-th Harmonic | 波动量 | int16 | 606 | 606 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 20-th Harmonic | 波动量 | int16 | 679 | 679 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 21-th Harmonic | 波动量 | int16 | 599 | 599 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 22-th Harmonic | 波动量 | int16 | 601 | 601 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 23-th Harmonic | 波动量 | int16 | 490 | 490 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 24-th Harmonic | 波动量 | int16 | 568 | 568 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 25-th Harmonic | 波动量 | int16 | 664 | 664 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 26-th Harmonic | 波动量 | int16 | 658 | 658 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 27-th Harmonic | 波动量 | int16 | 592 | 592 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 28-th Harmonic | 波动量 | int16 | 612 | 612 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 29-th Harmonic | 波动量 | int16 | 512 | 512 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 30-th Harmonic | 波动量 | int16 | 626 | 626 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 Current 31-th Harmonic | 波动量 | int16 | 606 | 606 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current THD | 波动量 | int16 | 7038 | 7038 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 2-th Harmonic | 波动量 | int16 | 1249 | 1249 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 3-th Harmonic | 波动量 | int16 | 1280 | 1280 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 4-th Harmonic | 波动量 | int16 | 1259 | 1259 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 5-th Harmonic | 波动量 | int16 | 1211 | 1211 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 6-th Harmonic | 波动量 | int16 | 1225 | 1225 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 7-th Harmonic | 波动量 | int16 | 1093 | 1093 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 8-th Harmonic | 波动量 | int16 | 1956 | 1956 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 9-th Harmonic | 波动量 | int16 | 1242 | 1242 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 10-th Harmonic | 波动量 | int16 | 1357 | 1357 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 11-th Harmonic | 波动量 | int16 | 1136 | 1136 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 12-th Harmonic | 波动量 | int16 | 1241 | 1241 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 13-th Harmonic | 波动量 | int16 | 1233 | 1233 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 14-th Harmonic | 波动量 | int16 | 1271 | 1271 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 15-th Harmonic | 波动量 | int16 | 1321 | 1321 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 16-th Harmonic | 波动量 | int16 | 1148 | 1148 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 17-th Harmonic | 波动量 | int16 | 1332 | 1332 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 18-th Harmonic | 波动量 | int16 | 1386 | 1386 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 19-th Harmonic | 波动量 | int16 | 1225 | 1225 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 20-th Harmonic | 波动量 | int16 | 1217 | 1217 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 21-th Harmonic | 波动量 | int16 | 1235 | 1235 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 22-th Harmonic | 波动量 | int16 | 1161 | 1161 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 23-th Harmonic | 波动量 | int16 | 1230 | 1230 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 24-th Harmonic | 波动量 | int16 | 1170 | 1170 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 25-th Harmonic | 波动量 | int16 | 1283 | 1283 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 26-th Harmonic | 波动量 | int16 | 1280 | 1280 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 27-th Harmonic | 波动量 | int16 | 1318 | 1318 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 28-th Harmonic | 波动量 | int16 | 1249 | 1249 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 29-th Harmonic | 波动量 | int16 | 1448 | 1448 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 30-th Harmonic | 波动量 | int16 | 1241 | 1241 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 Current 31-th Harmonic | 波动量 | int16 | 1121 | 1121 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current THD | 波动量 | int16 | 9999 | 9999 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 2-th Harmonic | 波动量 | int16 | 1817 | 1817 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 3-th Harmonic | 波动量 | int16 | 1872 | 1872 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 4-th Harmonic | 波动量 | int16 | 2037 | 2037 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 5-th Harmonic | 波动量 | int16 | 1921 | 1921 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 6-th Harmonic | 波动量 | int16 | 1838 | 1838 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 7-th Harmonic | 波动量 | int16 | 2050 | 2050 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 8-th Harmonic | 波动量 | int16 | 1957 | 1957 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 9-th Harmonic | 波动量 | int16 | 1891 | 1891 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 10-th Harmonic | 波动量 | int16 | 1999 | 1999 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 11-th Harmonic | 波动量 | int16 | 2003 | 2003 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 12-th Harmonic | 波动量 | int16 | 2007 | 2007 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 13-th Harmonic | 波动量 | int16 | 1904 | 1904 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 14-th Harmonic | 波动量 | int16 | 2042 | 2042 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 15-th Harmonic | 波动量 | int16 | 1766 | 1766 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 16-th Harmonic | 波动量 | int16 | 1814 | 1814 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 17-th Harmonic | 波动量 | int16 | 2012 | 2012 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 18-th Harmonic | 波动量 | int16 | 1887 | 1887 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 19-th Harmonic | 波动量 | int16 | 2054 | 2054 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 20-th Harmonic | 波动量 | int16 | 1828 | 1828 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 21-th Harmonic | 波动量 | int16 | 1948 | 1948 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 22-th Harmonic | 波动量 | int16 | 1935 | 1935 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 23-th Harmonic | 波动量 | int16 | 2151 | 2151 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 24-th Harmonic | 波动量 | int16 | 1922 | 1922 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 25-th Harmonic | 波动量 | int16 | 2011 | 2011 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 26-th Harmonic | 波动量 | int16 | 1983 | 1983 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 27-th Harmonic | 波动量 | int16 | 1803 | 1803 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 28-th Harmonic | 波动量 | int16 | 1882 | 1882 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 29-th Harmonic | 波动量 | int16 | 1733 | 1733 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 Current 30-th Harmonic | 波动量 | int16 | 1918 | 1918 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current THD | 波动量 | int16 | 2931 | 2931 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 2-th Harmonic | 波动量 | int16 | 607 | 607 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 3-th Harmonic | 波动量 | int16 | 515 | 515 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 4-th Harmonic | 波动量 | int16 | 452 | 452 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 5-th Harmonic | 波动量 | int16 | 510 | 510 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 6-th Harmonic | 波动量 | int16 | 582 | 582 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 7-th Harmonic | 波动量 | int16 | 628 | 628 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 8-th Harmonic | 波动量 | int16 | 477 | 477 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 9-th Harmonic | 波动量 | int16 | 393 | 393 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 10-th Harmonic | 波动量 | int16 | 486 | 486 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 11-th Harmonic | 波动量 | int16 | 711 | 711 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 12-th Harmonic | 波动量 | int16 | 462 | 462 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 13-th Harmonic | 波动量 | int16 | 564 | 564 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 14-th Harmonic | 波动量 | int16 | 446 | 446 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 15-th Harmonic | 波动量 | int16 | 445 | 445 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 16-th Harmonic | 波动量 | int16 | 575 | 575 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 17-th Harmonic | 波动量 | int16 | 495 | 495 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 18-th Harmonic | 波动量 | int16 | 524 | 524 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 19-th Harmonic | 波动量 | int16 | 435 | 435 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 20-th Harmonic | 波动量 | int16 | 559 | 559 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 21-th Harmonic | 波动量 | int16 | 527 | 527 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 22-th Harmonic | 波动量 | int16 | 666 | 666 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 23-th Harmonic | 波动量 | int16 | 626 | 626 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 24-th Harmonic | 波动量 | int16 | 582 | 582 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 25-th Harmonic | 波动量 | int16 | 449 | 449 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 26-th Harmonic | 波动量 | int16 | 515 | 515 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 27-th Harmonic | 波动量 | int16 | 602 | 602 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 28-th Harmonic | 波动量 | int16 | 543 | 543 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 29-th Harmonic | 波动量 | int16 | 498 | 498 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 30-th Harmonic | 波动量 | int16 | 579 | 579 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 Current 31-th Harmonic | 波动量 | int16 | 436 | 436 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current THD | 波动量 | int16 | 6207 | 6207 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 2-th Harmonic | 波动量 | int16 | 927 | 927 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 3-th Harmonic | 波动量 | int16 | 933 | 933 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 4-th Harmonic | 波动量 | int16 | 1127 | 1127 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 5-th Harmonic | 波动量 | int16 | 1159 | 1159 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 6-th Harmonic | 波动量 | int16 | 941 | 941 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 7-th Harmonic | 波动量 | int16 | 958 | 958 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 8-th Harmonic | 波动量 | int16 | 1836 | 1836 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 9-th Harmonic | 波动量 | int16 | 1029 | 1029 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 10-th Harmonic | 波动量 | int16 | 1290 | 1290 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 11-th Harmonic | 波动量 | int16 | 1233 | 1233 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 12-th Harmonic | 波动量 | int16 | 1227 | 1227 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 13-th Harmonic | 波动量 | int16 | 1090 | 1090 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 14-th Harmonic | 波动量 | int16 | 1023 | 1023 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 15-th Harmonic | 波动量 | int16 | 1048 | 1048 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 16-th Harmonic | 波动量 | int16 | 1137 | 1137 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 17-th Harmonic | 波动量 | int16 | 1159 | 1159 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 18-th Harmonic | 波动量 | int16 | 1188 | 1188 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 19-th Harmonic | 波动量 | int16 | 1284 | 1284 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 20-th Harmonic | 波动量 | int16 | 1016 | 1016 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 21-th Harmonic | 波动量 | int16 | 1180 | 1180 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 22-th Harmonic | 波动量 | int16 | 962 | 962 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 23-th Harmonic | 波动量 | int16 | 1081 | 1081 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 24-th Harmonic | 波动量 | int16 | 1121 | 1121 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 25-th Harmonic | 波动量 | int16 | 897 | 897 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 26-th Harmonic | 波动量 | int16 | 1114 | 1114 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 27-th Harmonic | 波动量 | int16 | 1324 | 1324 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 28-th Harmonic | 波动量 | int16 | 1054 | 1054 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 29-th Harmonic | 波动量 | int16 | 1229 | 1229 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 30-th Harmonic | 波动量 | int16 | 1062 | 1062 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 Current 31-th Harmonic | 波动量 | int16 | 941 | 941 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current THD | 波动量 | int16 | 9999 | 9999 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 2-th Harmonic | 波动量 | int16 | 1860 | 1860 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 3-th Harmonic | 波动量 | int16 | 2304 | 2304 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 4-th Harmonic | 波动量 | int16 | 1934 | 1934 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 5-th Harmonic | 波动量 | int16 | 1899 | 1899 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 6-th Harmonic | 波动量 | int16 | 1734 | 1734 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 7-th Harmonic | 波动量 | int16 | 1812 | 1812 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 8-th Harmonic | 波动量 | int16 | 2138 | 2138 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 9-th Harmonic | 波动量 | int16 | 1882 | 1882 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 10-th Harmonic | 波动量 | int16 | 1810 | 1810 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 11-th Harmonic | 波动量 | int16 | 1884 | 1884 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 12-th Harmonic | 波动量 | int16 | 1644 | 1644 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 13-th Harmonic | 波动量 | int16 | 1907 | 1907 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 14-th Harmonic | 波动量 | int16 | 1983 | 1983 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 15-th Harmonic | 波动量 | int16 | 1835 | 1835 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 16-th Harmonic | 波动量 | int16 | 1716 | 1716 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 17-th Harmonic | 波动量 | int16 | 1789 | 1789 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 18-th Harmonic | 波动量 | int16 | 1868 | 1868 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 19-th Harmonic | 波动量 | int16 | 1746 | 1746 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 20-th Harmonic | 波动量 | int16 | 1908 | 1908 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 21-th Harmonic | 波动量 | int16 | 1939 | 1939 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 22-th Harmonic | 波动量 | int16 | 1815 | 1815 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 23-th Harmonic | 波动量 | int16 | 1788 | 1788 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 24-th Harmonic | 波动量 | int16 | 1812 | 1812 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 25-th Harmonic | 波动量 | int16 | 1711 | 1711 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 26-th Harmonic | 波动量 | int16 | 1734 | 1734 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 27-th Harmonic | 波动量 | int16 | 2051 | 2051 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 28-th Harmonic | 波动量 | int16 | 1780 | 1780 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 29-th Harmonic | 波动量 | int16 | 1918 | 1918 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 30-th Harmonic | 波动量 | int16 | 1744 | 1744 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 Current 31-th Harmonic | 波动量 | int16 | 1790 | 1790 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current THD | 波动量 | int16 | 6890 | 6890 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 2-th Harmonic | 波动量 | int16 | 1227 | 1227 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 3-th Harmonic | 波动量 | int16 | 1389 | 1389 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 4-th Harmonic | 波动量 | int16 | 1114 | 1114 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 5-th Harmonic | 波动量 | int16 | 1218 | 1218 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 6-th Harmonic | 波动量 | int16 | 1168 | 1168 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 7-th Harmonic | 波动量 | int16 | 1249 | 1249 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 8-th Harmonic | 波动量 | int16 | 1428 | 1428 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 9-th Harmonic | 波动量 | int16 | 1235 | 1235 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 10-th Harmonic | 波动量 | int16 | 1029 | 1029 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 11-th Harmonic | 波动量 | int16 | 1303 | 1303 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 12-th Harmonic | 波动量 | int16 | 1308 | 1308 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 13-th Harmonic | 波动量 | int16 | 1313 | 1313 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 14-th Harmonic | 波动量 | int16 | 1262 | 1262 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 15-th Harmonic | 波动量 | int16 | 1061 | 1061 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 16-th Harmonic | 波动量 | int16 | 1201 | 1201 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 17-th Harmonic | 波动量 | int16 | 1428 | 1428 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 18-th Harmonic | 波动量 | int16 | 1259 | 1259 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 19-th Harmonic | 波动量 | int16 | 1311 | 1311 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 20-th Harmonic | 波动量 | int16 | 1220 | 1220 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 21-th Harmonic | 波动量 | int16 | 1161 | 1161 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 22-th Harmonic | 波动量 | int16 | 1339 | 1339 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 23-th Harmonic | 波动量 | int16 | 1104 | 1104 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 24-th Harmonic | 波动量 | int16 | 1141 | 1141 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 25-th Harmonic | 波动量 | int16 | 1192 | 1192 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 26-th Harmonic | 波动量 | int16 | 1349 | 1349 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 27-th Harmonic | 波动量 | int16 | 1389 | 1389 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 28-th Harmonic | 波动量 | int16 | 1268 | 1268 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 29-th Harmonic | 波动量 | int16 | 1395 | 1395 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 30-th Harmonic | 波动量 | int16 | 1130 | 1130 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 Current 31-th Harmonic | 波动量 | int16 | 1403 | 1403 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current THD | 波动量 | int16 | 2613 | 2613 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 2-th Harmonic | 波动量 | int16 | 516 | 516 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 3-th Harmonic | 波动量 | int16 | 539 | 539 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 4-th Harmonic | 波动量 | int16 | 400 | 400 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 5-th Harmonic | 波动量 | int16 | 305 | 305 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 6-th Harmonic | 波动量 | int16 | 423 | 423 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 7-th Harmonic | 波动量 | int16 | 727 | 727 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 8-th Harmonic | 波动量 | int16 | 552 | 552 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 9-th Harmonic | 波动量 | int16 | 529 | 529 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 10-th Harmonic | 波动量 | int16 | 441 | 441 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 11-th Harmonic | 波动量 | int16 | 511 | 511 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 12-th Harmonic | 波动量 | int16 | 473 | 473 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 13-th Harmonic | 波动量 | int16 | 539 | 539 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 14-th Harmonic | 波动量 | int16 | 532 | 532 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 15-th Harmonic | 波动量 | int16 | 484 | 484 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 16-th Harmonic | 波动量 | int16 | 465 | 465 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 17-th Harmonic | 波动量 | int16 | 624 | 624 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 18-th Harmonic | 波动量 | int16 | 581 | 581 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 19-th Harmonic | 波动量 | int16 | 590 | 590 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 20-th Harmonic | 波动量 | int16 | 484 | 484 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 21-th Harmonic | 波动量 | int16 | 524 | 524 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 22-th Harmonic | 波动量 | int16 | 510 | 510 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 23-th Harmonic | 波动量 | int16 | 607 | 607 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 24-th Harmonic | 波动量 | int16 | 621 | 621 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 25-th Harmonic | 波动量 | int16 | 487 | 487 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 26-th Harmonic | 波动量 | int16 | 510 | 510 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 27-th Harmonic | 波动量 | int16 | 556 | 556 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 28-th Harmonic | 波动量 | int16 | 499 | 499 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 29-th Harmonic | 波动量 | int16 | 578 | 578 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 30-th Harmonic | 波动量 | int16 | 646 | 646 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 Current 31-th Harmonic | 波动量 | int16 | 457 | 457 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current THD | 波动量 | int16 | 4013 | 4013 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 2-th Harmonic | 波动量 | int16 | 611 | 611 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 3-th Harmonic | 波动量 | int16 | 647 | 647 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 4-th Harmonic | 波动量 | int16 | 658 | 658 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 5-th Harmonic | 波动量 | int16 | 694 | 694 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 6-th Harmonic | 波动量 | int16 | 762 | 762 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 7-th Harmonic | 波动量 | int16 | 675 | 675 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 8-th Harmonic | 波动量 | int16 | 722 | 722 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 9-th Harmonic | 波动量 | int16 | 816 | 816 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 10-th Harmonic | 波动量 | int16 | 760 | 760 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 11-th Harmonic | 波动量 | int16 | 651 | 651 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 12-th Harmonic | 波动量 | int16 | 872 | 872 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 13-th Harmonic | 波动量 | int16 | 631 | 631 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 14-th Harmonic | 波动量 | int16 | 741 | 741 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 15-th Harmonic | 波动量 | int16 | 766 | 766 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 16-th Harmonic | 波动量 | int16 | 658 | 658 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 17-th Harmonic | 波动量 | int16 | 716 | 716 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 18-th Harmonic | 波动量 | int16 | 743 | 743 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 19-th Harmonic | 波动量 | int16 | 790 | 790 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 20-th Harmonic | 波动量 | int16 | 773 | 773 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 21-th Harmonic | 波动量 | int16 | 716 | 716 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 22-th Harmonic | 波动量 | int16 | 795 | 795 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 23-th Harmonic | 波动量 | int16 | 702 | 702 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 24-th Harmonic | 波动量 | int16 | 606 | 606 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 25-th Harmonic | 波动量 | int16 | 770 | 770 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 26-th Harmonic | 波动量 | int16 | 792 | 792 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 27-th Harmonic | 波动量 | int16 | 880 | 880 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 28-th Harmonic | 波动量 | int16 | 816 | 816 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 29-th Harmonic | 波动量 | int16 | 702 | 702 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 30-th Harmonic | 波动量 | int16 | 770 | 770 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 Current 31-th Harmonic | 波动量 | int16 | 634 | 634 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current THD | 波动量 | int16 | 6702 | 6702 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 2-th Harmonic | 波动量 | int16 | 1178 | 1178 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 3-th Harmonic | 波动量 | int16 | 1286 | 1286 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 4-th Harmonic | 波动量 | int16 | 1027 | 1027 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 5-th Harmonic | 波动量 | int16 | 1184 | 1184 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 6-th Harmonic | 波动量 | int16 | 1314 | 1314 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 7-th Harmonic | 波动量 | int16 | 1128 | 1128 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 8-th Harmonic | 波动量 | int16 | 1318 | 1318 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 9-th Harmonic | 波动量 | int16 | 1242 | 1242 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 10-th Harmonic | 波动量 | int16 | 1330 | 1330 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 11-th Harmonic | 波动量 | int16 | 1228 | 1228 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 12-th Harmonic | 波动量 | int16 | 1214 | 1214 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 13-th Harmonic | 波动量 | int16 | 1213 | 1213 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 14-th Harmonic | 波动量 | int16 | 1249 | 1249 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 15-th Harmonic | 波动量 | int16 | 1039 | 1039 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 16-th Harmonic | 波动量 | int16 | 1283 | 1283 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 17-th Harmonic | 波动量 | int16 | 1007 | 1007 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 18-th Harmonic | 波动量 | int16 | 1056 | 1056 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 19-th Harmonic | 波动量 | int16 | 1162 | 1162 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 20-th Harmonic | 波动量 | int16 | 1130 | 1130 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 21-th Harmonic | 波动量 | int16 | 1184 | 1184 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 22-th Harmonic | 波动量 | int16 | 1007 | 1007 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 23-th Harmonic | 波动量 | int16 | 1100 | 1100 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 24-th Harmonic | 波动量 | int16 | 916 | 916 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 25-th Harmonic | 波动量 | int16 | 979 | 979 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 26-th Harmonic | 波动量 | int16 | 1272 | 1272 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 27-th Harmonic | 波动量 | int16 | 1027 | 1027 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 28-th Harmonic | 波动量 | int16 | 1046 | 1046 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 29-th Harmonic | 波动量 | int16 | 1095 | 1095 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 30-th Harmonic | 波动量 | int16 | 1074 | 1074 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 Current 31-th Harmonic | 波动量 | int16 | 1094 | 1094 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current THD | 波动量 | int16 | 4629 | 4629 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 2-th Harmonic | 波动量 | int16 | 790 | 790 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 3-th Harmonic | 波动量 | int16 | 792 | 792 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 4-th Harmonic | 波动量 | int16 | 821 | 821 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 5-th Harmonic | 波动量 | int16 | 811 | 811 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 6-th Harmonic | 波动量 | int16 | 771 | 771 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 7-th Harmonic | 波动量 | int16 | 737 | 737 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 8-th Harmonic | 波动量 | int16 | 1624 | 1624 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 9-th Harmonic | 波动量 | int16 | 652 | 652 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 10-th Harmonic | 波动量 | int16 | 917 | 917 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 11-th Harmonic | 波动量 | int16 | 784 | 784 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 12-th Harmonic | 波动量 | int16 | 841 | 841 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 13-th Harmonic | 波动量 | int16 | 726 | 726 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 14-th Harmonic | 波动量 | int16 | 745 | 745 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 15-th Harmonic | 波动量 | int16 | 750 | 750 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 16-th Harmonic | 波动量 | int16 | 851 | 851 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 17-th Harmonic | 波动量 | int16 | 749 | 749 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 18-th Harmonic | 波动量 | int16 | 772 | 772 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 19-th Harmonic | 波动量 | int16 | 929 | 929 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 20-th Harmonic | 波动量 | int16 | 643 | 643 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 21-th Harmonic | 波动量 | int16 | 917 | 917 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 22-th Harmonic | 波动量 | int16 | 731 | 731 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 23-th Harmonic | 波动量 | int16 | 742 | 742 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 24-th Harmonic | 波动量 | int16 | 701 | 701 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 25-th Harmonic | 波动量 | int16 | 758 | 758 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 26-th Harmonic | 波动量 | int16 | 710 | 710 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 27-th Harmonic | 波动量 | int16 | 1049 | 1049 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 28-th Harmonic | 波动量 | int16 | 814 | 814 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 29-th Harmonic | 波动量 | int16 | 1002 | 1002 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 30-th Harmonic | 波动量 | int16 | 830 | 830 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 Current 31-th Harmonic | 波动量 | int16 | 845 | 845 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current THD | 波动量 | int16 | 9999 | 9999 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 2-th Harmonic | 波动量 | int16 | 1941 | 1941 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 3-th Harmonic | 波动量 | int16 | 1979 | 1979 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 4-th Harmonic | 波动量 | int16 | 1770 | 1770 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 5-th Harmonic | 波动量 | int16 | 1840 | 1840 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 6-th Harmonic | 波动量 | int16 | 1886 | 1886 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 7-th Harmonic | 波动量 | int16 | 2000 | 2000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 8-th Harmonic | 波动量 | int16 | 1888 | 1888 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 9-th Harmonic | 波动量 | int16 | 1882 | 1882 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 10-th Harmonic | 波动量 | int16 | 1731 | 1731 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 11-th Harmonic | 波动量 | int16 | 1866 | 1866 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 12-th Harmonic | 波动量 | int16 | 1783 | 1783 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 13-th Harmonic | 波动量 | int16 | 1710 | 1710 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 14-th Harmonic | 波动量 | int16 | 1979 | 1979 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 15-th Harmonic | 波动量 | int16 | 1980 | 1980 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 16-th Harmonic | 波动量 | int16 | 2193 | 2193 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 17-th Harmonic | 波动量 | int16 | 1872 | 1872 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 18-th Harmonic | 波动量 | int16 | 1923 | 1923 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 19-th Harmonic | 波动量 | int16 | 1637 | 1637 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 20-th Harmonic | 波动量 | int16 | 1951 | 1951 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 21-th Harmonic | 波动量 | int16 | 1959 | 1959 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 22-th Harmonic | 波动量 | int16 | 1706 | 1706 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 23-th Harmonic | 波动量 | int16 | 1997 | 1997 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 24-th Harmonic | 波动量 | int16 | 1792 | 1792 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 25-th Harmonic | 波动量 | int16 | 1871 | 1871 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 26-th Harmonic | 波动量 | int16 | 2635 | 2635 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 27-th Harmonic | 波动量 | int16 | 2644 | 2644 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 28-th Harmonic | 波动量 | int16 | 2665 | 2665 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 29-th Harmonic | 波动量 | int16 | 2737 | 2737 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 30-th Harmonic | 波动量 | int16 | 2391 | 2391 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 Current 31-th Harmonic | 波动量 | int16 | 2774 | 2774 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current THD | 波动量 | int16 | 7963 | 7963 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 2-th Harmonic | 波动量 | int16 | 1510 | 1510 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 3-th Harmonic | 波动量 | int16 | 1369 | 1369 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 4-th Harmonic | 波动量 | int16 | 1494 | 1494 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 5-th Harmonic | 波动量 | int16 | 1554 | 1554 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 6-th Harmonic | 波动量 | int16 | 1490 | 1490 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 7-th Harmonic | 波动量 | int16 | 1383 | 1383 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 8-th Harmonic | 波动量 | int16 | 1215 | 1215 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 9-th Harmonic | 波动量 | int16 | 1442 | 1442 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 10-th Harmonic | 波动量 | int16 | 1552 | 1552 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 11-th Harmonic | 波动量 | int16 | 1530 | 1530 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 12-th Harmonic | 波动量 | int16 | 1471 | 1471 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 13-th Harmonic | 波动量 | int16 | 1489 | 1489 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 14-th Harmonic | 波动量 | int16 | 1331 | 1331 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 15-th Harmonic | 波动量 | int16 | 1588 | 1588 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 16-th Harmonic | 波动量 | int16 | 1463 | 1463 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 17-th Harmonic | 波动量 | int16 | 1402 | 1402 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 18-th Harmonic | 波动量 | int16 | 1359 | 1359 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 19-th Harmonic | 波动量 | int16 | 1442 | 1442 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 20-th Harmonic | 波动量 | int16 | 1468 | 1468 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 21-th Harmonic | 波动量 | int16 | 1511 | 1511 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 22-th Harmonic | 波动量 | int16 | 1402 | 1402 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 23-th Harmonic | 波动量 | int16 | 1488 | 1488 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 24-th Harmonic | 波动量 | int16 | 1478 | 1478 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 25-th Harmonic | 波动量 | int16 | 1558 | 1558 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 26-th Harmonic | 波动量 | int16 | 1286 | 1286 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 27-th Harmonic | 波动量 | int16 | 1548 | 1548 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 28-th Harmonic | 波动量 | int16 | 1400 | 1400 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 29-th Harmonic | 波动量 | int16 | 1378 | 1378 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 30-th Harmonic | 波动量 | int16 | 1498 | 1498 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 Current 31-th Harmonic | 波动量 | int16 | 1436 | 1436 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 1 Current Unbalance Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 2 Current Unbalance Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 3 Current Unbalance Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 4 Current Unbalance Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 5 Current Unbalance Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 6 Current Unbalance Factor | 波动量 | int16 | 62 | 62 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 7 Current Unbalance Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 8 Current Unbalance Factor | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | User Channel 9 Current Unbalance Factor | 波动量 | int16 | 969 | 969 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of V2 to V1 Vb/Vbc phase angle | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of V3 to V1 Vc/Vca phase angle | 波动量 | int16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 1 Current to V1 | 波动量 | int16 | 666 | 666 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 2 Current to V2 | 波动量 | int16 | 1813 | 1813 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 3 Current to V3 | 波动量 | int16 | 1888 | 1888 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 4 Current to V4 | 波动量 | int16 | 1729 | 1729 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 6 Current to V6 | 波动量 | int16 | 3024 | 3024 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 8 Current to V8 | 波动量 | int16 | 1356 | 1356 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 9 Current to V9 | 波动量 | int16 | 456 | 456 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 10 Current to V10 | 波动量 | int16 | 465 | 465 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 11 Current to V11 | 波动量 | int16 | 1012 | 1012 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 13 Current to V13 | 波动量 | int16 | 2460 | 2460 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 14 Current to V14 | 波动量 | int16 | 937 | 937 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 16 Current to V16 | 波动量 | int16 | 1941 | 1941 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 17 Current to V17 | 波动量 | int16 | 2697 | 2697 | 0 | 0.0% | ✓
AcuRev2100 | Phase Angle of Load 18 Current to V18 | 波动量 | int16 | 2660 | 2660 | 0 | 0.0% | ✓
AcuRev2100 | Channel 1 Address | 其他 | uint16 | 200 | 200 | 0 | 0.0% | ✓
AcuRev2100 | Channel 1 Parity | 其他 | uint16 | 3 | 3 | 0 | 0.0% | ✓
AcuRev2100 | Channel 2 Parity | 其他 | uint16 | 3 | 3 | 0 | 0.0% | ✓
AcuRev2100 | Channel 1 Baud Rate | 其他 | uint16 | 19200 | 19200 | 0 | 0.0% | ✓
AcuRev2100 | Channel 2 Baud Rate | 其他 | uint16 | 11520 | 11520 | 0 | 0.0% | ✓
AcuRev2100 | Password | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Pulse Constant | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Pulse Width | 其他 | uint16 | 80 | 80 | 0 | 0.0% | ✓
AcuRev2100 | Channel 2 Address | 其他 | uint16 | 101 | 101 | 0 | 0.0% | ✓
AcuRev2100 | Demand Method | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Demand Window | 波动量 | uint16 | 30 | 30 | 0 | 0.0% | ✓
AcuRev2100 | Demand Sub Interval | 波动量 | uint16 | 15 | 15 | 0 | 0.0% | ✓
AcuRev2100 | CT2 Value | 其他 | uint16 | 333 | 333 | 0 | 0.0% | ✓
AcuRev2100 | LCD Backlight Time | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Reactive Power Calculation Method | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | VAR/PF Convention | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
AcuRev2100 | Nominal Voltage | 稳定量 | uint16 | 400 | 400 | 0 | 0.0% | ✓
AcuRev2100 | Service Configuration | 其他 | uint16 | 5 | 5 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 1 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 2 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 3 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 4 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 5 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 6 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 7 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 8 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 9 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 10 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 11 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 12 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 13 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 14 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 15 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 16 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 17 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | Input Channel 18 CT | 其他 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
AcuRev2100 | CT2 Type | 其他 | uint16 | 85 | 85 | 0 | 0.0% | ✓
AcuRev2100 | Meter Model | 其他 | uint32 | 1213411377 | 1213411377 | 0 | 0.0% | ✓
AcuRev2100 | Hardware version | 其他 | uint32 | 825110578 | 825110578 | 0 | 0.0% | ✓
AcuRev2100 | Software version | 其他 | uint32 | 825111089 | 825111089 | 0 | 0.0% | ✓
AcuRev2100 | Software date | 其他 | uint32 | 842346553 | 842346553 | 0 | 0.0% | ✓
AcuRev2100 | Restore Factory Setting | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Enable 10 Years TOU settings | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Non-Standard Content Seal Option | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | Sealing Status | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
AcuRev2100 | user01 User Name | 其他 | uint16 | 28257 | 28257 | 0 | 0.0% | ✓
AcuRev2100 | user02 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user03 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user04 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user05 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user06 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user07 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user08 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user09 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user10 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user11 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user12 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user13 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user14 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user15 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user16 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user17 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
AcuRev2100 | user18 User Name | 其他 | uint16 | 30067 | 30067 | 0 | 0.0% | ✓
Acuvim3 | System Frequency | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Average Line-to-Neutral Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A-B Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B-C Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C-A Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Average Line-to-Line Voltage | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Line Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Line Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Line Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Neutral Current | 波动量 | float32 | 0.0005 | 0.0005 | 0 | 0.0% | ✓
Acuvim3 | Average Line Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Load Nature | 其他 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Load Nature | 其他 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Load Nature | 其他 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Load Nature | 其他 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Leading Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Leading Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Leading Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Leading Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Lagging Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Lagging Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Lagging Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Lagging Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase AB Line-to-Line Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase BC Line-to-Line Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase CA Line-to-Line Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Zero Sequence Ratio Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Zero Sequence Ratio Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Voltage Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Voltage THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Voltage THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Voltage THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Voltage THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Voltage THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Voltage THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Voltage THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Voltage THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Voltage THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Voltage Crest Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Voltage Crest Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Voltage Crest Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase N Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase N Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase N Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current TDD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current TDD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current TDD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase N Current TDD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current Crest-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current Crest-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current Crest-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase N Current Crest-Factor | 波动量 | float32 | 256 | 256 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current K-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current K-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current K-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase N Current K-Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Voltage Flicker | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Voltage Flicker | 波动量 | float32 | 17.0167 | 17.0167 | 0 | 0.0% | ✓
Acuvim3 | Phase C Voltage Flicker | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Average Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Energy-Import | 稳定量 | float64 | 13.4214 | 13.4214 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Energy-Import | 稳定量 | float64 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Energy-Import | 稳定量 | float64 | 14.5859 | 14.5859 | 0 | 0.0% | ✓
Acuvim3 | System Active Energy-Import | 稳定量 | float64 | 9.0281 | 9.0281 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Energy-Import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Energy-Import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Energy-Import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Energy-Import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Energy-Export | 稳定量 | float64 | 0.1512 | 0.1512 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Energy-Export | 稳定量 | float64 | 0.0024 | 0.0024 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Energy-Export | 稳定量 | float64 | 0.1452 | 0.1452 | 0 | 0.0% | ✓
Acuvim3 | System Active Energy-Export | 稳定量 | float64 | 0.0055 | 0.0055 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Energy-Export | 稳定量 | float64 | 3.6346 | 3.6346 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Energy-Export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Energy-Export | 稳定量 | float64 | 2.6844 | 2.6844 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Energy-Export | 稳定量 | float64 | 4.8445 | 4.8445 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Energy-Net | 稳定量 | float64 | 13.2703 | 13.2703 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Energy-Net | 稳定量 | float64 | -0.0023 | -0.0023 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Energy-Net | 稳定量 | float64 | 14.4407 | 14.4407 | 0 | 0.0% | ✓
Acuvim3 | System Active Energy-Net | 稳定量 | float64 | 9.0225 | 9.0225 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Energy-Net | 稳定量 | float64 | -3.6346 | -3.6346 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Energy-Net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Energy-Net | 稳定量 | float64 | -2.6844 | -2.6844 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Energy-Net | 稳定量 | float64 | -4.8445 | -4.8445 | 0 | 0.0% | ✓
Acuvim3 | Phase A Active Energy-Total | 稳定量 | float64 | 13.5726 | 13.5726 | 0 | 0.0% | ✓
Acuvim3 | Phase B Active Energy-Total | 稳定量 | float64 | 0.0025 | 0.0025 | 0 | 0.0% | ✓
Acuvim3 | Phase C Active Energy-Total | 稳定量 | float64 | 14.7311 | 14.7311 | 0 | 0.0% | ✓
Acuvim3 | System Active Energy-Total | 稳定量 | float64 | 9.0337 | 9.0337 | 0 | 0.0% | ✓
Acuvim3 | Phase A Reactive Energy-Total | 稳定量 | float64 | 3.6346 | 3.6346 | 0 | 0.0% | ✓
Acuvim3 | Phase B Reactive Energy-Total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acuvim3 | Phase C Reactive Energy-Total | 稳定量 | float64 | 2.6844 | 2.6844 | 0 | 0.0% | ✓
Acuvim3 | System Reactive Energy-Total | 稳定量 | float64 | 4.8445 | 4.8445 | 0 | 0.0% | ✓
Acuvim3 | Phase A Apparent Energy | 稳定量 | float64 | 14.5733 | 14.5733 | 0 | 0.0% | ✓
Acuvim3 | Phase B Apparent Energy | 稳定量 | float64 | 0.0031 | 0.0031 | 0 | 0.0% | ✓
Acuvim3 | Phase C Apparent Energy | 稳定量 | float64 | 15.489 | 15.489 | 0 | 0.0% | ✓
Acuvim3 | System Apparent Energy | 稳定量 | float64 | 10.3145 | 10.3145 | 0 | 0.0% | ✓
Acuvim3 | Service Configuration | 其他 | uint16 | 4 | 4 | 0 | 0.0% | ✓
Acuvim3 | Phase Order | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Frequency | 稳定量 | float32 | 49.9995 | 49.9995 | 0 | 0.0% | ✓
Acurev4100 | Phase A Line-to-Neutral Voltage | 稳定量 | float32 | 57.2392 | 57.2392 | 0 | 0.0% | ✓
Acurev4100 | Phase C Line-to-Neutral Voltage | 稳定量 | float32 | 56.7134 | 56.7134 | 0 | 0.0% | ✓
Acurev4100 | Average Line-to-Neutral Voltage | 稳定量 | float32 | 56.9376 | 56.9376 | 0 | 0.0% | ✓
Acurev4100 | Phase A-B Line-to-Line Voltage | 稳定量 | float32 | 98.8228 | 98.8228 | 0 | 0.0% | ✓
Acurev4100 | Phase B-C Line-to-Line Voltage | 稳定量 | float32 | 98.3747 | 98.3747 | 0 | 0.0% | ✓
Acurev4100 | Phase C-A Line-to-Line Voltage | 稳定量 | float32 | 98.6568 | 98.6568 | 0 | 0.0% | ✓
Acurev4100 | Average Line-to-Line Voltage | 稳定量 | float32 | 98.6192 | 98.6192 | 0 | 0.0% | ✓
Acurev4100 | Phase A Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Line-to-Neutral Voltage Phase Angle | 波动量 | float32 | 119.939 | 119.939 | 0 | 0.0% | ✓
Acurev4100 | Phase A Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Average Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current Phase Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Active Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Reactive Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Apparent Power | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Load Nature | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Average Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Import Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Export Active Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Import Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Export Reactive Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Apparent Power Demand | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Negative Sequence Magnitude | 波动量 | float32 | 56.9638 | 56.9638 | 0 | 0.0% | ✓
Acurev4100 | Voltage Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Negative Sequence Angle | 波动量 | float32 | 359.9926 | 359.9926 | 0 | 0.0% | ✓
Acurev4100 | Voltage Unbalance Factor Magnitude | 波动量 | float32 | 150 | 150 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage THD | 波动量 | float32 | 0.0142 | 0.0142 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage THD Odd | 波动量 | float32 | 0.0136 | 0.0136 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage THD Even | 波动量 | float32 | 0.0056 | 0.0056 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage Crest Factor | 波动量 | float32 | 1.4143 | 1.4143 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage THFF Factor | 波动量 | float32 | 0.4438 | 0.4438 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 2 percentage | 波动量 | float32 | 0.001 | 0.001 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 3 percentage | 波动量 | float32 | 0.0066 | 0.0066 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 4 percentage | 波动量 | float32 | 0.0018 | 0.0018 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 5 percentage | 波动量 | float32 | 0.0029 | 0.0029 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 6 percentage | 波动量 | float32 | 0.0009 | 0.0009 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 7 percentage | 波动量 | float32 | 0.004 | 0.004 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 8 percentage | 波动量 | float32 | 0.0025 | 0.0025 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 9 percentage | 波动量 | float32 | 0.002 | 0.002 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 10 percentage | 波动量 | float32 | 0.0013 | 0.0013 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 12 percentage | 波动量 | float32 | 0.002 | 0.002 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 13 percentage | 波动量 | float32 | 0.0037 | 0.0037 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 14 percentage | 波动量 | float32 | 0.0015 | 0.0015 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 15 percentage | 波动量 | float32 | 0.0037 | 0.0037 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 16 percentage | 波动量 | float32 | 0.0016 | 0.0016 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 17 percentage | 波动量 | float32 | 0.003 | 0.003 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 18 percentage | 波动量 | float32 | 0.0004 | 0.0004 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 19 percentage | 波动量 | float32 | 0.0021 | 0.0021 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 20 percentage | 波动量 | float32 | 0.0011 | 0.0011 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 21 percentage | 波动量 | float32 | 0.0018 | 0.0018 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 22 percentage | 波动量 | float32 | 0.0011 | 0.0011 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 23 percentage | 波动量 | float32 | 0.0014 | 0.0014 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 24 percentage | 波动量 | float32 | 0.0016 | 0.0016 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 25 percentage | 波动量 | float32 | 0.003 | 0.003 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 26 percentage | 波动量 | float32 | 0.001 | 0.001 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 27 percentage | 波动量 | float32 | 0.001 | 0.001 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 29 percentage | 波动量 | float32 | 0.0025 | 0.0025 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 30 percentage | 波动量 | float32 | 0.0006 | 0.0006 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage individual Harmonics 31 percentage | 波动量 | float32 | 0.0013 | 0.0013 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage THD | 波动量 | float32 | 0.0198 | 0.0198 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage THD Odd | 波动量 | float32 | 0.0192 | 0.0192 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage THFF Factor | 波动量 | float32 | 0.4438 | 0.4438 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 2 percentage | 波动量 | float32 | 0.0029 | 0.0029 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 3 percentage | 波动量 | float32 | 0.0166 | 0.0166 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 4 percentage | 波动量 | float32 | 0.0014 | 0.0014 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 5 percentage | 波动量 | float32 | 0.0051 | 0.0051 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 7 percentage | 波动量 | float32 | 0.0019 | 0.0019 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 8 percentage | 波动量 | float32 | 0.0011 | 0.0011 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 9 percentage | 波动量 | float32 | 0.0017 | 0.0017 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 10 percentage | 波动量 | float32 | 0.0003 | 0.0003 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 11 percentage | 波动量 | float32 | 0.0017 | 0.0017 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 12 percentage | 波动量 | float32 | 0.0009 | 0.0009 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 13 percentage | 波动量 | float32 | 0.0032 | 0.0032 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 14 percentage | 波动量 | float32 | 0.0003 | 0.0003 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 15 percentage | 波动量 | float32 | 0.0035 | 0.0035 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 16 percentage | 波动量 | float32 | 0.0006 | 0.0006 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 17 percentage | 波动量 | float32 | 0.0023 | 0.0023 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 18 percentage | 波动量 | float32 | 0.0009 | 0.0009 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 19 percentage | 波动量 | float32 | 0.0021 | 0.0021 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 20 percentage | 波动量 | float32 | 0.0008 | 0.0008 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 21 percentage | 波动量 | float32 | 0.0016 | 0.0016 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 22 percentage | 波动量 | float32 | 0.0005 | 0.0005 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 23 percentage | 波动量 | float32 | 0.002 | 0.002 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 24 percentage | 波动量 | float32 | 0.0003 | 0.0003 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 25 percentage | 波动量 | float32 | 0.002 | 0.002 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 26 percentage | 波动量 | float32 | 0.0015 | 0.0015 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 27 percentage | 波动量 | float32 | 0.0019 | 0.0019 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 28 percentage | 波动量 | float32 | 0.0011 | 0.0011 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 29 percentage | 波动量 | float32 | 0.0007 | 0.0007 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 30 percentage | 波动量 | float32 | 0.0004 | 0.0004 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage individual Harmonics 31 percentage | 波动量 | float32 | 0.0012 | 0.0012 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage THD | 波动量 | float32 | 0.026 | 0.026 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage THD Odd | 波动量 | float32 | 0.0257 | 0.0257 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage THD Even | 波动量 | float32 | 0.005 | 0.005 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage Crest Factor | 波动量 | float32 | 1.4144 | 1.4144 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage THFF Factor | 波动量 | float32 | 0.4438 | 0.4438 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 2 percentage | 波动量 | float32 | 0.001 | 0.001 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 3 percentage | 波动量 | float32 | 0.0234 | 0.0234 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 5 percentage | 波动量 | float32 | 0.0066 | 0.0066 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 6 percentage | 波动量 | float32 | 0.0012 | 0.0012 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 7 percentage | 波动量 | float32 | 0.0037 | 0.0037 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 8 percentage | 波动量 | float32 | 0.0019 | 0.0019 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 9 percentage | 波动量 | float32 | 0.0022 | 0.0022 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 10 percentage | 波动量 | float32 | 0.0007 | 0.0007 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 12 percentage | 波动量 | float32 | 0.0009 | 0.0009 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 13 percentage | 波动量 | float32 | 0.0037 | 0.0037 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 14 percentage | 波动量 | float32 | 0.0015 | 0.0015 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 15 percentage | 波动量 | float32 | 0.0036 | 0.0036 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 16 percentage | 波动量 | float32 | 0.0018 | 0.0018 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 17 percentage | 波动量 | float32 | 0.0022 | 0.0022 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 19 percentage | 波动量 | float32 | 0.002 | 0.002 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 20 percentage | 波动量 | float32 | 0.0007 | 0.0007 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 21 percentage | 波动量 | float32 | 0.0019 | 0.0019 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 22 percentage | 波动量 | float32 | 0.0015 | 0.0015 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 23 percentage | 波动量 | float32 | 0.0005 | 0.0005 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 24 percentage | 波动量 | float32 | 0.0007 | 0.0007 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 25 percentage | 波动量 | float32 | 0.0021 | 0.0021 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 26 percentage | 波动量 | float32 | 0.001 | 0.001 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 27 percentage | 波动量 | float32 | 0.003 | 0.003 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 28 percentage | 波动量 | float32 | 0.0016 | 0.0016 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 29 percentage | 波动量 | float32 | 0.0015 | 0.0015 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 30 percentage | 波动量 | float32 | 0.0008 | 0.0008 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage individual Harmonics 31 percentage | 波动量 | float32 | 0.0017 | 0.0017 | 0 | 0.0% | ✓
Acurev4100 | Average Voltage THD | 波动量 | float32 | 0.018 | 0.018 | 0 | 0.0% | ✓
Acurev4100 | Average Voltage THD Odd | 波动量 | float32 | 0.0169 | 0.0169 | 0 | 0.0% | ✓
Acurev4100 | Average Voltage THD Even | 波动量 | float32 | 0.0057 | 0.0057 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current THD | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current THD Odd | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current THD Even | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current K Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 2 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 3 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 4 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 5 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 6 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 7 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 8 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 9 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 10 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 11 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 12 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 13 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 14 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 15 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 16 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 17 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 18 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 19 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 20 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 21 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 22 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 23 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 24 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 25 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 26 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 27 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 28 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 29 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 30 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current individual Harmonics 31 percentage | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Positive Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Zero Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Negative Sequence Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Positive Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Zero Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Negative Sequence Angle | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Unbalance Factor Magnitude | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 active energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 active energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 active energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 active energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 reactive energy import | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 reactive energy export | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 reactive energy net | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 reactive energy total | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 apparent energy | 稳定量 | float64 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI1 pulse count | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI2 pulse count | 其他 | uint32 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | DI3 pulse count | 其他 | uint32 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | DI4 pulse count | 其他 | uint32 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | Current Rated Value | 波动量 | uint16 | 50000 | 50000 | 0 | 0.0% | ✓
Acurev4100 | Voltage Rated Value | 稳定量 | uint16 | 50 | 50 | 0 | 0.0% | ✓
Acurev4100 | Voltage Sag Enable | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Voltage Sag Threshold | 稳定量 | uint16 | 90 | 90 | 0 | 0.0% | ✓
Acurev4100 | Voltage Sag Jitter | 稳定量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
Acurev4100 | Voltage Sag Triggers Waveform Recording | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Voltage Sag - switch to output DO | 稳定量 | uint16 | 8 | 8 | 0 | 0.0% | ✓
Acurev4100 | Voltage Sag - switch to output RO | 稳定量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | Voltage Swell Enable | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Voltage Swell Threshold | 稳定量 | uint16 | 150 | 150 | 0 | 0.0% | ✓
Acurev4100 | Voltage Swell Jitter | 稳定量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
Acurev4100 | Voltage Swell Triggers Waveform Recording | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Voltage Swell - switch to output DO | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Swell - switch to output RO | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Interruption Enable | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Voltage Interruption Threshold | 稳定量 | uint16 | 20 | 20 | 0 | 0.0% | ✓
Acurev4100 | Voltage Interruption Jitter | 稳定量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
Acurev4100 | Voltage Interruption Triggers Waveform Recording | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Voltage Interruption - switch to output DO | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Interruption - switch to output RO | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Current Swell Enable | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Current Swell Threshold | 波动量 | uint16 | 150 | 150 | 0 | 0.0% | ✓
Acurev4100 | Current Swell Jitter | 波动量 | uint16 | 10 | 10 | 0 | 0.0% | ✓
Acurev4100 | Current Triggers Waveform Recording | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Current Swell - switch to output DO | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Current Swell - switch to output RO | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | sampling rate | 其他 | uint16 | 3 | 3 | 0 | 0.0% | ✓
Acurev4100 | Number of cycles before the event occurred | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Number of cycles after the event occurred | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | DI1 Trigger | 其他 | uint16 | 255 | 255 | 0 | 0.0% | ✓
Acurev4100 | DI2 Trigger | 其他 | uint16 | 255 | 255 | 0 | 0.0% | ✓
Acurev4100 | DI3 Trigger | 其他 | uint16 | 255 | 255 | 0 | 0.0% | ✓
Acurev4100 | DI4 Trigger | 其他 | uint16 | 255 | 255 | 0 | 0.0% | ✓
Acurev4100 | Manually Trigger | 其他 | uint16 | 255 | 255 | 0 | 0.0% | ✓
Acurev4100 | System Frequency Max value | 稳定量 | float32 | 130.4576 | 130.4576 | 0 | 0.0% | ✓
Acurev4100 | System Frequency Max value Timestamp | 稳定量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase A Line-to-Neutral Voltage Max value | 稳定量 | float32 | 1983774.125 | 1983774.125 | 0 | 0.0% | ✓
Acurev4100 | Phase A Line-to-Neutral Voltage Max value Timestamp | 稳定量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase B Line-to-Neutral Voltage Max value | 稳定量 | float32 | 1972309.375 | 1972309.375 | 0 | 0.0% | ✓
Acurev4100 | Phase B Line-to-Neutral Voltage Max value Timestamp | 稳定量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase C Line-to-Neutral Voltage Max value | 稳定量 | float32 | 1967606.75 | 1967606.75 | 0 | 0.0% | ✓
Acurev4100 | Phase C Line-to-Neutral Voltage Max value Timestamp | 稳定量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase AB Line-to-Line Voltage Max value | 稳定量 | float32 | 3426472.25 | 3426472.25 | 0 | 0.0% | ✓
Acurev4100 | Phase AB Line-to-Line Voltage Max value Timestamp | 稳定量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase BC Line-to-Line Voltage Max value | 稳定量 | float32 | 3448257.5 | 3448257.5 | 0 | 0.0% | ✓
Acurev4100 | Phase BC Line-to-Line Voltage Max value Timestamp | 稳定量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase CA Line-to-Line Voltage Max value | 稳定量 | float32 | 3432756.75 | 3432756.75 | 0 | 0.0% | ✓
Acurev4100 | Phase CA Line-to-Line Voltage Max value Timestamp | 稳定量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
Acurev4100 | Phase A Current Max value | 波动量 | float32 | 213.016 | 213.016 | 0 | 0.0% | ✓
Acurev4100 | Phase A Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase A Active Power Max value | 波动量 | float32 | 45041.6094 | 45041.6094 | 0 | 0.0% | ✓
Acurev4100 | Phase A Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase A Reactive Power Max value | 波动量 | float32 | 45046.75 | 45046.75 | 0 | 0.0% | ✓
Acurev4100 | Phase A Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase A Apparent Power Max value | 波动量 | float32 | 79162.4375 | 79162.4375 | 0 | 0.0% | ✓
Acurev4100 | Phase A Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase A Power Factor Max value | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Phase A Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage THD Max value | 波动量 | float32 | 29996.4023 | 29996.4023 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage THD Max value Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
Acurev4100 | Phase B Current Max value | 波动量 | float32 | 98.8724 | 98.8724 | 0 | 0.0% | ✓
Acurev4100 | Phase B Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase B Active Power Max value | 波动量 | float32 | 33088.0898 | 33088.0898 | 0 | 0.0% | ✓
Acurev4100 | Phase B Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase B Reactive Power Max value | 波动量 | float32 | 34532.8555 | 34532.8555 | 0 | 0.0% | ✓
Acurev4100 | Phase B Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase B Apparent Power Max value | 波动量 | float32 | 66025.5234 | 66025.5234 | 0 | 0.0% | ✓
Acurev4100 | Phase B Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase B Power Factor Max value | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Phase B Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage THD Max value | 波动量 | float32 | 5892.3442 | 5892.3442 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage THD Max value Timestamp | 波动量 | uint16 | 6662 | 6662 | 0 | 0.0% | ✓
Acurev4100 | Phase C Current Max value | 波动量 | float32 | 106.443 | 106.443 | 0 | 0.0% | ✓
Acurev4100 | Phase C Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase C Active Power Max value | 波动量 | float32 | 33655.6797 | 33655.6797 | 0 | 0.0% | ✓
Acurev4100 | Phase C Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase C Reactive Power Max value | 波动量 | float32 | 34388.3945 | 34388.3945 | 0 | 0.0% | ✓
Acurev4100 | Phase C Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase C Apparent Power Max value | 波动量 | float32 | 65930.4141 | 65930.4141 | 0 | 0.0% | ✓
Acurev4100 | Phase C Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase C Power Factor Max value | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Phase C Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage THD Max value | 波动量 | float32 | 10636.7256 | 10636.7256 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Voltage Unbalance Factor Magnitude Max value | 波动量 | float32 | 150 | 150 | 0 | 0.0% | ✓
Acurev4100 | Voltage Unbalance Factor Magnitude Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current Max value | 波动量 | float32 | 99.1591 | 99.1591 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Active Power Max value | 波动量 | float32 | 22586.2207 | 22586.2207 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Reactive Power Max value | 波动量 | float32 | 22589.4844 | 22589.4844 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Apparent Power Max value | 波动量 | float32 | 39698.0352 | 39698.0352 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Power Factor Max value | 波动量 | float32 | 1.0013 | 1.0013 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current THD Max value | 波动量 | float32 | 11849.0889 | 11849.0889 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current Max value | 波动量 | float32 | 98.8724 | 98.8724 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Active Power Max value | 波动量 | float32 | 33088.0898 | 33088.0898 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Reactive Power Max value | 波动量 | float32 | 34532.8555 | 34532.8555 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Apparent Power Max value | 波动量 | float32 | 66025.5234 | 66025.5234 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Power Factor Max value | 波动量 | float32 | 1.001 | 1.001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current THD Max value | 波动量 | float32 | 18203.3906 | 18203.3906 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current Max value | 波动量 | float32 | 98.7979 | 98.7979 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Active Power Max value | 波动量 | float32 | 33655.6797 | 33655.6797 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Reactive Power Max value | 波动量 | float32 | 34388.3945 | 34388.3945 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Apparent Power Max value | 波动量 | float32 | 65930.4141 | 65930.4141 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Power Factor Max value | 波动量 | float32 | 1.0009 | 1.0009 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current THD Max value | 波动量 | float32 | 50014.1758 | 50014.1758 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current Max value | 波动量 | float32 | 98.5914 | 98.5914 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Active Power Max value | 波动量 | float32 | 22457.875 | 22457.875 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Reactive Power Max value | 波动量 | float32 | 22457.6387 | 22457.6387 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Apparent Power Max value | 波动量 | float32 | 39464.4062 | 39464.4062 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Power Factor Max value | 波动量 | float32 | 1.0013 | 1.0013 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current THD Max value | 波动量 | float32 | 25148.9082 | 25148.9082 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current Max value | 波动量 | float32 | 0.0007 | 0.0007 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Power Factor Max value | 波动量 | float32 | 0.007 | 0.007 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current THD Max value | 波动量 | float32 | 5139.1572 | 5139.1572 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Active Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Reactive Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Apparent Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Apparent Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Power Factor Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Power Factor Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current THD Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current THD Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Active Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Reactive Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Apparent Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Apparent Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Power Factor Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Power Factor Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current THD Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current THD Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current Max value | 波动量 | float32 | 0.0007 | 0.0007 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Reactive Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Power Factor Max value | 波动量 | float32 | 0.0109 | 0.0109 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current THD Max value | 波动量 | float32 | 392.7067 | 392.7067 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Active Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Reactive Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Apparent Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Apparent Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Power Factor Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Power Factor Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current THD Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current THD Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current Max value | 波动量 | float32 | 0.0008 | 0.0008 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Power Factor Max value | 波动量 | float32 | 0.0092 | 0.0092 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current THD Max value | 波动量 | float32 | 720.66 | 720.66 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current Max value | 波动量 | float32 | 0.0006 | 0.0006 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Active Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Power Factor Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Power Factor Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current THD Max value | 波动量 | float32 | 354.2667 | 354.2667 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Active Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Reactive Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Apparent Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Apparent Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Power Factor Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Power Factor Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current THD Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current THD Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current Max value | 波动量 | float32 | 0.0097 | 0.0097 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Power Factor Max value | 波动量 | float32 | 0.0081 | 0.0081 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current THD Max value | 波动量 | float32 | 1615.493 | 1615.493 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current Max value | 波动量 | float32 | 0.0097 | 0.0097 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Power Factor Max value | 波动量 | float32 | 0.017 | 0.017 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current THD Max value | 波动量 | float32 | 1048.8672 | 1048.8672 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current Max value | 波动量 | float32 | 0.0097 | 0.0097 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Active Power Max value | 波动量 | float32 | 0.0034 | 0.0034 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Apparent Power Max value | 波动量 | float32 | 0.2597 | 0.2597 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Power Factor Max value | 波动量 | float32 | 0.0114 | 0.0114 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current THD Max value | 波动量 | float32 | 1226.6229 | 1226.6229 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current Max value | 波动量 | float32 | 0.0097 | 0.0097 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Active Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Reactive Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Apparent Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Apparent Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Power Factor Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Power Factor Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current THD Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current THD Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current Max value | 波动量 | float32 | 0.0006 | 0.0006 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Power Factor Max value | 波动量 | float32 | 0.0081 | 0.0081 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current THD Max value | 波动量 | float32 | 435.6893 | 435.6893 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current Max value | 波动量 | float32 | 0.0006 | 0.0006 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Power Factor Max value | 波动量 | float32 | 0.0009 | 0.0009 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current THD Max value | 波动量 | float32 | 347.5359 | 347.5359 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current Max value | 波动量 | float32 | 0.0006 | 0.0006 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Power Factor Max value | 波动量 | float32 | 0.0112 | 0.0112 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current THD Max value | 波动量 | float32 | 2369.9612 | 2369.9612 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current Max value | 波动量 | float32 | 0.0008 | 0.0008 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Power Factor Max value | 波动量 | float32 | 0.0144 | 0.0144 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current THD Max value | 波动量 | float32 | 1239.2365 | 1239.2365 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current Max value | 波动量 | float32 | 0.0008 | 0.0008 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Power Factor Max value | 波动量 | float32 | 0.0129 | 0.0129 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current THD Max value | 波动量 | float32 | 966.7012 | 966.7012 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current Max value | 波动量 | float32 | 0.0007 | 0.0007 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Power Factor Max value | 波动量 | float32 | 0.0213 | 0.0213 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current THD Max value | 波动量 | float32 | 874.1249 | 874.1249 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current Max value | 波动量 | float32 | 0.0096 | 0.0096 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Power Factor Max value | 波动量 | float32 | 0.0056 | 0.0056 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current THD Max value | 波动量 | float32 | 877.7515 | 877.7515 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current Max value | 波动量 | float32 | 0.63 | 0.63 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Power Factor Max value | 波动量 | float32 | 0.0119 | 0.0119 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Power Factor Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current THD Max value | 波动量 | float32 | 493.768 | 493.768 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current THD Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Max value | 波动量 | float32 | 98.9431 | 98.9431 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Active Power Max value | 波动量 | float32 | 39702.8047 | 39702.8047 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Reactive Power Max value | 波动量 | float32 | 43843.9453 | 43843.9453 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Apparent Power Max value | 波动量 | float32 | 146374.0625 | 146374.0625 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 1 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 1 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Max value | 波动量 | float32 | 76.0215 | 76.0215 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Active Power Max value | 波动量 | float32 | 22457.875 | 22457.875 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Reactive Power Max value | 波动量 | float32 | 22457.6387 | 22457.6387 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Apparent Power Max value | 波动量 | float32 | 39464.4062 | 39464.4062 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 2 Power Factor | 波动量 | float32 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 2 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Max value | 波动量 | float32 | 0.0002 | 0.0002 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Reactive Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 3 Power Factor | 波动量 | float32 | 0.0109 | 0.0109 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 3 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Max value | 波动量 | float32 | 0.0005 | 0.0005 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Apparent Power Max value | 波动量 | float32 | 0.0002 | 0.0002 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 4 Power Factor | 波动量 | float32 | 0.0073 | 0.0073 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 4 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Max value | 波动量 | float32 | 0.0097 | 0.0097 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Active Power Max value | 波动量 | float32 | 0.0034 | 0.0034 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Apparent Power Max value | 波动量 | float32 | 0.2597 | 0.2597 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 5 Power Factor | 波动量 | float32 | 0.013 | 0.013 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 5 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Max value | 波动量 | float32 | 0.0032 | 0.0032 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Apparent Power Max value | 波动量 | float32 | 0.0001 | 0.0001 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 6 Power Factor | 波动量 | float32 | 0.0081 | 0.0081 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 6 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Max value | 波动量 | float32 | 0.0007 | 0.0007 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Apparent Power Max value | 波动量 | float32 | 0.0003 | 0.0003 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 7 Power Factor | 波动量 | float32 | 0.0093 | 0.0093 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 7 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Max value | 波动量 | float32 | 0.21 | 0.21 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Active Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Reactive Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Apparent Power Max value | 波动量 | float32 | 0.0002 | 0.0002 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Apparent Power Max value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 8 Power Factor | 波动量 | float32 | 0.0161 | 0.0161 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 8 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Active Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Reactive Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Apparent Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Apparent Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 9 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 9 Power Factor Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Active Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Reactive Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Apparent Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Apparent Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 10 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 10 Power Factor Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Active Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Reactive Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Apparent Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Apparent Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 11 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 11 Power Factor Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Active Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Active Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Reactive Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Reactive Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Apparent Power Max value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Apparent Power Max value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 12 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Max User Channel 12 Power Factor Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | System Frequency Min value | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | System Frequency Min value Timestamp | 稳定量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase A Line-to-Neutral Voltage Min value | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Line-to-Neutral Voltage Min value Timestamp | 稳定量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase B Line-to-Neutral Voltage Min value | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Line-to-Neutral Voltage Min value Timestamp | 稳定量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase C Line-to-Neutral Voltage Min value | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Line-to-Neutral Voltage Min value Timestamp | 稳定量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase AB Line-to-Line Voltage Min value | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase AB Line-to-Line Voltage Min value Timestamp | 稳定量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase BC Line-to-Line Voltage Min value | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase BC Line-to-Line Voltage Min value Timestamp | 稳定量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase CA Line-to-Line Voltage Min value | 稳定量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase CA Line-to-Line Voltage Min value Timestamp | 稳定量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase A Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase A Active Power Min value | 波动量 | float32 | -79162.0312 | -79162.0312 | 0 | 0.0% | ✓
Acurev4100 | Phase A Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase A Reactive Power Min value | 波动量 | float32 | -12423.8418 | -12423.8418 | 0 | 0.0% | ✓
Acurev4100 | Phase A Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase A Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase A Power Factor Min value | 波动量 | float32 | -1.0013 | -1.0013 | 0 | 0.0% | ✓
Acurev4100 | Phase A Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase A Voltage THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase B Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase B Active Power Min value | 波动量 | float32 | -33931.1055 | -33931.1055 | 0 | 0.0% | ✓
Acurev4100 | Phase B Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase B Reactive Power Min value | 波动量 | float32 | -20721.1523 | -20721.1523 | 0 | 0.0% | ✓
Acurev4100 | Phase B Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase B Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase B Power Factor Min value | 波动量 | float32 | -1 | -1 | 0 | 0.0% | ✓
Acurev4100 | Phase B Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase B Voltage THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase C Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase C Active Power Min value | 波动量 | float32 | -32716.9863 | -32716.9863 | 0 | 0.0% | ✓
Acurev4100 | Phase C Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase C Reactive Power Min value | 波动量 | float32 | -34703.8711 | -34703.8711 | 0 | 0.0% | ✓
Acurev4100 | Phase C Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase C Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Phase C Power Factor Min value | 波动量 | float32 | -1.0013 | -1.0013 | 0 | 0.0% | ✓
Acurev4100 | Phase C Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Phase C Voltage THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Voltage Unbalance Factor Magnitude Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Voltage Unbalance Factor Magnitude Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Active Power Min value | 波动量 | float32 | -39697.8203 | -39697.8203 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Reactive Power Min value | 波动量 | float32 | -6229.0933 | -6229.0933 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Power Factor Min value | 波动量 | float32 | -1.0007 | -1.0007 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 1 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Active Power Min value | 波动量 | float32 | -33931.1055 | -33931.1055 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Reactive Power Min value | 波动量 | float32 | -20721.1523 | -20721.1523 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Power Factor Min value | 波动量 | float32 | -1.0013 | -1.0013 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 2 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Active Power Min value | 波动量 | float32 | -32716.9863 | -32716.9863 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Reactive Power Min value | 波动量 | float32 | -34703.8711 | -34703.8711 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Power Factor Min value | 波动量 | float32 | -1.0004 | -1.0004 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 3 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Active Power Min value | 波动量 | float32 | -39464.2148 | -39464.2148 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Reactive Power Min value | 波动量 | float32 | -6194.748 | -6194.748 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Power Factor Min value | 波动量 | float32 | -1.0013 | -1.0013 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 4 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Power Factor Min value | 波动量 | float32 | -0.013 | -0.013 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 5 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Reactive Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Power Factor Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Power Factor Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 6 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Reactive Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Power Factor Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Power Factor Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 7 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Power Factor Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Power Factor Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 8 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Reactive Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Power Factor Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Power Factor Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 9 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Power Factor Min value | 波动量 | float32 | -0.022 | -0.022 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 10 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Power Factor Min value | 波动量 | float32 | -0.0167 | -0.0167 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 11 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Reactive Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Power Factor Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Power Factor Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 12 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Power Factor Min value | 波动量 | float32 | -0.0102 | -0.0102 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 13 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Power Factor Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Power Factor Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 14 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Reactive Power Min value | 波动量 | float32 | -0.0139 | -0.0139 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Power Factor Min value | 波动量 | float32 | -0.0268 | -0.0268 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 15 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Reactive Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Power Factor Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Power Factor Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 16 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Power Factor Min value | 波动量 | float32 | -0.0041 | -0.0041 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 17 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Reactive Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Power Factor Min value | 波动量 | float32 | -0.0098 | -0.0098 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 18 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Power Factor Min value | 波动量 | float32 | -0.0072 | -0.0072 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 19 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Power Factor Min value | 波动量 | float32 | -0.0088 | -0.0088 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 20 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Power Factor Min value | 波动量 | float32 | -0.02 | -0.02 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 21 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Power Factor Min value | 波动量 | float32 | -0.007 | -0.007 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 22 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Power Factor Min value | 波动量 | float32 | -0.0159 | -0.0159 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Power Factor Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 23 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Reactive Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Power Factor Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Power Factor Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current THD Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Input Channel 24 Current THD Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Active Power Min value | 波动量 | float32 | -56815.6406 | -56815.6406 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Reactive Power Min value | 波动量 | float32 | -42064.4531 | -42064.4531 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 1 Power Factor | 波动量 | float32 | -1.1394 | -1.1394 | 0 | 0.0% | ✓
Acurev4100 | User Channel 1 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Active Power Min value | 波动量 | float32 | -39464.2148 | -39464.2148 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Reactive Power Min value | 波动量 | float32 | -6194.748 | -6194.748 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 2 Power Factor | 波动量 | float32 | -1.1329 | -1.1329 | 0 | 0.0% | ✓
Acurev4100 | User Channel 2 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 3 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 3 Power Factor Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 4 Power Factor | 波动量 | float32 | -0.022 | -0.022 | 0 | 0.0% | ✓
Acurev4100 | User Channel 4 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Reactive Power Min value | 波动量 | float32 | -0.0139 | -0.0139 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 5 Power Factor | 波动量 | float32 | -0.01 | -0.01 | 0 | 0.0% | ✓
Acurev4100 | User Channel 5 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 6 Power Factor | 波动量 | float32 | -0.0041 | -0.0041 | 0 | 0.0% | ✓
Acurev4100 | User Channel 6 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 7 Power Factor | 波动量 | float32 | -0.0093 | -0.0093 | 0 | 0.0% | ✓
Acurev4100 | User Channel 7 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Active Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Reactive Power Min value Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 8 Power Factor | 波动量 | float32 | -0.0036 | -0.0036 | 0 | 0.0% | ✓
Acurev4100 | User Channel 8 Power Factor Timestamp | 波动量 | uint16 | 6661 | 6661 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Reactive Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 9 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 9 Power Factor Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Reactive Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 10 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 10 Power Factor Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Reactive Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 11 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 11 Power Factor Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Current Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Active Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Active Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Reactive Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Reactive Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Apparent Power Min value | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Apparent Power Min value Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | Min User Channel 12 Power Factor | 波动量 | float32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | User Channel 12 Power Factor Timestamp | 波动量 | uint16 | 6145 | 6145 | 0 | 0.0% | ✓
Acurev4100 | The Number of the Waveform Record Group | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Data state of waveform record window | 其他 | uint16 | 255 | 255 | 0 | 0.0% | ✓
Acurev4100 | Latest Waveform Record Groupe Number | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | The index of the PQEvent Log | 其他 | uint16 | 48 | 48 | 0 | 0.0% | ✓
Acurev4100 | The Number of the PQEvent Log | 其他 | uint16 | 200 | 200 | 0 | 0.0% | ✓
Acurev4100 | Serial Number1 | 其他 | uint16 | 16712 | 16712 | 0 | 0.0% | ✓
Acurev4100 | Serial Number2 | 其他 | uint16 | 12336 | 12336 | 0 | 0.0% | ✓
Acurev4100 | Serial Number3 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Serial Number4 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Hardware version | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Function Model Type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Reserved11 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Current Input Type | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Power Supply Type | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | MAC address1 | 其他 | uint16 | 17731 | 17731 | 0 | 0.0% | ✓
Acurev4100 | MAC address2 | 其他 | uint16 | 12342 | 12342 | 0 | 0.0% | ✓
Acurev4100 | MAC address3 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | MAC address4 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Certification Type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | AIAO or DIDO flag | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Reserved 21 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Reserved 22 | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Reserved 23 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Hardware Patch Number | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Firmware version | 其他 | uint32 | 825110579 | 825110579 | 0 | 0.0% | ✓
Acurev4100 | Firmware release date1 | 其他 | uint32 | 842412085 | 842412085 | 0 | 0.0% | ✓
Acurev4100 | Firmware release date2 | 其他 | uint16 | 12345 | 12345 | 0 | 0.0% | ✓
Acurev4100 | Firmware patch number | 其他 | uint16 | 12340 | 12340 | 0 | 0.0% | ✓
Acurev4100 | bootloader product string | 其他 | uint32 | 1296122162 | 1296122162 | 0 | 0.0% | ✓
Acurev4100 | bootloader version | 其他 | uint32 | 825110578 | 825110578 | 0 | 0.0% | ✓
Acurev4100 | bootloader release date1 | 其他 | uint32 | 842412081 | 842412081 | 0 | 0.0% | ✓
Acurev4100 | bootloader release date2 | 其他 | uint16 | 12595 | 12595 | 0 | 0.0% | ✓
Acurev4100 | bootloader patch number | 其他 | uint16 | 12339 | 12339 | 0 | 0.0% | ✓
Acurev4100 | Password | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Baud Rate | 其他 | uint16 | 19200 | 19200 | 0 | 0.0% | ✓
Acurev4100 | Parity | 其他 | uint16 | 3 | 3 | 0 | 0.0% | ✓
Acurev4100 | DHCP enable | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | IP address | 其他 | uint32 | 3232236274 | 3232236274 | 0 | 0.0% | ✓
Acurev4100 | Subnet mask | 其他 | uint32 | 4294966784 | 4294966784 | 0 | 0.0% | ✓
Acurev4100 | Gateway | 其他 | uint32 | 3232236289 | 3232236289 | 0 | 0.0% | ✓
Acurev4100 | DNS primary server | 其他 | uint32 | 134744072 | 134744072 | 0 | 0.0% | ✓
Acurev4100 | DNS secondary server | 其他 | uint32 | 134743044 | 134743044 | 0 | 0.0% | ✓
Acurev4100 | Modbus Slave ID | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | RS485 protocol | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Modbus TCP Enable | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Modbus TCP port | 其他 | uint16 | 502 | 502 | 0 | 0.0% | ✓
Acurev4100 | BACnet MS/TP Meter address | 其他 | uint16 | 5 | 5 | 0 | 0.0% | ✓
Acurev4100 | BACnet MS/TP Maximum number of message frames | 其他 | uint16 | 255 | 255 | 0 | 0.0% | ✓
Acurev4100 | BACnet MS/TP ID | 其他 | uint32 | 5 | 5 | 0 | 0.0% | ✓
Acurev4100 | BACnet MS/TP Database Revision | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | LCD Backlight Time | 其他 | uint16 | 120 | 120 | 0 | 0.0% | ✓
Acurev4100 | Device run time | 其他 | uint32 | 14625512 | 14625512 | 0 | 0.0% | ✓
Acurev4100 | Device load time | 其他 | uint32 | 354217 | 354217 | 0 | 0.0% | ✓
Acurev4100 | MaxDemand Clear Mode | 波动量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | MaxDemand Clear Date Setting | 波动量 | uint32 | 520093696 | 520093696 | 0 | 0.0% | ✓
Acurev4100 | MaxDemand Clear Total Count | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Timestamp of the most recent MaxDemand Clear | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Timestamp of the most recent MaxDemand Clear | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Timestamp of the most recent MaxDemand Clear | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Non-standard Seal Parameter Select | 其他 | uint16 | 16 | 16 | 0 | 0.0% | ✓
Acurev4100 | Week | 其他 | uint16 | 3 | 3 | 0 | 0.0% | ✓
Acurev4100 | Year | 其他 | uint16 | 2026 | 2026 | 0 | 0.0% | ✓
Acurev4100 | Month | 其他 | uint16 | 6 | 6 | 0 | 0.0% | ✓
Acurev4100 | Day | 其他 | uint16 | 10 | 10 | 0 | 0.0% | ✓
Acurev4100 | Hour | 其他 | uint16 | 17 | 17 | 0 | 0.0% | ✓
Acurev4100 | Minute | 其他 | uint16 | 28 | 28 | 0 | 0.0% | ✓
Acurev4100 | Second | 其他 | uint16 | 55 | 55 | 0 | 0.0% | ✓
Acurev4100 | TempPassword | 其他 | uint16 | 8630 | 8630 | 0 | 0.0% | ✓
Acurev4100 | Sealing Status | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Frequency Selection | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Service Configuration | 其他 | uint16 | 4 | 4 | 0 | 0.0% | ✓
Acurev4100 | Reserve1 | 其他 | uint32 | 500 | 500 | 0 | 0.0% | ✓
Acurev4100 | Reserve2 | 其他 | uint16 | 500 | 500 | 0 | 0.0% | ✓
Acurev4100 | channel1 input wiring | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | channel1 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel1 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel1 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel1 voltage assignment | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel2 input wiring | 其他 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | channel2 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel2 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel2 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel2 voltage assignment | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | channel3 input wiring | 其他 | uint16 | 3 | 3 | 0 | 0.0% | ✓
Acurev4100 | channel3 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel3 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel3 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel3 voltage assignment | 稳定量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | channel4 input wiring | 其他 | uint16 | 4 | 4 | 0 | 0.0% | ✓
Acurev4100 | channel4 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel4 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel4 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel4 voltage assignment | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel5 input wiring | 其他 | uint16 | 5 | 5 | 0 | 0.0% | ✓
Acurev4100 | channel5 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel5 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel5 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel5 voltage assignment | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | channel6 input wiring | 其他 | uint16 | 6 | 6 | 0 | 0.0% | ✓
Acurev4100 | channel6 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel6 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel6 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel6 voltage assignment | 稳定量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | channel7 input wiring | 其他 | uint16 | 7 | 7 | 0 | 0.0% | ✓
Acurev4100 | channel7 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel7 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel7 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel7 voltage assignment | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel8 input wiring | 其他 | uint16 | 8 | 8 | 0 | 0.0% | ✓
Acurev4100 | channel8 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel8 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel8 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel8 voltage assignment | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | channel9 input wiring | 其他 | uint16 | 9 | 9 | 0 | 0.0% | ✓
Acurev4100 | channel9 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel9 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel9 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel9 voltage assignment | 稳定量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | channel10 input wiring | 其他 | uint16 | 10 | 10 | 0 | 0.0% | ✓
Acurev4100 | channel10 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel10 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel10 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel10 voltage assignment | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel11 input wiring | 其他 | uint16 | 11 | 11 | 0 | 0.0% | ✓
Acurev4100 | channel11 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel11 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel11 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel11 voltage assignment | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | channel12 input wiring | 其他 | uint16 | 12 | 12 | 0 | 0.0% | ✓
Acurev4100 | channel12 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel12 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel12 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel12 voltage assignment | 稳定量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | channel13 input wiring | 其他 | uint16 | 13 | 13 | 0 | 0.0% | ✓
Acurev4100 | channel13 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel13 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel13 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel13 voltage assignment | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel14 input wiring | 其他 | uint16 | 14 | 14 | 0 | 0.0% | ✓
Acurev4100 | channel14 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel14 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel14 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel14 voltage assignment | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | channel15 input wiring | 其他 | uint16 | 15 | 15 | 0 | 0.0% | ✓
Acurev4100 | channel15 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel15 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel15 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel15 voltage assignment | 稳定量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | channel16 input wiring | 其他 | uint16 | 16 | 16 | 0 | 0.0% | ✓
Acurev4100 | channel16 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel16 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel16 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel16 voltage assignment | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel17 input wiring | 其他 | uint16 | 17 | 17 | 0 | 0.0% | ✓
Acurev4100 | channel17 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel17 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel17 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel17 voltage assignment | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | channel18 input wiring | 其他 | uint16 | 18 | 18 | 0 | 0.0% | ✓
Acurev4100 | channel18 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel18 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel18 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel18 voltage assignment | 稳定量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | channel19 input wiring | 其他 | uint16 | 19 | 19 | 0 | 0.0% | ✓
Acurev4100 | channel19 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel19 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel19 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel19 voltage assignment | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel20 input wiring | 其他 | uint16 | 20 | 20 | 0 | 0.0% | ✓
Acurev4100 | channel20 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel20 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel20 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel20 voltage assignment | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | channel21 input wiring | 其他 | uint16 | 21 | 21 | 0 | 0.0% | ✓
Acurev4100 | channel21 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel21 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel21 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel21 voltage assignment | 稳定量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | channel22 input wiring | 其他 | uint16 | 22 | 22 | 0 | 0.0% | ✓
Acurev4100 | channel22 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel22 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel22 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel22 voltage assignment | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel23 input wiring | 其他 | uint16 | 23 | 23 | 0 | 0.0% | ✓
Acurev4100 | channel23 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel23 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel23 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel23 voltage assignment | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | channel24 input wiring | 其他 | uint16 | 24 | 24 | 0 | 0.0% | ✓
Acurev4100 | channel24 CT type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel24 primary | 其他 | uint16 | 1000 | 1000 | 0 | 0.0% | ✓
Acurev4100 | channel24 direction | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | channel24 voltage assignment | 稳定量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | user 1 input channel assignment | 其他 | uint32 | 7 | 7 | 0 | 0.0% | ✓
Acurev4100 | user 2 input channel assignment | 其他 | uint32 | 56 | 56 | 0 | 0.0% | ✓
Acurev4100 | user 3 input channel assignment | 其他 | uint32 | 448 | 448 | 0 | 0.0% | ✓
Acurev4100 | user 4 input channel assignment | 其他 | uint32 | 3584 | 3584 | 0 | 0.0% | ✓
Acurev4100 | user 5 input channel assignment | 其他 | uint32 | 28672 | 28672 | 0 | 0.0% | ✓
Acurev4100 | user 6 input channel assignment | 其他 | uint32 | 229376 | 229376 | 0 | 0.0% | ✓
Acurev4100 | user 7 input channel assignment | 其他 | uint32 | 1835008 | 1835008 | 0 | 0.0% | ✓
Acurev4100 | user 8 input channel assignment | 其他 | uint32 | 14680064 | 14680064 | 0 | 0.0% | ✓
Acurev4100 | user 9 input channel assignment | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | user 10 input channel assignment | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | user 11 input channel assignment | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | user 12 input channel assignment | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Demand Method | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Demand Interval | 波动量 | uint16 | 30 | 30 | 0 | 0.0% | ✓
Acurev4100 | Demand update rate | 波动量 | uint16 | 30 | 30 | 0 | 0.0% | ✓
Acurev4100 | VAR/PF Convention | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Energy Calculation Method | 稳定量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Reactive Power Calculation Method | 波动量 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Phase Order | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Energy Reading Display format | 稳定量 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | Reserve3 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Energy pulse constant | 稳定量 | uint32 | 100000000 | 100000000 | 0 | 0.0% | ✓
Acurev4100 | Pulse LED width | 其他 | uint16 | 100 | 100 | 0 | 0.0% | ✓
Acurev4100 | Pulse LED parameter selection | 其他 | uint16 | 253 | 253 | 0 | 0.0% | ✓
Acurev4100 | DO1 Type | 其他 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | DO1 Pulse width | 其他 | uint16 | 100 | 100 | 0 | 0.0% | ✓
Acurev4100 | DO1 parameter selection | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO2 Type | 其他 | uint16 | 2 | 2 | 0 | 0.0% | ✓
Acurev4100 | DO2 Pulse width | 其他 | uint16 | 100 | 100 | 0 | 0.0% | ✓
Acurev4100 | DO2 parameter selection | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO3 Type | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | DO3 Pulse width | 其他 | uint16 | 100 | 100 | 0 | 0.0% | ✓
Acurev4100 | DO3 parameter selection | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO4 Type | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | DO4 Pulse width | 其他 | uint16 | 100 | 100 | 0 | 0.0% | ✓
Acurev4100 | DO4 parameter selection | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO5 Type | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | DO5 Pulse width | 其他 | uint16 | 100 | 100 | 0 | 0.0% | ✓
Acurev4100 | DO5 parameter selection | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO6 Type | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | DO6 Pulse width | 其他 | uint16 | 100 | 100 | 0 | 0.0% | ✓
Acurev4100 | DO6 parameter selection | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO7 Type | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | DO7 Pulse width | 其他 | uint16 | 100 | 100 | 0 | 0.0% | ✓
Acurev4100 | DO7 parameter selection | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DO8 Type | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | DO8 Pulse width | 其他 | uint16 | 100 | 100 | 0 | 0.0% | ✓
Acurev4100 | DO8parameter selection | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI1 Type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI1 pulse constant | 其他 | uint32 | 10000 | 10000 | 0 | 0.0% | ✓
Acurev4100 | DI2 Type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI2 pulse constant | 其他 | uint32 | 10000 | 10000 | 0 | 0.0% | ✓
Acurev4100 | DI3 Type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI3 pulse constant | 其他 | uint32 | 10000 | 10000 | 0 | 0.0% | ✓
Acurev4100 | DI4 Type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | DI4 pulse constant | 其他 | uint32 | 10000 | 10000 | 0 | 0.0% | ✓
Acurev4100 | RO1 Type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | RO1 Control Mode | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | RO1 Pulse Width | 其他 | uint16 | 100 | 100 | 0 | 0.0% | ✓
Acurev4100 | RO2 Type | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | RO2 Control Mode | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | RO2 Pulse Width | 其他 | uint16 | 100 | 100 | 0 | 0.0% | ✓
Acurev4100 | Clear energy | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear Max demand | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear MaxDemand ClearCount and Timestamp | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear max/min | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear device run time | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear load time | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Factory reset | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Network reset | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear SOE Log | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear alarm Log | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear PQ event Log | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear Waveform | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear Data Log1 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear Data Log2 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear Data Log3 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear Trend Log | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear DI Count | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear Year 10 Holiday Number Setting | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Restore TOU factory setting | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Clear TOU Energy | 稳定量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Device Reboot | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | The index of the SOE Log | 其他 | uint16 | 4 | 4 | 0 | 0.0% | ✓
Acurev4100 | Number of the SOE Log | 其他 | uint16 | 4 | 4 | 0 | 0.0% | ✓
Acurev4100 | Web2 Meter Setting Status | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 DHCP enable | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Web2 Eth1 IP address | 其他 | uint32 | 3232236297 | 3232236297 | 0 | 0.0% | ✓
Acurev4100 | Web2 Eth1 Subnet mask | 其他 | uint32 | 4294966784 | 4294966784 | 0 | 0.0% | ✓
Acurev4100 | Web2 Eth1 Gateway | 其他 | uint32 | 3232236289 | 3232236289 | 0 | 0.0% | ✓
Acurev4100 | Web2 Eth1 DNS primary server | 其他 | uint32 | 134744072 | 134744072 | 0 | 0.0% | ✓
Acurev4100 | Web2 DNS secondary server | 其他 | uint32 | 134743044 | 134743044 | 0 | 0.0% | ✓
Acurev4100 | Web2 Eth2 IP address | 其他 | uint32 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 WIFI IP address | 其他 | uint32 | 3232261121 | 3232261121 | 0 | 0.0% | ✓
Acurev4100 | Web2 Device Reboot | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 Factory reset | 波动量 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 Network reset | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 Enable clock synchronization | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 Mode Setting | 其他 | uint16 | 1 | 1 | 0 | 0.0% | ✓
Acurev4100 | Web2 Firmware version1 | 其他 | uint16 | 12590 | 12590 | 0 | 0.0% | ✓
Acurev4100 | Web2 Firmware version2 | 其他 | uint16 | 28720 | 28720 | 0 | 0.0% | ✓
Acurev4100 | Web2 Serial Number1 | 其他 | uint16 | 16712 | 16712 | 0 | 0.0% | ✓
Acurev4100 | Web2 Serial Number2 | 其他 | uint16 | 12336 | 12336 | 0 | 0.0% | ✓
Acurev4100 | Web2 Serial Number3 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 Serial Number4 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 ETH1 MAC address1 | 其他 | uint16 | 13104 | 13104 | 0 | 0.0% | ✓
Acurev4100 | Web2 ETH1 MAC address2 | 其他 | uint16 | 26166 | 26166 | 0 | 0.0% | ✓
Acurev4100 | Web2 ETH1 MAC address3 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 ETH1 MAC address4 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 ETH2 MAC address1 | 其他 | uint16 | 13104 | 13104 | 0 | 0.0% | ✓
Acurev4100 | Web2 ETH2 MAC address2 | 其他 | uint16 | 26166 | 26166 | 0 | 0.0% | ✓
Acurev4100 | Web2 ETH2 MAC address3 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 ETH2 MAC address4 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 WIFI MAC address1 | 其他 | uint16 | 25136 | 25136 | 0 | 0.0% | ✓
Acurev4100 | Web2 WIFI MAC address2 | 其他 | uint16 | 13410 | 13410 | 0 | 0.0% | ✓
Acurev4100 | Web2 WIFI MAC address3 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓
Acurev4100 | Web2 WIFI MAC address4 | 其他 | uint16 | 0 | 0 | 0 | 0.0% | ✓

## 用例Mapping
用例ID | 用例函数名 | 测试类型 | 验证点 | 关联TC编号
PT-001 | test_pt_001_config | 功能 | 启用Pass Through，Ethernet设备SlaveID均在101–247范围内 | TestCase_AcuHMI_008_05_config
PT-002 | test_pt_002_data_collected | 功能 | 按型号寄存器表经透传读到可比对数据；缺表/无响应则skip并诊断 | TestCase_AcuHMI_008_05_data
PT-003 | test_pt_003_passthrough_matches_direct | 数据正确性 | 透传路径(A) ↔ 直连真实电表(B) 逐寄存器数值一致率达标 | TestCase_AcuHMI_008_05_case05
PT-004 | test_pt_case01_enable_disable_toggle | 功能 | Disable+Save后透传读取失败；Enable+Save后恢复读取 | TestCase_AcuHMI_008_05_case01
PT-005 | test_pt_case07_concurrent_masters | 并发 | 多Modbus主站并发以不同SlaveID经透传读取，各自正常、无串扰 | TestCase_AcuHMI_008_05_case07
PT-006 | test_pt_case02_valid_slaveid_save | 边界 | 有效SlaveID(101–247)保存成功且持久化生效 | TestCase_AcuHMI_008_05_case02
PT-007 | test_pt_case03_slaveid_boundary | 边界 | 越界SlaveID(100/248)被拒；边界值(101/247)保存成功 | TestCase_AcuHMI_008_05_case03
PT-008 | test_pt_case04_duplicate_slaveid | 异常 | 两设备配置相同SlaveID应被拒绝或不同时生效 | TestCase_AcuHMI_008_05_case04
PT-009 | test_pt_case06_disabled_blocks_access | 功能 | Pass Through关闭后无法经透传SlaveID访问下游设备，系统其余功能正常 | TestCase_AcuHMI_008_05_case06