## block
blockId | type | start | count | isEnable | NAME
0 | VIRTUAL_BLOCK | 0 | 1 | true | isOnline
1 | HOLDING_REGISTER | 8192 | 72 | true | System Basic Reading | 8264
2 | HOLDING_REGISTER | 8264 | 112 | true | Input Channal Basic Reading 1 | 8376
3 | HOLDING_REGISTER | 8376 | 112 | true | Input Channal Basic Reading 2 | 8488
4 | HOLDING_REGISTER | 8488 | 112 | true | Input Channal Basic Reading 3 | 8600
5 | HOLDING_REGISTER | 8600 | 72 | true | User Channal Basic Reading 1 | 8672
6 | HOLDING_REGISTER | 8672 | 72 | true | User Channal Basic Reading 2 | 8744
7 | HOLDING_REGISTER | 8960 | 48 | true | Demand 1 | 9008
8 | HOLDING_REGISTER | 9008 | 96 | true | Demand 2 | 9104
9 | HOLDING_REGISTER | 9104 | 96 | true | Demand 3 | 9200
10 | HOLDING_REGISTER | 9200 | 96 | true | Demand 4 | 9296
11 | HOLDING_REGISTER | 9296 | 72 | true | Demand 5 | 9368
12 | HOLDING_REGISTER | 9368 | 72 | true | Demand 6 | 9440
13 | HOLDING_REGISTER | 9728 | 84 | true | Power Quality 1 | 9812
14 | HOLDING_REGISTER | 9812 | 70 | true | Power Quality 2 | 9882
15 | HOLDING_REGISTER | 9882 | 70 | true | Power Quality 3 | 9952
16 | HOLDING_REGISTER | 9952 | 74 | true | Power Quality 4 | 10026
17 | HOLDING_REGISTER | 10026 | 68 | true | Power Quality 5 | 10094
18 | HOLDING_REGISTER | 10094 | 68 | true | Power Quality 6 | 10162
19 | HOLDING_REGISTER | 10162 | 68 | true | Power Quality 7 | 10230
20 | HOLDING_REGISTER | 10230 | 68 | true | Power Quality 8 | 10298
21 | HOLDING_REGISTER | 10298 | 68 | true | Power Quality 9 | 10366
22 | HOLDING_REGISTER | 10366 | 68 | true | Power Quality 10 | 10434
23 | HOLDING_REGISTER | 10434 | 68 | true | Harmonics 11 | 10502
24 | HOLDING_REGISTER | 10502 | 68 | true | Harmonics 12 | 10570
25 | HOLDING_REGISTER | 10570 | 68 | true | Harmonics 13 | 10638
26 | HOLDING_REGISTER | 10638 | 68 | true | Harmonics 14 | 10706
27 | HOLDING_REGISTER | 10706 | 68 | true | Harmonics 15 | 10774
28 | HOLDING_REGISTER | 10774 | 68 | true | Harmonics 16 | 10842
29 | HOLDING_REGISTER | 10842 | 68 | true | Harmonics 17 | 10910
30 | HOLDING_REGISTER | 10910 | 68 | true | Harmonics 18 | 10978
31 | HOLDING_REGISTER | 10978 | 68 | true | Harmonics 19 | 11046
32 | HOLDING_REGISTER | 11046 | 68 | true | Harmonics 20 | 11114
33 | HOLDING_REGISTER | 11114 | 68 | true | Harmonics 21 | 11182
34 | HOLDING_REGISTER | 11182 | 68 | true | Harmonics 22 | 11250
35 | HOLDING_REGISTER | 11250 | 68 | true | Harmonics 23 | 11318
36 | HOLDING_REGISTER | 11318 | 68 | true | Harmonics 24 | 11386
37 | HOLDING_REGISTER | 11386 | 68 | true | Harmonics 25 | 11454
38 | HOLDING_REGISTER | 11454 | 68 | true | Harmonics 26 | 11522
39 | HOLDING_REGISTER | 11522 | 68 | true | Harmonics 27 | 11590
40 | HOLDING_REGISTER | 11590 | 84 | true | Sequence 1 | 11674
41 | HOLDING_REGISTER | 11674 | 84 | true | Sequence 2 | 11758
42 | HOLDING_REGISTER | 12288 | 124 | true | Energy 1 | 12412
43 | HOLDING_REGISTER | 12412 | 124 | true | Energy 2 | 12536
44 | HOLDING_REGISTER | 12536 | 124 | true | Energy 3 | 12660
45 | HOLDING_REGISTER | 12660 | 124 | true | Energy 4 | 12784
46 | HOLDING_REGISTER | 12784 | 124 | true | Energy 5 | 12908
47 | HOLDING_REGISTER | 12908 | 124 | true | Energy 6 | 13032
48 | HOLDING_REGISTER | 13032 | 124 | true | Energy 7 | 13156
49 | HOLDING_REGISTER | 13156 | 124 | true | Energy 8 | 13280
50 | HOLDING_REGISTER | 13280 | 124 | true | Energy 9 | 13404
51 | HOLDING_REGISTER | 13404 | 124 | true | Energy 10 | 13528
52 | HOLDING_REGISTER | 13528 | 124 | true | Energy 11 | 13652
53 | HOLDING_REGISTER | 13652 | 76 | true | Energy 12 | 13728
54 | HOLDING_REGISTER | 25600 | 8 | true | DI Pulse Count | 25608
55 | INPUT_STATUS | 0 | 4 | true | DI Status | 4
56 | COIL_STATUS | 0 | 8 | true | DO Status | 8
57 | COIL_STATUS | 32 | 2 | true | RO Status | 34
58 | HOLDING_REGISTER | 25856 | 26 | true | Device Settings Class PQ | 25882
59 | HOLDING_REGISTER | 25968 | 8 | true | Device Settings Class Waveform | 25976
60 | HOLDING_REGISTER | 14080 | 120 | true | System Max Demand | 14200
61 | HOLDING_REGISTER | 14200 | 120 | true | Input Channal Max Demand 1 | 14320
62 | HOLDING_REGISTER | 14320 | 120 | true | Input Channal Max Demand 2 | 14440
63 | HOLDING_REGISTER | 14440 | 120 | true | Input Channal Max Demand 3 | 14560
64 | HOLDING_REGISTER | 14560 | 120 | true | Input Channal Max Demand 4 | 14680
65 | HOLDING_REGISTER | 14680 | 120 | true | Input Channal Max Demand 5 | 14800
66 | HOLDING_REGISTER | 14800 | 120 | true | Input Channal Max Demand 6 | 14920
67 | HOLDING_REGISTER | 14920 | 120 | true | User Channal Max Demand 1 | 15040
68 | HOLDING_REGISTER | 15040 | 120 | true | User Channal Max Demand 2 | 15160
69 | HOLDING_REGISTER | 15160 | 120 | true | User Channal Max Demand 3 | 15280
70 | HOLDING_REGISTER | 20992 | 42 | true | Max value record 1 | 21034
71 | HOLDING_REGISTER | 21034 | 114 | true | Max value record 2 | 21148
72 | HOLDING_REGISTER | 21148 | 108 | true | Max value record 3 | 21256
73 | HOLDING_REGISTER | 21256 | 108 | true | Max value record 4 | 21364
74 | HOLDING_REGISTER | 21364 | 108 | true | Max value record 5 | 21472
75 | HOLDING_REGISTER | 21472 | 108 | true | Max value record 6 | 21580
76 | HOLDING_REGISTER | 21580 | 108 | true | Max value record 7 | 21688
77 | HOLDING_REGISTER | 21688 | 108 | true | Max value record 8 | 21796
78 | HOLDING_REGISTER | 21796 | 108 | true | Max value record 9 | 21904
79 | HOLDING_REGISTER | 21904 | 108 | true | Max value record 10 | 22012
80 | HOLDING_REGISTER | 22012 | 120 | true | Max value record 11 | 22132
81 | HOLDING_REGISTER | 22132 | 120 | true | Max value record 12 | 22252
82 | HOLDING_REGISTER | 22252 | 120 | true | Max value record 13 | 22372
83 | HOLDING_REGISTER | 22528 | 42 | true | Min value record 1 | 22570
84 | HOLDING_REGISTER | 22570 | 114 | true | Min value record 2 | 22684
85 | HOLDING_REGISTER | 22684 | 108 | true | Min value record 3 | 22792
86 | HOLDING_REGISTER | 22792 | 108 | true | Min value record 4 | 22900
87 | HOLDING_REGISTER | 22900 | 108 | true | Min value record 5 | 23008
88 | HOLDING_REGISTER | 23008 | 108 | true | Min value record 6 | 23116
89 | HOLDING_REGISTER | 23116 | 108 | true | Min value record 7 | 23224
90 | HOLDING_REGISTER | 23224 | 108 | true | Min value record 8 | 23332
91 | HOLDING_REGISTER | 23332 | 108 | true | Min value record 9 | 23440
92 | HOLDING_REGISTER | 23440 | 108 | true | Min value record 10 | 23548
93 | HOLDING_REGISTER | 23548 | 120 | true | Min value record 11 | 23668
94 | HOLDING_REGISTER | 23668 | 120 | true | Min value record 12 | 23788
95 | HOLDING_REGISTER | 23788 | 120 | true | Min value record 13 | 23908
96 | HOLDING_REGISTER | 26115 | 3 | true | Waveform | 26118
97 | HOLDING_REGISTER | 26369 | 2 | true | PQ Event | 26371
98 | HOLDING_REGISTER | 61504 | 49 | true | Product Info | 61553
99 | HOLDING_REGISTER | 61440 | 6 | true | Firmware Version Info | 61446
100 | HOLDING_REGISTER | 61456 | 8 | true | Bootloader Info | 61464
101 | HOLDING_REGISTER | 4096 | 44 | true | Device Settings Basic 1 | 4140
102 | HOLDING_REGISTER | 4160 | 6 | true | Metrology Settings 1 | 4166
103 | HOLDING_REGISTER | 4166 | 120 | true | Metrology Settings 2 | 4286
104 | HOLDING_REGISTER | 4286 | 37 | true | Metrology Settings 3 | 4323
105 | HOLDING_REGISTER | 4352 | 42 | true | Device Settings Basic 3 | 4394
106 | HOLDING_REGISTER | 4400 | 21 | true | Device Settings Basic 4 | 4421 | Energy pulse constant
107 | HOLDING_REGISTER | 25344 | 2 | true | SOE Log Status | 25346 | Pulse Constant

## blockParams
ID | blockId | paramId | Start(Dec) | descrption | paramType | unit | dataType | byteOrder | RW | Reg | scale | analysisUnitId | north | conf | range | readings |  | paramType
1 | 0 | 0-1 | 0 | IsOnline | IsOnline |  | isOnline | 1 | R | 1 | 1 |  |  |  | 7 |  |  | IsOnline
2 | 1 | 1-1 | 8192 | System Frequency | FREQ_Hz | Hz | float32 | 22 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-35-1 |  | FREQ_Hz
3 | 1 | 1-2 | 8194 | Phase A Line-to-Neutral Voltage | VLN_a_V | V | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-35-1 |  | VLN_a_V
4 | 1 | 1-3 | 8196 | Phase B Line-to-Neutral Voltage | VLN_b_V | V | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-35-1 |  | VLN_b_V
5 | 1 | 1-4 | 8198 | Phase C Line-to-Neutral Voltage | VLN_c_V | V | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-35-1 |  | VLN_c_V
6 | 1 | 1-5 | 8200 | Average Line-to-Neutral Voltage | VLN_avg_V | V | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | VLN_avg_V
7 | 1 | 1-6 | 8202 | Phase A-B Line-to-Line Voltage | VLL_ab_V | V | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | VLL_ab_V
8 | 1 | 1-7 | 8204 | Phase B-C Line-to-Line Voltage | VLL_bc_V | V | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | VLL_bc_V
9 | 1 | 1-8 | 8206 | Phase C-A Line-to-Line Voltage | VLL_ca_V | V | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | VLL_ca_V
10 | 1 | 1-9 | 8208 | Average Line-to-Line Voltage | VLL_avg_V | V | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | VLL_avg_V
11 | 1 | 1-10 | 8210 | Phase A Line-to-Neutral Voltage Phase Angle | ANG_VLN_a | ° | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | ANG_VLN_a
12 | 1 | 1-11 | 8212 | Phase B Line-to-Neutral Voltage Phase Angle | ANG_VLN_b | ° | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | ANG_VLN_b
13 | 1 | 1-12 | 8214 | Phase C Line-to-Neutral Voltage Phase Angle | ANG_VLN_c | ° | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | ANG_VLN_c
14 | 1 | 1-13 | 8216 | Phase A Current | I_a_A | A | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | I_a_A
15 | 1 | 1-14 | 8218 | Phase A Active Power | P_a_kW | kW | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | P_a_kW
16 | 1 | 1-15 | 8220 | Phase A Reactive Power | Q_a_kvar | kvar | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | Q_a_kvar
17 | 1 | 1-16 | 8222 | Phase A Apparent Power | S_a_kVA | kVA | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | S_a_kVA
18 | 1 | 1-17 | 8224 | Phase A Load Nature | LC_a |  | uint32 | 55 | R | 2 | 1 |  |  |  |  | 9
19 | 1 | 1-18 | 8226 | Phase A Power Factor | PF_a | % | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9 |  | PF_a
20 | 1 | 1-19 | 8228 | Phase B Current | I_b_A | A | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | I_b_A
21 | 1 | 1-20 | 8230 | Phase B Active Power | P_b_kW | kW | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | P_b_kW
22 | 1 | 1-21 | 8232 | Phase B Reactive Power | Q_b_kvar | kvar | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | Q_b_kvar
23 | 1 | 1-22 | 8234 | Phase B Apparent Power | S_b_kVA | kVA | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | S_b_kVA
24 | 1 | 1-23 | 8236 | Phase B Load Nature | LC_b |  | uint32 | 55 | R | 2 | 1 |  |  |  |  | 9
25 | 1 | 1-24 | 8238 | Phase B Power Factor | PF_b | % | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9 |  | PF_b
26 | 1 | 1-25 | 8240 | Phase C Current | I_c_A | A | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | I_c_A
27 | 1 | 1-26 | 8242 | Phase C Active Power | P_c_kW | kW | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | P_c_kW
28 | 1 | 1-27 | 8244 | Phase C Reactive Power | Q_c_kvar | kvar | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | Q_c_kvar
29 | 1 | 1-28 | 8246 | Phase C Apparent Power | S_c_kVA | kVA | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | S_c_kVA
30 | 1 | 1-29 | 8248 | Phase C Load Nature | LC_c |  | uint32 | 55 | R | 2 | 1 |  |  |  |  | 9
31 | 1 | 1-30 | 8250 | Phase C Power Factor | PF_c | % | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9 |  | PF_c
32 | 1 | 1-31 | 8252 | System Average Current | I_avg_A | A | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | I_avg_A
33 | 1 | 1-32 | 8254 | System Active Power | P_kW | kW | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | P_kW
34 | 1 | 1-33 | 8256 | System Reactive Power | Q_kvar | kvar | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | Q_kvar
35 | 1 | 1-34 | 8258 | System Apparent Power | S_kVA | kVA | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9-2-1 |  | S_kVA
36 | 1 | 1-35 | 8260 | System Load Nature | LC |  | uint32 | 55 | R | 2 | 1 |  |  |  |  | 9
37 | 1 | 1-36 | 8262 | System Power Factor | PF | % | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8-40 | 9 |  | PF
38 | 2 | 2-1 | 8264 | Input Channel 1 Current | I_001_A | A | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_001_A
39 | 2 | 2-2 | 8266 | Input Channel 1 Active Power | P_001_kW | kW | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_001_kW
40 | 2 | 2-3 | 8268 | Input Channel 1 Reactive Power | Q_001_kvar | kvar | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_001_kvar
41 | 2 | 2-4 | 8270 | Input Channel 1 Apparent Power | S_001_kVA | kVA | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_001_kVA
42 | 2 | 2-5 | 8272 | Input Channel 1 Load Nature | LC_001 |  | uint32 | 55 | R | 2 | 1 |  |  |  |  | 10
43 | 2 | 2-6 | 8274 | Input Channel 1 Power Factor | PF_001 | % | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_001
44 | 2 | 2-7 | 8276 | Input Channel 1 Current Phase Angle | ANG_I_001 | ° | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_001
45 | 2 | 2-8 | 8278 | Input Channel 2 Current | I_002_A | A | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_002_A
46 | 2 | 2-9 | 8280 | Input Channel 2 Active Power | P_002_kW | kW | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_002_kW
47 | 2 | 2-10 | 8282 | Input Channel 2 Reactive Power | Q_002_kvar | kvar | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_002_kvar
48 | 2 | 2-11 | 8284 | Input Channel 2 Apparent Power | S_002_kVA | kVA | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_002_kVA
49 | 2 | 2-12 | 8286 | Input Channel 2 Load Nature | LC_002 |  | uint32 | 55 | R | 2 | 1 |  |  |  |  | 10
50 | 2 | 2-13 | 8288 | Input Channel 2 Power Factor | PF_002 | % | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_002
51 | 2 | 2-14 | 8290 | Input Channel 2 Current Phase Angle | ANG_I_002 | ° | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_002
52 | 2 | 2-15 | 8292 | Input Channel 3 Current | I_003_A | A | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_003_A
53 | 2 | 2-16 | 8294 | Input Channel 3 Active Power | P_003_kW | kW | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_003_kW
54 | 2 | 2-17 | 8296 | Input Channel 3 Reactive Power | Q_003_kvar | kvar | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_003_kvar
55 | 2 | 2-18 | 8298 | Input Channel 3 Apparent Power | S_003_kVA | kVA | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_003_kVA
56 | 2 | 2-19 | 8300 | Input Channel 3 Load Nature | LC_003 |  | uint32 | 55 | R | 2 | 1 |  |  |  |  | 10
57 | 2 | 2-20 | 8302 | Input Channel 3 Power Factor | PF_003 | % | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_003
58 | 2 | 2-21 | 8304 | Input Channel 3 Current Phase Angle | ANG_I_003 | ° | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_003
59 | 2 | 2-22 | 8306 | Input Channel 4 Current | I_004_A | A | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_004_A
60 | 2 | 2-23 | 8308 | Input Channel 4 Active Power | P_004_kW | kW | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_004_kW
61 | 2 | 2-24 | 8310 | Input Channel 4 Reactive Power | Q_004_kvar | kvar | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_004_kvar
62 | 2 | 2-25 | 8312 | Input Channel 4 Apparent Power | S_004_kVA | kVA | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_004_kVA
63 | 2 | 2-26 | 8314 | Input Channel 4 Load Nature | LC_004 |  | uint32 | 55 | R | 2 | 1 |  |  |  |  | 10
64 | 2 | 2-27 | 8316 | Input Channel 4 Power Factor | PF_004 | % | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_004
65 | 2 | 2-28 | 8318 | Input Channel 4 Current Phase Angle | ANG_I_004 | ° | float32 | 55 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_004
66 | 2 | 2-29 | 8320 | Input Channel 5 Current | I_005_A | A | float32 | 22 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_005_A
67 | 2 | 2-30 | 8322 | Input Channel 5 Active Power | P_005_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_005_kW
68 | 2 | 2-31 | 8324 | Input Channel 5 Reactive Power | Q_005_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_005_kvar
69 | 2 | 2-32 | 8326 | Input Channel 5 Apparent Power | S_005_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_005_kVA
70 | 2 | 2-33 | 8328 | Input Channel 5 Load Nature | LC_005 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
71 | 2 | 2-34 | 8330 | Input Channel 5 Power Factor | PF_005 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_005
72 | 2 | 2-35 | 8332 | Input Channel 5 Current Phase Angle | ANG_I_005 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_005
73 | 2 | 2-36 | 8334 | Input Channel 6 Current | I_006_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_006_A
74 | 2 | 2-37 | 8336 | Input Channel 6 Active Power | P_006_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_006_kW
75 | 2 | 2-38 | 8338 | Input Channel 6 Reactive Power | Q_006_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_006_kvar
76 | 2 | 2-39 | 8340 | Input Channel 6 Apparent Power | S_006_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_006_kVA
77 | 2 | 2-40 | 8342 | Input Channel 6 Load Nature | LC_006 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
78 | 2 | 2-41 | 8344 | Input Channel 6 Power Factor | PF_006 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_006
79 | 2 | 2-42 | 8346 | Input Channel 6 Current Phase Angle | ANG_I_006 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_006
80 | 2 | 2-43 | 8348 | Input Channel 7 Current | I_007_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_007_A
81 | 2 | 2-44 | 8350 | Input Channel 7 Active Power | P_007_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_007_kW
82 | 2 | 2-45 | 8352 | Input Channel 7 Reactive Power | Q_007_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_007_kvar
83 | 2 | 2-46 | 8354 | Input Channel 7 Apparent Power | S_007_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_007_kVA
84 | 2 | 2-47 | 8356 | Input Channel 7 Load Nature | LC_007 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
85 | 2 | 2-48 | 8358 | Input Channel 7 Power Factor | PF_007 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_007
86 | 2 | 2-49 | 8360 | Input Channel 7 Current Phase Angle | ANG_I_007 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_007
87 | 2 | 2-50 | 8362 | Input Channel 8 Current | I_008_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_008_A
88 | 2 | 2-51 | 8364 | Input Channel 8 Active Power | P_008_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_008_kW
89 | 2 | 2-52 | 8366 | Input Channel 8 Reactive Power | Q_008_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_008_kvar
90 | 2 | 2-53 | 8368 | Input Channel 8 Apparent Power | S_008_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_008_kVA
91 | 2 | 2-54 | 8370 | Input Channel 8 Load Nature | LC_008 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
92 | 2 | 2-55 | 8372 | Input Channel 8 Power Factor | PF_008 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_008
93 | 2 | 2-56 | 8374 | Input Channel 8 Current Phase Angle | ANG_I_008 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_008
94 | 3 | 3-1 | 8376 | Input Channel 9 Current | I_009_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_009_A
95 | 3 | 3-2 | 8378 | Input Channel 9 Active Power | P_009_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_009_kW
96 | 3 | 3-3 | 8380 | Input Channel 9 Reactive Power | Q_009_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_009_kvar
97 | 3 | 3-4 | 8382 | Input Channel 9 Apparent Power | S_009_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_009_kVA
98 | 3 | 3-5 | 8384 | Input Channel 9 Load Nature | LC_009 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
99 | 3 | 3-6 | 8386 | Input Channel 9 Power Factor | PF_009 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_009
100 | 3 | 3-7 | 8388 | Input Channel 9 Current Phase Angle | ANG_I_009 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_009
101 | 3 | 3-8 | 8390 | Input Channel 10 Current | I_010_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_010_A
102 | 3 | 3-9 | 8392 | Input Channel 10 Active Power | P_010_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_010_kW
103 | 3 | 3-10 | 8394 | Input Channel 10 Reactive Power | Q_010_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_010_kvar
104 | 3 | 3-11 | 8396 | Input Channel 10 Apparent Power | S_010_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_010_kVA
105 | 3 | 3-12 | 8398 | Input Channel 10 Load Nature | LC_010 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
106 | 3 | 3-13 | 8400 | Input Channel 10 Power Factor | PF_010 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_010
107 | 3 | 3-14 | 8402 | Input Channel 10 Current Phase Angle | ANG_I_010 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_010
108 | 3 | 3-15 | 8404 | Input Channel 11 Current | I_011_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_011_A
109 | 3 | 3-16 | 8406 | Input Channel 11 Active Power | P_011_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_011_kW
110 | 3 | 3-17 | 8408 | Input Channel 11 Reactive Power | Q_011_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_011_kvar
111 | 3 | 3-18 | 8410 | Input Channel 11 Apparent Power | S_011_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_011_kVA
112 | 3 | 3-19 | 8412 | Input Channel 11 Load Nature | LC_011 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
113 | 3 | 3-20 | 8414 | Input Channel 11 Power Factor | PF_011 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_011
114 | 3 | 3-21 | 8416 | Input Channel 11 Current Phase Angle | ANG_I_011 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_011
115 | 3 | 3-22 | 8418 | Input Channel 12 Current | I_012_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_012_A
116 | 3 | 3-23 | 8420 | Input Channel 12 Active Power | P_012_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_012_kW
117 | 3 | 3-24 | 8422 | Input Channel 12 Reactive Power | Q_012_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_012_kvar
118 | 3 | 3-25 | 8424 | Input Channel 12 Apparent Power | S_012_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_012_kVA
119 | 3 | 3-26 | 8426 | Input Channel 12 Load Nature | LC_012 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
120 | 3 | 3-27 | 8428 | Input Channel 12 Power Factor | PF_012 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_012
121 | 3 | 3-28 | 8430 | Input Channel 12 Current Phase Angle | ANG_I_012 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_012
122 | 3 | 3-29 | 8432 | Input Channel 13 Current | I_013_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_013_A
123 | 3 | 3-30 | 8434 | Input Channel 13 Active Power | P_013_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_013_kW
124 | 3 | 3-31 | 8436 | Input Channel 13 Reactive Power | Q_013_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_013_kvar
125 | 3 | 3-32 | 8438 | Input Channel 13 Apparent Power | S_013_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_013_kVA
126 | 3 | 3-33 | 8440 | Input Channel 13 Load Nature | LC_013 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
127 | 3 | 3-34 | 8442 | Input Channel 13 Power Factor | PF_013 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_013
128 | 3 | 3-35 | 8444 | Input Channel 13 Current Phase Angle | ANG_I_013 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_013
129 | 3 | 3-36 | 8446 | Input Channel 14 Current | I_014_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_014_A
130 | 3 | 3-37 | 8448 | Input Channel 14 Active Power | P_014_kW | kW | float32 | 22 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_014_kW
131 | 3 | 3-38 | 8450 | Input Channel 14 Reactive Power | Q_014_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_014_kvar
132 | 3 | 3-39 | 8452 | Input Channel 14 Apparent Power | S_014_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_014_kVA
133 | 3 | 3-40 | 8454 | Input Channel 14 Load Nature | LC_014 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
134 | 3 | 3-41 | 8456 | Input Channel 14 Power Factor | PF_014 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_014
135 | 3 | 3-42 | 8458 | Input Channel 14 Current Phase Angle | ANG_I_014 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_014
136 | 3 | 3-43 | 8460 | Input Channel 15 Current | I_015_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_015_A
137 | 3 | 3-44 | 8462 | Input Channel 15 Active Power | P_015_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_015_kW
138 | 3 | 3-45 | 8464 | Input Channel 15 Reactive Power | Q_015_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_015_kvar
139 | 3 | 3-46 | 8466 | Input Channel 15 Apparent Power | S_015_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_015_kVA
140 | 3 | 3-47 | 8468 | Input Channel 15 Load Nature | LC_015 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
141 | 3 | 3-48 | 8470 | Input Channel 15 Power Factor | PF_015 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_015
142 | 3 | 3-49 | 8472 | Input Channel 15 Current Phase Angle | ANG_I_015 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_015
143 | 3 | 3-50 | 8474 | Input Channel 16 Current | I_016_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_016_A
144 | 3 | 3-51 | 8476 | Input Channel 16 Active Power | P_016_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_016_kW
145 | 3 | 3-52 | 8478 | Input Channel 16 Reactive Power | Q_016_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_016_kvar
146 | 3 | 3-53 | 8480 | Input Channel 16 Apparent Power | S_016_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_016_kVA
147 | 3 | 3-54 | 8482 | Input Channel 16 Load Nature | LC_016 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
148 | 3 | 3-55 | 8484 | Input Channel 16 Power Factor | PF_016 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_016
149 | 3 | 3-56 | 8486 | Input Channel 16 Current Phase Angle | ANG_I_016 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_016
150 | 4 | 4-1 | 8488 | Input Channel 17 Current | I_017_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_017_A
151 | 4 | 4-2 | 8490 | Input Channel 17 Active Power | P_017_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_017_kW
152 | 4 | 4-3 | 8492 | Input Channel 17 Reactive Power | Q_017_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_017_kvar
153 | 4 | 4-4 | 8494 | Input Channel 17 Apparent Power | S_017_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_017_kVA
154 | 4 | 4-5 | 8496 | Input Channel 17 Load Nature | LC_017 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
155 | 4 | 4-6 | 8498 | Input Channel 17 Power Factor | PF_017 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_017
156 | 4 | 4-7 | 8500 | Input Channel 17 Current Phase Angle | ANG_I_017 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_017
157 | 4 | 4-8 | 8502 | Input Channel 18 Current | I_018_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_018_A
158 | 4 | 4-9 | 8504 | Input Channel 18 Active Power | P_018_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_018_kW
159 | 4 | 4-10 | 8506 | Input Channel 18 Reactive Power | Q_018_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_018_kvar
160 | 4 | 4-11 | 8508 | Input Channel 18 Apparent Power | S_018_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_018_kVA
161 | 4 | 4-12 | 8510 | Input Channel 18 Load Nature | LC_018 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
162 | 4 | 4-13 | 8512 | Input Channel 18 Power Factor | PF_018 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_018
163 | 4 | 4-14 | 8514 | Input Channel 18 Current Phase Angle | ANG_I_018 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_018
164 | 4 | 4-15 | 8516 | Input Channel 19 Current | I_019_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_019_A
165 | 4 | 4-16 | 8518 | Input Channel 19 Active Power | P_019_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_019_kW
166 | 4 | 4-17 | 8520 | Input Channel 19 Reactive Power | Q_019_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_019_kvar
167 | 4 | 4-18 | 8522 | Input Channel 19 Apparent Power | S_019_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_019_kVA
168 | 4 | 4-19 | 8524 | Input Channel 19 Load Nature | LC_019 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
169 | 4 | 4-20 | 8526 | Input Channel 19 Power Factor | PF_019 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_019
170 | 4 | 4-21 | 8528 | Input Channel 19 Current Phase Angle | ANG_I_019 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_019
171 | 4 | 4-22 | 8530 | Input Channel 20 Current | I_020_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_020_A
172 | 4 | 4-23 | 8532 | Input Channel 20 Active Power | P_020_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_020_kW
173 | 4 | 4-24 | 8534 | Input Channel 20 Reactive Power | Q_020_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_020_kvar
174 | 4 | 4-25 | 8536 | Input Channel 20 Apparent Power | S_020_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_020_kVA
175 | 4 | 4-26 | 8538 | Input Channel 20 Load Nature | LC_020 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
176 | 4 | 4-27 | 8540 | Input Channel 20 Power Factor | PF_020 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_020
177 | 4 | 4-28 | 8542 | Input Channel 20 Current Phase Angle | ANG_I_020 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_020
178 | 4 | 4-29 | 8544 | Input Channel 21 Current | I_021_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_021_A
179 | 4 | 4-30 | 8546 | Input Channel 21 Active Power | P_021_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_021_kW
180 | 4 | 4-31 | 8548 | Input Channel 21 Reactive Power | Q_021_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_021_kvar
181 | 4 | 4-32 | 8550 | Input Channel 21 Apparent Power | S_021_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_021_kVA
182 | 4 | 4-33 | 8552 | Input Channel 21 Load Nature | LC_021 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
183 | 4 | 4-34 | 8554 | Input Channel 21 Power Factor | PF_021 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_021
184 | 4 | 4-35 | 8556 | Input Channel 21 Current Phase Angle | ANG_I_021 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_021
185 | 4 | 4-36 | 8558 | Input Channel 22 Current | I_022_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_022_A
186 | 4 | 4-37 | 8560 | Input Channel 22 Active Power | P_022_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_022_kW
187 | 4 | 4-38 | 8562 | Input Channel 22 Reactive Power | Q_022_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_022_kvar
188 | 4 | 4-39 | 8564 | Input Channel 22 Apparent Power | S_022_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_022_kVA
189 | 4 | 4-40 | 8566 | Input Channel 22 Load Nature | LC_022 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
190 | 4 | 4-41 | 8568 | Input Channel 22 Power Factor | PF_022 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_022
191 | 4 | 4-42 | 8570 | Input Channel 22 Current Phase Angle | ANG_I_022 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_022
192 | 4 | 4-43 | 8572 | Input Channel 23 Current | I_023_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_023_A
193 | 4 | 4-44 | 8574 | Input Channel 23 Active Power | P_023_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_023_kW
194 | 4 | 4-45 | 8576 | Input Channel 23 Reactive Power | Q_023_kvar | kvar | float32 | 22 | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_023_kvar
195 | 4 | 4-46 | 8578 | Input Channel 23 Apparent Power | S_023_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_023_kVA
196 | 4 | 4-47 | 8580 | Input Channel 23 Load Nature | LC_023 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
197 | 4 | 4-48 | 8582 | Input Channel 23 Power Factor | PF_023 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_023
198 | 4 | 4-49 | 8584 | Input Channel 23 Current Phase Angle | ANG_I_023 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_023
199 | 4 | 4-50 | 8586 | Input Channel 24 Current | I_024_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | I_024_A
200 | 4 | 4-51 | 8588 | Input Channel 24 Active Power | P_024_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1-35 |  | P_024_kW
201 | 4 | 4-52 | 8590 | Input Channel 24 Reactive Power | Q_024_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_024_kvar
202 | 4 | 4-53 | 8592 | Input Channel 24 Apparent Power | S_024_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_024_kVA
203 | 4 | 4-54 | 8594 | Input Channel 24 Load Nature | LC_024 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
204 | 4 | 4-55 | 8596 | Input Channel 24 Power Factor | PF_024 | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_024
205 | 4 | 4-56 | 8598 | Input Channel 24 Current Phase Angle | ANG_I_024 | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | ANG_I_024
206 | 5 | 5-1 | 8600 | User Channel 1 Current | I_s001_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s001_A | I_s001_%
207 | 5 | 5-2 | 8602 | User Channel 1 Active Power | P_s001_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s001_kW
208 | 5 | 5-3 | 8604 | User Channel 1 Reactive Power | Q_s001_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s001_kvar
209 | 5 | 5-4 | 8606 | User Channel 1 Apparent Power | S_s001_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s001_kVA
210 | 5 | 5-5 | 8608 | User Channel 1 Load Nature | LC_s001 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
211 | 5 | 5-6 | 8610 | User Channel 1 Power Factor | PF_s001 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | PF_s001
212 | 5 | 5-7 | 8612 | User Channel 2 Current | I_s002_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s002_A | I_s002_%
213 | 5 | 5-8 | 8614 | User Channel 2 Active Power | P_s002_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s002_kW
214 | 5 | 5-9 | 8616 | User Channel 2 Reactive Power | Q_s002_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s002_kvar
215 | 5 | 5-10 | 8618 | User Channel 2 Apparent Power | S_s002_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s002_kVA
216 | 5 | 5-11 | 8620 | User Channel 2 Load Nature | LC_s002 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
217 | 5 | 5-12 | 8622 | User Channel 2 Power Factor | PF_s002 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | PF_s002
218 | 5 | 5-13 | 8624 | User Channel 3 Current | I_s003_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s003_A | I_s003_%
219 | 5 | 5-14 | 8626 | User Channel 3 Active Power | P_s003_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s003_kW
220 | 5 | 5-15 | 8628 | User Channel 3 Reactive Power | Q_s003_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s003_kvar
221 | 5 | 5-16 | 8630 | User Channel 3 Apparent Power | S_s003_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s003_kVA
222 | 5 | 5-17 | 8632 | User Channel 3 Load Nature | LC_s003 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
223 | 5 | 5-18 | 8634 | User Channel 3 Power Factor | PF_s003 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | PF_s003
224 | 5 | 5-19 | 8636 | User Channel 4 Current | I_s004_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s004_A | I_s004_%
225 | 5 | 5-20 | 8638 | User Channel 4 Active Power | P_s004_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s004_kW
226 | 5 | 5-21 | 8640 | User Channel 4 Reactive Power | Q_s004_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s004_kvar
227 | 5 | 5-22 | 8642 | User Channel 4 Apparent Power | S_s004_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s004_kVA
228 | 5 | 5-23 | 8644 | User Channel 4 Load Nature | LC_s004 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
229 | 5 | 5-24 | 8646 | User Channel 4 Power Factor | PF_s004 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | PF_s004
230 | 5 | 5-25 | 8648 | User Channel 5 Current | I_s005_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s005_A | I_s005_%
231 | 5 | 5-26 | 8650 | User Channel 5 Active Power | P_s005_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s005_kW
232 | 5 | 5-27 | 8652 | User Channel 5 Reactive Power | Q_s005_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s005_kvar
233 | 5 | 5-28 | 8654 | User Channel 5 Apparent Power | S_s005_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s005_kVA
234 | 5 | 5-29 | 8656 | User Channel 5 Load Nature | LC_s005 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
235 | 5 | 5-30 | 8658 | User Channel 5 Power Factor | PF_s005 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | PF_s005
236 | 5 | 5-31 | 8660 | User Channel 6 Current | I_s006_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s006_A | I_s006_%
237 | 5 | 5-32 | 8662 | User Channel 6 Active Power | P_s006_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s006_kW
238 | 5 | 5-33 | 8664 | User Channel 6 Reactive Power | Q_s006_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s006_kvar
239 | 5 | 5-34 | 8666 | User Channel 6 Apparent Power | S_s006_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s006_kVA
240 | 5 | 5-35 | 8668 | User Channel 6 Load Nature | LC_s006 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
241 | 5 | 5-36 | 8670 | User Channel 6 Power Factor | PF_s006 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | PF_s006
242 | 6 | 6-1 | 8672 | User Channel 7 Current | I_s007_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s007_A | I_s007_%
243 | 6 | 6-2 | 8674 | User Channel 7 Active Power | P_s007_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s007_kW
244 | 6 | 6-3 | 8676 | User Channel 7 Reactive Power | Q_s007_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s007_kvar
245 | 6 | 6-4 | 8678 | User Channel 7 Apparent Power | S_s007_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s007_kVA
246 | 6 | 6-5 | 8680 | User Channel 7 Load Nature | LC_s007 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
247 | 6 | 6-6 | 8682 | User Channel 7 Power Factor | PF_s007 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | PF_s007
248 | 6 | 6-7 | 8684 | User Channel 8 Current | I_s008_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s008_A | I_s008_%
249 | 6 | 6-8 | 8686 | User Channel 8 Active Power | P_s008_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s008_kW
250 | 6 | 6-9 | 8688 | User Channel 8 Reactive Power | Q_s008_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s008_kvar
251 | 6 | 6-10 | 8690 | User Channel 8 Apparent Power | S_s008_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s008_kVA
252 | 6 | 6-11 | 8692 | User Channel 8 Load Nature | LC_s008 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
253 | 6 | 6-12 | 8694 | User Channel 8 Power Factor | PF_s008 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_s008
254 | 6 | 6-13 | 8696 | User Channel 9 Current | I_s009_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s009_A | I_s009_%
255 | 6 | 6-14 | 8698 | User Channel 9 Active Power | P_s009_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s009_kW
256 | 6 | 6-15 | 8700 | User Channel 9 Reactive Power | Q_s009_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s009_kvar
257 | 6 | 6-16 | 8702 | User Channel 9 Apparent Power | S_s009_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s009_kVA
258 | 6 | 6-17 | 8704 | User Channel 9 Load Nature | LC_s009 |  | uint32 | 6 | R | 2 | 1 |  |  |  |  | 10
259 | 6 | 6-18 | 8706 | User Channel 9 Power Factor | PF_s009 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | PF_s009
260 | 6 | 6-19 | 8708 | User Channel 10 Current | I_s010_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s010_A | I_s010_%
261 | 6 | 6-20 | 8710 | User Channel 10 Active Power | P_s010_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s010_kW
262 | 6 | 6-21 | 8712 | User Channel 10 Reactive Power | Q_s010_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s010_kvar
263 | 6 | 6-22 | 8714 | User Channel 10 Apparent Power | S_s010_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s010_kVA
264 | 6 | 6-23 | 8716 | User Channel 10 Load Nature | LC_s010 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
265 | 6 | 6-24 | 8718 | User Channel 10 Power Factor | PF_s010 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-35 |  | PF_s010
266 | 6 | 6-25 | 8720 | User Channel 11 Current | I_s011_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s011_A | I_s011_%
267 | 6 | 6-26 | 8722 | User Channel 11 Active Power | P_s011_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s011_kW
268 | 6 | 6-27 | 8724 | User Channel 11 Reactive Power | Q_s011_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s011_kvar
269 | 6 | 6-28 | 8726 | User Channel 11 Apparent Power | S_s011_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s011_kVA
270 | 6 | 6-29 | 8728 | User Channel 11 Load Nature | LC_s011 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
271 | 6 | 6-30 | 8730 | User Channel 11 Power Factor | PF_s011 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | PF_s011
272 | 6 | 6-31 | 8732 | User Channel 12 Current | I_s012_% | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 | I_s012_A | I_s012_%
273 | 6 | 6-32 | 8734 | User Channel 12 Active Power | P_s012_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | P_s012_kW
274 | 6 | 6-33 | 8736 | User Channel 12 Reactive Power | Q_s012_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | Q_s012_kvar
275 | 6 | 6-34 | 8738 | User Channel 12 Apparent Power | S_s012_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10-2-1 |  | S_s012_kVA
276 | 6 | 6-35 | 8740 | User Channel 12 Load Nature | LC_s012 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 10
277 | 6 | 6-36 | 8742 | User Channel 12 Power Factor | PF_s012 |  | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8 | 10 |  | PF_s012
278 | 7 | 7-1 | 8960 | Phase A Current Demand | DMD_I_a_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_I_a_A
279 | 7 | 7-2 | 8962 | Phase A Import Active Power Demand | DMD_IMP_P_a_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_IMP_P_a_kW
280 | 7 | 7-3 | 8964 | Phase A Export Active Power Demand | DMD_EXP_P_a_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_EXP_P_a_kW
281 | 7 | 7-4 | 8966 | Phase A Import Reactive Power Demand | DMD_IMP_Q_a_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_IMP_Q_a_kvar
282 | 7 | 7-5 | 8968 | Phase A Export Reactive Power Demand | DMD_EXP_Q_a_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_EXP_Q_a_kvar
283 | 7 | 7-6 | 8970 | Phase A Apparent Power Demand | DMD_S_a_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_S_a_kVA
284 | 7 | 7-7 | 8972 | Phase B Current Demand | DMD_I_b_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_I_b_A
285 | 7 | 7-8 | 8974 | Phase B Import Active Power Demand | DMD_IMP_P_b_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_IMP_P_b_kW
286 | 7 | 7-9 | 8976 | Phase B Export Active Power Demand | DMD_EXP_P_b_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_EXP_P_b_kW
287 | 7 | 7-10 | 8978 | Phase B Import Reactive Power Demand | DMD_IMP_Q_b_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_IMP_Q_b_kvar
288 | 7 | 7-11 | 8980 | Phase B Export Reactive Power Demand | DMD_EXP_Q_b_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_EXP_Q_b_kvar
289 | 7 | 7-12 | 8982 | Phase B Apparent Power Demand | DMD_S_b_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_S_b_kVA
290 | 7 | 7-13 | 8984 | Phase C Current Demand | DMD_I_c_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_I_c_A
291 | 7 | 7-14 | 8986 | Phase C Import Active Power Demand | DMD_IMP_P_c_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_IMP_P_c_kW
292 | 7 | 7-15 | 8988 | Phase C Export Active Power Demand | DMD_EXP_P_c_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_EXP_P_c_kW
293 | 7 | 7-16 | 8990 | Phase C Import Reactive Power Demand | DMD_IMP_Q_c_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_IMP_Q_c_kvar
294 | 7 | 7-17 | 8992 | Phase C Export Reactive Power Demand | DMD_EXP_Q_c_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_EXP_Q_c_kvar
295 | 7 | 7-18 | 8994 | Phase C Apparent Power Demand | DMD_S_c_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_S_c_kVA
296 | 7 | 7-19 | 8996 | System Average Current Demand | DMD_I_avg_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_I_avg_A
297 | 7 | 7-20 | 8998 | System Import Active Power Demand | DMD_IMP_P_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_IMP_P_kW
298 | 7 | 7-21 | 9000 | System Export Active Power Demand | DMD_EXP_P_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_EXP_P_kW
299 | 7 | 7-22 | 9002 | System Import Reactive Power Demand | DMD_IMP_Q_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_IMP_Q_kvar
300 | 7 | 7-23 | 9004 | System Export Reactive Power Demand | DMD_EXP_Q_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_EXP_Q_kvar
301 | 7 | 7-24 | 9006 | System Apparent Power Demand | DMD_S_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 15-2-1 |  | DMD_S_kVA
302 | 8 | 8-1 | 9008 | Input Channel 1 Current Demand | DMD_I_001_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_001_A
303 | 8 | 8-2 | 9010 | Input Channel 1 Import Active Power Demand | DMD_IMP_P_001_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_001_kW
304 | 8 | 8-3 | 9012 | Input Channel 1 Export Active Power Demand | DMD_EXP_P_001_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_001_kW
305 | 8 | 8-4 | 9014 | Input Channel 1 Import Reactive Power Demand | DMD_IMP_Q_001_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_001_kvar
306 | 8 | 8-5 | 9016 | Input Channel 1 Export Reactive Power Demand | DMD_EXP_Q_001_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_001_kvar
307 | 8 | 8-6 | 9018 | Input Channel 1 Apparent Power Demand | DMD_S_001_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_001_kVA
308 | 8 | 8-7 | 9020 | Input Channel 2 Current Demand | DMD_I_002_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_002_A
309 | 8 | 8-8 | 9022 | Input Channel 2 Import Active Power Demand | DMD_IMP_P_002_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_002_kW
310 | 8 | 8-9 | 9024 | Input Channel 2 Export Active Power Demand | DMD_EXP_P_002_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_002_kW
311 | 8 | 8-10 | 9026 | Input Channel 2 Import Reactive Power Demand | DMD_IMP_Q_002_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_002_kvar
312 | 8 | 8-11 | 9028 | Input Channel 2 Export Reactive Power Demand | DMD_EXP_Q_002_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_002_kvar
313 | 8 | 8-12 | 9030 | Input Channel 2 Apparent Power Demand | DMD_S_002_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_002_kVA
314 | 8 | 8-13 | 9032 | Input Channel 3 Current Demand | DMD_I_003_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_003_A
315 | 8 | 8-14 | 9034 | Input Channel 3 Import Active Power Demand | DMD_IMP_P_003_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_003_kW
316 | 8 | 8-15 | 9036 | Input Channel 3 Export Active Power Demand | DMD_EXP_P_003_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_003_kW
317 | 8 | 8-16 | 9038 | Input Channel 3 Import Reactive Power Demand | DMD_IMP_Q_003_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_003_kvar
318 | 8 | 8-17 | 9040 | Input Channel 3 Export Reactive Power Demand | DMD_EXP_Q_003_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_003_kvar
319 | 8 | 8-18 | 9042 | Input Channel 3 Apparent Power Demand | DMD_S_003_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_003_kVA
320 | 8 | 8-19 | 9044 | Input Channel 4 Current Demand | DMD_I_004_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_004_A
321 | 8 | 8-20 | 9046 | Input Channel 4 Import Active Power Demand | DMD_IMP_P_004_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_004_kW
322 | 8 | 8-21 | 9048 | Input Channel 4 Export Active Power Demand | DMD_EXP_P_004_kW | kW | float32 | 22 | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_004_kW
323 | 8 | 8-22 | 9050 | Input Channel 4 Import Reactive Power Demand | DMD_IMP_Q_004_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_004_kvar
324 | 8 | 8-23 | 9052 | Input Channel 4 Export Reactive Power Demand | DMD_EXP_Q_004_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_004_kvar
325 | 8 | 8-24 | 9054 | Input Channel 4 Apparent Power Demand | DMD_S_004_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_004_kVA
326 | 8 | 8-25 | 9056 | Input Channel 5 Current Demand | DMD_I_005_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_005_A
327 | 8 | 8-26 | 9058 | Input Channel 5 Import Active Power Demand | DMD_IMP_P_005_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_005_kW
328 | 8 | 8-27 | 9060 | Input Channel 5 Export Active Power Demand | DMD_EXP_P_005_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_005_kW
329 | 8 | 8-28 | 9062 | Input Channel 5 Import Reactive Power Demand | DMD_IMP_Q_005_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_005_kvar
330 | 8 | 8-29 | 9064 | Input Channel 5 Export Reactive Power Demand | DMD_EXP_Q_005_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_005_kvar
331 | 8 | 8-30 | 9066 | Input Channel 5 Apparent Power Demand | DMD_S_005_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_005_kVA
332 | 8 | 8-31 | 9068 | Input Channel 6 Current Demand | DMD_I_006_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_006_A
333 | 8 | 8-32 | 9070 | Input Channel 6 Import Active Power Demand | DMD_IMP_P_006_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_006_kW
334 | 8 | 8-33 | 9072 | Input Channel 6 Export Active Power Demand | DMD_EXP_P_006_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_006_kW
335 | 8 | 8-34 | 9074 | Input Channel 6 Import Reactive Power Demand | DMD_IMP_Q_006_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_006_kvar
336 | 8 | 8-35 | 9076 | Input Channel 6 Export Reactive Power Demand | DMD_EXP_Q_006_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_006_kvar
337 | 8 | 8-36 | 9078 | Input Channel 6 Apparent Power Demand | DMD_S_006_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_006_kVA
338 | 8 | 8-37 | 9080 | Input Channel 7 Current Demand | DMD_I_007_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_007_A
339 | 8 | 8-38 | 9082 | Input Channel 7 Import Active Power Demand | DMD_IMP_P_007_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_007_kW
340 | 8 | 8-39 | 9084 | Input Channel 7 Export Active Power Demand | DMD_EXP_P_007_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_007_kW
341 | 8 | 8-40 | 9086 | Input Channel 7 Import Reactive Power Demand | DMD_IMP_Q_007_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_007_kvar
342 | 8 | 8-41 | 9088 | Input Channel 7 Export Reactive Power Demand | DMD_EXP_Q_007_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_007_kvar
343 | 8 | 8-42 | 9090 | Input Channel 7 Apparent Power Demand | DMD_S_007_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_007_kVA
344 | 8 | 8-43 | 9092 | Input Channel 8 Current Demand | DMD_I_008_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_008_A
345 | 8 | 8-44 | 9094 | Input Channel 8 Import Active Power Demand | DMD_IMP_P_008_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_008_kW
346 | 8 | 8-45 | 9096 | Input Channel 8 Export Active Power Demand | DMD_EXP_P_008_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_008_kW
347 | 8 | 8-46 | 9098 | Input Channel 8 Import Reactive Power Demand | DMD_IMP_Q_008_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_008_kvar
348 | 8 | 8-47 | 9100 | Input Channel 8 Export Reactive Power Demand | DMD_EXP_Q_008_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_008_kvar
349 | 8 | 8-48 | 9102 | Input Channel 8 Apparent Power Demand | DMD_S_008_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_008_kVA
350 | 9 | 9-1 | 9104 | Input Channel 9 Current Demand | DMD_I_009_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_009_A
351 | 9 | 9-2 | 9106 | Input Channel 9 Import Active Power Demand | DMD_IMP_P_009_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_009_kW
352 | 9 | 9-3 | 9108 | Input Channel 9 Export Active Power Demand | DMD_EXP_P_009_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_009_kW
353 | 9 | 9-4 | 9110 | Input Channel 9 Import Reactive Power Demand | DMD_IMP_Q_009_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_009_kvar
354 | 9 | 9-5 | 9112 | Input Channel 9 Export Reactive Power Demand | DMD_EXP_Q_009_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_009_kvar
355 | 9 | 9-6 | 9114 | Input Channel 9 Apparent Power Demand | DMD_S_009_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_009_kVA
356 | 9 | 9-7 | 9116 | Input Channel 10 Current Demand | DMD_I_010_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_010_A
357 | 9 | 9-8 | 9118 | Input Channel 10 Import Active Power Demand | DMD_IMP_P_010_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_010_kW
358 | 9 | 9-9 | 9120 | Input Channel 10 Export Active Power Demand | DMD_EXP_P_010_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_010_kW
359 | 9 | 9-10 | 9122 | Input Channel 10 Import Reactive Power Demand | DMD_IMP_Q_010_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_010_kvar
360 | 9 | 9-11 | 9124 | Input Channel 10 Export Reactive Power Demand | DMD_EXP_Q_010_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_010_kvar
361 | 9 | 9-12 | 9126 | Input Channel 10 Apparent Power Demand | DMD_S_010_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_010_kVA
362 | 9 | 9-13 | 9128 | Input Channel 11 Current Demand | DMD_I_011_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_011_A
363 | 9 | 9-14 | 9130 | Input Channel 11 Import Active Power Demand | DMD_IMP_P_011_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_011_kW
364 | 9 | 9-15 | 9132 | Input Channel 11 Export Active Power Demand | DMD_EXP_P_011_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_011_kW
365 | 9 | 9-16 | 9134 | Input Channel 11 Import Reactive Power Demand | DMD_IMP_Q_011_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_011_kvar
366 | 9 | 9-17 | 9136 | Input Channel 11 Export Reactive Power Demand | DMD_EXP_Q_011_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_011_kvar
367 | 9 | 9-18 | 9138 | Input Channel 11 Apparent Power Demand | DMD_S_011_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_011_kVA
368 | 9 | 9-19 | 9140 | Input Channel 12 Current Demand | DMD_I_012_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_012_A
369 | 9 | 9-20 | 9142 | Input Channel 12 Import Active Power Demand | DMD_IMP_P_012_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_012_kW
370 | 9 | 9-21 | 9144 | Input Channel 12 Export Active Power Demand | DMD_EXP_P_012_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_012_kW
371 | 9 | 9-22 | 9146 | Input Channel 12 Import Reactive Power Demand | DMD_IMP_Q_012_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_012_kvar
372 | 9 | 9-23 | 9148 | Input Channel 12 Export Reactive Power Demand | DMD_EXP_Q_012_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_012_kvar
373 | 9 | 9-24 | 9150 | Input Channel 12 Apparent Power Demand | DMD_S_012_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_012_kVA
374 | 9 | 9-25 | 9152 | Input Channel 13 Current Demand | DMD_I_013_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_013_A
375 | 9 | 9-26 | 9154 | Input Channel 13 Import Active Power Demand | DMD_IMP_P_013_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_013_kW
376 | 9 | 9-27 | 9156 | Input Channel 13 Export Active Power Demand | DMD_EXP_P_013_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_013_kW
377 | 9 | 9-28 | 9158 | Input Channel 13 Import Reactive Power Demand | DMD_IMP_Q_013_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_013_kvar
378 | 9 | 9-29 | 9160 | Input Channel 13 Export Reactive Power Demand | DMD_EXP_Q_013_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_013_kvar
379 | 9 | 9-30 | 9162 | Input Channel 13 Apparent Power Demand | DMD_S_013_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_013_kVA
380 | 9 | 9-31 | 9164 | Input Channel 14 Current Demand | DMD_I_014_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_014_A
381 | 9 | 9-32 | 9166 | Input Channel 14 Import Active Power Demand | DMD_IMP_P_014_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_014_kW
382 | 9 | 9-33 | 9168 | Input Channel 14 Export Active Power Demand | DMD_EXP_P_014_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_014_kW
383 | 9 | 9-34 | 9170 | Input Channel 14 Import Reactive Power Demand | DMD_IMP_Q_014_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_014_kvar
384 | 9 | 9-35 | 9172 | Input Channel 14 Export Reactive Power Demand | DMD_EXP_Q_014_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_014_kvar
385 | 9 | 9-36 | 9174 | Input Channel 14 Apparent Power Demand | DMD_S_014_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_014_kVA
386 | 9 | 9-37 | 9176 | Input Channel 15 Current Demand | DMD_I_015_A | A | float32 | 22 | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_015_A
387 | 9 | 9-38 | 9178 | Input Channel 15 Import Active Power Demand | DMD_IMP_P_015_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_015_kW
388 | 9 | 9-39 | 9180 | Input Channel 15 Export Active Power Demand | DMD_EXP_P_015_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_015_kW
389 | 9 | 9-40 | 9182 | Input Channel 15 Import Reactive Power Demand | DMD_IMP_Q_015_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_015_kvar
390 | 9 | 9-41 | 9184 | Input Channel 15 Export Reactive Power Demand | DMD_EXP_Q_015_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_015_kvar
391 | 9 | 9-42 | 9186 | Input Channel 15 Apparent Power Demand | DMD_S_015_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_015_kVA
392 | 9 | 9-43 | 9188 | Input Channel 16 Current Demand | DMD_I_016_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_016_A
393 | 9 | 9-44 | 9190 | Input Channel 16 Import Active Power Demand | DMD_IMP_P_016_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_016_kW
394 | 9 | 9-45 | 9192 | Input Channel 16 Export Active Power Demand | DMD_EXP_P_016_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_016_kW
395 | 9 | 9-46 | 9194 | Input Channel 16 Import Reactive Power Demand | DMD_IMP_Q_016_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_016_kvar
396 | 9 | 9-47 | 9196 | Input Channel 16 Export Reactive Power Demand | DMD_EXP_Q_016_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_016_kvar
397 | 9 | 9-48 | 9198 | Input Channel 16 Apparent Power Demand | DMD_S_016_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_016_kVA
398 | 10 | 10-1 | 9200 | Input Channel 17 Current Demand | DMD_I_017_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_017_A
399 | 10 | 10-2 | 9202 | Input Channel 17 Import Active Power Demand | DMD_IMP_P_017_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_017_kW
400 | 10 | 10-3 | 9204 | Input Channel 17 Export Active Power Demand | DMD_EXP_P_017_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_017_kW
401 | 10 | 10-4 | 9206 | Input Channel 17 Import Reactive Power Demand | DMD_IMP_Q_017_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_017_kvar
402 | 10 | 10-5 | 9208 | Input Channel 17 Export Reactive Power Demand | DMD_EXP_Q_017_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_017_kvar
403 | 10 | 10-6 | 9210 | Input Channel 17 Apparent Power Demand | DMD_S_017_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_017_kVA
404 | 10 | 10-7 | 9212 | Input Channel 18 Current Demand | DMD_I_018_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_018_A
405 | 10 | 10-8 | 9214 | Input Channel 18 Import Active Power Demand | DMD_IMP_P_018_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_018_kW
406 | 10 | 10-9 | 9216 | Input Channel 18 Export Active Power Demand | DMD_EXP_P_018_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_018_kW
407 | 10 | 10-10 | 9218 | Input Channel 18 Import Reactive Power Demand | DMD_IMP_Q_018_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_018_kvar
408 | 10 | 10-11 | 9220 | Input Channel 18 Export Reactive Power Demand | DMD_EXP_Q_018_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_018_kvar
409 | 10 | 10-12 | 9222 | Input Channel 18 Apparent Power Demand | DMD_S_018_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_018_kVA
410 | 10 | 10-13 | 9224 | Input Channel 19 Current Demand | DMD_I_019_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_019_A
411 | 10 | 10-14 | 9226 | Input Channel 19 Import Active Power Demand | DMD_IMP_P_019_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_019_kW
412 | 10 | 10-15 | 9228 | Input Channel 19 Export Active Power Demand | DMD_EXP_P_019_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_019_kW
413 | 10 | 10-16 | 9230 | Input Channel 19 Import Reactive Power Demand | DMD_IMP_Q_019_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_019_kvar
414 | 10 | 10-17 | 9232 | Input Channel 19 Export Reactive Power Demand | DMD_EXP_Q_019_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_019_kvar
415 | 10 | 10-18 | 9234 | Input Channel 19 Apparent Power Demand | DMD_S_019_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_019_kVA
416 | 10 | 10-19 | 9236 | Input Channel 20 Current Demand | DMD_I_020_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_020_A
417 | 10 | 10-20 | 9238 | Input Channel 20 Import Active Power Demand | DMD_IMP_P_020_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_020_kW
418 | 10 | 10-21 | 9240 | Input Channel 20 Export Active Power Demand | DMD_EXP_P_020_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_020_kW
419 | 10 | 10-22 | 9242 | Input Channel 20 Import Reactive Power Demand | DMD_IMP_Q_020_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_020_kvar
420 | 10 | 10-23 | 9244 | Input Channel 20 Export Reactive Power Demand | DMD_EXP_Q_020_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_020_kvar
421 | 10 | 10-24 | 9246 | Input Channel 20 Apparent Power Demand | DMD_S_020_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_020_kVA
422 | 10 | 10-25 | 9248 | Input Channel 21 Current Demand | DMD_I_021_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_021_A
423 | 10 | 10-26 | 9250 | Input Channel 21 Import Active Power Demand | DMD_IMP_P_021_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_021_kW
424 | 10 | 10-27 | 9252 | Input Channel 21 Export Active Power Demand | DMD_EXP_P_021_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_021_kW
425 | 10 | 10-28 | 9254 | Input Channel 21 Import Reactive Power Demand | DMD_IMP_Q_021_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_021_kvar
426 | 10 | 10-29 | 9256 | Input Channel 21 Export Reactive Power Demand | DMD_EXP_Q_021_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_021_kvar
427 | 10 | 10-30 | 9258 | Input Channel 21 Apparent Power Demand | DMD_S_021_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_021_kVA
428 | 10 | 10-31 | 9260 | Input Channel 22 Current Demand | DMD_I_022_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_022_A
429 | 10 | 10-32 | 9262 | Input Channel 22 Import Active Power Demand | DMD_IMP_P_022_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_022_kW
430 | 10 | 10-33 | 9264 | Input Channel 22 Export Active Power Demand | DMD_EXP_P_022_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_022_kW
431 | 10 | 10-34 | 9266 | Input Channel 22 Import Reactive Power Demand | DMD_IMP_Q_022_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_022_kvar
432 | 10 | 10-35 | 9268 | Input Channel 22 Export Reactive Power Demand | DMD_EXP_Q_022_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_022_kvar
433 | 10 | 10-36 | 9270 | Input Channel 22 Apparent Power Demand | DMD_S_022_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_022_kVA
434 | 10 | 10-37 | 9272 | Input Channel 23 Current Demand | DMD_I_023_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_023_A
435 | 10 | 10-38 | 9274 | Input Channel 23 Import Active Power Demand | DMD_IMP_P_023_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_023_kW
436 | 10 | 10-39 | 9276 | Input Channel 23 Export Active Power Demand | DMD_EXP_P_023_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_023_kW
437 | 10 | 10-40 | 9278 | Input Channel 23 Import Reactive Power Demand | DMD_IMP_Q_023_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_023_kvar
438 | 10 | 10-41 | 9280 | Input Channel 23 Export Reactive Power Demand | DMD_EXP_Q_023_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_023_kvar
439 | 10 | 10-42 | 9282 | Input Channel 23 Apparent Power Demand | DMD_S_023_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_023_kVA
440 | 10 | 10-43 | 9284 | Input Channel 24 Current Demand | DMD_I_024_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_024_A
441 | 10 | 10-44 | 9286 | Input Channel 24 Import Active Power Demand | DMD_IMP_P_024_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_024_kW
442 | 10 | 10-45 | 9288 | Input Channel 24 Export Active Power Demand | DMD_EXP_P_024_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_024_kW
443 | 10 | 10-46 | 9290 | Input Channel 24 Import Reactive Power Demand | DMD_IMP_Q_024_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_024_kvar
444 | 10 | 10-47 | 9292 | Input Channel 24 Export Reactive Power Demand | DMD_EXP_Q_024_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_024_kvar
445 | 10 | 10-48 | 9294 | Input Channel 24 Apparent Power Demand | DMD_S_024_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_024_kVA
446 | 11 | 11-1 | 9296 | User Channel 1 Current Demand | DMD_I_s001_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s001_A
447 | 11 | 11-2 | 9298 | User Channel 1 Import Active Power Demand | DMD_IMP_P_s001_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s001_kW
448 | 11 | 11-3 | 9300 | User Channel 1 Export Active Power Demand | DMD_EXP_P_s001_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s001_kW
449 | 11 | 11-4 | 9302 | User Channel 1 Import Reactive Power Demand | DMD_IMP_Q_s001_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s001_kvar
450 | 11 | 11-5 | 9304 | User Channel 1 Export Reactive Power Demand | DMD_EXP_Q_s001_kvar | kvar | float32 | 22 | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s001_kvar
451 | 11 | 11-6 | 9306 | User Channel 1 Apparent Power Demand | DMD_S_s001_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s001_kVA
452 | 11 | 11-7 | 9308 | User Channel 2 Current Demand | DMD_I_s002_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s002_A
453 | 11 | 11-8 | 9310 | User Channel 2 Import Active Power Demand | DMD_IMP_P_s002_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s002_kW
454 | 11 | 11-9 | 9312 | User Channel 2 Export Active Power Demand | DMD_EXP_P_s002_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s002_kW
455 | 11 | 11-10 | 9314 | User Channel 2 Import Reactive Power Demand | DMD_IMP_Q_s002_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s002_kvar
456 | 11 | 11-11 | 9316 | User Channel 2 Export Reactive Power Demand | DMD_EXP_Q_s002_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s002_kvar
457 | 11 | 11-12 | 9318 | User Channel 2 Apparent Power Demand | DMD_S_s002_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s002_kVA
458 | 11 | 11-13 | 9320 | User Channel 3 Current Demand | DMD_I_s003_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s003_A
459 | 11 | 11-14 | 9322 | User Channel 3 Import Active Power Demand | DMD_IMP_P_s003_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s003_kW
460 | 11 | 11-15 | 9324 | User Channel 3 Export Active Power Demand | DMD_EXP_P_s003_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s003_kW
461 | 11 | 11-16 | 9326 | User Channel 3 Import Reactive Power Demand | DMD_IMP_Q_s003_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s003_kvar
462 | 11 | 11-17 | 9328 | User Channel 3 Export Reactive Power Demand | DMD_EXP_Q_s003_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s003_kvar
463 | 11 | 11-18 | 9330 | User Channel 3 Apparent Power Demand | DMD_S_s003_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s003_kVA
464 | 11 | 11-19 | 9332 | User Channel 4 Current Demand | DMD_I_s004_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s004_A
465 | 11 | 11-20 | 9334 | User Channel 4 Import Active Power Demand | DMD_IMP_P_s004_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s004_kW
466 | 11 | 11-21 | 9336 | User Channel 4 Export Active Power Demand | DMD_EXP_P_s004_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s004_kW
467 | 11 | 11-22 | 9338 | User Channel 4 Import Reactive Power Demand | DMD_IMP_Q_s004_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s004_kvar
468 | 11 | 11-23 | 9340 | User Channel 4 Export Reactive Power Demand | DMD_EXP_Q_s004_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s004_kvar
469 | 11 | 11-24 | 9342 | User Channel 4 Apparent Power Demand | DMD_S_s004_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s004_kVA
470 | 11 | 11-25 | 9344 | User Channel 5 Current Demand | DMD_I_s005_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s005_A
471 | 11 | 11-26 | 9346 | User Channel 5 Import Active Power Demand | DMD_IMP_P_s005_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s005_kW
472 | 11 | 11-27 | 9348 | User Channel 5 Export Active Power Demand | DMD_EXP_P_s005_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s005_kW
473 | 11 | 11-28 | 9350 | User Channel 5 Import Reactive Power Demand | DMD_IMP_Q_s005_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s005_kvar
474 | 11 | 11-29 | 9352 | User Channel 5 Export Reactive Power Demand | DMD_EXP_Q_s005_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s005_kvar
475 | 11 | 11-30 | 9354 | User Channel 5 Apparent Power Demand | DMD_S_s005_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s005_kVA
476 | 11 | 11-31 | 9356 | User Channel 6 Current Demand | DMD_I_s006_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s006_A
477 | 11 | 11-32 | 9358 | User Channel 6 Import Active Power Demand | DMD_IMP_P_s006_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s006_kW
478 | 11 | 11-33 | 9360 | User Channel 6 Export Active Power Demand | DMD_EXP_P_s006_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s006_kW
479 | 11 | 11-34 | 9362 | User Channel 6 Import Reactive Power Demand | DMD_IMP_Q_s006_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s006_kvar
480 | 11 | 11-35 | 9364 | User Channel 6 Export Reactive Power Demand | DMD_EXP_Q_s006_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s006_kvar
481 | 11 | 11-36 | 9366 | User Channel 6 Apparent Power Demand | DMD_S_s006_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s006_kVA
482 | 12 | 12-1 | 9368 | User Channel 7 Current Demand | DMD_I_s007_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s007_A
483 | 12 | 12-2 | 9370 | User Channel 7 Import Active Power Demand | DMD_IMP_P_s007_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s007_kW
484 | 12 | 12-3 | 9372 | User Channel 7 Export Active Power Demand | DMD_EXP_P_s007_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s007_kW
485 | 12 | 12-4 | 9374 | User Channel 7 Import Reactive Power Demand | DMD_IMP_Q_s007_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s007_kvar
486 | 12 | 12-5 | 9376 | User Channel 7 Export Reactive Power Demand | DMD_EXP_Q_s007_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s007_kvar
487 | 12 | 12-6 | 9378 | User Channel 7 Apparent Power Demand | DMD_S_s007_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s007_kVA
488 | 12 | 12-7 | 9380 | User Channel 8 Current Demand | DMD_I_s008_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s008_A
489 | 12 | 12-8 | 9382 | User Channel 8 Import Active Power Demand | DMD_IMP_P_s008_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s008_kW
490 | 12 | 12-9 | 9384 | User Channel 8 Export Active Power Demand | DMD_EXP_P_s008_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s008_kW
491 | 12 | 12-10 | 9386 | User Channel 8 Import Reactive Power Demand | DMD_IMP_Q_s008_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s008_kvar
492 | 12 | 12-11 | 9388 | User Channel 8 Export Reactive Power Demand | DMD_EXP_Q_s008_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s008_kvar
493 | 12 | 12-12 | 9390 | User Channel 8 Apparent Power Demand | DMD_S_s008_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s008_kVA
494 | 12 | 12-13 | 9392 | User Channel 9 Current Demand | DMD_I_s009_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s009_A
495 | 12 | 12-14 | 9394 | User Channel 9 Import Active Power Demand | DMD_IMP_P_s009_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s009_kW
496 | 12 | 12-15 | 9396 | User Channel 9 Export Active Power Demand | DMD_EXP_P_s009_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s009_kW
497 | 12 | 12-16 | 9398 | User Channel 9 Import Reactive Power Demand | DMD_IMP_Q_s009_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s009_kvar
498 | 12 | 12-17 | 9400 | User Channel 9 Export Reactive Power Demand | DMD_EXP_Q_s009_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s009_kvar
499 | 12 | 12-18 | 9402 | User Channel 9 Apparent Power Demand | DMD_S_s009_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s009_kVA
500 | 12 | 12-19 | 9404 | User Channel 10 Current Demand | DMD_I_s010_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s010_A
501 | 12 | 12-20 | 9406 | User Channel 10 Import Active Power Demand | DMD_IMP_P_s010_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s010_kW
502 | 12 | 12-21 | 9408 | User Channel 10 Export Active Power Demand | DMD_EXP_P_s010_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s010_kW
503 | 12 | 12-22 | 9410 | User Channel 10 Import Reactive Power Demand | DMD_IMP_Q_s010_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s010_kvar
504 | 12 | 12-23 | 9412 | User Channel 10 Export Reactive Power Demand | DMD_EXP_Q_s010_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s010_kvar
505 | 12 | 12-24 | 9414 | User Channel 10 Apparent Power Demand | DMD_S_s010_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s010_kVA
506 | 12 | 12-25 | 9416 | User Channel 11 Current Demand | DMD_I_s011_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s011_A
507 | 12 | 12-26 | 9418 | User Channel 11 Import Active Power Demand | DMD_IMP_P_s011_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s011_kW
508 | 12 | 12-27 | 9420 | User Channel 11 Export Active Power Demand | DMD_EXP_P_s011_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s011_kW
509 | 12 | 12-28 | 9422 | User Channel 11 Import Reactive Power Demand | DMD_IMP_Q_s011_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s011_kvar
510 | 12 | 12-29 | 9424 | User Channel 11 Export Reactive Power Demand | DMD_EXP_Q_s011_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s011_kvar
511 | 12 | 12-30 | 9426 | User Channel 11 Apparent Power Demand | DMD_S_s011_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s011_kVA
512 | 12 | 12-31 | 9428 | User Channel 12 Current Demand | DMD_I_s012_A | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_I_s012_A
513 | 12 | 12-32 | 9430 | User Channel 12 Import Active Power Demand | DMD_IMP_P_s012_kW | kW | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_P_s012_kW
514 | 12 | 12-33 | 9432 | User Channel 12 Export Active Power Demand | DMD_EXP_P_s012_kW | kW | float32 | 22 | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_P_s012_kW
515 | 12 | 12-34 | 9434 | User Channel 12 Import Reactive Power Demand | DMD_IMP_Q_s012_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_IMP_Q_s012_kvar
516 | 12 | 12-35 | 9436 | User Channel 12 Export Reactive Power Demand | DMD_EXP_Q_s012_kvar | kvar | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_EXP_Q_s012_kvar
517 | 12 | 12-36 | 9438 | User Channel 12 Apparent Power Demand | DMD_S_s012_kVA | kVA | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-41 | 16-2-1 |  | DMD_S_s012_kVA
518 | 13 | 13-1 | 9728 | Voltage Positive Sequence Magnitude | MAG_SEQ_POS_V | V | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13-36 |  | MAG_SEQ_POS_V
519 | 13 | 13-2 | 9730 | Voltage Zero Sequence Magnitude | MAG_SEQ_ZERO_V | V | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13-36 |  | MAG_SEQ_ZERO_V
520 | 13 | 13-3 | 9732 | Voltage Negative Sequence Magnitude | MAG_SEQ_NEG_V | V | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13-36 |  | MAG_SEQ_NEG_V
521 | 13 | 13-4 | 9734 | Voltage Positive Sequence Angle | ANG_SEQ_POS_V | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13-36 |  | ANG_SEQ_POS_V
522 | 13 | 13-5 | 9736 | Voltage Zero Sequence Angle | ANG_SEQ_ZERO_V | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13-36 |  | ANG_SEQ_ZERO_V
523 | 13 | 13-6 | 9738 | Voltage Negative Sequence Angle | ANG_SEQ_NEG_V | ° | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13-36 |  | ANG_SEQ_NEG_V
524 | 13 | 13-7 | 9740 | Voltage Unbalance Factor Magnitude | UNBL_V_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13-36-38 |  | UNBL_V_%
525 | 13 | 13-8 | 9742 | Phase A Voltage THD | THD_V_a_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | THD_V_a_%
526 | 13 | 13-9 | 9744 | Phase A Voltage THD Odd | OTHD_V_a_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | OTHD_V_a_%
527 | 13 | 13-10 | 9746 | Phase A Voltage THD Even | ETHD_V_a_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | ETHD_V_a_%
528 | 13 | 13-11 | 9748 | Phase A Voltage Crest Factor | CF_V_a_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | CF_V_a_%
529 | 13 | 13-12 | 9750 | Phase A Voltage THFF Factor | THFF_V_a_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | THFF_V_a_%
530 | 13 | 13-13 | 9752 | Phase A Voltage individual Harmonics 2 percentage | HAR2_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
531 | 13 | 13-14 | 9754 | Phase A Voltage individual Harmonics 3 percentage | HAR3_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
532 | 13 | 13-15 | 9756 | Phase A Voltage individual Harmonics 4 percentage | HAR4_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
533 | 13 | 13-16 | 9758 | Phase A Voltage individual Harmonics 5 percentage | HAR5_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
534 | 13 | 13-17 | 9760 | Phase A Voltage individual Harmonics 6 percentage | HAR6_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
535 | 13 | 13-18 | 9762 | Phase A Voltage individual Harmonics 7 percentage | HAR7_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
536 | 13 | 13-19 | 9764 | Phase A Voltage individual Harmonics 8 percentage | HAR8_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
537 | 13 | 13-20 | 9766 | Phase A Voltage individual Harmonics 9 percentage | HAR9_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
538 | 13 | 13-21 | 9768 | Phase A Voltage individual Harmonics 10 percentage | HAR10_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
539 | 13 | 13-22 | 9770 | Phase A Voltage individual Harmonics 11 percentage | HAR11_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
540 | 13 | 13-23 | 9772 | Phase A Voltage individual Harmonics 12 percentage | HAR12_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
541 | 13 | 13-24 | 9774 | Phase A Voltage individual Harmonics 13 percentage | HAR13_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
542 | 13 | 13-25 | 9776 | Phase A Voltage individual Harmonics 14 percentage | HAR14_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
543 | 13 | 13-26 | 9778 | Phase A Voltage individual Harmonics 15 percentage | HAR15_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
544 | 13 | 13-27 | 9780 | Phase A Voltage individual Harmonics 16 percentage | HAR16_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
545 | 13 | 13-28 | 9782 | Phase A Voltage individual Harmonics 17 percentage | HAR17_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
546 | 13 | 13-29 | 9784 | Phase A Voltage individual Harmonics 18 percentage | HAR18_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
547 | 13 | 13-30 | 9786 | Phase A Voltage individual Harmonics 19 percentage | HAR19_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
548 | 13 | 13-31 | 9788 | Phase A Voltage individual Harmonics 20 percentage | HAR20_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
549 | 13 | 13-32 | 9790 | Phase A Voltage individual Harmonics 21 percentage | HAR21_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
550 | 13 | 13-33 | 9792 | Phase A Voltage individual Harmonics 22 percentage | HAR22_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
551 | 13 | 13-34 | 9794 | Phase A Voltage individual Harmonics 23 percentage | HAR23_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
552 | 13 | 13-35 | 9796 | Phase A Voltage individual Harmonics 24 percentage | HAR24_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
553 | 13 | 13-36 | 9798 | Phase A Voltage individual Harmonics 25 percentage | HAR25_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
554 | 13 | 13-37 | 9800 | Phase A Voltage individual Harmonics 26 percentage | HAR26_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
555 | 13 | 13-38 | 9802 | Phase A Voltage individual Harmonics 27 percentage | HAR27_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
556 | 13 | 13-39 | 9804 | Phase A Voltage individual Harmonics 28 percentage | HAR28_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
557 | 13 | 13-40 | 9806 | Phase A Voltage individual Harmonics 29 percentage | HAR29_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
558 | 13 | 13-41 | 9808 | Phase A Voltage individual Harmonics 30 percentage | HAR30_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
559 | 13 | 13-42 | 9810 | Phase A Voltage individual Harmonics 31 percentage | HAR31_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
560 | 14 | 14-1 | 9812 | Phase B Voltage THD | THD_V_b_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | THD_V_b_%
561 | 14 | 14-2 | 9814 | Phase B Voltage THD Odd | OTHD_V_b_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | OTHD_V_b_%
562 | 14 | 14-3 | 9816 | Phase B Voltage THD Even | ETHD_V_b_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | ETHD_V_b_%
563 | 14 | 14-4 | 9818 | Phase B Voltage Crest Factor | CF_V_b_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | CF_V_b_%
564 | 14 | 14-5 | 9820 | Phase B Voltage THFF Factor | THFF_V_b_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | THFF_V_b_%
565 | 14 | 14-6 | 9822 | Phase B Voltage individual Harmonics 2 percentage | HAR2_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
566 | 14 | 14-7 | 9824 | Phase B Voltage individual Harmonics 3 percentage | HAR3_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
567 | 14 | 14-8 | 9826 | Phase B Voltage individual Harmonics 4 percentage | HAR4_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
568 | 14 | 14-9 | 9828 | Phase B Voltage individual Harmonics 5 percentage | HAR5_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
569 | 14 | 14-10 | 9830 | Phase B Voltage individual Harmonics 6 percentage | HAR6_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
570 | 14 | 14-11 | 9832 | Phase B Voltage individual Harmonics 7 percentage | HAR7_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
571 | 14 | 14-12 | 9834 | Phase B Voltage individual Harmonics 8 percentage | HAR8_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
572 | 14 | 14-13 | 9836 | Phase B Voltage individual Harmonics 9 percentage | HAR9_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
573 | 14 | 14-14 | 9838 | Phase B Voltage individual Harmonics 10 percentage | HAR10_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
574 | 14 | 14-15 | 9840 | Phase B Voltage individual Harmonics 11 percentage | HAR11_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
575 | 14 | 14-16 | 9842 | Phase B Voltage individual Harmonics 12 percentage | HAR12_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
576 | 14 | 14-17 | 9844 | Phase B Voltage individual Harmonics 13 percentage | HAR13_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
577 | 14 | 14-18 | 9846 | Phase B Voltage individual Harmonics 14 percentage | HAR14_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
578 | 14 | 14-19 | 9848 | Phase B Voltage individual Harmonics 15 percentage | HAR15_V_b_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 38
579 | 14 | 14-20 | 9850 | Phase B Voltage individual Harmonics 16 percentage | HAR16_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
580 | 14 | 14-21 | 9852 | Phase B Voltage individual Harmonics 17 percentage | HAR17_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
581 | 14 | 14-22 | 9854 | Phase B Voltage individual Harmonics 18 percentage | HAR18_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
582 | 14 | 14-23 | 9856 | Phase B Voltage individual Harmonics 19 percentage | HAR19_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
583 | 14 | 14-24 | 9858 | Phase B Voltage individual Harmonics 20 percentage | HAR20_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
584 | 14 | 14-25 | 9860 | Phase B Voltage individual Harmonics 21 percentage | HAR21_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
585 | 14 | 14-26 | 9862 | Phase B Voltage individual Harmonics 22 percentage | HAR22_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
586 | 14 | 14-27 | 9864 | Phase B Voltage individual Harmonics 23 percentage | HAR23_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
587 | 14 | 14-28 | 9866 | Phase B Voltage individual Harmonics 24 percentage | HAR24_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
588 | 14 | 14-29 | 9868 | Phase B Voltage individual Harmonics 25 percentage | HAR25_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
589 | 14 | 14-30 | 9870 | Phase B Voltage individual Harmonics 26 percentage | HAR26_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
590 | 14 | 14-31 | 9872 | Phase B Voltage individual Harmonics 27 percentage | HAR27_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
591 | 14 | 14-32 | 9874 | Phase B Voltage individual Harmonics 28 percentage | HAR28_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
592 | 14 | 14-33 | 9876 | Phase B Voltage individual Harmonics 29 percentage | HAR29_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
593 | 14 | 14-34 | 9878 | Phase B Voltage individual Harmonics 30 percentage | HAR30_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
594 | 14 | 14-35 | 9880 | Phase B Voltage individual Harmonics 31 percentage | HAR31_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
595 | 15 | 15-1 | 9882 | Phase C Voltage THD | THD_V_c_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | THD_V_c_%
596 | 15 | 15-2 | 9884 | Phase C Voltage THD Odd | OTHD_V_c_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | OTHD_V_c_%
597 | 15 | 15-3 | 9886 | Phase C Voltage THD Even | ETHD_V_c_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | ETHD_V_c_%
598 | 15 | 15-4 | 9888 | Phase C Voltage Crest Factor | CF_V_c_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | CF_V_c_%
599 | 15 | 15-5 | 9890 | Phase C Voltage THFF Factor | THFF_V_c_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | THFF_V_c_%
600 | 15 | 15-6 | 9892 | Phase C Voltage individual Harmonics 2 percentage | HAR2_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
601 | 15 | 15-7 | 9894 | Phase C Voltage individual Harmonics 3 percentage | HAR3_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
602 | 15 | 15-8 | 9896 | Phase C Voltage individual Harmonics 4 percentage | HAR4_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
603 | 15 | 15-9 | 9898 | Phase C Voltage individual Harmonics 5 percentage | HAR5_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
604 | 15 | 15-10 | 9900 | Phase C Voltage individual Harmonics 6 percentage | HAR6_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
605 | 15 | 15-11 | 9902 | Phase C Voltage individual Harmonics 7 percentage | HAR7_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
606 | 15 | 15-12 | 9904 | Phase C Voltage individual Harmonics 8 percentage | HAR8_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
607 | 15 | 15-13 | 9906 | Phase C Voltage individual Harmonics 9 percentage | HAR9_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
608 | 15 | 15-14 | 9908 | Phase C Voltage individual Harmonics 10 percentage | HAR10_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
609 | 15 | 15-15 | 9910 | Phase C Voltage individual Harmonics 11 percentage | HAR11_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
610 | 15 | 15-16 | 9912 | Phase C Voltage individual Harmonics 12 percentage | HAR12_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
611 | 15 | 15-17 | 9914 | Phase C Voltage individual Harmonics 13 percentage | HAR13_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
612 | 15 | 15-18 | 9916 | Phase C Voltage individual Harmonics 14 percentage | HAR14_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
613 | 15 | 15-19 | 9918 | Phase C Voltage individual Harmonics 15 percentage | HAR15_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
614 | 15 | 15-20 | 9920 | Phase C Voltage individual Harmonics 16 percentage | HAR16_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
615 | 15 | 15-21 | 9922 | Phase C Voltage individual Harmonics 17 percentage | HAR17_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
616 | 15 | 15-22 | 9924 | Phase C Voltage individual Harmonics 18 percentage | HAR18_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
617 | 15 | 15-23 | 9926 | Phase C Voltage individual Harmonics 19 percentage | HAR19_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
618 | 15 | 15-24 | 9928 | Phase C Voltage individual Harmonics 20 percentage | HAR20_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
619 | 15 | 15-25 | 9930 | Phase C Voltage individual Harmonics 21 percentage | HAR21_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
620 | 15 | 15-26 | 9932 | Phase C Voltage individual Harmonics 22 percentage | HAR22_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
621 | 15 | 15-27 | 9934 | Phase C Voltage individual Harmonics 23 percentage | HAR23_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
622 | 15 | 15-28 | 9936 | Phase C Voltage individual Harmonics 24 percentage | HAR24_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
623 | 15 | 15-29 | 9938 | Phase C Voltage individual Harmonics 25 percentage | HAR25_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
624 | 15 | 15-30 | 9940 | Phase C Voltage individual Harmonics 26 percentage | HAR26_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
625 | 15 | 15-31 | 9942 | Phase C Voltage individual Harmonics 27 percentage | HAR27_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
626 | 15 | 15-32 | 9944 | Phase C Voltage individual Harmonics 28 percentage | HAR28_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
627 | 15 | 15-33 | 9946 | Phase C Voltage individual Harmonics 29 percentage | HAR29_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
628 | 15 | 15-34 | 9948 | Phase C Voltage individual Harmonics 30 percentage | HAR30_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
629 | 15 | 15-35 | 9950 | Phase C Voltage individual Harmonics 31 percentage | HAR31_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 38
630 | 16 | 16-1 | 9952 | Average Voltage THD | THD_V_avg_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | THD_V_avg_%
631 | 16 | 16-2 | 9954 | Average Voltage THD Odd | OTHD_V_avg_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | OTHD_V_avg_%
632 | 16 | 16-3 | 9956 | Average Voltage THD Even | ETHD_V_avg_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 13 |  | ETHD_V_avg_%
633 | 16 | 16-4 | 9958 | Input Channel 1 Current THD | THD_I_001_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_001_%
634 | 16 | 16-5 | 9960 | Input Channel 1 Current THD Odd | OTHD_I_001_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_001_%
635 | 16 | 16-6 | 9962 | Input Channel 1 Current THD Even | ETHD_I_001_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_001_%
636 | 16 | 16-7 | 9964 | Input Channel 1 Current K Factor | KF_I_001_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_001_%
637 | 16 | 16-8 | 9966 | Input Channel 1 Current individual Harmonics 2 percentage | HAR2_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
638 | 16 | 16-9 | 9968 | Input Channel 1 Current individual Harmonics 3 percentage | HAR3_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
639 | 16 | 16-10 | 9970 | Input Channel 1 Current individual Harmonics 4 percentage | HAR4_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
640 | 16 | 16-11 | 9972 | Input Channel 1 Current individual Harmonics 5 percentage | HAR5_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
641 | 16 | 16-12 | 9974 | Input Channel 1 Current individual Harmonics 6 percentage | HAR6_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
642 | 16 | 16-13 | 9976 | Input Channel 1 Current individual Harmonics 7 percentage | HAR7_I_001_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 39
643 | 16 | 16-14 | 9978 | Input Channel 1 Current individual Harmonics 8 percentage | HAR8_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
644 | 16 | 16-15 | 9980 | Input Channel 1 Current individual Harmonics 9 percentage | HAR9_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
645 | 16 | 16-16 | 9982 | Input Channel 1 Current individual Harmonics 10 percentage | HAR10_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
646 | 16 | 16-17 | 9984 | Input Channel 1 Current individual Harmonics 11 percentage | HAR11_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
647 | 16 | 16-18 | 9986 | Input Channel 1 Current individual Harmonics 12 percentage | HAR12_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
648 | 16 | 16-19 | 9988 | Input Channel 1 Current individual Harmonics 13 percentage | HAR13_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
649 | 16 | 16-20 | 9990 | Input Channel 1 Current individual Harmonics 14 percentage | HAR14_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
650 | 16 | 16-21 | 9992 | Input Channel 1 Current individual Harmonics 15 percentage | HAR15_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
651 | 16 | 16-22 | 9994 | Input Channel 1 Current individual Harmonics 16 percentage | HAR16_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
652 | 16 | 16-23 | 9996 | Input Channel 1 Current individual Harmonics 17 percentage | HAR17_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
653 | 16 | 16-24 | 9998 | Input Channel 1 Current individual Harmonics 18 percentage | HAR18_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
654 | 16 | 16-25 | 10000 | Input Channel 1 Current individual Harmonics 19 percentage | HAR19_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
655 | 16 | 16-26 | 10002 | Input Channel 1 Current individual Harmonics 20 percentage | HAR20_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
656 | 16 | 16-27 | 10004 | Input Channel 1 Current individual Harmonics 21 percentage | HAR21_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
657 | 16 | 16-28 | 10006 | Input Channel 1 Current individual Harmonics 22 percentage | HAR22_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
658 | 16 | 16-29 | 10008 | Input Channel 1 Current individual Harmonics 23 percentage | HAR23_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
659 | 16 | 16-30 | 10010 | Input Channel 1 Current individual Harmonics 24 percentage | HAR24_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
660 | 16 | 16-31 | 10012 | Input Channel 1 Current individual Harmonics 25 percentage | HAR25_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
661 | 16 | 16-32 | 10014 | Input Channel 1 Current individual Harmonics 26 percentage | HAR26_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
662 | 16 | 16-33 | 10016 | Input Channel 1 Current individual Harmonics 27 percentage | HAR27_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
663 | 16 | 16-34 | 10018 | Input Channel 1 Current individual Harmonics 28 percentage | HAR28_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
664 | 16 | 16-35 | 10020 | Input Channel 1 Current individual Harmonics 29 percentage | HAR29_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
665 | 16 | 16-36 | 10022 | Input Channel 1 Current individual Harmonics 30 percentage | HAR30_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
666 | 16 | 16-37 | 10024 | Input Channel 1 Current individual Harmonics 31 percentage | HAR31_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
667 | 17 | 17-1 | 10026 | Input Channel 2 Current THD | THD_I_002_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_002_%
668 | 17 | 17-2 | 10028 | Input Channel 2 Current THD Odd | OTHD_I_002_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_002_%
669 | 17 | 17-3 | 10030 | Input Channel 2 Current THD Even | ETHD_I_002_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_002_%
670 | 17 | 17-4 | 10032 | Input Channel 2 Current K Factor | KF_I_002_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_002_%
671 | 17 | 17-5 | 10034 | Input Channel 2 Current individual Harmonics 2 percentage | HAR2_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
672 | 17 | 17-6 | 10036 | Input Channel 2 Current individual Harmonics 3 percentage | HAR3_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
673 | 17 | 17-7 | 10038 | Input Channel 2 Current individual Harmonics 4 percentage | HAR4_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
674 | 17 | 17-8 | 10040 | Input Channel 2 Current individual Harmonics 5 percentage | HAR5_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
675 | 17 | 17-9 | 10042 | Input Channel 2 Current individual Harmonics 6 percentage | HAR6_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
676 | 17 | 17-10 | 10044 | Input Channel 2 Current individual Harmonics 7 percentage | HAR7_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
677 | 17 | 17-11 | 10046 | Input Channel 2 Current individual Harmonics 8 percentage | HAR8_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
678 | 17 | 17-12 | 10048 | Input Channel 2 Current individual Harmonics 9 percentage | HAR9_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
679 | 17 | 17-13 | 10050 | Input Channel 2 Current individual Harmonics 10 percentage | HAR10_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
680 | 17 | 17-14 | 10052 | Input Channel 2 Current individual Harmonics 11 percentage | HAR11_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
681 | 17 | 17-15 | 10054 | Input Channel 2 Current individual Harmonics 12 percentage | HAR12_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
682 | 17 | 17-16 | 10056 | Input Channel 2 Current individual Harmonics 13 percentage | HAR13_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
683 | 17 | 17-17 | 10058 | Input Channel 2 Current individual Harmonics 14 percentage | HAR14_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
684 | 17 | 17-18 | 10060 | Input Channel 2 Current individual Harmonics 15 percentage | HAR15_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
685 | 17 | 17-19 | 10062 | Input Channel 2 Current individual Harmonics 16 percentage | HAR16_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
686 | 17 | 17-20 | 10064 | Input Channel 2 Current individual Harmonics 17 percentage | HAR17_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
687 | 17 | 17-21 | 10066 | Input Channel 2 Current individual Harmonics 18 percentage | HAR18_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
688 | 17 | 17-22 | 10068 | Input Channel 2 Current individual Harmonics 19 percentage | HAR19_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
689 | 17 | 17-23 | 10070 | Input Channel 2 Current individual Harmonics 20 percentage | HAR20_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
690 | 17 | 17-24 | 10072 | Input Channel 2 Current individual Harmonics 21 percentage | HAR21_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
691 | 17 | 17-25 | 10074 | Input Channel 2 Current individual Harmonics 22 percentage | HAR22_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
692 | 17 | 17-26 | 10076 | Input Channel 2 Current individual Harmonics 23 percentage | HAR23_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
693 | 17 | 17-27 | 10078 | Input Channel 2 Current individual Harmonics 24 percentage | HAR24_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
694 | 17 | 17-28 | 10080 | Input Channel 2 Current individual Harmonics 25 percentage | HAR25_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
695 | 17 | 17-29 | 10082 | Input Channel 2 Current individual Harmonics 26 percentage | HAR26_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
696 | 17 | 17-30 | 10084 | Input Channel 2 Current individual Harmonics 27 percentage | HAR27_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
697 | 17 | 17-31 | 10086 | Input Channel 2 Current individual Harmonics 28 percentage | HAR28_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
698 | 17 | 17-32 | 10088 | Input Channel 2 Current individual Harmonics 29 percentage | HAR29_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
699 | 17 | 17-33 | 10090 | Input Channel 2 Current individual Harmonics 30 percentage | HAR30_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
700 | 17 | 17-34 | 10092 | Input Channel 2 Current individual Harmonics 31 percentage | HAR31_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
701 | 18 | 18-1 | 10094 | Input Channel 3 Current THD | THD_I_003_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_003_%
702 | 18 | 18-2 | 10096 | Input Channel 3 Current THD Odd | OTHD_I_003_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_003_%
703 | 18 | 18-3 | 10098 | Input Channel 3 Current THD Even | ETHD_I_003_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_003_%
704 | 18 | 18-4 | 10100 | Input Channel 3 Current K Factor | KF_I_003_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_003_%
705 | 18 | 18-5 | 10102 | Input Channel 3 Current individual Harmonics 2 percentage | HAR2_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
706 | 18 | 18-6 | 10104 | Input Channel 3 Current individual Harmonics 3 percentage | HAR3_I_003_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 39
707 | 18 | 18-7 | 10106 | Input Channel 3 Current individual Harmonics 4 percentage | HAR4_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
708 | 18 | 18-8 | 10108 | Input Channel 3 Current individual Harmonics 5 percentage | HAR5_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
709 | 18 | 18-9 | 10110 | Input Channel 3 Current individual Harmonics 6 percentage | HAR6_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
710 | 18 | 18-10 | 10112 | Input Channel 3 Current individual Harmonics 7 percentage | HAR7_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
711 | 18 | 18-11 | 10114 | Input Channel 3 Current individual Harmonics 8 percentage | HAR8_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
712 | 18 | 18-12 | 10116 | Input Channel 3 Current individual Harmonics 9 percentage | HAR9_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
713 | 18 | 18-13 | 10118 | Input Channel 3 Current individual Harmonics 10 percentage | HAR10_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
714 | 18 | 18-14 | 10120 | Input Channel 3 Current individual Harmonics 11 percentage | HAR11_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
715 | 18 | 18-15 | 10122 | Input Channel 3 Current individual Harmonics 12 percentage | HAR12_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
716 | 18 | 18-16 | 10124 | Input Channel 3 Current individual Harmonics 13 percentage | HAR13_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
717 | 18 | 18-17 | 10126 | Input Channel 3 Current individual Harmonics 14 percentage | HAR14_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
718 | 18 | 18-18 | 10128 | Input Channel 3 Current individual Harmonics 15 percentage | HAR15_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
719 | 18 | 18-19 | 10130 | Input Channel 3 Current individual Harmonics 16 percentage | HAR16_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
720 | 18 | 18-20 | 10132 | Input Channel 3 Current individual Harmonics 17 percentage | HAR17_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
721 | 18 | 18-21 | 10134 | Input Channel 3 Current individual Harmonics 18 percentage | HAR18_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
722 | 18 | 18-22 | 10136 | Input Channel 3 Current individual Harmonics 19 percentage | HAR19_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
723 | 18 | 18-23 | 10138 | Input Channel 3 Current individual Harmonics 20 percentage | HAR20_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
724 | 18 | 18-24 | 10140 | Input Channel 3 Current individual Harmonics 21 percentage | HAR21_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
725 | 18 | 18-25 | 10142 | Input Channel 3 Current individual Harmonics 22 percentage | HAR22_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
726 | 18 | 18-26 | 10144 | Input Channel 3 Current individual Harmonics 23 percentage | HAR23_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
727 | 18 | 18-27 | 10146 | Input Channel 3 Current individual Harmonics 24 percentage | HAR24_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
728 | 18 | 18-28 | 10148 | Input Channel 3 Current individual Harmonics 25 percentage | HAR25_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
729 | 18 | 18-29 | 10150 | Input Channel 3 Current individual Harmonics 26 percentage | HAR26_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
730 | 18 | 18-30 | 10152 | Input Channel 3 Current individual Harmonics 27 percentage | HAR27_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
731 | 18 | 18-31 | 10154 | Input Channel 3 Current individual Harmonics 28 percentage | HAR28_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
732 | 18 | 18-32 | 10156 | Input Channel 3 Current individual Harmonics 29 percentage | HAR29_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
733 | 18 | 18-33 | 10158 | Input Channel 3 Current individual Harmonics 30 percentage | HAR30_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
734 | 18 | 18-34 | 10160 | Input Channel 3 Current individual Harmonics 31 percentage | HAR31_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
735 | 19 | 19-1 | 10162 | Input Channel 4 Current THD | THD_I_004_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_004_%
736 | 19 | 19-2 | 10164 | Input Channel 4 Current THD Odd | OTHD_I_004_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_004_%
737 | 19 | 19-3 | 10166 | Input Channel 4 Current THD Even | ETHD_I_004_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_004_%
738 | 19 | 19-4 | 10168 | Input Channel 4 Current K Factor | KF_I_004_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_004_%
739 | 19 | 19-5 | 10170 | Input Channel 4 Current individual Harmonics 2 percentage | HAR2_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
740 | 19 | 19-6 | 10172 | Input Channel 4 Current individual Harmonics 3 percentage | HAR3_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
741 | 19 | 19-7 | 10174 | Input Channel 4 Current individual Harmonics 4 percentage | HAR4_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
742 | 19 | 19-8 | 10176 | Input Channel 4 Current individual Harmonics 5 percentage | HAR5_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
743 | 19 | 19-9 | 10178 | Input Channel 4 Current individual Harmonics 6 percentage | HAR6_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
744 | 19 | 19-10 | 10180 | Input Channel 4 Current individual Harmonics 7 percentage | HAR7_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
745 | 19 | 19-11 | 10182 | Input Channel 4 Current individual Harmonics 8 percentage | HAR8_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
746 | 19 | 19-12 | 10184 | Input Channel 4 Current individual Harmonics 9 percentage | HAR9_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
747 | 19 | 19-13 | 10186 | Input Channel 4 Current individual Harmonics 10 percentage | HAR10_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
748 | 19 | 19-14 | 10188 | Input Channel 4 Current individual Harmonics 11 percentage | HAR11_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
749 | 19 | 19-15 | 10190 | Input Channel 4 Current individual Harmonics 12 percentage | HAR12_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
750 | 19 | 19-16 | 10192 | Input Channel 4 Current individual Harmonics 13 percentage | HAR13_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
751 | 19 | 19-17 | 10194 | Input Channel 4 Current individual Harmonics 14 percentage | HAR14_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
752 | 19 | 19-18 | 10196 | Input Channel 4 Current individual Harmonics 15 percentage | HAR15_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
753 | 19 | 19-19 | 10198 | Input Channel 4 Current individual Harmonics 16 percentage | HAR16_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
754 | 19 | 19-20 | 10200 | Input Channel 4 Current individual Harmonics 17 percentage | HAR17_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
755 | 19 | 19-21 | 10202 | Input Channel 4 Current individual Harmonics 18 percentage | HAR18_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
756 | 19 | 19-22 | 10204 | Input Channel 4 Current individual Harmonics 19 percentage | HAR19_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
757 | 19 | 19-23 | 10206 | Input Channel 4 Current individual Harmonics 20 percentage | HAR20_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
758 | 19 | 19-24 | 10208 | Input Channel 4 Current individual Harmonics 21 percentage | HAR21_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
759 | 19 | 19-25 | 10210 | Input Channel 4 Current individual Harmonics 22 percentage | HAR22_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
760 | 19 | 19-26 | 10212 | Input Channel 4 Current individual Harmonics 23 percentage | HAR23_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
761 | 19 | 19-27 | 10214 | Input Channel 4 Current individual Harmonics 24 percentage | HAR24_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
762 | 19 | 19-28 | 10216 | Input Channel 4 Current individual Harmonics 25 percentage | HAR25_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
763 | 19 | 19-29 | 10218 | Input Channel 4 Current individual Harmonics 26 percentage | HAR26_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
764 | 19 | 19-30 | 10220 | Input Channel 4 Current individual Harmonics 27 percentage | HAR27_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
765 | 19 | 19-31 | 10222 | Input Channel 4 Current individual Harmonics 28 percentage | HAR28_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
766 | 19 | 19-32 | 10224 | Input Channel 4 Current individual Harmonics 29 percentage | HAR29_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
767 | 19 | 19-33 | 10226 | Input Channel 4 Current individual Harmonics 30 percentage | HAR30_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
768 | 19 | 19-34 | 10228 | Input Channel 4 Current individual Harmonics 31 percentage | HAR31_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
769 | 20 | 20-1 | 10230 | Input Channel 5 Current THD | THD_I_005_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_005_%
770 | 20 | 20-2 | 10232 | Input Channel 5 Current THD Odd | OTHD_I_005_% | % | float32 | 22 | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_005_%
771 | 20 | 20-3 | 10234 | Input Channel 5 Current THD Even | ETHD_I_005_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_005_%
772 | 20 | 20-4 | 10236 | Input Channel 5 Current K Factor | KF_I_005_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_005_%
773 | 20 | 20-5 | 10238 | Input Channel 5 Current individual Harmonics 2 percentage | HAR2_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
774 | 20 | 20-6 | 10240 | Input Channel 5 Current individual Harmonics 3 percentage | HAR3_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
775 | 20 | 20-7 | 10242 | Input Channel 5 Current individual Harmonics 4 percentage | HAR4_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
776 | 20 | 20-8 | 10244 | Input Channel 5 Current individual Harmonics 5 percentage | HAR5_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
777 | 20 | 20-9 | 10246 | Input Channel 5 Current individual Harmonics 6 percentage | HAR6_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
778 | 20 | 20-10 | 10248 | Input Channel 5 Current individual Harmonics 7 percentage | HAR7_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
779 | 20 | 20-11 | 10250 | Input Channel 5 Current individual Harmonics 8 percentage | HAR8_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
780 | 20 | 20-12 | 10252 | Input Channel 5 Current individual Harmonics 9 percentage | HAR9_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
781 | 20 | 20-13 | 10254 | Input Channel 5 Current individual Harmonics 10 percentage | HAR10_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
782 | 20 | 20-14 | 10256 | Input Channel 5 Current individual Harmonics 11 percentage | HAR11_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
783 | 20 | 20-15 | 10258 | Input Channel 5 Current individual Harmonics 12 percentage | HAR12_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
784 | 20 | 20-16 | 10260 | Input Channel 5 Current individual Harmonics 13 percentage | HAR13_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
785 | 20 | 20-17 | 10262 | Input Channel 5 Current individual Harmonics 14 percentage | HAR14_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
786 | 20 | 20-18 | 10264 | Input Channel 5 Current individual Harmonics 15 percentage | HAR15_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
787 | 20 | 20-19 | 10266 | Input Channel 5 Current individual Harmonics 16 percentage | HAR16_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
788 | 20 | 20-20 | 10268 | Input Channel 5 Current individual Harmonics 17 percentage | HAR17_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
789 | 20 | 20-21 | 10270 | Input Channel 5 Current individual Harmonics 18 percentage | HAR18_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
790 | 20 | 20-22 | 10272 | Input Channel 5 Current individual Harmonics 19 percentage | HAR19_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
791 | 20 | 20-23 | 10274 | Input Channel 5 Current individual Harmonics 20 percentage | HAR20_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
792 | 20 | 20-24 | 10276 | Input Channel 5 Current individual Harmonics 21 percentage | HAR21_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
793 | 20 | 20-25 | 10278 | Input Channel 5 Current individual Harmonics 22 percentage | HAR22_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
794 | 20 | 20-26 | 10280 | Input Channel 5 Current individual Harmonics 23 percentage | HAR23_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
795 | 20 | 20-27 | 10282 | Input Channel 5 Current individual Harmonics 24 percentage | HAR24_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
796 | 20 | 20-28 | 10284 | Input Channel 5 Current individual Harmonics 25 percentage | HAR25_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
797 | 20 | 20-29 | 10286 | Input Channel 5 Current individual Harmonics 26 percentage | HAR26_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
798 | 20 | 20-30 | 10288 | Input Channel 5 Current individual Harmonics 27 percentage | HAR27_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
799 | 20 | 20-31 | 10290 | Input Channel 5 Current individual Harmonics 28 percentage | HAR28_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
800 | 20 | 20-32 | 10292 | Input Channel 5 Current individual Harmonics 29 percentage | HAR29_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
801 | 20 | 20-33 | 10294 | Input Channel 5 Current individual Harmonics 30 percentage | HAR30_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
802 | 20 | 20-34 | 10296 | Input Channel 5 Current individual Harmonics 31 percentage | HAR31_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
803 | 21 | 21-1 | 10298 | Input Channel 6 Current THD | THD_I_006_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_006_%
804 | 21 | 21-2 | 10300 | Input Channel 6 Current THD Odd | OTHD_I_006_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_006_%
805 | 21 | 21-3 | 10302 | Input Channel 6 Current THD Even | ETHD_I_006_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_006_%
806 | 21 | 21-4 | 10304 | Input Channel 6 Current K Factor | KF_I_006_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_006_%
807 | 21 | 21-5 | 10306 | Input Channel 6 Current individual Harmonics 2 percentage | HAR2_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
808 | 21 | 21-6 | 10308 | Input Channel 6 Current individual Harmonics 3 percentage | HAR3_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
809 | 21 | 21-7 | 10310 | Input Channel 6 Current individual Harmonics 4 percentage | HAR4_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
810 | 21 | 21-8 | 10312 | Input Channel 6 Current individual Harmonics 5 percentage | HAR5_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
811 | 21 | 21-9 | 10314 | Input Channel 6 Current individual Harmonics 6 percentage | HAR6_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
812 | 21 | 21-10 | 10316 | Input Channel 6 Current individual Harmonics 7 percentage | HAR7_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
813 | 21 | 21-11 | 10318 | Input Channel 6 Current individual Harmonics 8 percentage | HAR8_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
814 | 21 | 21-12 | 10320 | Input Channel 6 Current individual Harmonics 9 percentage | HAR9_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
815 | 21 | 21-13 | 10322 | Input Channel 6 Current individual Harmonics 10 percentage | HAR10_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
816 | 21 | 21-14 | 10324 | Input Channel 6 Current individual Harmonics 11 percentage | HAR11_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
817 | 21 | 21-15 | 10326 | Input Channel 6 Current individual Harmonics 12 percentage | HAR12_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
818 | 21 | 21-16 | 10328 | Input Channel 6 Current individual Harmonics 13 percentage | HAR13_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
819 | 21 | 21-17 | 10330 | Input Channel 6 Current individual Harmonics 14 percentage | HAR14_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
820 | 21 | 21-18 | 10332 | Input Channel 6 Current individual Harmonics 15 percentage | HAR15_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
821 | 21 | 21-19 | 10334 | Input Channel 6 Current individual Harmonics 16 percentage | HAR16_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
822 | 21 | 21-20 | 10336 | Input Channel 6 Current individual Harmonics 17 percentage | HAR17_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
823 | 21 | 21-21 | 10338 | Input Channel 6 Current individual Harmonics 18 percentage | HAR18_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
824 | 21 | 21-22 | 10340 | Input Channel 6 Current individual Harmonics 19 percentage | HAR19_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
825 | 21 | 21-23 | 10342 | Input Channel 6 Current individual Harmonics 20 percentage | HAR20_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
826 | 21 | 21-24 | 10344 | Input Channel 6 Current individual Harmonics 21 percentage | HAR21_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
827 | 21 | 21-25 | 10346 | Input Channel 6 Current individual Harmonics 22 percentage | HAR22_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
828 | 21 | 21-26 | 10348 | Input Channel 6 Current individual Harmonics 23 percentage | HAR23_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
829 | 21 | 21-27 | 10350 | Input Channel 6 Current individual Harmonics 24 percentage | HAR24_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
830 | 21 | 21-28 | 10352 | Input Channel 6 Current individual Harmonics 25 percentage | HAR25_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
831 | 21 | 21-29 | 10354 | Input Channel 6 Current individual Harmonics 26 percentage | HAR26_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
832 | 21 | 21-30 | 10356 | Input Channel 6 Current individual Harmonics 27 percentage | HAR27_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
833 | 21 | 21-31 | 10358 | Input Channel 6 Current individual Harmonics 28 percentage | HAR28_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
834 | 21 | 21-32 | 10360 | Input Channel 6 Current individual Harmonics 29 percentage | HAR29_I_006_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 39
835 | 21 | 21-33 | 10362 | Input Channel 6 Current individual Harmonics 30 percentage | HAR30_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
836 | 21 | 21-34 | 10364 | Input Channel 6 Current individual Harmonics 31 percentage | HAR31_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
837 | 22 | 22-1 | 10366 | Input Channel 7 Current THD | THD_I_007_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_007_%
838 | 22 | 22-2 | 10368 | Input Channel 7 Current THD Odd | OTHD_I_007_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_007_%
839 | 22 | 22-3 | 10370 | Input Channel 7 Current THD Even | ETHD_I_007_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_007_%
840 | 22 | 22-4 | 10372 | Input Channel 7 Current K Factor | KF_I_007_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_007_%
841 | 22 | 22-5 | 10374 | Input Channel 7 Current individual Harmonics 2 percentage | HAR2_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
842 | 22 | 22-6 | 10376 | Input Channel 7 Current individual Harmonics 3 percentage | HAR3_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
843 | 22 | 22-7 | 10378 | Input Channel 7 Current individual Harmonics 4 percentage | HAR4_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
844 | 22 | 22-8 | 10380 | Input Channel 7 Current individual Harmonics 5 percentage | HAR5_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
845 | 22 | 22-9 | 10382 | Input Channel 7 Current individual Harmonics 6 percentage | HAR6_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
846 | 22 | 22-10 | 10384 | Input Channel 7 Current individual Harmonics 7 percentage | HAR7_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
847 | 22 | 22-11 | 10386 | Input Channel 7 Current individual Harmonics 8 percentage | HAR8_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
848 | 22 | 22-12 | 10388 | Input Channel 7 Current individual Harmonics 9 percentage | HAR9_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
849 | 22 | 22-13 | 10390 | Input Channel 7 Current individual Harmonics 10 percentage | HAR10_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
850 | 22 | 22-14 | 10392 | Input Channel 7 Current individual Harmonics 11 percentage | HAR11_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
851 | 22 | 22-15 | 10394 | Input Channel 7 Current individual Harmonics 12 percentage | HAR12_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
852 | 22 | 22-16 | 10396 | Input Channel 7 Current individual Harmonics 13 percentage | HAR13_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
853 | 22 | 22-17 | 10398 | Input Channel 7 Current individual Harmonics 14 percentage | HAR14_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
854 | 22 | 22-18 | 10400 | Input Channel 7 Current individual Harmonics 15 percentage | HAR15_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
855 | 22 | 22-19 | 10402 | Input Channel 7 Current individual Harmonics 16 percentage | HAR16_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
856 | 22 | 22-20 | 10404 | Input Channel 7 Current individual Harmonics 17 percentage | HAR17_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
857 | 22 | 22-21 | 10406 | Input Channel 7 Current individual Harmonics 18 percentage | HAR18_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
858 | 22 | 22-22 | 10408 | Input Channel 7 Current individual Harmonics 19 percentage | HAR19_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
859 | 22 | 22-23 | 10410 | Input Channel 7 Current individual Harmonics 20 percentage | HAR20_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
860 | 22 | 22-24 | 10412 | Input Channel 7 Current individual Harmonics 21 percentage | HAR21_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
861 | 22 | 22-25 | 10414 | Input Channel 7 Current individual Harmonics 22 percentage | HAR22_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
862 | 22 | 22-26 | 10416 | Input Channel 7 Current individual Harmonics 23 percentage | HAR23_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
863 | 22 | 22-27 | 10418 | Input Channel 7 Current individual Harmonics 24 percentage | HAR24_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
864 | 22 | 22-28 | 10420 | Input Channel 7 Current individual Harmonics 25 percentage | HAR25_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
865 | 22 | 22-29 | 10422 | Input Channel 7 Current individual Harmonics 26 percentage | HAR26_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
866 | 22 | 22-30 | 10424 | Input Channel 7 Current individual Harmonics 27 percentage | HAR27_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
867 | 22 | 22-31 | 10426 | Input Channel 7 Current individual Harmonics 28 percentage | HAR28_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
868 | 22 | 22-32 | 10428 | Input Channel 7 Current individual Harmonics 29 percentage | HAR29_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
869 | 22 | 22-33 | 10430 | Input Channel 7 Current individual Harmonics 30 percentage | HAR30_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
870 | 22 | 22-34 | 10432 | Input Channel 7 Current individual Harmonics 31 percentage | HAR31_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
871 | 23 | 23-1 | 10434 | Input Channel 8 Current THD | THD_I_008_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_008_%
872 | 23 | 23-2 | 10436 | Input Channel 8 Current THD Odd | OTHD_I_008_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_008_%
873 | 23 | 23-3 | 10438 | Input Channel 8 Current THD Even | ETHD_I_008_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_008_%
874 | 23 | 23-4 | 10440 | Input Channel 8 Current K Factor | KF_I_008_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_008_%
875 | 23 | 23-5 | 10442 | Input Channel 8 Current individual Harmonics 2 percentage | HAR2_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
876 | 23 | 23-6 | 10444 | Input Channel 8 Current individual Harmonics 3 percentage | HAR3_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
877 | 23 | 23-7 | 10446 | Input Channel 8 Current individual Harmonics 4 percentage | HAR4_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
878 | 23 | 23-8 | 10448 | Input Channel 8 Current individual Harmonics 5 percentage | HAR5_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
879 | 23 | 23-9 | 10450 | Input Channel 8 Current individual Harmonics 6 percentage | HAR6_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
880 | 23 | 23-10 | 10452 | Input Channel 8 Current individual Harmonics 7 percentage | HAR7_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
881 | 23 | 23-11 | 10454 | Input Channel 8 Current individual Harmonics 8 percentage | HAR8_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
882 | 23 | 23-12 | 10456 | Input Channel 8 Current individual Harmonics 9 percentage | HAR9_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
883 | 23 | 23-13 | 10458 | Input Channel 8 Current individual Harmonics 10 percentage | HAR10_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
884 | 23 | 23-14 | 10460 | Input Channel 8 Current individual Harmonics 11 percentage | HAR11_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
885 | 23 | 23-15 | 10462 | Input Channel 8 Current individual Harmonics 12 percentage | HAR12_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
886 | 23 | 23-16 | 10464 | Input Channel 8 Current individual Harmonics 13 percentage | HAR13_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
887 | 23 | 23-17 | 10466 | Input Channel 8 Current individual Harmonics 14 percentage | HAR14_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
888 | 23 | 23-18 | 10468 | Input Channel 8 Current individual Harmonics 15 percentage | HAR15_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
889 | 23 | 23-19 | 10470 | Input Channel 8 Current individual Harmonics 16 percentage | HAR16_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
890 | 23 | 23-20 | 10472 | Input Channel 8 Current individual Harmonics 17 percentage | HAR17_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
891 | 23 | 23-21 | 10474 | Input Channel 8 Current individual Harmonics 18 percentage | HAR18_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
892 | 23 | 23-22 | 10476 | Input Channel 8 Current individual Harmonics 19 percentage | HAR19_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
893 | 23 | 23-23 | 10478 | Input Channel 8 Current individual Harmonics 20 percentage | HAR20_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
894 | 23 | 23-24 | 10480 | Input Channel 8 Current individual Harmonics 21 percentage | HAR21_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
895 | 23 | 23-25 | 10482 | Input Channel 8 Current individual Harmonics 22 percentage | HAR22_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
896 | 23 | 23-26 | 10484 | Input Channel 8 Current individual Harmonics 23 percentage | HAR23_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
897 | 23 | 23-27 | 10486 | Input Channel 8 Current individual Harmonics 24 percentage | HAR24_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
898 | 23 | 23-28 | 10488 | Input Channel 8 Current individual Harmonics 25 percentage | HAR25_I_008_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 39
899 | 23 | 23-29 | 10490 | Input Channel 8 Current individual Harmonics 26 percentage | HAR26_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
900 | 23 | 23-30 | 10492 | Input Channel 8 Current individual Harmonics 27 percentage | HAR27_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
901 | 23 | 23-31 | 10494 | Input Channel 8 Current individual Harmonics 28 percentage | HAR28_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
902 | 23 | 23-32 | 10496 | Input Channel 8 Current individual Harmonics 29 percentage | HAR29_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
903 | 23 | 23-33 | 10498 | Input Channel 8 Current individual Harmonics 30 percentage | HAR30_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
904 | 23 | 23-34 | 10500 | Input Channel 8 Current individual Harmonics 31 percentage | HAR31_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
905 | 24 | 24-1 | 10502 | Input Channel 9 Current THD | THD_I_009_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_009_%
906 | 24 | 24-2 | 10504 | Input Channel 9 Current THD Odd | OTHD_I_009_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_009_%
907 | 24 | 24-3 | 10506 | Input Channel 9 Current THD Even | ETHD_I_009_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_009_%
908 | 24 | 24-4 | 10508 | Input Channel 9 Current K Factor | KF_I_009_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_009_%
909 | 24 | 24-5 | 10510 | Input Channel 9 Current individual Harmonics 2 percentage | HAR2_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
910 | 24 | 24-6 | 10512 | Input Channel 9 Current individual Harmonics 3 percentage | HAR3_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
911 | 24 | 24-7 | 10514 | Input Channel 9 Current individual Harmonics 4 percentage | HAR4_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
912 | 24 | 24-8 | 10516 | Input Channel 9 Current individual Harmonics 5 percentage | HAR5_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
913 | 24 | 24-9 | 10518 | Input Channel 9 Current individual Harmonics 6 percentage | HAR6_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
914 | 24 | 24-10 | 10520 | Input Channel 9 Current individual Harmonics 7 percentage | HAR7_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
915 | 24 | 24-11 | 10522 | Input Channel 9 Current individual Harmonics 8 percentage | HAR8_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
916 | 24 | 24-12 | 10524 | Input Channel 9 Current individual Harmonics 9 percentage | HAR9_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
917 | 24 | 24-13 | 10526 | Input Channel 9 Current individual Harmonics 10 percentage | HAR10_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
918 | 24 | 24-14 | 10528 | Input Channel 9 Current individual Harmonics 11 percentage | HAR11_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
919 | 24 | 24-15 | 10530 | Input Channel 9 Current individual Harmonics 12 percentage | HAR12_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
920 | 24 | 24-16 | 10532 | Input Channel 9 Current individual Harmonics 13 percentage | HAR13_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
921 | 24 | 24-17 | 10534 | Input Channel 9 Current individual Harmonics 14 percentage | HAR14_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
922 | 24 | 24-18 | 10536 | Input Channel 9 Current individual Harmonics 15 percentage | HAR15_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
923 | 24 | 24-19 | 10538 | Input Channel 9 Current individual Harmonics 16 percentage | HAR16_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
924 | 24 | 24-20 | 10540 | Input Channel 9 Current individual Harmonics 17 percentage | HAR17_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
925 | 24 | 24-21 | 10542 | Input Channel 9 Current individual Harmonics 18 percentage | HAR18_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
926 | 24 | 24-22 | 10544 | Input Channel 9 Current individual Harmonics 19 percentage | HAR19_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
927 | 24 | 24-23 | 10546 | Input Channel 9 Current individual Harmonics 20 percentage | HAR20_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
928 | 24 | 24-24 | 10548 | Input Channel 9 Current individual Harmonics 21 percentage | HAR21_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
929 | 24 | 24-25 | 10550 | Input Channel 9 Current individual Harmonics 22 percentage | HAR22_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
930 | 24 | 24-26 | 10552 | Input Channel 9 Current individual Harmonics 23 percentage | HAR23_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
931 | 24 | 24-27 | 10554 | Input Channel 9 Current individual Harmonics 24 percentage | HAR24_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
932 | 24 | 24-28 | 10556 | Input Channel 9 Current individual Harmonics 25 percentage | HAR25_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
933 | 24 | 24-29 | 10558 | Input Channel 9 Current individual Harmonics 26 percentage | HAR26_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
934 | 24 | 24-30 | 10560 | Input Channel 9 Current individual Harmonics 27 percentage | HAR27_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
935 | 24 | 24-31 | 10562 | Input Channel 9 Current individual Harmonics 28 percentage | HAR28_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
936 | 24 | 24-32 | 10564 | Input Channel 9 Current individual Harmonics 29 percentage | HAR29_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
937 | 24 | 24-33 | 10566 | Input Channel 9 Current individual Harmonics 30 percentage | HAR30_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
938 | 24 | 24-34 | 10568 | Input Channel 9 Current individual Harmonics 31 percentage | HAR31_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
939 | 25 | 25-1 | 10570 | Input Channel 10 Current THD | THD_I_010_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_010_%
940 | 25 | 25-2 | 10572 | Input Channel 10 Current THD Odd | OTHD_I_010_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_010_%
941 | 25 | 25-3 | 10574 | Input Channel 10 Current THD Even | ETHD_I_010_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_010_%
942 | 25 | 25-4 | 10576 | Input Channel 10 Current K Factor | KF_I_010_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_010_%
943 | 25 | 25-5 | 10578 | Input Channel 10 Current individual Harmonics 2 percentage | HAR2_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
944 | 25 | 25-6 | 10580 | Input Channel 10 Current individual Harmonics 3 percentage | HAR3_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
945 | 25 | 25-7 | 10582 | Input Channel 10 Current individual Harmonics 4 percentage | HAR4_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
946 | 25 | 25-8 | 10584 | Input Channel 10 Current individual Harmonics 5 percentage | HAR5_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
947 | 25 | 25-9 | 10586 | Input Channel 10 Current individual Harmonics 6 percentage | HAR6_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
948 | 25 | 25-10 | 10588 | Input Channel 10 Current individual Harmonics 7 percentage | HAR7_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
949 | 25 | 25-11 | 10590 | Input Channel 10 Current individual Harmonics 8 percentage | HAR8_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
950 | 25 | 25-12 | 10592 | Input Channel 10 Current individual Harmonics 9 percentage | HAR9_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
951 | 25 | 25-13 | 10594 | Input Channel 10 Current individual Harmonics 10 percentage | HAR10_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
952 | 25 | 25-14 | 10596 | Input Channel 10 Current individual Harmonics 11 percentage | HAR11_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
953 | 25 | 25-15 | 10598 | Input Channel 10 Current individual Harmonics 12 percentage | HAR12_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
954 | 25 | 25-16 | 10600 | Input Channel 10 Current individual Harmonics 13 percentage | HAR13_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
955 | 25 | 25-17 | 10602 | Input Channel 10 Current individual Harmonics 14 percentage | HAR14_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
956 | 25 | 25-18 | 10604 | Input Channel 10 Current individual Harmonics 15 percentage | HAR15_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
957 | 25 | 25-19 | 10606 | Input Channel 10 Current individual Harmonics 16 percentage | HAR16_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
958 | 25 | 25-20 | 10608 | Input Channel 10 Current individual Harmonics 17 percentage | HAR17_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
959 | 25 | 25-21 | 10610 | Input Channel 10 Current individual Harmonics 18 percentage | HAR18_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
960 | 25 | 25-22 | 10612 | Input Channel 10 Current individual Harmonics 19 percentage | HAR19_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
961 | 25 | 25-23 | 10614 | Input Channel 10 Current individual Harmonics 20 percentage | HAR20_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
962 | 25 | 25-24 | 10616 | Input Channel 10 Current individual Harmonics 21 percentage | HAR21_I_010_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 39
963 | 25 | 25-25 | 10618 | Input Channel 10 Current individual Harmonics 22 percentage | HAR22_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
964 | 25 | 25-26 | 10620 | Input Channel 10 Current individual Harmonics 23 percentage | HAR23_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
965 | 25 | 25-27 | 10622 | Input Channel 10 Current individual Harmonics 24 percentage | HAR24_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
966 | 25 | 25-28 | 10624 | Input Channel 10 Current individual Harmonics 25 percentage | HAR25_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
967 | 25 | 25-29 | 10626 | Input Channel 10 Current individual Harmonics 26 percentage | HAR26_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
968 | 25 | 25-30 | 10628 | Input Channel 10 Current individual Harmonics 27 percentage | HAR27_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
969 | 25 | 25-31 | 10630 | Input Channel 10 Current individual Harmonics 28 percentage | HAR28_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
970 | 25 | 25-32 | 10632 | Input Channel 10 Current individual Harmonics 29 percentage | HAR29_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
971 | 25 | 25-33 | 10634 | Input Channel 10 Current individual Harmonics 30 percentage | HAR30_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
972 | 25 | 25-34 | 10636 | Input Channel 10 Current individual Harmonics 31 percentage | HAR31_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
973 | 26 | 26-1 | 10638 | Input Channel 11 Current THD | THD_I_011_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_011_%
974 | 26 | 26-2 | 10640 | Input Channel 11 Current THD Odd | OTHD_I_011_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_011_%
975 | 26 | 26-3 | 10642 | Input Channel 11 Current THD Even | ETHD_I_011_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_011_%
976 | 26 | 26-4 | 10644 | Input Channel 11 Current K Factor | KF_I_011_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_011_%
977 | 26 | 26-5 | 10646 | Input Channel 11 Current individual Harmonics 2 percentage | HAR2_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
978 | 26 | 26-6 | 10648 | Input Channel 11 Current individual Harmonics 3 percentage | HAR3_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
979 | 26 | 26-7 | 10650 | Input Channel 11 Current individual Harmonics 4 percentage | HAR4_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
980 | 26 | 26-8 | 10652 | Input Channel 11 Current individual Harmonics 5 percentage | HAR5_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
981 | 26 | 26-9 | 10654 | Input Channel 11 Current individual Harmonics 6 percentage | HAR6_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
982 | 26 | 26-10 | 10656 | Input Channel 11 Current individual Harmonics 7 percentage | HAR7_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
983 | 26 | 26-11 | 10658 | Input Channel 11 Current individual Harmonics 8 percentage | HAR8_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
984 | 26 | 26-12 | 10660 | Input Channel 11 Current individual Harmonics 9 percentage | HAR9_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
985 | 26 | 26-13 | 10662 | Input Channel 11 Current individual Harmonics 10 percentage | HAR10_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
986 | 26 | 26-14 | 10664 | Input Channel 11 Current individual Harmonics 11 percentage | HAR11_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
987 | 26 | 26-15 | 10666 | Input Channel 11 Current individual Harmonics 12 percentage | HAR12_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
988 | 26 | 26-16 | 10668 | Input Channel 11 Current individual Harmonics 13 percentage | HAR13_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
989 | 26 | 26-17 | 10670 | Input Channel 11 Current individual Harmonics 14 percentage | HAR14_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
990 | 26 | 26-18 | 10672 | Input Channel 11 Current individual Harmonics 15 percentage | HAR15_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
991 | 26 | 26-19 | 10674 | Input Channel 11 Current individual Harmonics 16 percentage | HAR16_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
992 | 26 | 26-20 | 10676 | Input Channel 11 Current individual Harmonics 17 percentage | HAR17_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
993 | 26 | 26-21 | 10678 | Input Channel 11 Current individual Harmonics 18 percentage | HAR18_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
994 | 26 | 26-22 | 10680 | Input Channel 11 Current individual Harmonics 19 percentage | HAR19_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
995 | 26 | 26-23 | 10682 | Input Channel 11 Current individual Harmonics 20 percentage | HAR20_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
996 | 26 | 26-24 | 10684 | Input Channel 11 Current individual Harmonics 21 percentage | HAR21_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
997 | 26 | 26-25 | 10686 | Input Channel 11 Current individual Harmonics 22 percentage | HAR22_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
998 | 26 | 26-26 | 10688 | Input Channel 11 Current individual Harmonics 23 percentage | HAR23_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
999 | 26 | 26-27 | 10690 | Input Channel 11 Current individual Harmonics 24 percentage | HAR24_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1000 | 26 | 26-28 | 10692 | Input Channel 11 Current individual Harmonics 25 percentage | HAR25_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1001 | 26 | 26-29 | 10694 | Input Channel 11 Current individual Harmonics 26 percentage | HAR26_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1002 | 26 | 26-30 | 10696 | Input Channel 11 Current individual Harmonics 27 percentage | HAR27_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1003 | 26 | 26-31 | 10698 | Input Channel 11 Current individual Harmonics 28 percentage | HAR28_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1004 | 26 | 26-32 | 10700 | Input Channel 11 Current individual Harmonics 29 percentage | HAR29_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1005 | 26 | 26-33 | 10702 | Input Channel 11 Current individual Harmonics 30 percentage | HAR30_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1006 | 26 | 26-34 | 10704 | Input Channel 11 Current individual Harmonics 31 percentage | HAR31_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1007 | 27 | 27-1 | 10706 | Input Channel 12 Current THD | THD_I_012_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_012_%
1008 | 27 | 27-2 | 10708 | Input Channel 12 Current THD Odd | OTHD_I_012_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_012_%
1009 | 27 | 27-3 | 10710 | Input Channel 12 Current THD Even | ETHD_I_012_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_012_%
1010 | 27 | 27-4 | 10712 | Input Channel 12 Current K Factor | KF_I_012_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_012_%
1011 | 27 | 27-5 | 10714 | Input Channel 12 Current individual Harmonics 2 percentage | HAR2_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1012 | 27 | 27-6 | 10716 | Input Channel 12 Current individual Harmonics 3 percentage | HAR3_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1013 | 27 | 27-7 | 10718 | Input Channel 12 Current individual Harmonics 4 percentage | HAR4_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1014 | 27 | 27-8 | 10720 | Input Channel 12 Current individual Harmonics 5 percentage | HAR5_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1015 | 27 | 27-9 | 10722 | Input Channel 12 Current individual Harmonics 6 percentage | HAR6_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1016 | 27 | 27-10 | 10724 | Input Channel 12 Current individual Harmonics 7 percentage | HAR7_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1017 | 27 | 27-11 | 10726 | Input Channel 12 Current individual Harmonics 8 percentage | HAR8_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1018 | 27 | 27-12 | 10728 | Input Channel 12 Current individual Harmonics 9 percentage | HAR9_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1019 | 27 | 27-13 | 10730 | Input Channel 12 Current individual Harmonics 10 percentage | HAR10_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1020 | 27 | 27-14 | 10732 | Input Channel 12 Current individual Harmonics 11 percentage | HAR11_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1021 | 27 | 27-15 | 10734 | Input Channel 12 Current individual Harmonics 12 percentage | HAR12_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1022 | 27 | 27-16 | 10736 | Input Channel 12 Current individual Harmonics 13 percentage | HAR13_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1023 | 27 | 27-17 | 10738 | Input Channel 12 Current individual Harmonics 14 percentage | HAR14_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1024 | 27 | 27-18 | 10740 | Input Channel 12 Current individual Harmonics 15 percentage | HAR15_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1025 | 27 | 27-19 | 10742 | Input Channel 12 Current individual Harmonics 16 percentage | HAR16_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1026 | 27 | 27-20 | 10744 | Input Channel 12 Current individual Harmonics 17 percentage | HAR17_I_012_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 39
1027 | 27 | 27-21 | 10746 | Input Channel 12 Current individual Harmonics 18 percentage | HAR18_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1028 | 27 | 27-22 | 10748 | Input Channel 12 Current individual Harmonics 19 percentage | HAR19_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1029 | 27 | 27-23 | 10750 | Input Channel 12 Current individual Harmonics 20 percentage | HAR20_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1030 | 27 | 27-24 | 10752 | Input Channel 12 Current individual Harmonics 21 percentage | HAR21_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1031 | 27 | 27-25 | 10754 | Input Channel 12 Current individual Harmonics 22 percentage | HAR22_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1032 | 27 | 27-26 | 10756 | Input Channel 12 Current individual Harmonics 23 percentage | HAR23_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1033 | 27 | 27-27 | 10758 | Input Channel 12 Current individual Harmonics 24 percentage | HAR24_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1034 | 27 | 27-28 | 10760 | Input Channel 12 Current individual Harmonics 25 percentage | HAR25_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1035 | 27 | 27-29 | 10762 | Input Channel 12 Current individual Harmonics 26 percentage | HAR26_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1036 | 27 | 27-30 | 10764 | Input Channel 12 Current individual Harmonics 27 percentage | HAR27_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1037 | 27 | 27-31 | 10766 | Input Channel 12 Current individual Harmonics 28 percentage | HAR28_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1038 | 27 | 27-32 | 10768 | Input Channel 12 Current individual Harmonics 29 percentage | HAR29_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1039 | 27 | 27-33 | 10770 | Input Channel 12 Current individual Harmonics 30 percentage | HAR30_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1040 | 27 | 27-34 | 10772 | Input Channel 12 Current individual Harmonics 31 percentage | HAR31_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1041 | 28 | 28-1 | 10774 | Input Channel 13 Current THD | THD_I_013_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_013_%
1042 | 28 | 28-2 | 10776 | Input Channel 13 Current THD Odd | OTHD_I_013_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_013_%
1043 | 28 | 28-3 | 10778 | Input Channel 13 Current THD Even | ETHD_I_013_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_013_%
1044 | 28 | 28-4 | 10780 | Input Channel 13 Current K Factor | KF_I_013_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_013_%
1045 | 28 | 28-5 | 10782 | Input Channel 13 Current individual Harmonics 2 percentage | HAR2_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1046 | 28 | 28-6 | 10784 | Input Channel 13 Current individual Harmonics 3 percentage | HAR3_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1047 | 28 | 28-7 | 10786 | Input Channel 13 Current individual Harmonics 4 percentage | HAR4_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1048 | 28 | 28-8 | 10788 | Input Channel 13 Current individual Harmonics 5 percentage | HAR5_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1049 | 28 | 28-9 | 10790 | Input Channel 13 Current individual Harmonics 6 percentage | HAR6_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1050 | 28 | 28-10 | 10792 | Input Channel 13 Current individual Harmonics 7 percentage | HAR7_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1051 | 28 | 28-11 | 10794 | Input Channel 13 Current individual Harmonics 8 percentage | HAR8_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1052 | 28 | 28-12 | 10796 | Input Channel 13 Current individual Harmonics 9 percentage | HAR9_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1053 | 28 | 28-13 | 10798 | Input Channel 13 Current individual Harmonics 10 percentage | HAR10_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1054 | 28 | 28-14 | 10800 | Input Channel 13 Current individual Harmonics 11 percentage | HAR11_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1055 | 28 | 28-15 | 10802 | Input Channel 13 Current individual Harmonics 12 percentage | HAR12_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1056 | 28 | 28-16 | 10804 | Input Channel 13 Current individual Harmonics 13 percentage | HAR13_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1057 | 28 | 28-17 | 10806 | Input Channel 13 Current individual Harmonics 14 percentage | HAR14_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1058 | 28 | 28-18 | 10808 | Input Channel 13 Current individual Harmonics 15 percentage | HAR15_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1059 | 28 | 28-19 | 10810 | Input Channel 13 Current individual Harmonics 16 percentage | HAR16_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1060 | 28 | 28-20 | 10812 | Input Channel 13 Current individual Harmonics 17 percentage | HAR17_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1061 | 28 | 28-21 | 10814 | Input Channel 13 Current individual Harmonics 18 percentage | HAR18_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1062 | 28 | 28-22 | 10816 | Input Channel 13 Current individual Harmonics 19 percentage | HAR19_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1063 | 28 | 28-23 | 10818 | Input Channel 13 Current individual Harmonics 20 percentage | HAR20_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1064 | 28 | 28-24 | 10820 | Input Channel 13 Current individual Harmonics 21 percentage | HAR21_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1065 | 28 | 28-25 | 10822 | Input Channel 13 Current individual Harmonics 22 percentage | HAR22_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1066 | 28 | 28-26 | 10824 | Input Channel 13 Current individual Harmonics 23 percentage | HAR23_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1067 | 28 | 28-27 | 10826 | Input Channel 13 Current individual Harmonics 24 percentage | HAR24_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1068 | 28 | 28-28 | 10828 | Input Channel 13 Current individual Harmonics 25 percentage | HAR25_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1069 | 28 | 28-29 | 10830 | Input Channel 13 Current individual Harmonics 26 percentage | HAR26_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1070 | 28 | 28-30 | 10832 | Input Channel 13 Current individual Harmonics 27 percentage | HAR27_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1071 | 28 | 28-31 | 10834 | Input Channel 13 Current individual Harmonics 28 percentage | HAR28_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1072 | 28 | 28-32 | 10836 | Input Channel 13 Current individual Harmonics 29 percentage | HAR29_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1073 | 28 | 28-33 | 10838 | Input Channel 13 Current individual Harmonics 30 percentage | HAR30_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1074 | 28 | 28-34 | 10840 | Input Channel 13 Current individual Harmonics 31 percentage | HAR31_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1075 | 29 | 29-1 | 10842 | Input Channel 14 Current THD | THD_I_014_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_014_%
1076 | 29 | 29-2 | 10844 | Input Channel 14 Current THD Odd | OTHD_I_014_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_014_%
1077 | 29 | 29-3 | 10846 | Input Channel 14 Current THD Even | ETHD_I_014_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_014_%
1078 | 29 | 29-4 | 10848 | Input Channel 14 Current K Factor | KF_I_014_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_014_%
1079 | 29 | 29-5 | 10850 | Input Channel 14 Current individual Harmonics 2 percentage | HAR2_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1080 | 29 | 29-6 | 10852 | Input Channel 14 Current individual Harmonics 3 percentage | HAR3_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1081 | 29 | 29-7 | 10854 | Input Channel 14 Current individual Harmonics 4 percentage | HAR4_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1082 | 29 | 29-8 | 10856 | Input Channel 14 Current individual Harmonics 5 percentage | HAR5_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1083 | 29 | 29-9 | 10858 | Input Channel 14 Current individual Harmonics 6 percentage | HAR6_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1084 | 29 | 29-10 | 10860 | Input Channel 14 Current individual Harmonics 7 percentage | HAR7_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1085 | 29 | 29-11 | 10862 | Input Channel 14 Current individual Harmonics 8 percentage | HAR8_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1086 | 29 | 29-12 | 10864 | Input Channel 14 Current individual Harmonics 9 percentage | HAR9_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1087 | 29 | 29-13 | 10866 | Input Channel 14 Current individual Harmonics 10 percentage | HAR10_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1088 | 29 | 29-14 | 10868 | Input Channel 14 Current individual Harmonics 11 percentage | HAR11_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1089 | 29 | 29-15 | 10870 | Input Channel 14 Current individual Harmonics 12 percentage | HAR12_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1090 | 29 | 29-16 | 10872 | Input Channel 14 Current individual Harmonics 13 percentage | HAR13_I_014_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 39
1091 | 29 | 29-17 | 10874 | Input Channel 14 Current individual Harmonics 14 percentage | HAR14_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1092 | 29 | 29-18 | 10876 | Input Channel 14 Current individual Harmonics 15 percentage | HAR15_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1093 | 29 | 29-19 | 10878 | Input Channel 14 Current individual Harmonics 16 percentage | HAR16_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1094 | 29 | 29-20 | 10880 | Input Channel 14 Current individual Harmonics 17 percentage | HAR17_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1095 | 29 | 29-21 | 10882 | Input Channel 14 Current individual Harmonics 18 percentage | HAR18_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1096 | 29 | 29-22 | 10884 | Input Channel 14 Current individual Harmonics 19 percentage | HAR19_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1097 | 29 | 29-23 | 10886 | Input Channel 14 Current individual Harmonics 20 percentage | HAR20_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1098 | 29 | 29-24 | 10888 | Input Channel 14 Current individual Harmonics 21 percentage | HAR21_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1099 | 29 | 29-25 | 10890 | Input Channel 14 Current individual Harmonics 22 percentage | HAR22_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1100 | 29 | 29-26 | 10892 | Input Channel 14 Current individual Harmonics 23 percentage | HAR23_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1101 | 29 | 29-27 | 10894 | Input Channel 14 Current individual Harmonics 24 percentage | HAR24_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1102 | 29 | 29-28 | 10896 | Input Channel 14 Current individual Harmonics 25 percentage | HAR25_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1103 | 29 | 29-29 | 10898 | Input Channel 14 Current individual Harmonics 26 percentage | HAR26_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1104 | 29 | 29-30 | 10900 | Input Channel 14 Current individual Harmonics 27 percentage | HAR27_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1105 | 29 | 29-31 | 10902 | Input Channel 14 Current individual Harmonics 28 percentage | HAR28_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1106 | 29 | 29-32 | 10904 | Input Channel 14 Current individual Harmonics 29 percentage | HAR29_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1107 | 29 | 29-33 | 10906 | Input Channel 14 Current individual Harmonics 30 percentage | HAR30_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1108 | 29 | 29-34 | 10908 | Input Channel 14 Current individual Harmonics 31 percentage | HAR31_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1109 | 30 | 30-1 | 10910 | Input Channel 15 Current THD | THD_I_015_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_015_%
1110 | 30 | 30-2 | 10912 | Input Channel 15 Current THD Odd | OTHD_I_015_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_015_%
1111 | 30 | 30-3 | 10914 | Input Channel 15 Current THD Even | ETHD_I_015_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_015_%
1112 | 30 | 30-4 | 10916 | Input Channel 15 Current K Factor | KF_I_015_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_015_%
1113 | 30 | 30-5 | 10918 | Input Channel 15 Current individual Harmonics 2 percentage | HAR2_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1114 | 30 | 30-6 | 10920 | Input Channel 15 Current individual Harmonics 3 percentage | HAR3_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1115 | 30 | 30-7 | 10922 | Input Channel 15 Current individual Harmonics 4 percentage | HAR4_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1116 | 30 | 30-8 | 10924 | Input Channel 15 Current individual Harmonics 5 percentage | HAR5_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1117 | 30 | 30-9 | 10926 | Input Channel 15 Current individual Harmonics 6 percentage | HAR6_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1118 | 30 | 30-10 | 10928 | Input Channel 15 Current individual Harmonics 7 percentage | HAR7_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1119 | 30 | 30-11 | 10930 | Input Channel 15 Current individual Harmonics 8 percentage | HAR8_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1120 | 30 | 30-12 | 10932 | Input Channel 15 Current individual Harmonics 9 percentage | HAR9_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1121 | 30 | 30-13 | 10934 | Input Channel 15 Current individual Harmonics 10 percentage | HAR10_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1122 | 30 | 30-14 | 10936 | Input Channel 15 Current individual Harmonics 11 percentage | HAR11_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1123 | 30 | 30-15 | 10938 | Input Channel 15 Current individual Harmonics 12 percentage | HAR12_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1124 | 30 | 30-16 | 10940 | Input Channel 15 Current individual Harmonics 13 percentage | HAR13_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1125 | 30 | 30-17 | 10942 | Input Channel 15 Current individual Harmonics 14 percentage | HAR14_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1126 | 30 | 30-18 | 10944 | Input Channel 15 Current individual Harmonics 15 percentage | HAR15_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1127 | 30 | 30-19 | 10946 | Input Channel 15 Current individual Harmonics 16 percentage | HAR16_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1128 | 30 | 30-20 | 10948 | Input Channel 15 Current individual Harmonics 17 percentage | HAR17_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1129 | 30 | 30-21 | 10950 | Input Channel 15 Current individual Harmonics 18 percentage | HAR18_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1130 | 30 | 30-22 | 10952 | Input Channel 15 Current individual Harmonics 19 percentage | HAR19_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1131 | 30 | 30-23 | 10954 | Input Channel 15 Current individual Harmonics 20 percentage | HAR20_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1132 | 30 | 30-24 | 10956 | Input Channel 15 Current individual Harmonics 21 percentage | HAR21_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1133 | 30 | 30-25 | 10958 | Input Channel 15 Current individual Harmonics 22 percentage | HAR22_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1134 | 30 | 30-26 | 10960 | Input Channel 15 Current individual Harmonics 23 percentage | HAR23_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1135 | 30 | 30-27 | 10962 | Input Channel 15 Current individual Harmonics 24 percentage | HAR24_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1136 | 30 | 30-28 | 10964 | Input Channel 15 Current individual Harmonics 25 percentage | HAR25_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1137 | 30 | 30-29 | 10966 | Input Channel 15 Current individual Harmonics 26 percentage | HAR26_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1138 | 30 | 30-30 | 10968 | Input Channel 15 Current individual Harmonics 27 percentage | HAR27_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1139 | 30 | 30-31 | 10970 | Input Channel 15 Current individual Harmonics 28 percentage | HAR28_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1140 | 30 | 30-32 | 10972 | Input Channel 15 Current individual Harmonics 29 percentage | HAR29_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1141 | 30 | 30-33 | 10974 | Input Channel 15 Current individual Harmonics 30 percentage | HAR30_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1142 | 30 | 30-34 | 10976 | Input Channel 15 Current individual Harmonics 31 percentage | HAR31_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1143 | 31 | 31-1 | 10978 | Input Channel 16 Current THD | THD_I_016_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_016_%
1144 | 31 | 31-2 | 10980 | Input Channel 16 Current THD Odd | OTHD_I_016_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_016_%
1145 | 31 | 31-3 | 10982 | Input Channel 16 Current THD Even | ETHD_I_016_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_016_%
1146 | 31 | 31-4 | 10984 | Input Channel 16 Current K Factor | KF_I_016_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_016_%
1147 | 31 | 31-5 | 10986 | Input Channel 16 Current individual Harmonics 2 percentage | HAR2_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1148 | 31 | 31-6 | 10988 | Input Channel 16 Current individual Harmonics 3 percentage | HAR3_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1149 | 31 | 31-7 | 10990 | Input Channel 16 Current individual Harmonics 4 percentage | HAR4_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1150 | 31 | 31-8 | 10992 | Input Channel 16 Current individual Harmonics 5 percentage | HAR5_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1151 | 31 | 31-9 | 10994 | Input Channel 16 Current individual Harmonics 6 percentage | HAR6_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1152 | 31 | 31-10 | 10996 | Input Channel 16 Current individual Harmonics 7 percentage | HAR7_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1153 | 31 | 31-11 | 10998 | Input Channel 16 Current individual Harmonics 8 percentage | HAR8_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1154 | 31 | 31-12 | 11000 | Input Channel 16 Current individual Harmonics 9 percentage | HAR9_I_016_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 39
1155 | 31 | 31-13 | 11002 | Input Channel 16 Current individual Harmonics 10 percentage | HAR10_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1156 | 31 | 31-14 | 11004 | Input Channel 16 Current individual Harmonics 11 percentage | HAR11_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1157 | 31 | 31-15 | 11006 | Input Channel 16 Current individual Harmonics 12 percentage | HAR12_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1158 | 31 | 31-16 | 11008 | Input Channel 16 Current individual Harmonics 13 percentage | HAR13_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1159 | 31 | 31-17 | 11010 | Input Channel 16 Current individual Harmonics 14 percentage | HAR14_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1160 | 31 | 31-18 | 11012 | Input Channel 16 Current individual Harmonics 15 percentage | HAR15_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1161 | 31 | 31-19 | 11014 | Input Channel 16 Current individual Harmonics 16 percentage | HAR16_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1162 | 31 | 31-20 | 11016 | Input Channel 16 Current individual Harmonics 17 percentage | HAR17_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1163 | 31 | 31-21 | 11018 | Input Channel 16 Current individual Harmonics 18 percentage | HAR18_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1164 | 31 | 31-22 | 11020 | Input Channel 16 Current individual Harmonics 19 percentage | HAR19_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1165 | 31 | 31-23 | 11022 | Input Channel 16 Current individual Harmonics 20 percentage | HAR20_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1166 | 31 | 31-24 | 11024 | Input Channel 16 Current individual Harmonics 21 percentage | HAR21_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1167 | 31 | 31-25 | 11026 | Input Channel 16 Current individual Harmonics 22 percentage | HAR22_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1168 | 31 | 31-26 | 11028 | Input Channel 16 Current individual Harmonics 23 percentage | HAR23_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1169 | 31 | 31-27 | 11030 | Input Channel 16 Current individual Harmonics 24 percentage | HAR24_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1170 | 31 | 31-28 | 11032 | Input Channel 16 Current individual Harmonics 25 percentage | HAR25_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1171 | 31 | 31-29 | 11034 | Input Channel 16 Current individual Harmonics 26 percentage | HAR26_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1172 | 31 | 31-30 | 11036 | Input Channel 16 Current individual Harmonics 27 percentage | HAR27_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1173 | 31 | 31-31 | 11038 | Input Channel 16 Current individual Harmonics 28 percentage | HAR28_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1174 | 31 | 31-32 | 11040 | Input Channel 16 Current individual Harmonics 29 percentage | HAR29_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1175 | 31 | 31-33 | 11042 | Input Channel 16 Current individual Harmonics 30 percentage | HAR30_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1176 | 31 | 31-34 | 11044 | Input Channel 16 Current individual Harmonics 31 percentage | HAR31_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1177 | 32 | 32-1 | 11046 | Input Channel 17 Current THD | THD_I_017_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_017_%
1178 | 32 | 32-2 | 11048 | Input Channel 17 Current THD Odd | OTHD_I_017_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_017_%
1179 | 32 | 32-3 | 11050 | Input Channel 17 Current THD Even | ETHD_I_017_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_017_%
1180 | 32 | 32-4 | 11052 | Input Channel 17 Current K Factor | KF_I_017_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_017_%
1181 | 32 | 32-5 | 11054 | Input Channel 17 Current individual Harmonics 2 percentage | HAR2_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1182 | 32 | 32-6 | 11056 | Input Channel 17 Current individual Harmonics 3 percentage | HAR3_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1183 | 32 | 32-7 | 11058 | Input Channel 17 Current individual Harmonics 4 percentage | HAR4_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1184 | 32 | 32-8 | 11060 | Input Channel 17 Current individual Harmonics 5 percentage | HAR5_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1185 | 32 | 32-9 | 11062 | Input Channel 17 Current individual Harmonics 6 percentage | HAR6_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1186 | 32 | 32-10 | 11064 | Input Channel 17 Current individual Harmonics 7 percentage | HAR7_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1187 | 32 | 32-11 | 11066 | Input Channel 17 Current individual Harmonics 8 percentage | HAR8_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1188 | 32 | 32-12 | 11068 | Input Channel 17 Current individual Harmonics 9 percentage | HAR9_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1189 | 32 | 32-13 | 11070 | Input Channel 17 Current individual Harmonics 10 percentage | HAR10_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1190 | 32 | 32-14 | 11072 | Input Channel 17 Current individual Harmonics 11 percentage | HAR11_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1191 | 32 | 32-15 | 11074 | Input Channel 17 Current individual Harmonics 12 percentage | HAR12_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1192 | 32 | 32-16 | 11076 | Input Channel 17 Current individual Harmonics 13 percentage | HAR13_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1193 | 32 | 32-17 | 11078 | Input Channel 17 Current individual Harmonics 14 percentage | HAR14_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1194 | 32 | 32-18 | 11080 | Input Channel 17 Current individual Harmonics 15 percentage | HAR15_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1195 | 32 | 32-19 | 11082 | Input Channel 17 Current individual Harmonics 16 percentage | HAR16_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1196 | 32 | 32-20 | 11084 | Input Channel 17 Current individual Harmonics 17 percentage | HAR17_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1197 | 32 | 32-21 | 11086 | Input Channel 17 Current individual Harmonics 18 percentage | HAR18_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1198 | 32 | 32-22 | 11088 | Input Channel 17 Current individual Harmonics 19 percentage | HAR19_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1199 | 32 | 32-23 | 11090 | Input Channel 17 Current individual Harmonics 20 percentage | HAR20_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1200 | 32 | 32-24 | 11092 | Input Channel 17 Current individual Harmonics 21 percentage | HAR21_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1201 | 32 | 32-25 | 11094 | Input Channel 17 Current individual Harmonics 22 percentage | HAR22_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1202 | 32 | 32-26 | 11096 | Input Channel 17 Current individual Harmonics 23 percentage | HAR23_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1203 | 32 | 32-27 | 11098 | Input Channel 17 Current individual Harmonics 24 percentage | HAR24_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1204 | 32 | 32-28 | 11100 | Input Channel 17 Current individual Harmonics 25 percentage | HAR25_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1205 | 32 | 32-29 | 11102 | Input Channel 17 Current individual Harmonics 26 percentage | HAR26_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1206 | 32 | 32-30 | 11104 | Input Channel 17 Current individual Harmonics 27 percentage | HAR27_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1207 | 32 | 32-31 | 11106 | Input Channel 17 Current individual Harmonics 28 percentage | HAR28_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1208 | 32 | 32-32 | 11108 | Input Channel 17 Current individual Harmonics 29 percentage | HAR29_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1209 | 32 | 32-33 | 11110 | Input Channel 17 Current individual Harmonics 30 percentage | HAR30_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1210 | 32 | 32-34 | 11112 | Input Channel 17 Current individual Harmonics 31 percentage | HAR31_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1211 | 33 | 33-1 | 11114 | Input Channel 18 Current THD | THD_I_018_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_018_%
1212 | 33 | 33-2 | 11116 | Input Channel 18 Current THD Odd | OTHD_I_018_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_018_%
1213 | 33 | 33-3 | 11118 | Input Channel 18 Current THD Even | ETHD_I_018_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_018_%
1214 | 33 | 33-4 | 11120 | Input Channel 18 Current K Factor | KF_I_018_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_018_%
1215 | 33 | 33-5 | 11122 | Input Channel 18 Current individual Harmonics 2 percentage | HAR2_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1216 | 33 | 33-6 | 11124 | Input Channel 18 Current individual Harmonics 3 percentage | HAR3_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1217 | 33 | 33-7 | 11126 | Input Channel 18 Current individual Harmonics 4 percentage | HAR4_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1218 | 33 | 33-8 | 11128 | Input Channel 18 Current individual Harmonics 5 percentage | HAR5_I_018_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 39
1219 | 33 | 33-9 | 11130 | Input Channel 18 Current individual Harmonics 6 percentage | HAR6_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1220 | 33 | 33-10 | 11132 | Input Channel 18 Current individual Harmonics 7 percentage | HAR7_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1221 | 33 | 33-11 | 11134 | Input Channel 18 Current individual Harmonics 8 percentage | HAR8_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1222 | 33 | 33-12 | 11136 | Input Channel 18 Current individual Harmonics 9 percentage | HAR9_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1223 | 33 | 33-13 | 11138 | Input Channel 18 Current individual Harmonics 10 percentage | HAR10_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1224 | 33 | 33-14 | 11140 | Input Channel 18 Current individual Harmonics 11 percentage | HAR11_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1225 | 33 | 33-15 | 11142 | Input Channel 18 Current individual Harmonics 12 percentage | HAR12_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1226 | 33 | 33-16 | 11144 | Input Channel 18 Current individual Harmonics 13 percentage | HAR13_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1227 | 33 | 33-17 | 11146 | Input Channel 18 Current individual Harmonics 14 percentage | HAR14_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1228 | 33 | 33-18 | 11148 | Input Channel 18 Current individual Harmonics 15 percentage | HAR15_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1229 | 33 | 33-19 | 11150 | Input Channel 18 Current individual Harmonics 16 percentage | HAR16_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1230 | 33 | 33-20 | 11152 | Input Channel 18 Current individual Harmonics 17 percentage | HAR17_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1231 | 33 | 33-21 | 11154 | Input Channel 18 Current individual Harmonics 18 percentage | HAR18_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1232 | 33 | 33-22 | 11156 | Input Channel 18 Current individual Harmonics 19 percentage | HAR19_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1233 | 33 | 33-23 | 11158 | Input Channel 18 Current individual Harmonics 20 percentage | HAR20_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1234 | 33 | 33-24 | 11160 | Input Channel 18 Current individual Harmonics 21 percentage | HAR21_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1235 | 33 | 33-25 | 11162 | Input Channel 18 Current individual Harmonics 22 percentage | HAR22_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1236 | 33 | 33-26 | 11164 | Input Channel 18 Current individual Harmonics 23 percentage | HAR23_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1237 | 33 | 33-27 | 11166 | Input Channel 18 Current individual Harmonics 24 percentage | HAR24_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1238 | 33 | 33-28 | 11168 | Input Channel 18 Current individual Harmonics 25 percentage | HAR25_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1239 | 33 | 33-29 | 11170 | Input Channel 18 Current individual Harmonics 26 percentage | HAR26_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1240 | 33 | 33-30 | 11172 | Input Channel 18 Current individual Harmonics 27 percentage | HAR27_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1241 | 33 | 33-31 | 11174 | Input Channel 18 Current individual Harmonics 28 percentage | HAR28_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1242 | 33 | 33-32 | 11176 | Input Channel 18 Current individual Harmonics 29 percentage | HAR29_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1243 | 33 | 33-33 | 11178 | Input Channel 18 Current individual Harmonics 30 percentage | HAR30_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1244 | 33 | 33-34 | 11180 | Input Channel 18 Current individual Harmonics 31 percentage | HAR31_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1245 | 34 | 34-1 | 11182 | Input Channel 19 Current THD | THD_I_019_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_019_%
1246 | 34 | 34-2 | 11184 | Input Channel 19 Current THD Odd | OTHD_I_019_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_019_%
1247 | 34 | 34-3 | 11186 | Input Channel 19 Current THD Even | ETHD_I_019_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_019_%
1248 | 34 | 34-4 | 11188 | Input Channel 19 Current K Factor | KF_I_019_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_019_%
1249 | 34 | 34-5 | 11190 | Input Channel 19 Current individual Harmonics 2 percentage | HAR2_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1250 | 34 | 34-6 | 11192 | Input Channel 19 Current individual Harmonics 3 percentage | HAR3_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1251 | 34 | 34-7 | 11194 | Input Channel 19 Current individual Harmonics 4 percentage | HAR4_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1252 | 34 | 34-8 | 11196 | Input Channel 19 Current individual Harmonics 5 percentage | HAR5_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1253 | 34 | 34-9 | 11198 | Input Channel 19 Current individual Harmonics 6 percentage | HAR6_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1254 | 34 | 34-10 | 11200 | Input Channel 19 Current individual Harmonics 7 percentage | HAR7_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1255 | 34 | 34-11 | 11202 | Input Channel 19 Current individual Harmonics 8 percentage | HAR8_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1256 | 34 | 34-12 | 11204 | Input Channel 19 Current individual Harmonics 9 percentage | HAR9_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1257 | 34 | 34-13 | 11206 | Input Channel 19 Current individual Harmonics 10 percentage | HAR10_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1258 | 34 | 34-14 | 11208 | Input Channel 19 Current individual Harmonics 11 percentage | HAR11_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1259 | 34 | 34-15 | 11210 | Input Channel 19 Current individual Harmonics 12 percentage | HAR12_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1260 | 34 | 34-16 | 11212 | Input Channel 19 Current individual Harmonics 13 percentage | HAR13_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1261 | 34 | 34-17 | 11214 | Input Channel 19 Current individual Harmonics 14 percentage | HAR14_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1262 | 34 | 34-18 | 11216 | Input Channel 19 Current individual Harmonics 15 percentage | HAR15_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1263 | 34 | 34-19 | 11218 | Input Channel 19 Current individual Harmonics 16 percentage | HAR16_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1264 | 34 | 34-20 | 11220 | Input Channel 19 Current individual Harmonics 17 percentage | HAR17_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1265 | 34 | 34-21 | 11222 | Input Channel 19 Current individual Harmonics 18 percentage | HAR18_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1266 | 34 | 34-22 | 11224 | Input Channel 19 Current individual Harmonics 19 percentage | HAR19_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1267 | 34 | 34-23 | 11226 | Input Channel 19 Current individual Harmonics 20 percentage | HAR20_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1268 | 34 | 34-24 | 11228 | Input Channel 19 Current individual Harmonics 21 percentage | HAR21_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1269 | 34 | 34-25 | 11230 | Input Channel 19 Current individual Harmonics 22 percentage | HAR22_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1270 | 34 | 34-26 | 11232 | Input Channel 19 Current individual Harmonics 23 percentage | HAR23_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1271 | 34 | 34-27 | 11234 | Input Channel 19 Current individual Harmonics 24 percentage | HAR24_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1272 | 34 | 34-28 | 11236 | Input Channel 19 Current individual Harmonics 25 percentage | HAR25_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1273 | 34 | 34-29 | 11238 | Input Channel 19 Current individual Harmonics 26 percentage | HAR26_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1274 | 34 | 34-30 | 11240 | Input Channel 19 Current individual Harmonics 27 percentage | HAR27_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1275 | 34 | 34-31 | 11242 | Input Channel 19 Current individual Harmonics 28 percentage | HAR28_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1276 | 34 | 34-32 | 11244 | Input Channel 19 Current individual Harmonics 29 percentage | HAR29_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1277 | 34 | 34-33 | 11246 | Input Channel 19 Current individual Harmonics 30 percentage | HAR30_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1278 | 34 | 34-34 | 11248 | Input Channel 19 Current individual Harmonics 31 percentage | HAR31_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1279 | 35 | 35-1 | 11250 | Input Channel 20 Current THD | THD_I_020_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_020_%
1280 | 35 | 35-2 | 11252 | Input Channel 20 Current THD Odd | OTHD_I_020_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_020_%
1281 | 35 | 35-3 | 11254 | Input Channel 20 Current THD Even | ETHD_I_020_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_020_%
1282 | 35 | 35-4 | 11256 | Input Channel 20 Current K Factor | KF_I_020_% | % | float32 | 22 | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_020_%
1283 | 35 | 35-5 | 11258 | Input Channel 20 Current individual Harmonics 2 percentage | HAR2_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1284 | 35 | 35-6 | 11260 | Input Channel 20 Current individual Harmonics 3 percentage | HAR3_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1285 | 35 | 35-7 | 11262 | Input Channel 20 Current individual Harmonics 4 percentage | HAR4_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1286 | 35 | 35-8 | 11264 | Input Channel 20 Current individual Harmonics 5 percentage | HAR5_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1287 | 35 | 35-9 | 11266 | Input Channel 20 Current individual Harmonics 6 percentage | HAR6_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1288 | 35 | 35-10 | 11268 | Input Channel 20 Current individual Harmonics 7 percentage | HAR7_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1289 | 35 | 35-11 | 11270 | Input Channel 20 Current individual Harmonics 8 percentage | HAR8_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1290 | 35 | 35-12 | 11272 | Input Channel 20 Current individual Harmonics 9 percentage | HAR9_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1291 | 35 | 35-13 | 11274 | Input Channel 20 Current individual Harmonics 10 percentage | HAR10_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1292 | 35 | 35-14 | 11276 | Input Channel 20 Current individual Harmonics 11 percentage | HAR11_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1293 | 35 | 35-15 | 11278 | Input Channel 20 Current individual Harmonics 12 percentage | HAR12_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1294 | 35 | 35-16 | 11280 | Input Channel 20 Current individual Harmonics 13 percentage | HAR13_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1295 | 35 | 35-17 | 11282 | Input Channel 20 Current individual Harmonics 14 percentage | HAR14_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1296 | 35 | 35-18 | 11284 | Input Channel 20 Current individual Harmonics 15 percentage | HAR15_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1297 | 35 | 35-19 | 11286 | Input Channel 20 Current individual Harmonics 16 percentage | HAR16_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1298 | 35 | 35-20 | 11288 | Input Channel 20 Current individual Harmonics 17 percentage | HAR17_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1299 | 35 | 35-21 | 11290 | Input Channel 20 Current individual Harmonics 18 percentage | HAR18_I_020 % | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1300 | 35 | 35-22 | 11292 | Input Channel 20 Current individual Harmonics 19 percentage | HAR19_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1301 | 35 | 35-23 | 11294 | Input Channel 20 Current individual Harmonics 20 percentage | HAR20_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1302 | 35 | 35-24 | 11296 | Input Channel 20 Current individual Harmonics 21 percentage | HAR21_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1303 | 35 | 35-25 | 11298 | Input Channel 20 Current individual Harmonics 22 percentage | HAR22_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1304 | 35 | 35-26 | 11300 | Input Channel 20 Current individual Harmonics 23 percentage | HAR23_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1305 | 35 | 35-27 | 11302 | Input Channel 20 Current individual Harmonics 24 percentage | HAR24_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1306 | 35 | 35-28 | 11304 | Input Channel 20 Current individual Harmonics 25 percentage | HAR25_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1307 | 35 | 35-29 | 11306 | Input Channel 20 Current individual Harmonics 26 percentage | HAR26_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1308 | 35 | 35-30 | 11308 | Input Channel 20 Current individual Harmonics 27 percentage | HAR27_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1309 | 35 | 35-31 | 11310 | Input Channel 20 Current individual Harmonics 28 percentage | HAR28_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1310 | 35 | 35-32 | 11312 | Input Channel 20 Current individual Harmonics 29 percentage | HAR29_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1311 | 35 | 35-33 | 11314 | Input Channel 20 Current individual Harmonics 30 percentage | HAR30_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1312 | 35 | 35-34 | 11316 | Input Channel 20 Current individual Harmonics 31 percentage | HAR31_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1313 | 36 | 36-1 | 11318 | Input Channel 21 Current THD | THD_I_021_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_021_%
1314 | 36 | 36-2 | 11320 | Input Channel 21 Current THD Odd | OTHD_I_021_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_021_%
1315 | 36 | 36-3 | 11322 | Input Channel 21 Current THD Even | ETHD_I_021_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_021_%
1316 | 36 | 36-4 | 11324 | Input Channel 21 Current K Factor | KF_I_021_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_021_%
1317 | 36 | 36-5 | 11326 | Input Channel 21 Current individual Harmonics 2 percentage | HAR2_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1318 | 36 | 36-6 | 11328 | Input Channel 21 Current individual Harmonics 3 percentage | HAR3_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1319 | 36 | 36-7 | 11330 | Input Channel 21 Current individual Harmonics 4 percentage | HAR4_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1320 | 36 | 36-8 | 11332 | Input Channel 21 Current individual Harmonics 5 percentage | HAR5_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1321 | 36 | 36-9 | 11334 | Input Channel 21 Current individual Harmonics 6 percentage | HAR6_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1322 | 36 | 36-10 | 11336 | Input Channel 21 Current individual Harmonics 7 percentage | HAR7_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1323 | 36 | 36-11 | 11338 | Input Channel 21 Current individual Harmonics 8 percentage | HAR8_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1324 | 36 | 36-12 | 11340 | Input Channel 21 Current individual Harmonics 9 percentage | HAR9_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1325 | 36 | 36-13 | 11342 | Input Channel 21 Current individual Harmonics 10 percentage | HAR10_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1326 | 36 | 36-14 | 11344 | Input Channel 21 Current individual Harmonics 11 percentage | HAR11_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1327 | 36 | 36-15 | 11346 | Input Channel 21 Current individual Harmonics 12 percentage | HAR12_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1328 | 36 | 36-16 | 11348 | Input Channel 21 Current individual Harmonics 13 percentage | HAR13_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1329 | 36 | 36-17 | 11350 | Input Channel 21 Current individual Harmonics 14 percentage | HAR14_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1330 | 36 | 36-18 | 11352 | Input Channel 21 Current individual Harmonics 15 percentage | HAR15_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1331 | 36 | 36-19 | 11354 | Input Channel 21 Current individual Harmonics 16 percentage | HAR16_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1332 | 36 | 36-20 | 11356 | Input Channel 21 Current individual Harmonics 17 percentage | HAR17_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1333 | 36 | 36-21 | 11358 | Input Channel 21 Current individual Harmonics 18 percentage | HAR18_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1334 | 36 | 36-22 | 11360 | Input Channel 21 Current individual Harmonics 19 percentage | HAR19_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1335 | 36 | 36-23 | 11362 | Input Channel 21 Current individual Harmonics 20 percentage | HAR20_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1336 | 36 | 36-24 | 11364 | Input Channel 21 Current individual Harmonics 21 percentage | HAR21_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1337 | 36 | 36-25 | 11366 | Input Channel 21 Current individual Harmonics 22 percentage | HAR22_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1338 | 36 | 36-26 | 11368 | Input Channel 21 Current individual Harmonics 23 percentage | HAR23_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1339 | 36 | 36-27 | 11370 | Input Channel 21 Current individual Harmonics 24 percentage | HAR24_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1340 | 36 | 36-28 | 11372 | Input Channel 21 Current individual Harmonics 25 percentage | HAR25_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1341 | 36 | 36-29 | 11374 | Input Channel 21 Current individual Harmonics 26 percentage | HAR26_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1342 | 36 | 36-30 | 11376 | Input Channel 21 Current individual Harmonics 27 percentage | HAR27_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1343 | 36 | 36-31 | 11378 | Input Channel 21 Current individual Harmonics 28 percentage | HAR28_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1344 | 36 | 36-32 | 11380 | Input Channel 21 Current individual Harmonics 29 percentage | HAR29_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1345 | 36 | 36-33 | 11382 | Input Channel 21 Current individual Harmonics 30 percentage | HAR30_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1346 | 36 | 36-34 | 11384 | Input Channel 21 Current individual Harmonics 31 percentage | HAR31_I_021_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 39
1347 | 37 | 37-1 | 11386 | Input Channel 22 Current THD | THD_I_022_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_022_%
1348 | 37 | 37-2 | 11388 | Input Channel 22 Current THD Odd | OTHD_I_022_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_022_%
1349 | 37 | 37-3 | 11390 | Input Channel 22 Current THD Even | ETHD_I_022_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_022_%
1350 | 37 | 37-4 | 11392 | Input Channel 22 Current K Factor | KF_I_022_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_022_%
1351 | 37 | 37-5 | 11394 | Input Channel 22 Current individual Harmonics 2 percentage | HAR2_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1352 | 37 | 37-6 | 11396 | Input Channel 22 Current individual Harmonics 3 percentage | HAR3_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1353 | 37 | 37-7 | 11398 | Input Channel 22 Current individual Harmonics 4 percentage | HAR4_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1354 | 37 | 37-8 | 11400 | Input Channel 22 Current individual Harmonics 5 percentage | HAR5_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1355 | 37 | 37-9 | 11402 | Input Channel 22 Current individual Harmonics 6 percentage | HAR6_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1356 | 37 | 37-10 | 11404 | Input Channel 22 Current individual Harmonics 7 percentage | HAR7_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1357 | 37 | 37-11 | 11406 | Input Channel 22 Current individual Harmonics 8 percentage | HAR8_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1358 | 37 | 37-12 | 11408 | Input Channel 22 Current individual Harmonics 9 percentage | HAR9_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1359 | 37 | 37-13 | 11410 | Input Channel 22 Current individual Harmonics 10 percentage | HAR10_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1360 | 37 | 37-14 | 11412 | Input Channel 22 Current individual Harmonics 11 percentage | HAR11_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1361 | 37 | 37-15 | 11414 | Input Channel 22 Current individual Harmonics 12 percentage | HAR12_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1362 | 37 | 37-16 | 11416 | Input Channel 22 Current individual Harmonics 13 percentage | HAR13_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1363 | 37 | 37-17 | 11418 | Input Channel 22 Current individual Harmonics 14 percentage | HAR14_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1364 | 37 | 37-18 | 11420 | Input Channel 22 Current individual Harmonics 15 percentage | HAR15_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1365 | 37 | 37-19 | 11422 | Input Channel 22 Current individual Harmonics 16 percentage | HAR16_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1366 | 37 | 37-20 | 11424 | Input Channel 22 Current individual Harmonics 17 percentage | HAR17_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1367 | 37 | 37-21 | 11426 | Input Channel 22 Current individual Harmonics 18 percentage | HAR18_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1368 | 37 | 37-22 | 11428 | Input Channel 22 Current individual Harmonics 19 percentage | HAR19_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1369 | 37 | 37-23 | 11430 | Input Channel 22 Current individual Harmonics 20 percentage | HAR20_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1370 | 37 | 37-24 | 11432 | Input Channel 22 Current individual Harmonics 21 percentage | HAR21_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1371 | 37 | 37-25 | 11434 | Input Channel 22 Current individual Harmonics 22 percentage | HAR22_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1372 | 37 | 37-26 | 11436 | Input Channel 22 Current individual Harmonics 23 percentage | HAR23_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1373 | 37 | 37-27 | 11438 | Input Channel 22 Current individual Harmonics 24 percentage | HAR24_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1374 | 37 | 37-28 | 11440 | Input Channel 22 Current individual Harmonics 25 percentage | HAR25_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1375 | 37 | 37-29 | 11442 | Input Channel 22 Current individual Harmonics 26 percentage | HAR26_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1376 | 37 | 37-30 | 11444 | Input Channel 22 Current individual Harmonics 27 percentage | HAR27_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1377 | 37 | 37-31 | 11446 | Input Channel 22 Current individual Harmonics 28 percentage | HAR28_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1378 | 37 | 37-32 | 11448 | Input Channel 22 Current individual Harmonics 29 percentage | HAR29_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1379 | 37 | 37-33 | 11450 | Input Channel 22 Current individual Harmonics 30 percentage | HAR30_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1380 | 37 | 37-34 | 11452 | Input Channel 22 Current individual Harmonics 31 percentage | HAR31_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1381 | 38 | 38-1 | 11454 | Input Channel 23 Current THD | THD_I_023_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_023_%
1382 | 38 | 38-2 | 11456 | Input Channel 23 Current THD Odd | OTHD_I_023_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_023_%
1383 | 38 | 38-3 | 11458 | Input Channel 23 Current THD Even | ETHD_I_023_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_023_%
1384 | 38 | 38-4 | 11460 | Input Channel 23 Current K Factor | KF_I_023_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_023_%
1385 | 38 | 38-5 | 11462 | Input Channel 23 Current individual Harmonics 2 percentage | HAR2_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1386 | 38 | 38-6 | 11464 | Input Channel 23 Current individual Harmonics 3 percentage | HAR3_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1387 | 38 | 38-7 | 11466 | Input Channel 23 Current individual Harmonics 4 percentage | HAR4_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1388 | 38 | 38-8 | 11468 | Input Channel 23 Current individual Harmonics 5 percentage | HAR5_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1389 | 38 | 38-9 | 11470 | Input Channel 23 Current individual Harmonics 6 percentage | HAR6_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1390 | 38 | 38-10 | 11472 | Input Channel 23 Current individual Harmonics 7 percentage | HAR7_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1391 | 38 | 38-11 | 11474 | Input Channel 23 Current individual Harmonics 8 percentage | HAR8_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1392 | 38 | 38-12 | 11476 | Input Channel 23 Current individual Harmonics 9 percentage | HAR9_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1393 | 38 | 38-13 | 11478 | Input Channel 23 Current individual Harmonics 10 percentage | HAR10_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1394 | 38 | 38-14 | 11480 | Input Channel 23 Current individual Harmonics 11 percentage | HAR11_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1395 | 38 | 38-15 | 11482 | Input Channel 23 Current individual Harmonics 12 percentage | HAR12_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1396 | 38 | 38-16 | 11484 | Input Channel 23 Current individual Harmonics 13 percentage | HAR13_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1397 | 38 | 38-17 | 11486 | Input Channel 23 Current individual Harmonics 14 percentage | HAR14_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1398 | 38 | 38-18 | 11488 | Input Channel 23 Current individual Harmonics 15 percentage | HAR15_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1399 | 38 | 38-19 | 11490 | Input Channel 23 Current individual Harmonics 16 percentage | HAR16_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1400 | 38 | 38-20 | 11492 | Input Channel 23 Current individual Harmonics 17 percentage | HAR17_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1401 | 38 | 38-21 | 11494 | Input Channel 23 Current individual Harmonics 18 percentage | HAR18_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1402 | 38 | 38-22 | 11496 | Input Channel 23 Current individual Harmonics 19 percentage | HAR19_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1403 | 38 | 38-23 | 11498 | Input Channel 23 Current individual Harmonics 20 percentage | HAR20_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1404 | 38 | 38-24 | 11500 | Input Channel 23 Current individual Harmonics 21 percentage | HAR21_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1405 | 38 | 38-25 | 11502 | Input Channel 23 Current individual Harmonics 22 percentage | HAR22_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1406 | 38 | 38-26 | 11504 | Input Channel 23 Current individual Harmonics 23 percentage | HAR23_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1407 | 38 | 38-27 | 11506 | Input Channel 23 Current individual Harmonics 24 percentage | HAR24_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1408 | 38 | 38-28 | 11508 | Input Channel 23 Current individual Harmonics 25 percentage | HAR25_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1409 | 38 | 38-29 | 11510 | Input Channel 23 Current individual Harmonics 26 percentage | HAR26_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1410 | 38 | 38-30 | 11512 | Input Channel 23 Current individual Harmonics 27 percentage | HAR27_I_023_% | % | float32 | 22 | R | 2 | 1 |  |  |  |  | 39
1411 | 38 | 38-31 | 11514 | Input Channel 23 Current individual Harmonics 28 percentage | HAR28_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1412 | 38 | 38-32 | 11516 | Input Channel 23 Current individual Harmonics 29 percentage | HAR29_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1413 | 38 | 38-33 | 11518 | Input Channel 23 Current individual Harmonics 30 percentage | HAR30_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1414 | 38 | 38-34 | 11520 | Input Channel 23 Current individual Harmonics 31 percentage | HAR31_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1415 | 39 | 39-1 | 11522 | Input Channel 24 Current THD | THD_I_024_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | THD_I_024_%
1416 | 39 | 39-2 | 11524 | Input Channel 24 Current THD Odd | OTHD_I_024_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | OTHD_I_024_%
1417 | 39 | 39-3 | 11526 | Input Channel 24 Current THD Even | ETHD_I_024_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | ETHD_I_024_%
1418 | 39 | 39-4 | 11528 | Input Channel 24 Current K Factor | KF_I_024_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14 |  | KF_I_024_%
1419 | 39 | 39-5 | 11530 | Input Channel 24 Current individual Harmonics 2 percentage | HAR2_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1420 | 39 | 39-6 | 11532 | Input Channel 24 Current individual Harmonics 3 percentage | HAR3_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1421 | 39 | 39-7 | 11534 | Input Channel 24 Current individual Harmonics 4 percentage | HAR4_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1422 | 39 | 39-8 | 11536 | Input Channel 24 Current individual Harmonics 5 percentage | HAR5_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1423 | 39 | 39-9 | 11538 | Input Channel 24 Current individual Harmonics 6 percentage | HAR6_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1424 | 39 | 39-10 | 11540 | Input Channel 24 Current individual Harmonics 7 percentage | HAR7_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1425 | 39 | 39-11 | 11542 | Input Channel 24 Current individual Harmonics 8 percentage | HAR8_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1426 | 39 | 39-12 | 11544 | Input Channel 24 Current individual Harmonics 9 percentage | HAR9_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1427 | 39 | 39-13 | 11546 | Input Channel 24 Current individual Harmonics 10 percentage | HAR10_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1428 | 39 | 39-14 | 11548 | Input Channel 24 Current individual Harmonics 11 percentage | HAR11_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1429 | 39 | 39-15 | 11550 | Input Channel 24 Current individual Harmonics 12 percentage | HAR12_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1430 | 39 | 39-16 | 11552 | Input Channel 24 Current individual Harmonics 13 percentage | HAR13_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1431 | 39 | 39-17 | 11554 | Input Channel 24 Current individual Harmonics 14 percentage | HAR14_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1432 | 39 | 39-18 | 11556 | Input Channel 24 Current individual Harmonics 15 percentage | HAR15_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1433 | 39 | 39-19 | 11558 | Input Channel 24 Current individual Harmonics 16 percentage | HAR16_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1434 | 39 | 39-20 | 11560 | Input Channel 24 Current individual Harmonics 17 percentage | HAR17_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1435 | 39 | 39-21 | 11562 | Input Channel 24 Current individual Harmonics 18 percentage | HAR18_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1436 | 39 | 39-22 | 11564 | Input Channel 24 Current individual Harmonics 19 percentage | HAR19_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1437 | 39 | 39-23 | 11566 | Input Channel 24 Current individual Harmonics 20 percentage | HAR20_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1438 | 39 | 39-24 | 11568 | Input Channel 24 Current individual Harmonics 21 percentage | HAR21_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1439 | 39 | 39-25 | 11570 | Input Channel 24 Current individual Harmonics 22 percentage | HAR22_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1440 | 39 | 39-26 | 11572 | Input Channel 24 Current individual Harmonics 23 percentage | HAR23_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1441 | 39 | 39-27 | 11574 | Input Channel 24 Current individual Harmonics 24 percentage | HAR24_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1442 | 39 | 39-28 | 11576 | Input Channel 24 Current individual Harmonics 25 percentage | HAR25_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1443 | 39 | 39-29 | 11578 | Input Channel 24 Current individual Harmonics 26 percentage | HAR26_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1444 | 39 | 39-30 | 11580 | Input Channel 24 Current individual Harmonics 27 percentage | HAR27_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1445 | 39 | 39-31 | 11582 | Input Channel 24 Current individual Harmonics 28 percentage | HAR28_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1446 | 39 | 39-32 | 11584 | Input Channel 24 Current individual Harmonics 29 percentage | HAR29_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1447 | 39 | 39-33 | 11586 | Input Channel 24 Current individual Harmonics 30 percentage | HAR30_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1448 | 39 | 39-34 | 11588 | Input Channel 24 Current individual Harmonics 31 percentage | HAR31_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  |  | 39
1449 | 40 | 40-1 | 11590 | User Channel 1 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s001 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s001
1450 | 40 | 40-2 | 11592 | User Channel 1 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s001 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s001
1451 | 40 | 40-3 | 11594 | User Channel 1 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s001 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s001
1452 | 40 | 40-4 | 11596 | User Channel 1 Current Positive Sequence Angle | ANG_SEQ_POS_I_s001 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s001
1453 | 40 | 40-5 | 11598 | User Channel 1 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s001 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s001
1454 | 40 | 40-6 | 11600 | User Channel 1 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s001 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s001
1455 | 40 | 40-7 | 11602 | User Channel 1 Current Unbalance Factor Magnitude | UNBL_I_s001_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s001_%
1456 | 40 | 40-8 | 11604 | User Channel 2 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s002 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s002
1457 | 40 | 40-9 | 11606 | User Channel 2 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s002 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s002
1458 | 40 | 40-10 | 11608 | User Channel 2 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s002 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s002
1459 | 40 | 40-11 | 11610 | User Channel 2 Current Positive Sequence Angle | ANG_SEQ_POS_I_s002 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s002
1460 | 40 | 40-12 | 11612 | User Channel 2 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s002 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s002
1461 | 40 | 40-13 | 11614 | User Channel 2 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s002 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s002
1462 | 40 | 40-14 | 11616 | User Channel 2 Current Unbalance Factor Magnitude | UNBL_I_s002_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s002_%
1463 | 40 | 40-15 | 11618 | User Channel 3 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s003 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s003
1464 | 40 | 40-16 | 11620 | User Channel 3 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s003 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s003
1465 | 40 | 40-17 | 11622 | User Channel 3 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s003 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s003
1466 | 40 | 40-18 | 11624 | User Channel 3 Current Positive Sequence Angle | ANG_SEQ_POS_I_s003 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s003
1467 | 40 | 40-19 | 11626 | User Channel 3 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s003 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s003
1468 | 40 | 40-20 | 11628 | User Channel 3 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s003 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s003
1469 | 40 | 40-21 | 11630 | User Channel 3 Current Unbalance Factor Magnitude | UNBL_I_s003_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s003_%
1470 | 40 | 40-22 | 11632 | User Channel 4 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s004 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s004
1471 | 40 | 40-23 | 11634 | User Channel 4 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s004 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s004
1472 | 40 | 40-24 | 11636 | User Channel 4 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s004 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s004
1473 | 40 | 40-25 | 11638 | User Channel 4 Current Positive Sequence Angle | ANG_SEQ_POS_I_s004 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s004
1474 | 40 | 40-26 | 11640 | User Channel 4 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s004 | A | float32 | 22 | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s004
1475 | 40 | 40-27 | 11642 | User Channel 4 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s004 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s004
1476 | 40 | 40-28 | 11644 | User Channel 4 Current Unbalance Factor Magnitude | UNBL_I_s004_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s004_%
1477 | 40 | 40-29 | 11646 | User Channel 5 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s005 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s005
1478 | 40 | 40-30 | 11648 | User Channel 5 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s005 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s005
1479 | 40 | 40-31 | 11650 | User Channel 5 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s005 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s005
1480 | 40 | 40-32 | 11652 | User Channel 5 Current Positive Sequence Angle | ANG_SEQ_POS_I_s005 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s005
1481 | 40 | 40-33 | 11654 | User Channel 5 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s005 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s005
1482 | 40 | 40-34 | 11656 | User Channel 5 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s005 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s005
1483 | 40 | 40-35 | 11658 | User Channel 5 Current Unbalance Factor Magnitude | UNBL_I_s005_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s005_%
1484 | 40 | 40-36 | 11660 | User Channel 6 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s006 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s006
1485 | 40 | 40-37 | 11662 | User Channel 6 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s006 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s006
1486 | 40 | 40-38 | 11664 | User Channel 6 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s006 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s006
1487 | 40 | 40-39 | 11666 | User Channel 6 Current Positive Sequence Angle | ANG_SEQ_POS_I_s006 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s006
1488 | 40 | 40-40 | 11668 | User Channel 6 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s006 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s006
1489 | 40 | 40-41 | 11670 | User Channel 6 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s006 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s006
1490 | 40 | 40-42 | 11672 | User Channel 6 Current Unbalance Factor Magnitude | UNBL_I_s006_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s006_%
1491 | 41 | 41-1 | 11674 | User Channel 7 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s007 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s007
1492 | 41 | 41-2 | 11676 | User Channel 7 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s007 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s007
1493 | 41 | 41-3 | 11678 | User Channel 7 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s007 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s007
1494 | 41 | 41-4 | 11680 | User Channel 7 Current Positive Sequence Angle | ANG_SEQ_POS_I_s007 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s007
1495 | 41 | 41-5 | 11682 | User Channel 7 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s007 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s007
1496 | 41 | 41-6 | 11684 | User Channel 7 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s007 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s007
1497 | 41 | 41-7 | 11686 | User Channel 7 Current Unbalance Factor Magnitude | UNBL_I_s007_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s007_%
1498 | 41 | 41-8 | 11688 | User Channel 8 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s008 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s008
1499 | 41 | 41-9 | 11690 | User Channel 8 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s008 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s008
1500 | 41 | 41-10 | 11692 | User Channel 8 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s008 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s008
1501 | 41 | 41-11 | 11694 | User Channel 8 Current Positive Sequence Angle | ANG_SEQ_POS_I_s008 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s008
1502 | 41 | 41-12 | 11696 | User Channel 8 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s008 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s008
1503 | 41 | 41-13 | 11698 | User Channel 8 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s008 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s008
1504 | 41 | 41-14 | 11700 | User Channel 8 Current Unbalance Factor Magnitude | UNBL_I_s008_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s008_%
1505 | 41 | 41-15 | 11702 | User Channel 9 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s009 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s009
1506 | 41 | 41-16 | 11704 | User Channel 9 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s009 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s009
1507 | 41 | 41-17 | 11706 | User Channel 9 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s009 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s009
1508 | 41 | 41-18 | 11708 | User Channel 9 Current Positive Sequence Angle | ANG_SEQ_POS_I_s009 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s009
1509 | 41 | 41-19 | 11710 | User Channel 9 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s009 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s009
1510 | 41 | 41-20 | 11712 | User Channel 9 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s009 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s009
1511 | 41 | 41-21 | 11714 | User Channel 9 Current Unbalance Factor Magnitude | UNBL_I_s009_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s009_%
1512 | 41 | 41-22 | 11716 | User Channel 10 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s010 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s010
1513 | 41 | 41-23 | 11718 | User Channel 10 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s010 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s010
1514 | 41 | 41-24 | 11720 | User Channel 10 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s010 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s010
1515 | 41 | 41-25 | 11722 | User Channel 10 Current Positive Sequence Angle | ANG_SEQ_POS_I_s010 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s010
1516 | 41 | 41-26 | 11724 | User Channel 10 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s010 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s010
1517 | 41 | 41-27 | 11726 | User Channel 10 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s010 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s010
1518 | 41 | 41-28 | 11728 | User Channel 10 Current Unbalance Factor Magnitude | UNBL_I_s010_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s010_%
1519 | 41 | 41-29 | 11730 | User Channel 11 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s011 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s011
1520 | 41 | 41-30 | 11732 | User Channel 11 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s011 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s011
1521 | 41 | 41-31 | 11734 | User Channel 11 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s011 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s011
1522 | 41 | 41-32 | 11736 | User Channel 11 Current Positive Sequence Angle | ANG_SEQ_POS_I_s011 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s011
1523 | 41 | 41-33 | 11738 | User Channel 11 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s011 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s011
1524 | 41 | 41-34 | 11740 | User Channel 11 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s011 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s011
1525 | 41 | 41-35 | 11742 | User Channel 11 Current Unbalance Factor Magnitude | UNBL_I_s011_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s011_%
1526 | 41 | 41-36 | 11744 | User Channel 12 Current Positive Sequence Magnitude | MAG_SEQ_POS_I_s012 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_POS_I_s012
1527 | 41 | 41-37 | 11746 | User Channel 12 Current Zero Sequence Magnitude | MAG_SEQ_ZERO_I_s012 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_ZERO_I_s012
1528 | 41 | 41-38 | 11748 | User Channel 12 Current Negative Sequence Magnitude | MAG_SEQ_NEG_I_s012 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | MAG_SEQ_NEG_I_s012
1529 | 41 | 41-39 | 11750 | User Channel 12 Current Positive Sequence Angle | ANG_SEQ_POS_I_s012 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_POS_I_s012
1530 | 41 | 41-40 | 11752 | User Channel 12 Current Zero Sequence Angle | ANG_SEQ_ZERO_I_s012 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_ZERO_I_s012
1531 | 41 | 41-41 | 11754 | User Channel 12 Current Negative Sequence Angle | ANG_SEQ_NEG_I_s012 | A | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | ANG_SEQ_NEG_I_s012
1532 | 41 | 41-42 | 11756 | User Channel 12 Current Unbalance Factor Magnitude | UNBL_I_s012_% | % | float32 |  | R | 2 | 1 |  | 4 |  | 4-7-8-42 | 14-37 |  | UNBL_I_s012_%
1533 | 42 | 42-1 | 12288 | Phase A active energy import | EP_IMP_a_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_IMP_a_kWh
1534 | 42 | 42-2 | 12292 | Phase A active energy export | EP_EXP_a_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_EXP_a_kWh
1535 | 42 | 42-3 | 12296 | Phase A active energy net | EP_NET_a_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_NET_a_kWh
1536 | 42 | 42-4 | 12300 | Phase A active energy total | EP_TOTAL_a_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_TOTAL_a_kWh
1537 | 42 | 42-5 | 12304 | Phase A reactive energy import | EQ_IMP_a_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_IMP_a_kvarh
1538 | 42 | 42-6 | 12308 | Phase A reactive energy export | EQ_EXP_a_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_EXP_a_kvarh
1539 | 42 | 42-7 | 12312 | Phase A reactive energy net | EQ_NET_a_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_NET_a_kvarh
1540 | 42 | 42-8 | 12316 | Phase A reactive energy total | EQ_TOTAL_a_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_TOTAL_a_kvarh
1541 | 42 | 42-9 | 12320 | Phase A apparent energy | ES_a_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | ES_a_kVAh
1542 | 42 | 42-10 | 12324 | Phase B active energy import | EP_IMP_b_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_IMP_b_kWh
1543 | 42 | 42-11 | 12328 | Phase B active energy export | EP_EXP_b_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_EXP_b_kWh
1544 | 42 | 42-12 | 12332 | Phase B active energy net | EP_NET_b_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_NET_b_kWh
1545 | 42 | 42-13 | 12336 | Phase B active energy total | EP_TOTAL_b_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_TOTAL_b_kWh
1546 | 42 | 42-14 | 12340 | Phase B reactive energy import | EQ_IMP_b_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_IMP_b_kvarh
1547 | 42 | 42-15 | 12344 | Phase B reactive energy export | EQ_EXP_b_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_EXP_b_kvarh
1548 | 42 | 42-16 | 12348 | Phase B reactive energy net | EQ_NET_b_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_NET_b_kvarh
1549 | 42 | 42-17 | 12352 | Phase B reactive energy total | EQ_TOTAL_b_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_TOTAL_b_kvarh
1550 | 42 | 42-18 | 12356 | Phase B apparent energy | ES_b_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | ES_b_kVAh
1551 | 42 | 42-19 | 12360 | Phase C active energy import | EP_IMP_c_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_IMP_c_kWh
1552 | 42 | 42-20 | 12364 | Phase C active energy export | EP_EXP_c_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_EXP_c_kWh
1553 | 42 | 42-21 | 12368 | Phase C active energy net | EP_NET_c_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_NET_c_kWh
1554 | 42 | 42-22 | 12372 | Phase C active energy total | EP_TOTAL_c_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EP_TOTAL_c_kWh
1555 | 42 | 42-23 | 12376 | Phase C reactive energy import | EQ_IMP_c_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_IMP_c_kvarh
1556 | 42 | 42-24 | 12380 | Phase C reactive energy export | EQ_EXP_c_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_EXP_c_kvarh
1557 | 42 | 42-25 | 12384 | Phase C reactive energy net | EQ_NET_c_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_NET_c_kvarh
1558 | 42 | 42-26 | 12388 | Phase C reactive energy total | EQ_TOTAL_c_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | EQ_TOTAL_c_kvarh
1559 | 42 | 42-27 | 12392 | Phase C apparent energy | ES_c_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1-26 |  | ES_c_kVAh
1560 | 42 | 42-28 | 12396 | System active energy import | EP_IMP_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1 |  | EP_IMP_kWh
1561 | 42 | 42-29 | 12400 | System active energy export | EP_EXP_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1 |  | EP_EXP_kWh
1562 | 42 | 42-30 | 12404 | System active energy net | EP_NET_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1 |  | EP_NET_kWh
1563 | 42 | 42-31 | 12408 | System active energy total | EP_TOTAL_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1 |  | EP_TOTAL_kWh
1564 | 43 | 43-1 | 12412 | System reactive energy import | EQ_IMP_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1 |  | EQ_IMP_kvarh
1565 | 43 | 43-2 | 12416 | System reactive energy export | EQ_EXP_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1 |  | EQ_EXP_kvarh
1566 | 43 | 43-3 | 12420 | System reactive energy net | EQ_NET_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1 |  | EQ_NET_kvarh
1567 | 43 | 43-4 | 12424 | System reactive energy total | EQ_TOTAL_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1 |  | EQ_TOTAL_kvarh
1568 | 43 | 43-5 | 12428 | System apparent energy | ES_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 11-3-1 |  | ES_kVAh
1569 | 43 | 43-6 | 12432 | Input Channel 1 active energy import | EP_IMP_001_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_001_kWh
1570 | 43 | 43-7 | 12436 | Input Channel 1 active energy export | EP_EXP_001_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_001_kWh
1571 | 43 | 43-8 | 12440 | Input Channel 1 active energy net | EP_NET_001_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_001_kWh
1572 | 43 | 43-9 | 12444 | Input Channel 1 active energy total | EP_TOTAL_001_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_001_kWh
1573 | 43 | 43-10 | 12448 | Input Channel 1 reactive energy import | EQ_IMP_001_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_001_kvarh
1574 | 43 | 43-11 | 12452 | Input Channel 1 reactive energy export | EQ_EXP_001_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_001_kvarh
1575 | 43 | 43-12 | 12456 | Input Channel 1 reactive energy net | EQ_NET_001_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_001_kvarh
1576 | 43 | 43-13 | 12460 | Input Channel 1 reactive energy total | EQ_TOTAL_001_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_001_kvarh
1577 | 43 | 43-14 | 12464 | Input Channel 1 apparent energy | ES_001_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_001_kVAh
1578 | 43 | 43-15 | 12468 | Input Channel 2 active energy import | EP_IMP_002_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_002_kWh
1579 | 43 | 43-16 | 12472 | Input Channel 2 active energy export | EP_EXP_002_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_002_kWh
1580 | 43 | 43-17 | 12476 | Input Channel 2 active energy net | EP_NET_002_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_002_kWh
1581 | 43 | 43-18 | 12480 | Input Channel 2 active energy total | EP_TOTAL_002_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_002_kWh
1582 | 43 | 43-19 | 12484 | Input Channel 2 reactive energy import | EQ_IMP_002_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_002_kvarh
1583 | 43 | 43-20 | 12488 | Input Channel 2 reactive energy export | EQ_EXP_002_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_002_kvarh
1584 | 43 | 43-21 | 12492 | Input Channel 2 reactive energy net | EQ_NET_002_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_002_kvarh
1585 | 43 | 43-22 | 12496 | Input Channel 2 reactive energy total | EQ_TOTAL_002_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_002_kvarh
1586 | 43 | 43-23 | 12500 | Input Channel 2 apparent energy | ES_002_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_002_kVAh
1587 | 43 | 43-24 | 12504 | Input Channel 3 active energy import | EP_IMP_003_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_003_kWh
1588 | 43 | 43-25 | 12508 | Input Channel 3 active energy export | EP_EXP_003_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_003_kWh
1589 | 43 | 43-26 | 12512 | Input Channel 3 active energy net | EP_NET_003_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_003_kWh
1590 | 43 | 43-27 | 12516 | Input Channel 3 active energy total | EP_TOTAL_003_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_003_kWh
1591 | 43 | 43-28 | 12520 | Input Channel 3 reactive energy import | EQ_IMP_003_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_003_kvarh
1592 | 43 | 43-29 | 12524 | Input Channel 3 reactive energy export | EQ_EXP_003_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_003_kvarh
1593 | 43 | 43-30 | 12528 | Input Channel 3 reactive energy net | EQ_NET_003_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_003_kvarh
1594 | 43 | 43-31 | 12532 | Input Channel 3 reactive energy total | EQ_TOTAL_003_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_003_kvarh
1595 | 44 | 44-1 | 12536 | Input Channel 3 apparent energy | ES_003_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_003_kVAh
1596 | 44 | 44-2 | 12540 | Input Channel 4 active energy import | EP_IMP_004_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_004_kWh
1597 | 44 | 44-3 | 12544 | Input Channel 4 active energy export | EP_EXP_004_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_004_kWh
1598 | 44 | 44-4 | 12548 | Input Channel 4 active energy net | EP_NET_004_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_004_kWh
1599 | 44 | 44-5 | 12552 | Input Channel 4 active energy total | EP_TOTAL_004_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_004_kWh
1600 | 44 | 44-6 | 12556 | Input Channel 4 reactive energy import | EQ_IMP_004_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_004_kvarh
1601 | 44 | 44-7 | 12560 | Input Channel 4 reactive energy export | EQ_EXP_004_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_004_kvarh
1602 | 44 | 44-8 | 12564 | Input Channel 4 reactive energy net | EQ_NET_004_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_004_kvarh
1603 | 44 | 44-9 | 12568 | Input Channel 4 reactive energy total | EQ_TOTAL_004_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_004_kvarh
1604 | 44 | 44-10 | 12572 | Input Channel 4 apparent energy | ES_004_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_004_kVAh
1605 | 44 | 44-11 | 12576 | Input Channel 5 active energy import | EP_IMP_005_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_005_kWh
1606 | 44 | 44-12 | 12580 | Input Channel 5 active energy export | EP_EXP_005_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_005_kWh
1607 | 44 | 44-13 | 12584 | Input Channel 5 active energy net | EP_NET_005_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_005_kWh
1608 | 44 | 44-14 | 12588 | Input Channel 5 active energy total | EP_TOTAL_005_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_005_kWh
1609 | 44 | 44-15 | 12592 | Input Channel 5 reactive energy import | EQ_IMP_005_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_005_kvarh
1610 | 44 | 44-16 | 12596 | Input Channel 5 reactive energy export | EQ_EXP_005_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_005_kvarh
1611 | 44 | 44-17 | 12600 | Input Channel 5 reactive energy net | EQ_NET_005_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_005_kvarh
1612 | 44 | 44-18 | 12604 | Input Channel 5 reactive energy total | EQ_TOTAL_005_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_005_kvarh
1613 | 44 | 44-19 | 12608 | Input Channel 5 apparent energy | ES_005_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_005_kVAh
1614 | 44 | 44-20 | 12612 | Input Channel 6 active energy import | EP_IMP_006_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_006_kWh
1615 | 44 | 44-21 | 12616 | Input Channel 6 active energy export | EP_EXP_006_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_006_kWh
1616 | 44 | 44-22 | 12620 | Input Channel 6 active energy net | EP_NET_006_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_006_kWh
1617 | 44 | 44-23 | 12624 | Input Channel 6 active energy total | EP_TOTAL_006_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_006_kWh
1618 | 44 | 44-24 | 12628 | Input Channel 6 reactive energy import | EQ_IMP_006_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_006_kvarh
1619 | 44 | 44-25 | 12632 | Input Channel 6 reactive energy export | EQ_EXP_006_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_006_kvarh
1620 | 44 | 44-26 | 12636 | Input Channel 6 reactive energy net | EQ_NET_006_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_006_kvarh
1621 | 44 | 44-27 | 12640 | Input Channel 6 reactive energy total | EQ_TOTAL_006_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_006_kvarh
1622 | 44 | 44-28 | 12644 | Input Channel 6 apparent energy | ES_006_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_006_kVAh
1623 | 44 | 44-29 | 12648 | Input Channel 7 active energy import | EP_IMP_007_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_007_kWh
1624 | 44 | 44-30 | 12652 | Input Channel 7 active energy export | EP_EXP_007_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_007_kWh
1625 | 44 | 44-31 | 12656 | Input Channel 7 active energy net | EP_NET_007_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_007_kWh
1626 | 45 | 45-1 | 12660 | Input Channel 7 active energy total | EP_TOTAL_007_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_007_kWh
1627 | 45 | 45-2 | 12664 | Input Channel 7 reactive energy import | EQ_IMP_007_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_007_kvarh
1628 | 45 | 45-3 | 12668 | Input Channel 7 reactive energy export | EQ_EXP_007_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_007_kvarh
1629 | 45 | 45-4 | 12672 | Input Channel 7 reactive energy net | EQ_NET_007_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_007_kvarh
1630 | 45 | 45-5 | 12676 | Input Channel 7 reactive energy total | EQ_TOTAL_007_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_007_kvarh
1631 | 45 | 45-6 | 12680 | Input Channel 7 apparent energy | ES_007_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_007_kVAh
1632 | 45 | 45-7 | 12684 | Input Channel 8 active energy import | EP_IMP_008_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_008_kWh
1633 | 45 | 45-8 | 12688 | Input Channel 8 active energy export | EP_EXP_008_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_008_kWh
1634 | 45 | 45-9 | 12692 | Input Channel 8 active energy net | EP_NET_008_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_008_kWh
1635 | 45 | 45-10 | 12696 | Input Channel 8 active energy total | EP_TOTAL_008_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_008_kWh
1636 | 45 | 45-11 | 12700 | Input Channel 8 reactive energy import | EQ_IMP_008_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_008_kvarh
1637 | 45 | 45-12 | 12704 | Input Channel 8 reactive energy export | EQ_EXP_008_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_008_kvarh
1638 | 45 | 45-13 | 12708 | Input Channel 8 reactive energy net | EQ_NET_008_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_008_kvarh
1639 | 45 | 45-14 | 12712 | Input Channel 8 reactive energy total | EQ_TOTAL_008_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_008_kvarh
1640 | 45 | 45-15 | 12716 | Input Channel 8 apparent energy | ES_008_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_008_kVAh
1641 | 45 | 45-16 | 12720 | Input Channel 9 active energy import | EP_IMP_009_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_009_kWh
1642 | 45 | 45-17 | 12724 | Input Channel 9 active energy export | EP_EXP_009_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_009_kWh
1643 | 45 | 45-18 | 12728 | Input Channel 9 active energy net | EP_NET_009_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_009_kWh
1644 | 45 | 45-19 | 12732 | Input Channel 9 active energy total | EP_TOTAL_009_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_009_kWh
1645 | 45 | 45-20 | 12736 | Input Channel 9 reactive energy import | EQ_IMP_009_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_009_kvarh
1646 | 45 | 45-21 | 12740 | Input Channel 9 reactive energy export | EQ_EXP_009_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_009_kvarh
1647 | 45 | 45-22 | 12744 | Input Channel 9 reactive energy net | EQ_NET_009_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_009_kvarh
1648 | 45 | 45-23 | 12748 | Input Channel 9 reactive energy total | EQ_TOTAL_009_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_009_kvarh
1649 | 45 | 45-24 | 12752 | Input Channel 9 apparent energy | ES_009_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_009_kVAh
1650 | 45 | 45-25 | 12756 | Input Channel 10 active energy import | EP_IMP_010_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_010_kWh
1651 | 45 | 45-26 | 12760 | Input Channel 10 active energy export | EP_EXP_010_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_010_kWh
1652 | 45 | 45-27 | 12764 | Input Channel 10 active energy net | EP_NET_010_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_010_kWh
1653 | 45 | 45-28 | 12768 | Input Channel 10 active energy total | EP_TOTAL_010_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_010_kWh
1654 | 45 | 45-29 | 12772 | Input Channel 10 reactive energy import | EQ_IMP_010_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_010_kvarh
1655 | 45 | 45-30 | 12776 | Input Channel 10 reactive energy export | EQ_EXP_010_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_010_kvarh
1656 | 45 | 45-31 | 12780 | Input Channel 10 reactive energy net | EQ_NET_010_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_010_kvarh
1657 | 46 | 46-1 | 12784 | Input Channel 10 reactive energy total | EQ_TOTAL_010_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_010_kvarh
1658 | 46 | 46-2 | 12788 | Input Channel 10 apparent energy | ES_010_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_010_kVAh
1659 | 46 | 46-3 | 12792 | Input Channel 11 active energy import | EP_IMP_011_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_011_kWh
1660 | 46 | 46-4 | 12796 | Input Channel 11 active energy export | EP_EXP_011_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_011_kWh
1661 | 46 | 46-5 | 12800 | Input Channel 11 active energy net | EP_NET_011_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_011_kWh
1662 | 46 | 46-6 | 12804 | Input Channel 11 active energy total | EP_TOTAL_011_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_011_kWh
1663 | 46 | 46-7 | 12808 | Input Channel 11 reactive energy import | EQ_IMP_011_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_011_kvarh
1664 | 46 | 46-8 | 12812 | Input Channel 11 reactive energy export | EQ_EXP_011_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_011_kvarh
1665 | 46 | 46-9 | 12816 | Input Channel 11 reactive energy net | EQ_NET_011_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_011_kvarh
1666 | 46 | 46-10 | 12820 | Input Channel 11 reactive energy total | EQ_TOTAL_011_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_011_kvarh
1667 | 46 | 46-11 | 12824 | Input Channel 11 apparent energy | ES_011_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_011_kVAh
1668 | 46 | 46-12 | 12828 | Input Channel 12 active energy import | EP_IMP_012_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_012_kWh
1669 | 46 | 46-13 | 12832 | Input Channel 12 active energy export | EP_EXP_012_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_012_kWh
1670 | 46 | 46-14 | 12836 | Input Channel 12 active energy net | EP_NET_012_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_012_kWh
1671 | 46 | 46-15 | 12840 | Input Channel 12 active energy total | EP_TOTAL_012_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_012_kWh
1672 | 46 | 46-16 | 12844 | Input Channel 12 reactive energy import | EQ_IMP_012_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_012_kvarh
1673 | 46 | 46-17 | 12848 | Input Channel 12 reactive energy export | EQ_EXP_012_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_012_kvarh
1674 | 46 | 46-18 | 12852 | Input Channel 12 reactive energy net | EQ_NET_012_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_012_kvarh
1675 | 46 | 46-19 | 12856 | Input Channel 12 reactive energy total | EQ_TOTAL_012_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_012_kvarh
1676 | 46 | 46-20 | 12860 | Input Channel 12 apparent energy | ES_012_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_012_kVAh
1677 | 46 | 46-21 | 12864 | Input Channel 13 active energy import | EP_IMP_013_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_013_kWh
1678 | 46 | 46-22 | 12868 | Input Channel 13 active energy export | EP_EXP_013_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_013_kWh
1679 | 46 | 46-23 | 12872 | Input Channel 13 active energy net | EP_NET_013_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_013_kWh
1680 | 46 | 46-24 | 12876 | Input Channel 13 active energy total | EP_TOTAL_013_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_013_kWh
1681 | 46 | 46-25 | 12880 | Input Channel 13 reactive energy import | EQ_IMP_013_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_013_kvarh
1682 | 46 | 46-26 | 12884 | Input Channel 13 reactive energy export | EQ_EXP_013_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_013_kvarh
1683 | 46 | 46-27 | 12888 | Input Channel 13 reactive energy net | EQ_NET_013_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_013_kvarh
1684 | 46 | 46-28 | 12892 | Input Channel 13 reactive energy total | EQ_TOTAL_013_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_013_kvarh
1685 | 46 | 46-29 | 12896 | Input Channel 13 apparent energy | ES_013_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_013_kVAh
1686 | 46 | 46-30 | 12900 | Input Channel 14 active energy import | EP_IMP_014_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_014_kWh
1687 | 46 | 46-31 | 12904 | Input Channel 14 active energy export | EP_EXP_014_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_014_kWh
1688 | 47 | 47-1 | 12908 | Input Channel 14 active energy net | EP_NET_014_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_014_kWh
1689 | 47 | 47-2 | 12912 | Input Channel 14 active energy total | EP_TOTAL_014_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_014_kWh
1690 | 47 | 47-3 | 12916 | Input Channel 14 reactive energy import | EQ_IMP_014_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_014_kvarh
1691 | 47 | 47-4 | 12920 | Input Channel 14 reactive energy export | EQ_EXP_014_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_014_kvarh
1692 | 47 | 47-5 | 12924 | Input Channel 14 reactive energy net | EQ_NET_014_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_014_kvarh
1693 | 47 | 47-6 | 12928 | Input Channel 14 reactive energy total | EQ_TOTAL_014_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_014_kvarh
1694 | 47 | 47-7 | 12932 | Input Channel 14 apparent energy | ES_014_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_014_kVAh
1695 | 47 | 47-8 | 12936 | Input Channel 15 active energy import | EP_IMP_015_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_015_kWh
1696 | 47 | 47-9 | 12940 | Input Channel 15 active energy export | EP_EXP_015_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_015_kWh
1697 | 47 | 47-10 | 12944 | Input Channel 15 active energy net | EP_NET_015_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_015_kWh
1698 | 47 | 47-11 | 12948 | Input Channel 15 active energy total | EP_TOTAL_015_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_015_kWh
1699 | 47 | 47-12 | 12952 | Input Channel 15 reactive energy import | EQ_IMP_015_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_015_kvarh
1700 | 47 | 47-13 | 12956 | Input Channel 15 reactive energy export | EQ_EXP_015_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_015_kvarh
1701 | 47 | 47-14 | 12960 | Input Channel 15 reactive energy net | EQ_NET_015_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_015_kvarh
1702 | 47 | 47-15 | 12964 | Input Channel 15 reactive energy total | EQ_TOTAL_015_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_015_kvarh
1703 | 47 | 47-16 | 12968 | Input Channel 15 apparent energy | ES_015_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_015_kVAh
1704 | 47 | 47-17 | 12972 | Input Channel 16 active energy import | EP_IMP_016_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_016_kWh
1705 | 47 | 47-18 | 12976 | Input Channel 16 active energy export | EP_EXP_016_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_016_kWh
1706 | 47 | 47-19 | 12980 | Input Channel 16 active energy net | EP_NET_016_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_016_kWh
1707 | 47 | 47-20 | 12984 | Input Channel 16 active energy total | EP_TOTAL_016_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_016_kWh
1708 | 47 | 47-21 | 12988 | Input Channel 16 reactive energy import | EQ_IMP_016_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_016_kvarh
1709 | 47 | 47-22 | 12992 | Input Channel 16 reactive energy export | EQ_EXP_016_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_016_kvarh
1710 | 47 | 47-23 | 12996 | Input Channel 16 reactive energy net | EQ_NET_016_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_016_kvarh
1711 | 47 | 47-24 | 13000 | Input Channel 16 reactive energy total | EQ_TOTAL_016_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_016_kvarh
1712 | 47 | 47-25 | 13004 | Input Channel 16 apparent energy | ES_016_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_016_kVAh
1713 | 47 | 47-26 | 13008 | Input Channel 17 active energy import | EP_IMP_017_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_017_kWh
1714 | 47 | 47-27 | 13012 | Input Channel 17 active energy export | EP_EXP_017_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_017_kWh
1715 | 47 | 47-28 | 13016 | Input Channel 17 active energy net | EP_NET_017_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_017_kWh
1716 | 47 | 47-29 | 13020 | Input Channel 17 active energy total | EP_TOTAL_017_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_017_kWh
1717 | 47 | 47-30 | 13024 | Input Channel 17 reactive energy import | EQ_IMP_017_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_017_kvarh
1718 | 47 | 47-31 | 13028 | Input Channel 17 reactive energy export | EQ_EXP_017_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_017_kvarh
1719 | 48 | 48-1 | 13032 | Input Channel 17 reactive energy net | EQ_NET_017_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_017_kvarh
1720 | 48 | 48-2 | 13036 | Input Channel 17 reactive energy total | EQ_TOTAL_017_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_017_kvarh
1721 | 48 | 48-3 | 13040 | Input Channel 17 apparent energy | ES_017_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_017_kVAh
1722 | 48 | 48-4 | 13044 | Input Channel 18 active energy import | EP_IMP_018_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_018_kWh
1723 | 48 | 48-5 | 13048 | Input Channel 18 active energy export | EP_EXP_018_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_018_kWh
1724 | 48 | 48-6 | 13052 | Input Channel 18 active energy net | EP_NET_018_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_018_kWh
1725 | 48 | 48-7 | 13056 | Input Channel 18 active energy total | EP_TOTAL_018_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_018_kWh
1726 | 48 | 48-8 | 13060 | Input Channel 18 reactive energy import | EQ_IMP_018_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_018_kvarh
1727 | 48 | 48-9 | 13064 | Input Channel 18 reactive energy export | EQ_EXP_018_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_018_kvarh
1728 | 48 | 48-10 | 13068 | Input Channel 18 reactive energy net | EQ_NET_018_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_018_kvarh
1729 | 48 | 48-11 | 13072 | Input Channel 18 reactive energy total | EQ_TOTAL_018_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_018_kvarh
1730 | 48 | 48-12 | 13076 | Input Channel 18 apparent energy | ES_018_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_018_kVAh
1731 | 48 | 48-13 | 13080 | Input Channel 19 active energy import | EP_IMP_019_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_019_kWh
1732 | 48 | 48-14 | 13084 | Input Channel 19 active energy export | EP_EXP_019_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_019_kWh
1733 | 48 | 48-15 | 13088 | Input Channel 19 active energy net | EP_NET_019_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_019_kWh
1734 | 48 | 48-16 | 13092 | Input Channel 19 active energy total | EP_TOTAL_019_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_019_kWh
1735 | 48 | 48-17 | 13096 | Input Channel 19 reactive energy import | EQ_IMP_019_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_019_kvarh
1736 | 48 | 48-18 | 13100 | Input Channel 19 reactive energy export | EQ_EXP_019_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_019_kvarh
1737 | 48 | 48-19 | 13104 | Input Channel 19 reactive energy net | EQ_NET_019_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_019_kvarh
1738 | 48 | 48-20 | 13108 | Input Channel 19 reactive energy total | EQ_TOTAL_019_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_019_kvarh
1739 | 48 | 48-21 | 13112 | Input Channel 19 apparent energy | ES_019_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_019_kVAh
1740 | 48 | 48-22 | 13116 | Input Channel 20 active energy import | EP_IMP_020_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_020_kWh
1741 | 48 | 48-23 | 13120 | Input Channel 20 active energy export | EP_EXP_020_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_020_kWh
1742 | 48 | 48-24 | 13124 | Input Channel 20 active energy net | EP_NET_020_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_020_kWh
1743 | 48 | 48-25 | 13128 | Input Channel 20 active energy total | EP_TOTAL_020_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_020_kWh
1744 | 48 | 48-26 | 13132 | Input Channel 20 reactive energy import | EQ_IMP_020_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_020_kvarh
1745 | 48 | 48-27 | 13136 | Input Channel 20 reactive energy export | EQ_EXP_020_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_020_kvarh
1746 | 48 | 48-28 | 13140 | Input Channel 20 reactive energy net | EQ_NET_020_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_020_kvarh
1747 | 48 | 48-29 | 13144 | Input Channel 20 reactive energy total | EQ_TOTAL_020_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_020_kvarh
1748 | 48 | 48-30 | 13148 | Input Channel 20 apparent energy | ES_020_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_020_kVAh
1749 | 48 | 48-31 | 13152 | Input Channel 21 active energy import | EP_IMP_021_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_021_kWh
1750 | 49 | 49-1 | 13156 | Input Channel 21 active energy export | EP_EXP_021_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_021_kWh
1751 | 49 | 49-2 | 13160 | Input Channel 21 active energy net | EP_NET_021_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_021_kWh
1752 | 49 | 49-3 | 13164 | Input Channel 21 active energy total | EP_TOTAL_021_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_021_kWh
1753 | 49 | 49-4 | 13168 | Input Channel 21 reactive energy import | EQ_IMP_021_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_021_kvarh
1754 | 49 | 49-5 | 13172 | Input Channel 21 reactive energy export | EQ_EXP_021_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_021_kvarh
1755 | 49 | 49-6 | 13176 | Input Channel 21 reactive energy net | EQ_NET_021_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_021_kvarh
1756 | 49 | 49-7 | 13180 | Input Channel 21 reactive energy total | EQ_TOTAL_021_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_021_kvarh
1757 | 49 | 49-8 | 13184 | Input Channel 21 apparent energy | ES_021_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_021_kVAh
1758 | 49 | 49-9 | 13188 | Input Channel 22 active energy import | EP_IMP_022_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_022_kWh
1759 | 49 | 49-10 | 13192 | Input Channel 22 active energy export | EP_EXP_022_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_022_kWh
1760 | 49 | 49-11 | 13196 | Input Channel 22 active energy net | EP_NET_022_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_022_kWh
1761 | 49 | 49-12 | 13200 | Input Channel 22 active energy total | EP_TOTAL_022_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_022_kWh
1762 | 49 | 49-13 | 13204 | Input Channel 22 reactive energy import | EQ_IMP_022_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_022_kvarh
1763 | 49 | 49-14 | 13208 | Input Channel 22 reactive energy export | EQ_EXP_022_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_022_kvarh
1764 | 49 | 49-15 | 13212 | Input Channel 22 reactive energy net | EQ_NET_022_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_022_kvarh
1765 | 49 | 49-16 | 13216 | Input Channel 22 reactive energy total | EQ_TOTAL_022_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_022_kvarh
1766 | 49 | 49-17 | 13220 | Input Channel 22 apparent energy | ES_022_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_022_kVAh
1767 | 49 | 49-18 | 13224 | Input Channel 23 active energy import | EP_IMP_023_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_023_kWh
1768 | 49 | 49-19 | 13228 | Input Channel 23 active energy export | EP_EXP_023_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_023_kWh
1769 | 49 | 49-20 | 13232 | Input Channel 23 active energy net | EP_NET_023_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_023_kWh
1770 | 49 | 49-21 | 13236 | Input Channel 23 active energy total | EP_TOTAL_023_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_023_kWh
1771 | 49 | 49-22 | 13240 | Input Channel 23 reactive energy import | EQ_IMP_023_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_023_kvarh
1772 | 49 | 49-23 | 13244 | Input Channel 23 reactive energy export | EQ_EXP_023_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_023_kvarh
1773 | 49 | 49-24 | 13248 | Input Channel 23 reactive energy net | EQ_NET_023_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_023_kvarh
1774 | 49 | 49-25 | 13252 | Input Channel 23 reactive energy total | EQ_TOTAL_023_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_023_kvarh
1775 | 49 | 49-26 | 13256 | Input Channel 23 apparent energy | ES_023_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_023_kVAh
1776 | 49 | 49-27 | 13260 | Input Channel 24 active energy import | EP_IMP_024_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_024_kWh
1777 | 49 | 49-28 | 13264 | Input Channel 24 active energy export | EP_EXP_024_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_024_kWh
1778 | 49 | 49-29 | 13268 | Input Channel 24 active energy net | EP_NET_024_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_024_kWh
1779 | 49 | 49-30 | 13272 | Input Channel 24 active energy total | EP_TOTAL_024_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_024_kWh
1780 | 49 | 49-31 | 13276 | Input Channel 24 reactive energy import | EQ_IMP_024_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_024_kvarh
1781 | 50 | 50-1 | 13280 | Input Channel 24 reactive energy export | EQ_EXP_024_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_024_kvarh
1782 | 50 | 50-2 | 13284 | Input Channel 24 reactive energy net | EQ_NET_024_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_024_kvarh
1783 | 50 | 50-3 | 13288 | Input Channel 24 reactive energy total | EQ_TOTAL_024_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_024_kvarh
1784 | 50 | 50-4 | 13292 | Input Channel 24 apparent energy | ES_024_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_024_kVAh
1785 | 50 | 50-5 | 13296 | User Channel 1 active energy import | EP_IMP_s001_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s001_kWh
1786 | 50 | 50-6 | 13300 | User Channel 1 active energy export | EP_EXP_s001_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s001_kWh
1787 | 50 | 50-7 | 13304 | User Channel 1 active energy net | EP_NET_s001_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s001_kWh
1788 | 50 | 50-8 | 13308 | User Channel 1 active energy total | EP_TOTAL_s001_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s001_kWh
1789 | 50 | 50-9 | 13312 | User Channel 1 reactive energy import | EQ_IMP_s001_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s001_kvarh
1790 | 50 | 50-10 | 13316 | User Channel 1 reactive energy export | EQ_EXP_s001_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s001_kvarh
1791 | 50 | 50-11 | 13320 | User Channel 1 reactive energy net | EQ_NET_s001_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s001_kvarh
1792 | 50 | 50-12 | 13324 | User Channel 1 reactive energy total | EQ_TOTAL_s001_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s001_kvarh
1793 | 50 | 50-13 | 13328 | User Channel 1 apparent energy | ES_s001_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s001_kVAh
1794 | 50 | 50-14 | 13332 | User Channel 2 active energy import | EP_IMP_s002_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s002_kWh
1795 | 50 | 50-15 | 13336 | User Channel 2 active energy export | EP_EXP_s002_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s002_kWh
1796 | 50 | 50-16 | 13340 | User Channel 2 active energy net | EP_NET_s002_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s002_kWh
1797 | 50 | 50-17 | 13344 | User Channel 2 active energy total | EP_TOTAL_s002_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s002_kWh
1798 | 50 | 50-18 | 13348 | User Channel 2 reactive energy import | EQ_IMP_s002_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s002_kvarh
1799 | 50 | 50-19 | 13352 | User Channel 2 reactive energy export | EQ_EXP_s002_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s002_kvarh
1800 | 50 | 50-20 | 13356 | User Channel 2 reactive energy net | EQ_NET_s002_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s002_kvarh
1801 | 50 | 50-21 | 13360 | User Channel 2 reactive energy total | EQ_TOTAL_s002_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s002_kvarh
1802 | 50 | 50-22 | 13364 | User Channel 2 apparent energy | ES_s002_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s002_kVAh
1803 | 50 | 50-23 | 13368 | User Channel 3 active energy import | EP_IMP_s003_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s003_kWh
1804 | 50 | 50-24 | 13372 | User Channel 3 active energy export | EP_EXP_s003_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s003_kWh
1805 | 50 | 50-25 | 13376 | User Channel 3 active energy net | EP_NET_s003_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s003_kWh
1806 | 50 | 50-26 | 13380 | User Channel 3 active energy total | EP_TOTAL_s003_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s003_kWh
1807 | 50 | 50-27 | 13384 | User Channel 3 reactive energy import | EQ_IMP_s003_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s003_kvarh
1808 | 50 | 50-28 | 13388 | User Channel 3 reactive energy export | EQ_EXP_s003_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s003_kvarh
1809 | 50 | 50-29 | 13392 | User Channel 3 reactive energy net | EQ_NET_s003_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s003_kvarh
1810 | 50 | 50-30 | 13396 | User Channel 3 reactive energy total | EQ_TOTAL_s003_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s003_kvarh
1811 | 50 | 50-31 | 13400 | User Channel 3 apparent energy | ES_s003_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s003_kVAh
1812 | 51 | 51-1 | 13404 | User Channel 4 active energy import | EP_IMP_s004_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s004_kWh
1813 | 51 | 51-2 | 13408 | User Channel 4 active energy export | EP_EXP_s004_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s004_kWh
1814 | 51 | 51-3 | 13412 | User Channel 4 active energy net | EP_NET_s004_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s004_kWh
1815 | 51 | 51-4 | 13416 | User Channel 4 active energy total | EP_TOTAL_s004_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s004_kWh
1816 | 51 | 51-5 | 13420 | User Channel 4 reactive energy import | EQ_IMP_s004_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s004_kvarh
1817 | 51 | 51-6 | 13424 | User Channel 4 reactive energy export | EQ_EXP_s004_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s004_kvarh
1818 | 51 | 51-7 | 13428 | User Channel 4 reactive energy net | EQ_NET_s004_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s004_kvarh
1819 | 51 | 51-8 | 13432 | User Channel 4 reactive energy total | EQ_TOTAL_s004_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s004_kvarh
1820 | 51 | 51-9 | 13436 | User Channel 4 apparent energy | ES_s004_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s004_kVAh
1821 | 51 | 51-10 | 13440 | User Channel 5 active energy import | EP_IMP_s005_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s005_kWh
1822 | 51 | 51-11 | 13444 | User Channel 5 active energy export | EP_EXP_s005_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s005_kWh
1823 | 51 | 51-12 | 13448 | User Channel 5 active energy net | EP_NET_s005_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s005_kWh
1824 | 51 | 51-13 | 13452 | User Channel 5 active energy total | EP_TOTAL_s005_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s005_kWh
1825 | 51 | 51-14 | 13456 | User Channel 5 reactive energy import | EQ_IMP_s005_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s005_kvarh
1826 | 51 | 51-15 | 13460 | User Channel 5 reactive energy export | EQ_EXP_s005_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s005_kvarh
1827 | 51 | 51-16 | 13464 | User Channel 5 reactive energy net | EQ_NET_s005_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s005_kvarh
1828 | 51 | 51-17 | 13468 | User Channel 5 reactive energy total | EQ_TOTAL_s005_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s005_kvarh
1829 | 51 | 51-18 | 13472 | User Channel 5 apparent energy | ES_s005_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s005_kVAh
1830 | 51 | 51-19 | 13476 | User Channel 6 active energy import | EP_IMP_s006_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s006_kWh
1831 | 51 | 51-20 | 13480 | User Channel 6 active energy export | EP_EXP_s006_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s006_kWh
1832 | 51 | 51-21 | 13484 | User Channel 6 active energy net | EP_NET_s006_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s006_kWh
1833 | 51 | 51-22 | 13488 | User Channel 6 active energy total | EP_TOTAL_s006_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s006_kWh
1834 | 51 | 51-23 | 13492 | User Channel 6 reactive energy import | EQ_IMP_s006_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s006_kvarh
1835 | 51 | 51-24 | 13496 | User Channel 6 reactive energy export | EQ_EXP_s006_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s006_kvarh
1836 | 51 | 51-25 | 13500 | User Channel 6 reactive energy net | EQ_NET_s006_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s006_kvarh
1837 | 51 | 51-26 | 13504 | User Channel 6 reactive energy total | EQ_TOTAL_s006_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s006_kvarh
1838 | 51 | 51-27 | 13508 | User Channel 6 apparent energy | ES_s006_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s006_kVAh
1839 | 51 | 51-28 | 13512 | User Channel 7 active energy import | EP_IMP_s007_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s007_kWh
1840 | 51 | 51-29 | 13516 | User Channel 7 active energy export | EP_EXP_s007_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s007_kWh
1841 | 51 | 51-30 | 13520 | User Channel 7 active energy net | EP_NET_s007_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s007_kWh
1842 | 51 | 51-31 | 13524 | User Channel 7 active energy total | EP_TOTAL_s007_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s007_kWh
1843 | 52 | 52-1 | 13528 | User Channel 7 reactive energy import | EQ_IMP_s007_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s007_kvarh
1844 | 52 | 52-2 | 13532 | User Channel 7 reactive energy export | EQ_EXP_s007_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s007_kvarh
1845 | 52 | 52-3 | 13536 | User Channel 7 reactive energy net | EQ_NET_s007_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s007_kvarh
1846 | 52 | 52-4 | 13540 | User Channel 7 reactive energy total | EQ_TOTAL_s007_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s007_kvarh
1847 | 52 | 52-5 | 13544 | User Channel 7 apparent energy | ES_s007_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s007_kVAh
1848 | 52 | 52-6 | 13548 | User Channel 8 active energy import | EP_IMP_s008_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s008_kWh
1849 | 52 | 52-7 | 13552 | User Channel 8 active energy export | EP_EXP_s008_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s008_kWh
1850 | 52 | 52-8 | 13556 | User Channel 8 active energy net | EP_NET_s008_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s008_kWh
1851 | 52 | 52-9 | 13560 | User Channel 8 active energy total | EP_TOTAL_s008_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s008_kWh
1852 | 52 | 52-10 | 13564 | User Channel 8 reactive energy import | EQ_IMP_s008_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s008_kvarh
1853 | 52 | 52-11 | 13568 | User Channel 8 reactive energy export | EQ_EXP_s008_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s008_kvarh
1854 | 52 | 52-12 | 13572 | User Channel 8 reactive energy net | EQ_NET_s008_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s008_kvarh
1855 | 52 | 52-13 | 13576 | User Channel 8 reactive energy total | EQ_TOTAL_s008_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s008_kvarh
1856 | 52 | 52-14 | 13580 | User Channel 8 apparent energy | ES_s008_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s008_kVAh
1857 | 52 | 52-15 | 13584 | User Channel 9 active energy import | EP_IMP_s009_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s009_kWh
1858 | 52 | 52-16 | 13588 | User Channel 9 active energy export | EP_EXP_s009_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s009_kWh
1859 | 52 | 52-17 | 13592 | User Channel 9 active energy net | EP_NET_s009_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s009_kWh
1860 | 52 | 52-18 | 13596 | User Channel 9 active energy total | EP_TOTAL_s009_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s009_kWh
1861 | 52 | 52-19 | 13600 | User Channel 9 reactive energy import | EQ_IMP_s009_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s009_kvarh
1862 | 52 | 52-20 | 13604 | User Channel 9 reactive energy export | EQ_EXP_s009_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s009_kvarh
1863 | 52 | 52-21 | 13608 | User Channel 9 reactive energy net | EQ_NET_s009_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s009_kvarh
1864 | 52 | 52-22 | 13612 | User Channel 9 reactive energy total | EQ_TOTAL_s009_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s009_kvarh
1865 | 52 | 52-23 | 13616 | User Channel 9 apparent energy | ES_s009_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s009_kVAh
1866 | 52 | 52-24 | 13620 | User Channel 10 active energy import | EP_IMP_s010_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s010_kWh
1867 | 52 | 52-25 | 13624 | User Channel 10 active energy export | EP_EXP_s010_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s010_kWh
1868 | 52 | 52-26 | 13628 | User Channel 10 active energy net | EP_NET_s010_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s010_kWh
1869 | 52 | 52-27 | 13632 | User Channel 10 active energy total | EP_TOTAL_s010_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s010_kWh
1870 | 52 | 52-28 | 13636 | User Channel 10 reactive energy import | EQ_IMP_s010_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s010_kvarh
1871 | 52 | 52-29 | 13640 | User Channel 10 reactive energy export | EQ_EXP_s010_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s010_kvarh
1872 | 52 | 52-30 | 13644 | User Channel 10 reactive energy net | EQ_NET_s010_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s010_kvarh
1873 | 52 | 52-31 | 13648 | User Channel 10 reactive energy total | EQ_TOTAL_s010_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s010_kvarh
1874 | 53 | 53-1 | 13652 | User Channel 10 apparent energy | ES_s010_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s010_kVAh
1875 | 53 | 53-2 | 13656 | User Channel 11 active energy import | EP_IMP_s011_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s011_kWh
1876 | 53 | 53-3 | 13660 | User Channel 11 active energy export | EP_EXP_s011_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s011_kWh
1877 | 53 | 53-4 | 13664 | User Channel 11 active energy net | EP_NET_s011_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s011_kWh
1878 | 53 | 53-5 | 13668 | User Channel 11 active energy total | EP_TOTAL_s011_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s011_kWh
1879 | 53 | 53-6 | 13672 | User Channel 11 reactive energy import | EQ_IMP_s011_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s011_kvarh
1880 | 53 | 53-7 | 13676 | User Channel 11 reactive energy export | EQ_EXP_s011_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s011_kvarh
1881 | 53 | 53-8 | 13680 | User Channel 11 reactive energy net | EQ_NET_s011_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s011_kvarh
1882 | 53 | 53-9 | 13684 | User Channel 11 reactive energy total | EQ_TOTAL_s011_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s011_kvarh
1883 | 53 | 53-10 | 13688 | User Channel 11 apparent energy | ES_s011_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s011_kVAh
1884 | 53 | 53-11 | 13692 | User Channel 12 active energy import | EP_IMP_s012_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_IMP_s012_kWh
1885 | 53 | 53-12 | 13696 | User Channel 12 active energy export | EP_EXP_s012_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_EXP_s012_kWh
1886 | 53 | 53-13 | 13700 | User Channel 12 active energy net | EP_NET_s012_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_NET_s012_kWh
1887 | 53 | 53-14 | 13704 | User Channel 12 active energy total | EP_TOTAL_s012_kWh | kWh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EP_TOTAL_s012_kWh
1888 | 53 | 53-15 | 13708 | User Channel 12 reactive energy import | EQ_IMP_s012_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_IMP_s012_kvarh
1889 | 53 | 53-16 | 13712 | User Channel 12 reactive energy export | EQ_EXP_s012_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_EXP_s012_kvarh
1890 | 53 | 53-17 | 13716 | User Channel 12 reactive energy net | EQ_NET_s012_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_NET_s012_kvarh
1891 | 53 | 53-18 | 13720 | User Channel 12 reactive energy total | EQ_TOTAL_s012_kvarh | kvarh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | EQ_TOTAL_s012_kvarh
1892 | 53 | 53-19 | 13724 | User Channel 12 apparent energy | ES_s012_kVAh | kVAh | double |  | R | 4 | 1 |  | 4 |  | 4-43 | 12-3-1 |  | ES_s012_kVAh
1893 | 54 | 54-1 | 25600 | DI1 pulse count | DI_PC_001 |  | uint32 |  | R/W | 2 | 1 |  |  |  | 4-5 | 26 |  | DI_PC_001
1894 | 54 | 54-2 | 25602 | DI2 pulse count | DI_PC_002 |  | uint32 |  | R/W | 2 | 1 |  |  |  | 4-5 | 26 |  | DI_PC_002
1895 | 54 | 54-3 | 25604 | DI3 pulse count | DI_PC_003 |  | uint32 |  | R/W | 2 | 1 |  |  |  | 4-5 | 26 |  | DI_PC_003
1896 | 54 | 54-4 | 25606 | DI4 pulse count | DI_PC_004 |  | uint32 |  | R/W | 2 | 1 |  |  |  | 4-5 | 26 |  | DI_PC_004
1897 | 55 | 55-1 | 0 | DI1 status | DI_ST_001 |  | uint16 |  | R | 1 | 1 |  |  |  | 4-7-44 | 26 |  | DI_ST_001
1898 | 55 | 55-2 | 1 | DI2 status | DI_ST_002 |  | uint16 |  | R | 1 | 1 |  |  |  | 4-7-44 | 26 |  | DI_ST_002
1899 | 55 | 55-3 | 2 | DI3 status | DI_ST_003 |  | uint16 |  | R | 1 | 1 |  |  |  | 4-7-44 | 26 |  | DI_ST_003
1900 | 55 | 55-4 | 3 | DI4 status | DI_ST_004 |  | uint16 |  | R | 1 | 1 |  |  |  | 4-7-44 | 26 |  | DI_ST_004
1901 | 55 | 55-5 | 0 | DO1 status | DO_ST_001 |  | uint16 |  | R/W | 1 | 1 |  |  |  | 22-4-34 | 26 |  | DO_ST_001
1902 | 55 | 55-6 | 1 | DO2 status | DO_ST_002 |  | uint16 |  | R/W | 1 | 1 |  |  |  | 22-4-34 | 26 |  | DO_ST_002
1903 | 55 | 55-7 | 2 | DO3 status | DO_ST_003 |  | uint16 |  | R/W | 1 | 1 |  |  |  | 22-4-34 | 26 |  | DO_ST_003
1904 | 55 | 55-8 | 3 | DO4 status | DO_ST_004 |  | uint16 |  | R/W | 1 | 1 |  |  |  | 22-4-34 | 26 |  | DO_ST_004
1905 | 56 | 56-1 | 4 | DO5 status | DO_ST_005 |  | uint16 |  | R/W | 1 | 1 |  |  |  | 22-4-34 | 26 |  | DO_ST_005
1906 | 56 | 56-2 | 5 | DO6 status | DO_ST_006 |  | uint16 |  | R/W | 1 | 1 |  |  |  | 22-4-34 | 26 |  | DO_ST_006
1907 | 56 | 56-3 | 6 | DO7 status | DO_ST_007 |  | uint16 |  | R/W | 1 | 1 |  |  |  | 22-4-34 | 26 |  | DO_ST_007
1908 | 56 | 56-4 | 7 | DO8 status | DO_ST_008 |  | uint16 |  | R/W | 1 | 1 |  |  |  | 22-4-34 | 26 |  | DO_ST_008
1909 | 57 | 57-1 | 32 | RO1 status | RO_ST_001 |  | uint16 |  | R/W | 1 | 1 |  |  |  | 22-4-25 | 26 |  | RO_ST_001
1910 | 57 | 57-2 | 33 | RO2 status | RO_ST_002 |  | uint16 |  | R/W | 1 | 1 |  |  |  | 22-4-25 | 26 |  | RO_ST_002
1911 | 58 | 58-1 | 25856 | Current Rated Value | Conf_NominalCurrent |  | uint16 |  | R/W | 1 | 1 |  |  | 27-30 |  | 35
1912 | 58 | 58-2 | 25857 | Voltage Rated Value | Conf_NominalVolt |  | uint16 |  | R/W | 1 | 1 |  |  | 27-30 |  | 35
1913 | 58 | 58-3 | 25858 | Voltage Sag Enable | Conf_VoltSag_Enable |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1914 | 58 | 58-4 | 25859 | Voltage Sag Threshold | Conf_VoltSag_Threshold |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1915 | 58 | 58-5 | 25860 | Voltage Sag Jitter | Conf_VoltSag_Hyst |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1916 | 58 | 58-6 | 25861 | Voltage Sag Triggers Waveform Recording | Conf_VoltSag_TrigWave |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1917 | 58 | 58-7 | 25862 | Voltage Sag - switch to output DO | Conf_VoltSag_TrigDO |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1918 | 58 | 58-8 | 25863 | Voltage Sag - switch to output RO | Conf_VoltSag_TrigRO |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1919 | 58 | 58-9 | 25864 | Voltage Swell Enable | Conf_VoltSwell_Enable |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1920 | 58 | 58-10 | 25865 | Voltage Swell Threshold | Conf_VoltSwell_Threshold |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1921 | 58 | 58-11 | 25866 | Voltage Swell Jitter | Conf_VoltSwell_Hyst |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1922 | 58 | 58-12 | 25867 | Voltage Swell Triggers Waveform Recording | Conf_VoltSwell_TrigWave |  | uint16 | 1 | R/W | 1 | 1 |  |  | 27
1923 | 58 | 58-13 | 25868 | Voltage Swell - switch to output DO | Conf_VoltSwell_TrigDO |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1924 | 58 | 58-14 | 25869 | Voltage Swell - switch to output RO | Conf_VoltSwell_TrigRO |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1925 | 58 | 58-15 | 25870 | Voltage Interruption Enable | Conf_VoltInt_Enable |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1926 | 58 | 58-16 | 25871 | Voltage Interruption Threshold | Conf_VoltInt_Threshold |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1927 | 58 | 58-17 | 25872 | Voltage Interruption Jitter | Conf_VoltInt_Hyst |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1928 | 58 | 58-18 | 25873 | Voltage Interruption Triggers Waveform Recording | Conf_VoltInt_TrigWave |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1929 | 58 | 58-19 | 25874 | Voltage Interruption - switch to output DO | Conf_VoltInt_TrigDO |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1930 | 58 | 58-20 | 25875 | Voltage Interruption - switch to output RO | Conf_VoltInt_TrigRO |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1931 | 58 | 58-21 | 25876 | Current Swell Enable | Conf_CurrentSwell_Enable |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1932 | 58 | 58-22 | 25877 | Current Swell Threshold | Conf_CurrentSwell_Threshold |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1933 | 58 | 58-23 | 25878 | Current Swell Jitter | Conf_CurrentSwell_Hyst |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1934 | 58 | 58-24 | 25879 | Current Triggers Waveform Recording | Conf_CurrentSwell_TrigWave |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1935 | 58 | 58-25 | 25880 | Current Swell - switch to output DO | Conf_CurrentSwell_TrigDO |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1936 | 58 | 58-26 | 25881 | Current Swell - switch to output RO | Conf_CurrentSwell_TrigRO |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1937 | 59 | 59-1 | 25968 | sampling rate | Conf_SampleRate |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1938 | 59 | 59-2 | 25969 | Number of cycles before the event occurred | Conf_Cyc_Pre_Evt |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1939 | 59 | 59-3 | 25970 | Number of cycles after the event occurred | Conf_Cyc_Post_Evt |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1940 | 59 | 59-4 | 25971 | DI1 Trigger | Conf_DI1_Trig |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1941 | 59 | 59-5 | 25972 | DI2 Trigger | Conf_DI2_Trig |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1942 | 59 | 59-6 | 25973 | DI3 Trigger | Conf_DI3_Trig |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1943 | 59 | 59-7 | 25974 | DI4 Trigger | Conf_DI4_Trig |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1944 | 59 | 59-8 | 25975 | Manually Trigger | Conf_Manual_Trig |  | uint16 |  | R/W | 1 | 1 |  |  | 27
1945 | 60 | 60-1 | 14080 | Phase A Max Current Demand | MAX_DMD_I_a_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1946 | 60 | 60-2 | 14082 | Phase A Max Current Demand Timestamp | MAX_DMDTS_I_a_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1947 | 60 | 60-3 | 14084 | Phase A Max Current Demand Timestamp | MAX_DMDTS_I_a_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1948 | 60 | 60-4 | 14085 | Phase A Import Active Power Max Demand | MAX_DMD_IMP_P_a_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1949 | 60 | 60-5 | 14087 | Phase A Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_a_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1950 | 60 | 60-6 | 14089 | Phase A Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_a_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1951 | 60 | 60-7 | 14090 | Phase A Export Active Power Max Demand | MAX_DMD_EXP_P_a_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1952 | 60 | 60-8 | 14092 | Phase A Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_a_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1953 | 60 | 60-9 | 14094 | Phase A Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_a_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1954 | 60 | 60-10 | 14095 | Phase A Import Reactive Power Max Demand | MAX_DMD_IMP_Q_a_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1955 | 60 | 60-11 | 14097 | Phase A Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_a_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1956 | 60 | 60-12 | 14099 | Phase A Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_a_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1957 | 60 | 60-13 | 14100 | Phase A Export Reactive Power Max Demand | MAX_DMD_EXP_Q_a_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1958 | 60 | 60-14 | 14102 | Phase A Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_a_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1959 | 60 | 60-15 | 14104 | Phase A Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_a_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1960 | 60 | 60-16 | 14105 | Phase A Apparent Power Max Demand | MAX_DMD_S_a_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1961 | 60 | 60-17 | 14107 | Phase A Apparent Power Max Demand Timestamp | MAX_DMDTS_S_a_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1962 | 60 | 60-18 | 14109 | Phase A Apparent Power Max Demand Timestamp | MAX_DMDTS_S_a_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1963 | 60 | 60-19 | 14110 | Phase B Current Max Demand | MAX_DMD_I_b_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1964 | 60 | 60-20 | 14112 | Phase B Current Max Demand Timestamp | MAX_DMDTS_I_b_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1965 | 60 | 60-21 | 14114 | Phase B Current Max Demand Timestamp | MAX_DMDTS_I_b_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1966 | 60 | 60-22 | 14115 | Phase B Import Active Power Max Demand | MAX_DMD_IMP_P_b_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1967 | 60 | 60-23 | 14117 | Phase B Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_b_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1968 | 60 | 60-24 | 14119 | Phase B Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_b_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1969 | 60 | 60-25 | 14120 | Phase B Export Active Power Max Demand | MAX_DMD_EXP_P_b_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1970 | 60 | 60-26 | 14122 | Phase B Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_b_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1971 | 60 | 60-27 | 14124 | Phase B Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_b_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1972 | 60 | 60-28 | 14125 | Phase B Import Reactive Power Max Demand | MAX_DMD_IMP_Q_b_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1973 | 60 | 60-29 | 14127 | Phase B Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_b_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1974 | 60 | 60-30 | 14129 | Phase B Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_b_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1975 | 60 | 60-31 | 14130 | Phase B Export Reactive Power Max Demand | MAX_DMD_EXP_Q_b_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1976 | 60 | 60-32 | 14132 | Phase B Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_b_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1977 | 60 | 60-33 | 14134 | Phase B Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_b_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1978 | 60 | 60-34 | 14135 | Phase B Apparent Power Max Demand | MAX_DMD_S_b_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1979 | 60 | 60-35 | 14137 | Phase B Apparent Power Max Demand Timestamp | MAX_DMDTS_S_b_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1980 | 60 | 60-36 | 14139 | Phase B Apparent Power Max Demand Timestamp | MAX_DMDTS_S_b_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1981 | 60 | 60-37 | 14140 | Phase C Current Max Demand | MAX_DMD_I_c_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1982 | 60 | 60-38 | 14142 | Phase C Current Max Demand Timestamp | MAX_DMDTS_I_c_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1983 | 60 | 60-39 | 14144 | Phase C Current Max Demand Timestamp | MAX_DMDTS_I_c_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1984 | 60 | 60-40 | 14145 | Phase C Import Active Power Max Demand | MAX_DMD_IMP_P_c_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1985 | 60 | 60-41 | 14147 | Phase C Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_c_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1986 | 60 | 60-42 | 14149 | Phase C Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_c_2 |  | uint16 | 1 | R | 1 | 1 |  |  |  |  | 20
1987 | 60 | 60-43 | 14150 | Phase C Export Active Power Max Demand | MAX_DMD_EXP_P_c_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1988 | 60 | 60-44 | 14152 | Phase C Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_c_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1989 | 60 | 60-45 | 14154 | Phase C Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_c_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1990 | 60 | 60-46 | 14155 | Phase C Import Reactive Power Max Demand | MAX_DMD_IMP_Q_c_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1991 | 60 | 60-47 | 14157 | Phase C Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_c_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1992 | 60 | 60-48 | 14159 | Phase C Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_c_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1993 | 60 | 60-49 | 14160 | Phase C Export Reactive Power Max Demand | MAX_DMD_EXP_Q_c_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1994 | 60 | 60-50 | 14162 | Phase C Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_c_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1995 | 60 | 60-51 | 14164 | Phase C Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_c_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1996 | 60 | 60-52 | 14165 | Phase C Apparent Power Max Demand | MAX_DMD_S_c_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
1997 | 60 | 60-53 | 14167 | Phase C Apparent Power Max Demand Timestamp | MAX_DMDTS_S_c_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
1998 | 60 | 60-54 | 14169 | Phase C Apparent Power Max Demand Timestamp | MAX_DMDTS_S_c_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
1999 | 60 | 60-55 | 14170 | System Average Current Max Demand | MAX_DMD_I_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
2000 | 60 | 60-56 | 14172 | System Average Current Max Demand Timestamp | MAX_DMDTS_I_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
2001 | 60 | 60-57 | 14174 | System Average Current Max Demand Timestamp | MAX_DMDTS_I_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
2002 | 60 | 60-58 | 14175 | System Import Active Power Max Demand | MAX_DMD_IMP_P_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
2003 | 60 | 60-59 | 14177 | System Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
2004 | 60 | 60-60 | 14179 | System Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
2005 | 60 | 60-61 | 14180 | System Export Active Power Max Demand | MAX_DMD_EXP_P_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
2006 | 60 | 60-62 | 14182 | System Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
2007 | 60 | 60-63 | 14184 | System Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
2008 | 60 | 60-64 | 14185 | System Import Reactive Power Max Demand | MAX_DMD_IMP_Q_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
2009 | 60 | 60-65 | 14187 | System Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
2010 | 60 | 60-66 | 14189 | System Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
2011 | 60 | 60-67 | 14190 | System Export Reactive Power Max Demand | MAX_DMD_EXP_Q_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
2012 | 60 | 60-68 | 14192 | System Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
2013 | 60 | 60-69 | 14194 | System Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
2014 | 60 | 60-70 | 14195 | System Apparent Power Max Demand | MAX_DMD_S_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 20
2015 | 60 | 60-71 | 14197 | System Apparent Power Max Demand Timestamp | MAX_DMDTS_S_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 20
2016 | 60 | 60-72 | 14199 | System Apparent Power Max Demand Timestamp | MAX_DMDTS_S_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 20
2017 | 61 | 61-1 | 14200 | Input Channel 1 Current Max Demand | MAX_DMD_I_001_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2018 | 61 | 61-2 | 14202 | Input Channel 1 Current Max Demand Timestamp | MAX_DMDTS_I_001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2019 | 61 | 61-3 | 14204 | Input Channel 1 Current Max Demand Timestamp | MAX_DMDTS_I_001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2020 | 61 | 61-4 | 14205 | Input Channel 1 Import Active Power Max Demand | MAX_DMD_IMP_P_001_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2021 | 61 | 61-5 | 14207 | Input Channel 1 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2022 | 61 | 61-6 | 14209 | Input Channel 1 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2023 | 61 | 61-7 | 14210 | Input Channel 1 Export Active Power Max Demand | MAX_DMD_EXP_P_001_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2024 | 61 | 61-8 | 14212 | Input Channel 1 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2025 | 61 | 61-9 | 14214 | Input Channel 1 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2026 | 61 | 61-10 | 14215 | Input Channel 1 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_001_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2027 | 61 | 61-11 | 14217 | Input Channel 1 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2028 | 61 | 61-12 | 14219 | Input Channel 1 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2029 | 61 | 61-13 | 14220 | Input Channel 1 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_001_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2030 | 61 | 61-14 | 14222 | Input Channel 1 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2031 | 61 | 61-15 | 14224 | Input Channel 1 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2032 | 61 | 61-16 | 14225 | Input Channel 1 Apparent Power Max Demand | MAX_DMD_S_001_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2033 | 61 | 61-17 | 14227 | Input Channel 1 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2034 | 61 | 61-18 | 14229 | Input Channel 1 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2035 | 61 | 61-19 | 14230 | Input Channel 2 Current Max Demand | MAX_DMD_I_002_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2036 | 61 | 61-20 | 14232 | Input Channel 2 Current Max Demand Timestamp | MAX_DMDTS_I_002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2037 | 61 | 61-21 | 14234 | Input Channel 2 Current Max Demand Timestamp | MAX_DMDTS_I_002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2038 | 61 | 61-22 | 14235 | Input Channel 2 Import Active Power Max Demand | MAX_DMD_IMP_P_002_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2039 | 61 | 61-23 | 14237 | Input Channel 2 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2040 | 61 | 61-24 | 14239 | Input Channel 2 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2041 | 61 | 61-25 | 14240 | Input Channel 2 Export Active Power Max Demand | MAX_DMD_EXP_P_002_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2042 | 61 | 61-26 | 14242 | Input Channel 2 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2043 | 61 | 61-27 | 14244 | Input Channel 2 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2044 | 61 | 61-28 | 14245 | Input Channel 2 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_002_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2045 | 61 | 61-29 | 14247 | Input Channel 2 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2046 | 61 | 61-30 | 14249 | Input Channel 2 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2047 | 61 | 61-31 | 14250 | Input Channel 2 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_002_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2048 | 61 | 61-32 | 14252 | Input Channel 2 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2049 | 61 | 61-33 | 14254 | Input Channel 2 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2050 | 61 | 61-34 | 14255 | Input Channel 2 Apparent Power Max Demand | MAX_DMD_S_002_kVA | kVA | float32 | 22 | R | 2 | 1 |  |  |  | 6 | 21
2051 | 61 | 61-35 | 14257 | Input Channel 2 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2052 | 61 | 61-36 | 14259 | Input Channel 2 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2053 | 61 | 61-37 | 14260 | Input Channel 3 Current Max Demand | MAX_DMD_I_003_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2054 | 61 | 61-38 | 14262 | Input Channel 3 Current Max Demand Timestamp | MAX_DMDTS_I_003_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2055 | 61 | 61-39 | 14264 | Input Channel 3 Current Max Demand Timestamp | MAX_DMDTS_I_003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2056 | 61 | 61-40 | 14265 | Input Channel 3 Import Active Power Max Demand | MAX_DMD_IMP_P_003_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2057 | 61 | 61-41 | 14267 | Input Channel 3 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_003_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2058 | 61 | 61-42 | 14269 | Input Channel 3 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2059 | 61 | 61-43 | 14270 | Input Channel 3 Export Active Power Max Demand | MAX_DMD_EXP_P_003_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2060 | 61 | 61-44 | 14272 | Input Channel 3 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_003_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2061 | 61 | 61-45 | 14274 | Input Channel 3 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2062 | 61 | 61-46 | 14275 | Input Channel 3 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_003_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2063 | 61 | 61-47 | 14277 | Input Channel 3 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_003_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2064 | 61 | 61-48 | 14279 | Input Channel 3 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2065 | 61 | 61-49 | 14280 | Input Channel 3 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_003_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2066 | 61 | 61-50 | 14282 | Input Channel 3 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_003_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2067 | 61 | 61-51 | 14284 | Input Channel 3 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2068 | 61 | 61-52 | 14285 | Input Channel 3 Apparent Power Max Demand | MAX_DMD_S_003_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2069 | 61 | 61-53 | 14287 | Input Channel 3 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_003_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2070 | 61 | 61-54 | 14289 | Input Channel 3 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2071 | 61 | 61-55 | 14290 | Input Channel 4 Current Max Demand | MAX_DMD_I_004_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2072 | 61 | 61-56 | 14292 | Input Channel 4 Current Max Demand Timestamp | MAX_DMDTS_I_004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2073 | 61 | 61-57 | 14294 | Input Channel 4 Current Max Demand Timestamp | MAX_DMDTS_I_004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2074 | 61 | 61-58 | 14295 | Input Channel 4 Import Active Power Max Demand | MAX_DMD_IMP_P_004_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2075 | 61 | 61-59 | 14297 | Input Channel 4 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2076 | 61 | 61-60 | 14299 | Input Channel 4 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2077 | 61 | 61-61 | 14300 | Input Channel 4 Export Active Power Max Demand | MAX_DMD_EXP_P_004_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2078 | 61 | 61-62 | 14302 | Input Channel 4 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2079 | 61 | 61-63 | 14304 | Input Channel 4 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2080 | 61 | 61-64 | 14305 | Input Channel 4 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_004_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2081 | 61 | 61-65 | 14307 | Input Channel 4 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2082 | 61 | 61-66 | 14309 | Input Channel 4 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2083 | 61 | 61-67 | 14310 | Input Channel 4 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_004_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2084 | 61 | 61-68 | 14312 | Input Channel 4 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2085 | 61 | 61-69 | 14314 | Input Channel 4 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2086 | 61 | 61-70 | 14315 | Input Channel 4 Apparent Power Max Demand | MAX_DMD_S_004_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2087 | 61 | 61-71 | 14317 | Input Channel 4 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2088 | 61 | 61-72 | 14319 | Input Channel 4 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2089 | 62 | 62-1 | 14320 | Input Channel 5 Current Max Demand | MAX_DMD_I_005_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2090 | 62 | 62-2 | 14322 | Input Channel 5 Current Max Demand Timestamp | MAX_DMDTS_I_005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2091 | 62 | 62-3 | 14324 | Input Channel 5 Current Max Demand Timestamp | MAX_DMDTS_I_005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2092 | 62 | 62-4 | 14325 | Input Channel 5 Import Active Power Max Demand | MAX_DMD_IMP_P_005_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2093 | 62 | 62-5 | 14327 | Input Channel 5 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2094 | 62 | 62-6 | 14329 | Input Channel 5 Import Active Power Max Demand timestamp | MAX_DMDTS_IMP_P_005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2095 | 62 | 62-7 | 14330 | Input Channel 5 Export Active Power Max Demand | MAX_DMD_EXP_P_005_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2096 | 62 | 62-8 | 14332 | Input Channel 5 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2097 | 62 | 62-9 | 14334 | Input Channel 5 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2098 | 62 | 62-10 | 14335 | Input Channel 5 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_005_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2099 | 62 | 62-11 | 14337 | Input Channel 5 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2100 | 62 | 62-12 | 14339 | Input Channel 5 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2101 | 62 | 62-13 | 14340 | Input Channel 5 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_005_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2102 | 62 | 62-14 | 14342 | Input Channel 5 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2103 | 62 | 62-15 | 14344 | Input Channel 5 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2104 | 62 | 62-16 | 14345 | Input Channel 5 Apparent Power Max Demand | MAX_DMD_S_005_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2105 | 62 | 62-17 | 14347 | Input Channel 5 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2106 | 62 | 62-18 | 14349 | Input Channel 5 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2107 | 62 | 62-19 | 14350 | Input Channel 6 Current Max Demand | MAX_DMD_I_006_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2108 | 62 | 62-20 | 14352 | Input Channel 6 Current Max Demand Timestamp | MAX_DMDTS_I_006_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2109 | 62 | 62-21 | 14354 | Input Channel 6 Current Max Demand Timestamp | MAX_DMDTS_I_006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2110 | 62 | 62-22 | 14355 | Input Channel 6 Import Active Power Max Demand | MAX_DMD_IMP_P_006_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2111 | 62 | 62-23 | 14357 | Input Channel 6 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_006_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2112 | 62 | 62-24 | 14359 | Input Channel 6 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2113 | 62 | 62-25 | 14360 | Input Channel 6 Export Active Power Max Demand | MAX_DMD_EXP_P_006_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2114 | 62 | 62-26 | 14362 | Input Channel 6 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_006_1 |  | uint32 | 6 | R | 2 | 1 |  |  |  |  | 21
2115 | 62 | 62-27 | 14364 | Input Channel 6 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2116 | 62 | 62-28 | 14365 | Input Channel 6 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_006_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2117 | 62 | 62-29 | 14367 | Input Channel 6 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_006_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2118 | 62 | 62-30 | 14369 | Input Channel 6 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2119 | 62 | 62-31 | 14370 | Input Channel 6 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_006_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2120 | 62 | 62-32 | 14372 | Input Channel 6 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_006_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2121 | 62 | 62-33 | 14374 | Input Channel 6 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2122 | 62 | 62-34 | 14375 | Input Channel 6 Apparent Power Max Demand | MAX_DMD_S_006_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2123 | 62 | 62-35 | 14377 | Input Channel 6 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_006_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2124 | 62 | 62-36 | 14379 | Input Channel 6 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2125 | 62 | 62-37 | 14380 | Input Channel 7 Current Max Demand | MAX_DMD_I_007_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2126 | 62 | 62-38 | 14382 | Input Channel 7 Current Max Demand Timestamp | MAX_DMDTS_I_007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2127 | 62 | 62-39 | 14384 | Input Channel 7 Current Max Demand Timestamp | MAX_DMDTS_I_007_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2128 | 62 | 62-40 | 14385 | Input Channel 7 Import Active Power Max Demand | MAX_DMD_IMP_P_007_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2129 | 62 | 62-41 | 14387 | Input Channel 7 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2130 | 62 | 62-42 | 14389 | Input Channel 7 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_007_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2131 | 62 | 62-43 | 14390 | Input Channel 7 Export Active Power Max Demand | MAX_DMD_EXP_P_007_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2132 | 62 | 62-44 | 14392 | Input Channel 7 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2133 | 62 | 62-45 | 14394 | Input Channel 7 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_007_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2134 | 62 | 62-46 | 14395 | Input Channel 7 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_007_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2135 | 62 | 62-47 | 14397 | Input Channel 7 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2136 | 62 | 62-48 | 14399 | Input Channel 7 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_007_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2137 | 62 | 62-49 | 14400 | Input Channel 7 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_007_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2138 | 62 | 62-50 | 14402 | Input Channel 7 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2139 | 62 | 62-51 | 14404 | Input Channel 7 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_007_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2140 | 62 | 62-52 | 14405 | Input Channel 7 Apparent Power Max Demand | MAX_DMD_S_007_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2141 | 62 | 62-53 | 14407 | Input Channel 7 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2142 | 62 | 62-54 | 14409 | Input Channel 7 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_007_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2143 | 62 | 62-55 | 14410 | Input Channel 8 Current Max Demand | MAX_DMD_I_008_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2144 | 62 | 62-56 | 14412 | Input Channel 8 Current Max Demand Timestamp | MAX_DMDTS_I_008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2145 | 62 | 62-57 | 14414 | Input Channel 8 Current Max Demand Timestamp | MAX_DMDTS_I_008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2146 | 62 | 62-58 | 14415 | Input Channel 8 Import Active Power Max Demand | MAX_DMD_IMP_P_008_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2147 | 62 | 62-59 | 14417 | Input Channel 8 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2148 | 62 | 62-60 | 14419 | Input Channel 8 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2149 | 62 | 62-61 | 14420 | Input Channel 8 Export Active Power Max Demand | MAX_DMD_EXP_P_008_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2150 | 62 | 62-62 | 14422 | Input Channel 8 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2151 | 62 | 62-63 | 14424 | Input Channel 8 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2152 | 62 | 62-64 | 14425 | Input Channel 8 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_008_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2153 | 62 | 62-65 | 14427 | Input Channel 8 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2154 | 62 | 62-66 | 14429 | Input Channel 8 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2155 | 62 | 62-67 | 14430 | Input Channel 8 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_008_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2156 | 62 | 62-68 | 14432 | Input Channel 8 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2157 | 62 | 62-69 | 14434 | Input Channel 8 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2158 | 62 | 62-70 | 14435 | Input Channel 8 Apparent Power Max Demand | MAX_DMD_S_008_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2159 | 62 | 62-71 | 14437 | Input Channel 8 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2160 | 62 | 62-72 | 14439 | Input Channel 8 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2161 | 63 | 63-1 | 14440 | Input Channel 9 Current Max Demand | MAX_DMD_I_009_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2162 | 63 | 63-2 | 14442 | Input Channel 9 Current Max Demand Timestamp | MAX_DMDTS_I_009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2163 | 63 | 63-3 | 14444 | Input Channel 9 Current Max Demand Timestamp | MAX_DMDTS_I_009_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2164 | 63 | 63-4 | 14445 | Input Channel 9 Import Active Power Max Demand | MAX_DMD_IMP_P_009_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2165 | 63 | 63-5 | 14447 | Input Channel 9 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2166 | 63 | 63-6 | 14449 | Input Channel 9 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_009_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2167 | 63 | 63-7 | 14450 | Input Channel 9 Export Active Power Max Demand | MAX_DMD_EXP_P_009_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2168 | 63 | 63-8 | 14452 | Input Channel 9 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2169 | 63 | 63-9 | 14454 | Input Channel 9 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_009_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2170 | 63 | 63-10 | 14455 | Input Channel 9 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_009_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2171 | 63 | 63-11 | 14457 | Input Channel 9 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2172 | 63 | 63-12 | 14459 | Input Channel 9 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_009_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2173 | 63 | 63-13 | 14460 | Input Channel 9 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_009_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2174 | 63 | 63-14 | 14462 | Input Channel 9 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2175 | 63 | 63-15 | 14464 | Input Channel 9 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_009_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2176 | 63 | 63-16 | 14465 | Input Channel 9 Apparent Power Max Demand | MAX_DMD_S_009_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2177 | 63 | 63-17 | 14467 | Input Channel 9 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2178 | 63 | 63-18 | 14469 | Input Channel 9 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_009_2 |  | uint16 | 1 | R | 1 | 1 |  |  |  |  | 21
2179 | 63 | 63-19 | 14470 | Input Channel 10 Current Max Demand | MAX_DMD_I_010_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2180 | 63 | 63-20 | 14472 | Input Channel 10 Current Max Demand Timestamp | MAX_DMDTS_I_010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2181 | 63 | 63-21 | 14474 | Input Channel 10 Current Max Demand Timestamp | MAX_DMDTS_I_010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2182 | 63 | 63-22 | 14475 | Input Channel 10 Import Active Power Max Demand | MAX_DMD_IMP_P_010_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2183 | 63 | 63-23 | 14477 | Input Channel 10 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2184 | 63 | 63-24 | 14479 | Input Channel 10 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2185 | 63 | 63-25 | 14480 | Input Channel 10 Export Active Power Max Demand | MAX_DMD_EXP_P_010_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2186 | 63 | 63-26 | 14482 | Input Channel 10 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2187 | 63 | 63-27 | 14484 | Input Channel 10 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2188 | 63 | 63-28 | 14485 | Input Channel 10 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_010_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2189 | 63 | 63-29 | 14487 | Input Channel 10 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2190 | 63 | 63-30 | 14489 | Input Channel 10 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2191 | 63 | 63-31 | 14490 | Input Channel 10 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_010_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2192 | 63 | 63-32 | 14492 | Input Channel 10 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2193 | 63 | 63-33 | 14494 | Input Channel 10 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2194 | 63 | 63-34 | 14495 | Input Channel 10 Apparent Power Max Demand | MAX_DMD_S_010_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2195 | 63 | 63-35 | 14497 | Input Channel 10 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2196 | 63 | 63-36 | 14499 | Input Channel 10 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2197 | 63 | 63-37 | 14500 | Input Channel 11 Current Max Demand | MAX_DMD_I_011_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2198 | 63 | 63-38 | 14502 | Input Channel 11 Current Max Demand Timestamp | MAX_DMDTS_I_011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2199 | 63 | 63-39 | 14504 | Input Channel 11 Current Max Demand Timestamp | MAX_DMDTS_I_011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2200 | 63 | 63-40 | 14505 | Input Channel 11 Import Active Power Max Demand | MAX_DMD_IMP_P_011_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2201 | 63 | 63-41 | 14507 | Input Channel 11 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2202 | 63 | 63-42 | 14509 | Input Channel 11 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2203 | 63 | 63-43 | 14510 | Input Channel 11 Export Active Power Max Demand | MAX_DMD_EXP_P_011_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2204 | 63 | 63-44 | 14512 | Input Channel 11 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2205 | 63 | 63-45 | 14514 | Input Channel 11 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2206 | 63 | 63-46 | 14515 | Input Channel 11 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_011_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2207 | 63 | 63-47 | 14517 | Input Channel 11 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2208 | 63 | 63-48 | 14519 | Input Channel 11 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2209 | 63 | 63-49 | 14520 | Input Channel 11 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_011_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2210 | 63 | 63-50 | 14522 | Input Channel 11 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2211 | 63 | 63-51 | 14524 | Input Channel 11 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2212 | 63 | 63-52 | 14525 | Input Channel 11 Apparent Power Max Demand | MAX_DMD_S_011_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2213 | 63 | 63-53 | 14527 | Input Channel 11 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2214 | 63 | 63-54 | 14529 | Input Channel 11 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2215 | 63 | 63-55 | 14530 | Input Channel 12 Current Max Demand | MAX_DMD_I_012_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2216 | 63 | 63-56 | 14532 | Input Channel 12 Current Max Demand Timestamp | MAX_DMDTS_I_012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2217 | 63 | 63-57 | 14534 | Input Channel 12 Current Max Demand Timestamp | MAX_DMDTS_I_012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2218 | 63 | 63-58 | 14535 | Input Channel 12 Import Active Power Max Demand | MAX_DMD_IMP_P_012_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2219 | 63 | 63-59 | 14537 | Input Channel 12 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2220 | 63 | 63-60 | 14539 | Input Channel 12 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2221 | 63 | 63-61 | 14540 | Input Channel 12 Export Active Power Max Demand | MAX_DMD_EXP_P_012_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2222 | 63 | 63-62 | 14542 | Input Channel 12 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2223 | 63 | 63-63 | 14544 | Input Channel 12 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2224 | 63 | 63-64 | 14545 | Input Channel 12 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_012_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2225 | 63 | 63-65 | 14547 | Input Channel 12 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2226 | 63 | 63-66 | 14549 | Input Channel 12 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2227 | 63 | 63-67 | 14550 | Input Channel 12 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_012_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2228 | 63 | 63-68 | 14552 | Input Channel 12 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2229 | 63 | 63-69 | 14554 | Input Channel 12 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2230 | 63 | 63-70 | 14555 | Input Channel 12 Apparent Power Max Demand | MAX_DMD_S_012_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2231 | 63 | 63-71 | 14557 | Input Channel 12 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2232 | 63 | 63-72 | 14559 | Input Channel 12 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2233 | 64 | 64-1 | 14560 | Input Channel 13 Current Max Demand | MAX_DMD_I_013_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2234 | 64 | 64-2 | 14562 | Input Channel 13 Current Max Demand Timestamp | MAX_DMDTS_I_013_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2235 | 64 | 64-3 | 14564 | Input Channel 13 Current Max Demand Timestamp | MAX_DMDTS_I_013_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2236 | 64 | 64-4 | 14565 | Input Channel 13 Import Active Power Max Demand | MAX_DMD_IMP_P_013_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2237 | 64 | 64-5 | 14567 | Input Channel 13 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_013_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2238 | 64 | 64-6 | 14569 | Input Channel 13 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_013_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2239 | 64 | 64-7 | 14570 | Input Channel 13 Export Active Power Max Demand | MAX_DMD_EXP_P_013_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2240 | 64 | 64-8 | 14572 | Input Channel 13 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_013_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2241 | 64 | 64-9 | 14574 | Input Channel 13 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_013_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2242 | 64 | 64-10 | 14575 | Input Channel 13 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_013_kvar | kvar | float32 | 22 | R | 2 | 1 |  |  |  | 6 | 21
2243 | 64 | 64-11 | 14577 | Input Channel 13 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_013_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2244 | 64 | 64-12 | 14579 | Input Channel 13 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_013_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2245 | 64 | 64-13 | 14580 | Input Channel 13 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_013_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2246 | 64 | 64-14 | 14582 | Input Channel 13 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_013_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2247 | 64 | 64-15 | 14584 | Input Channel 13 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_013_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2248 | 64 | 64-16 | 14585 | Input Channel 13 Apparent Power Max Demand | MAX_DMD_S_013_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2249 | 64 | 64-17 | 14587 | Input Channel 13 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_013_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2250 | 64 | 64-18 | 14589 | Input Channel 13 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_013_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2251 | 64 | 64-19 | 14590 | Input Channel 14 Current Max Demand | MAX_DMD_I_014_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2252 | 64 | 64-20 | 14592 | Input Channel 14 Current Max Demand Timestamp | MAX_DMDTS_I_014_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2253 | 64 | 64-21 | 14594 | Input Channel 14 Current Max Demand Timestamp | MAX_DMDTS_I_014_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2254 | 64 | 64-22 | 14595 | Input Channel 14 Import Active Power Max Demand | MAX_DMD_IMP_P_014_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2255 | 64 | 64-23 | 14597 | Input Channel 14 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_014_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2256 | 64 | 64-24 | 14599 | Input Channel 14 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_014_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2257 | 64 | 64-25 | 14600 | Input Channel 14 Export Active Power Max Demand | MAX_DMD_EXP_P_014_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2258 | 64 | 64-26 | 14602 | Input Channel 14 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_014_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2259 | 64 | 64-27 | 14604 | Input Channel 14 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_014_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2260 | 64 | 64-28 | 14605 | Input Channel 14 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_014_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2261 | 64 | 64-29 | 14607 | Input Channel 14 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_014_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2262 | 64 | 64-30 | 14609 | Input Channel 14 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_014_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2263 | 64 | 64-31 | 14610 | Input Channel 14 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_014_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2264 | 64 | 64-32 | 14612 | Input Channel 14 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_014_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2265 | 64 | 64-33 | 14614 | Input Channel 14 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_014_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2266 | 64 | 64-34 | 14615 | Input Channel 14 Apparent Power Max Demand | MAX_DMD_S_014_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2267 | 64 | 64-35 | 14617 | Input Channel 14 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_014_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2268 | 64 | 64-36 | 14619 | Input Channel 14 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_014_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2269 | 64 | 64-37 | 14620 | Input Channel 15 Current Max Demand | MAX_DMD_I_015_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2270 | 64 | 64-38 | 14622 | Input Channel 15 Current Max Demand Timestamp | MAX_DMDTS_I_015_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2271 | 64 | 64-39 | 14624 | Input Channel 15 Current Max Demand Timestamp | MAX_DMDTS_I_015_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2272 | 64 | 64-40 | 14625 | Input Channel 15 Import Active Power Max Demand | MAX_DMD_IMP_P_015_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2273 | 64 | 64-41 | 14627 | Input Channel 15 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_015_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2274 | 64 | 64-42 | 14629 | Input Channel 15 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_015_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2275 | 64 | 64-43 | 14630 | Input Channel 15 Export Active Power Max Demand | MAX_DMD_EXP_P_015_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2276 | 64 | 64-44 | 14632 | Input Channel 15 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_015_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2277 | 64 | 64-45 | 14634 | Input Channel 15 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_015_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2278 | 64 | 64-46 | 14635 | Input Channel 15 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_015_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2279 | 64 | 64-47 | 14637 | Input Channel 15 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_015_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2280 | 64 | 64-48 | 14639 | Input Channel 15 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_015_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2281 | 64 | 64-49 | 14640 | Input Channel 15 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_015_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2282 | 64 | 64-50 | 14642 | Input Channel 15 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_015_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2283 | 64 | 64-51 | 14644 | Input Channel 15 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_015_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2284 | 64 | 64-52 | 14645 | Input Channel 15 Apparent Power Max Demand | MAX_DMD_S_015_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2285 | 64 | 64-53 | 14647 | Input Channel 15 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_015_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2286 | 64 | 64-54 | 14649 | Input Channel 15 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_015_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2287 | 64 | 64-55 | 14650 | Input Channel 16 Current Max Demand | MAX_DMD_I_016_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2288 | 64 | 64-56 | 14652 | Input Channel 16 Current Max Demand Timestamp | MAX_DMDTS_I_016_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2289 | 64 | 64-57 | 14654 | Input Channel 16 Current Max Demand Timestamp | MAX_DMDTS_I_016_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2290 | 64 | 64-58 | 14655 | Input Channel 16 Import Active Power Max Demand | MAX_DMD_IMP_P_016_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2291 | 64 | 64-59 | 14657 | Input Channel 16 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_016_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2292 | 64 | 64-60 | 14659 | Input Channel 16 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_016_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2293 | 64 | 64-61 | 14660 | Input Channel 16 Export Active Power Max Demand | MAX_DMD_EXP_P_016_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2294 | 64 | 64-62 | 14662 | Input Channel 16 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_016_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2295 | 64 | 64-63 | 14664 | Input Channel 16 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_016_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2296 | 64 | 64-64 | 14665 | Input Channel 16 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_016_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2297 | 64 | 64-65 | 14667 | Input Channel 16 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_016_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2298 | 64 | 64-66 | 14669 | Input Channel 16 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_016_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2299 | 64 | 64-67 | 14670 | Input Channel 16 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_016_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2300 | 64 | 64-68 | 14672 | Input Channel 16 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_016_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2301 | 64 | 64-69 | 14674 | Input Channel 16 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_016_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2302 | 64 | 64-70 | 14675 | Input Channel 16 Apparent Power Max Demand | MAX_DMD_S_016_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2303 | 64 | 64-71 | 14677 | Input Channel 16 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_016_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2304 | 64 | 64-72 | 14679 | Input Channel 16 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_016_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2305 | 65 | 65-1 | 14680 | Input Channel 17 Current Max Demand | MAX_DMD_I_017_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2306 | 65 | 65-2 | 14682 | Input Channel 17 Current Max Demand Timestamp | MAX_DMDTS_I_017_1 |  | uint32 | 6 | R | 2 | 1 |  |  |  |  | 21
2307 | 65 | 65-3 | 14684 | Input Channel 17 Current Max Demand Timestamp | MAX_DMDTS_I_017_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2308 | 65 | 65-4 | 14685 | Input Channel 17 Import Active Power Max Demand | MAX_DMD_IMP_P_017_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2309 | 65 | 65-5 | 14687 | Input Channel 17 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_017_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2310 | 65 | 65-6 | 14689 | Input Channel 17 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_017_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2311 | 65 | 65-7 | 14690 | Input Channel 17 Export Active Power Max Demand | MAX_DMD_EXP_P_017_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2312 | 65 | 65-8 | 14692 | Input Channel 17 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_017_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2313 | 65 | 65-9 | 14694 | Input Channel 17 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_017_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2314 | 65 | 65-10 | 14695 | Input Channel 17 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_017_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2315 | 65 | 65-11 | 14697 | Input Channel 17 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_017_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2316 | 65 | 65-12 | 14699 | Input Channel 17 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_017_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2317 | 65 | 65-13 | 14700 | Input Channel 17 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_017_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2318 | 65 | 65-14 | 14702 | Input Channel 17 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_017_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2319 | 65 | 65-15 | 14704 | Input Channel 17 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_017_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2320 | 65 | 65-16 | 14705 | Input Channel 17 Apparent Power Max Demand | MAX_DMD_S_017_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2321 | 65 | 65-17 | 14707 | Input Channel 17 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_017_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2322 | 65 | 65-18 | 14709 | Input Channel 17 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_017_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2323 | 65 | 65-19 | 14710 | Input Channel 18 Current Max Demand | MAX_DMD_I_018_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2324 | 65 | 65-20 | 14712 | Input Channel 18 Current Max Demand Timestamp | MAX_DMDTS_I_018_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2325 | 65 | 65-21 | 14714 | Input Channel 18 Current Max Demand Timestamp | MAX_DMDTS_I_018_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2326 | 65 | 65-22 | 14715 | Input Channel 18 Import Active Power Max Demand | MAX_DMD_IMP_P_018_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2327 | 65 | 65-23 | 14717 | Input Channel 18 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_018_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2328 | 65 | 65-24 | 14719 | Input Channel 18 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_018_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2329 | 65 | 65-25 | 14720 | Input Channel 18 Export Active Power Max Demand | MAX_DMD_EXP_P_018_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2330 | 65 | 65-26 | 14722 | Input Channel 18 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_018_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2331 | 65 | 65-27 | 14724 | Input Channel 18 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_018_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2332 | 65 | 65-28 | 14725 | Input Channel 18 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_018_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2333 | 65 | 65-29 | 14727 | Input Channel 18 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_018_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2334 | 65 | 65-30 | 14729 | Input Channel 18 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_018_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2335 | 65 | 65-31 | 14730 | Input Channel 18 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_018_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2336 | 65 | 65-32 | 14732 | Input Channel 18 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_018_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2337 | 65 | 65-33 | 14734 | Input Channel 18 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_018_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2338 | 65 | 65-34 | 14735 | Input Channel 18 Apparent Power Max Demand | MAX_DMD_S_018_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2339 | 65 | 65-35 | 14737 | Input Channel 18 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_018_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2340 | 65 | 65-36 | 14739 | Input Channel 18 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_018_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2341 | 65 | 65-37 | 14740 | Input Channel 19 Current Max Demand | MAX_DMD_I_019_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2342 | 65 | 65-38 | 14742 | Input Channel 19 Current Max Demand Timestamp | MAX_DMDTS_I_019_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2343 | 65 | 65-39 | 14744 | Input Channel 19 Current Max Demand Timestamp | MAX_DMDTS_I_019_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2344 | 65 | 65-40 | 14745 | Input Channel 19 Import Active Power Max Demand | MAX_DMD_IMP_P_019_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2345 | 65 | 65-41 | 14747 | Input Channel 19 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_019_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2346 | 65 | 65-42 | 14749 | Input Channel 19 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_019_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2347 | 65 | 65-43 | 14750 | Input Channel 19 Export Active Power Max Demand | MAX_DMD_EXP_P_019_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2348 | 65 | 65-44 | 14752 | Input Channel 19 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_019_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2349 | 65 | 65-45 | 14754 | Input Channel 19 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_019_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2350 | 65 | 65-46 | 14755 | Input Channel 19 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_019_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2351 | 65 | 65-47 | 14757 | Input Channel 19 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_019_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2352 | 65 | 65-48 | 14759 | Input Channel 19 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_019_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2353 | 65 | 65-49 | 14760 | Input Channel 19 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_019_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2354 | 65 | 65-50 | 14762 | Input Channel 19 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_019_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2355 | 65 | 65-51 | 14764 | Input Channel 19 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_019_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2356 | 65 | 65-52 | 14765 | Input Channel 19 Apparent Power Max Demand | MAX_DMD_S_019_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2357 | 65 | 65-53 | 14767 | Input Channel 19 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_019_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2358 | 65 | 65-54 | 14769 | Input Channel 19 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_019_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2359 | 65 | 65-55 | 14770 | Input Channel 20 Current Max Demand | MAX_DMD_I_020_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2360 | 65 | 65-56 | 14772 | Input Channel 20 Current Max Demand Timestamp | MAX_DMDTS_I_020_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2361 | 65 | 65-57 | 14774 | Input Channel 20 Current Max Demand Timestamp | MAX_DMDTS_I_020_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2362 | 65 | 65-58 | 14775 | Input Channel 20 Import Active Power Max Demand | MAX_DMD_IMP_P_020_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2363 | 65 | 65-59 | 14777 | Input Channel 20 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_020_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2364 | 65 | 65-60 | 14779 | Input Channel 20 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_020_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2365 | 65 | 65-61 | 14780 | Input Channel 20 Export Active Power Max Demand | MAX_DMD_EXP_P_020_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2366 | 65 | 65-62 | 14782 | Input Channel 20 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_020_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2367 | 65 | 65-63 | 14784 | Input Channel 20 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_020_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2368 | 65 | 65-64 | 14785 | Input Channel 20 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_020_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2369 | 65 | 65-65 | 14787 | Input Channel 20 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_020_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2370 | 65 | 65-66 | 14789 | Input Channel 20 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_020_2 |  | uint16 | 1 | R | 1 | 1 |  |  |  |  | 21
2371 | 65 | 65-67 | 14790 | Input Channel 20 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_020_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2372 | 65 | 65-68 | 14792 | Input Channel 20 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_020_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2373 | 65 | 65-69 | 14794 | Input Channel 20 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_020_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2374 | 65 | 65-70 | 14795 | Input Channel 20 Apparent Power Max Demand | MAX_DMD_S_020_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2375 | 65 | 65-71 | 14797 | Input Channel 20 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_020_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2376 | 65 | 65-72 | 14799 | Input Channel 20 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_020_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2377 | 66 | 66-1 | 14800 | Input Channel 21 Current Max Demand | MAX_DMD_I_021_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2378 | 66 | 66-2 | 14802 | Input Channel 21 Current Max Demand Timestamp | MAX_DMDTS_I_021_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2379 | 66 | 66-3 | 14804 | Input Channel 21 Current Max Demand Timestamp | MAX_DMDTS_I_021_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2380 | 66 | 66-4 | 14805 | Input Channel 21 Import Active Power Max Demand | MAX_DMD_IMP_P_021_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2381 | 66 | 66-5 | 14807 | Input Channel 21 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_021_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2382 | 66 | 66-6 | 14809 | Input Channel 21 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_021_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2383 | 66 | 66-7 | 14810 | Input Channel 21 Export Active Power Max Demand | MAX_DMD_EXP_P_021_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2384 | 66 | 66-8 | 14812 | Input Channel 21 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_021_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2385 | 66 | 66-9 | 14814 | Input Channel 21 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_021_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2386 | 66 | 66-10 | 14815 | Input Channel 21 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_021_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2387 | 66 | 66-11 | 14817 | Input Channel 21 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_021_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2388 | 66 | 66-12 | 14819 | Input Channel 21 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_021_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2389 | 66 | 66-13 | 14820 | Input Channel 21 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_021_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2390 | 66 | 66-14 | 14822 | Input Channel 21 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_021_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2391 | 66 | 66-15 | 14824 | Input Channel 21 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_021_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2392 | 66 | 66-16 | 14825 | Input Channel 21 Apparent Power Max Demand | MAX_DMD_S_021_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2393 | 66 | 66-17 | 14827 | Input Channel 21 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_021_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2394 | 66 | 66-18 | 14829 | Input Channel 21 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_021_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2395 | 66 | 66-19 | 14830 | Input Channel 22 Current Max Demand | MAX_DMD_I_022_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2396 | 66 | 66-20 | 14832 | Input Channel 22 Current Max Demand Timestamp | MAX_DMDTS_I_022_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2397 | 66 | 66-21 | 14834 | Input Channel 22 Current Max Demand Timestamp | MAX_DMDTS_I_022_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2398 | 66 | 66-22 | 14835 | Input Channel 22 Import Active Power Max Demand | MAX_DMD_IMP_P_022_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2399 | 66 | 66-23 | 14837 | Input Channel 22 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_022_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2400 | 66 | 66-24 | 14839 | Input Channel 22 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_022_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2401 | 66 | 66-25 | 14840 | Input Channel 22 Export Active Power Max Demand | MAX_DMD_EXP_P_022_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2402 | 66 | 66-26 | 14842 | Input Channel 22 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_022_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2403 | 66 | 66-27 | 14844 | Input Channel 22 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_022_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2404 | 66 | 66-28 | 14845 | Input Channel 22 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_022_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2405 | 66 | 66-29 | 14847 | Input Channel 22 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_022_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2406 | 66 | 66-30 | 14849 | Input Channel 22 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_022_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2407 | 66 | 66-31 | 14850 | Input Channel 22 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_022_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2408 | 66 | 66-32 | 14852 | Input Channel 22 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_022_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2409 | 66 | 66-33 | 14854 | Input Channel 22 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_022_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2410 | 66 | 66-34 | 14855 | Input Channel 22 Apparent Power Max Demand | MAX_DMD_S_022_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2411 | 66 | 66-35 | 14857 | Input Channel 22 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_022_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2412 | 66 | 66-36 | 14859 | Input Channel 22 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_022_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2413 | 66 | 66-37 | 14860 | Input Channel 23 Current Max Demand | MAX_DMD_I_023_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2414 | 66 | 66-38 | 14862 | Input Channel 23 Current Max Demand Timestamp | MAX_DMDTS_I_023_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2415 | 66 | 66-39 | 14864 | Input Channel 23 Current Max Demand Timestamp | MAX_DMDTS_I_023_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2416 | 66 | 66-40 | 14865 | Input Channel 23 Import Active Power Max Demand | MAX_DMD_IMP_P_023_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2417 | 66 | 66-41 | 14867 | Input Channel 23 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_023_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2418 | 66 | 66-42 | 14869 | Input Channel 23 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_023_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2419 | 66 | 66-43 | 14870 | Input Channel 23 Export Active Power Max Demand | MAX_DMD_EXP_P_023_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2420 | 66 | 66-44 | 14872 | Input Channel 23 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_023_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2421 | 66 | 66-45 | 14874 | Input Channel 23 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_023_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2422 | 66 | 66-46 | 14875 | Input Channel 23 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_023_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2423 | 66 | 66-47 | 14877 | Input Channel 23 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_023_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2424 | 66 | 66-48 | 14879 | Input Channel 23 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_023_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2425 | 66 | 66-49 | 14880 | Input Channel 23 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_023_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2426 | 66 | 66-50 | 14882 | Input Channel 23 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_023_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2427 | 66 | 66-51 | 14884 | Input Channel 23 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_023_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2428 | 66 | 66-52 | 14885 | Input Channel 23 Apparent Power Max Demand | MAX_DMD_S_023_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2429 | 66 | 66-53 | 14887 | Input Channel 23 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_023_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2430 | 66 | 66-54 | 14889 | Input Channel 23 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_023_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2431 | 66 | 66-55 | 14890 | Input Channel 24 Current Max Demand | MAX_DMD_I_024_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2432 | 66 | 66-56 | 14892 | Input Channel 24 Current Max Demand Timestamp | MAX_DMDTS_I_024_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2433 | 66 | 66-57 | 14894 | Input Channel 24 Current Max Demand Timestamp | MAX_DMDTS_I_024_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2434 | 66 | 66-58 | 14895 | Input Channel 24 Import Active Power Max Demand | MAX_DMD_IMP_P_024_kW | kW | float32 | 22 | R | 2 | 1 |  |  |  | 6 | 21
2435 | 66 | 66-59 | 14897 | Input Channel 24 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_024_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2436 | 66 | 66-60 | 14899 | Input Channel 24 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_024_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2437 | 66 | 66-61 | 14900 | Input Channel 24 Export Active Power Max Demand | MAX_DMD_EXP_P_024_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2438 | 66 | 66-62 | 14902 | Input Channel 24 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_024_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2439 | 66 | 66-63 | 14904 | Input Channel 24 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_024_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2440 | 66 | 66-64 | 14905 | Input Channel 24 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_024_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2441 | 66 | 66-65 | 14907 | Input Channel 24 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_024_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2442 | 66 | 66-66 | 14909 | Input Channel 24 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_024_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2443 | 66 | 66-67 | 14910 | Input Channel 24 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_024_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2444 | 66 | 66-68 | 14912 | Input Channel 24 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_024_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2445 | 66 | 66-69 | 14914 | Input Channel 24 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_024_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2446 | 66 | 66-70 | 14915 | Input Channel 24 Apparent Power Max Demand | MAX_DMD_S_024_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2447 | 66 | 66-71 | 14917 | Input Channel 24 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_024_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2448 | 66 | 66-72 | 14919 | Input Channel 24 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_024_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2449 | 67 | 67-1 | 14920 | User Channel 1 Current Max Demand | MAX_DMD_I_s001_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2450 | 67 | 67-2 | 14922 | User Channel 1 Current Max Demand Timestamp | MAX_DMDTS_I_s001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2451 | 67 | 67-3 | 14924 | User Channel 1 Current Max Demand Timestamp | MAX_DMDTS_I_s001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2452 | 67 | 67-4 | 14925 | User Channel 1 Import Active Power Max Demand | MAX_DMD_IMP_P_s001_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2453 | 67 | 67-5 | 14927 | User Channel 1 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2454 | 67 | 67-6 | 14929 | User Channel 1 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2455 | 67 | 67-7 | 14930 | User Channel 1 Export Active Power Max Demand | MAX_DMD_EXP_P_s001_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2456 | 67 | 67-8 | 14932 | User Channel 1 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2457 | 67 | 67-9 | 14934 | User Channel 1 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2458 | 67 | 67-10 | 14935 | User Channel 1 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s001_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2459 | 67 | 67-11 | 14937 | User Channel 1 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2460 | 67 | 67-12 | 14939 | User Channel 1 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2461 | 67 | 67-13 | 14940 | User Channel 1 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s001_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2462 | 67 | 67-14 | 14942 | User Channel 1 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2463 | 67 | 67-15 | 14944 | User Channel 1 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2464 | 67 | 67-16 | 14945 | User Channel 1 Apparent Power Max Demand | MAX_DMD_S_s001_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2465 | 67 | 67-17 | 14947 | User Channel 1 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s001_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2466 | 67 | 67-18 | 14949 | User Channel 1 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s001_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2467 | 67 | 67-19 | 14950 | User Channel 2 Current Max Demand | MAX_DMD_I_s002_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2468 | 67 | 67-20 | 14952 | User Channel 2 Current Max Demand Timestamp | MAX_DMDTS_I_s002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2469 | 67 | 67-21 | 14954 | User Channel 2 Current Max Demand Timestamp | MAX_DMDTS_I_s002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2470 | 67 | 67-22 | 14955 | User Channel 2 Import Active Power Max Demand | MAX_DMD_IMP_P_s002_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2471 | 67 | 67-23 | 14957 | User Channel 2 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2472 | 67 | 67-24 | 14959 | User Channel 2 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2473 | 67 | 67-25 | 14960 | User Channel 2 Export Active Power Max Demand | MAX_DMD_EXP_P_s002_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2474 | 67 | 67-26 | 14962 | User Channel 2 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2475 | 67 | 67-27 | 14964 | User Channel 2 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2476 | 67 | 67-28 | 14965 | User Channel 2 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s002_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2477 | 67 | 67-29 | 14967 | User Channel 2 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2478 | 67 | 67-30 | 14969 | User Channel 2 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2479 | 67 | 67-31 | 14970 | User Channel 2 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s002_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2480 | 67 | 67-32 | 14972 | User Channel 2 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2481 | 67 | 67-33 | 14974 | User Channel 2 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2482 | 67 | 67-34 | 14975 | User Channel 2 Apparent Power Max Demand | MAX_DMD_S_s002_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2483 | 67 | 67-35 | 14977 | User Channel 2 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s002_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2484 | 67 | 67-36 | 14979 | User Channel 2 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s002_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2485 | 67 | 67-37 | 14980 | User Channel 3 Current Max Demand | MAX_DMD_I_s003_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2486 | 67 | 67-38 | 14982 | User Channel 3 Current Max Demand Timestamp | MAX_DMDTS_I_s003_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2487 | 67 | 67-39 | 14984 | User Channel 3 Current Max Demand Timestamp | MAX_DMDTS_I_s003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2488 | 67 | 67-40 | 14985 | User Channel 3 Import Active Power Max Demand | MAX_DMD_IMP_P_s003_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2489 | 67 | 67-41 | 14987 | User Channel 3 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s003_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2490 | 67 | 67-42 | 14989 | User Channel 3 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2491 | 67 | 67-43 | 14990 | User Channel 3 Export Active Power Max Demand | MAX_DMD_EXP_P_s003_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2492 | 67 | 67-44 | 14992 | User Channel 3 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s003_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2493 | 67 | 67-45 | 14994 | User Channel 3 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2494 | 67 | 67-46 | 14995 | User Channel 3 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s003_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2495 | 67 | 67-47 | 14997 | User Channel 3 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s003_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2496 | 67 | 67-48 | 14999 | User Channel 3 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2497 | 67 | 67-49 | 15000 | User Channel 3 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s003_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2498 | 67 | 67-50 | 15002 | User Channel 3 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s003_1 |  | uint32 | 6 | R | 2 | 1 |  |  |  |  | 21
2499 | 67 | 67-51 | 15004 | User Channel 3 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2500 | 67 | 67-52 | 15005 | User Channel 3 Apparent Power Max Demand | MAX_DMD_S_s003_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2501 | 67 | 67-53 | 15007 | User Channel 3 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s003_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2502 | 67 | 67-54 | 15009 | User Channel 3 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s003_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2503 | 67 | 67-55 | 15010 | User Channel 4 Current Max Demand | MAX_DMD_I_s004_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2504 | 67 | 67-56 | 15012 | User Channel 4 Current Max Demand Timestamp | MAX_DMDTS_I_s004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2505 | 67 | 67-57 | 15014 | User Channel 4 Current Max Demand Timestamp | MAX_DMDTS_I_s004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2506 | 67 | 67-58 | 15015 | User Channel 4 Import Active Power Max Demand | MAX_DMD_IMP_P_s004_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2507 | 67 | 67-59 | 15017 | User Channel 4 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2508 | 67 | 67-60 | 15019 | User Channel 4 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2509 | 67 | 67-61 | 15020 | User Channel 4 Export Active Power Max Demand | MAX_DMD_EXP_P_s004_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2510 | 67 | 67-62 | 15022 | User Channel 4 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2511 | 67 | 67-63 | 15024 | User Channel 4 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2512 | 67 | 67-64 | 15025 | User Channel 4 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s004_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2513 | 67 | 67-65 | 15027 | User Channel 4 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2514 | 67 | 67-66 | 15029 | User Channel 4 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2515 | 67 | 67-67 | 15030 | User Channel 4 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s004_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2516 | 67 | 67-68 | 15032 | User Channel 4 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2517 | 67 | 67-69 | 15034 | User Channel 4 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2518 | 67 | 67-70 | 15035 | User Channel 4 Apparent Power Max Demand | MAX_DMD_S_s004_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2519 | 67 | 67-71 | 15037 | User Channel 4 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s004_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2520 | 67 | 67-72 | 15039 | User Channel 4 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s004_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2521 | 68 | 68-1 | 15040 | User Channel 5 Current Max Demand | MAX_DMD_I_s005_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2522 | 68 | 68-2 | 15042 | User Channel 5 Current Max Demand Timestamp | MAX_DMDTS_I_s005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2523 | 68 | 68-3 | 15044 | User Channel 5 Current Max Demand Timestamp | MAX_DMDTS_I_s005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2524 | 68 | 68-4 | 15045 | User Channel 5 Import Active Power Max Demand | MAX_DMD_IMP_P_s005_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2525 | 68 | 68-5 | 15047 | User Channel 5 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2526 | 68 | 68-6 | 15049 | User Channel 5 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2527 | 68 | 68-7 | 15050 | User Channel 5 Export Active Power Max Demand | MAX_DMD_EXP_P_s005_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2528 | 68 | 68-8 | 15052 | User Channel 5 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2529 | 68 | 68-9 | 15054 | User Channel 5 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2530 | 68 | 68-10 | 15055 | User Channel 5 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s005_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2531 | 68 | 68-11 | 15057 | User Channel 5 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2532 | 68 | 68-12 | 15059 | User Channel 5 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2533 | 68 | 68-13 | 15060 | User Channel 5 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s005_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2534 | 68 | 68-14 | 15062 | User Channel 5 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2535 | 68 | 68-15 | 15064 | User Channel 5 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2536 | 68 | 68-16 | 15065 | User Channel 5 Apparent Power Max Demand | MAX_DMD_S_s005_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2537 | 68 | 68-17 | 15067 | User Channel 5 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s005_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2538 | 68 | 68-18 | 15069 | User Channel 5 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s005_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2539 | 68 | 68-19 | 15070 | User Channel 6 Current Max Demand | MAX_DMD_I_s006_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2540 | 68 | 68-20 | 15072 | User Channel 6 Current Max Demand Timestamp | MAX_DMDTS_I_s006_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2541 | 68 | 68-21 | 15074 | User Channel 6 Current Max Demand Timestamp | MAX_DMDTS_I_s006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2542 | 68 | 68-22 | 15075 | User Channel 6 Import Active Power Max Demand | MAX_DMD_IMP_P_s006_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2543 | 68 | 68-23 | 15077 | User Channel 6 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s006_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2544 | 68 | 68-24 | 15079 | User Channel 6 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2545 | 68 | 68-25 | 15080 | User Channel 6 Export Active Power Max Demand | MAX_DMD_EXP_P_s006_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2546 | 68 | 68-26 | 15082 | User Channel 6 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s006_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2547 | 68 | 68-27 | 15084 | User Channel 6 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2548 | 68 | 68-28 | 15085 | User Channel 6 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s006_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2549 | 68 | 68-29 | 15087 | User Channel 6 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s006_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2550 | 68 | 68-30 | 15089 | User Channel 6 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2551 | 68 | 68-31 | 15090 | User Channel 6 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s006_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2552 | 68 | 68-32 | 15092 | User Channel 6 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s006_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2553 | 68 | 68-33 | 15094 | User Channel 6 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2554 | 68 | 68-34 | 15095 | User Channel 6 Apparent Power Max Demand | MAX_DMD_S_s006_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2555 | 68 | 68-35 | 15097 | User Channel 6 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s006_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2556 | 68 | 68-36 | 15099 | User Channel 6 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s006_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2557 | 68 | 68-37 | 15100 | User Channel 7 Current Max Demand | MAX_DMD_I_s007_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2558 | 68 | 68-38 | 15102 | User Channel 7 Current Max Demand Timestamp | MAX_DMDTS_I_s007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2559 | 68 | 68-39 | 15104 | User Channel 7 Current Max Demand Timestamp | MAX_DMDTS_I_s007_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2560 | 68 | 68-40 | 15105 | User Channel 7 Import Active Power Max Demand | MAX_DMD_IMP_P_s007_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2561 | 68 | 68-41 | 15107 | User Channel 7 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2562 | 68 | 68-42 | 15109 | User Channel 7 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s007_2 |  | uint16 | 1 | R | 1 | 1 |  |  |  |  | 21
2563 | 68 | 68-43 | 15110 | User Channel 7 Export Active Power Max Demand | MAX_DMD_EXP_P_s007_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2564 | 68 | 68-44 | 15112 | User Channel 7 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2565 | 68 | 68-45 | 15114 | User Channel 7 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s007_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2566 | 68 | 68-46 | 15115 | User Channel 7 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s007_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2567 | 68 | 68-47 | 15117 | User Channel 7 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2568 | 68 | 68-48 | 15119 | User Channel 7 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s007_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2569 | 68 | 68-49 | 15120 | User Channel 7 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s007_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2570 | 68 | 68-50 | 15122 | User Channel 7 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2571 | 68 | 68-51 | 15124 | User Channel 7 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s007_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2572 | 68 | 68-52 | 15125 | User Channel 7 Apparent Power Max Demand | MAX_DMD_S_s007_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2573 | 68 | 68-53 | 15127 | User Channel 7 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s007_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2574 | 68 | 68-54 | 15129 | User Channel 7 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s007_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2575 | 68 | 68-55 | 15130 | User Channel 8 Current Max Demand | MAX_DMD_I_s008_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2576 | 68 | 68-56 | 15132 | User Channel 8 Current Max Demand Timestamp | MAX_DMDTS_I_s008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2577 | 68 | 68-57 | 15134 | User Channel 8 Current Max Demand Timestamp | MAX_DMDTS_I_s008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2578 | 68 | 68-58 | 15135 | User Channel 8 Import Active Power Max Demand | MAX_DMD_IMP_P_s008_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2579 | 68 | 68-59 | 15137 | User Channel 8 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2580 | 68 | 68-60 | 15139 | User Channel 8 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2581 | 68 | 68-61 | 15140 | User Channel 8 Export Active Power Max Demand | MAX_DMD_EXP_P_s008_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2582 | 68 | 68-62 | 15142 | User Channel 8 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2583 | 68 | 68-63 | 15144 | User Channel 8 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2584 | 68 | 68-64 | 15145 | User Channel 8 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s008_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2585 | 68 | 68-65 | 15147 | User Channel 8 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2586 | 68 | 68-66 | 15149 | User Channel 8 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2587 | 68 | 68-67 | 15150 | User Channel 8 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s008_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2588 | 68 | 68-68 | 15152 | User Channel 8 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2589 | 68 | 68-69 | 15154 | User Channel 8 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2590 | 68 | 68-70 | 15155 | User Channel 8 Apparent Power Max Demand | MAX_DMD_S_s008_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2591 | 68 | 68-71 | 15157 | User Channel 8 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s008_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2592 | 68 | 68-72 | 15159 | User Channel 8 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s008_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2593 | 69 | 69-1 | 15160 | User Channel 9 Current Max Demand | MAX_DMD_I_s009_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2594 | 69 | 69-2 | 15162 | User Channel 9 Current Max Demand Timestamp | MAX_DMDTS_I_s009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2595 | 69 | 69-3 | 15164 | User Channel 9 Current Max Demand Timestamp | MAX_DMDTS_I_s009_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2596 | 69 | 69-4 | 15165 | User Channel 9 Import Active Power Max Demand | MAX_DMD_IMP_P_s009_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2597 | 69 | 69-5 | 15167 | User Channel 9 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2598 | 69 | 69-6 | 15169 | User Channel 9 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s009_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2599 | 69 | 69-7 | 15170 | User Channel 9 Export Active Power Max Demand | MAX_DMD_EXP_P_s009_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2600 | 69 | 69-8 | 15172 | User Channel 9 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2601 | 69 | 69-9 | 15174 | User Channel 9 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s009_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2602 | 69 | 69-10 | 15175 | User Channel 9 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s009_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2603 | 69 | 69-11 | 15177 | User Channel 9 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2604 | 69 | 69-12 | 15179 | User Channel 9 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s009_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2605 | 69 | 69-13 | 15180 | User Channel 9 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s009_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2606 | 69 | 69-14 | 15182 | User Channel 9 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2607 | 69 | 69-15 | 15184 | User Channel 9 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s009_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2608 | 69 | 69-16 | 15185 | User Channel 9 Apparent Power Max Demand | MAX_DMD_S_s009_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2609 | 69 | 69-17 | 15187 | User Channel 9 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s009_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2610 | 69 | 69-18 | 15189 | User Channel 9 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s009_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2611 | 69 | 69-19 | 15190 | User Channel 10 Current Max Demand | MAX_DMD_I_s010_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2612 | 69 | 69-20 | 15192 | User Channel 10 Current Max Demand Timestamp | MAX_DMDTS_I_s010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2613 | 69 | 69-21 | 15194 | User Channel 10 Current Max Demand Timestamp | MAX_DMDTS_I_s010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2614 | 69 | 69-22 | 15195 | User Channel 10 Import Active Power Max Demand | MAX_DMD_IMP_P_s010_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2615 | 69 | 69-23 | 15197 | User Channel 10 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2616 | 69 | 69-24 | 15199 | User Channel 10 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2617 | 69 | 69-25 | 15200 | User Channel 10 Export Active Power Max Demand | MAX_DMD_EXP_P_s010_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2618 | 69 | 69-26 | 15202 | User Channel 10 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2619 | 69 | 69-27 | 15204 | User Channel 10 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2620 | 69 | 69-28 | 15205 | User Channel 10 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s010_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2621 | 69 | 69-29 | 15207 | User Channel 10 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2622 | 69 | 69-30 | 15209 | User Channel 10 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2623 | 69 | 69-31 | 15210 | User Channel 10 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s010_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2624 | 69 | 69-32 | 15212 | User Channel 10 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2625 | 69 | 69-33 | 15214 | User Channel 10 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2626 | 69 | 69-34 | 15215 | User Channel 10 Apparent Power Max Demand | MAX_DMD_S_s010_kVA | kVA | float32 | 22 | R | 2 | 1 |  |  |  | 6 | 21
2627 | 69 | 69-35 | 15217 | User Channel 10 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s010_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2628 | 69 | 69-36 | 15219 | User Channel 10 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s010_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2629 | 69 | 69-37 | 15220 | User Channel 11 Current Max Demand | MAX_DMD_I_s011_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2630 | 69 | 69-38 | 15222 | User Channel 11 Current Max Demand Timestamp | MAX_DMDTS_I_s011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2631 | 69 | 69-39 | 15224 | User Channel 11 Current Max Demand Timestamp | MAX_DMDTS_I_s011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2632 | 69 | 69-40 | 15225 | User Channel 11 Import Active Power Max Demand | MAX_DMD_IMP_P_s011_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2633 | 69 | 69-41 | 15227 | User Channel 11 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2634 | 69 | 69-42 | 15229 | User Channel 11 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2635 | 69 | 69-43 | 15230 | User Channel 11 Export Active Power Max Demand | MAX_DMD_EXP_P_s011_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2636 | 69 | 69-44 | 15232 | User Channel 11 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2637 | 69 | 69-45 | 15234 | User Channel 11 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2638 | 69 | 69-46 | 15235 | User Channel 11 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s011_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2639 | 69 | 69-47 | 15237 | User Channel 11 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2640 | 69 | 69-48 | 15239 | User Channel 11 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2641 | 69 | 69-49 | 15240 | User Channel 11 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s011_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2642 | 69 | 69-50 | 15242 | User Channel 11 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2643 | 69 | 69-51 | 15244 | User Channel 11 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2644 | 69 | 69-52 | 15245 | User Channel 11 Apparent Power Max Demand | MAX_DMD_S_s011_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2645 | 69 | 69-53 | 15247 | User Channel 11 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s011_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2646 | 69 | 69-54 | 15249 | User Channel 11 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s011_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2647 | 69 | 69-55 | 15250 | User Channel 12 Current Max Demand | MAX_DMD_I_s012_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2648 | 69 | 69-56 | 15252 | User Channel 12 Current Max Demand Timestamp | MAX_DMDTS_I_s012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2649 | 69 | 69-57 | 15254 | User Channel 12 Current Max Demand Timestamp | MAX_DMDTS_I_s012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2650 | 69 | 69-58 | 15255 | User Channel 12 Import Active Power Max Demand | MAX_DMD_IMP_P_s012_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2651 | 69 | 69-59 | 15257 | User Channel 12 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2652 | 69 | 69-60 | 15259 | User Channel 12 Import Active Power Max Demand Timestamp | MAX_DMDTS_IMP_P_s012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2653 | 69 | 69-61 | 15260 | User Channel 12 Export Active Power Max Demand | MAX_DMD_EXP_P_s012_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2654 | 69 | 69-62 | 15262 | User Channel 12 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2655 | 69 | 69-63 | 15264 | User Channel 12 Export Active Power Max Demand Timestamp | MAX_DMDTS_EXP_P_s012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2656 | 69 | 69-64 | 15265 | User Channel 12 Import Reactive Power Max Demand | MAX_DMD_IMP_Q_s012_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2657 | 69 | 69-65 | 15267 | User Channel 12 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2658 | 69 | 69-66 | 15269 | User Channel 12 Import Reactive Power Max Demand Timestamp | MAX_DMDTS_IMP_Q_s012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2659 | 69 | 69-67 | 15270 | User Channel 12 Export Reactive Power Max Demand | MAX_DMD_EXP_Q_s012_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2660 | 69 | 69-68 | 15272 | User Channel 12 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2661 | 69 | 69-69 | 15274 | User Channel 12 Export Reactive Power Max Demand Timestamp | MAX_DMDTS_EXP_Q_s012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2662 | 69 | 69-70 | 15275 | User Channel 12 Apparent Power Max Demand | MAX_DMD_S_s012_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 21
2663 | 69 | 69-71 | 15277 | User Channel 12 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s012_1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 21
2664 | 69 | 69-72 | 15279 | User Channel 12 Apparent Power Max Demand Timestamp | MAX_DMDTS_S_s012_2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 21
2665 | 70 | 70-1 | 20992 | System Frequency Max value | MAX_FREQ_Hz | Hz | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2666 | 70 | 70-2 | 20994 | System Frequency Max value Timestamp | MAX_TS_FREQ |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2667 | 70 | 70-3 | 20998 | Phase A Line-to-Neutral Voltage Max value | MAX_VLN_a_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2668 | 70 | 70-4 | 21000 | Phase A Line-to-Neutral Voltage Max value Timestamp | MAX_VLNTS_a |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2669 | 70 | 70-5 | 21004 | Phase B Line-to-Neutral Voltage Max value | MAX_VLN_b_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2670 | 70 | 70-6 | 21006 | Phase B Line-to-Neutral Voltage Max value Timestamp | MAX_VLNTS_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2671 | 70 | 70-7 | 21010 | Phase C Line-to-Neutral Voltage Max value | MAX_VLN_c_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2672 | 70 | 70-8 | 21012 | Phase C Line-to-Neutral Voltage Max value Timestamp | MAX_VLNTS_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2673 | 70 | 70-9 | 21016 | Phase AB Line-to-Line Voltage Max value | MAX_VLL_ab_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2674 | 70 | 70-10 | 21018 | Phase AB Line-to-Line Voltage Max value Timestamp | MAX_VLLTS_ab_V |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2675 | 70 | 70-11 | 21022 | Phase BC Line-to-Line Voltage Max value | MAX_VLL_bc_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2676 | 70 | 70-12 | 21024 | Phase BC Line-to-Line Voltage Max value Timestamp | MAX_VLLTS_bc_V |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2677 | 70 | 70-13 | 21028 | Phase CA Line-to-Line Voltage Max value | MAX_VLL_ca_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2678 | 70 | 70-14 | 21030 | Phase CA Line-to-Line Voltage Max value Timestamp | MAX_VLLTS_ca_V |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2679 | 71 | 71-1 | 21034 | Phase A Current Max value | MAX_I_a_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2680 | 71 | 71-2 | 21036 | Phase A Current Max value Timestamp | MAX_TS_I_a_A |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2681 | 71 | 71-3 | 21040 | Phase A Active Power Max value | MAX_P_a_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2682 | 71 | 71-4 | 21042 | Phase A Active Power Max value Timestamp | MAX_TS_P_a |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2683 | 71 | 71-5 | 21046 | Phase A Reactive Power Max value | MAX_Q_a_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2684 | 71 | 71-6 | 21048 | Phase A Reactive Power Max value Timestamp | MAX_TS_Q_a |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2685 | 71 | 71-7 | 21052 | Phase A Apparent Power Max value | MAX_S_a_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2686 | 71 | 71-8 | 21054 | Phase A Apparent Power Max value Timestamp | MAX_TS_S_a |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2687 | 71 | 71-9 | 21058 | Phase A Power Factor Max value | MAX_PF_a | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2688 | 71 | 71-10 | 21060 | Phase A Power Factor Max value Timestamp | MAX_TS_PF_a |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2689 | 71 | 71-11 | 21064 | Phase A Voltage THD Max value | MAX_THD_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2690 | 71 | 71-12 | 21066 | Phase A Voltage THD Max value Timestamp | MAX_TS_THD_V_a |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 23
2691 | 71 | 71-13 | 21070 | Phase B Current Max value | MAX_I_b_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2692 | 71 | 71-14 | 21072 | Phase B Current Max value Timestamp | MAX_TS_I_b_A |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2693 | 71 | 71-15 | 21076 | Phase B Active Power Max value | MAX_P_b_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2694 | 71 | 71-16 | 21078 | Phase B Active Power Max value Timestamp | MAX_TS_P_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2695 | 71 | 71-17 | 21082 | Phase B Reactive Power Max value | MAX_Q_b_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2696 | 71 | 71-18 | 21084 | Phase B Reactive Power Max value Timestamp | MAX_TS_Q_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2697 | 71 | 71-19 | 21088 | Phase B Apparent Power Max value | MAX_S_b_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2698 | 71 | 71-20 | 21090 | Phase B Apparent Power Max value Timestamp | MAX_TS_S_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2699 | 71 | 71-21 | 21094 | Phase B Power Factor Max value | MAX_PF_b | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2700 | 71 | 71-22 | 21096 | Phase B Power Factor Max value Timestamp | MAX_TS_PF_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2701 | 71 | 71-23 | 21100 | Phase B Voltage THD Max value | MAX_THD_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2702 | 71 | 71-24 | 21102 | Phase B Voltage THD Max value Timestamp | MAX_TS_THD_V_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2703 | 71 | 71-25 | 21106 | Phase C Current Max value | MAX_I_c_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2704 | 71 | 71-26 | 21108 | Phase C Current Max value Timestamp | MAX_TS_I_c_A |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2705 | 71 | 71-27 | 21112 | Phase C Active Power Max value | MAX_P_c_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2706 | 71 | 71-28 | 21114 | Phase C Active Power Max value Timestamp | MAX_TS_P_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2707 | 71 | 71-29 | 21118 | Phase C Reactive Power Max value | MAX_Q_c_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2708 | 71 | 71-30 | 21120 | Phase C Reactive Power Max value Timestamp | MAX_TS_Q_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2709 | 71 | 71-31 | 21124 | Phase C Apparent Power Max value | MAX_S_c_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2710 | 71 | 71-32 | 21126 | Phase C Apparent Power Max value Timestamp | MAX_TS_S_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2711 | 71 | 71-33 | 21130 | Phase C Power Factor Max value | MAX_PF_c | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2712 | 71 | 71-34 | 21132 | Phase C Power Factor Max value Timestamp | MAX_TS_PF_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2713 | 71 | 71-35 | 21136 | Phase C Voltage THD Max value | MAX_THD_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2714 | 71 | 71-36 | 21138 | Phase C Voltage THD Max value Timestamp | MAX_TS_THD_V_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2715 | 71 | 71-37 | 21142 | Voltage Unbalance Factor Magnitude Max value | MAX_UNBL_V_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
2716 | 71 | 71-38 | 21144 | Voltage Unbalance Factor Magnitude Max value Timestamp | MAX_UNBLTS_V_% |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
2717 | 72 | 72-1 | 21148 | Input Channel 1 Current Max value | MAX_I_001_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2718 | 72 | 72-2 | 21150 | Input Channel 1 Current Max value Timestamp | MAX_TS_I_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2719 | 72 | 72-3 | 21154 | Input Channel 1 Active Power Max value | MAX_P_001_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2720 | 72 | 72-4 | 21156 | Input Channel 1 Active Power Max value Timestamp | MAX_TS_P_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2721 | 72 | 72-5 | 21160 | Input Channel 1 Reactive Power Max value | MAX_Q_001_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2722 | 72 | 72-6 | 21162 | Input Channel 1 Reactive Power Max value Timestamp | MAX_TS_Q_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2723 | 72 | 72-7 | 21166 | Input Channel 1 Apparent Power Max value | MAX_S_001_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2724 | 72 | 72-8 | 21168 | Input Channel 1 Apparent Power Max value Timestamp | MAX_TS_S_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2725 | 72 | 72-9 | 21172 | Input Channel 1 Power Factor Max value | MAX_PF_001 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2726 | 72 | 72-10 | 21174 | Input Channel 1 Power Factor Max value Timestamp | MAX_TS_PF_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2727 | 72 | 72-11 | 21178 | Input Channel 1 Current THD Max value | MAX_THD_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2728 | 72 | 72-12 | 21180 | Input Channel 1 Current THD Max value Timestamp | MAX_TS_THD_I_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2729 | 72 | 72-13 | 21184 | Input Channel 2 Current Max value | MAX_I_002_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2730 | 72 | 72-14 | 21186 | Input Channel 2 Current Max value Timestamp | MAX_TS_I_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2731 | 72 | 72-15 | 21190 | Input Channel 2 Active Power Max value | MAX_P_002_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2732 | 72 | 72-16 | 21192 | Input Channel 2 Active Power Max value Timestamp | MAX_TS_P_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2733 | 72 | 72-17 | 21196 | Input Channel 2 Reactive Power Max value | MAX_Q_002_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2734 | 72 | 72-18 | 21198 | Input Channel 2 Reactive Power Max value Timestamp | MAX_TS_Q_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2735 | 72 | 72-19 | 21202 | Input Channel 2 Apparent Power Max value | MAX_S_002_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2736 | 72 | 72-20 | 21204 | Input Channel 2 Apparent Power Max value Timestamp | MAX_TS_S_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2737 | 72 | 72-21 | 21208 | Input Channel 2 Power Factor Max value | MAX_PF_002 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2738 | 72 | 72-22 | 21210 | Input Channel 2 Power Factor Max value Timestamp | MAX_TS_PF_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2739 | 72 | 72-23 | 21214 | Input Channel 2 Current THD Max value | MAX_THD_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2740 | 72 | 72-24 | 21216 | Input Channel 2 Current THD Max value Timestamp | MAX_TS_THD_I_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2741 | 72 | 72-25 | 21220 | Input Channel 3 Current Max value | MAX_I_003_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2742 | 72 | 72-26 | 21222 | Input Channel 3 Current Max value Timestamp | MAX_TS_I_003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2743 | 72 | 72-27 | 21226 | Input Channel 3 Active Power Max value | MAX_P_003_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2744 | 72 | 72-28 | 21228 | Input Channel 3 Active Power Max value Timestamp | MAX_TS_P_003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2745 | 72 | 72-29 | 21232 | Input Channel 3 Reactive Power Max value | MAX_Q_003_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2746 | 72 | 72-30 | 21234 | Input Channel 3 Reactive Power Max value Timestamp | MAX_TS_Q_003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2747 | 72 | 72-31 | 21238 | Input Channel 3 Apparent Power Max value | MAX_S_003_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2748 | 72 | 72-32 | 21240 | Input Channel 3 Apparent Power Max value Timestamp | MAX_TS_S_003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2749 | 72 | 72-33 | 21244 | Input Channel 3 Power Factor Max value | MAX_PF_003 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2750 | 72 | 72-34 | 21246 | Input Channel 3 Power Factor Max value Timestamp | MAX_TS_PF_003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2751 | 72 | 72-35 | 21250 | Input Channel 3 Current THD Max value | MAX_THD_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2752 | 72 | 72-36 | 21252 | Input Channel 3 Current THD Max value Timestamp | MAX_TS_THD_I_003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2753 | 73 | 73-1 | 21256 | Input Channel 4 Current Max value | MAX_I_004_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2754 | 73 | 73-2 | 21258 | Input Channel 4 Current Max value Timestamp | MAX_TS_I_004 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
2755 | 73 | 73-3 | 21262 | Input Channel 4 Active Power Max value | MAX_P_004_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2756 | 73 | 73-4 | 21264 | Input Channel 4 Active Power Max value Timestamp | MAX_TS_P_004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2757 | 73 | 73-5 | 21268 | Input Channel 4 Reactive Power Max value | MAX_Q_004_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2758 | 73 | 73-6 | 21270 | Input Channel 4 Reactive Power Max value Timestamp | MAX_TS_Q_004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2759 | 73 | 73-7 | 21274 | Input Channel 4 Apparent Power Max value | MAX_S_004_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2760 | 73 | 73-8 | 21276 | Input Channel 4 Apparent Power Max value Timestamp | MAX_TS_S_004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2761 | 73 | 73-9 | 21280 | Input Channel 4 Power Factor Max value | MAX_PF_004 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2762 | 73 | 73-10 | 21282 | Input Channel 4 Power Factor Max value Timestamp | MAX_TS_PF_004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2763 | 73 | 73-11 | 21286 | Input Channel 4 Current THD Max value | MAX_THD_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2764 | 73 | 73-12 | 21288 | Input Channel 4 Current THD Max value Timestamp | MAX_TS_THD_I_004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2765 | 73 | 73-13 | 21292 | Input Channel 5 Current Max value | MAX_I_005_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2766 | 73 | 73-14 | 21294 | Input Channel 5 Current Max value Timestamp | MAX_TS_I_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2767 | 73 | 73-15 | 21298 | Input Channel 5 Active Power Max value | MAX_P_005_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2768 | 73 | 73-16 | 21300 | Input Channel 5 Active Power Max value Timestamp | MAX_TS_P_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2769 | 73 | 73-17 | 21304 | Input Channel 5 Reactive Power Max value | MAX_Q_005_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2770 | 73 | 73-18 | 21306 | Input Channel 5 Reactive Power Max value Timestamp | MAX_TS_Q_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2771 | 73 | 73-19 | 21310 | Input Channel 5 Apparent Power Max value | MAX_S_005_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2772 | 73 | 73-20 | 21312 | Input Channel 5 Apparent Power Max value Timestamp | MAX_TS_S_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2773 | 73 | 73-21 | 21316 | Input Channel 5 Power Factor Max value | MAX_PF_005 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2774 | 73 | 73-22 | 21318 | Input Channel 5 Power Factor Max value Timestamp | MAX_TS_PF_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2775 | 73 | 73-23 | 21322 | Input Channel 5 Current THD Max value | MAX_THD_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2776 | 73 | 73-24 | 21324 | Input Channel 5 Current THD Max value Timestamp | MAX_TS_THD_I_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2777 | 73 | 73-25 | 21328 | Input Channel 6 Current Max value | MAX_I_006_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2778 | 73 | 73-26 | 21330 | Input Channel 6 Current Max value Timestamp | MAX_TS_I_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2779 | 73 | 73-27 | 21334 | Input Channel 6 Active Power Max value | MAX_P_006_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2780 | 73 | 73-28 | 21336 | Input Channel 6 Active Power Max value Timestamp | MAX_TS_P_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2781 | 73 | 73-29 | 21340 | Input Channel 6 Reactive Power Max value | MAX_Q_006_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2782 | 73 | 73-30 | 21342 | Input Channel 6 Reactive Power Max value Timestamp | MAX_TS_Q_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2783 | 73 | 73-31 | 21346 | Input Channel 6 Apparent Power Max value | MAX_S_006_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2784 | 73 | 73-32 | 21348 | Input Channel 6 Apparent Power Max value Timestamp | MAX_TS_S_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2785 | 73 | 73-33 | 21352 | Input Channel 6 Power Factor Max value | MAX_PF_006 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2786 | 73 | 73-34 | 21354 | Input Channel 6 Power Factor Max value Timestamp | MAX_TS_PF_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2787 | 73 | 73-35 | 21358 | Input Channel 6 Current THD Max value | MAX_THD_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2788 | 73 | 73-36 | 21360 | Input Channel 6 Current THD Max value Timestamp | MAX_TS_THD_I_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2789 | 74 | 74-1 | 21364 | Input Channel 7 Current Max value | MAX_I_007_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2790 | 74 | 74-2 | 21366 | Input Channel 7 Current Max value Timestamp | MAX_TS_I_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2791 | 74 | 74-3 | 21370 | Input Channel 7 Active Power Max value | MAX_P_007_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2792 | 74 | 74-4 | 21372 | Input Channel 7 Active Power Max value Timestamp | MAX_TS_P_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2793 | 74 | 74-5 | 21376 | Input Channel 7 Reactive Power Max value | MAX_Q_007_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2794 | 74 | 74-6 | 21378 | Input Channel 7 Reactive Power Max value Timestamp | MAX_TS_Q_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2795 | 74 | 74-7 | 21382 | Input Channel 7 Apparent Power Max value | MAX_S_007_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2796 | 74 | 74-8 | 21384 | Input Channel 7 Apparent Power Max value Timestamp | MAX_TS_S_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2797 | 74 | 74-9 | 21388 | Input Channel 7 Power Factor Max value | MAX_PF_007 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2798 | 74 | 74-10 | 21390 | Input Channel 7 Power Factor Max value Timestamp | MAX_TS_PF_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2799 | 74 | 74-11 | 21394 | Input Channel 7 Current THD Max value | MAX_THD_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2800 | 74 | 74-12 | 21396 | Input Channel 7 Current THD Max value Timestamp | MAX_TS_THD_I_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2801 | 74 | 74-13 | 21400 | Input Channel 8 Current Max value | MAX_I_008_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2802 | 74 | 74-14 | 21402 | Input Channel 8 Current Max value Timestamp | MAX_TS_I_008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2803 | 74 | 74-15 | 21406 | Input Channel 8 Active Power Max value | MAX_P_008_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2804 | 74 | 74-16 | 21408 | Input Channel 8 Active Power Max value Timestamp | MAX_TS_P_008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2805 | 74 | 74-17 | 21412 | Input Channel 8 Reactive Power Max value | MAX_Q_008_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2806 | 74 | 74-18 | 21414 | Input Channel 8 Reactive Power Max value Timestamp | MAX_TS_Q_008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2807 | 74 | 74-19 | 21418 | Input Channel 8 Apparent Power Max value | MAX_S_008_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2808 | 74 | 74-20 | 21420 | Input Channel 8 Apparent Power Max value Timestamp | MAX_TS_S_008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2809 | 74 | 74-21 | 21424 | Input Channel 8 Power Factor Max value | MAX_PF_008 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2810 | 74 | 74-22 | 21426 | Input Channel 8 Power Factor Max value Timestamp | MAX_TS_PF_008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2811 | 74 | 74-23 | 21430 | Input Channel 8 Current THD Max value | MAX_THD_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2812 | 74 | 74-24 | 21432 | Input Channel 8 Current THD Max value Timestamp | MAX_TS_THD_I_008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2813 | 74 | 74-25 | 21436 | Input Channel 9 Current Max value | MAX_I_009_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2814 | 74 | 74-26 | 21438 | Input Channel 9 Current Max value Timestamp | MAX_TS_I_009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2815 | 74 | 74-27 | 21442 | Input Channel 9 Active Power Max value | MAX_P_009_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2816 | 74 | 74-28 | 21444 | Input Channel 9 Active Power Max value Timestamp | MAX_TS_P_009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2817 | 74 | 74-29 | 21448 | Input Channel 9 Reactive Power Max value | MAX_Q_009_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2818 | 74 | 74-30 | 21450 | Input Channel 9 Reactive Power Max value Timestamp | MAX_TS_Q_009 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
2819 | 74 | 74-31 | 21454 | Input Channel 9 Apparent Power Max value | MAX_S_009_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2820 | 74 | 74-32 | 21456 | Input Channel 9 Apparent Power Max value Timestamp | MAX_TS_S_009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2821 | 74 | 74-33 | 21460 | Input Channel 9 Power Factor Max value | MAX_PF_009 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2822 | 74 | 74-34 | 21462 | Input Channel 9 Power Factor Max value Timestamp | MAX_TS_PF_009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2823 | 74 | 74-35 | 21466 | Input Channel 9 Current THD Max value | MAX_THD_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2824 | 74 | 74-36 | 21468 | Input Channel 9 Current THD Max value Timestamp | MAX_TS_THD_I_009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2825 | 75 | 75-1 | 21472 | Input Channel 10 Current Max value | MAX_I_010_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2826 | 75 | 75-2 | 21474 | Input Channel 10 Current Max value Timestamp | MAX_TS_I_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2827 | 75 | 75-3 | 21478 | Input Channel 10 Active Power Max value | MAX_P_010_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2828 | 75 | 75-4 | 21480 | Input Channel 10 Active Power Max value Timestamp | MAX_TS_P_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2829 | 75 | 75-5 | 21484 | Input Channel 10 Reactive Power Max value | MAX_Q_010_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2830 | 75 | 75-6 | 21486 | Input Channel 10 Reactive Power Max value Timestamp | MAX_TS_Q_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2831 | 75 | 75-7 | 21490 | Input Channel 10 Apparent Power Max value | MAX_S_010_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2832 | 75 | 75-8 | 21492 | Input Channel 10 Apparent Power Max value Timestamp | MAX_TS_S_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2833 | 75 | 75-9 | 21496 | Input Channel 10 Power Factor Max value | MAX_PF_010 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2834 | 75 | 75-10 | 21498 | Input Channel 10 Power Factor Max value Timestamp | MAX_TS_PF_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2835 | 75 | 75-11 | 21502 | Input Channel 10 Current THD Max value | MAX_THD_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2836 | 75 | 75-12 | 21504 | Input Channel 10 Current THD Max value Timestamp | MAX_TS_THD_I_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2837 | 75 | 75-13 | 21508 | Input Channel 11 Current Max value | MAX_I_011_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2838 | 75 | 75-14 | 21510 | Input Channel 11 Current Max value Timestamp | MAX_TS_I_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2839 | 75 | 75-15 | 21514 | Input Channel 11 Active Power Max value | MAX_P_011_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2840 | 75 | 75-16 | 21516 | Input Channel 11 Active Power Max value Timestamp | MAX_TS_P_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2841 | 75 | 75-17 | 21520 | Input Channel 11 Reactive Power Max value | MAX_Q_011_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2842 | 75 | 75-18 | 21522 | Input Channel 11 Reactive Power Max value Timestamp | MAX_TS_Q_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2843 | 75 | 75-19 | 21526 | Input Channel 11 Apparent Power Max value | MAX_S_011_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2844 | 75 | 75-20 | 21528 | Input Channel 11 Apparent Power Max value Timestamp | MAX_TS_S_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2845 | 75 | 75-21 | 21532 | Input Channel 11 Power Factor Max value | MAX_PF_011 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2846 | 75 | 75-22 | 21534 | Input Channel 11 Power Factor Max value Timestamp | MAX_TS_PF_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2847 | 75 | 75-23 | 21538 | Input Channel 11 Current THD Max value | MAX_THD_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2848 | 75 | 75-24 | 21540 | Input Channel 11 Current THD Max value Timestamp | MAX_TS_THD_I_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2849 | 75 | 75-25 | 21544 | Input Channel 12 Current Max value | MAX_I_012_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2850 | 75 | 75-26 | 21546 | Input Channel 12 Current Max value Timestamp | MAX_TS_I_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2851 | 75 | 75-27 | 21550 | Input Channel 12 Active Power Max value | MAX_P_012_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2852 | 75 | 75-28 | 21552 | Input Channel 12 Active Power Max value Timestamp | MAX_TS_P_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2853 | 75 | 75-29 | 21556 | Input Channel 12 Reactive Power Max value | MAX_Q_012_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2854 | 75 | 75-30 | 21558 | Input Channel 12 Reactive Power Max value Timestamp | MAX_TS_Q_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2855 | 75 | 75-31 | 21562 | Input Channel 12 Apparent Power Max value | MAX_S_012_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2856 | 75 | 75-32 | 21564 | Input Channel 12 Apparent Power Max value Timestamp | MAX_TS_S_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2857 | 75 | 75-33 | 21568 | Input Channel 12 Power Factor Max value | MAX_PF_012 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2858 | 75 | 75-34 | 21570 | Input Channel 12 Power Factor Max value Timestamp | MAX_TS_PF_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2859 | 75 | 75-35 | 21574 | Input Channel 12 Current THD Max value | MAX_THD_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2860 | 75 | 75-36 | 21576 | Input Channel 12 Current THD Max value Timestamp | MAX_TS_THD_I_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2861 | 76 | 76-1 | 21580 | Input Channel 13 Current Max value | MAX_I_013_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2862 | 76 | 76-2 | 21582 | Input Channel 13 Current Max value Timestamp | MAX_TS_I_013 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2863 | 76 | 76-3 | 21586 | Input Channel 13 Active Power Max value | MAX_P_013_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2864 | 76 | 76-4 | 21588 | Input Channel 13 Active Power Max value Timestamp | MAX_TS_P_013 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2865 | 76 | 76-5 | 21592 | Input Channel 13 Reactive Power Max value | MAX_Q_013_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2866 | 76 | 76-6 | 21594 | Input Channel 13 Reactive Power Max value Timestamp | MAX_TS_Q_013 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2867 | 76 | 76-7 | 21598 | Input Channel 13 Apparent Power Max value | MAX_S_013_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2868 | 76 | 76-8 | 21600 | Input Channel 13 Apparent Power Max value Timestamp | MAX_TS_S_013 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2869 | 76 | 76-9 | 21604 | Input Channel 13 Power Factor Max value | MAX_PF_013 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2870 | 76 | 76-10 | 21606 | Input Channel 13 Power Factor Max value Timestamp | MAX_TS_PF_013 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2871 | 76 | 76-11 | 21610 | Input Channel 13 Current THD Max value | MAX_THD_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2872 | 76 | 76-12 | 21612 | Input Channel 13 Current THD Max value Timestamp | MAX_TS_THD_I_013 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2873 | 76 | 76-13 | 21616 | Input Channel 14 Current Max value | MAX_I_014_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2874 | 76 | 76-14 | 21618 | Input Channel 14 Current Max value Timestamp | MAX_TS_I_014 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2875 | 76 | 76-15 | 21622 | Input Channel 14 Active Power Max value | MAX_P_014_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2876 | 76 | 76-16 | 21624 | Input Channel 14 Active Power Max value Timestamp | MAX_TS_P_014 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2877 | 76 | 76-17 | 21628 | Input Channel 14 Reactive Power Max value | MAX_Q_014_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2878 | 76 | 76-18 | 21630 | Input Channel 14 Reactive Power Max value Timestamp | MAX_TS_Q_014 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2879 | 76 | 76-19 | 21634 | Input Channel 14 Apparent Power Max value | MAX_S_014_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2880 | 76 | 76-20 | 21636 | Input Channel 14 Apparent Power Max value Timestamp | MAX_TS_S_014 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2881 | 76 | 76-21 | 21640 | Input Channel 14 Power Factor Max value | MAX_PF_014 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2882 | 76 | 76-22 | 21642 | Input Channel 14 Power Factor Max value Timestamp | MAX_TS_PF_014 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
2883 | 76 | 76-23 | 21646 | Input Channel 14 Current THD Max value | MAX_THD_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2884 | 76 | 76-24 | 21648 | Input Channel 14 Current THD Max value Timestamp | MAX_TS_THD_I_014 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2885 | 76 | 76-25 | 21652 | Input Channel 15 Current Max value | MAX_I_015_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2886 | 76 | 76-26 | 21654 | Input Channel 15 Current Max value Timestamp | MAX_TS_I_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2887 | 76 | 76-27 | 21658 | Input Channel 15 Active Power Max value | MAX_P_015_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2888 | 76 | 76-28 | 21660 | Input Channel 15 Active Power Max value Timestamp | MAX_TS_P_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2889 | 76 | 76-29 | 21664 | Input Channel 15 Reactive Power Max value | MAX_Q_015_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2890 | 76 | 76-30 | 21666 | Input Channel 15 Reactive Power Max value Timestamp | MAX_TS_Q_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2891 | 76 | 76-31 | 21670 | Input Channel 15 Apparent Power Max value | MAX_S_015_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2892 | 76 | 76-32 | 21672 | Input Channel 15 Apparent Power Max value Timestamp | MAX_TS_S_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2893 | 76 | 76-33 | 21676 | Input Channel 15 Power Factor Max value | MAX_PF_015 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2894 | 76 | 76-34 | 21678 | Input Channel 15 Power Factor Max value Timestamp | MAX_TS_PF_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2895 | 76 | 76-35 | 21682 | Input Channel 15 Current THD Max value | MAX_THD_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2896 | 76 | 76-36 | 21684 | Input Channel 15 Current THD Max value Timestamp | MAX_TS_THD_I_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2897 | 77 | 77-1 | 21688 | Input Channel 16 Current Max value | MAX_I_016_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2898 | 77 | 77-2 | 21690 | Input Channel 16 Current Max value Timestamp | MAX_TS_I_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2899 | 77 | 77-3 | 21694 | Input Channel 16 Active Power Max value | MAX_P_016_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2900 | 77 | 77-4 | 21696 | Input Channel 16 Active Power Max value Timestamp | MAX_TS_P_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2901 | 77 | 77-5 | 21700 | Input Channel 16 Reactive Power Max value | MAX_Q_016_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2902 | 77 | 77-6 | 21702 | Input Channel 16 Reactive Power Max value Timestamp | MAX_TS_Q_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2903 | 77 | 77-7 | 21706 | Input Channel 16 Apparent Power Max value | MAX_S_016_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2904 | 77 | 77-8 | 21708 | Input Channel 16 Apparent Power Max value Timestamp | MAX_TS_S_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2905 | 77 | 77-9 | 21712 | Input Channel 16 Power Factor Max value | MAX_PF_016 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2906 | 77 | 77-10 | 21714 | Input Channel 16 Power Factor Max value Timestamp | MAX_TS_PF_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2907 | 77 | 77-11 | 21718 | Input Channel 16 Current THD Max value | MAX_THD_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2908 | 77 | 77-12 | 21720 | Input Channel 16 Current THD Max value Timestamp | MAX_TS_THD_I_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2909 | 77 | 77-13 | 21724 | Input Channel 17 Current Max value | MAX_I_017_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2910 | 77 | 77-14 | 21726 | Input Channel 17 Current Max value Timestamp | MAX_TS_I_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2911 | 77 | 77-15 | 21730 | Input Channel 17 Active Power Max value | MAX_P_017_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2912 | 77 | 77-16 | 21732 | Input Channel 17 Active Power Max value Timestamp | MAX_TS_P_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2913 | 77 | 77-17 | 21736 | Input Channel 17 Reactive Power Max value | MAX_Q_017_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2914 | 77 | 77-18 | 21738 | Input Channel 17 Reactive Power Max value Timestamp | MAX_TS_Q_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2915 | 77 | 77-19 | 21742 | Input Channel 17 Apparent Power Max value | MAX_S_017_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2916 | 77 | 77-20 | 21744 | Input Channel 17 Apparent Power Max value Timestamp | MAX_TS_S_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2917 | 77 | 77-21 | 21748 | Input Channel 17 Power Factor Max value | MAX_PF_017 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2918 | 77 | 77-22 | 21750 | Input Channel 17 Power Factor Max value Timestamp | MAX_TS_PF_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2919 | 77 | 77-23 | 21754 | Input Channel 17 Current THD Max value | MAX_THD_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2920 | 77 | 77-24 | 21756 | Input Channel 17 Current THD Max value Timestamp | MAX_TS_THD_I_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2921 | 77 | 77-25 | 21760 | Input Channel 18 Current Max value | MAX_I_018_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2922 | 77 | 77-26 | 21762 | Input Channel 18 Current Max value Timestamp | MAX_TS_I_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2923 | 77 | 77-27 | 21766 | Input Channel 18 Active Power Max value | MAX_P_018_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2924 | 77 | 77-28 | 21768 | Input Channel 18 Active Power Max value Timestamp | MAX_TS_P_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2925 | 77 | 77-29 | 21772 | Input Channel 18 Reactive Power Max value | MAX_Q_018_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2926 | 77 | 77-30 | 21774 | Input Channel 18 Reactive Power Max value Timestamp | MAX_TS_Q_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2927 | 77 | 77-31 | 21778 | Input Channel 18 Apparent Power Max value | MAX_S_018_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2928 | 77 | 77-32 | 21780 | Input Channel 18 Apparent Power Max value Timestamp | MAX_TS_S_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2929 | 77 | 77-33 | 21784 | Input Channel 18 Power Factor Max value | MAX_PF_018 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2930 | 77 | 77-34 | 21786 | Input Channel 18 Power Factor Max value Timestamp | MAX_TS_PF_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2931 | 77 | 77-35 | 21790 | Input Channel 18 Current THD Max value | MAX_THD_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2932 | 77 | 77-36 | 21792 | Input Channel 18 Current THD Max value Timestamp | MAX_TS_THD_I_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2933 | 78 | 78-1 | 21796 | Input Channel 19 Current Max value | MAX_I_019_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2934 | 78 | 78-2 | 21798 | Input Channel 19 Current Max value Timestamp | MAX_TS_I_019 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2935 | 78 | 78-3 | 21802 | Input Channel 19 Active Power Max value | MAX_P_019_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2936 | 78 | 78-4 | 21804 | Input Channel 19 Active Power Max value Timestamp | MAX_TS_P_019 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2937 | 78 | 78-5 | 21808 | Input Channel 19 Reactive Power Max value | MAX_Q_019_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2938 | 78 | 78-6 | 21810 | Input Channel 19 Reactive Power Max value Timestamp | MAX_TS_Q_019 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2939 | 78 | 78-7 | 21814 | Input Channel 19 Apparent Power Max value | MAX_S_019_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2940 | 78 | 78-8 | 21816 | Input Channel 19 Apparent Power Max value Timestamp | MAX_TS_S_019 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2941 | 78 | 78-9 | 21820 | Input Channel 19 Power Factor Max value | MAX_PF_019 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2942 | 78 | 78-10 | 21822 | Input Channel 19 Power Factor Max value Timestamp | MAX_TS_PF_019 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2943 | 78 | 78-11 | 21826 | Input Channel 19 Current THD Max value | MAX_THD_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2944 | 78 | 78-12 | 21828 | Input Channel 19 Current THD Max value Timestamp | MAX_TS_THD_I_019 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2945 | 78 | 78-13 | 21832 | Input Channel 20 Current Max value | MAX_I_020_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2946 | 78 | 78-14 | 21834 | Input Channel 20 Current Max value Timestamp | MAX_TS_I_020 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
2947 | 78 | 78-15 | 21838 | Input Channel 20 Active Power Max value | MAX_P_020_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2948 | 78 | 78-16 | 21840 | Input Channel 20 Active Power Max value Timestamp | MAX_TS_P_020 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2949 | 78 | 78-17 | 21844 | Input Channel 20 Reactive Power Max value | MAX_Q_020_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2950 | 78 | 78-18 | 21846 | Input Channel 20 Reactive Power Max value Timestamp | MAX_TS_Q_020 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2951 | 78 | 78-19 | 21850 | Input Channel 20 Apparent Power Max value | MAX_S_020_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2952 | 78 | 78-20 | 21852 | Input Channel 20 Apparent Power Max value Timestamp | MAX_TS_S_020 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2953 | 78 | 78-21 | 21856 | Input Channel 20 Power Factor Max value | MAX_PF_020 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2954 | 78 | 78-22 | 21858 | Input Channel 20 Power Factor Max value Timestamp | MAX_TS_PF_020 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2955 | 78 | 78-23 | 21862 | Input Channel 20 Current THD Max value | MAX_THD_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2956 | 78 | 78-24 | 21864 | Input Channel 20 Current THD Max value Timestamp | MAX_TS_THD_I_020 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2957 | 78 | 78-25 | 21868 | Input Channel 21 Current Max value | MAX_I_021_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2958 | 78 | 78-26 | 21870 | Input Channel 21 Current Max value Timestamp | MAX_TS_I_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2959 | 78 | 78-27 | 21874 | Input Channel 21 Active Power Max value | MAX_P_021_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2960 | 78 | 78-28 | 21876 | Input Channel 21 Active Power Max value Timestamp | MAX_TS_P_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2961 | 78 | 78-29 | 21880 | Input Channel 21 Reactive Power Max value | MAX_Q_021_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2962 | 78 | 78-30 | 21882 | Input Channel 21 Reactive Power Max value Timestamp | MAX_TS_Q_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2963 | 78 | 78-31 | 21886 | Input Channel 21 Apparent Power Max value | MAX_S_021_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2964 | 78 | 78-32 | 21888 | Input Channel 21 Apparent Power Max value Timestamp | MAX_TS_S_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2965 | 78 | 78-33 | 21892 | Input Channel 21 Power Factor Max value | MAX_PF_021 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2966 | 78 | 78-34 | 21894 | Input Channel 21 Power Factor Max value Timestamp | MAX_TS_PF_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2967 | 78 | 78-35 | 21898 | Input Channel 21 Current THD Max value | MAX_THD_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2968 | 78 | 78-36 | 21900 | Input Channel 21 Current THD Max value Timestamp | MAX_TS_THD_I_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2969 | 79 | 79-1 | 21904 | Input Channel 22 Current Max value | MAX_I_022_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2970 | 79 | 79-2 | 21906 | Input Channel 22 Current Max value Timestamp | MAX_TS_I_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2971 | 79 | 79-3 | 21910 | Input Channel 22 Active Power Max value | MAX_P_022_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2972 | 79 | 79-4 | 21912 | Input Channel 22 Active Power Max value Timestamp | MAX_TS_P_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2973 | 79 | 79-5 | 21916 | Input Channel 22 Reactive Power Max value | MAX_Q_022_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2974 | 79 | 79-6 | 21918 | Input Channel 22 Reactive Power Max value Timestamp | MAX_TS_Q_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2975 | 79 | 79-7 | 21922 | Input Channel 22 Apparent Power Max value | MAX_S_022_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2976 | 79 | 79-8 | 21924 | Input Channel 22 Apparent Power Max value Timestamp | MAX_TS_S_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2977 | 79 | 79-9 | 21928 | Input Channel 22 Power Factor Max value | MAX_PF_022 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2978 | 79 | 79-10 | 21930 | Input Channel 22 Power Factor Max value Timestamp | MAX_TS_PF_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2979 | 79 | 79-11 | 21934 | Input Channel 22 Current THD Max value | MAX_THD_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2980 | 79 | 79-12 | 21936 | Input Channel 22 Current THD Max value Timestamp | MAX_TS_THD_I_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2981 | 79 | 79-13 | 21940 | Input Channel 23 Current Max value | MAX_I_023_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2982 | 79 | 79-14 | 21942 | Input Channel 23 Current Max value Timestamp | MAX_TS_I_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2983 | 79 | 79-15 | 21946 | Input Channel 23 Active Power Max value | MAX_P_023_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2984 | 79 | 79-16 | 21948 | Input Channel 23 Active Power Max value Timestamp | MAX_TS_P_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2985 | 79 | 79-17 | 21952 | Input Channel 23 Reactive Power Max value | MAX_Q_023_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2986 | 79 | 79-18 | 21954 | Input Channel 23 Reactive Power Max value Timestamp | MAX_TS_Q_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2987 | 79 | 79-19 | 21958 | Input Channel 23 Apparent Power Max value | MAX_S_023_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2988 | 79 | 79-20 | 21960 | Input Channel 23 Apparent Power Max value Timestamp | MAX_TS_S_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2989 | 79 | 79-21 | 21964 | Input Channel 23 Power Factor Max value | MAX_PF_023 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2990 | 79 | 79-22 | 21966 | Input Channel 23 Power Factor Max value Timestamp | MAX_TS_PF_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2991 | 79 | 79-23 | 21970 | Input Channel 23 Current THD Max value | MAX_THD_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2992 | 79 | 79-24 | 21972 | Input Channel 23 Current THD Max value Timestamp | MAX_TS_THD_I_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2993 | 79 | 79-25 | 21976 | Input Channel 24 Current Max value | MAX_I_024_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2994 | 79 | 79-26 | 21978 | Input Channel 24 Current Max value Timestamp | MAX_TS_I_024 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2995 | 79 | 79-27 | 21982 | Input Channel 24 Active Power Max value | MAX_P_024_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2996 | 79 | 79-28 | 21984 | Input Channel 24 Active Power Max value Timestamp | MAX_TS_P_024 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2997 | 79 | 79-29 | 21988 | Input Channel 24 Reactive Power Max value | MAX_Q_024_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
2998 | 79 | 79-30 | 21990 | Input Channel 24 Reactive Power Max value Timestamp | MAX_TS_Q_024 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
2999 | 79 | 79-31 | 21994 | Input Channel 24 Apparent Power Max value | MAX_S_024_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3000 | 79 | 79-32 | 21996 | Input Channel 24 Apparent Power Max value Timestamp | MAX_TS_S_024 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3001 | 79 | 79-33 | 22000 | Input Channel 24 Power Factor Max value | MAX_PF_024 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3002 | 79 | 79-34 | 22002 | Input Channel 24 Power Factor Max value Timestamp | MAX_TS_PF_024 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3003 | 79 | 79-35 | 22006 | Input Channel 24 Current THD Max value | MAX_THD_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3004 | 79 | 79-36 | 22008 | Input Channel 24 Current THD Max value Timestamp | MAX_TS_THD_I_024 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3005 | 80 | 80-1 | 22012 | User Channel 1 Current Max value | MAX_I_s001_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3006 | 80 | 80-2 | 22014 | User Channel 1 Current Max value Timestamp | MAX_TS_I_s001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3007 | 80 | 80-3 | 22018 | User Channel 1 Active Power Max value | MAX_P_s001_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3008 | 80 | 80-4 | 22020 | User Channel 1 Active Power Max value Timestamp | MAX_TS_P_s001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3009 | 80 | 80-5 | 22024 | User Channel 1 Reactive Power Max value | MAX_Q_s001_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3010 | 80 | 80-6 | 22026 | User Channel 1 Reactive Power Max value Timestamp | MAX_TS_Q_s001 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
3011 | 80 | 80-7 | 22030 | User Channel 1 Apparent Power Max value | MAX_S_s001_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3012 | 80 | 80-8 | 22032 | User Channel 1 Apparent Power Max value Timestamp | MAX_TS_S_s001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3013 | 80 | 80-9 | 22036 | Max User Channel 1 Power Factor | MAX_PF_s001 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3014 | 80 | 80-10 | 22038 | Max User Channel 1 Power Factor Timestamp | MAX_TS_PF_s001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3015 | 80 | 80-11 | 22042 | User Channel 2 Current Max value | MAX_I_s002_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3016 | 80 | 80-12 | 22044 | User Channel 2 Current Max value Timestamp | MAX_TS_I_s002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3017 | 80 | 80-13 | 22048 | User Channel 2 Active Power Max value | MAX_P_s002_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3018 | 80 | 80-14 | 22050 | User Channel 2 Active Power Max value Timestamp | MAX_TS_P_s002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3019 | 80 | 80-15 | 22054 | User Channel 2 Reactive Power Max value | MAX_Q_s002_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3020 | 80 | 80-16 | 22056 | User Channel 2 Reactive Power Max value Timestamp | MAX_TS_Q_s002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3021 | 80 | 80-17 | 22060 | User Channel 2 Apparent Power Max value | MAX_S_s002_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3022 | 80 | 80-18 | 22062 | User Channel 2 Apparent Power Max value Timestamp | MAX_TS_S_s002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3023 | 80 | 80-19 | 22066 | Max User Channel 2 Power Factor | MAX_PF_s002 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3024 | 80 | 80-20 | 22068 | Max User Channel 2 Power Factor Timestamp | MAX_TS_PF_s002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3025 | 80 | 80-21 | 22072 | User Channel 3 Current Max value | MAX_I_s003_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3026 | 80 | 80-22 | 22074 | User Channel 3 Current Max value Timestamp | MAX_TS_I_s003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3027 | 80 | 80-23 | 22078 | User Channel 3 Active Power Max value | MAX_P_s003_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3028 | 80 | 80-24 | 22080 | User Channel 3 Active Power Max value Timestamp | MAX_TS_P_s003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3029 | 80 | 80-25 | 22084 | User Channel 3 Reactive Power Max value | MAX_Q_s003_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3030 | 80 | 80-26 | 22086 | User Channel 3 Reactive Power Max value Timestamp | MAX_TS_Q_s003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3031 | 80 | 80-27 | 22090 | User Channel 3 Apparent Power Max value | MAX_S_s003_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3032 | 80 | 80-28 | 22092 | User Channel 3 Apparent Power Max value Timestamp | MAX_TS_S_s003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3033 | 80 | 80-29 | 22096 | Max User Channel 3 Power Factor | MAX_PF_s003 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3034 | 80 | 80-30 | 22098 | Max User Channel 3 Power Factor Timestamp | MAX_TS_PF_s003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3035 | 80 | 80-31 | 22102 | User Channel 4 Current Max value | MAX_I_s004_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3036 | 80 | 80-32 | 22104 | User Channel 4 Current Max value Timestamp | MAX_TS_I_s004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3037 | 80 | 80-33 | 22108 | User Channel 4 Active Power Max value | MAX_P_s004_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3038 | 80 | 80-34 | 22110 | User Channel 4 Active Power Max value Timestamp | MAX_TS_P_s004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3039 | 80 | 80-35 | 22114 | User Channel 4 Reactive Power Max value | MAX_Q_s004_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3040 | 80 | 80-36 | 22116 | User Channel 4 Reactive Power Max value Timestamp | MAX_TS_Q_s004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3041 | 80 | 80-37 | 22120 | User Channel 4 Apparent Power Max value | MAX_S_s004_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3042 | 80 | 80-38 | 22122 | User Channel 4 Apparent Power Max value Timestamp | MAX_TS_S_s004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3043 | 80 | 80-39 | 22126 | Max User Channel 4 Power Factor | MAX_PF_s004 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3044 | 80 | 80-40 | 22128 | Max User Channel 4 Power Factor Timestamp | MAX_TS_PF_s004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3045 | 81 | 81-1 | 22132 | User Channel 5 Current Max value | MAX_I_s005_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3046 | 81 | 81-2 | 22134 | User Channel 5 Current Max value Timestamp | MAX_TS_I_s005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3047 | 81 | 81-3 | 22138 | User Channel 5 Active Power Max value | MAX_P_s005_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3048 | 81 | 81-4 | 22140 | User Channel 5 Active Power Max value Timestamp | MAX_TS_P_s005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3049 | 81 | 81-5 | 22144 | User Channel 5 Reactive Power Max value | MAX_Q_s005_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3050 | 81 | 81-6 | 22146 | User Channel 5 Reactive Power Max value Timestamp | MAX_TS_Q_s005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3051 | 81 | 81-7 | 22150 | User Channel 5 Apparent Power Max value | MAX_S_s005_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3052 | 81 | 81-8 | 22152 | User Channel 5 Apparent Power Max value Timestamp | MAX_TS_S_s005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3053 | 81 | 81-9 | 22156 | Max User Channel 5 Power Factor | MAX_PF_s005 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3054 | 81 | 81-10 | 22158 | Max User Channel 5 Power Factor Timestamp | MAX_TS_PF_s005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3055 | 81 | 81-11 | 22162 | User Channel 6 Current Max value | MAX_I_s006_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3056 | 81 | 81-12 | 22164 | User Channel 6 Current Max value Timestamp | MAX_TS_I_s006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3057 | 81 | 81-13 | 22168 | User Channel 6 Active Power Max value | MAX_P_s006_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3058 | 81 | 81-14 | 22170 | User Channel 6 Active Power Max value Timestamp | MAX_TS_P_s006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3059 | 81 | 81-15 | 22174 | User Channel 6 Reactive Power Max value | MAX_Q_s006_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3060 | 81 | 81-16 | 22176 | User Channel 6 Reactive Power Max value Timestamp | MAX_TS_Q_s006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3061 | 81 | 81-17 | 22180 | User Channel 6 Apparent Power Max value | MAX_S_s006_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3062 | 81 | 81-18 | 22182 | User Channel 6 Apparent Power Max value Timestamp | MAX_TS_S_s006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3063 | 81 | 81-19 | 22186 | Max User Channel 6 Power Factor | MAX_PF_s006 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3064 | 81 | 81-20 | 22188 | Max User Channel 6 Power Factor Timestamp | MAX_TS_PF_s006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3065 | 81 | 81-21 | 22192 | User Channel 7 Current Max value | MAX_I_s007_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3066 | 81 | 81-22 | 22194 | User Channel 7 Current Max value Timestamp | MAX_TS_I_s007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3067 | 81 | 81-23 | 22198 | User Channel 7 Active Power Max value | MAX_P_s007_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3068 | 81 | 81-24 | 22200 | User Channel 7 Active Power Max value Timestamp | MAX_TS_P_s007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3069 | 81 | 81-25 | 22204 | User Channel 7 Reactive Power Max value | MAX_Q_s007_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3070 | 81 | 81-26 | 22206 | User Channel 7 Reactive Power Max value Timestamp | MAX_TS_Q_s007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3071 | 81 | 81-27 | 22210 | User Channel 7 Apparent Power Max value | MAX_S_s007_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3072 | 81 | 81-28 | 22212 | User Channel 7 Apparent Power Max value Timestamp | MAX_TS_S_s007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3073 | 81 | 81-29 | 22216 | Max User Channel 7 Power Factor | MAX_PF_s007 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3074 | 81 | 81-30 | 22218 | Max User Channel 7 Power Factor Timestamp | MAX_TS_PF_s007 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
3075 | 81 | 81-31 | 22222 | User Channel 8 Current Max value | MAX_I_s008_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3076 | 81 | 81-32 | 22224 | User Channel 8 Current Max value Timestamp | MAX_TS_I_s008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3077 | 81 | 81-33 | 22228 | User Channel 8 Active Power Max value | MAX_P_s008_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3078 | 81 | 81-34 | 22230 | User Channel 8 Active Power Max value Timestamp | MAX_TS_P_s008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3079 | 81 | 81-35 | 22234 | User Channel 8 Reactive Power Max value | MAX_Q_s008_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3080 | 81 | 81-36 | 22236 | User Channel 8 Reactive Power Max value Timestamp | MAX_TS_Q_s008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3081 | 81 | 81-37 | 22240 | User Channel 8 Apparent Power Max value | MAX_S_s008_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3082 | 81 | 81-38 | 22242 | User Channel 8 Apparent Power Max value Timestamp | MAX_TS_S_s008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3083 | 81 | 81-39 | 22246 | Max User Channel 8 Power Factor | MAX_PF_s008 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3084 | 81 | 81-40 | 22248 | Max User Channel 8 Power Factor Timestamp | MAX_TS_PF_s008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3085 | 82 | 82-1 | 22252 | User Channel 9 Current Max value | MAX_I_s009_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3086 | 82 | 82-2 | 22254 | User Channel 9 Current Max value Timestamp | MAX_TS_I_s009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3087 | 82 | 82-3 | 22258 | User Channel 9 Active Power Max value | MAX_P_s009_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3088 | 82 | 82-4 | 22260 | User Channel 9 Active Power Max value Timestamp | MAX_TS_P_s009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3089 | 82 | 82-5 | 22264 | User Channel 9 Reactive Power Max value | MAX_Q_s009_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3090 | 82 | 82-6 | 22266 | User Channel 9 Reactive Power Max value Timestamp | MAX_TS_Q_s009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3091 | 82 | 82-7 | 22270 | User Channel 9 Apparent Power Max value | MAX_S_s009_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3092 | 82 | 82-8 | 22272 | User Channel 9 Apparent Power Max value Timestamp | MAX_TS_S_s009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3093 | 82 | 82-9 | 22276 | Max User Channel 9 Power Factor | MAX_PF_s009 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3094 | 82 | 82-10 | 22278 | Max User Channel 9 Power Factor Timestamp | MAX_TS_PF_s009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3095 | 82 | 82-11 | 22282 | User Channel 10 Current Max value | MAX_I_s010_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3096 | 82 | 82-12 | 22284 | User Channel 10 Current Max value Timestamp | MAX_TS_I_s010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3097 | 82 | 82-13 | 22288 | User Channel 10 Active Power Max value | MAX_P_s010_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3098 | 82 | 82-14 | 22290 | User Channel 10 Active Power Max value Timestamp | MAX_TS_P_s010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3099 | 82 | 82-15 | 22294 | User Channel 10 Reactive Power Max value | MAX_Q_s010_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3100 | 82 | 82-16 | 22296 | User Channel 10 Reactive Power Max value Timestamp | MAX_TS_Q_s010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3101 | 82 | 82-17 | 22300 | User Channel 10 Apparent Power Max value | MAX_S_s010_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3102 | 82 | 82-18 | 22302 | User Channel 10 Apparent Power Max value Timestamp | MAX_TS_S_s010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3103 | 82 | 82-19 | 22306 | Max User Channel 10 Power Factor | MAX_PF_s010 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3104 | 82 | 82-20 | 22308 | Max User Channel 10 Power Factor Timestamp | MAX_TS_PF_s010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3105 | 82 | 82-21 | 22312 | User Channel 11 Current Max value | MAX_I_s011_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3106 | 82 | 82-22 | 22314 | User Channel 11 Current Max value Timestamp | MAX_TS_I_s011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3107 | 82 | 82-23 | 22318 | User Channel 11 Active Power Max value | MAX_P_s011_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3108 | 82 | 82-24 | 22320 | User Channel 11 Active Power Max value Timestamp | MAX_TS_P_s011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3109 | 82 | 82-25 | 22324 | User Channel 11 Reactive Power Max value | MAX_Q_s011_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3110 | 82 | 82-26 | 22326 | User Channel 11 Reactive Power Max value Timestamp | MAX_TS_Q_s011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3111 | 82 | 82-27 | 22330 | User Channel 11 Apparent Power Max value | MAX_S_s011_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3112 | 82 | 82-28 | 22332 | User Channel 11 Apparent Power Max value Timestamp | MAX_TS_S_s011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3113 | 82 | 82-29 | 22336 | Max User Channel 11 Power Factor | MAX_PF_s011 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3114 | 82 | 82-30 | 22338 | Max User Channel 11 Power Factor Timestamp | MAX_TS_PF_s011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3115 | 82 | 82-31 | 22342 | User Channel 12 Current Max value | MAX_I_s012_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3116 | 82 | 82-32 | 22344 | User Channel 12 Current Max value Timestamp | MAX_TS_I_s012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3117 | 82 | 82-33 | 22348 | User Channel 12 Active Power Max value | MAX_P_s012_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3118 | 82 | 82-34 | 22350 | User Channel 12 Active Power Max value Timestamp | MAX_TS_P_s012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3119 | 82 | 82-35 | 22354 | User Channel 12 Reactive Power Max value | MAX_Q_s012_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3120 | 82 | 82-36 | 22356 | User Channel 12 Reactive Power Max value Timestamp | MAX_TS_Q_s012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3121 | 82 | 82-37 | 22360 | User Channel 12 Apparent Power Max value | MAX_S_s012_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3122 | 82 | 82-38 | 22362 | User Channel 12 Apparent Power Max value Timestamp | MAX_TS_S_s012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3123 | 82 | 82-39 | 22366 | Max User Channel 12 Power Factor | MAX_PF_s012 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3124 | 82 | 82-40 | 22368 | Max User Channel 12 Power Factor Timestamp | MAX_TS_PF_s012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3125 | 83 | 83-1 | 22528 | System Frequency Min value | MIN_FREQ_Hz | Hz | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3126 | 83 | 83-2 | 22530 | System Frequency Min value Timestamp | MIN_TS_FREQ |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3127 | 83 | 83-3 | 22534 | Phase A Line-to-Neutral Voltage Min value | MIN_VLN_a_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3128 | 83 | 83-4 | 22536 | Phase A Line-to-Neutral Voltage Min value Timestamp | MIN_VLNTS_a |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3129 | 83 | 83-5 | 22540 | Phase B Line-to-Neutral Voltage Min value | MIN_VLN_b_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3130 | 83 | 83-6 | 22542 | Phase B Line-to-Neutral Voltage Min value Timestamp | MIN_VLNTS_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3131 | 83 | 83-7 | 22546 | Phase C Line-to-Neutral Voltage Min value | MIN_VLN_c_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3132 | 83 | 83-8 | 22548 | Phase C Line-to-Neutral Voltage Min value Timestamp | MIN_VLNTS_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3133 | 83 | 83-9 | 22552 | Phase AB Line-to-Line Voltage Min value | MIN_VLL_ab_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3134 | 83 | 83-10 | 22554 | Phase AB Line-to-Line Voltage Min value Timestamp | MIN_VLLTS_ab_V |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3135 | 83 | 83-11 | 22558 | Phase BC Line-to-Line Voltage Min value | MIN_VLL_bc_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3136 | 83 | 83-12 | 22560 | Phase BC Line-to-Line Voltage Min value Timestamp | MIN_VLLTS_bc_V |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3137 | 83 | 83-13 | 22564 | Phase CA Line-to-Line Voltage Min value | MIN_VLL_ca_V | V | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3138 | 83 | 83-14 | 22566 | Phase CA Line-to-Line Voltage Min value Timestamp | MIN_VLLTS_ca_V |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 23
3139 | 84 | 84-1 | 22570 | Phase A Current Min value | MIN_I_a_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3140 | 84 | 84-2 | 22572 | Phase A Current Min value Timestamp | MIN_TS_I_a_A |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3141 | 84 | 84-3 | 22576 | Phase A Active Power Min value | MIN_P_a_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3142 | 84 | 84-4 | 22578 | Phase A Active Power Min value Timestamp | MIN_TS_P_a |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3143 | 84 | 84-5 | 22582 | Phase A Reactive Power Min value | MIN_Q_a_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3144 | 84 | 84-6 | 22584 | Phase A Reactive Power Min value Timestamp | MIN_TS_Q_a |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3145 | 84 | 84-7 | 22588 | Phase A Apparent Power Min value | MIN_S_a_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3146 | 84 | 84-8 | 22590 | Phase A Apparent Power Min value Timestamp | MIN_TS_S_a |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3147 | 84 | 84-9 | 22594 | Phase A Power Factor Min value | MIN_PF_a | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3148 | 84 | 84-10 | 22596 | Phase A Power Factor Min value Timestamp | MIN_TS_PF_a |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3149 | 84 | 84-11 | 22600 | Phase A Voltage THD Min value | MIN_THD_V_a_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3150 | 84 | 84-12 | 22602 | Phase A Voltage THD Min value Timestamp | MIN_TS_THD_V_a |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3151 | 84 | 84-13 | 22606 | Phase B Current Min value | MIN_I_b_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3152 | 84 | 84-14 | 22608 | Phase B Current Min value Timestamp | MIN_TS_I_b_A |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3153 | 84 | 84-15 | 22612 | Phase B Active Power Min value | MIN_P_b_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3154 | 84 | 84-16 | 22614 | Phase B Active Power Min value Timestamp | MIN_TS_P_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3155 | 84 | 84-17 | 22618 | Phase B Reactive Power Min value | MIN_Q_b_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3156 | 84 | 84-18 | 22620 | Phase B Reactive Power Min value Timestamp | MIN_TS_Q_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3157 | 84 | 84-19 | 22624 | Phase B Apparent Power Min value | MIN_S_b_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3158 | 84 | 84-20 | 22626 | Phase B Apparent Power Min value Timestamp | MIN_TS_S_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3159 | 84 | 84-21 | 22630 | Phase B Power Factor Min value | MIN_PF_b | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3160 | 84 | 84-22 | 22632 | Phase B Power Factor Min value Timestamp | MIN_TS_PF_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3161 | 84 | 84-23 | 22636 | Phase B Voltage THD Min value | MIN_THD_V_b_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3162 | 84 | 84-24 | 22638 | Phase B Voltage THD Min value Timestamp | MIN_TS_THD_V_b |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3163 | 84 | 84-25 | 22642 | Phase C Current Min value | MIN_I_c_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3164 | 84 | 84-26 | 22644 | Phase C Current Min value Timestamp | MIN_TS_I_c_A |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3165 | 84 | 84-27 | 22648 | Phase C Active Power Min value | MIN_P_c_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3166 | 84 | 84-28 | 22650 | Phase C Active Power Min value Timestamp | MIN_TS_P_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3167 | 84 | 84-29 | 22654 | Phase C Reactive Power Min value | MIN_Q_c_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3168 | 84 | 84-30 | 22656 | Phase C Reactive Power Min value Timestamp | MIN_TS_Q_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3169 | 84 | 84-31 | 22660 | Phase C Apparent Power Min value | MIN_S_c_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3170 | 84 | 84-32 | 22662 | Phase C Apparent Power Min value Timestamp | MIN_TS_S_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3171 | 84 | 84-33 | 22666 | Phase C Power Factor Min value | MIN_PF_c | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3172 | 84 | 84-34 | 22668 | Phase C Power Factor Min value Timestamp | MIN_TS_PF_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3173 | 84 | 84-35 | 22672 | Phase C Voltage THD Min value | MIN_THD_V_c_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3174 | 84 | 84-36 | 22674 | Phase C Voltage THD Min value Timestamp | MIN_TS_THD_V_c |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3175 | 84 | 84-37 | 22678 | Voltage Unbalance Factor Magnitude Min value | MIN_UNBL_V_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 23
3176 | 84 | 84-38 | 22680 | Voltage Unbalance Factor Magnitude Min value Timestamp | MIN_UNBLTS_V_% |  | uint64 |  | R | 4 | 1 |  |  |  |  | 23
3177 | 85 | 85-1 | 22684 | Input Channel 1 Current Min value | MIN_I_001_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3178 | 85 | 85-2 | 22686 | Input Channel 1 Current Min value Timestamp | MIN_TS_I_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3179 | 85 | 85-3 | 22690 | Input Channel 1 Active Power Min value | MIN_P_001_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3180 | 85 | 85-4 | 22692 | Input Channel 1 Active Power Min value Timestamp | MIN_TS_P_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3181 | 85 | 85-5 | 22696 | Input Channel 1 Reactive Power Min value | MIN_Q_001_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3182 | 85 | 85-6 | 22698 | Input Channel 1 Reactive Power Min value Timestamp | MIN_TS_Q_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3183 | 85 | 85-7 | 22702 | Input Channel 1 Apparent Power Min value | MIN_S_001_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3184 | 85 | 85-8 | 22704 | Input Channel 1 Apparent Power Min value Timestamp | MIN_TS_S_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3185 | 85 | 85-9 | 22708 | Input Channel 1 Power Factor Min value | MIN_PF_001 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3186 | 85 | 85-10 | 22710 | Input Channel 1 Power Factor Min value Timestamp | MIN_TS_PF_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3187 | 85 | 85-11 | 22714 | Input Channel 1 Current THD Min value | MIN_THD_I_001_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3188 | 85 | 85-12 | 22716 | Input Channel 1 Current THD Min value Timestamp | MIN_TS_THD_I_001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3189 | 85 | 85-13 | 22720 | Input Channel 2 Current Min value | MIN_I_002_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3190 | 85 | 85-14 | 22722 | Input Channel 2 Current Min value Timestamp | MIN_TS_I_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3191 | 85 | 85-15 | 22726 | Input Channel 2 Active Power Min value | MIN_P_002_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3192 | 85 | 85-16 | 22728 | Input Channel 2 Active Power Min value Timestamp | MIN_TS_P_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3193 | 85 | 85-17 | 22732 | Input Channel 2 Reactive Power Min value | MIN_Q_002_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3194 | 85 | 85-18 | 22734 | Input Channel 2 Reactive Power Min value Timestamp | MIN_TS_Q_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3195 | 85 | 85-19 | 22738 | Input Channel 2 Apparent Power Min value | MIN_S_002_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3196 | 85 | 85-20 | 22740 | Input Channel 2 Apparent Power Min value Timestamp | MIN_TS_S_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3197 | 85 | 85-21 | 22744 | Input Channel 2 Power Factor Min value | MIN_PF_002 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3198 | 85 | 85-22 | 22746 | Input Channel 2 Power Factor Min value Timestamp | MIN_TS_PF_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3199 | 85 | 85-23 | 22750 | Input Channel 2 Current THD Min value | MIN_THD_I_002_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3200 | 85 | 85-24 | 22752 | Input Channel 2 Current THD Min value Timestamp | MIN_TS_THD_I_002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3201 | 85 | 85-25 | 22756 | Input Channel 3 Current Min value | MIN_I_003_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3202 | 85 | 85-26 | 22758 | Input Channel 3 Current Min value Timestamp | MIN_TS_I_003 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
3203 | 85 | 85-27 | 22762 | Input Channel 3 Active Power Min value | MIN_P_003_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3204 | 85 | 85-28 | 22764 | Input Channel 3 Active Power Min value Timestamp | MIN_TS_P_003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3205 | 85 | 85-29 | 22768 | Input Channel 3 Reactive Power Min value | MIN_Q_003_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3206 | 85 | 85-30 | 22770 | Input Channel 3 Reactive Power Min value Timestamp | MIN_TS_Q_003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3207 | 85 | 85-31 | 22774 | Input Channel 3 Apparent Power Min value | MIN_S_003_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3208 | 85 | 85-32 | 22776 | Input Channel 3 Apparent Power Min value Timestamp | MIN_TS_S_003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3209 | 85 | 85-33 | 22780 | Input Channel 3 Power Factor Min value | MIN_PF_003 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3210 | 85 | 85-34 | 22782 | Input Channel 3 Power Factor Min value Timestamp | MIN_TS_PF_003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3211 | 85 | 85-35 | 22786 | Input Channel 3 Current THD Min value | MIN_THD_I_003_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3212 | 85 | 85-36 | 22788 | Input Channel 3 Current THD Min value Timestamp | MIN_TS_THD_I_003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3213 | 86 | 86-1 | 22792 | Input Channel 4 Current Min value | MIN_I_004_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3214 | 86 | 86-2 | 22794 | Input Channel 4 Current Min value Timestamp | MIN_TS_I_004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3215 | 86 | 86-3 | 22798 | Input Channel 4 Active Power Min value | MIN_P_004_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3216 | 86 | 86-4 | 22800 | Input Channel 4 Active Power Min value Timestamp | MIN_TS_P_004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3217 | 86 | 86-5 | 22804 | Input Channel 4 Reactive Power Min value | MIN_Q_004_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3218 | 86 | 86-6 | 22806 | Input Channel 4 Reactive Power Min value Timestamp | MIN_TS_Q_004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3219 | 86 | 86-7 | 22810 | Input Channel 4 Apparent Power Min value | MIN_S_004_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3220 | 86 | 86-8 | 22812 | Input Channel 4 Apparent Power Min value Timestamp | MIN_TS_S_004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3221 | 86 | 86-9 | 22816 | Input Channel 4 Power Factor Min value | MIN_PF_004 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3222 | 86 | 86-10 | 22818 | Input Channel 4 Power Factor Min value Timestamp | MIN_TS_PF_004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3223 | 86 | 86-11 | 22822 | Input Channel 4 Current THD Min value | MIN_THD_I_004_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3224 | 86 | 86-12 | 22824 | Input Channel 4 Current THD Min value Timestamp | MIN_TS_THD_I_004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3225 | 86 | 86-13 | 22828 | Input Channel 5 Current Min value | MIN_I_005_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3226 | 86 | 86-14 | 22830 | Input Channel 5 Current Min value Timestamp | MIN_TS_I_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3227 | 86 | 86-15 | 22834 | Input Channel 5 Active Power Min value | MIN_P_005_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3228 | 86 | 86-16 | 22836 | Input Channel 5 Active Power Min value Timestamp | MIN_TS_P_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3229 | 86 | 86-17 | 22840 | Input Channel 5 Reactive Power Min value | MIN_Q_005_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3230 | 86 | 86-18 | 22842 | Input Channel 5 Reactive Power Min value Timestamp | MIN_TS_Q_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3231 | 86 | 86-19 | 22846 | Input Channel 5 Apparent Power Min value | MIN_S_005_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3232 | 86 | 86-20 | 22848 | Input Channel 5 Apparent Power Min value Timestamp | MIN_TS_S_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3233 | 86 | 86-21 | 22852 | Input Channel 5 Power Factor Min value | MIN_PF_005 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3234 | 86 | 86-22 | 22854 | Input Channel 5 Power Factor Min value Timestamp | MIN_TS_PF_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3235 | 86 | 86-23 | 22858 | Input Channel 5 Current THD Min value | MIN_THD_I_005_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3236 | 86 | 86-24 | 22860 | Input Channel 5 Current THD Min value Timestamp | MIN_TS_THD_I_005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3237 | 86 | 86-25 | 22864 | Input Channel 6 Current Min value | MIN_I_006_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3238 | 86 | 86-26 | 22866 | Input Channel 6 Current Min value Timestamp | MIN_TS_I_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3239 | 86 | 86-27 | 22870 | Input Channel 6 Active Power Min value | MIN_P_006_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3240 | 86 | 86-28 | 22872 | Input Channel 6 Active Power Min value Timestamp | MIN_TS_P_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3241 | 86 | 86-29 | 22876 | Input Channel 6 Reactive Power Min value | MIN_Q_006_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3242 | 86 | 86-30 | 22878 | Input Channel 6 Reactive Power Min value Timestamp | MIN_TS_Q_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3243 | 86 | 86-31 | 22882 | Input Channel 6 Apparent Power Min value | MIN_S_006_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3244 | 86 | 86-32 | 22884 | Input Channel 6 Apparent Power Min value Timestamp | MIN_TS_S_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3245 | 86 | 86-33 | 22888 | Input Channel 6 Power Factor Min value | MIN_PF_006 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3246 | 86 | 86-34 | 22890 | Input Channel 6 Power Factor Min value Timestamp | MIN_TS_PF_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3247 | 86 | 86-35 | 22894 | Input Channel 6 Current THD Min value | MIN_THD_I_006_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3248 | 86 | 86-36 | 22896 | Input Channel 6 Current THD Min value Timestamp | MIN_TS_THD_I_006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3249 | 87 | 87-1 | 22900 | Input Channel 7 Current Min value | MIN_I_007_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3250 | 87 | 87-2 | 22902 | Input Channel 7 Current Min value Timestamp | MIN_TS_I_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3251 | 87 | 87-3 | 22906 | Input Channel 7 Active Power Min value | MIN_P_007_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3252 | 87 | 87-4 | 22908 | Input Channel 7 Active Power Min value Timestamp | MIN_TS_P_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3253 | 87 | 87-5 | 22912 | Input Channel 7 Reactive Power Min value | MIN_Q_007_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3254 | 87 | 87-6 | 22914 | Input Channel 7 Reactive Power Min value Timestamp | MIN_TS_Q_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3255 | 87 | 87-7 | 22918 | Input Channel 7 Apparent Power Min value | MIN_S_007_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3256 | 87 | 87-8 | 22920 | Input Channel 7 Apparent Power Min value Timestamp | MIN_TS_S_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3257 | 87 | 87-9 | 22924 | Input Channel 7 Power Factor Min value | MIN_PF_007 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3258 | 87 | 87-10 | 22926 | Input Channel 7 Power Factor Min value Timestamp | MIN_TS_PF_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3259 | 87 | 87-11 | 22930 | Input Channel 7 Current THD Min value | MIN_THD_I_007_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3260 | 87 | 87-12 | 22932 | Input Channel 7 Current THD Min value Timestamp | MIN_TS_THD_I_007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3261 | 87 | 87-13 | 22936 | Input Channel 8 Current Min value | MIN_I_008_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3262 | 87 | 87-14 | 22938 | Input Channel 8 Current Min value Timestamp | MIN_TS_I_008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3263 | 87 | 87-15 | 22942 | Input Channel 8 Active Power Min value | MIN_P_008_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3264 | 87 | 87-16 | 22944 | Input Channel 8 Active Power Min value Timestamp | MIN_TS_P_008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3265 | 87 | 87-17 | 22948 | Input Channel 8 Reactive Power Min value | MIN_Q_008_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3266 | 87 | 87-18 | 22950 | Input Channel 8 Reactive Power Min value Timestamp | MIN_TS_Q_008 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
3267 | 87 | 87-19 | 22954 | Input Channel 8 Apparent Power Min value | MIN_S_008_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3268 | 87 | 87-20 | 22956 | Input Channel 8 Apparent Power Min value Timestamp | MIN_TS_S_008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3269 | 87 | 87-21 | 22960 | Input Channel 8 Power Factor Min value | MIN_PF_008 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3270 | 87 | 87-22 | 22962 | Input Channel 8 Power Factor Min value Timestamp | MIN_TS_PF_008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3271 | 87 | 87-23 | 22966 | Input Channel 8 Current THD Min value | MIN_THD_I_008_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3272 | 87 | 87-24 | 22968 | Input Channel 8 Current THD Min value Timestamp | MIN_TS_THD_I_008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3273 | 87 | 87-25 | 22972 | Input Channel 9 Current Min value | MIN_I_009_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3274 | 87 | 87-26 | 22974 | Input Channel 9 Current Min value Timestamp | MIN_TS_I_009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3275 | 87 | 87-27 | 22978 | Input Channel 9 Active Power Min value | MIN_P_009_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3276 | 87 | 87-28 | 22980 | Input Channel 9 Active Power Min value Timestamp | MIN_TS_P_009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3277 | 87 | 87-29 | 22984 | Input Channel 9 Reactive Power Min value | MIN_Q_009_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3278 | 87 | 87-30 | 22986 | Input Channel 9 Reactive Power Min value Timestamp | MIN_TS_Q_009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3279 | 87 | 87-31 | 22990 | Input Channel 9 Apparent Power Min value | MIN_S_009_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3280 | 87 | 87-32 | 22992 | Input Channel 9 Apparent Power Min value Timestamp | MIN_TS_S_009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3281 | 87 | 87-33 | 22996 | Input Channel 9 Power Factor Min value | MIN_PF_009 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3282 | 87 | 87-34 | 22998 | Input Channel 9 Power Factor Min value Timestamp | MIN_TS_PF_009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3283 | 87 | 87-35 | 23002 | Input Channel 9 Current THD Min value | MIN_THD_I_009_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3284 | 87 | 87-36 | 23004 | Input Channel 9 Current THD Min value Timestamp | MIN_TS_THD_I_009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3285 | 88 | 88-1 | 23008 | Input Channel 10 Current Min value | MIN_I_010_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3286 | 88 | 88-2 | 23010 | Input Channel 10 Current Min value Timestamp | MIN_TS_I_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3287 | 88 | 88-3 | 23014 | Input Channel 10 Active Power Min value | MIN_P_010_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3288 | 88 | 88-4 | 23016 | Input Channel 10 Active Power Min value Timestamp | MIN_TS_P_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3289 | 88 | 88-5 | 23020 | Input Channel 10 Reactive Power Min value | MIN_Q_010_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3290 | 88 | 88-6 | 23022 | Input Channel 10 Reactive Power Min value Timestamp | MIN_TS_Q_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3291 | 88 | 88-7 | 23026 | Input Channel 10 Apparent Power Min value | MIN_S_010_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3292 | 88 | 88-8 | 23028 | Input Channel 10 Apparent Power Min value Timestamp | MIN_TS_S_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3293 | 88 | 88-9 | 23032 | Input Channel 10 Power Factor Min value | MIN_PF_010 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3294 | 88 | 88-10 | 23034 | Input Channel 10 Power Factor Min value Timestamp | MIN_TS_PF_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3295 | 88 | 88-11 | 23038 | Input Channel 10 Current THD Min value | MIN_THD_I_010_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3296 | 88 | 88-12 | 23040 | Input Channel 10 Current THD Min value Timestamp | MIN_TS_THD_I_010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3297 | 88 | 88-13 | 23044 | Input Channel 11 Current Min value | MIN_I_011_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3298 | 88 | 88-14 | 23046 | Input Channel 11 Current Min value Timestamp | MIN_TS_I_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3299 | 88 | 88-15 | 23050 | Input Channel 11 Active Power Min value | MIN_P_011_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3300 | 88 | 88-16 | 23052 | Input Channel 11 Active Power Min value Timestamp | MIN_TS_P_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3301 | 88 | 88-17 | 23056 | Input Channel 11 Reactive Power Min value | MIN_Q_011_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3302 | 88 | 88-18 | 23058 | Input Channel 11 Reactive Power Min value Timestamp | MIN_TS_Q_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3303 | 88 | 88-19 | 23062 | Input Channel 11 Apparent Power Min value | MIN_S_011_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3304 | 88 | 88-20 | 23064 | Input Channel 11 Apparent Power Min value Timestamp | MIN_TS_S_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3305 | 88 | 88-21 | 23068 | Input Channel 11 Power Factor Min value | MIN_PF_011 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3306 | 88 | 88-22 | 23070 | Input Channel 11 Power Factor Min value Timestamp | MIN_TS_PF_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3307 | 88 | 88-23 | 23074 | Input Channel 11 Current THD Min value | MIN_THD_I_011_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3308 | 88 | 88-24 | 23076 | Input Channel 11 Current THD Min value Timestamp | MIN_TS_THD_I_011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3309 | 88 | 88-25 | 23080 | Input Channel 12 Current Min value | MIN_I_012_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3310 | 88 | 88-26 | 23082 | Input Channel 12 Current Min value Timestamp | MIN_TS_I_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3311 | 88 | 88-27 | 23086 | Input Channel 12 Active Power Min value | MIN_P_012_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3312 | 88 | 88-28 | 23088 | Input Channel 12 Active Power Min value Timestamp | MIN_TS_P_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3313 | 88 | 88-29 | 23092 | Input Channel 12 Reactive Power Min value | MIN_Q_012_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3314 | 88 | 88-30 | 23094 | Input Channel 12 Reactive Power Min value Timestamp | MIN_TS_Q_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3315 | 88 | 88-31 | 23098 | Input Channel 12 Apparent Power Min value | MIN_S_012_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3316 | 88 | 88-32 | 23100 | Input Channel 12 Apparent Power Min value Timestamp | MIN_TS_S_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3317 | 88 | 88-33 | 23104 | Input Channel 12 Power Factor Min value | MIN_PF_012 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3318 | 88 | 88-34 | 23106 | Input Channel 12 Power Factor Min value Timestamp | MIN_TS_PF_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3319 | 88 | 88-35 | 23110 | Input Channel 12 Current THD Min value | MIN_THD_I_012_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3320 | 88 | 88-36 | 23112 | Input Channel 12 Current THD Min value Timestamp | MIN_TS_THD_I_012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3321 | 89 | 89-1 | 23116 | Input Channel 13 Current Min value | MIN_I_013_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3322 | 89 | 89-2 | 23118 | Input Channel 13 Current Min value Timestamp | MIN_TS_I_013 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3323 | 89 | 89-3 | 23122 | Input Channel 13 Active Power Min value | MIN_P_013_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3324 | 89 | 89-4 | 23124 | Input Channel 13 Active Power Min value Timestamp | MIN_TS_P_013 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3325 | 89 | 89-5 | 23128 | Input Channel 13 Reactive Power Min value | MIN_Q_013_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3326 | 89 | 89-6 | 23130 | Input Channel 13 Reactive Power Min value Timestamp | MIN_TS_Q_013 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3327 | 89 | 89-7 | 23134 | Input Channel 13 Apparent Power Min value | MIN_S_013_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3328 | 89 | 89-8 | 23136 | Input Channel 13 Apparent Power Min value Timestamp | MIN_TS_S_013 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3329 | 89 | 89-9 | 23140 | Input Channel 13 Power Factor Min value | MIN_PF_013 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3330 | 89 | 89-10 | 23142 | Input Channel 13 Power Factor Min value Timestamp | MIN_TS_PF_013 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
3331 | 89 | 89-11 | 23146 | Input Channel 13 Current THD Min value | MIN_THD_I_013_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3332 | 89 | 89-12 | 23148 | Input Channel 13 Current THD Min value Timestamp | MIN_TS_THD_I_013 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3333 | 89 | 89-13 | 23152 | Input Channel 14 Current Min value | MIN_I_014_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3334 | 89 | 89-14 | 23154 | Input Channel 14 Current Min value Timestamp | MIN_TS_I_014 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3335 | 89 | 89-15 | 23158 | Input Channel 14 Active Power Min value | MIN_P_014_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3336 | 89 | 89-16 | 23160 | Input Channel 14 Active Power Min value Timestamp | MIN_TS_P_014 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3337 | 89 | 89-17 | 23164 | Input Channel 14 Reactive Power Min value | MIN_Q_014_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3338 | 89 | 89-18 | 23166 | Input Channel 14 Reactive Power Min value Timestamp | MIN_TS_Q_014 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3339 | 89 | 89-19 | 23170 | Input Channel 14 Apparent Power Min value | MIN_S_014_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3340 | 89 | 89-20 | 23172 | Input Channel 14 Apparent Power Min value Timestamp | MIN_TS_S_014 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3341 | 89 | 89-21 | 23176 | Input Channel 14 Power Factor Min value | MIN_PF_014 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3342 | 89 | 89-22 | 23178 | Input Channel 14 Power Factor Min value Timestamp | MIN_TS_PF_014 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3343 | 89 | 89-23 | 23182 | Input Channel 14 Current THD Min value | MIN_THD_I_014_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3344 | 89 | 89-24 | 23184 | Input Channel 14 Current THD Min value Timestamp | MIN_TS_THD_I_014 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3345 | 89 | 89-25 | 23188 | Input Channel 15 Current Min value | MIN_I_015_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3346 | 89 | 89-26 | 23190 | Input Channel 15 Current Min value Timestamp | MIN_TS_I_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3347 | 89 | 89-27 | 23194 | Input Channel 15 Active Power Min value | MIN_P_015_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3348 | 89 | 89-28 | 23196 | Input Channel 15 Active Power Min value Timestamp | MIN_TS_P_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3349 | 89 | 89-29 | 23200 | Input Channel 15 Reactive Power Min value | MIN_Q_015_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3350 | 89 | 89-30 | 23202 | Input Channel 15 Reactive Power Min value Timestamp | MIN_TS_Q_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3351 | 89 | 89-31 | 23206 | Input Channel 15 Apparent Power Min value | MIN_S_015_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3352 | 89 | 89-32 | 23208 | Input Channel 15 Apparent Power Min value Timestamp | MIN_TS_S_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3353 | 89 | 89-33 | 23212 | Input Channel 15 Power Factor Min value | MIN_PF_015 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3354 | 89 | 89-34 | 23214 | Input Channel 15 Power Factor Min value Timestamp | MIN_TS_PF_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3355 | 89 | 89-35 | 23218 | Input Channel 15 Current THD Min value | MIN_THD_I_015_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3356 | 89 | 89-36 | 23220 | Input Channel 15 Current THD Min value Timestamp | MIN_TS_THD_I_015 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3357 | 90 | 90-1 | 23224 | Input Channel 16 Current Min value | MIN_I_016_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3358 | 90 | 90-2 | 23226 | Input Channel 16 Current Min value Timestamp | MIN_TS_I_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3359 | 90 | 90-3 | 23230 | Input Channel 16 Active Power Min value | MIN_P_016_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3360 | 90 | 90-4 | 23232 | Input Channel 16 Active Power Min value Timestamp | MIN_TS_P_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3361 | 90 | 90-5 | 23236 | Input Channel 16 Reactive Power Min value | MIN_Q_016_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3362 | 90 | 90-6 | 23238 | Input Channel 16 Reactive Power Min value Timestamp | MIN_TS_Q_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3363 | 90 | 90-7 | 23242 | Input Channel 16 Apparent Power Min value | MIN_S_016_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3364 | 90 | 90-8 | 23244 | Input Channel 16 Apparent Power Min value Timestamp | MIN_TS_S_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3365 | 90 | 90-9 | 23248 | Input Channel 16 Power Factor Min value | MIN_PF_016 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3366 | 90 | 90-10 | 23250 | Input Channel 16 Power Factor Min value Timestamp | MIN_TS_PF_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3367 | 90 | 90-11 | 23254 | Input Channel 16 Current THD Min value | MIN_THD_I_016_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3368 | 90 | 90-12 | 23256 | Input Channel 16 Current THD Min value Timestamp | MIN_TS_THD_I_016 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3369 | 90 | 90-13 | 23260 | Input Channel 17 Current Min value | MIN_I_017_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3370 | 90 | 90-14 | 23262 | Input Channel 17 Current Min value Timestamp | MIN_TS_I_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3371 | 90 | 90-15 | 23266 | Input Channel 17 Active Power Min value | MIN_P_017_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3372 | 90 | 90-16 | 23268 | Input Channel 17 Active Power Min value Timestamp | MIN_TS_P_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3373 | 90 | 90-17 | 23272 | Input Channel 17 Reactive Power Min value | MIN_Q_017_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3374 | 90 | 90-18 | 23274 | Input Channel 17 Reactive Power Min value Timestamp | MIN_TS_Q_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3375 | 90 | 90-19 | 23278 | Input Channel 17 Apparent Power Min value | MIN_S_017_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3376 | 90 | 90-20 | 23280 | Input Channel 17 Apparent Power Min value Timestamp | MIN_TS_S_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3377 | 90 | 90-21 | 23284 | Input Channel 17 Power Factor Min value | MIN_PF_017 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3378 | 90 | 90-22 | 23286 | Input Channel 17 Power Factor Min value Timestamp | MIN_TS_PF_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3379 | 90 | 90-23 | 23290 | Input Channel 17 Current THD Min value | MIN_THD_I_017_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3380 | 90 | 90-24 | 23292 | Input Channel 17 Current THD Min value Timestamp | MIN_TS_THD_I_017 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3381 | 90 | 90-25 | 23296 | Input Channel 18 Current Min value | MIN_I_018_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3382 | 90 | 90-26 | 23298 | Input Channel 18 Current Min value Timestamp | MIN_TS_I_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3383 | 90 | 90-27 | 23302 | Input Channel 18 Active Power Min value | MIN_P_018_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3384 | 90 | 90-28 | 23304 | Input Channel 18 Active Power Min value Timestamp | MIN_TS_P_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3385 | 90 | 90-29 | 23308 | Input Channel 18 Reactive Power Min value | MIN_Q_018_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3386 | 90 | 90-30 | 23310 | Input Channel 18 Reactive Power Min value Timestamp | MIN_TS_Q_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3387 | 90 | 90-31 | 23314 | Input Channel 18 Apparent Power Min value | MIN_S_018_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3388 | 90 | 90-32 | 23316 | Input Channel 18 Apparent Power Min value Timestamp | MIN_TS_S_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3389 | 90 | 90-33 | 23320 | Input Channel 18 Power Factor Min value | MIN_PF_018 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3390 | 90 | 90-34 | 23322 | Input Channel 18 Power Factor Min value Timestamp | MIN_TS_PF_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3391 | 90 | 90-35 | 23326 | Input Channel 18 Current THD Min value | MIN_THD_I_018_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3392 | 90 | 90-36 | 23328 | Input Channel 18 Current THD Min value Timestamp | MIN_TS_THD_I_018 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3393 | 91 | 91-1 | 23332 | Input Channel 19 Current Min value | MIN_I_019_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3394 | 91 | 91-2 | 23334 | Input Channel 19 Current Min value Timestamp | MIN_TS_I_019 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
3395 | 91 | 91-3 | 23338 | Input Channel 19 Active Power Min value | MIN_P_019_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3396 | 91 | 91-4 | 23340 | Input Channel 19 Active Power Min value Timestamp | MIN_TS_P_019 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3397 | 91 | 91-5 | 23344 | Input Channel 19 Reactive Power Min value | MIN_Q_019_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3398 | 91 | 91-6 | 23346 | Input Channel 19 Reactive Power Min value Timestamp | MIN_TS_Q_019 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3399 | 91 | 91-7 | 23350 | Input Channel 19 Apparent Power Min value | MIN_S_019_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3400 | 91 | 91-8 | 23352 | Input Channel 19 Apparent Power Min value Timestamp | MIN_TS_S_019 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3401 | 91 | 91-9 | 23356 | Input Channel 19 Power Factor Min value | MIN_PF_019 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3402 | 91 | 91-10 | 23358 | Input Channel 19 Power Factor Min value Timestamp | MIN_TS_PF_019 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3403 | 91 | 91-11 | 23362 | Input Channel 19 Current THD Min value | MIN_THD_I_019_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3404 | 91 | 91-12 | 23364 | Input Channel 19 Current THD Min value Timestamp | MIN_TS_THD_I_019 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3405 | 91 | 91-13 | 23368 | Input Channel 20 Current Min value | MIN_I_020_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3406 | 91 | 91-14 | 23370 | Input Channel 20 Current Min value Timestamp | MIN_TS_I_020 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3407 | 91 | 91-15 | 23374 | Input Channel 20 Active Power Min value | MIN_P_020_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3408 | 91 | 91-16 | 23376 | Input Channel 20 Active Power Min value Timestamp | MIN_TS_P_020 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3409 | 91 | 91-17 | 23380 | Input Channel 20 Reactive Power Min value | MIN_Q_020_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3410 | 91 | 91-18 | 23382 | Input Channel 20 Reactive Power Min value Timestamp | MIN_TS_Q_020 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3411 | 91 | 91-19 | 23386 | Input Channel 20 Apparent Power Min value | MIN_S_020_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3412 | 91 | 91-20 | 23388 | Input Channel 20 Apparent Power Min value Timestamp | MIN_TS_S_020 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3413 | 91 | 91-21 | 23392 | Input Channel 20 Power Factor Min value | MIN_PF_020 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3414 | 91 | 91-22 | 23394 | Input Channel 20 Power Factor Min value Timestamp | MIN_TS_PF_020 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3415 | 91 | 91-23 | 23398 | Input Channel 20 Current THD Min value | MIN_THD_I_020_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3416 | 91 | 91-24 | 23400 | Input Channel 20 Current THD Min value Timestamp | MIN_TS_THD_I_020 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3417 | 91 | 91-25 | 23404 | Input Channel 21 Current Min value | MIN_I_021_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3418 | 91 | 91-26 | 23406 | Input Channel 21 Current Min value Timestamp | MIN_TS_I_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3419 | 91 | 91-27 | 23410 | Input Channel 21 Active Power Min value | MIN_P_021_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3420 | 91 | 91-28 | 23412 | Input Channel 21 Active Power Min value Timestamp | MIN_TS_P_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3421 | 91 | 91-29 | 23416 | Input Channel 21 Reactive Power Min value | MIN_Q_021_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3422 | 91 | 91-30 | 23418 | Input Channel 21 Reactive Power Min value Timestamp | MIN_TS_Q_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3423 | 91 | 91-31 | 23422 | Input Channel 21 Apparent Power Min value | MIN_S_021_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3424 | 91 | 91-32 | 23424 | Input Channel 21 Apparent Power Min value Timestamp | MIN_TS_S_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3425 | 91 | 91-33 | 23428 | Input Channel 21 Power Factor Min value | MIN_PF_021 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3426 | 91 | 91-34 | 23430 | Input Channel 21 Power Factor Min value Timestamp | MIN_TS_PF_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3427 | 91 | 91-35 | 23434 | Input Channel 21 Current THD Min value | MIN_THD_I_021_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3428 | 91 | 91-36 | 23436 | Input Channel 21 Current THD Min value Timestamp | MIN_TS_THD_I_021 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3429 | 92 | 92-1 | 23440 | Input Channel 22 Current Min value | MIN_I_022_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3430 | 92 | 92-2 | 23442 | Input Channel 22 Current Min value Timestamp | MIN_TS_I_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3431 | 92 | 92-3 | 23446 | Input Channel 22 Active Power Min value | MIN_P_022_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3432 | 92 | 92-4 | 23448 | Input Channel 22 Active Power Min value Timestamp | MIN_TS_P_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3433 | 92 | 92-5 | 23452 | Input Channel 22 Reactive Power Min value | MIN_Q_022_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3434 | 92 | 92-6 | 23454 | Input Channel 22 Reactive Power Min value Timestamp | MIN_TS_Q_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3435 | 92 | 92-7 | 23458 | Input Channel 22 Apparent Power Min value | MIN_S_022_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3436 | 92 | 92-8 | 23460 | Input Channel 22 Apparent Power Min value Timestamp | MIN_TS_S_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3437 | 92 | 92-9 | 23464 | Input Channel 22 Power Factor Min value | MIN_PF_022 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3438 | 92 | 92-10 | 23466 | Input Channel 22 Power Factor Min value Timestamp | MIN_TS_PF_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3439 | 92 | 92-11 | 23470 | Input Channel 22 Current THD Min value | MIN_THD_I_022_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3440 | 92 | 92-12 | 23472 | Input Channel 22 Current THD Min value Timestamp | MIN_TS_THD_I_022 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3441 | 92 | 92-13 | 23476 | Input Channel 23 Current Min value | MIN_I_023_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3442 | 92 | 92-14 | 23478 | Input Channel 23 Current Min value Timestamp | MIN_TS_I_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3443 | 92 | 92-15 | 23482 | Input Channel 23 Active Power Min value | MIN_P_023_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3444 | 92 | 92-16 | 23484 | Input Channel 23 Active Power Min value Timestamp | MIN_TS_P_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3445 | 92 | 92-17 | 23488 | Input Channel 23 Reactive Power Min value | MIN_Q_023_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3446 | 92 | 92-18 | 23490 | Input Channel 23 Reactive Power Min value Timestamp | MIN_TS_Q_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3447 | 92 | 92-19 | 23494 | Input Channel 23 Apparent Power Min value | MIN_S_023_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3448 | 92 | 92-20 | 23496 | Input Channel 23 Apparent Power Min value Timestamp | MIN_TS_S_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3449 | 92 | 92-21 | 23500 | Input Channel 23 Power Factor Min value | MIN_PF_023 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3450 | 92 | 92-22 | 23502 | Input Channel 23 Power Factor Min value Timestamp | MIN_TS_PF_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3451 | 92 | 92-23 | 23506 | Input Channel 23 Current THD Min value | MIN_THD_I_023_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3452 | 92 | 92-24 | 23508 | Input Channel 23 Current THD Min value Timestamp | MIN_TS_THD_I_023 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3453 | 92 | 92-25 | 23512 | Input Channel 24 Current Min value | MIN_I_024_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3454 | 92 | 92-26 | 23514 | Input Channel 24 Current Min value Timestamp | MIN_TS_I_024 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3455 | 92 | 92-27 | 23518 | Input Channel 24 Active Power Min value | MIN_P_024_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3456 | 92 | 92-28 | 23520 | Input Channel 24 Active Power Min value Timestamp | MIN_TS_P_024 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3457 | 92 | 92-29 | 23524 | Input Channel 24 Reactive Power Min value | MIN_Q_024_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3458 | 92 | 92-30 | 23526 | Input Channel 24 Reactive Power Min value Timestamp | MIN_TS_Q_024 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
3459 | 92 | 92-31 | 23530 | Input Channel 24 Apparent Power Min value | MIN_S_024_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3460 | 92 | 92-32 | 23532 | Input Channel 24 Apparent Power Min value Timestamp | MIN_TS_S_024 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3461 | 92 | 92-33 | 23536 | Input Channel 24 Power Factor Min value | MIN_PF_024 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3462 | 92 | 92-34 | 23538 | Input Channel 24 Power Factor Min value Timestamp | MIN_TS_PF_024 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3463 | 92 | 92-35 | 23542 | Input Channel 24 Current THD Min value | MIN_THD_I_024_% | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3464 | 92 | 92-36 | 23544 | Input Channel 24 Current THD Min value Timestamp | MIN_TS_THD_I_024 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3465 | 93 | 93-1 | 23548 | User Channel 1 Current Min value | MIN_I_s001_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3466 | 93 | 93-2 | 23550 | User Channel 1 Current Min value Timestamp | MIN_TS_I_s001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3467 | 93 | 93-3 | 23554 | User Channel 1 Active Power Min value | MIN_P_s001_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3468 | 93 | 93-4 | 23556 | User Channel 1 Active Power Min value Timestamp | MIN_TS_P_s001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3469 | 93 | 93-5 | 23560 | User Channel 1 Reactive Power Min value | MIN_Q_s001_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3470 | 93 | 93-6 | 23562 | User Channel 1 Reactive Power Min value Timestamp | MIN_TS_Q_s001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3471 | 93 | 93-7 | 23566 | User Channel 1 Apparent Power Min value | MIN_S_s001_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3472 | 93 | 93-8 | 23568 | User Channel 1 Apparent Power Min value Timestamp | MIN_TS_S_s001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3473 | 93 | 93-9 | 23572 | Min User Channel 1 Power Factor | MIN_PF_s001 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3474 | 93 | 93-10 | 23574 | User Channel 1 Power Factor Timestamp | MIN_TS_PF_s001 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3475 | 93 | 93-11 | 23578 | User Channel 2 Current Min value | MIN_I_s002_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3476 | 93 | 93-12 | 23580 | User Channel 2 Current Min value Timestamp | MIN_TS_I_s002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3477 | 93 | 93-13 | 23584 | User Channel 2 Active Power Min value | MIN_P_s002_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3478 | 93 | 93-14 | 23586 | User Channel 2 Active Power Min value Timestamp | MIN_TS_P_s002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3479 | 93 | 93-15 | 23590 | User Channel 2 Reactive Power Min value | MIN_Q_s002_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3480 | 93 | 93-16 | 23592 | User Channel 2 Reactive Power Min value Timestamp | MIN_TS_Q_s002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3481 | 93 | 93-17 | 23596 | User Channel 2 Apparent Power Min value | MIN_S_s002_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3482 | 93 | 93-18 | 23598 | User Channel 2 Apparent Power Min value Timestamp | MIN_TS_S_s002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3483 | 93 | 93-19 | 23602 | Min User Channel 2 Power Factor | MIN_PF_s002 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3484 | 93 | 93-20 | 23604 | User Channel 2 Power Factor Timestamp | MIN_TS_PF_s002 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3485 | 93 | 93-21 | 23608 | User Channel 3 Current Min value | MIN_I_s003_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3486 | 93 | 93-22 | 23610 | User Channel 3 Current Min value Timestamp | MIN_TS_I_s003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3487 | 93 | 93-23 | 23614 | User Channel 3 Active Power Min value | MIN_P_s003_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3488 | 93 | 93-24 | 23616 | User Channel 3 Active Power Min value Timestamp | MIN_TS_P_s003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3489 | 93 | 93-25 | 23620 | User Channel 3 Reactive Power Min value | MIN_Q_s003_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3490 | 93 | 93-26 | 23622 | User Channel 3 Reactive Power Min value Timestamp | MIN_TS_Q_s003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3491 | 93 | 93-27 | 23626 | User Channel 3 Apparent Power Min value | MIN_S_s003_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3492 | 93 | 93-28 | 23628 | User Channel 3 Apparent Power Min value Timestamp | MIN_TS_S_s003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3493 | 93 | 93-29 | 23632 | Min User Channel 3 Power Factor | MIN_PF_s003 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3494 | 93 | 93-30 | 23634 | User Channel 3 Power Factor Timestamp | MIN_TS_PF_s003 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3495 | 93 | 93-31 | 23638 | User Channel 4 Current Min value | MIN_I_s004_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3496 | 93 | 93-32 | 23640 | User Channel 4 Current Min value Timestamp | MIN_TS_I_s004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3497 | 93 | 93-33 | 23644 | User Channel 4 Active Power Min value | MIN_P_s004_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3498 | 93 | 93-34 | 23646 | User Channel 4 Active Power Min value Timestamp | MIN_TS_P_s004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3499 | 93 | 93-35 | 23650 | User Channel 4 Reactive Power Min value | MIN_Q_s004_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3500 | 93 | 93-36 | 23652 | User Channel 4 Reactive Power Min value Timestamp | MIN_TS_Q_s004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3501 | 93 | 93-37 | 23656 | User Channel 4 Apparent Power Min value | MIN_S_s004_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3502 | 93 | 93-38 | 23658 | User Channel 4 Apparent Power Min value Timestamp | MIN_TS_S_s004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3503 | 93 | 93-39 | 23662 | Min User Channel 4 Power Factor | MIN_PF_s004 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3504 | 93 | 93-40 | 23664 | User Channel 4 Power Factor Timestamp | MIN_TS_PF_s004 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3505 | 94 | 94-1 | 23668 | User Channel 5 Current Min value | MIN_I_s005_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3506 | 94 | 94-2 | 23670 | User Channel 5 Current Min value Timestamp | MIN_TS_I_s005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3507 | 94 | 94-3 | 23674 | User Channel 5 Active Power Min value | MIN_P_s005_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3508 | 94 | 94-4 | 23676 | User Channel 5 Active Power Min value Timestamp | MIN_TS_P_s005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3509 | 94 | 94-5 | 23680 | User Channel 5 Reactive Power Min value | MIN_Q_s005_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3510 | 94 | 94-6 | 23682 | User Channel 5 Reactive Power Min value Timestamp | MIN_TS_Q_s005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3511 | 94 | 94-7 | 23686 | User Channel 5 Apparent Power Min value | MIN_S_s005_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3512 | 94 | 94-8 | 23688 | User Channel 5 Apparent Power Min value Timestamp | MIN_TS_S_s005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3513 | 94 | 94-9 | 23692 | Min User Channel 5 Power Factor | MIN_PF_s005 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3514 | 94 | 94-10 | 23694 | User Channel 5 Power Factor Timestamp | MIN_TS_PF_s005 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3515 | 94 | 94-11 | 23698 | User Channel 6 Current Min value | MIN_I_s006_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3516 | 94 | 94-12 | 23700 | User Channel 6 Current Min value Timestamp | MIN_TS_I_s006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3517 | 94 | 94-13 | 23704 | User Channel 6 Active Power Min value | MIN_P_s006_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3518 | 94 | 94-14 | 23706 | User Channel 6 Active Power Min value Timestamp | MIN_TS_P_s006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3519 | 94 | 94-15 | 23710 | User Channel 6 Reactive Power Min value | MIN_Q_s006_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3520 | 94 | 94-16 | 23712 | User Channel 6 Reactive Power Min value Timestamp | MIN_TS_Q_s006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3521 | 94 | 94-17 | 23716 | User Channel 6 Apparent Power Min value | MIN_S_s006_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3522 | 94 | 94-18 | 23718 | User Channel 6 Apparent Power Min value Timestamp | MIN_TS_S_s006 |  | uint64 | 14 | R | 4 | 1 |  |  |  |  | 24
3523 | 94 | 94-19 | 23722 | Min User Channel 6 Power Factor | MIN_PF_s006 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3524 | 94 | 94-20 | 23724 | User Channel 6 Power Factor Timestamp | MIN_TS_PF_s006 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3525 | 94 | 94-21 | 23728 | User Channel 7 Current Min value | MIN_I_s007_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3526 | 94 | 94-22 | 23730 | User Channel 7 Current Min value Timestamp | MIN_TS_I_s007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3527 | 94 | 94-23 | 23734 | User Channel 7 Active Power Min value | MIN_P_s007_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3528 | 94 | 94-24 | 23736 | User Channel 7 Active Power Min value Timestamp | MIN_TS_P_s007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3529 | 94 | 94-25 | 23740 | User Channel 7 Reactive Power Min value | MIN_Q_s007_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3530 | 94 | 94-26 | 23742 | User Channel 7 Reactive Power Min value Timestamp | MIN_TS_Q_s007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3531 | 94 | 94-27 | 23746 | User Channel 7 Apparent Power Min value | MIN_S_s007_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3532 | 94 | 94-28 | 23748 | User Channel 7 Apparent Power Min value Timestamp | MIN_TS_S_s007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3533 | 94 | 94-29 | 23752 | Min User Channel 7 Power Factor | MIN_PF_s007 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3534 | 94 | 94-30 | 23754 | User Channel 7 Power Factor Timestamp | MIN_TS_PF_s007 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3535 | 94 | 94-31 | 23758 | User Channel 8 Current Min value | MIN_I_s008_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3536 | 94 | 94-32 | 23760 | User Channel 8 Current Min value Timestamp | MIN_TS_I_s008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3537 | 94 | 94-33 | 23764 | User Channel 8 Active Power Min value | MIN_P_s008_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3538 | 94 | 94-34 | 23766 | User Channel 8 Active Power Min value Timestamp | MIN_TS_P_s008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3539 | 94 | 94-35 | 23770 | User Channel 8 Reactive Power Min value | MIN_Q_s008_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3540 | 94 | 94-36 | 23772 | User Channel 8 Reactive Power Min value Timestamp | MIN_TS_Q_s008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3541 | 94 | 94-37 | 23776 | User Channel 8 Apparent Power Min value | MIN_S_s008_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3542 | 94 | 94-38 | 23778 | User Channel 8 Apparent Power Min value Timestamp | MIN_TS_S_s008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3543 | 94 | 94-39 | 23782 | Min User Channel 8 Power Factor | MIN_PF_s008 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3544 | 94 | 94-40 | 23784 | User Channel 8 Power Factor Timestamp | MIN_TS_PF_s008 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3545 | 95 | 95-1 | 23788 | User Channel 9 Current Min value | MIN_I_s009_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3546 | 95 | 95-2 | 23790 | User Channel 9 Current Min value Timestamp | MIN_TS_I_s009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3547 | 95 | 95-3 | 23794 | User Channel 9 Active Power Min value | MIN_P_s009_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3548 | 95 | 95-4 | 23796 | User Channel 9 Active Power Min value Timestamp | MIN_TS_P_s009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3549 | 95 | 95-5 | 23800 | User Channel 9 Reactive Power Min value | MIN_Q_s009_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3550 | 95 | 95-6 | 23802 | User Channel 9 Reactive Power Min value Timestamp | MIN_TS_Q_s009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3551 | 95 | 95-7 | 23806 | User Channel 9 Apparent Power Min value | MIN_S_s009_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3552 | 95 | 95-8 | 23808 | User Channel 9 Apparent Power Min value Timestamp | MIN_TS_S_s009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3553 | 95 | 95-9 | 23812 | Min User Channel 9 Power Factor | MIN_PF_s009 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3554 | 95 | 95-10 | 23814 | User Channel 9 Power Factor Timestamp | MIN_TS_PF_s009 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3555 | 95 | 95-11 | 23818 | User Channel 10 Current Min value | MIN_I_s010_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3556 | 95 | 95-12 | 23820 | User Channel 10 Current Min value Timestamp | MIN_TS_I_s010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3557 | 95 | 95-13 | 23824 | User Channel 10 Active Power Min value | MIN_P_s010_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3558 | 95 | 95-14 | 23826 | User Channel 10 Active Power Min value Timestamp | MIN_TS_P_s010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3559 | 95 | 95-15 | 23830 | User Channel 10 Reactive Power Min value | MIN_Q_s010_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3560 | 95 | 95-16 | 23832 | User Channel 10 Reactive Power Min value Timestamp | MIN_TS_Q_s010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3561 | 95 | 95-17 | 23836 | User Channel 10 Apparent Power Min value | MIN_S_s010_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3562 | 95 | 95-18 | 23838 | User Channel 10 Apparent Power Min value Timestamp | MIN_TS_S_s010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3563 | 95 | 95-19 | 23842 | Min User Channel 10 Power Factor | MIN_PF_s010 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3564 | 95 | 95-20 | 23844 | User Channel 10 Power Factor Timestamp | MIN_TS_PF_s010 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3565 | 95 | 95-21 | 23848 | User Channel 11 Current Min value | MIN_I_s011_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3566 | 95 | 95-22 | 23850 | User Channel 11 Current Min value Timestamp | MIN_TS_I_s011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3567 | 95 | 95-23 | 23854 | User Channel 11 Active Power Min value | MIN_P_s011_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3568 | 95 | 95-24 | 23856 | User Channel 11 Active Power Min value Timestamp | MIN_TS_P_s011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3569 | 95 | 95-25 | 23860 | User Channel 11 Reactive Power Min value | MIN_Q_s011_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3570 | 95 | 95-26 | 23862 | User Channel 11 Reactive Power Min value Timestamp | MIN_TS_Q_s011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3571 | 95 | 95-27 | 23866 | User Channel 11 Apparent Power Min value | MIN_S_s011_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3572 | 95 | 95-28 | 23868 | User Channel 11 Apparent Power Min value Timestamp | MIN_TS_S_s011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3573 | 95 | 95-29 | 23872 | Min User Channel 11 Power Factor | MIN_PF_s011 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3574 | 95 | 95-30 | 23874 | User Channel 11 Power Factor Timestamp | MIN_TS_PF_s011 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3575 | 95 | 95-31 | 23878 | User Channel 12 Current Min value | MIN_I_s012_A | A | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3576 | 95 | 95-32 | 23880 | User Channel 12 Current Min value Timestamp | MIN_TS_I_s012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3577 | 95 | 95-33 | 23884 | User Channel 12 Active Power Min value | MIN_P_s012_kW | kW | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3578 | 95 | 95-34 | 23886 | User Channel 12 Active Power Min value Timestamp | MIN_TS_P_s012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3579 | 95 | 95-35 | 23890 | User Channel 12 Reactive Power Min value | MIN_Q_s012_kvar | kvar | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3580 | 95 | 95-36 | 23892 | User Channel 12 Reactive Power Min value Timestamp | MIN_TS_Q_s012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3581 | 95 | 95-37 | 23896 | User Channel 12 Apparent Power Min value | MIN_S_s012_kVA | kVA | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3582 | 95 | 95-38 | 23898 | User Channel 12 Apparent Power Min value Timestamp | MIN_TS_S_s012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3583 | 95 | 95-39 | 23902 | Min User Channel 12 Power Factor | MIN_PF_s012 | % | float32 |  | R | 2 | 1 |  |  |  | 6 | 24
3584 | 95 | 95-40 | 23904 | User Channel 12 Power Factor Timestamp | MIN_TS_PF_s012 |  | uint64 |  | R | 4 | 1 |  |  |  |  | 24
3585 | 96 | 96-1 | 26115 | The Number of the Waveform Record Group | totalWaveformNum |  | uint16 |  | R | 1 | 1 |  |  |  | 7-8 | 17
3586 | 96 | 96-2 | 26116 | Data state of waveform record window | waveformDataState |  | uint16 | 1 | R | 1 | 1 |  |  |  | 7-8 | 17
3587 | 96 | 96-3 | 26117 | Latest Waveform Record Groupe Number | lastWaveformNum |  | uint16 | 1 | R | 1 | 1 |  |  |  | 7-8 | 17
3588 | 97 | 97-1 | 26369 | The index of the PQEvent Log | lastPQEventNum |  | uint16 |  | R | 1 | 1 |  |  |  | 7-8 | 17
3589 | 97 | 97-2 | 26370 | The Number of the PQEvent Log | totalPQEventNum |  | uint16 |  | R | 1 | 1 |  |  |  | 7-8 | 17
3590 | 98 | 98-1 | 61504 | Serial Number1 | Conf_Serial_Number1 |  | uint64 |  | R/W | 4 | 1 |  |  |  |  | 18-35
3591 | 98 | 98-2 | 61508 | Serial Number2 | Conf_Serial_Number2 |  | uint64 |  | R/W | 4 | 1 |  |  |  |  | 18-35
3592 | 98 | 98-3 | 61512 | Serial Number3 | Conf_Serial_Number3 |  | uint64 |  | R/W | 4 | 1 |  |  |  |  | 18-35
3593 | 98 | 98-4 | 61516 | Serial Number4 | Conf_Serial_Number4 |  | uint64 |  | R/W | 4 | 1 |  |  |  |  | 18-35
3594 | 98 | 98-5 | 61520 | Hardware version | Conf_Hardware_version |  | uint32 |  | R/W | 2 | 1 |  |  |  |  | 18
3595 | 98 | 98-6 | 61522 | Function Model Type | Conf_Function_Model_Type |  | uint16 |  | R/W | 1 | 1 |  |  |  |  | 18-35
3596 | 98 | 98-7 | 61523 | Reserved11 | Conf_Reserved11 |  | uint16 |  | R/W | 1 | 1 |  |  |  |  | 18
3597 | 98 | 98-8 | 61524 | Current Input Type | Info_Current_Input_Type |  | uint16 | 1 | R/W | 1 | 1 |  |  |  |  | 18-28-35
3598 | 98 | 98-9 | 61525 | Power Supply Type | Power_Supply_Type |  | uint16 | 1 | R/W | 1 | 1 |  |  |  |  | 18-35
3599 | 98 | 98-10 | 61526 | MAC address1 | Conf_MAC_address1 |  | uint64 |  | R/W | 4 | 1 |  |  |  |  | 18-35
3600 | 98 | 98-11 | 61530 | MAC address2 | Conf_MAC_address2 |  | uint64 |  | R/W | 4 | 1 |  |  |  |  | 18-35
3601 | 98 | 98-12 | 61534 | MAC address3 | Conf_MAC_address3 |  | uint64 |  | R/W | 4 | 1 |  |  |  |  | 18-35
3602 | 98 | 98-13 | 61538 | MAC address4 | Conf_MAC_address4 |  | uint64 |  | R/W | 4 | 1 |  |  |  |  | 18-35
3603 | 98 | 98-14 | 61542 | Certification Type | Conf_Certification_Type |  | uint16 |  | R/W | 1 | 1 |  |  |  |  | 18
3604 | 98 | 98-15 | 61543 | AIAO or DIDO flag | Conf_AIAO_or_DIDO_flag |  | uint32 |  | R/W | 2 | 1 |  |  |  |  | 18
3605 | 98 | 98-16 | 61545 | Reserved 21 | Conf_Reserved_21 |  | uint64 |  | R/W | 4 | 1 |  |  |  |  | 18
3606 | 98 | 98-17 | 61549 | Reserved 22 | Conf_Reserved_22 |  | uint32 |  | R/W | 2 | 1 |  |  |  |  | 18
3607 | 98 | 98-18 | 61551 | Reserved 23 | Conf_Reserved_23 |  | uint16 |  | R/W | 1 | 1 |  |  |  |  | 18
3608 | 98 | 98-19 | 61552 | Hardware Patch Number | Conf_Hardware_Patch_Number |  | uint16 |  | R/W | 1 | 1 |  |  |  |  | 18
3609 | 99 | 99-1 | 61440 | Firmware version | Conf_Firmware_version |  | uint32 |  | R | 2 | 1 |  |  |  |  | 18
3610 | 99 | 99-2 | 61442 | Firmware release date1 | Conf_Firmware_release_date1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 18
3611 | 99 | 99-3 | 61444 | Firmware release date2 | Conf_Firmware_release_date2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 18
3612 | 99 | 99-4 | 61445 | Firmware patch number | Conf_Firmware_patch_number |  | uint16 |  | R | 1 | 1 |  |  |  |  | 18
3613 | 100 | 100-1 | 61456 | bootloader product string | Conf_bootloader_product_string |  | uint32 |  | R | 2 | 1 |  |  |  |  | 18
3614 | 100 | 100-2 | 61458 | bootloader version | Conf_bootloader_version |  | uint32 |  | R | 2 | 1 |  |  |  |  | 18
3615 | 100 | 100-3 | 61460 | bootloader release date1 | Conf_bootloader_release_date1 |  | uint32 |  | R | 2 | 1 |  |  |  |  | 18
3616 | 100 | 100-4 | 61462 | bootloader release date2 | Conf_bootloader_release_date2 |  | uint16 |  | R | 1 | 1 |  |  |  |  | 18
3617 | 100 | 100-5 | 61463 | bootloader patch number | Conf_bootloader_patch_number |  | uint16 |  | R | 1 | 1 |  |  |  |  | 18
3618 | 101 | 101-1 | 4096 | Password | Conf_Password |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3619 | 101 | 101-2 | 4097 | Baud Rate | Conf_Baud |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 35
3620 | 101 | 101-3 | 4098 | Parity | Conf_Parity |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3621 | 101 | 101-4 | 4099 | DHCP enable | Conf_DHCP_Enable |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 35
3622 | 101 | 101-5 | 4100 | IP address | Conf_IP |  | uint32 |  | R/W | 2 | 1 |  |  | 30 |  | 35
3623 | 101 | 101-6 | 4102 | Subnet mask | Conf_Mask |  | uint32 |  | R/W | 2 | 1 |  |  | 30 |  | 35
3624 | 101 | 101-7 | 4104 | Gateway | Conf_Gateway |  | uint32 |  | R/W | 2 | 1 |  |  | 30
3625 | 101 | 101-8 | 4106 | DNS primary server | Conf_DNS_Primary |  | uint32 |  | R/W | 2 | 1 |  |  | 30
3626 | 101 | 101-9 | 4108 | DNS secondary server | Conf_DNS_Second |  | uint32 |  | R/W | 2 | 1 |  |  | 30
3627 | 101 | 101-10 | 4110 | Modbus Slave ID | Conf_Slave_Id |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 35-18
3628 | 101 | 101-11 | 4111 | RS485 protocol | Conf_RS485_Protocal |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 35
3629 | 101 | 101-12 | 4112 | Modbus TCP Enable | Conf_Modbus_TCP_Enable |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 35
3630 | 101 | 101-13 | 4113 | Modbus TCP port | Conf_Modbus_TCP_Port |  | uint16 | 1 | R/W | 1 | 1 |  |  | 30 |  | 35
3631 | 101 | 101-14 | 4114 | BACnet MS/TP Meter address | Conf_BACnet_Addr |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 35
3632 | 101 | 101-15 | 4115 | BACnet MS/TP Maximum number of message frames | Conf_BACnet_Max_Frames_Number |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3633 | 101 | 101-16 | 4116 | BACnet MS/TP ID | Conf_BACnet_ID |  | uint32 |  | R/W | 2 | 1 |  |  | 30 |  | 35
3634 | 101 | 101-17 | 4118 | BACnet MS/TP Database Revision | Conf_BACnet_DB_Revision |  | uint16 |  | R | 1 | 1 |  |  | 30
3635 | 101 | 101-18 | 4119 | LCD Backlight Time | Conf_LCD_Backlight_Time |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3636 | 101 | 101-19 | 4120 | Device run time | Conf_Device_Run_Time |  | uint32 |  | R/W | 2 | 1 |  |  | 30
3637 | 101 | 101-20 | 4122 | Device load time | Conf_Device_Load_Time |  | uint32 |  | R/W | 2 | 1 |  |  | 30
3638 | 101 | 101-21 | 4124 | MaxDemand Clear Mode | Conf_MaxDemand_Clear_Mode |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3639 | 101 | 101-22 | 4125 | MaxDemand Clear Date Setting | Conf_MaxDemand_Clear_Date_Setting |  | uint32 |  | R/W | 2 | 1 |  |  | 30
3640 | 101 | 101-23 | 4127 | MaxDemand Clear Total Count | Conf_MaxDemand_Clear_Total_Count |  | uint16 |  | R | 1 | 1 |  |  | 30
3641 | 101 | 101-24 | 4128 | Timestamp of the most recent MaxDemand Clear | Conf_MaxDemand_Clear_Latest_TS_001 |  | uint16 |  | R | 1 | 1 |  |  | 30
3642 | 101 | 101-25 | 4129 | Timestamp of the most recent MaxDemand Clear | Conf_MaxDemand_Clear_Latest_TS_002 |  | uint16 |  | R | 1 | 1 |  |  | 30
3643 | 101 | 101-26 | 4130 | Timestamp of the most recent MaxDemand Clear | Conf_MaxDemand_Clear_Latest_TS_003 |  | uint16 |  | R | 1 | 1 |  |  | 30
3644 | 101 | 101-27 | 4131 | Non-standard Seal Parameter Select | Conf_Seal_Parameter_Select |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3645 | 101 | 101-28 | 4132 | Week | Conf_Week |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3646 | 101 | 101-29 | 4133 | Year | Conf_Year |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3647 | 101 | 101-30 | 4134 | Month | Conf_Month |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3648 | 101 | 101-31 | 4135 | Day | Conf_Day |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3649 | 101 | 101-32 | 4136 | Hour | Conf_Hour |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3650 | 101 | 101-33 | 4137 | Minute | Conf_Minute |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3651 | 101 | 101-34 | 4138 | Second | Conf_Second |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3652 | 101 | 101-35 | 4139 | TempPassword | TempPassword |  | uint16 |  | R | 1 | 1 |  |  | 30
3653 | 102 | 102-1 | 4160 | Sealing Status | Conf_Sealing_Status |  | uint16 | 1 | R | 1 | 1 |  |  | 27-28-30 |  | 9-11-13-15-35-18
3654 | 102 | 102-2 | 4161 | Frequency Selection | Conf_Frequency |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 35
3655 | 102 | 102-3 | 4162 | Service Configuration | Conf_Service |  | uint16 |  | R/W | 1 | 1 |  |  | 27-28-30 |  | 9-11-13-15-35-20-23-36-38
3656 | 102 | 102-4 | 4163 | Reserve1 | Conf_Reserve1 |  | uint32 |  | R/W | 2 | 1
3657 | 102 | 102-5 | 4165 | Reserve2 | Conf_Reserve2 |  | uint16 |  | R/W | 1 | 1
3658 | 103 | 103-1 | 4166 | channel1 input wiring | Conf_Input_Wiring_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3659 | 103 | 103-2 | 4167 | channel1 CT type | Conf_CT_Type_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3660 | 103 | 103-3 | 4168 | channel1 primary | Conf_Primary_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3661 | 103 | 103-4 | 4169 | channel1 direction | Conf_Direction_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3662 | 103 | 103-5 | 4170 | channel1 voltage assignment | Conf_Voltage_Assignment_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3663 | 103 | 103-6 | 4171 | channel2 input wiring | Conf_Input_Wiring_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3664 | 103 | 103-7 | 4172 | channel2 CT type | Conf_CT_Type_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3665 | 103 | 103-8 | 4173 | channel2 primary | Conf_Primary_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3666 | 103 | 103-9 | 4174 | channel2 direction | Conf_Direction_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3667 | 103 | 103-10 | 4175 | channel2 voltage assignment | Conf_Voltage_Assignment_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3668 | 103 | 103-11 | 4176 | channel3 input wiring | Conf_Input_Wiring_003 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3669 | 103 | 103-12 | 4177 | channel3 CT type | Conf_CT_Type_003 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3670 | 103 | 103-13 | 4178 | channel3 primary | Conf_Primary_003 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3671 | 103 | 103-14 | 4179 | channel3 direction | Conf_Direction_003 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3672 | 103 | 103-15 | 4180 | channel3 voltage assignment | Conf_Voltage_Assignment_003 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3673 | 103 | 103-16 | 4181 | channel4 input wiring | Conf_Input_Wiring_004 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3674 | 103 | 103-17 | 4182 | channel4 CT type | Conf_CT_Type_004 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3675 | 103 | 103-18 | 4183 | channel4 primary | Conf_Primary_004 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3676 | 103 | 103-19 | 4184 | channel4 direction | Conf_Direction_004 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3677 | 103 | 103-20 | 4185 | channel4 voltage assignment | Conf_Voltage_Assignment_004 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3678 | 103 | 103-21 | 4186 | channel5 input wiring | Conf_Input_Wiring_005 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3679 | 103 | 103-22 | 4187 | channel5 CT type | Conf_CT_Type_005 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3680 | 103 | 103-23 | 4188 | channel5 primary | Conf_Primary_005 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3681 | 103 | 103-24 | 4189 | channel5 direction | Conf_Direction_005 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3682 | 103 | 103-25 | 4190 | channel5 voltage assignment | Conf_Voltage_Assignment_005 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3683 | 103 | 103-26 | 4191 | channel6 input wiring | Conf_Input_Wiring_006 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3684 | 103 | 103-27 | 4192 | channel6 CT type | Conf_CT_Type_006 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3685 | 103 | 103-28 | 4193 | channel6 primary | Conf_Primary_006 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3686 | 103 | 103-29 | 4194 | channel6 direction | Conf_Direction_006 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3687 | 103 | 103-30 | 4195 | channel6 voltage assignment | Conf_Voltage_Assignment_006 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3688 | 103 | 103-31 | 4196 | channel7 input wiring | Conf_Input_Wiring_007 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3689 | 103 | 103-32 | 4197 | channel7 CT type | Conf_CT_Type_007 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3690 | 103 | 103-33 | 4198 | channel7 primary | Conf_Primary_007 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3691 | 103 | 103-34 | 4199 | channel7 direction | Conf_Direction_007 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3692 | 103 | 103-35 | 4200 | channel7 voltage assignment | Conf_Voltage_Assignment_007 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3693 | 103 | 103-36 | 4201 | channel8 input wiring | Conf_Input_Wiring_008 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3694 | 103 | 103-37 | 4202 | channel8 CT type | Conf_CT_Type_008 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3695 | 103 | 103-38 | 4203 | channel8 primary | Conf_Primary_008 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3696 | 103 | 103-39 | 4204 | channel8 direction | Conf_Direction_008 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3697 | 103 | 103-40 | 4205 | channel8 voltage assignment | Conf_Voltage_Assignment_008 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3698 | 103 | 103-41 | 4206 | channel9 input wiring | Conf_Input_Wiring_009 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3699 | 103 | 103-42 | 4207 | channel9 CT type | Conf_CT_Type_009 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3700 | 103 | 103-43 | 4208 | channel9 primary | Conf_Primary_009 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3701 | 103 | 103-44 | 4209 | channel9 direction | Conf_Direction_009 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3702 | 103 | 103-45 | 4210 | channel9 voltage assignment | Conf_Voltage_Assignment_009 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3703 | 103 | 103-46 | 4211 | channel10 input wiring | Conf_Input_Wiring_010 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3704 | 103 | 103-47 | 4212 | channel10 CT type | Conf_CT_Type_010 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3705 | 103 | 103-48 | 4213 | channel10 primary | Conf_Primary_010 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3706 | 103 | 103-49 | 4214 | channel10 direction | Conf_Direction_010 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3707 | 103 | 103-50 | 4215 | channel10 voltage assignment | Conf_Voltage_Assignment_010 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3708 | 103 | 103-51 | 4216 | channel11 input wiring | Conf_Input_Wiring_011 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3709 | 103 | 103-52 | 4217 | channel11 CT type | Conf_CT_Type_011 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3710 | 103 | 103-53 | 4218 | channel11 primary | Conf_Primary_011 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3711 | 103 | 103-54 | 4219 | channel11 direction | Conf_Direction_011 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3712 | 103 | 103-55 | 4220 | channel11 voltage assignment | Conf_Voltage_Assignment_011 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3713 | 103 | 103-56 | 4221 | channel12 input wiring | Conf_Input_Wiring_012 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3714 | 103 | 103-57 | 4222 | channel12 CT type | Conf_CT_Type_012 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3715 | 103 | 103-58 | 4223 | channel12 primary | Conf_Primary_012 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3716 | 103 | 103-59 | 4224 | channel12 direction | Conf_Direction_012 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3717 | 103 | 103-60 | 4225 | channel12 voltage assignment | Conf_Voltage_Assignment_012 |  | uint16 | 1 | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3718 | 103 | 103-61 | 4226 | channel13 input wiring | Conf_Input_Wiring_013 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3719 | 103 | 103-62 | 4227 | channel13 CT type | Conf_CT_Type_013 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3720 | 103 | 103-63 | 4228 | channel13 primary | Conf_Primary_013 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3721 | 103 | 103-64 | 4229 | channel13 direction | Conf_Direction_013 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3722 | 103 | 103-65 | 4230 | channel13 voltage assignment | Conf_Voltage_Assignment_013 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3723 | 103 | 103-66 | 4231 | channel14 input wiring | Conf_Input_Wiring_014 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3724 | 103 | 103-67 | 4232 | channel14 CT type | Conf_CT_Type_014 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3725 | 103 | 103-68 | 4233 | channel14 primary | Conf_Primary_014 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3726 | 103 | 103-69 | 4234 | channel14 direction | Conf_Direction_014 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3727 | 103 | 103-70 | 4235 | channel14 voltage assignment | Conf_Voltage_Assignment_014 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3728 | 103 | 103-71 | 4236 | channel15 input wiring | Conf_Input_Wiring_015 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3729 | 103 | 103-72 | 4237 | channel15 CT type | Conf_CT_Type_015 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3730 | 103 | 103-73 | 4238 | channel15 primary | Conf_Primary_015 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3731 | 103 | 103-74 | 4239 | channel15 direction | Conf_Direction_015 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3732 | 103 | 103-75 | 4240 | channel15 voltage assignment | Conf_Voltage_Assignment_015 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3733 | 103 | 103-76 | 4241 | channel16 input wiring | Conf_Input_Wiring_016 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3734 | 103 | 103-77 | 4242 | channel16 CT type | Conf_CT_Type_016 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3735 | 103 | 103-78 | 4243 | channel16 primary | Conf_Primary_016 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3736 | 103 | 103-79 | 4244 | channel16 direction | Conf_Direction_016 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3737 | 103 | 103-80 | 4245 | channel16 voltage assignment | Conf_Voltage_Assignment_016 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3738 | 103 | 103-81 | 4246 | channel17 input wiring | Conf_Input_Wiring_017 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3739 | 103 | 103-82 | 4247 | channel17 CT type | Conf_CT_Type_017 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3740 | 103 | 103-83 | 4248 | channel17 primary | Conf_Primary_017 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3741 | 103 | 103-84 | 4249 | channel17 direction | Conf_Direction_017 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3742 | 103 | 103-85 | 4250 | channel17 voltage assignment | Conf_Voltage_Assignment_017 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3743 | 103 | 103-86 | 4251 | channel18 input wiring | Conf_Input_Wiring_018 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3744 | 103 | 103-87 | 4252 | channel18 CT type | Conf_CT_Type_018 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3745 | 103 | 103-88 | 4253 | channel18 primary | Conf_Primary_018 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3746 | 103 | 103-89 | 4254 | channel18 direction | Conf_Direction_018 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3747 | 103 | 103-90 | 4255 | channel18 voltage assignment | Conf_Voltage_Assignment_018 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3748 | 103 | 103-91 | 4256 | channel19 input wiring | Conf_Input_Wiring_019 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3749 | 103 | 103-92 | 4257 | channel19 CT type | Conf_CT_Type_019 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3750 | 103 | 103-93 | 4258 | channel19 primary | Conf_Primary_019 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3751 | 103 | 103-94 | 4259 | channel19 direction | Conf_Direction_019 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3752 | 103 | 103-95 | 4260 | channel19 voltage assignment | Conf_Voltage_Assignment_019 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3753 | 103 | 103-96 | 4261 | channel20 input wiring | Conf_Input_Wiring_020 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3754 | 103 | 103-97 | 4262 | channel20 CT type | Conf_CT_Type_020 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3755 | 103 | 103-98 | 4263 | channel20 primary | Conf_Primary_020 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3756 | 103 | 103-99 | 4264 | channel20 direction | Conf_Direction_020 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3757 | 103 | 103-100 | 4265 | channel20 voltage assignment | Conf_Voltage_Assignment_020 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3758 | 103 | 103-101 | 4266 | channel21 input wiring | Conf_Input_Wiring_021 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3759 | 103 | 103-102 | 4267 | channel21 CT type | Conf_CT_Type_021 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3760 | 103 | 103-103 | 4268 | channel21 primary | Conf_Primary_021 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3761 | 103 | 103-104 | 4269 | channel21 direction | Conf_Direction_021 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3762 | 103 | 103-105 | 4270 | channel21 voltage assignment | Conf_Voltage_Assignment_021 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3763 | 103 | 103-106 | 4271 | channel22 input wiring | Conf_Input_Wiring_022 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3764 | 103 | 103-107 | 4272 | channel22 CT type | Conf_CT_Type_022 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3765 | 103 | 103-108 | 4273 | channel22 primary | Conf_Primary_022 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3766 | 103 | 103-109 | 4274 | channel22 direction | Conf_Direction_022 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3767 | 103 | 103-110 | 4275 | channel22 voltage assignment | Conf_Voltage_Assignment_022 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3768 | 103 | 103-111 | 4276 | channel23 input wiring | Conf_Input_Wiring_023 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3769 | 103 | 103-112 | 4277 | channel23 CT type | Conf_CT_Type_023 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3770 | 103 | 103-113 | 4278 | channel23 primary | Conf_Primary_023 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3771 | 103 | 103-114 | 4279 | channel23 direction | Conf_Direction_023 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3772 | 103 | 103-115 | 4280 | channel23 voltage assignment | Conf_Voltage_Assignment_023 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3773 | 103 | 103-116 | 4281 | channel24 input wiring | Conf_Input_Wiring_024 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-10
3774 | 103 | 103-117 | 4282 | channel24 CT type | Conf_CT_Type_024 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3775 | 103 | 103-118 | 4283 | channel24 primary | Conf_Primary_024 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35
3776 | 103 | 103-119 | 4284 | channel24 direction | Conf_Direction_024 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15
3777 | 103 | 103-120 | 4285 | channel24 voltage assignment | Conf_Voltage_Assignment_024 |  | uint16 |  | R/W | 1 | 1 |  |  | 28 |  | 9-11-13-15-35-20-23-36-38-10
3778 | 104 | 104-1 | 4286 | user 1 input channel assignment | Conf_Input_Channel_Assignment_s001 |  | uint32 |  | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3779 | 104 | 104-2 | 4288 | user 2 input channel assignment | Conf_Input_Channel_Assignment_s002 |  | uint32 |  | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3780 | 104 | 104-3 | 4290 | user 3 input channel assignment | Conf_Input_Channel_Assignment_s003 |  | uint32 |  | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3781 | 104 | 104-4 | 4292 | user 4 input channel assignment | Conf_Input_Channel_Assignment_s004 |  | uint32 | 6 | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3782 | 104 | 104-5 | 4294 | user 5 input channel assignment | Conf_Input_Channel_Assignment_s005 |  | uint32 |  | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3783 | 104 | 104-6 | 4296 | user 6 input channel assignment | Conf_Input_Channel_Assignment_s006 |  | uint32 |  | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3784 | 104 | 104-7 | 4298 | user 7 input channel assignment | Conf_Input_Channel_Assignment_s007 |  | uint32 |  | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3785 | 104 | 104-8 | 4300 | user 8 input channel assignment | Conf_Input_Channel_Assignment_s008 |  | uint32 |  | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3786 | 104 | 104-9 | 4302 | user 9 input channel assignment | Conf_Input_Channel_Assignment_s009 |  | uint32 |  | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3787 | 104 | 104-10 | 4304 | user 10 input channel assignment | Conf_Input_Channel_Assignment_s010 |  | uint32 |  | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3788 | 104 | 104-11 | 4306 | user 11 input channel assignment | Conf_Input_Channel_Assignment_s011 |  | uint32 |  | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3789 | 104 | 104-12 | 4308 | user 12 input channel assignment | Conf_Input_Channel_Assignment_s012 |  | uint32 |  | R/W | 2 | 1 |  |  | 28-29 |  | 9-11-13-15-35-20-23-36-38
3790 | 104 | 104-13 | 4310 | Demand Method | Conf_Demand_Method |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3791 | 104 | 104-14 | 4311 | Demand Interval | Conf_Demand_Interval |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3792 | 104 | 104-15 | 4312 | Demand update rate | Conf_Demand_Update_Rate |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3793 | 104 | 104-16 | 4313 | VAR/PF Convention | Conf_VAR_PF_Convention |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3794 | 104 | 104-17 | 4314 | Energy Calculation Method | Conf_Energy_Calculation_Method |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3795 | 104 | 104-18 | 4315 | Reactive Power Calculation Method | Conf_Reactive_Power_Calculation_Method |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3796 | 104 | 104-19 | 4316 | Phase Order | Conf_Phase_Order |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3797 | 104 | 104-20 | 4317 | Energy Reading Display format | Conf_Energy_Reading_Display_Format |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3798 | 104 | 104-21 | 4318 | Reserve3 | Conf_Reserve3 |  | uint16 |  | R/W | 1 | 1
3799 | 104 | 104-22 | 4319 | Energy pulse constant | Conf_Energy_Pulse_Constant |  | uint32 |  | R/W | 2 | 0.001 |  |  | 30 |  | 35
3800 | 104 | 104-23 | 4321 | Pulse LED width | Conf_Pulse_LED_Width |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3801 | 104 | 104-24 | 4322 | Pulse LED parameter selection | Conf_Pulse_LED_Parameter_Selection |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3802 | 105 | 105-1 | 4352 | DO1 Type | Conf_DO_Type_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3803 | 105 | 105-2 | 4353 | DO1 Pulse width | Conf_DO_Pulse_Width_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3804 | 105 | 105-3 | 4354 | DO1 parameter selection | Conf_DO_Parameter_Selection_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3805 | 105 | 105-4 | 4355 | DO2 Type | Conf_DO_Type_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3806 | 105 | 105-5 | 4356 | DO2 Pulse width | Conf_DO_Pulse_Width_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3807 | 105 | 105-6 | 4357 | DO2 parameter selection | Conf_DO_Parameter_Selection_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3808 | 105 | 105-7 | 4358 | DO3 Type | Conf_DO_Type_003 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3809 | 105 | 105-8 | 4359 | DO3 Pulse width | Conf_DO_Pulse_Width_003 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3810 | 105 | 105-9 | 4360 | DO3 parameter selection | Conf_DO_Parameter_Selection_003 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3811 | 105 | 105-10 | 4361 | DO4 Type | Conf_DO_Type_004 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3812 | 105 | 105-11 | 4362 | DO4 Pulse width | Conf_DO_Pulse_Width_004 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3813 | 105 | 105-12 | 4363 | DO4 parameter selection | Conf_DO_Parameter_Selection_004 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3814 | 105 | 105-13 | 4364 | DO5 Type | Conf_DO_Type_005 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3815 | 105 | 105-14 | 4365 | DO5 Pulse width | Conf_DO_Pulse_Width_005 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3816 | 105 | 105-15 | 4366 | DO5 parameter selection | Conf_DO_Parameter_Selection_005 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3817 | 105 | 105-16 | 4367 | DO6 Type | Conf_DO_Type_006 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3818 | 105 | 105-17 | 4368 | DO6 Pulse width | Conf_DO_Pulse_Width_006 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3819 | 105 | 105-18 | 4369 | DO6 parameter selection | Conf_DO_Parameter_Selection_006 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3820 | 105 | 105-19 | 4370 | DO7 Type | Conf_DO_Type_007 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3821 | 105 | 105-20 | 4371 | DO7 Pulse width | Conf_DO_Pulse_Width_007 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3822 | 105 | 105-21 | 4372 | DO7 parameter selection | Conf_DO_Parameter_Selection_007 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3823 | 105 | 105-22 | 4373 | DO8 Type | Conf_DO_Type_008 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3824 | 105 | 105-23 | 4374 | DO8 Pulse width | Conf_DO_Pulse_Width_008 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3825 | 105 | 105-24 | 4375 | DO8parameter selection | Conf_DO_Parameter_Selection_008 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3826 | 105 | 105-25 | 4376 | DI1 Type | Conf_DI_Type_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3827 | 105 | 105-26 | 4377 | DI1 pulse constant | Conf_DI_Pulse_Constant_001 |  | uint32 |  | R/W | 2 | 0.001 |  |  | 30 |  | 26
3828 | 105 | 105-27 | 4379 | DI2 Type | Conf_DI_Type_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3829 | 105 | 105-28 | 4380 | DI2 pulse constant | Conf_DI_Pulse_Constant_002 |  | uint32 |  | R/W | 2 | 0.001 |  |  | 30 |  | 26
3830 | 105 | 105-29 | 4382 | DI3 Type | Conf_DI_Type_003 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3831 | 105 | 105-30 | 4383 | DI3 pulse constant | Conf_DI_Pulse_Constant_003 |  | uint32 |  | R/W | 2 | 0.001 |  |  | 30 |  | 26
3832 | 105 | 105-31 | 4385 | DI4 Type | Conf_DI_Type_004 |  | uint16 |  | R/W | 1 | 1 |  |  | 30 |  | 26
3833 | 105 | 105-32 | 4386 | DI4 pulse constant | Conf_DI_Pulse_Constant_004 |  | uint32 |  | R/W | 2 | 0.001 |  |  | 30 |  | 26
3834 | 105 | 105-33 | 4388 | RO1 Type | Conf_RO_Type_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3835 | 105 | 105-34 | 4389 | RO1 Control Mode | Conf_RO_Control_Mode_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3836 | 105 | 105-35 | 4390 | RO1 Pulse Width | Conf_RO_Pulse_Width_001 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3837 | 105 | 105-36 | 4391 | RO2 Type | Conf_RO_Type_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3838 | 105 | 105-37 | 4392 | RO2 Control Mode | Conf_RO_Control_Mode_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3839 | 105 | 105-38 | 4393 | RO2 Pulse Width | Conf_RO_Pulse_Width_002 |  | uint16 |  | R/W | 1 | 1 |  |  | 30
3840 | 106 | 106-1 | 4400 | Clear energy | Conf_Clear_Energy |  | uint16 |  | W | 1 | 1
3841 | 106 | 106-2 | 4401 | Clear Max demand | Conf_Clear_Max_Demand |  | uint16 |  | W | 1 | 1
3842 | 106 | 106-3 | 4402 | Clear MaxDemand ClearCount and Timestamp | Conf_Clear_MaxDemand_ClearCount_Timestamp |  | uint16 |  | W | 1 | 1 |  |  | 30
3843 | 106 | 106-4 | 4403 | Clear max/min | Conf_Clear_Max_Min |  | uint16 |  | W | 1 | 1
3844 | 106 | 106-5 | 4404 | Clear device run time | Conf_Clear_Device_Run_Time |  | uint16 |  | W | 1 | 1
3845 | 106 | 106-6 | 4405 | Clear load time | Conf_Clear_Load_Time |  | uint16 | 1 | W | 1 | 1
3846 | 106 | 106-7 | 4406 | Factory reset | Conf_Reset_Factory |  | uint16 |  | W | 1 | 1
3847 | 106 | 106-8 | 4407 | Network reset | Conf_Reset_Network |  | uint16 |  | W | 1 | 1
3848 | 106 | 106-9 | 4408 | Clear SOE Log | Conf_Clear_SOE_Log |  | uint16 |  | W | 1 | 1
3849 | 106 | 106-10 | 4409 | Clear alarm Log | Conf_Clear_Alarm_Log |  | uint16 |  | W | 1 | 1
3850 | 106 | 106-11 | 4410 | Clear PQ event Log | Conf_Clear_PQEvent_Log |  | uint16 |  | W | 1 | 1
3851 | 106 | 106-12 | 4411 | Clear Waveform | Conf_Clear_Waveform |  | uint16 |  | W | 1 | 1
3852 | 106 | 106-13 | 4412 | Clear Data Log1 | Conf_Clear_Data_Log1 |  | uint16 |  | W | 1 | 1
3853 | 106 | 106-14 | 4413 | Clear Data Log2 | Conf_Clear_Data_Log2 |  | uint16 |  | W | 1 | 1
3854 | 106 | 106-15 | 4414 | Clear Data Log3 | Conf_Clear_Data_Log3 |  | uint16 |  | W | 1 | 1
3855 | 106 | 106-16 | 4415 | Clear Trend Log | Conf_Clear_Trend_Log |  | uint16 |  | W | 1 | 1
3856 | 106 | 106-17 | 4416 | Clear DI Count | Conf_Clear_DI_Count |  | uint16 |  | W | 1 | 1
3857 | 106 | 106-18 | 4417 | Clear Year 10 Holiday Number Setting | Conf_Clear_Year10_Holiday_Number_Setting |  | uint16 |  | W | 1 | 1
3858 | 106 | 106-19 | 4418 | Restore TOU factory setting | Conf_Restore_TOU_Factory_Setting |  | uint16 |  | W | 1 | 1
3859 | 106 | 106-20 | 4419 | Clear TOU Energy | Conf_TOU_Energy |  | uint16 |  | W | 1 | 1
3860 | 106 | 106-21 | 4420 | Device Reboot | Conf_Device_Reboot |  | uint16 |  | W | 1 | 1
3861 | 107 | 107-1 | 25344 | The index of the SOE Log | SOE_Index |  | uint16 |  | R | 1 | 1 |  |  |  |  | 19
3862 | 107 | 107-2 | 25345 | Number of the SOE Log | SOE_Number |  | uint16 |  | R | 1 | 1 |  |  |  |  | 19

## analysisUnits
analysisUnitId | analysisUnitTypeName

## analysisParams
threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis | threePhaseMeterAnalysis
three_phase_realtime | three_phase_energy_demand | three_phase_thd | three_phase_harmonics | three_phase_sequence
VLN_a_V | EP_IMP_a_kWh | THD_V_a_% | HAR2_V_a_% | SEQ_POS_REAL_I
ANG_VLN_a | EQ_IMP_a_kvarh | OTHD_V_a_% | HAR3_V_a_% | SEQ_NEG_REAL_I
VLL_ab_V | EP_EXP_a_kWh | ETHD_V_a_% | HAR4_V_a_% | SEQ_ZERO_REAL_I
ANG_VLL_ab | EQ_EXP_a_kvarh | CF_V_a_% | HAR5_V_a_% | SEQ_POS_IMG_I
I_a_A | EP_NET_a_kWh | THD_I_a_% | HAR6_V_a_% | SEQ_NEG_IMG_I
ANG_I_a | EQ_NET_a_kvarh | OTHD_I_a_% | HAR7_V_a_% | SEQ_ZERO_IMG_I
P_a_kW | EP_TOTAL_a_kWh | ETHD_I_a_% | HAR8_V_a_% | SEQ_POS_REAL_V
Q_a_kvar | EQ_TOTAL_a_kvarh | TDD_I_a_% | HAR9_V_a_% | SEQ_NEG_REAL_V
S_a_kVA | ES_a_kVAh | CF_I_a_% | HAR10_V_a_% | SEQ_ZERO_REAL_V
LC_a | EP_IMP_b_kWh | KF_I_a_% | HAR11_V_a_% | SEQ_POS_IMG_V
PF_a | EQ_IMP_b_kvarh | THD_V_b_% | HAR12_V_a_% | SEQ_NEG_IMG_V
LEAD_PF_a | EP_EXP_b_kWh | OTHD_V_b_% | HAR13_V_a_% | SEQ_ZERO_IMG_V
LAG_PF_a | EQ_EXP_b_kvarh | ETHD_V_b_% | HAR14_V_a_% | UNBL_V_%
VLN_b_V | EP_NET_b_kWh | CF_V_b_% | HAR15_V_a_% | UNBL_I_%
ANG_VLN_b | EQ_NET_b_kvarh | THD_I_b_% | HAR16_V_a_% | SEQ_ZERO_RATIO_V_%
VLL_bc_V | EP_TOTAL_b_kWh | OTHD_I_b_% | HAR17_V_a_% | SEQ_ZERO_RATIO_I_%
ANG_VLL_bb | EQ_TOTAL_b_kvarh | ETHD_I_b_% | HAR18_V_a_%
I_b_A | ES_b_kVAh | TDD_I_b_% | HAR19_V_a_%
ANG_I_b | EP_IMP_c_kWh | CF_I_b_% | HAR20_V_a_%
P_b_kW | EQ_IMP_c_kvarh | KF_I_b_% | HAR21_V_a_%
Q_b_kvar | EP_EXP_c_kWh | THD_V_c_% | HAR22_V_a_%
S_b_kVA | EQ_EXP_c_kvarh | OTHD_V_c_% | HAR23_V_a_%
LC_b | EP_NET_c_kWh | ETHD_V_c_% | HAR24_V_a_%
PF_b | EQ_NET_c_kvarh | CF_V_c_% | HAR25_V_a_%
LEAD_PF_b | EP_TOTAL_c_kWh | THD_I_c_% | HAR26_V_a_%
LAG_PF_b | EQ_TOTAL_c_kvarh | OTHD_I_c_% | HAR27_V_a_%
VLN_c_V | ES_c_kVAh | ETHD_I_c_% | HAR28_V_a_%
ANG_VLN_c | EP_IMP_kWh | TDD_I_c_% | HAR29_V_a_%
VLL_ca_V | EQ_IMP_kvarh | CF_I_c_% | HAR30_V_a_%
ANG_VLL_cb | EP_EXP_kWh | KF_I_c_% | HAR31_V_a_%
I_c_A | EQ_EXP_kvarh | THD_V_avg_% | HAR32_V_a_%
ANG_I_c | EP_NET_kWh | OTHD_V_avg_% | HAR33_V_a_%
P_c_kW | EQ_NET_kvarh | ETHD_V_avg_% | HAR34_V_a_%
Q_c_kvar | EP_TOTAL_kWh | CF_V_avg_% | HAR35_V_a_%
S_c_kVA | EQ_TOTAL_kvarh | THD_I_avg_% | HAR36_V_a_%
LC_c | ES_kVAh | OTHD_I_avg_% | HAR37_V_a_%
PF_c | DMD_P_a_kW | ETHD_I_avg_% | HAR38_V_a_%
LEAD_PF_c | DMD_Q_a_kvar | TDD_I_avg_% | HAR39_V_a_%
LAG_PF_c | DMD_S_a_kVA | CF_I_avg_% | HAR40_V_a_%
VLN_avg_V | DMD_P_b_kW | KF_I_avg_% | HAR41_V_a_%
VLL_avg_V | DMD_Q_b_kvar |  | HAR42_V_a_%
I_avg_A | DMD_S_b_kVA |  | HAR43_V_a_%
LC_avg | DMD_P_c_kW |  | HAR44_V_a_%
I_n_A | DMD_Q_c_kvar |  | HAR45_V_a_%
P_kW | DMD_S_c_kVA |  | HAR46_V_a_%
Q_kvar | DMD_P_kW |  | HAR47_V_a_%
S_kVA | DMD_Q_kvar |  | HAR48_V_a_%
PF | DMD_S_kVA |  | HAR49_V_a_%
LEAD_PF |  |  | HAR50_V_a_%
LAG_PF |  |  | HAR51_V_a_%
FREQ_Hz |  |  | HAR52_V_a_%
HAR53_V_a_%
HAR54_V_a_%
HAR55_V_a_%
HAR56_V_a_%
HAR57_V_a_%
HAR58_V_a_%
HAR59_V_a_%
HAR60_V_a_%
HAR61_V_a_%
HAR62_V_a_%
HAR63_V_a_%
HAR64_V_a_%
HAR65_V_a_%
HAR66_V_a_%
HAR67_V_a_%
HAR68_V_a_%
HAR69_V_a_%
HAR70_V_a_%
HAR71_V_a_%
HAR72_V_a_%
HAR73_V_a_%
HAR74_V_a_%
HAR75_V_a_%
HAR76_V_a_%
HAR77_V_a_%
HAR78_V_a_%
HAR79_V_a_%
HAR80_V_a_%
HAR81_V_a_%
HAR82_V_a_%
HAR83_V_a_%
HAR84_V_a_%
HAR85_V_a_%
HAR86_V_a_%
HAR87_V_a_%
HAR88_V_a_%
HAR89_V_a_%
HAR90_V_a_%
HAR91_V_a_%
HAR92_V_a_%
HAR93_V_a_%
HAR94_V_a_%
HAR95_V_a_%
HAR96_V_a_%
HAR97_V_a_%
HAR98_V_a_%
HAR99_V_a_%
HAR100_V_a_%
HAR101_V_a_%
HAR102_V_a_%
HAR103_V_a_%
HAR104_V_a_%
HAR105_V_a_%
HAR106_V_a_%
HAR107_V_a_%
HAR108_V_a_%
HAR109_V_a_%
HAR110_V_a_%
HAR111_V_a_%
HAR112_V_a_%
HAR113_V_a_%
HAR114_V_a_%
HAR115_V_a_%
HAR116_V_a_%
HAR117_V_a_%
HAR118_V_a_%
HAR119_V_a_%
HAR120_V_a_%
HAR121_V_a_%
HAR122_V_a_%
HAR123_V_a_%
HAR124_V_a_%
HAR125_V_a_%
HAR126_V_a_%
HAR127_V_a_%
ANG_HAR2_V_a
ANG_HAR3_V_a
ANG_HAR4_V_a
ANG_HAR5_V_a
ANG_HAR6_V_a
ANG_HAR7_V_a
ANG_HAR8_V_a
ANG_HAR9_V_a
ANG_HAR10_V_a
ANG_HAR11_V_a
ANG_HAR12_V_a
ANG_HAR13_V_a
ANG_HAR14_V_a
ANG_HAR15_V_a
ANG_HAR16_V_a
ANG_HAR17_V_a
ANG_HAR18_V_a
ANG_HAR19_V_a
ANG_HAR20_V_a
ANG_HAR21_V_a
ANG_HAR22_V_a
ANG_HAR23_V_a
ANG_HAR24_V_a
ANG_HAR25_V_a
ANG_HAR26_V_a
ANG_HAR27_V_a
ANG_HAR28_V_a
ANG_HAR29_V_a
ANG_HAR30_V_a
ANG_HAR31_V_a
ANG_HAR32_V_a
ANG_HAR33_V_a
ANG_HAR34_V_a
ANG_HAR35_V_a
ANG_HAR36_V_a
ANG_HAR37_V_a
ANG_HAR38_V_a
ANG_HAR39_V_a
ANG_HAR40_V_a
ANG_HAR41_V_a
ANG_HAR42_V_a
ANG_HAR43_V_a
ANG_HAR44_V_a
ANG_HAR45_V_a
ANG_HAR46_V_a
ANG_HAR47_V_a
ANG_HAR48_V_a
ANG_HAR49_V_a
ANG_HAR50_V_a
ANG_HAR51_V_a
ANG_HAR52_V_a
ANG_HAR53_V_a
ANG_HAR54_V_a
ANG_HAR55_V_a
ANG_HAR56_V_a
ANG_HAR57_V_a
ANG_HAR58_V_a
ANG_HAR59_V_a
ANG_HAR60_V_a
ANG_HAR61_V_a
ANG_HAR62_V_a
ANG_HAR63_V_a
ANG_HAR64_V_a
ANG_HAR65_V_a
ANG_HAR66_V_a
ANG_HAR67_V_a
ANG_HAR68_V_a
ANG_HAR69_V_a
ANG_HAR70_V_a
ANG_HAR71_V_a
ANG_HAR72_V_a
ANG_HAR73_V_a
ANG_HAR74_V_a
ANG_HAR75_V_a
ANG_HAR76_V_a
ANG_HAR77_V_a
ANG_HAR78_V_a
ANG_HAR79_V_a
ANG_HAR80_V_a
ANG_HAR81_V_a
ANG_HAR82_V_a
ANG_HAR83_V_a
ANG_HAR84_V_a
ANG_HAR85_V_a
ANG_HAR86_V_a
ANG_HAR87_V_a
ANG_HAR88_V_a
ANG_HAR89_V_a
ANG_HAR90_V_a
ANG_HAR91_V_a
ANG_HAR92_V_a
ANG_HAR93_V_a
ANG_HAR94_V_a
ANG_HAR95_V_a
ANG_HAR96_V_a
ANG_HAR97_V_a
ANG_HAR98_V_a
ANG_HAR99_V_a
ANG_HAR100_V_a
ANG_HAR101_V_a
ANG_HAR102_V_a
ANG_HAR103_V_a
ANG_HAR104_V_a
ANG_HAR105_V_a
ANG_HAR106_V_a
ANG_HAR107_V_a
ANG_HAR108_V_a
ANG_HAR109_V_a
ANG_HAR110_V_a
ANG_HAR111_V_a
ANG_HAR112_V_a
ANG_HAR113_V_a
ANG_HAR114_V_a
ANG_HAR115_V_a
ANG_HAR116_V_a
ANG_HAR117_V_a
ANG_HAR118_V_a
ANG_HAR119_V_a
ANG_HAR120_V_a
ANG_HAR121_V_a
ANG_HAR122_V_a
ANG_HAR123_V_a
ANG_HAR124_V_a
ANG_HAR125_V_a
ANG_HAR126_V_a
ANG_HAR127_V_a
HAR2_V_b_%
HAR3_V_b_%
HAR4_V_b_%
HAR5_V_b_%
HAR6_V_b_%
HAR7_V_b_%
HAR8_V_b_%
HAR9_V_b_%
HAR10_V_b_%
HAR11_V_b_%
HAR12_V_b_%
HAR13_V_b_%
HAR14_V_b_%
HAR15_V_b_%
HAR16_V_b_%
HAR17_V_b_%
HAR18_V_b_%
HAR19_V_b_%
HAR20_V_b_%
HAR21_V_b_%
HAR22_V_b_%
HAR23_V_b_%
HAR24_V_b_%
HAR25_V_b_%
HAR26_V_b_%
HAR27_V_b_%
HAR28_V_b_%
HAR29_V_b_%
HAR30_V_b_%
HAR31_V_b_%
HAR32_V_b_%
HAR33_V_b_%
HAR34_V_b_%
HAR35_V_b_%
HAR36_V_b_%
HAR37_V_b_%
HAR38_V_b_%
HAR39_V_b_%
HAR40_V_b_%
HAR41_V_b_%
HAR42_V_b_%
HAR43_V_b_%
HAR44_V_b_%
HAR45_V_b_%
HAR46_V_b_%
HAR47_V_b_%
HAR48_V_b_%
HAR49_V_b_%
HAR50_V_b_%
HAR51_V_b_%
HAR52_V_b_%
HAR53_V_b_%
HAR54_V_b_%
HAR55_V_b_%
HAR56_V_b_%
HAR57_V_b_%
HAR58_V_b_%
HAR59_V_b_%
HAR60_V_b_%
HAR61_V_b_%
HAR62_V_b_%
HAR63_V_b_%
HAR64_V_b_%
HAR65_V_b_%
HAR66_V_b_%
HAR67_V_b_%
HAR68_V_b_%
HAR69_V_b_%
HAR70_V_b_%
HAR71_V_b_%
HAR72_V_b_%
HAR73_V_b_%
HAR74_V_b_%
HAR75_V_b_%
HAR76_V_b_%
HAR77_V_b_%
HAR78_V_b_%
HAR79_V_b_%
HAR80_V_b_%
HAR81_V_b_%
HAR82_V_b_%
HAR83_V_b_%
HAR84_V_b_%
HAR85_V_b_%
HAR86_V_b_%
HAR87_V_b_%
HAR88_V_b_%
HAR89_V_b_%
HAR90_V_b_%
HAR91_V_b_%
HAR92_V_b_%
HAR93_V_b_%
HAR94_V_b_%
HAR95_V_b_%
HAR96_V_b_%
HAR97_V_b_%
HAR98_V_b_%
HAR99_V_b_%
HAR100_V_b_%
HAR101_V_b_%
HAR102_V_b_%
HAR103_V_b_%
HAR104_V_b_%
HAR105_V_b_%
HAR106_V_b_%
HAR107_V_b_%
HAR108_V_b_%
HAR109_V_b_%
HAR110_V_b_%
HAR111_V_b_%
HAR112_V_b_%
HAR113_V_b_%
HAR114_V_b_%
HAR115_V_b_%
HAR116_V_b_%
HAR117_V_b_%
HAR118_V_b_%
HAR119_V_b_%
HAR120_V_b_%
HAR121_V_b_%
HAR122_V_b_%
HAR123_V_b_%
HAR124_V_b_%
HAR125_V_b_%
HAR126_V_b_%
HAR127_V_b_%
ANG_HAR2_V_b
ANG_HAR3_V_b
ANG_HAR4_V_b
ANG_HAR5_V_b
ANG_HAR6_V_b
ANG_HAR7_V_b
ANG_HAR8_V_b
ANG_HAR9_V_b
ANG_HAR10_V_b
ANG_HAR11_V_b
ANG_HAR12_V_b
ANG_HAR13_V_b
ANG_HAR14_V_b
ANG_HAR15_V_b
ANG_HAR16_V_b
ANG_HAR17_V_b
ANG_HAR18_V_b
ANG_HAR19_V_b
ANG_HAR20_V_b
ANG_HAR21_V_b
ANG_HAR22_V_b
ANG_HAR23_V_b
ANG_HAR24_V_b
ANG_HAR25_V_b
ANG_HAR26_V_b
ANG_HAR27_V_b
ANG_HAR28_V_b
ANG_HAR29_V_b
ANG_HAR30_V_b
ANG_HAR31_V_b
ANG_HAR32_V_b
ANG_HAR33_V_b
ANG_HAR34_V_b
ANG_HAR35_V_b
ANG_HAR36_V_b
ANG_HAR37_V_b
ANG_HAR38_V_b
ANG_HAR39_V_b
ANG_HAR40_V_b
ANG_HAR41_V_b
ANG_HAR42_V_b
ANG_HAR43_V_b
ANG_HAR44_V_b
ANG_HAR45_V_b
ANG_HAR46_V_b
ANG_HAR47_V_b
ANG_HAR48_V_b
ANG_HAR49_V_b
ANG_HAR50_V_b
ANG_HAR51_V_b
ANG_HAR52_V_b
ANG_HAR53_V_b
ANG_HAR54_V_b
ANG_HAR55_V_b
ANG_HAR56_V_b
ANG_HAR57_V_b
ANG_HAR58_V_b
ANG_HAR59_V_b
ANG_HAR60_V_b
ANG_HAR61_V_b
ANG_HAR62_V_b
ANG_HAR63_V_b
ANG_HAR64_V_b
ANG_HAR65_V_b
ANG_HAR66_V_b
ANG_HAR67_V_b
ANG_HAR68_V_b
ANG_HAR69_V_b
ANG_HAR70_V_b
ANG_HAR71_V_b
ANG_HAR72_V_b
ANG_HAR73_V_b
ANG_HAR74_V_b
ANG_HAR75_V_b
ANG_HAR76_V_b
ANG_HAR77_V_b
ANG_HAR78_V_b
ANG_HAR79_V_b
ANG_HAR80_V_b
ANG_HAR81_V_b
ANG_HAR82_V_b
ANG_HAR83_V_b
ANG_HAR84_V_b
ANG_HAR85_V_b
ANG_HAR86_V_b
ANG_HAR87_V_b
ANG_HAR88_V_b
ANG_HAR89_V_b
ANG_HAR90_V_b
ANG_HAR91_V_b
ANG_HAR92_V_b
ANG_HAR93_V_b
ANG_HAR94_V_b
ANG_HAR95_V_b
ANG_HAR96_V_b
ANG_HAR97_V_b
ANG_HAR98_V_b
ANG_HAR99_V_b
ANG_HAR100_V_b
ANG_HAR101_V_b
ANG_HAR102_V_b
ANG_HAR103_V_b
ANG_HAR104_V_b
ANG_HAR105_V_b
ANG_HAR106_V_b
ANG_HAR107_V_b
ANG_HAR108_V_b
ANG_HAR109_V_b
ANG_HAR110_V_b
ANG_HAR111_V_b
ANG_HAR112_V_b
ANG_HAR113_V_b
ANG_HAR114_V_b
ANG_HAR115_V_b
ANG_HAR116_V_b
ANG_HAR117_V_b
ANG_HAR118_V_b
ANG_HAR119_V_b
ANG_HAR120_V_b
ANG_HAR121_V_b
ANG_HAR122_V_b
ANG_HAR123_V_b
ANG_HAR124_V_b
ANG_HAR125_V_b
ANG_HAR126_V_b
ANG_HAR127_V_b
HAR2_V_c_%
HAR3_V_c_%
HAR4_V_c_%
HAR5_V_c_%
HAR6_V_c_%
HAR7_V_c_%
HAR8_V_c_%
HAR9_V_c_%
HAR10_V_c_%
HAR11_V_c_%
HAR12_V_c_%
HAR13_V_c_%
HAR14_V_c_%
HAR15_V_c_%
HAR16_V_c_%
HAR17_V_c_%
HAR18_V_c_%
HAR19_V_c_%
HAR20_V_c_%
HAR21_V_c_%
HAR22_V_c_%
HAR23_V_c_%
HAR24_V_c_%
HAR25_V_c_%
HAR26_V_c_%
HAR27_V_c_%
HAR28_V_c_%
HAR29_V_c_%
HAR30_V_c_%
HAR31_V_c_%
HAR32_V_c_%
HAR33_V_c_%
HAR34_V_c_%
HAR35_V_c_%
HAR36_V_c_%
HAR37_V_c_%
HAR38_V_c_%
HAR39_V_c_%
HAR40_V_c_%
HAR41_V_c_%
HAR42_V_c_%
HAR43_V_c_%
HAR44_V_c_%
HAR45_V_c_%
HAR46_V_c_%
HAR47_V_c_%
HAR48_V_c_%
HAR49_V_c_%
HAR50_V_c_%
HAR51_V_c_%
HAR52_V_c_%
HAR53_V_c_%
HAR54_V_c_%
HAR55_V_c_%
HAR56_V_c_%
HAR57_V_c_%
HAR58_V_c_%
HAR59_V_c_%
HAR60_V_c_%
HAR61_V_c_%
HAR62_V_c_%
HAR63_V_c_%
HAR64_V_c_%
HAR65_V_c_%
HAR66_V_c_%
HAR67_V_c_%
HAR68_V_c_%
HAR69_V_c_%
HAR70_V_c_%
HAR71_V_c_%
HAR72_V_c_%
HAR73_V_c_%
HAR74_V_c_%
HAR75_V_c_%
HAR76_V_c_%
HAR77_V_c_%
HAR78_V_c_%
HAR79_V_c_%
HAR80_V_c_%
HAR81_V_c_%
HAR82_V_c_%
HAR83_V_c_%
HAR84_V_c_%
HAR85_V_c_%
HAR86_V_c_%
HAR87_V_c_%
HAR88_V_c_%
HAR89_V_c_%
HAR90_V_c_%
HAR91_V_c_%
HAR92_V_c_%
HAR93_V_c_%
HAR94_V_c_%
HAR95_V_c_%
HAR96_V_c_%
HAR97_V_c_%
HAR98_V_c_%
HAR99_V_c_%
HAR100_V_c_%
HAR101_V_c_%
HAR102_V_c_%
HAR103_V_c_%
HAR104_V_c_%
HAR105_V_c_%
HAR106_V_c_%
HAR107_V_c_%
HAR108_V_c_%
HAR109_V_c_%
HAR110_V_c_%
HAR111_V_c_%
HAR112_V_c_%
HAR113_V_c_%
HAR114_V_c_%
HAR115_V_c_%
HAR116_V_c_%
HAR117_V_c_%
HAR118_V_c_%
HAR119_V_c_%
HAR120_V_c_%
HAR121_V_c_%
HAR122_V_c_%
HAR123_V_c_%
HAR124_V_c_%
HAR125_V_c_%
HAR126_V_c_%
HAR127_V_c_%
ANG_HAR2_V_c
ANG_HAR3_V_c
ANG_HAR4_V_c
ANG_HAR5_V_c
ANG_HAR6_V_c
ANG_HAR7_V_c
ANG_HAR8_V_c
ANG_HAR9_V_c
ANG_HAR10_V_c
ANG_HAR11_V_c
ANG_HAR12_V_c
ANG_HAR13_V_c
ANG_HAR14_V_c
ANG_HAR15_V_c
ANG_HAR16_V_c
ANG_HAR17_V_c
ANG_HAR18_V_c
ANG_HAR19_V_c
ANG_HAR20_V_c
ANG_HAR21_V_c
ANG_HAR22_V_c
ANG_HAR23_V_c
ANG_HAR24_V_c
ANG_HAR25_V_c
ANG_HAR26_V_c
ANG_HAR27_V_c
ANG_HAR28_V_c
ANG_HAR29_V_c
ANG_HAR30_V_c
ANG_HAR31_V_c
ANG_HAR32_V_c
ANG_HAR33_V_c
ANG_HAR34_V_c
ANG_HAR35_V_c
ANG_HAR36_V_c
ANG_HAR37_V_c
ANG_HAR38_V_c
ANG_HAR39_V_c
ANG_HAR40_V_c
ANG_HAR41_V_c
ANG_HAR42_V_c
ANG_HAR43_V_c
ANG_HAR44_V_c
ANG_HAR45_V_c
ANG_HAR46_V_c
ANG_HAR47_V_c
ANG_HAR48_V_c
ANG_HAR49_V_c
ANG_HAR50_V_c
ANG_HAR51_V_c
ANG_HAR52_V_c
ANG_HAR53_V_c
ANG_HAR54_V_c
ANG_HAR55_V_c
ANG_HAR56_V_c
ANG_HAR57_V_c
ANG_HAR58_V_c
ANG_HAR59_V_c
ANG_HAR60_V_c
ANG_HAR61_V_c
ANG_HAR62_V_c
ANG_HAR63_V_c
ANG_HAR64_V_c
ANG_HAR65_V_c
ANG_HAR66_V_c
ANG_HAR67_V_c
ANG_HAR68_V_c
ANG_HAR69_V_c
ANG_HAR70_V_c
ANG_HAR71_V_c
ANG_HAR72_V_c
ANG_HAR73_V_c
ANG_HAR74_V_c
ANG_HAR75_V_c
ANG_HAR76_V_c
ANG_HAR77_V_c
ANG_HAR78_V_c
ANG_HAR79_V_c
ANG_HAR80_V_c
ANG_HAR81_V_c
ANG_HAR82_V_c
ANG_HAR83_V_c
ANG_HAR84_V_c
ANG_HAR85_V_c
ANG_HAR86_V_c
ANG_HAR87_V_c
ANG_HAR88_V_c
ANG_HAR89_V_c
ANG_HAR90_V_c
ANG_HAR91_V_c
ANG_HAR92_V_c
ANG_HAR93_V_c
ANG_HAR94_V_c
ANG_HAR95_V_c
ANG_HAR96_V_c
ANG_HAR97_V_c
ANG_HAR98_V_c
ANG_HAR99_V_c
ANG_HAR100_V_c
ANG_HAR101_V_c
ANG_HAR102_V_c
ANG_HAR103_V_c
ANG_HAR104_V_c
ANG_HAR105_V_c
ANG_HAR106_V_c
ANG_HAR107_V_c
ANG_HAR108_V_c
ANG_HAR109_V_c
ANG_HAR110_V_c
ANG_HAR111_V_c
ANG_HAR112_V_c
ANG_HAR113_V_c
ANG_HAR114_V_c
ANG_HAR115_V_c
ANG_HAR116_V_c
ANG_HAR117_V_c
ANG_HAR118_V_c
ANG_HAR119_V_c
ANG_HAR120_V_c
ANG_HAR121_V_c
ANG_HAR122_V_c
ANG_HAR123_V_c
ANG_HAR124_V_c
ANG_HAR125_V_c
ANG_HAR126_V_c
ANG_HAR127_V_c
HAR2_I_a_%
HAR3_I_a_%
HAR4_I_a_%
HAR5_I_a_%
HAR6_I_a_%
HAR7_I_a_%
HAR8_I_a_%
HAR9_I_a_%
HAR10_I_a_%
HAR11_I_a_%
HAR12_I_a_%
HAR13_I_a_%
HAR14_I_a_%
HAR15_I_a_%
HAR16_I_a_%
HAR17_I_a_%
HAR18_I_a_%
HAR19_I_a_%
HAR20_I_a_%
HAR21_I_a_%
HAR22_I_a_%
HAR23_I_a_%
HAR24_I_a_%
HAR25_I_a_%
HAR26_I_a_%
HAR27_I_a_%
HAR28_I_a_%
HAR29_I_a_%
HAR30_I_a_%
HAR31_I_a_%
HAR32_I_a_%
HAR33_I_a_%
HAR34_I_a_%
HAR35_I_a_%
HAR36_I_a_%
HAR37_I_a_%
HAR38_I_a_%
HAR39_I_a_%
HAR40_I_a_%
HAR41_I_a_%
HAR42_I_a_%
HAR43_I_a_%
HAR44_I_a_%
HAR45_I_a_%
HAR46_I_a_%
HAR47_I_a_%
HAR48_I_a_%
HAR49_I_a_%
HAR50_I_a_%
HAR51_I_a_%
HAR52_I_a_%
HAR53_I_a_%
HAR54_I_a_%
HAR55_I_a_%
HAR56_I_a_%
HAR57_I_a_%
HAR58_I_a_%
HAR59_I_a_%
HAR60_I_a_%
HAR61_I_a_%
HAR62_I_a_%
HAR63_I_a_%
HAR64_I_a_%
HAR65_I_a_%
HAR66_I_a_%
HAR67_I_a_%
HAR68_I_a_%
HAR69_I_a_%
HAR70_I_a_%
HAR71_I_a_%
HAR72_I_a_%
HAR73_I_a_%
HAR74_I_a_%
HAR75_I_a_%
HAR76_I_a_%
HAR77_I_a_%
HAR78_I_a_%
HAR79_I_a_%
HAR80_I_a_%
HAR81_I_a_%
HAR82_I_a_%
HAR83_I_a_%
HAR84_I_a_%
HAR85_I_a_%
HAR86_I_a_%
HAR87_I_a_%
HAR88_I_a_%
HAR89_I_a_%
HAR90_I_a_%
HAR91_I_a_%
HAR92_I_a_%
HAR93_I_a_%
HAR94_I_a_%
HAR95_I_a_%
HAR96_I_a_%
HAR97_I_a_%
HAR98_I_a_%
HAR99_I_a_%
HAR100_I_a_%
HAR101_I_a_%
HAR102_I_a_%
HAR103_I_a_%
HAR104_I_a_%
HAR105_I_a_%
HAR106_I_a_%
HAR107_I_a_%
HAR108_I_a_%
HAR109_I_a_%
HAR110_I_a_%
HAR111_I_a_%
HAR112_I_a_%
HAR113_I_a_%
HAR114_I_a_%
HAR115_I_a_%
HAR116_I_a_%
HAR117_I_a_%
HAR118_I_a_%
HAR119_I_a_%
HAR120_I_a_%
HAR121_I_a_%
HAR122_I_a_%
HAR123_I_a_%
HAR124_I_a_%
HAR125_I_a_%
HAR126_I_a_%
HAR127_I_a_%
ANG_HAR2_I_a
ANG_HAR3_I_a
ANG_HAR4_I_a
ANG_HAR5_I_a
ANG_HAR6_I_a
ANG_HAR7_I_a
ANG_HAR8_I_a
ANG_HAR9_I_a
ANG_HAR10_I_a
ANG_HAR11_I_a
ANG_HAR12_I_a
ANG_HAR13_I_a
ANG_HAR14_I_a
ANG_HAR15_I_a
ANG_HAR16_I_a
ANG_HAR17_I_a
ANG_HAR18_I_a
ANG_HAR19_I_a
ANG_HAR20_I_a
ANG_HAR21_I_a
ANG_HAR22_I_a
ANG_HAR23_I_a
ANG_HAR24_I_a
ANG_HAR25_I_a
ANG_HAR26_I_a
ANG_HAR27_I_a
ANG_HAR28_I_a
ANG_HAR29_I_a
ANG_HAR30_I_a
ANG_HAR31_I_a
ANG_HAR32_I_a
ANG_HAR33_I_a
ANG_HAR34_I_a
ANG_HAR35_I_a
ANG_HAR36_I_a
ANG_HAR37_I_a
ANG_HAR38_I_a
ANG_HAR39_I_a
ANG_HAR40_I_a
ANG_HAR41_I_a
ANG_HAR42_I_a
ANG_HAR43_I_a
ANG_HAR44_I_a
ANG_HAR45_I_a
ANG_HAR46_I_a
ANG_HAR47_I_a
ANG_HAR48_I_a
ANG_HAR49_I_a
ANG_HAR50_I_a
ANG_HAR51_I_a
ANG_HAR52_I_a
ANG_HAR53_I_a
ANG_HAR54_I_a
ANG_HAR55_I_a
ANG_HAR56_I_a
ANG_HAR57_I_a
ANG_HAR58_I_a
ANG_HAR59_I_a
ANG_HAR60_I_a
ANG_HAR61_I_a
ANG_HAR62_I_a
ANG_HAR63_I_a
ANG_HAR64_I_a
ANG_HAR65_I_a
ANG_HAR66_I_a
ANG_HAR67_I_a
ANG_HAR68_I_a
ANG_HAR69_I_a
ANG_HAR70_I_a
ANG_HAR71_I_a
ANG_HAR72_I_a
ANG_HAR73_I_a
ANG_HAR74_I_a
ANG_HAR75_I_a
ANG_HAR76_I_a
ANG_HAR77_I_a
ANG_HAR78_I_a
ANG_HAR79_I_a
ANG_HAR80_I_a
ANG_HAR81_I_a
ANG_HAR82_I_a
ANG_HAR83_I_a
ANG_HAR84_I_a
ANG_HAR85_I_a
ANG_HAR86_I_a
ANG_HAR87_I_a
ANG_HAR88_I_a
ANG_HAR89_I_a
ANG_HAR90_I_a
ANG_HAR91_I_a
ANG_HAR92_I_a
ANG_HAR93_I_a
ANG_HAR94_I_a
ANG_HAR95_I_a
ANG_HAR96_I_a
ANG_HAR97_I_a
ANG_HAR98_I_a
ANG_HAR99_I_a
ANG_HAR100_I_a
ANG_HAR101_I_a
ANG_HAR102_I_a
ANG_HAR103_I_a
ANG_HAR104_I_a
ANG_HAR105_I_a
ANG_HAR106_I_a
ANG_HAR107_I_a
ANG_HAR108_I_a
ANG_HAR109_I_a
ANG_HAR110_I_a
ANG_HAR111_I_a
ANG_HAR112_I_a
ANG_HAR113_I_a
ANG_HAR114_I_a
ANG_HAR115_I_a
ANG_HAR116_I_a
ANG_HAR117_I_a
ANG_HAR118_I_a
ANG_HAR119_I_a
ANG_HAR120_I_a
ANG_HAR121_I_a
ANG_HAR122_I_a
ANG_HAR123_I_a
ANG_HAR124_I_a
ANG_HAR125_I_a
ANG_HAR126_I_a
ANG_HAR127_I_a
ANG_HAR128_I_a
HAR2_I_b_%
HAR3_I_b_%
HAR4_I_b_%
HAR5_I_b_%
HAR6_I_b_%
HAR7_I_b_%
HAR8_I_b_%
HAR9_I_b_%
HAR10_I_b_%
HAR11_I_b_%
HAR12_I_b_%
HAR13_I_b_%
HAR14_I_b_%
HAR15_I_b_%
HAR16_I_b_%
HAR17_I_b_%
HAR18_I_b_%
HAR19_I_b_%
HAR20_I_b_%
HAR21_I_b_%
HAR22_I_b_%
HAR23_I_b_%
HAR24_I_b_%
HAR25_I_b_%
HAR26_I_b_%
HAR27_I_b_%
HAR28_I_b_%
HAR29_I_b_%
HAR30_I_b_%
HAR31_I_b_%
HAR32_I_b_%
HAR33_I_b_%
HAR34_I_b_%
HAR35_I_b_%
HAR36_I_b_%
HAR37_I_b_%
HAR38_I_b_%
HAR39_I_b_%
HAR40_I_b_%
HAR41_I_b_%
HAR42_I_b_%
HAR43_I_b_%
HAR44_I_b_%
HAR45_I_b_%
HAR46_I_b_%
HAR47_I_b_%
HAR48_I_b_%
HAR49_I_b_%
HAR50_I_b_%
HAR51_I_b_%
HAR52_I_b_%
HAR53_I_b_%
HAR54_I_b_%
HAR55_I_b_%
HAR56_I_b_%
HAR57_I_b_%
HAR58_I_b_%
HAR59_I_b_%
HAR60_I_b_%
HAR61_I_b_%
HAR62_I_b_%
HAR63_I_b_%
HAR64_I_b_%
HAR65_I_b_%
HAR66_I_b_%
HAR67_I_b_%
HAR68_I_b_%
HAR69_I_b_%
HAR70_I_b_%
HAR71_I_b_%
HAR72_I_b_%
HAR73_I_b_%
HAR74_I_b_%
HAR75_I_b_%
HAR76_I_b_%
HAR77_I_b_%
HAR78_I_b_%
HAR79_I_b_%
HAR80_I_b_%
HAR81_I_b_%
HAR82_I_b_%
HAR83_I_b_%
HAR84_I_b_%
HAR85_I_b_%
HAR86_I_b_%
HAR87_I_b_%
HAR88_I_b_%
HAR89_I_b_%
HAR90_I_b_%
HAR91_I_b_%
HAR92_I_b_%
HAR93_I_b_%
HAR94_I_b_%
HAR95_I_b_%
HAR96_I_b_%
HAR97_I_b_%
HAR98_I_b_%
HAR99_I_b_%
HAR100_I_b_%
HAR101_I_b_%
HAR102_I_b_%
HAR103_I_b_%
HAR104_I_b_%
HAR105_I_b_%
HAR106_I_b_%
HAR107_I_b_%
HAR108_I_b_%
HAR109_I_b_%
HAR110_I_b_%
HAR111_I_b_%
HAR112_I_b_%
HAR113_I_b_%
HAR114_I_b_%
HAR115_I_b_%
HAR116_I_b_%
HAR117_I_b_%
HAR118_I_b_%
HAR119_I_b_%
HAR120_I_b_%
HAR121_I_b_%
HAR122_I_b_%
HAR123_I_b_%
HAR124_I_b_%
HAR125_I_b_%
HAR126_I_b_%
HAR127_I_b_%
ANG_HAR2_I_b
ANG_HAR3_I_b
ANG_HAR4_I_b
ANG_HAR5_I_b
ANG_HAR6_I_b
ANG_HAR7_I_b
ANG_HAR8_I_b
ANG_HAR9_I_b
ANG_HAR10_I_b
ANG_HAR11_I_b
ANG_HAR12_I_b
ANG_HAR13_I_b
ANG_HAR14_I_b
ANG_HAR15_I_b
ANG_HAR16_I_b
ANG_HAR17_I_b
ANG_HAR18_I_b
ANG_HAR19_I_b
ANG_HAR20_I_b
ANG_HAR21_I_b
ANG_HAR22_I_b
ANG_HAR23_I_b
ANG_HAR24_I_b
ANG_HAR25_I_b
ANG_HAR26_I_b
ANG_HAR27_I_b
ANG_HAR28_I_b
ANG_HAR29_I_b
ANG_HAR30_I_b
ANG_HAR31_I_b
ANG_HAR32_I_b
ANG_HAR33_I_b
ANG_HAR34_I_b
ANG_HAR35_I_b
ANG_HAR36_I_b
ANG_HAR37_I_b
ANG_HAR38_I_b
ANG_HAR39_I_b
ANG_HAR40_I_b
ANG_HAR41_I_b
ANG_HAR42_I_b
ANG_HAR43_I_b
ANG_HAR44_I_b
ANG_HAR45_I_b
ANG_HAR46_I_b
ANG_HAR47_I_b
ANG_HAR48_I_b
ANG_HAR49_I_b
ANG_HAR50_I_b
ANG_HAR51_I_b
ANG_HAR52_I_b
ANG_HAR53_I_b
ANG_HAR54_I_b
ANG_HAR55_I_b
ANG_HAR56_I_b
ANG_HAR57_I_b
ANG_HAR58_I_b
ANG_HAR59_I_b
ANG_HAR60_I_b
ANG_HAR61_I_b
ANG_HAR62_I_b
ANG_HAR63_I_b
ANG_HAR64_I_b
ANG_HAR65_I_b
ANG_HAR66_I_b
ANG_HAR67_I_b
ANG_HAR68_I_b
ANG_HAR69_I_b
ANG_HAR70_I_b
ANG_HAR71_I_b
ANG_HAR72_I_b
ANG_HAR73_I_b
ANG_HAR74_I_b
ANG_HAR75_I_b
ANG_HAR76_I_b
ANG_HAR77_I_b
ANG_HAR78_I_b
ANG_HAR79_I_b
ANG_HAR80_I_b
ANG_HAR81_I_b
ANG_HAR82_I_b
ANG_HAR83_I_b
ANG_HAR84_I_b
ANG_HAR85_I_b
ANG_HAR86_I_b
ANG_HAR87_I_b
ANG_HAR88_I_b
ANG_HAR89_I_b
ANG_HAR90_I_b
ANG_HAR91_I_b
ANG_HAR92_I_b
ANG_HAR93_I_b
ANG_HAR94_I_b
ANG_HAR95_I_b
ANG_HAR96_I_b
ANG_HAR97_I_b
ANG_HAR98_I_b
ANG_HAR99_I_b
ANG_HAR100_I_b
ANG_HAR101_I_b
ANG_HAR102_I_b
ANG_HAR103_I_b
ANG_HAR104_I_b
ANG_HAR105_I_b
ANG_HAR106_I_b
ANG_HAR107_I_b
ANG_HAR108_I_b
ANG_HAR109_I_b
ANG_HAR110_I_b
ANG_HAR111_I_b
ANG_HAR112_I_b
ANG_HAR113_I_b
ANG_HAR114_I_b
ANG_HAR115_I_b
ANG_HAR116_I_b
ANG_HAR117_I_b
ANG_HAR118_I_b
ANG_HAR119_I_b
ANG_HAR120_I_b
ANG_HAR121_I_b
ANG_HAR122_I_b
ANG_HAR123_I_b
ANG_HAR124_I_b
ANG_HAR125_I_b
ANG_HAR126_I_b
ANG_HAR127_I_b
HAR2_I_c_%
HAR3_I_c_%
HAR4_I_c_%
HAR5_I_c_%
HAR6_I_c_%
HAR7_I_c_%
HAR8_I_c_%
HAR9_I_c_%
HAR10_I_c_%
HAR11_I_c_%
HAR12_I_c_%
HAR13_I_c_%
HAR14_I_c_%
HAR15_I_c_%
HAR16_I_c_%
HAR17_I_c_%
HAR18_I_c_%
HAR19_I_c_%
HAR20_I_c_%
HAR21_I_c_%
HAR22_I_c_%
HAR23_I_c_%
HAR24_I_c_%
HAR25_I_c_%
HAR26_I_c_%
HAR27_I_c_%
HAR28_I_c_%
HAR29_I_c_%
HAR30_I_c_%
HAR31_I_c_%
HAR32_I_c_%
HAR33_I_c_%
HAR34_I_c_%
HAR35_I_c_%
HAR36_I_c_%
HAR37_I_c_%
HAR38_I_c_%
HAR39_I_c_%
HAR40_I_c_%
HAR41_I_c_%
HAR42_I_c_%
HAR43_I_c_%
HAR44_I_c_%
HAR45_I_c_%
HAR46_I_c_%
HAR47_I_c_%
HAR48_I_c_%
HAR49_I_c_%
HAR50_I_c_%
HAR51_I_c_%
HAR52_I_c_%
HAR53_I_c_%
HAR54_I_c_%
HAR55_I_c_%
HAR56_I_c_%
HAR57_I_c_%
HAR58_I_c_%
HAR59_I_c_%
HAR60_I_c_%
HAR61_I_c_%
HAR62_I_c_%
HAR63_I_c_%
HAR64_I_c_%
HAR65_I_c_%
HAR66_I_c_%
HAR67_I_c_%
HAR68_I_c_%
HAR69_I_c_%
HAR70_I_c_%
HAR71_I_c_%
HAR72_I_c_%
HAR73_I_c_%
HAR74_I_c_%
HAR75_I_c_%
HAR76_I_c_%
HAR77_I_c_%
HAR78_I_c_%
HAR79_I_c_%
HAR80_I_c_%
HAR81_I_c_%
HAR82_I_c_%
HAR83_I_c_%
HAR84_I_c_%
HAR85_I_c_%
HAR86_I_c_%
HAR87_I_c_%
HAR88_I_c_%
HAR89_I_c_%
HAR90_I_c_%
HAR91_I_c_%
HAR92_I_c_%
HAR93_I_c_%
HAR94_I_c_%
HAR95_I_c_%
HAR96_I_c_%
HAR97_I_c_%
HAR98_I_c_%
HAR99_I_c_%
HAR100_I_c_%
HAR101_I_c_%
HAR102_I_c_%
HAR103_I_c_%
HAR104_I_c_%
HAR105_I_c_%
HAR106_I_c_%
HAR107_I_c_%
HAR108_I_c_%
HAR109_I_c_%
HAR110_I_c_%
HAR111_I_c_%
HAR112_I_c_%
HAR113_I_c_%
HAR114_I_c_%
HAR115_I_c_%
HAR116_I_c_%
HAR117_I_c_%
HAR118_I_c_%
HAR119_I_c_%
HAR120_I_c_%
HAR121_I_c_%
HAR122_I_c_%
HAR123_I_c_%
HAR124_I_c_%
HAR125_I_c_%
HAR126_I_c_%
HAR127_I_c_%
ANG_HAR2_I_c
ANG_HAR3_I_c
ANG_HAR4_I_c
ANG_HAR5_I_c
ANG_HAR6_I_c
ANG_HAR7_I_c
ANG_HAR8_I_c
ANG_HAR9_I_c
ANG_HAR10_I_c
ANG_HAR11_I_c
ANG_HAR12_I_c
ANG_HAR13_I_c
ANG_HAR14_I_c
ANG_HAR15_I_c
ANG_HAR16_I_c
ANG_HAR17_I_c
ANG_HAR18_I_c
ANG_HAR19_I_c
ANG_HAR20_I_c
ANG_HAR21_I_c
ANG_HAR22_I_c
ANG_HAR23_I_c
ANG_HAR24_I_c
ANG_HAR25_I_c
ANG_HAR26_I_c
ANG_HAR27_I_c
ANG_HAR28_I_c
ANG_HAR29_I_c
ANG_HAR30_I_c
ANG_HAR31_I_c
ANG_HAR32_I_c
ANG_HAR33_I_c
ANG_HAR34_I_c
ANG_HAR35_I_c
ANG_HAR36_I_c
ANG_HAR37_I_c
ANG_HAR38_I_c
ANG_HAR39_I_c
ANG_HAR40_I_c
ANG_HAR41_I_c
ANG_HAR42_I_c
ANG_HAR43_I_c
ANG_HAR44_I_c
ANG_HAR45_I_c
ANG_HAR46_I_c
ANG_HAR47_I_c
ANG_HAR48_I_c
ANG_HAR49_I_c
ANG_HAR50_I_c
ANG_HAR51_I_c
ANG_HAR52_I_c
ANG_HAR53_I_c
ANG_HAR54_I_c
ANG_HAR55_I_c
ANG_HAR56_I_c
ANG_HAR57_I_c
ANG_HAR58_I_c
ANG_HAR59_I_c
ANG_HAR60_I_c
ANG_HAR61_I_c
ANG_HAR62_I_c
ANG_HAR63_I_c
ANG_HAR64_I_c
ANG_HAR65_I_c
ANG_HAR66_I_c
ANG_HAR67_I_c
ANG_HAR68_I_c
ANG_HAR69_I_c
ANG_HAR70_I_c
ANG_HAR71_I_c
ANG_HAR72_I_c
ANG_HAR73_I_c
ANG_HAR74_I_c
ANG_HAR75_I_c
ANG_HAR76_I_c
ANG_HAR77_I_c
ANG_HAR78_I_c
ANG_HAR79_I_c
ANG_HAR80_I_c
ANG_HAR81_I_c
ANG_HAR82_I_c
ANG_HAR83_I_c
ANG_HAR84_I_c
ANG_HAR85_I_c
ANG_HAR86_I_c
ANG_HAR87_I_c
ANG_HAR88_I_c
ANG_HAR89_I_c
ANG_HAR90_I_c
ANG_HAR91_I_c
ANG_HAR92_I_c
ANG_HAR93_I_c
ANG_HAR94_I_c
ANG_HAR95_I_c
ANG_HAR96_I_c
ANG_HAR97_I_c
ANG_HAR98_I_c
ANG_HAR99_I_c
ANG_HAR100_I_c
ANG_HAR101_I_c
ANG_HAR102_I_c
ANG_HAR103_I_c
ANG_HAR104_I_c
ANG_HAR105_I_c
ANG_HAR106_I_c
ANG_HAR107_I_c
ANG_HAR108_I_c
ANG_HAR109_I_c
ANG_HAR110_I_c
ANG_HAR111_I_c
ANG_HAR112_I_c
ANG_HAR113_I_c
ANG_HAR114_I_c
ANG_HAR115_I_c
ANG_HAR116_I_c
ANG_HAR117_I_c
ANG_HAR118_I_c
ANG_HAR119_I_c
ANG_HAR120_I_c
ANG_HAR121_I_c
ANG_HAR122_I_c
ANG_HAR123_I_c
ANG_HAR124_I_c
ANG_HAR125_I_c
ANG_HAR126_I_c
ANG_HAR127_I_c

## analysisNames
analysisId | analysisUnitId | analysisName
1 | 1 | three_phase_realtime
2 | 1 | three_phase_energy_demand
3 | 1 | three_phase_thd
4 | 1 | three_phase_harmonics
5 | 1 | three_phase_sequence

## applications
appId | appName | isTimer | groupId | interval | isEnable | jsonConfig | appType | 说明
1 | bacnet | true | 4 | 5000 | true | "" | 2 | 不可选,使用datalog_range,目前有:AcuCloud,BACnet/IP,SNMP
2 | alarm | true | 0 | 0 | true | "" | 2 | 2.2.1章节使用
3 | alarm_ao_range | true | 8 | 1000 | true | "" | 2 | alarm_ao功能通过此app获取数据，然后根据自己的列表匹配后通过调用doAppParamsConfig,app传aio设备serialnumber，appname传ctr_ao
4 | north | true | 4 | 60000 | true | "" | 2 | 不可选,使用datalog_range,目前有:AcuCloud,BACnet/IP,SNMP
5 | realtime_system | true | 9 | 200 | true | "" | 1
6 | realtime_channel | true | 10 | 200 | true | "" | 1
7 | energy_system | true | 11 | 3000 | true | "" | 1
8 | energy_channel | true | 12 | 3000 | true | "" | 1
9 | thd_system | true | 13 | 3000 | true | "" | 1
10 | thd_channel | true | 14 | 3000 | true | "" | 1
11 | demand_system | true | 15 | 60000 | true | "" | 1
12 | demand_channel | true | 16 | 60000 | true | "" | 1
13 | PowerQuality | true | 17 | 5000 | true | "" | 1
14 | deviceInfo | true | 18 | 60000 | true | "" | 1
15 | SOElog | true | 19 | 5000 | true | "" | 1
16 | max_demand_system | true | 20 | 5000 | true | "" | 1
17 | max_demand_channel | true | 21 | 5000 | true | "" | 1
18 | ctrl_io | true | 22 | 5000 | true | "" | 1
19 | maxmin_system | true | 23 | 5000 | true | "" | 1
20 | maxmin_channel | true | 24 | 5000 | true | "" | 1
21 | acucloud | true | 4 | 5000 | true | "" | 1
22 | mqtt | true | 31 | 5000 | true | "" | 1
23 | ClassSSetting | true | 27 | 3000 | true | "" | 1
24 | UserAndCtSetting | true | 28 | 3000 | true | "" | 1
25 | Batch_UserAndCtSetting | true | 29 | 3000 | true | "" | 1
26 | GeneralSetting | true | 30 | 3000 | true | "" | 1
27 | trendlog | true | 1 | 3000 | true | "" | 1 | 可选datalog_range参数范围，将参数选择添加到group：mqtt
28 | trendlogreal | true | 2 | 3000 | true | "" | 1 | 可选datalog_range参数范围，将参数选择添加到group：trendlog_real
29 | trendlogenergy | true | 3 | 3000 | true | "" | 1 | 可选datalog_range参数范围，将参数选择添加到group：trendlogenergy
30 | datalog1 | true | 32 | 5000 | true | "" | 1 | 可选datalog_range参数范围，将参数选择添加到group：postparam
31 | datalog2 | true | 32 | 5000 | true | "" | 1
32 | datalog3 | true | 32 | 5000 | true | "" | 1
33 | deviceInspectionInfo | true | 35 | 5000 | true | "" | 1
34 | squence_system | true | 36 | 5000 | true | "" | 1
35 | squence_channel | true | 37 | 5000 | true | "" | 1
36 | harmonic_system | true | 38 | 5000 | true | "" | 1
37 | harmonic_channel | true | 39 | 5000 | true | "" | 1
38 | snmp | true | 4 | 5000 | true | "" | 1
39 | io | true | 26 | 5000 | true | "" | 1
40 | management | false | 45 | 5000 | false | "" | 2 | 加到此处是为调用doAppParamsConfig设置寄存器使用，但此app下参数都没有读属性，所以不能调用getParamByApplicationInfo读值， 开机时tApp isTimerEnable，isEnable 同时为1时会加到采集队列 之后按需采集appType=2的app会释放

## groups
groupId | groupType | paramCount
1 | trend |  | select from datalog_range, | 此分组参数是在web界面选择增减的 9月5日文档说选择范围是datalog_range 9月6日文档没提
2 | trendreal |  |  | 9-16文档第59页说可以选，subo10月13日输出了范围，固定
3 | trendenergy
4 | north_range |  | range | AcuCloud,BACnet/IP,SNMP不可选择,MQTT可选择参数，范围都是这个。比datalog_range还多energy参数
5 | diCounterRange |  |  | 比alarm_ao_range多energy(9月5日)DI status, DI counter, RO Status, DO status; AcuCloud,BACnet/IP,SNMP不可选择MQTT可选择参数，范围都是这个。比datalog_range还多energy参数
6 | alarm_ao_maxmin_range |  |  | Demand没有min所以min默认0
7 | alarm_range |  |  | 比alarm_ao_range多DI status
8 | alarm_ao_range |  |  | Basic Parameter (不含LN),Demand, Power Quality (不含individual harmonics)
9 | realtime_system |  | readings
10 | realtime_channel
11 | energy_system
12 | energy_channel
13 | thd_system
14 | thd_channel
15 | demand_system
16 | demand_channel
17 | PowerQuality
18 | deviceInfo
19 | SOElog
20 | max_demand_system
21 | max_demand_channel
22 | ctrl_io_range
23 | maxmin_system
24 | maxmin_channel |  |  | 20-23-36-38
25 | roStatusRange |  | range | 暂时没用，后边增加时会替换
26 | io |  | readings
27 | deviceSetting_ClassS |  | conf
28 | deviceSetting_UserAndCt
29 | deviceSetting_Batch_UserAndCt
30 | deviceSetting_General |  |  | 2.4Management
31 | mqtt |  | select from basicParamRange demandRange powerQualityRange energyRange
32 | datalog
33 | SNMP
34 | doStatusRange |  | range
35 | deviceInspectionInfo |  | readings
36 | squence_system |  | readings
37 | squence_channel |  | readings
38 | harmonic_system |  | readings
39 | harmonic_channel |  | readings
40 | basicParamRange |  | range
41 | demandRange
42 | powerQualityRange
43 | energyRange
44 | diStatusRange
45 | management |  | conf

## deviceTemplateInfo
label | description | version | firmwareVersion | deviceType | protocol | pqEvent | pqEventProto | waveform | waveformProto
AcuRev-4110 | AcuRev-4110 three-phase AC meter | v1.00p01 | v1.01p22 | threePhaseACMeter | { "type": "Modbus", "transports": ["modbus-tcp", "modbus-rtu"] } | true | AcuRev4110-Class-S-Event | true | AcuRev4110-Class-S-Waveform